2023-06-30 12:35 | NO | YES | NO | 20210082 | 35765 | 2021-09-23 05:16 | ORIGINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2021-08-24 11:03 | CENTRAL | NO | 2021 | 211 WASHINGTON STREET | SELMA | DALLAS | AL | 36703-4453 | 32.4099 | -87.0206 |  |  |  | YES | [5 empty] | 2021-08-24 11:03 | 1314563 | 1314799 | NATURAL GAS |  | 2.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-08-23 18:30 | OTHER | GAS WAS CONSUMED IN EXPLOSION, THERE WAS NO SUBSEQUENT FIRE. | 2.7 | YES | 0 | 2021-08-23 18:30 | YES | OPERATOR | 2021-08-23 18:55 | 2021-08-23 18:30 | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | YES | NO | NO |  |  |  | OTHER | MATERIAL NOT INVOLVED IN INCIDENT | [9 empty] | OTHER | [8 empty] | UNREGULATED MAIN PRESSURE INTRODUCED TO CUSTOMER'S EQUIPMENT CAUSING RELEASE OF GAS. | CLASS 3 LOCATION | 200000 | 204030.0546448088 | 0 | 0 | 550 | 561.0826502732242 | 0 | 0 |  | 11.82 | 32 | 36.30564784053156146179401993355481727575 | 0 | 0 | 200582 | 90278.7707556097721373754152823920265781 | 204627.4429429225557614617940199335548173 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 20 | 25 | 192.619(A)(1) | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [221 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | BART MASON | MANAGER PIPELINE SAFETY DISTRIBUTION | bart.mason@spireenergy.com | 251-288-9616 |  | BART MASON | bart.mason@spireenergy.com | 251-288-9616 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-575-3950 | craig.hoeferlin@spireenergy.com | ON AUGUST 23, 2021 AT 6:30 PM AN EXPLOSION OCCURRED AT 211 WASHINGTON STREET, SELMA, AL, CAUSING DAMAGE TO THE BOILER ROOM AT THE SELMA CONVENTION CENTER. WHILE PERFORMING A METER SWAP-OVER FOR THE CUSTOMER FROM A UTILIZATION PRESSURE TO INTERMEDIATE PRESSURE SYSTEM, SPIRE'S SERVICE TECH FAILED TO INSTALL THE REQUIRED SERVICE REGULATOR. THIS CAUSED THE INTRODUCTION OF LINE PRESSURE TO CUSTOMER'S EQUIPMENT RESULTING IN AN EXPLOSION AND DAMAGE TO THE BUILDING. SPIRE DETERMINED THE DAMAGE EXCEEDED THE FEDERAL REPORTING LIMITS ON AUGUST 24, 2021 AT APPROXIMATELY 11 AM.
2023-06-30 12:35 | NO | YES | NO | 20210083 | 35978 | 2021-09-24 13:43 | SUPPLEMENTAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-08-25 09:55 | PACIFIC | YES | 2021 | RACE STREET & PARK AVENUE | SAN JOSE | SANTA CLARA | CA | 95126 | 37.326 | -121.9115 | [5 empty] | YES | YES |  |  | 2021-08-25 13:53 | 1314710 | 1314934 | NATURAL GAS |  | 6107 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 300 | 2021-08-25 09:55 |  |  |  | 2021-08-25 10:03 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 3 | STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 498000 | 508034.836065573912 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 498000 | 224125.512295082106 | 508034.836065573912 | 15 | 0 | 28 | 0 | 1 | 28 | 15 | 50 | 50 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | X118101646 | 811 DIG | UTILITY OWNER | YES | NO | YES | 23 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY WAS NOT LOCATED OR MARKED | [170 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | rosa.duenas@pge.com | 510-298-7063 |  | SUSIE RICHMOND | gsr8@pge.com |  | ROSA DUENAS | GAS PROGRAM MANAGER | 510-298-7063 | rosa.duenas@pge.com | A THIRD-PARTY CONTRACTOR DAMAGED A UN-MARKED 3" STEEL GAS MAIN DURING HORIZONTAL BORING. THE 3" GAS MAIN WAS NOT LOCATED BY PG&E AND WAS STRUCK BY A 10" REAMER CAUSING A RELEASE OF GAS. GAS TRAVELED IN STORM AND SEWER SYSTEMS AS WELL AS COMMUNICATIONS VAULTS. CREWS ON SITE VENTED THE GAS TO PREVENT FURTHER MIGRATION AND ISOLATE. SAFE ZONES WERE ESTABLISHED, AND THE FD ASSISTED WITH EVACUATIONS WITHIN THE ESTABLISHED ZONE. THERE WERE NO INJURIES AND/OR FATALITIES. THIS INCIDENT IS BEING REPORTED DUE TO THE DAMAGE THRESHOLD REPORTING CRITERIA OF $122K+.
2023-06-30 12:35 | NO | YES | YES | 20210084 | 35921 | 2021-10-01 17:32 | SUPPLEMENTAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2021-09-02 18:35 | EASTERN | NO | 2021 | 27 PARK ST | MAYNARD | MIDDLESEX | MA | 01754 | 42.4268 | -71.4564 |  |  | YES |  |  |  |  | YES | TD WILLIAMSON THREE WAY STOPPERS | 2021-09-02 19:45 | 1315634 | 1315635, 1315730 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2021-09-02 16:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 4 | 2021-09-02 18:35 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-09-02 16:33 | 2021-09-02 17:12 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 4 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 2 | API5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN AT THIS TIME | 0.154 | [6 empty] | OTHER | [8 empty] | UNKNOWN TILL COMPLETION OF INCIDENT ANALYSIS | CLASS 3 LOCATION | 212051 | 216323.885587431754244 | 15874 | 16193.865437158474456 | 38676 | 39455.331967213125744 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 266601 | 119984.107838114828397 | 271973.082991803354444 | 0 | 0 | 1 | 3 | 0 | 3 | 0 | 58 | 56.8 | 60 | 192.619(C) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | DRIP |  | 0.1 |  | NO |  |  |  |  | OTHER | LEAK INVESTIGATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM NEVER EXCEEDED MAOP THUS NO INVESTIGATION WAS REQUIRED | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | MEGGAN PENA | MANAGER OPERATIONS GAS COMPLIANCE | meggan.pena@eversource.com | 5084689956 |  | MEGGAN PENA | meggan.pena@eversource.com | 5084689956 | MEGGAN PENA | MANAGER OPERATIONS GAS COMPLIANCE | 5084689956 | meggan.pena@eversource.com | REPORT FILED ON BY HALF OF NSTAR GAS COMPANY D/B/A EVERSOURCE ENERGY. BASED UPON THE INITIAL NARRATIVE PROVIDED BY THE MAYNARD FIRE DEPARTMENT TO EVERSOURCE, ON SEPTEMBER 2, 2021 AT 16:14, THE MAYNARD FIRE DEPARTMENT DISPATCH RESOURCES TO 27 PARK ST MAYNARD, MA DUE TO AN ODOR CALL. THE MAYNARD FIRE DEPARTMENT ARRIVED ON SITE AT 16:17 TO A STRUCTURE FIRE. EVERSOURCE RECEIVED A CALL FROM THE MAYNARD FIRE DEPARTMENT AT 16:33 NOTIFYING EVERSOURCE OF THE SUBJECT STRUCTURE FIRE. EVERSOURCE COORDINATED WITH THE MAYNARD FIRE DEPARTMENT, MASSACHUSETTS STATE FIRE MARSHALL, AND STATE REGULATORY AGENCY ON SITE. THE SITUATION WAS MADE SAFE THROUGH A MAINLINE REPAIR ON SEPTEMBER 3, 2021. A SECTION OF THE MAIN WITH A COUPLING WAS SECURED AND DELIVERED TO THE MASSACHUSETTS MATERIAL RESEARCH FACILITY FOR 3RD PARTY ANALYSIS. NEITHER THE MAYNARD FIRE DEPARTMENT NOR THE STATE FIRE MARSHALL REPORTS HAVE BEEN RELEASED AT THIS TIME. PLEASE NOTE THE FOLLOWING AS IT RELATES TO THIS REPORT: PART A.4, A.12 THIS WAS THE TIME THE COMPANY COMMENCED A LEAK INVESTIGATION DURING WHICH GAS READINGS WERE DETECTED. THE FINAL FAILURE AND CAUSE OF THE INCIDENT IS STILL PENDING THE INVESTIGATION. PART A.21 THE COMPANY RESPONDED YES BASED UPON THE INITIAL NARRATIVE PROVIDED BY THE MAYNARD FIRE DEPARTMENT AND GAS READINGS FOUND IN NEAR PROXIMITY TO THE STRUCTURE FIRE. NEITHER THE FIRE DEPARTMENT NOR THE STATE FIRE MARSHAL HAVE ISSUED THEIR FINDINGS AS TO WHETHER RELEASED GAS CAUGHT FIRE. PART A.21.A THE TIME THE MAYNARD FIRE DEPARTMENT ARRIVED ON SITE TO A STRUCTURE FIRE. PART A.21.D PER "SECTION III. CONCLUSION" OF THE MASSACHUSETTS FIRE DISTRICT FOURTEEN'S REGIONAL FIRE INVESTIGATION TEAM FIRE ORIGIN AND CAUSE INVESTIGATION REPORT, ISSUED TO EVERSOURCE ON OCTOBER 13, 2021, "THE MOST PLAUSIBLE HYPOTHESIS IS THAT OF FUEL GAS EXPLOSION. IT IS BELIEVED TO BE AN ACCIDENTAL LOW ORDER FUEL GAS EXPLOSION CAUSED [THE] FIRE." PART A.7,A.21.C, D2.F VALUES DEFAULTED TO 1 AND 0. THE AMOUNT OF GAS RELEASE IS UNKNOWN AT THIS TIME. PART D.2.A THE PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE IS CURRENTLY BASED ON A PROPERTY ASSESSMENT PROVIDED BY THE FIRE DEPARTMENT AS WELL AS COSTS ASSOCIATED WITH LANDSCAPING, PAVING AND CONCRETE. PART D.2.B THE REPAIR COST INCLUDES THE REPAIR COSTS AS WELL AS THE FOLLOW UP LEAK SURVEY COSTS PART E.2 AN AVERAGE OPERATING PRESSURE WAS OBTAINED PRIOR TO THE INCIDENT. PART E.3.B THE MAIN WAS INSTALLED IN 1968 PRE-CODE. THE DATE FOR MAOP WAS DEFAULTED TO 7/1/1970 AS THAT WAS WHEN 192.619(C) WAS ESTABLISHED. PART E.5 THE DRIP REFERENCED IS A DRIP ODORIZER - Z9000 PART E.6 THE COMPANY TOOK MULTIPLE READINGS NONE OF WHICH REACHED OR EXCEEDED 0.15%. THE READING PROVIDED WAS THE FIRST READILY DETECTABLE LEVEL RECORDED AT 0.07. THIS REPORT FUNCTIONALITY ROUNDED THE NUMBER UP TO 0.1.
2023-06-30 12:35 | NO | YES | NO | 20210086 | 36295 | 2021-10-11 22:58 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2021-09-13 10:24 | EASTERN | YES | 2021 | 10015 W FORT ST | DETROIT | WAYNE | MI | 48209 | 42.2925 | -83.1426 | [7 empty] | YES | BAG AND STOP SYSTEM | 2021-09-13 10:24 | 1316565 | 1316953 | NATURAL GAS |  | 2.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-09-11 17:08 |  |  |  | 2021-09-11 17:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1913 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 20000 | 20403.00546448088 | 1000 | 1020.150273224044 | 1000000 | 1020150.273224044 | 1000000 | 1020150.273224044 | DAMAGE TO GREAT LAKES WATER AUTHORITY, ATT, COMAST, AND DTE ELECTRIC. | 2.75 | 6 | 6.8073089700996677740863787375415282392 | 0 | 0 | 2021006 | 909557.4717131425489601328903654485049834 | 2061730.50949476302366777408637873754153 | 4 | 0 | 7 | 0 | 0 | 7 | 4 | 2 | 2 | 2 | 192.619(A)(1) | 1970-01-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE UNEXPECTED GROUND MOVEMENT RESULTED IN TWO MAJOR HEAVE AREAS AND DAMAGE TO EXISTING BUILDINGS, PAVEMENT, AND UTILITY STRUCTURES INCLUDING DTE GAS INFRASTRUCTURE AT/NEAR THE INTERSECTION OF FORT STREET AND DEARBORN STREET IN DETROIT, MICHIGAN. INVESTIGATIONS THUS FAR CONFIRM THE GROUND FAILURE OCCURRED DUE TO A RELATIVELY RAPID LOADING OF A LAYER OF SOFT CLAYS BETWEEN 25 AND 40 FT BELOW THE GROUND SURFACE. | [154 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  |  |  |  | FRENAE F SMITH | MANAGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | 9/12/21 GROUND HEAVE 10015 WEST FORT & DEARBORN STREET: GROUND HEAVE IMPACTED THE FOLLOWING UTILITIES: GREAT LAKES WATER AUTHORITY (GLWA), ATT, COMCAST, DTE ELECTRIC, AND DTE GAS (6-INCH CI 2 PSI, 16-INCH CI 10PSI, 24-INCH STEEL 145PSI). THE INVESTIGATION IS ONGOING WITH A UNIFORMED ICS (CITY OF DETROIT, MDOT, GLWA, DTE GAS) AND NO CAUSE HAS BEEN DETERMINED YET. A SUPPLEMENTAL REPORT WILL BE FILED WITH MORE DETAILS AND FOLLOW-UP OF THIS EVENT. 1/24/2022 UPDATE ON THE INCIDENT CAUSE: ON SEPTEMBER 11, 2021, SIGNIFICANT, UNEXPECTED GROUND MOVEMENT RESULTED IN TWO MAJOR HEAVE AREAS AND DAMAGE TO EXISTING BUILDINGS, PAVEMENT, AND UTILITY STRUCTURES INCLUDING DTE GAS INFRASTRUCTURE AT/NEAR THE INTERSECTION OF FORT STREET AND DEARBORN STREET IN DETROIT, MICHIGAN. INVESTIGATIONS THUS FAR CONFIRM THE GROUND FAILURE OCCURRED DUE TO A RELATIVELY RAPID LOADING OF A LAYER OF SOFT CLAYS BETWEEN 25 AND 40 FT BELOW THE GROUND SURFACE. DTE UNDERSTANDS THAT THE RELATIVELY RAPID LOADING WAS CAUSED BY THE INCREASE IN HEIGHT AND WEIGHT OF A MILL SCALE STOCKPILE AT THE FORT IRON AND METAL FACILITY. THE GROUND FAILURE OCCURRED CONCENTRICALLY AROUND THE LARGE STOCKPILE OF MATERIAL LOCATED AT THE PROPERTY, A METAL SCRAP YARD OWNED AND OPERATED BY FORT IRON & METAL COMPANY. ON INFORMATION AND BELIEF, THE MILL SCALE MATERIAL WAS STOCKPILED TO SOME DEGREE AT THIS LOCATION BY FORT SINCE AT LEAST MAY 2019.
2023-06-30 12:35 | NO | YES | YES | 20210087 | 36110 | 2021-10-12 22:18 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2021-09-13 20:00 | MOUNTAIN | NO | 2021 | 777 CANYON ROAD | SANTA FE | SANTA FE | NM | 87501 | 35.6804 | -105.9243 | [5 empty] | YES |  |  |  | 2021-09-13 20:55 | 1316663 | 1317031 | NATURAL GAS |  | 3.8 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-09-13 10:50 | OPERATOR/CONTRACTOR |  | 2.3 | NO | 0 | 2021-09-13 10:50 | NO |  |  | 2021-09-13 09:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1971 | 1971 | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 0.75 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | OTHER | [8 empty] | AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED (55 PSIG) 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS TO ISOLATE AND PLUG THE SERVICE LINE FOR ABANDONMENT. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15.21 | 58 | 65.80398671096345514950166112956810631229 | 0 | 0 | 58 | 38.05647840531561461794019933554817275748 | 65.80398671096345514950166112956810631229 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 2016-10-27 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.5 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [221 empty] | OTHER INCORRECT OPERATION | AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED (55 PSIG) 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS TO ISOLATE AND PLUG THE SERVICE LINE FOR ABANDONMENT. CREW FAILED TO FOLLOW PROCEDURE. |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ANDREA MARTINEZ | PIPELINE SAFETY MANAGEMENT SYSTEMS MANAGER | andrea.martinez@nmgco.com | 505-697-3518 |  | ANDREA MARTINEZ | andrea.martinez@nmgco.com | 505-427-6343 | TOM BULLARD | VP ENG-GAS MGMT-TECH SERVICES | 505-697-3599 | tom.bullard@nmgco.com | ON 9/13/2021 AT 10:50 AM, WHILE A CREW WAS ISOLATING AND RETIRING A SERVICE, AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS. THE THREE-MAN CREW (ACTING FOREMAN & 2 CREWMEN) ARRIVED TO RETIRE THE 3/4-INCH STEEL SERVICE AND DISCOVERED THAT NEITHER CREW MEMBER NOR THE ACTING FOREMAN HAD BROUGHT THE SAW TO CUT THE ASPHALT TO ACCESS THE SERVICE TEE CONNECTION AND PROPERLY ISOLATE THE SERVICE FOR RETIREMENT. THE CREW DECIDED TO CONTINUE THE JOB WITHOUT RETURNING TO THE SHOP TO GET THE SAW, AND INSTEAD DECIDED TO PROCEED TO MAKE THE REPAIR HOT WITH WHAT THEY DESCRIBED AS A CUT AND PLUG PROCEDURE. DURING THE CUT AND PLUG, AN IGNITION OCCURRED, AND ONE CREWMEN SUFFERED FIRST DEGREE BURNS, AND THE OTHER SUFFERED FIRST AND SECOND DEGREE BURNS. NEITHER THE ACTING FOREMAN NOR THE CREWMEN REPORTED THE IGNITION FIRE OR INJURIES UNTIL APPROXIMATELY 14:30 THAT AFTERNOON WHEN CREWMAN #2 CALLED THE SUPERVISOR AND REPORTED THAT A FLASH HAD OCCURRED, AND HE HAD BEEN INJURED. HE WAS TOLD TO SEEK MEDICAL TREATMENT. HE WAS SEEN BUT RELEASED BY CONCENTRA. LATER THAT AFTERNOON, ALL THREE MEMBERS OF THE CREW REPORTED TO THE OFFICE FOR INTERVIEWS AT THE SANTA FE OFFICE AT APPROXIMATELY 17:20 AND UPON DISCOVERY OF THE SEVERITY OF THEIR INJURIES, THE CREWMEN WERE SENT THE HOSPITAL BY THE AREA MANAGER. BOTH CREWMEN PROCEEDED TO THE HOSPITAL, CREWMAN #2 WAS ADMITTED TO THE HOSPITAL AS THE RESULT OF THIS INJURIES, AND CREWMAN #1 WAS TREATED AND RELEASED THAT EVENING. THE INCIDENT MET REPORTABLE CRITERIA WHEN CREWMAN #2 WAS ADMITTED TO THE HOSPITAL, AND COULD NOT BE TESTED FOR DRUG AND ALCOHOL DUE TO HIS ADMITTANCE TO THE HOSPITAL. THE ACTING FOREMAN AND CREWMAN #1 WERE DRUG AND ALCOHOL TESTED. GAS ODORANT TESTING WAS PERFORMED BY NM GAS AT 21:11. READINGS CONFIRMED PROPER ODORANT AT 0.53% GAS-IN-AIR. CREW FAILED TO FOLLOW PROCEDURES.
2023-06-30 12:35 | NO | YES | NO | 20210088 | 36125 | 2021-10-20 15:18 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2021-09-28 18:00 | EASTERN | YES | 2021 | LONG STREET | FORT BRAGG | CUMBERLAND | NC | 28310 | 35.1493 | -79.0092 | [6 empty] | YES |  |  | 2021-09-28 21:49 | 1318145 | 1318329 | NATURAL GAS |  | 5269 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-09-28 18:57 | NO |  |  | 2021-09-28 18:57 | YES | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1965 | UNKNOWN |  |  |  |  | 8 | API 5L GRADE B | UNKNOWN | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 200000 | 204030.0546448088 | 15000 | 15302.25409836066 | 0 | 0 |  | 4.5 | 23711 | 26901.3504983388704318936877076411960133 | 0 | 0 | 238711 | 112318.8964040630194518272425249169435216 | 246233.6592415083304318936877076411960133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 148 | 150 | 192.619(A)(1) | 1965-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT BEING A 3RD PARTY DAMAGE AND THE CONTRACTOR DAMAGED THE LINE WHILE BORING. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | NO | [5 empty] | YES | 48 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [171 empty] | CHRISTOPHER RANSOME | GAS REGULATORY ANALYST | christopher.ransome@duke-energy.com | (704) 731-4680 |  |  |  |  | FARRIS BERRY | MANAGER PIPELINE SAFETY | (704) 731-4618 | farris.berry@duke-energy.com | A 3RD PARTY CONTRACTOR BORED INTO A HIGH PRESSURE 8" STEEL DISTRIBUTION LINE WHILE INSTALLING TELECOMMUNICATION LINES. DAMAGE RESULTED IN 1 COMMERCIAL OUTAGE. EXCAVATION WAS PERFORMED ON A EXPIRED LOCATE TICKET. THE CONTRACTOR WAS AWARE THAT THEY WERE WORKING NEAR HIGH PRESSURE LINE. BETWEEN 07/27-08/05/2021 PIEDMONT WAS ON SITE WHILE THE CONTRACTOR WORKED NEAR THE GAS LINE. THE CONTRACTOR WAS ADVISED TO CONTACT PIEDMONT FOR ADDITIONAL STANDBYS WHEN NEEDED.
2023-06-30 12:35 | NO | YES | YES | 20210089 | 36201 | 2021-10-26 22:19 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-09-27 13:25 | CENTRAL | YES | 2021 | 501 WILLOW BLVD. | WILLOW SPRINGS | COOK | IL | 60480 | 41.7326 | -87.8787 | [5 empty] | YES |  |  |  | 2021-09-27 19:07 | 1318029 | 1318263 | NATURAL GAS |  | 238.9 | 18.5 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2021-09-27 13:25 | ALLOWED TO BURN OUT |  | 238.9 | NO | 0 | 2021-09-27 13:25 |  |  |  | 2021-09-27 14:06 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2009 | 2008 |  |  |  |  | 2 | ASTM D2513 | UPONOR PIPE COMPANY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 29700 | 30298.4631147541068 | 8625 | 8798.7961065573795 | 2845 | 2902.32752732240518 | 0 | 0 |  | 5.49 | 1312 | 1488.531561461794019933554817275747508306 | 102 | 115.724252491694352159468438538205980066 | 42584 | 19456.3998165268890946511627906976744186 | 43603.8425625873798520930232558139534884 | 5 | 0 | 2 | 0 | 1 | 2 | 1 | 21 | 22 | 25 | 192.619(A)(2) | 2009-02-16 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | PROBING DEVICE | POLE | YES | x2581427 | J.U.L.I.E. | CONTRACT LOCATOR | NO | YES | YES | 15 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | lquezad@southernco.com | 6305142036 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 6305142036 | lquezad@southernco.com | BLUE PEAK TENTS, INC. PUT UP A TENT ON TUESDAY, 9/21/21. THEY UTILIZED EXISTING HOLES IN THE PARKING LOT PAVEMENT, AND MADE A NEW HOLES IN THE PARKWAY FOR THE STAKES THAT HOLD DOWN THE TENT. WHEN THE EMPLOYEES FROM BLUE PEAK TENTS, INC. CAME BACK ON MONDAY 9/27/21 TO REMOVE THE TENT, THEY USED A GASOLINE-OPERATED HYDRAULIC STAKE PULLING MACHINE TO REMOVE THE STAKES. WHILE IN THE PROCESS OF REMOVING ONE OF THE STAKES, THERE WAS IGNITION OF NATURAL GAS. TWO EMPLOYEES FROM BLUE PEAK TENTS, INC. WERE INJURED. ONE EMPLOYEE WAS TAKEN TO THE HOSPITAL AND RELEASED THE FOLLOWING DAY, AND THE OTHER REFUSED MEDICAL ATTENTION. AFTER STOPPING THE FLOW OF NATURAL GAS AND EXPOSING THE 2-INCH GAS MAIN, IT WAS REVEALED THAT A 1-INCH DIAMETER STAKE HAD PIERCED THE MAIN. PART G3, QUESTION 14: WHEN SELECTING "EXCAVATION PRACTICES NOT SUFFICIENT (OTHER)" FROM THE DROP DOWN MENU, THERE IS NO ADDITIONAL FIELD AVAILABLE TO PROVIDE AN EXPLANATION, AS REQUESTED BY PHMSA AID PERSONNEL; THEREFORE, THE EXPLANATION IS PROVIDED HERE IN PART H. EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) MEANS THE EXCAVATOR EXCAVATED OUTSIDE THE SCOPE OF THE ONE CALL TICKET.
2023-06-30 12:35 | NO | YES | NO | 20210090 | 35924 | 2021-10-27 16:43 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-09-26 17:15 | EASTERN | NO | 2021 | 13950 ANDORRA DR. | WOODBRIDGE | PRINCE WILLIAM | VA | 22193 | 38.6503 | -77.3277 | [5 empty] | YES |  |  |  | 2021-10-18 17:21 | 1319785 | 1319926 | NATURAL GAS |  | 47.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-09-26 17:15 | OPERATOR/CONTRACTOR |  | 47.5 | NO | 3 | 2021-09-26 17:40 |  |  |  | 2021-09-26 18:25 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | 1997 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | METER & REGULATOR - ALUMINUM | [9 empty] | OTHER | [8 empty] | VEHICULAR IMPACT | CLASS 4 LOCATION | 574600 | 586178.3469945356824 | 18000 | 18362.704918032792 | 1120 | 1142.56830601092928 | 383 | 390.717554644808852 | ADMIN FEE - $383.00 | 5.31 | 252 | 285.906976744186046511627906976744186047 | 0 | 0 | 594355 | 267542.1344417176646165813953488372093023 | 606360.244749968398578511627906976744186 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 30 | 30 | 33 | 192.619(A)(2) | 1997-03-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE CAUSED BY VEHICULAR IMPACT AND NOT CONTROLLER(S) OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES | YES | CITATIONS: UNREASONABLE REFUSAL, EXPIRED REGISTRATION AND OPERATING AN UNINSURED VEHICLE | YES | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [118 empty] | YES | [23 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT COMPLIANCE | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | manager dot compliance | 703-750-5558 | SHANNON MALONEY | MANAGER DOT COMPLIANCE | 703-750-5558 | smaloney@washgas.com | ON 9/26/2021 AT APPROXIMATELY 17:15 HRS A VEHICLE TRAVELLING FROM HEREFORD RD TO SOUTHBOUND MINNEVILLE RD. LEFT THE ROADWAY AND TRAVELLED APPROXIMATELY 90 FEET AND STRUCK A METER SET ASSEMBLY SUPPLIED BY A 3/4" NATURAL GAS SERVICE, LOCATED AT 13950 ANDORRA DR. WOODBRIDGE, VA. PRINCE WILLIAM COUNTY FIRE BOARD NOTIFIED WASHINGTON GAS. WASHINGTON GAS RESPONDED AND LOCATED THE NATURAL GAS SERVICE AND OBTAINED GAS OFF BY SQUEEZE IN THE AREA OF THE FRONT YARD OF THE ABOVE ADDRESS. THE DRIVER WAS TRANSPORTED TO THE LOCAL HOSPITAL FOR PRECAUTIONARY MEASURES. THE NATURAL GAS SERVICE LINE WAS CAPPED OFF DUE TO STRUCTURAL DAMAGE TO THE RESIDENCE. THIS REPORT WAS DELAYED DUE TO THE UNKNOWN ESTIMATED PROPERTY DAMAGE AND SITE ACCESS LIMITATIONS.
2023-06-30 12:35 | NO | YES | NO | 20210091 | 37292 | 2021-10-29 09:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2021-10-06 10:08 | EASTERN | YES | 2021 | 3500 LAKELAND ROAD | GAINESVILLE | HALL | GA | 30506 | 34.369 | -83.8042 |  |  |  | YES | [5 empty] | 2021-10-06 12:12 | 1318790 | 1318985 | NATURAL GAS |  | 0.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-06 10:08 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2021-10-06 10:08 |  |  |  | 2021-10-06 10:28 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | TYPICAL METER SET | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.5 | 0.5 |  | CLASS 3 LOCATION | 140000 | 142821.03825136616 | 200 | 204.0300546448088 | 200 | 204.0300546448088 | 0 | 0 |  | 6.65 | 3 | 3.4036544850498338870431893687707641196 | 0 | 0 | 140403 | 63189.1610614890647800664451827242524917 | 143232.5020151408274338870431893687707641 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | 192.619(A)(2) | 1983-08-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [217 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A NATURAL GAS METER ON THE SIDE OF A RESIDENTIAL BUILDING RUPTURED WHEN LIGHTNING HIT AN UNKNOWN LOCATION AND TRAVELED ALONG THE CUSTOMER'S FUEL LINE AND ARCED ONTO THE GAS METER. AN ELBOW THAT WAS PART OF THE CUSTOMER'S FUEL LINE APPEARED TO BE IN CONTACT WITH THE GAS METER AT THE POINT WHERE THE DAMAGE OCCURRED. THE INCIDENT OCCURRED DURING A THUNDERSTORM, AND ACCORDING TO THE CUSTOMER, POWER TO THE HOME HAD GONE OUT AND CAME BACK ON SHORTLY BEFORE THE FIRE OCCURRED. THE ESCAPING NATURAL GAS IGNITED AS A RESULT OF THE ARC AND DAMAGED THE EXTERIOR OF THE RESIDENTIAL BUILDING LOCATED ADJACENT TO THE METER. ADDITIONAL NRC REPORT NUMBER 1318985 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2023-06-30 12:35 | NO | YES | NO | 20210093 | 36232 | 2021-11-05 16:02 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-07-21 11:18 | EASTERN | NO | 2021 | JOHN JAMES WAY & JOHN MARSHALL HWY | HAYMARKET | PRINCE WILLIAM | VA | 20169 | 38.8116 | -77.6458 |  | YES |  |  |  | YES |  |  |  | 2021-10-14 14:57 | 1319484 | 1319786 | NATURAL GAS |  | 2892 | 2508 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-21 11:20 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-07-21 11:19 | 2021-07-21 12:00 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2001 | 2000 |  |  |  |  | 12 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 84887 | 86597.496243169423028 | 5476 | 5586.342896174864944 | 0 | 0 |  | 3.96 | 11452 | 12992.8837209302325581395348837209302326 | 9932 | 11268.365448504983388704318936877076412 | 111747 | 54699.0091523814314246212624584717607973 | 116445.0883087795039188438538205980066446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2001-02-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA DOES NOT HAVE ANY CONTROL OVER THIS PORTION OF THE SYSTEM. IT IS MONITORING ONLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | CONTRACTOR | UNKNOWN/OTHER | GRADING | YES | A118200220 |  | CONTRACT LOCATOR | YES | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY WAS NOT LOCATED OR MARKED | [143 empty] | YES | [26 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | (703)639-7825 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | (703)639-7825 | SHANNON B. MALONEY | MANAGER PIPELINE SAFETY COMPLIANCE QUALITY | (703)750-5558 | smaloney@washgas.com | ON 7/21/21 AT 1118 HRS, WASHINGTON GAS RECEIVED A REPORT OF A NATURAL GAS BROKEN LINE AT JOHN MARSHALL HIGHWAY AND TRADING SQUARE HAYMARKET, VA. 20169 FROM PRINCE WILLIAM COUNTY FIRE BOARD. 1119 HRS WASHINGTON GAS DISPATCHED FIELD OPS CREWS FOR RESPONSE. 1120 HRS WASHINGTON GAS RECEIVED AN ALARM ON SCADA OF PRESSURE DROPPING AND PRESSURE OPERATIONS CREWS WERE DISPATCHED. THE FIRST FIELD OPS CREW ARRIVED AT 1200 HRS AND WORKED WITH THE FIRE DEPARTMENT TO SECURE THE SCENE AND RELAY INFORMATION TO WASHINGTON GAS DISPATCH FOR ADDITIONAL SUPPORT. THE FIRST ARRIVING CREWS BEGAN TO LOCATE THE CLOSEST DISTRIBUTION VALVE. THE AREA OF THIS VALVE #1 HAD BEEN RECENTLY REGRADED AND HAD EXTENSIVE VEGETATION GROWTH. THE CREWS LOCATED A BROKEN PORTION OF A LINE MARKER (IT HAD RECENTLY BEEN BUSHED HOGGED AND BROKEN OFF) AND FOUND THE VALVE COVER WAS FOUND UNDER 3-4" OF SOIL. CUSTOMER IMPACT THROUGH THE UTILIZATION OF CRITICAL VALVES TO STOP GAS, AND AREA OF THE DAMAGE (NATURAL GAS VENTING INTO THE ATMOSPHERE IN AN OPEN LOT AND THE CLOSEST STRUCTURE APPROXIMATELY 300FT. AWAY) WERE FACTORS CONSIDERED AS PART OF THE RESPONSE PLANNING. AT APPROXIMATELY 1445 HRS WASHINGTON GAS PRESSURE OPS BEGAN TO CONTROL THE FLOW OF NATURAL GAS, REDUCING THE PRESSURE TO 5PSIG BY USE OF VALVE #1. ONCE THE PRESSURE WAS STABILIZED CREWS BEGAN TO EXCAVATE UPSTREAM AND DOWNSTREAM OF THE BREAK AREA TO INSTALL (2) 2" BYPASSES. THESE BYPASSES WERE INSTALLED TO MAINTAIN THE DOWNSTREAM CUSTOMERS AND TO USE THE EXPOSED 12' PLASTIC TO DOUBLE SQUEEZE THE PIPE. GAS WAS SQUEEZED OFF AT 0400 HRS ON 7/22/2021. FURTHER INVESTIGATION AND REPAIRS COMMENCED. CURRENT VALVE ASSIGNMENTS WERE REVALUATED NETTING AN INCREASE OF CRITICAL VALES ON THE EXISTING INFRASTRUCTURE.
2023-06-30 12:35 | NO | YES | NO | 20210094 | 36260 | 2021-11-09 15:01 | SUPPLEMENTAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-10-17 00:15 | PACIFIC | YES | 2021 | MARKET CIRCLE & HWY 183 | SALINAS | MONTEREY | CA | 93901 | 36.6863 | -121.6773 | [5 empty] | YES |  |  |  | 2021-10-17 04:37 | 1319672 | 1319741 | NATURAL GAS |  | 5485 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-10-16 17:07 | YES | OPERATOR | 2021-10-16 17:19 | 2021-10-16 18:20 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 4 | STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DIG IN | CLASS 1 LOCATION | 0 | 0 | 90860 | 92690.85382513663784 | 3785 | 3861.26878415300654 | 0 | 0 | 0 | 3 | 164550 | 186690.4485049833887043189368770764119601 | 0 | 0 | 259195 | 150563.9524374013117095182724252491694352 | 283242.5711142730330843189368770764119601 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 4 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [171 empty] | ROSA DUENAS |  | r1dj@pge.com | [5 empty] | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-328-5776 | gsr8@pge.com | PG&E WAS NOTIFIED OF A DIG IN AT MARKET CIRCLE AND HWY 183 IN SALINAS, CA. FARM OPERATOR DUG AND DAMAGED TWO PG&E SUBSURFACE GAS FACILITIES: ONE 4-INCH STEEL DISTRIBUTION PIPE AND ONE 1 1/4-INCH STEEL SERVICE PIPE WITH MAOPS OF 60 PSI. PG&E CREW ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS ON 10/17 AT 02:44 HOURS. THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA REPORTED. POLICE AND FIRE DEPARTMENT WERE ONSITE. THIS INCIDENT WAS REPORTED TO THE DOT (#1319672) AND CPUC DUE TO THE RELEASE OF GAS ESTIMATED TO BE GREATER THAN 3MMCF.
2023-06-30 12:35 | NO | NO | NO | 20210095 | 36213 | 2021-11-16 21:13 | SUPPLEMENTAL FINAL | 1720 | BRENHAM UTILITY, CITY OF | 200 W VULCAN ST | BRENHAM | TX | 77834 | 2021-10-22 09:20 | CENTRAL | NO | 2021 | HWY 290 E @ S CHAPPELL HILL ST | BRENHAM | WASHINGTON | TX | 77833 | 30.142 | -96.3821 | YES |  |  |  |  | YES |  |  |  | 2021-10-22 11:35 | 1320155 | 1320663 | NATURAL GAS |  | 250 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-22 09:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | NO | 0 | 2021-10-22 09:20 | YES | OPERATOR | 2021-10-22 09:20 | 2021-10-22 09:27 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1994 | 1992 |  |  |  |  | 6 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2904 | 2962.516393442623776 | 583 | 594.747609289617652 | 2025 | 2065.8043032786891 | COST OF BRENHAM FD ALONG WITH 3 OTHER FIRE DEPARTMENTS MUTUAL AID | 8.05 | 2013 | 2283.852159468438538205980066445182724252 | 0 | 0 | 7525 | 3801.50463618539448858471760797342192691 | 7906.920465479369066205980066445182724252 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 28 | 28 | 60 | 192.619(A)(4) | 1980-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE CHANGES WAS FROM THE DAMAGE DUE TO THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | 2178065546 | TEXAS 811 IS THE ONLY ONE-CALL | UTILITY OWNER | YES | YES | UNKNOWN/OTHER |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [169 empty] | ANDE BOSTAIN | GAS SUPERINTINDENT | abostain@cityofbrenham.org | 19793377416 | 19793377419 | ANDE BOSTAIN | abostain@cityofbrenham.org | 19794511772 | ANDE BOSTAIN | GAS SUPERINTINDENT | 19794511772 | abostain@cityofbrenham.org | THE EXCAVATOR WAS WORKING ON THE ACCESS ROAD FOR THE ENTRANCE TO THE NEW SHOPPING CENTER. THE PROJECT HAS BEEN ONGOING SINCE FEBRUARY. THEY HAD NOT STARTED ON THIS SECTION UNTIL THE LAST COUPLE OF MONTHS. AFTER REMOVING AN OLD DRIVEWAY THAT EXISTED ALONG THE ROAD THEY HAD CHANGED THE GRADE OF THE AREA BY REMOVING A PORTION OF THE DIRT THAT COVERED THE 6" MAIN. THERE HAD BEEN A LOCATE DONE FOR A FIBER CONTRACTOR THAT WAS BASICALLY ALONG THE SAME PATH OF THE ROAD CONTRACTORS WORKSITE. THE MAIN WAS FLAGGED AND MARKED CORRECTLY ALONG THE PATH. ALL THE MARKINGS WERE PRESENT WHEN BURTS CONSTRUCTION REMOVED SOME MORE MATERIAL WITH A DOZER AND THEN BROUGHT IN A RECLAIMER TO MIX THE DIRT AND ROAD BASE FOR STABILIZATION. WHEN THE MIXER STARTED TO TILL THE DIRT IT HIT THE LINE DAMAGING IT AND CAUSING AN IGNITION. THE EQUIPMENT OPERATOR SHUT OFF THE MACHINE AND JUMPED OFF BUT BUT DID GET HIS RIGHT ARM BURNT TO THE POINT HE WAS TAKEN TO THE HOSPITAL BY HELICOPTER. THE RECLAIMER WAS ENGULFED IN FLAMES AND COMPLETELY DESTROYED. WE CLOSED A VALVE OFF ON THE WEST SIDE OF THE DAMAGE AND THEN DUG UP THE 6" AND SQUEEZED IT OFF TO STOP THE FLOW OF GAS ON THE EAST SIDE. THE FIRE DEPARTMENT PUT THE FIRE OUT. I CONTACTED THE RRC BY PHONE AND ALSO THE NRC. THE RRC SENT INVESTIGATORS OUT TO ACCESS THE SCENE AND INVESTIGATE IT. I CHECKED ON THE EMPLOYEE WHO WAS INJURED AND HIS SUPERVISOR SAID HE WAS RELEASED FROM THE HOSPITAL THAT SAME NIGHT WITH SEVERE BURNS ON HIS RIGHT ARM. THE DAMAGED RECLAIMER WAS REMOVED FROM THE SPOT ON THE 25TH OF OCTOBER 2021. ON TUESDAY THE 26TH OCTOBER 2021 WE DUG UP, LOWERED AND REPAIRED THE LINE WAS DAMAGED WITH THE RRC INSPECTORS ON SITE. ON THURSDAY THE GAS DEPARTMENT EXPOSED THE GAS MAIN ALONG THE AREA IN 4 DIFFERENT SPOTS VERIFYING ITS LOCATION AND DEPTH. ALL WERE ALREADY CORRECTLY MARKED BUT THESE AREAS HAD NOT HAD DIRT REMOVED FROM THE TOP OF THEM. THE CITY OF BRENHAM GAS DEPOARTMENT WILL CONTINUE TO MARK OUR FACILITIES IN ACCORDANCE WITH THE TEXAS AMINISTRATIVE CODE TITLE 16 PART 1 CHAPTER 18 FOR UNDERGROUND PIPELINE DAMAGE PREVENTION. WE HAVE PUT IN PLACE IN OUR PLAN REVIEW FOR DEVELOPEMENT SERVICES UNDER THE GAS DEPARTMENT COMMENTS SECTION VERBIAGE STATING THAT THE BUILDER, CONTRACTOR, DEVELOPER AND/OR EXCAVATORS THAT TAKE PART IN THESE WORK PROJECTS WILL MAINTAIN CONTACT WITH THE CITY OF BRENHAM AND BE AWARE OF THEIR RESPONSIBILITY OF PROTECTION OF EXISTING CITY UNTILITIES ON THESE SITES DURING THE DURATION OF THE PROJECT.
2023-06-30 12:35 | NO | YES | YES | 20210096 | 36361 | 2021-11-17 17:43 | SUPPLEMENTAL FINAL | 22364 | WEST BATON ROUGE PARISH NATURAL GAS SYSTEM | 880 N ALEXANDER, P.O. BOX 807 | PORT ALLEN | LA | 70767 | 2021-11-01 17:00 | CENTRAL | YES | 2021 | 4826 WOODLAWN | ADDIS | WEST BATON ROUGE | LA | 70710 | 30.38 | -91.2778 |  | YES | [7 empty] | 2021-11-01 16:16 | 1320955 | 1321074 | NATURAL GAS |  | 0.23 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-11-01 11:30 | ALLOWED TO BURN OUT |  | 0.23 | NO | 0 | 2021-11-01 11:30 | YES | OPERATOR | 2021-11-01 17:30 | 2021-11-01 11:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2021 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | YES | NO | 0.75 | 2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 250 | 255.037568306011 | 2000 | 2040.300546448088 | 0 | 0 |  | 5.59 | 1 | 1.13455149501661129568106312292358803987 | 0 | 0 | 2251 | 1013.271412572845243355481727574750830565 | 2296.47266624911561129568106312292358804 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 2019-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [221 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [34 empty] | YES |  |  |  | YES | [10 empty] | ADRIAN GENRE |  | adrian.genre@wbrcouncil.org | 2253362406 |  |  |  |  | ADRIAN GENRE |  | 2253362406 | adrian.genre@wbrcouncil.org | GAS CREW WAS INSTALLING A NEW 3/4 INCH PE SERVICE LINE WITH A PLASTIC BOLT ON SERVICE TEE ON A 4" PE MAIN. THE SERVICE LINE BEING INSTALLED WITH AN EFV WAS CONNECTED TO THE SERVICE TEE AT THE MAIN. THE TAP CUTTER ON THE SERVICE TEE WAS SCREWED CLOCKWISE TO TAP INTO THE MAIN TO PROVIDE GAS TO THE NEW CUSTOMER. AFTER TAP WAS COMPLETED AND THE GAS HAD BEEN INTRODUCED INTO THE SERVICE LINE FOR APPROXIMATELY 30 MINUTES, THE TAP SIDE OF THE EFV, THE FITTING (NUT THAT FASTENS THE EFV TO THE TAP) BLEW OFF. THE EMPLOYEE THAT WAS INJURED JUMPED INTO THE HOLE AND ATTEMPTED TO SCREW THE TAP CUTTER BACK DOWN INTO THE MAIN TO STOP GAS FLOW. WHILE TURNING THE TAP, APPROXIMATELY 2 ROUNDS, THE GAS IGNITED. THE INDIVIDUAL JUMPED OUT OF THE HOLE AND A CREW MEMBER WENT TO A CLOSE BY MAIN LINE VALVE TO TURN OFF THE GAS FEEDING THE DAMAGED SERVICE LINE. THIS MAIN LINE VALVE SHUT OFF GAS DOWNSTREAM OF THE CLOSED VALVE. THERE WAS A WATER SERVICE LOCATED IN THE SAME EXCAVATION THAT MELTED AND THE WATER EXTINGUISHED THE FIRE. THE MAIN LINE VALVE WAS TURNED OFF ELIMINATING THE GAS FLOW.
2023-06-30 12:35 | NO | YES | YES | 20210097 | 36095 | 2021-11-19 15:20 | SUPPLEMENTAL FINAL | 2392 | CITIZENS GAS & COKE UTILITY | 2020 N MERIDIAN ST | INDIANAPOLIS | IN | 46202 | 2021-10-22 09:04 | EASTERN | YES | 2021 | 558 N RYBOLT AVE | INDIANAPOLIS | MARION | IN | 46222 | 39.7749 | -86.2324 |  | YES | [7 empty] | 2021-10-22 10:13 | 1320137 | 132033 & 132538 | NATURAL GAS |  | 46000 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2021-10-22 08:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 44000 | YES | 0 | 2021-10-22 08:42 |  |  |  | 2021-10-22 09:04 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1993 | 1993 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.093 |  | 2406 | LEAK |  |  | OTHER | MELT HOLE FROM CUST. FIRE PIT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 6500 | 6630.976775956286 | 22700 | 23157.4112021857988 | 0 | 0 |  | 4.6 | 211600 | 240071.0963455149501661129568106312292359 | 0 | 0 | 240800 | 151982.0274631011464199335548172757475083 | 269859.4843236570349661129568106312292359 | 0 | 0 | 6 | 3 | 1 | 1 | 0 | 26.5 | 27 | 30 | 192.619(C) | 1993-06-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION INDICATED THE CAUSE OF THE INCIDENT WAS DUE TO A CUSTOMER'S OUTDOOR FIRE PIT MELTING A HOLE IN THE PLASTIC NATURAL GAS SERVICE LINE. SCADA HAS NO CONTROL ON THIS DISTRIBUTION SERVICE LINE FAILURE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HEAT FROM THE CUSTOMER'S OUTDOOR FIRE PIT DAMAGED THE NATURAL GAS SERVICE LINE. | [154 empty] | BEN WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | bwarren@citizensenergygroup.com | 3176912514 |  |  |  |  | BEN WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | 3176912514 | bwarren@citizensenergygroup.com | THE FINDINGS OF THE INVESTIGATION BY THE FIRE DEPARTMENT REVEALED THE HOMEOWNER HAD INSTALLED A FIRE PIT DIRECTLY OVER THE NATURAL GAS DISTRIBUTION SERVICE LINE. THE NATURAL GAS SERVICE LINE IS A 1/2" PLASTIC DISTRIBUTION SERVICE LINE INSERTED INSIDE AN ABANDON 1 1/4" STEEL LINE. THE HEAT FROM THE FIRE, WITHIN THE FIREPIT, HEATED THE 1 1/4" STEEL CASING LINE THEREFORE CREATING A HOLE IN THE 1/2" PLASTIC SERVICE LINE THAT WAS INSERTED WITHIN THE 1 1/4" STEEL CASING LINE. THIS HOLE ALLOWED GAS TO ESCAPE INSIDE THE CASING AND TRAVEL TO THE RESIDENTIAL HOME IT WAS SERVING, 558 N. RYBOLT AVE. ACCUMULATION OF THE NATURAL GAS OCCURRED WITHIN THE HOME AND WAS IGNITED BY THE CUSTOMER WHEN HE TRIED TO LIGHT A CIGARETTE. CEG'S OWN INVESTIGATION FINDINGS WERE CONSISTENT WITH THE FIRE DEPARTMENT'S.
2023-06-30 12:35 | NO | YES | NO | 20210098 | 36039 | 2021-11-23 19:13 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2021-10-28 12:50 | PACIFIC | YES | 2021 | 6997 W CHRISTINE ST | RATHDRUM | KOOTENAI | ID | 83858 | 47.8134 | -116.8803 | [5 empty] | YES |  |  |  | 2021-10-28 14:52 | 1320698 | 1320844 | NATURAL GAS |  | 110 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-28 12:46 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8 | YES | 38 | 2021-10-28 12:46 | YES | OPERATOR | 2021-10-28 12:48 | 2021-10-28 10:20 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | 2015 |  |  |  |  | 2 | ASTM D2513 | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 750000 | 765112.704918033 | 27619 | 28175.530396174871236 | 0 | 0 | 0 | 0 |  | 5.27 | 580 | 658.039867109634551495016611295681063123 | 0 | 0 | 778199 | 350348.9518229877990891794019933554817276 | 793946.2751813175057874950166112956810631 | 0 | 0 | 1 | 1 | 1 | 15 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2016-04-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3.8 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES |  |  |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2021440198 | PASSWORD | CONTRACT LOCATOR | YES | YES | YES | 2 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | BRIAN SCHULTZ | PIPELINE INTEGRITY PROGRAM MANAGER | brian.schultz@avistacorp.com | 509-495-2162 |  | JOSH FORT | josh.fort@avistacorp.com | 509-495-2656 | VERN MALENSKY | MANAGER NATURAL GAS INTEGRITY AND COMPLIANCE | 509-495-2706 | vern.malensky@avistacorp.com | AT APPROXIMATELY 10:00 A.M. PDT ON OCTOBER 28, 2021, PG CONTRACTORS, A THIRD-PARTY CONTRACTOR, WAS INSTALLING TELECOMMUNICATIONS INFRASTRUCTURE USING A HORIZONTAL DIRECTIONAL DRILL WHEN THEY SEVERED A 2" POLYETHYLENE (PE) MAIN AT THE INTERSECTION OF CHRISTINE STREET AND BEECHWOOD STREET IN FRONT OF 6997 W CHRISTINE ST., RATHDRUM, IDAHO. THE PE PIPE OPERATED AT A PRESSURE OF APPROXIMATELY 55 PSIG WITH AN MAOP OF 60 PSIG, WAS AT A DEPTH OF 36 INCHES, AND LOCATE MARKS WERE PRESENT AND ACCURATE. AVISTA WAS NOTIFIED AT 10:13 A.M. PDT AND WAS ON SITE AT 10:20 A.M. PDT. THE NORTHERN LAKES FIRE DISTRICT RESPONDED AND EVACUATED 3 NEARBY RESIDENCES AT 6971, 6997 AND 7025 W CHRISTINE STREET. THE LOCATION OF THE DAMAGE REQUIRED SQUEEZING THE 2" MAIN IN THREE LOCATIONS AS IT WAS CLOSE TO A TEE. THE SQUEEZES WERE COMPLETE AT 11:43 A.M. PDT TO CONTROL THE FLOW OF GAS. THE FIRE DEPARTMENT LEFT ONCE THE SCENE WAS SECURE. UNDERGROUND BARHOLE READINGS WERE TAKEN IN FRONT OF THE THREE EVACUATED HOUSES AND SHOWED 0 PERCENT LEL. INSIDE GAS READINGS WERE TAKEN AT 6997 W CHRISTINE STREET AT APPROXIMATELY 12:10 P.M. PDT AND SHOWED READINGS BETWEEN 10% AND 70% LEL. THE GAS SERVICEMAN EXITED THE HOUSE AND LEFT THE DOORS OPEN TO AIR OUT THE HOUSE. AT APPROXIMATELY 12:30 P.M. PDT THE HOMEOWNERS AT 7025 W CHRISTINE STREET CAME HOME AND REQUESTED TO ENTER THEIR HOUSE. A GAS SERVICEMAN CHECKED EACH ROOM OF THE HOUSE WITH A COMBUSTIBLE GAS INDICATOR AND FOUND READINGS OF 0% LEL, SO THE GAS SERVICEMAN CLEARED THE HOUSE FOR THE HOMEOWNERS TO REENTER. SHORTLY THEREAFTER, THE HOMEOWNERS AT 6997 W CHRISTINE STREET REQUESTED TO GET BACK INTO THEIR HOUSE. THE GAS SERVICEMAN CHECKED EACH ROOM WITH A COMBUSTIBLE GAS INDICATOR, WHICH NOW READ 0% LEL AND HE ALLOWED THE HOMEOWNERS BACK IN THEIR HOUSE. AT THIS TIME, THE GAS AND ELECTRICITY WERE STILL SHUT OFF TO THE HOUSE AND THE ELECTRIC METER HAD TO BE RE-INSTALLED. AFTER TURNING THE ELECTRICITY BACK ON THE HOMEOWNER REPORTED POPPING NOISES COMING FROM THE FURNACE. THE GAS SERVICEMAN CHECKED NEAR THE FURNACE AND FOUND 0% LEL AND DECIDED TO TURN THE FURNACE OFF AT THE THERMOSTAT. WHILE ENTERING THE HOUSE FROM THE GARAGE, THE GAS SERVICEMAN SAW A RED GLOW ABOVE HIS HEAD WHICH WAS AN IGNITION OF GAS AT APPROXIMATELY 12:46 P.M. PDT. THE GAS SERVICEMAN EXITED THROUGH THE OPEN GARAGE DOOR AND THE MALE HOMEOWNER EXITED THROUGH THE REAR GARAGE ACCESS DOOR. INDIVIDUALS ON SCENE THEN HELPED TO GET THE FEMALE HOMEOWNER OUT OF THE UPSTAIRS OF THE HOUSE THROUGH A WINDOW. SHORTLY THEREAFTER THE BUILDING WAS CONSUMED BY FLAMES. OPERATOR PERSONNEL ON SCENE CALLED 911 IMMEDIATELY AFTER THE GAS IGNITED AND THE NORTHERN LAKES FIRE DISTRICT WAS ON SCENE AT APPROXIMATELY 12:57 P.M. PDT. THE FEMALE HOMEOWNER WAS ASSESSED BY EMTS ON SITE AND THE MALE HOMEOWNER WENT TO THE HOSPITAL TO BE TREATED FOR SECOND DEGREE BURNS ON HIS FOREARM BUT WAS NOT ADMITTED. PRELIMINARY INVESTIGATION SUGGESTS THAT THERE WAS A POCKET OF GAS INSIDE THE HOUSE IN A LOCATION THAT COULD NOT BE DETECTED BY THE GAS SERVICEMAN'S INSTRUMENT. IT WAS THAT POCKET OF GAS THAT IGNITED CAUSING THE FIRE. THE BUILDING WAS DEEMED A TOTAL LOSS WITH A VALUE EXCEEDING $122,000 RESULTING IN THIS INCIDENT BEING REPORTABLE. AVISTA DENIES LIABILITY FOR DAMAGES AND INJURIES ASSOCIATED WITH THIS INCIDENT.
2023-06-30 12:35 | NO | NO | NO | 20210099 | 37698 | 2021-11-24 21:01 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-10-24 21:35 | CENTRAL | YES | 2021 | 1146 N 32ND ROAD | OTTAWA | LASALLE | IL | 61373 | 41.3961 | -88.9442 |  |  |  | YES | [5 empty] | 2021-10-25 01:08 | 1320321 | 1320522 | NATURAL GAS |  | 3.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-24 21:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.75 | NO | 0 | 2021-10-24 22:18 |  |  |  | 2021-10-24 23:11 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2020 | 2020 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | BACK OF METER BLOW OUT DUE TO ELECTRICAL DISCHARGE | CLASS 1 LOCATION | 75000 | 76511.2704918033 | 150 | 153.0225409836066 | 500 | 510.075136612022 | 0 | 0 |  | 6.53 | 24 | 27.22923588039867109634551495016611295681 | 0 | 0 | 75674 | 34062.1230206007508905315614617940199336 | 77201.597405279327271096345514950166113 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0.25 | 0.25 | 0.3 | 192.619(A)(1) | 2020-10-16 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [185 empty] | YES | [31 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | [5 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | ON THE DATE OF THE INCIDENT, THERE WERE THUNDERSTORMS AND HIGH WINDS. IT IS BELIEVED THAT A LIGHTNING STRIKE DAMAGED A NEARBY POWER LINE. THE STATE FIRE MARSHAL INVESTIGATED THIS FIRE. THEIR INVESTIGATION SHOWS THAT CORNBELT ELECTRIC WAS AT THIS PROPERTY ABOUT ONE HOUR BEFORE THE FIRE WORKING ON A DROPPED NEUTRAL LINE. CORNBELT MADE THE REPAIRS AND MOVED ON. THE ELECTRIC AND GAS ENTER THE BUILDING IN THE SAME AREA. FIRE MARSHAL STATED THERE WERE TWO THEORIES. 1. THE DAMAGED POWER LINE MAY HAVE STARTED THE FIRE AND DROPDOWN MAY HAVE DAMAGED THE METER SET AND CAUSED THE GAS RELEASE. 2. LIGHTNING MAY HAVE STRUCK THE METER SET AND BEGAN THE FIRE. A SUB SURFACE LEAKAGE SURVEY WAS CONDUCTED OVER THE MAIN AND SERVICE LINE AND NO LEAKS WERE FOUND BELOW GRADE. THIS SERVICE LINE HAS A PROPERTY LINE REGULATOR. A GRADE 3 LEAK WAS FOUND ON THE ABOVEGROUND PROPERTY LINE REGULATOR PIPING. THIS MINOR LEAK DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. NOTE: RECORDS INDICATE THAT THE SERVICE LINE WAS INSTALLED IN 1969, BUT THE METER SET WAS COMPLETELY REPLACED ON 10-16-20. SUPPLEMENTAL/FINAL REPORT SUBMITTED PER PHMSA AID REQUEST TO UPDATE THE INFORMATION IN A-4.
2023-06-30 12:35 | NO | NO | NO | 20210100 | 36071 | 2021-12-02 13:17 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-11-03 08:35 | EASTERN | NO | 2021 | DORMANSVILLE BLVD & CHURCH RD. | UPPER MARLBORO | PRINCE GEORGES | MD | 20774 | 38.8831 | -76.7594 | YES | YES |  |  |  | YES |  |  |  | 2021-11-03 13:54 | 1321098 | 1321235 | NATURAL GAS |  | 1150 | 2587 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-03 08:39 | YES | OPERATOR | 2021-11-03 08:43 | 2021-11-03 08:49 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 108 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2006 | 2006 |  |  |  |  | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 235 | 239.73531420765034 | 10018 | 10219.865437158472792 | 383 | 390.717554644808852 | ADMIN FEE | 3.96 | 4554 | 5166.747508305647840531561461794019933555 | 10245 | 11623.4800664451827242524916943521594684 | 25435 | 14497.0521860192829597740863787375415282 | 27640.545880761762548784053156146179402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 55 | 192.619(A)(2) | 2006-09-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" PL NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 21845297 | MARYLAND 811 | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [169 empty] | RICHARD FITZPATRICK | SUPERVISOR PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | smaloney@washgas.com | 7037505558 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON NOVEMBER 3, 2021, WASHINGTON GAS WAS NOTIFIED OF A DAMAGED FACILITY NEAR DORMANSVILLE BLVD. AND CHURCH RD. UPPER MARLBORO MD. WASHINGTON GAS DISPATCHED CREWS IN RESPONSE TO THE BROKEN LINE. ONCE ARRIVED, THE DAMAGED WAS DETERMINED TO BE A TWO-WAY FEED 8" PLASTIC MAIN. THE MAIN WAS STRUCK ON A CONSTRUCTION SITE BY A BACKHOE WITH A 48" BUCKET. NO TRAFFIC WAS AFFECTED DUE TO NEW CULVERT AND BRIDGE WAS BEING CONSTRUCTED. THE GAS MAIN WAS APPROXIMATELY 10' UNDER A CREEK BED KNOWN AS BLACK BRANCH HAD BEEN PREVIOUSLY BEEN DIVERTED DUE TO THE CONSTRUCTION OF A NEW BRIDGE. THE EXCAVATOR PLEASANTS CONSTRUCTION DID HAVE A VALID MISS UTILITY TICKET BUT FAILED TO MAINTAIN MARKS IN THE EXCAVATION AREA. WASHINGTON GAS EXCAVATED ON EACH SIDE OF THE DAMAGED FACILITY AND PERFORMED A SQEEZE OFF. THE WORK AREA WAS MADE SAFE TO ENTER TO COMMENCE REPAIRS.
2023-06-30 12:35 | NO | YES | NO | 20210101 | 36147 | 2021-12-16 14:01 | SUPPLEMENTAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 220 OPERATION WAY MAIL CODE J48 | CAYCE | SC | 29033 | 2021-11-22 12:09 | EASTERN | NO | 2021 | 301 EL BETHEL ROAD | CONWAY | HORRY | SC | 29568 | 33.8613 | -79.092 | YES | [8 empty] | 2021-11-22 18:25 | 1322715 | 1322830 | NATURAL GAS |  | 162.34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-22 12:09 | YES | OPERATOR | 2021-11-22 17:31 | 2021-11-22 12:33 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 204 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2014 | 2014 |  |  |  |  | 6 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5.5 | 5.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 156189 | 159336.251024590208316 | 0 | 0 | 0 | 0 | N/A | 8.64 | 1403 | 1591.775747508305647840531561461794019934 | 0 | 0 | 157592 | 71213.6245753567779107408637873754152824 | 160928.0267720985139638405315614617940199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 2014-07-14 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE CHANGE DUE TO THE LEAK WAS NOT SUBSTANTIAL ENOUGH TO BE OBSERVED BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | 2111022187 |  | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO MAINTAIN CLEARANCE | [169 empty] | JERAMY FREE | ENGINEER III - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 803-260-3602 |  | DONALD WATFORD | donald.watford@dominionenergy.com | 843-745-7984 | CINDY OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-817-9245 | cynthia.ostrander@dominionenergy.com | SUPPLEMENTAL REPORT CREATED TO CHANGE A4 TO 12:09 P.M. WHEN THE DAMAGE WAS DONE. ON NOVEMBER 22, 2021, AT APPROXIMATELY 12:09 P.M., DOMINION ENERGY SOUTH CAROLINA (DESC) GAS OPERATIONS RESPONDED TO A NOTIFICATION FROM A THIRD PARTY CONTRACTOR CONCERNING A NATURAL GAS LEAK NEAR 301 EL BETHEL ROAD IN CONWAY, SC. THE CONTRACTOR WAS PERFORMING A DIRECTIONAL DRILLING OPERATION TO INSTALL A WATER LINE PARALLEL TO THE DESC 6-INCH PLASTIC GAS MAIN. THE BORING CONTRACTOR HAD PROPERLY NOTIFIED SC811 AND THE GAS FACILITIES WERE ACCURATELY LOCATED AND MARKED. THE CONTRACTOR PERFORMED THE BORE, AND WHILE PERFORMING THE PULL BACK, THE BORING EQUIPMENT DRIFTED OFF THE ORIGINAL BORE PATH INTO THE NATURAL GAS LINE, CAUSING A LEAK. DESC OPERATIONS CREWS WERE ABLE TO ISOLATE THE LEAK AT APPROXIMATELY BY OPERATING TWO ISOLATION VALVES. NO CUSTOMERS' GAS SERVICE WAS LOST AND THE LEAK GARNERED AND NO MEDIA COVERAGE. THE DAMAGED GAS MAIN REQUIRED EXTENSIVE REPAIRS AND A NEW GAS MAIN WAS INSTALLED. THE TOTAL COST OF THE REPAIR WAS APPROXIMATELY $156,189, WHICH EXCEEDED THE REPORTABLE THRESHOLD OF $122,000. LDF: 322718
2023-06-30 12:35 | NO | NO | NO | 20210102 | 36161 | 2021-12-20 19:51 | ORIGINAL FINAL | 39257 | INTERIOR GAS UTILITY | 2525 PHILLIPS FIELD ROAD | FAIRBANKS | AK | 99709 | 2021-11-21 17:10 | ALASKA | NO | 2021 | 2942 TRIA ROAD | FAIRBANKS | FAIRBANKS NORTH STAR BOROUGH | AK | 99709 | 64.8038 | -147.7973 | YES |  |  | YES | [5 empty] | 2021-11-22 10:10 | 1322689 | 1322785 | NATURAL GAS |  | 559 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-21 17:14 | NO |  |  | 2021-11-21 17:44 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2019 | UNKNOWN |  |  |  |  | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | RUPTURE |  |  |  |  | OTHER | SPIRAL | 120 | 0.5 |  | CLASS 2 LOCATION | 10000 | 10201.50273224044 | 32000 | 32644.808743169408 | 25000 | 25503.7568306011 | 0 | 0 |  | 11.704 | 6543 | 7423.37043189368770764119601328903654485 | 0 | 0 | 73543 | 34446.5968288764415249169435215946843854 | 75773.4387379046357076411960132890365449 | 91 | 0 | 48 | 0 | 0 | 144 | 91 | 62 | 55 | 60 | 192.621 M | 1998-06-01 | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | NO | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES |  | YES | YES |  |  |  | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [221 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [37 empty] | YES | [6 empty] | YES |  | YES |  |  | ERIK WEFLEN | MECHANICAL ENGINEER | eweflen@interiorgas.com | 9074527111 | 9074578111 |  |  |  | DAN BRITTON | GENERAL MANAGER | 9074527111 | dwbritton@interiorgas.com | THE INTERIOR GAS UTILITY (IGU) LNG STORAGE AND VAPORIZATION SITE NUMBER 3 (SS3) IN FAIRBANKS, ALASKA SENT COLD GAS AND POSSIBLY LNG TO THE DISTRIBUTION SYSTEM. WHEN THE COLD GAS OR LNG ENTERED THE DISTRIBUTION SYSTEM, IT EMBRITTLED THE 8' UNDERGROUND HDPE PIPE, WHICH SUBSEQUENTLY RUPTURED IN A SECTION OF PIPING WITHIN IGU PROPERTY. THE HIGHEST RECORDED PRESSURE DOWNSTREAM OF THE DISTRIBUTION REGULATORS AT SS3 WAS 62PSIG. AT APPROXIMATELY 4:10PM ON 11/21/2021, A TEMPERATURE SWITCH ON THE OUTLET OF THE VAPORIZER MALFUNCTIONED AND CLOSED A VALVE TO STOP THE FLOW OF LNG THROUGH THE VAPORIZER. WITH NO LNG TO VAPORIZE, THE GLYCOL HEATER TURNED OFF DUE TO LOW DEMAND. AT ABOUT 4:55PM, AN OPERATOR NOTICED THAT THE FLOW OF LNG HAD STOPPED, AND THE DISTRIBUTION PRESSURE WAS DROPPING. THE OPERATOR OPENED THE CLOSED VAPORIZER VALVE VIA REMOTE CONTROL. THE OPERATOR DID NOT NOTICE THAT THE BOILER WAS NOT FIRING AND DID NOT MONITOR THE SITE LONG ENOUGH TO VERIFY THE SYSTEM WAS STABLE AND PROPER TEMPERATURES WHERE BEING MAINTAINED. DUE TO THE MALFUNCTIONING TEMPERATURE SWITCH AND A TEMPERATURE TRANSMITTER THAT HAD NOT BEEN PROGRAMMED TO ACT AS A BACKUP TO THE TEMPERATURE SWITCH, THE CONTROL SYSTEM DID NOT STOP THE FLOW OF LNG THROUGH THE VAPORIZER, UPON A LOW GAS TEMPERATURE ON THE OUTLET OF THE VAPORIZER. THE BOILER ATTEMPTED TO FIRE ABOUT THREE MINUTES AFTER THE LNG FLOW RESUMED BUT FAILED TO STAY RUNNING. THE SYSTEM ATTEMPTED TO START A BACK-UP BOILER ABOUT 10 MINUTES LATER, ABOUT WHEN THE DISTRIBUTION LINE RUPTURED. THE STANDARD OPERATING PROCEDURES WILL BE REVISED TO NO LONGER ALLOW CONTROL CHANGES FROM VIA REMOTE CONTROL (EXCEPT FOR EMERGENCY SHUT DOWNS AND SPECIFIED EXCEPTIONS) AND INSTEAD REQUIRE THE MONITORING OPERATOR TO TRAVEL TO THE SITE TO MAKE THE NECESSARY ADJUSTMENTS AND CHANGES. THE VAPORIZER TEMPERATURE SWITCHES WILL BE RECOMMISSIONED, AND THE TEMPERATURE TRANSMITTERS WILL BE ADDED INTO THE VAPORIZER SHUTDOWN PROGRAMMING LOGIC TO ADD REDUNDANCY. ADDITIONALLY, A DOWNSTREAM TEMPERATURE TRANSMITTER LOCATED ON THE METER SKID WILL BE USED TO SHUT DOWN THE LNG PUMPS IF LOW TEMPERATURE IS DETECTED INDICATING THE VAPORIZER SHUTDOWNS FAILED TO ACTIVATE AS A RESULT OF LOW OUTLET TEMPERATURE.
2023-06-30 12:35 | YES | NO | NO | 20210103 | 37242 | 2021-12-21 11:45 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-11-22 21:37 | EASTERN | YES | 2021 | 3906 HOGARTH AVENUE | FLINT | GENESEE | MI | 48532 | 42.9961 | -83.7368 | [5 empty] | YES |  |  |  | 2021-11-23 00:14 | 1322727 | 1322826 | NATURAL GAS |  | 180 | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2021-11-22 21:37 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 180 | YES | 25 | 2021-11-22 21:37 |  |  |  | 2021-11-22 21:57 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1979 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | YES | NO | 1 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | A HOME EXPLOSION AT 3906 HOGARTH AVENUE, FLINT MI COMPROMISED THE NATURAL GAS FACILITIES (METER AND RISER) AT 3906 AND 3830 HOGARTH AVENUE CAUSING GAS TO BE RELEASED RESULTING IN SECONDARY IGNITION. | CLASS 3 LOCATION | 248800 | 253813.3879781421472 | 480 | 489.67213114754112 | 6904 | 7043.117486338799776 | 0 | 0 |  | 3.3 | 594 | 673.923588039867109634551495016611295681 | 0 | 0 | 256778 | 115685.6750108927243011561461794019933555 | 262020.1011836683552056345514950166112957 | 0 | 0 | 25 | 1 | 0 | 37 | 0 | 52 | 52 | 60 | 192.619(A)(2) | 2005-09-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [111 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON MONDAY, NOVEMBER 22, 2021 AT APPROXIMATELY 21:37 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION FROM EMERGENCY PERSONNEL OF A POSSIBLE HOME EXPLOSION IN THE 3900 BLOCK OF HOGARTH AVENUE, FLINT (GENESEE COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) AND DISTRIBUTION EMPLOYEES WERE DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 21:57 HOURS AND 22:43 HOURS RESPECTIVELY. THE GSW CONFIRMED AN EXPLOSION AND SUBSEQUENT IGNITION INVOLVING THREE HOMES 3830, 3906, AND 3910 HOGARTH AVENUE. PRIOR TO THE EXPLOSION, CONSUMERS ENERGY WAS NOT NOTIFIED OF ANY ISSUES AT THESE PROPERTIES. A HOME EXPLOSION AT 3906 HOGARTH AVENUE, FLINT MI COMPROMISED THE NATURAL GAS FACILITIES (METER AND RISER) AT 3906 AND 3830 HOGARTH AVENUE CAUSING GAS TO BE RELEASED RESULTING IN SECONDARY IGNITION. DUE TO SAFETY CONCERNS CONSUMERS ENERGY EMPLOYEES WERE UNABLE TO IMMEDIATELY ACCESS THE IMPACTED PROPERTIES BUT BEGAN INVESTIGATING THE SURROUNDING AREAS. AS A PRECAUTION, NATURAL GAS SERVICE WAS DISCONTINUED AT ALL ACCESSIBLE HOMES ON HOGARTH AVENUE BETWEEN NEDRA AVENUE AND WALTON AVENUE. CONSUMERS ENERGY ALSO ASSISTED IN THE EVACUATION OF AFFECTED RESIDENTS. ZERO UNDERGROUND GAS READS WERE DISCOVERED. THE DISTRIBUTION CREW SQUEEZED AND CAPPED THE SERVICE LINES AT THE MAIN FOR 3830, 3906, 3910 HOGARTH AVENUE. WHEN IT WAS SAFE TO DO SO, CONSUMERS ENERGY EMPLOYEES CONTINUED TO INVESTIGATE THE ACCESSIBLE AREAS FOR UNDERGROUND GAS READS. ZERO READS WERE DISCOVERED. THE FOLLOWING DAY, CONSUMERS ENERGY EMPLOYEES CONTINUED THEIR INVESTIGATION BY PERFORMING BAR HOLE TESTING OF THE SERVICE LINES AND THE PIPELINE AS WELL AS SEWERS LOCATED IN THE AREA. ADDITIONAL AIR TESTING OF THE NATURAL GAS FACILITIES WAS UNABLE TO BE PERFORMED UNTIL THE POLICE RECOVERY INVESTIGATION WAS COMPLETE. THERE WERE TWO FATALITIES AND ONE INJURY REQUIRING OVERNIGHT HOSPITALIZATION AS WELL AS PROPERTY DAMAGE TO OTHER NEIGHBORING HOMES. ON TUESDAY, NOVEMBER 30, 2021, CONSUMERS ENERGY EMPLOYEES PERFORMED AN AIR TEST AT THE OPERATING PRESSURE (52 PSIG) ON THE SERVICE LINES LOCATED AT 3830, 3906 AND 3910 HOGARTH AVENUE. ZERO LEAKS WERE DISCOVERED DURING THE TESTING. AN EVALUATION OF METER READING INFORMATION OBTAINED FROM CONSUMERS ENERGY'S METER DATA MANAGEMENT SYSTEM (MDMS) INDICATED A SIGNIFICANT INCREASE IN USAGE ON NOVEMBER 22, 2021 BETWEEN 02:00 HOURS AND 21:10 HOURS. HOWEVER, THERE WERE NO ISSUES IDENTIFIED WITH THE REGULATED FACILITIES THAT PROVIDED NATURAL GAS SERVICE TO THESE PROPERTIES. ON MONDAY, DECEMBER 6, 2021 AN INITIAL JOINT-SCENE INVESTIGATION WAS HELD AT THE SITE. A CONSUMERS ENERGY INVESTIGATOR WAS IN ATTENDANCE AND PROVIDED INFORMATION KNOWN TO DATE AS WELL AS RESULTS OF OUR INVESTIGATION. DURING THE EXAMINATION, A DISCONNECTED NATURAL GAS CUSTOMER FUEL LINE WAS DISCOVERED AT/NEAR THE WATER HEATER BY THE MICHIGAN STATE FIRE INVESTIGATOR. THE PIPE SEGMENT WAS EXAMINED AND PHOTOGRAPHED BY THOSE IN ATTENDANCE. FURTHER EXAMINATION OF THE SCENE WAS POSTPONED, AND THE SITE SECURED UNTIL ADDITIONAL EQUIPMENT COULD BE OBTAINED TO ALLOW FOR SAFE ACCESS INTO THE BASEMENT OF THE PROPERTY. IN FEBRUARY, 2022, AUTHORITIES REVISITED THE SITE AND RECOVERED EVIDENCE FOR FURTHER EXAMINATION BY IMPACTED STAKEHOLDERS. ON SEPTEMBER 7, 2022 A LABORATORY EXAMINATION OF EVIDENCE AND ARTIFACTS RECOVERED FROM THE EXPLOSION SITE WAS PERFORMED AT THE NELDERVELD INC. EXAMINATION CENTER. THE EXAMINATION CONCLUDED THAT A NATURAL GAS LEAK ORIGINATED FROM INSIDE THE HOME AT 3906 HOGARTH AVENUE, BUT AN IGNITION SOURCE COULD NOT BE DETERMINED DUE TO EXTENSIVE DAMAGE.
2023-06-30 12:35 | NO | YES | NO | 20210104 | 36172 | 2021-12-22 13:18 | ORIGINAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2021-11-29 11:00 | MOUNTAIN | NO | 2021 | 920 11TH STREET | RAPID CITY | PENNINGTON | SD | 57701 | 44.0777 | -103.2375 | [5 empty] | YES |  |  |  | 2021-11-29 11:28 | 1323119 | 1323315 | NATURAL GAS |  | 46.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-11-29 11:00 | ALLOWED TO BURN OUT |  | 10.85 | YES | 4 | 2021-11-29 10:27 | YES | OPERATOR | 2021-11-29 10:27 | 2021-11-29 10:27 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | INSIDE RESIDENTIAL STRUCTURE. | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1967 | UNKNOWN |  |  |  |  | 1 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DAMAGE PULLED DISTRIBUTION MAIN APART AT AN ELBOW FITTING CONNECTION. | CLASS 3 LOCATION | 210000 | 214231.55737704924 | 8000 | 8161.202185792352 | 6500 | 6630.976775956286 | 0 | 0 |  | 6.22 | 288 | 326.750830564784053156146179401993355482 | 0 | 0 | 224788 | 101225.4711242580005863787375415282392027 | 229350.4871693626620531561461794019933555 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 30 | 30 | 34 | 192.619(A)(1) | 1993-09-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2129918149 |  | CONTRACT LOCATOR | NO | NO | YES | 3 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NOTIFICATION TO ONE-CALL CENTER MADE, BUT NOT SUFFICIENT | [171 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 2083776032 |  | GREG WATKINS | greg.watkins@mdu.com | 2083776032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 2083776032 | greg.watkins@mdu.com | ON NOVEMBER 29, 2021 AT 9:22 A.M. MST, AN EXCAVATOR NOTIFIED MONTANA-DAKOTA UTILITIES CO. (MDU) THAT THEY DAMAGED A 1" MAIN NEAR 920 11TH STREET, RAPID CITY, SOUTH DAKOTA. AN MDU FIRST RESPONDER ARRIVED AT 10:27 A.M. MST AND AFTER CHECKING IN WITH LOCAL FIRE DEPARTMENT PERSONNEL ON SCENE, BEGAN INVESTIGATING. WHILE THE MDU EMERGENCY RESPONDERS WERE WORKING TO SECURE THE DAMAGE, THE LEAKING NATURAL GAS CAUSED BY THE EXCAVATION DAMAGE MIGRATED AND SUBSEQUENTLY IGNITED CAUSING AN EXPLOSION AND A FIRE AT 920 11TH STREET. AN MDU CREW EXCAVATED AND SQUEEZED THE 2" STEEL MAIN UPSTREAM OF THE DAMAGED 1" MAIN. THE INVESTIGATION DETERMINED THE THIRD-PARTY EXCAVATOR LOCATE TICKET EXPIRED PRIOR TO COMMENCING WORK ON THE DATE OF THE INCIDENT.
2023-06-30 12:35 | NO | YES | NO | 20210106 | 38029 | 2021-12-23 11:31 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2021-12-01 00:55 | EASTERN | NO | 2021 | 58 VERMONT STREET | BROOKLYN | KINGS | NY | 11207 | 40.6786 | -73.8959 |  |  | YES | [6 empty] | 2021-12-01 15:47 | 1323353 | 1323471 | NATURAL GAS |  | 3.95 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-01 00:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.95 | YES | 6 | 2021-12-01 00:55 |  |  |  | 2021-12-01 01:11 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER | [9 empty] | OTHER | [8 empty] | METER TAMPERING OCCURRED RESULTING IN A NATURAL GAS EXPLOSION. | CLASS 4 LOCATION | 129300 | 131905.4303278688892 | 2000 | 2040.300546448088 | 5369 | 5477.186816939892236 | 0 | 0 |  | 7.21 | 28 | 31.76744186046511627906976744186046511628 | 0 | 0 | 136697 | 61526.4235786790316069534883720930232558 | 139454.6851331173345522790697674418604651 | 0 | 0 | 3 | 2 | 0 | 3 | 0 | 0.29 | 0.29 | 0.3 | 192.623 | 2009-05-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [111 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF TRANSPORTED COMMODITY | [156 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | UPDATE 5/10/2023: WE HAVE REVIEWED THIS INCIDENT IN DETAIL AND HAVE REASON TO BELIEVE THAT THERE WAS INTENTIONAL DAMAGE TO THE METERING EQUIPMENT IN AN EFFORT TO STEAL OR ATTEMPT TO STEAL, THE TRANSPORTED GAS. ALSO, COST TO CUSTOMER PROPERTY UNKNOW; THEREFORE WE APPLIED THE MINIMUM REPORTABLE ESTIMATE OF $129,300. THIS WILL BE OUR FINAL SUBMITTAL FOR THIS INCIDENT. NATIONAL GRID WAS NOTIFIED ON 12/1/2021 AT 00:54 REGARDING A FIRE/DISTURBANCE AT 58 VERMONT ST., BROOKLYN NY BY THE FDNY. FIRST RESPONDER WAS DISPATCHED AT 00:55 AND ARRIVED AT 01:11. FDNY WAS ONSITE. LOCATION WAS MADE SAFE AT 01:32 BY SHUTTING THE CURB VALVES AT 54, 56, 58 AND 60 VERMONT ST. SERVICE TO THE RESIDENCE INVOLVED IN THE FIRE, 58 VERMONT ST, WAS LATER DISCONNECTED AT THE MAIN ON 12/2 AT 10:30. TWO RESIDENTS WERE TAKEN TO A NEARBY HOSPITAL FOR OBSERVATION. THE CAUSE OF THE FIRE AND EXPLOSION IS CURRENTLY UNKNOWN AND UNDER INVESTIGATION AS OF 12/8/2021. AS OF 12/8, WE HAVE NOT BEEN GRANTED ACCESS TO THE PREMISES SINCE THE TIME OF THE INCIDENT. AS OF 12/23 WE STILL HAVE NOT BEEN GRANTED ACCESS. FOR QUESTION A4, THE TIME AN INCIDENT CRITERIA WAS MET IS ESTIMATED. THE EXACT TIMELINE FOR FIRE AND DISTURBANCE IS NOT FULLY DIFFERENTIATED. FURTHERMORE, AT THE TIME OF REPORTING, IT IS STILL NOT KNOWN WHERE THE INCIDENT INITIATED AND WHETHER IT OCCURRED ON CUSTOMER-OWNED OR COMPANY-OWNED PIPING OR EQUIPMENT FOR REPORTING PURPOSES. FOR QUESTION E3B, INFORMATION IS FOR SERVICE PIPING.
2023-06-30 12:35 | NO | YES | NO | 20210107 | 36290 | 2021-12-23 11:51 | SUPPLEMENTAL FINAL | 31588 | COSERV GAS, LTD | 7701 SOUTH STEMMONS | CORINTH | TX | 76210 | 2021-12-03 20:58 | CENTRAL | NO | 2021 | 971 HWY. 121 | ALLEN | COLLIN | TX | 75013 | 33.1412 | -96.6793 | [5 empty] | YES |  |  |  | 2021-12-03 20:56 | 1323575 | 1323797 | NATURAL GAS |  | 59.065 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-03 20:24 | OPERATOR/CONTRACTOR |  | 0 | NO | 40 | 2021-12-03 20:24 |  |  |  | 2021-12-03 21:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2020 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | METER SET | [9 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 600000 | 612090.1639344264 | 50100 | 51109.5286885246044 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 650100 | 292578.3043032788697 | 663199.6926229510044 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.621 M | 2020-10-28 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 285 | NO | [142 empty] | RODNEY HALE | GAS COMPLIANCE MANAGER | rhale@coserv.com | 19402180258 |  | JASON WALKER | jawalker@coserv.com | 19729787928 | JASON WALKER | DIRECTOR OF GAS OPERATIONS | 19729787928 | jawalker@coserv.com | THE DRIVER WAS TRAVELING EAST ON RIDGEVIEW DR. AND FAILED TO CONTROL HIS SPEED AND LOST CONTROL OF THE VEHICLE. THE VEHICLE STRUCK THE CENTER MEDIAN, CROSSED THE WESTBOUND LANES, AND TRAVELED INTO THE BACK ENTRYWAY OF LIFETIME FITNESS. THE VEHICLE HIT THE GAS METER AT THE BACK OF THE LIFETIME FITNESS BUILDING AT 971 HWY. 121 IN ALLEN TX. IGNITING A FIRE. THE CAR WAS ON FIRE AND SITTING ON THE CURB VALVE. THE VALVE COULD NOT BE ACCESSED TO SHUT THE GAS OFF SO THE POLYETHYLENE GAS LINE FEEDING THE METER HAD TO BE EXCAVATED AND SQUEEZED TO STOP THE FLOW OF GAS AND PUT OUT THE FIRE.* THERE ARE SEVERAL NATURAL BARRIERS THAT WOULD PREVENT SOMETHING LIKE THIS FROM EVER HAPPENING AGAIN. THE CAR HAD TO BE ON ITS SIDE TO BE ABLE TO FIT BETWEEN THE CONCRETE WALL AND THE VERY LARGE TREE PROTECTING THE METER. THE VALVE WAS RE-LOCATED ACROSS THE STREET TO ENSURE THAT THERE WILL BE ACCESSIBLE IN THE EVENT SOMETHING ELSE HAPPENS TO THE METER.
2023-06-30 12:35 | NO | YES | YES | 20210108 | 36350 | 2021-12-31 17:15 | SUPPLEMENTAL FINAL | 2456 | CLARKE - MOBILE COUNTIES GAS DIST | 2003 COLLEGE AVENUE P.O. BOX 608 | JACKSON | AL | 36545 | 2021-12-01 17:24 | CENTRAL | NO | 2021 | 1177 ABB ROAD | CHATOM | WASHINGTON | AL | 36518 | 31.4419 | -88.197 |  |  |  | YES | [5 empty] | 2021-12-01 17:43 | 1323379 |  | NATURAL GAS |  | 0.126 | 0.126 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-12-01 11:23 | OPERATOR/CONTRACTOR |  | 0.12 | NO | 0 | 2021-12-01 11:23 | NO |  |  | 2021-12-01 11:23 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | CONTROLLED RELEASE / PURGING OPERATIONS. | CLASS 3 LOCATION | 0 | 0 | 134 | 136.700136612021896 | 107 | 109.156079234972708 | 0 | 0 |  | 4.525 | 1 | 1.13455149501661129568106312292358803987 | 1 | 1.13455149501661129568106312292358803987 | 243 | 109.77463867027946371096345514950166113 | 248.12531883702782659136212624584717608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 60 | 192.619(A)(2) | 2021-11-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.6 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [221 empty] | OTHER INCORRECT OPERATION | THE UTILIZED GROUNDING TECHNIQUES (TO MITIGATE STATIC ELECTRICITY) WERE INCONSISTENT WITH CMC GAS POLICY. INCONSISTENT WITH CMC GAS POLICY, TECH 1 FAILED TO EMPLOY A VENT STACK ON THE VENT OUTLET TO DIRECT THE GAS FLOW UPWARD. (SEE NARRATIVE) |  |  | YES |  |  | COMMISSIONING | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | MIKE SASSER | COMPLIANCE MANAGER | msasser@cmcgas.com | 2512462428 |  | MIKE SASSER | msasser@cmcgas.com | 2512462428 | MIKE SASSER | COMPLIANCE MANAGER | 2512462428 | msasser@cmcgas.com | REPORTABLE INCIDENT NARRATIVE ON 1 DECEMBER 2021, AT APPROXIMATELY 11:23 HOURS, A CMC GAS CREW COMMISSIONING A NEW 2-INCH MDPE MAIN OF APPROXIMATELY 6,100 LF EXPERIENCED AN UNEXPECTED INCIDENT WHERE THE VENTING GAS IGNITED, INJURING ONE EMPLOYEE. INJURIES CONSISTED OF NON-LIFE-THREATENING BURNS ON HIS UPPER BODY. A 2.0 X 0.75-INCH, HIGH-VOLUME TAP WAS INSTALLED ON THE OUTLET END OF THE PIPELINE SEGMENT. NATURAL GAS WAS INTRODUCED INTO THE PIPELINE SEGMENT FROM THE SUPPLY END OF THE PIPELINE FROM A "FARM TAP" REGULATOR STATION. GAS FLOWED, PUSHING THE AIR OUT OF THE PIPELINE FOR APPROXIMATELY 8 MINUTES. AT APPROXIMATELY THE 8-MINUTE MARK OF THE PURGE, THE PURGE TECHNICIAN (TECH 1) ON THE SITE APPROACHED THE TAP TEE WHERE GAS WAS VENTING. AS TECH 1 REACHED FOR THE TAP, AN UNEXPECTED IGNITION OF THE GAS OCCURRED. BEFORE BEING ABLE TO REMOVE HIMSELF FROM THE FLASH, TECH 1 RECEIVED MINOR BURNS ON THE FACE AND ARM AREAS. THE FIRE-WATCH TECHNICIAN (TECH 3) NOTIFIED THE TECHNICIAN OPERATING THE SUPPLY VALVE (TECH 2) OF THE INCIDENT AND REQUESTED THE SUPPLY VALVE BE CLOSED. AS THE VOLUME OF GAS IN THE PIPE DIMINISHED, THE TECH 3 EXTINGUISHED THE SMALL FLAME. APPROXIMATE 5 MINUTES ELAPSED FROM THE TIME OF IGNITION UNTIL THE FLAME WAS EXTINGUISHED. ON-SITE PERSONNEL NOTIFIED THE CONSTRUCTION AND MAINTENANCE MANAGER, WHO NOTIFIED OTHER MANAGEMENT. ON SITE PERSONNEL TRANSPORTED THE INJURED TECHNICIAN TO THE LOCAL HOSPITAL EMERGENCY ROOM, APPROXIMATELY 3 MILES AWAY. TECH 1 WAS TREATED AND TRANSPORTED TO UNIVERSITY HOSPITAL IN MOBILE, ALABAMA, WHERE HE WAS ADMITTED FOR FURTHER TREATMENT AND OBSERVATION. CMC GAS PERSONNEL PLACED A PIPE SQUEEZE DEVICE ON THE 2-INCH MDPE PIPE UNTIL THE PIPE WAS CUT AND CAPPED. UPON NOTIFICATION OF THE HOSPITALIZATION OF TECH 1 AT 17:24 HOURS, THE COMPLIANCE MANAGER NOTIFIED THE ALABAMA PUBLIC SERVICE COMMISSION, PIPELINE SAFETY DIVISION OF THE INCIDENT, AND THE NATIONAL RESPONSE CENTER. THIS CALL WAS MADE AT 17:43 HOURS. TECH 1 WAS RELEASED FROM THE UNIVERSITY HOSPITAL ON DECEMBER 8TH AND WAS SUBSEQUENTLY RELEASED TO RETURN TO WORK ON 20 DECEMBER 2021. AT THE TIME OF THIS REPORT, THE INVESTIGATION HAS REVEALED THE FOLLOWING: 1) THE BELIEVED SOURCE OF IGNITION WAS STATIC ELECTRICITY. A. AT THE TIME OF THE IGNITION, THE AMBIENT AIR RELATIVE HUMIDITY WAS REPORTED AT 20% B. AT THE TIME OF THE IGNITION, THE AMBIENT AIR TEMPERATURE WAS REPORTED AT 72 DEGREES FAHRENHEIT. 2) THE UTILIZED GROUNDING TECHNIQUES (TO MITIGATE STATIC ELECTRICITY) WERE INCONSISTENT WITH CMC GAS POLICY. 3) INCONSISTENT WITH CMC GAS POLICY, TECH 1 FAILED TO EMPLOY A VENT STACK ON THE VENT OUTLET TO DIRECT THE GAS FLOW UPWARD. 4) TECH 2 (THE VALVE OPERATOR ON THE SUPPLY END OF THE PIPELINE) WAS DETERMINED TO BE WORKING OUTSIDE HIS OPERATOR QUALIFICATION. 5) TECH 1, WHO WAS ALSO MONITORING THE PURGE OF GAS DID NOT EMPLOY A COMBUSTIBLE GAS METER (CGI) OR A PERSONAL PROTECTIVE ATMOSPHERIC METER, INCONSISTENT WITH CMC GAS POLICY. 6) TECH 1 DID NOT DON THE FIRE-RESISTANT CLOTHING AND OTHER PERSONAL PROTECTIVE EQUIPMENT (PPE) WHICH WERE PROVIDED BY CMC GAS AND IS CMC GAS STANDARD PROCEDURE. MITIGATIVE MEASURES TAKEN TO PREVENT RECURRENCE: 1) ALL RELEVANT MEMBERS OF THE 12/01/21 INCIDENT CREW HAVE BEEN DISQUALIFIED, RETRAINED, AND REQUALIFIED ON RELEVANT OQ TASKS. 2) ALL RELEVANT MEMBERS OF THE 12/01/21 INCIDENT CREW HAVE ATTENDED A POLICY, STATIC MITIGATION, AND PPE REVIEW SESSION. 3) INTERNAL DISCIPLINARY ACTIONS TAKEN AS RELEVANT.
2023-06-30 12:35 | NO | YES | NO | 20220002 | 36243 | 2022-01-07 14:08 | SUPPLEMENTAL FINAL | 22763 | WISCONSIN GAS LLC DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2021-12-11 09:02 | CENTRAL | NO | 2021 | 517 WISCONSIN STREET | WAUPACA | WAUPACA | WI | 54981 | 44.3617 | -89.0944 |  |  | YES | [6 empty] | 2021-12-11 12:37 | 1324303 | 1324403 | NATURAL GAS |  | 19 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-11 09:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 17 | YES | 8 | 2021-12-11 09:12 |  |  |  | 2021-12-11 10:20 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1991 | 1991 | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | FURNACE BUTT WELDED |  | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 400000 | 408060.1092896176 | 1700 | 1734.2554644808748 | 1500 | 1530.225409836066 | 200000 | 204030.0546448088 | BOILER, WATER HEATER, BUILDING CONTENTS | 10 | 190 | 215.564784053156146179401993355481727575 | 0 | 0 | 603390 | 271595.5694134308091375415282392026578073 | 615570.2095927964969461794019933554817276 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1991-06-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE METERSET WAS STRUCK BY A SNOW PLOW THEREFORE NO CONTROLLER OPPORTUNITY TO INFLUENCE THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | PARKING LOT | 8 | NO | [118 empty] | YES | [23 empty] | LISA NYSTROM | GAS SYSTEM ANALYST | lisa.nystrom@wecenergygroup.com | 920-433-5704 |  | LISA NYSTROM | lisa.nystrom@wecenergygroup.com | 920-433-5704 | TIM STROMMEN | MANAGER GAS CODE COMPLIANCE | 414-221-5173 | tim.strommen@we-energies.com | AT 9:12 AM ON 12/11/21, WISCONSIN GAS COMPANY WAS NOTIFIED THAT A GAS METER ASSEMBLY WAS HIT AT 517 WISCONSIN STREET, WAUPACA, WI AND THAT A FIRE/EXPLOSION HAD OCCURRED. A COMPANY FIRST RESPONDER WAS DISPATCHED TO THE SCENE AND UPON ARRIVAL FOUND THAT A TRACTOR WITH A SNOW PLOW HIT THE GAS METER ASSEMBLY WHILE REMOVING SNOW, RESULTING IN THE GAS RELEASE. THE RELEASE OF GAS WAS STOPPED AT 10:35 AM BY USE OF A SERVICE CURB VALVE. NO FATALITIES OR PERSONAL INJURIES NECESSITATING IN-PATIENT HOSPITALIZATION OCCURRED; HOWEVER, IT WAS DETERMINED THAT THE GAS RELEASE CAUSED DWELLING DAMAGES IN EXCESS OF THE 191.3 REPORTING THRESHOLD OF $122,000. THE INVESTIGATION IDENTIFIED A SEVERED PIPE NIPPLE AT THE INLET TO THE METER SET REGULATOR AS THE SOURCE OF GAS RELEASE AFTER BEING HIT DURING THE SNOW PLOWING OPERATION. EIGHT RESIDENTS WERE EVACUATED FROM THE DWELLING IMMEDIATELY AFTER THE METER SET WAS STRUCK AND THE DWELLING REMAINS UNINHABITABLE DUE TO THE DAMAGES.
2023-06-30 12:35 | NO | NO | NO | 20220003 | 36421 | 2022-01-07 14:10 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-12-08 16:43 | EASTERN | YES | 2021 | E. 11 MILE ROAD | ROYAL OAK | OAKLAND | MI | 48067 | 42.4899 | -83.1414 | [5 empty] | YES |  |  |  | 2021-12-08 23:49 | 1324037 | 1324232 | NATURAL GAS |  | 3421 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-12-08 16:43 | NO |  |  | 2021-12-08 17:08 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | UNKNOWN |  |  |  |  | 4 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 3 | 9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 575 | 586.5864071038253 | 15392 | 15702.153005464485248 | 0 | 0 |  | 4.18 | 14300 | 16224.0863787375415282392026578073089701 | 0 | 0 | 30267 | 16568.8583470058864823887043189368770764 | 32512.8257913058520762392026578073089701 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 2016-07-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | WATER | YES | B013270027 |  | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO MAINTAIN CLEARANCE | [169 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON WEDNESDAY, DECEMBER 8, 2021 AT APPROXIMATELY 16:43 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE EXCAVATION DAMAGE FROM THE CONTRACTOR PERFORMING (BORING) WORK IN THE 300 BLOCK OF ELEVEN MILE ROAD, ROYAL OAK, (OAKLAND COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:08 HOURS AND CONFIRMED A DAMAGED AND BLOWING 4-INCH NATURAL GAS PIPELINE AT 315 ELEVEN MILE ROAD. DISTRIBUTION EMPLOYEES WERE DISPATCHED AT 17:02 HOURS AND ARRIVED ONSITE AT APPROXIMATELY 18:34 HOURS. THE DISTRIBUTION CREW EXCAVATED AT REMOTE LOCATIONS AND APPLIED SQUEEZERS TO CONTAIN THE BLOWING GAS. THE DAMAGED PIPELINE SEGMENT WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FOOT OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE AND NORMAL OPERATIONS RESUMED ON THURSDAY, DECEMBER 9, 2021 AT APPROXIMATELY 14:00 HOURS. THREE COMMERCIAL CUSTOMERS EXPERIENCED A LOSS OF SERVICE AS A RESULT OF THE DAMAGE AND SUBSEQUENT REPAIR. CONSUMERS ENERGY SERVICE EMPLOYEES REMAINED ONSITE AND CONTINUOUSLY MONITORED THE LOCATION UNTIL THE GAS WAS CONTAINED AND THE PIPELINE SEGMENT WAS REPAIRED. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE DAMAGE.
2023-06-30 12:35 | NO | YES | NO | 20220004 | 36224 | 2022-01-08 15:17 | SUPPLEMENTAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2021-12-09 09:19 | CENTRAL | NO | 2021 | 3111 WYANDOTTE ST | KANSAS CITY | JACKSON | MO | 64111 | 39.0707 | -94.5884 |  | YES |  |  |  |  | YES |  |  | 2021-12-09 11:14 | 1324107 | 13242511324239 | NATURAL GAS |  | 9519 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2021-12-09 09:19 |  |  |  | 2021-12-09 09:45 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | UNKNOWN |  |  |  |  | 20 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 2.3 | [7 empty] | CLASS 3 LOCATION | 196989 | 200958.382172131203516 | 0 | 0 | 500 | 510.075136612022 | 0 | 0 |  | 4.1195 | 39214 | 44490.3023255813953488372093023255813953 | 0 | 0 | 236703 | 114610.2835434140847748604651162790697674 | 245958.7596343246208648372093023255813953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 63 | 100 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 213344010 |  | CONTRACT LOCATOR | NO | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO MAINTAIN THE MARKS | [169 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY CONTRACTOR WAS PERFORMING SEWER WORK AND WHILE BREAKING OUT A SEWER BOX THE COMPANY'S 20-INCH COATED STEEL GAS MAIN WAS STRUCK RESULTING IN A LEAK. A TEMPORARY REPAIR WAS MADE BY INSTALLING A STYLE 126 REPAIR SLEEVE. A PERMANENT REPAIR WAS MADE BY INSTALLING STOPPER FITTINGS TO ISOLATE THE SECTION OF MAIN AND REPLACE 13-FEET OF 20-INCH COATED STEEL MAIN. THE COMPANY'S FACILITIES WERE ACCURATELY MARKED ON DECEMBER 2, 2021 BUT WERE NO LONGER VISIBLE THE DAY OF THE INCIDENT. THE EXCAVATOR DID NOT REQUEST A RENEWAL OF THE LOCATE MARKS. A 48 HOUR UPDATE TO THE NRC WAS MADE ON DECEMBER 9, 2021 AT 15:46. REPORT NUMBER 1324251.
2023-06-30 12:35 | NO | NO | NO | 20220005 | 36217 | 2022-01-10 09:47 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-12-16 12:13 | EASTERN | YES | 2021 | 7224 ANNAPOLIS RD | HYATTSVILLE | PRINCE GEORGE COUNTY | MD | 20784 | 38.9481 | -76.89 |  | YES | [7 empty] | 2021-12-16 14:11 | 1324714 |  | NATURAL GAS |  | 67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-16 11:44 | OPERATOR/CONTRACTOR |  | 67 | NO | 8 | 2021-12-16 12:13 |  |  |  | 2021-12-16 12:53 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN FREQUENCY OR SEAMLESS | UNKNOWN | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC BURNT HOLE IN THE PIPE. SEE DESCRIPTION IN NARRATIVE. | CLASS 4 LOCATION | 500 | 510.075136612022 | 108 | 110.176229508196752 | 8400 | 8569.2622950819696 | 383 | 390.717554644808852 | ADMINISTRATION COSTS | 3.01 | 202 | 229.179401993355481727574750830564784053 | 0 | 0 | 9593 | 4358.972624550680684807308970099667774086 | 9809.410617840352685727574750830564784053 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 25 | 192.619(A)(4) | 1970-11-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" WRPD NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [111 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [147 empty] | YES | [20 empty] | MARK AIESI | SUPERVISOR DOT PIPELINE SAFETY | mark.aiesi@washgas.com | 5714054623 |  | MARK AIESI | mark.aiesi@washgas.com | 5714054623 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON DECEMBER 16, 2021 AT APPROXIMATELY 1213 HOURS WASHINGTON GAS WAS NOTIFIED OF A GAS FED FIRE IN FRONT OF 7224 ANNAPOLIS ROAD, HYATTSVILLE, MD. WASHINGTON GAS DISPATCHED CREWS TO THE LOCATION WHO ARRIVED AND PERFORMED AN ASSESSMENT OF SITUATION, WHICH RESULTED IN THE IDENTIFICATION OF AN 8" WRPD MAIN LINE THAT WAS FEEDING THE CONTROLLED FIRE. NO WASHINGTON GAS CREWS, OR CONTRACTORS WERE WORKING AT THIS LOCATION AT THE TIME OF IGNITION. IT WAS DETERMINED THAT A TRANSFORMER SHORTED AT SURREY LANE AND ANNAPOLIS ROAD, WHICH RESULTED IN AN ELECTRICAL DISCHARGE THROUGH AN ADJACENT METAL FENCE INTO THE GROUND. THE METAL FENCE THAT IS ESTIMATED TO BE ROUGHLY 20 YEARS OLD WAS INSTALLED DIRECTLY OVER THE 8" WRPD MAIN. EVIDENCE SUGGESTS THAT THE ELECTRICAL DISCHARGE FROM THE TRANSFORMER TRAVELED DOWN THE FENCE AND DISCHARGED AT 7224 ANNAPOLIS ROAD, RESULTING IN AN ELECTRICAL ARC TO THE PIPE. THE GAS WAS TURNED OFF UTILIZING VALVES WHICH EXTINGUISHED THE FIRE. ONCE THE AREA WAS DEEMED SAFE, CREWS STARTED PERMANENT REPAIRS TO THE PIPE, INCLUDING ADDING NEW CATHODIC PROTECTION ANODES AND A TEST STATION. THE PIPE WAS REPAIRED USING A FULL SEAL CLAMP AND WAS NOT ABLE TO BE EXAMINED FOR PIPE SPECIFICATION AND WALL THICKNESS AS A RESULT. THERE WAS ONLY MINOR PROPERTY DAMAGE, WHICH WAS TO THE CHAIN LINK FENCE THAT HAD TO BE REMOVED TO REPAIR THE MAIN.
2023-06-30 12:35 | NO | YES | NO | 20220006 | 36261 | 2022-01-20 23:52 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2021-12-21 08:52 | MOUNTAIN | NO | 2021 | 5723 SHADY OAKS DRIVE | WINDSOR | LARIMER | CO | 80528 | 40.4833 | -104.9838 | [5 empty] | YES |  |  |  | 2022-01-06 12:58 | 1326030 | 1326116 | NATURAL GAS |  | 299 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-21 08:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 299 | NO | 0 | 2021-12-21 08:52 | YES | OPERATOR | 2021-12-21 08:53 | 2021-12-21 08:52 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 17 |  |  | 2708 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 700000 | 714105.1912568308 | 21219 | 21646.568647540989636 | 2000 | 2040.300546448088 | 0 | 0 |  | 5.02 | 1501 | 1702.961794019933554817275747508305647841 | 0 | 0 | 724720 | 326470.4755689711181695780730897009966777 | 739495.0222448398111908172757475083056478 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2021-01-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | NO | [5 empty] | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [171 empty] | MARK NOLAN | PRINCIPAL ENGINEER | mark.nolan@xcelenergy.com | 303.571.3931 |  | TAMMY BOWIE | tammy.l.bowie@xcelenergy.com | 970-225-7865 | CHRIS AKINS | MANAGER PIPELINE COMPLIANCE | 303.571.3298 | christopher.a.akins@xcelenergy.com | A CONTRACTOR FOR HOME BUILDER WAS DIGGING TO LOWER WATER PIT WHEN 4" PE MAIN WAS DAMAGED AND BLOWING GAS IGNITED. NO LOCATE REQUEST WAS MADE; EXCAVATOR WAS DIGGING OFF OLD UTILITY MARKS. THE DAMAGED HOME AND SERVICE INTERRUPTIONS OCCURRED ON HOMES THAT WERE NOT YET SOLD OR OCCUPIED. LOCAL OPERATIONS OBSERVED THE FIRE AND RESPONDED TO SCENE BEFORE BEING NOTIFIED BY OUR DISPATCH OR LOCAL FIRE DEPARTMENT. A21A IGNITION TIME IS ESTIMATED, BUT GAS HAD IGNITED PRIOR TO OUR PERSONNEL'S ARRIVAL ON SCENE. D2A PROPERTY DAMAGE IS ESTIMATED.
2023-06-30 12:35 | NO | YES | NO | 20220007 | 37504 | 2022-02-04 19:20 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-01-06 14:13 | PACIFIC | NO | 2022 | 4244 BULLFROG RD | CLE ELUM | KITTITAS | WA | 98922 | 47.2059 | -120.9798 |  |  |  | YES | [5 empty] | 2022-01-06 20:39 | 1326070 | 1326135 | NATURAL GAS |  | 112 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-01-06 14:13 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 9 | NO | 0 | 2022-01-06 14:41 |  |  |  | 2022-01-06 15:30 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2008 | 2008 | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | EQUIPMENT BODY SEPARATED BY EXTERNAL LOAD | CLASS 4 LOCATION | 510450 | 510450 | 9457 | 9457 | 1583 | 1583 | 0 | 0 |  | 11 | 1232 | 1232 | 0 | 0 | 522722 | 230773.9189599540883755344070278184480234 | 522722 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 50 | 60 | 192.619(A)(2) | 2008-05-02 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 8.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | HEAVY SNOWFALL | [212 empty] | MICHAEL KIDD | REGULATORY COMPLIANCE ANALYST | michael.kidd@pse.com | [5 empty] | YVONNE WANG | SUPERVISOR COMPLIANCE SUPPORT | 425-424-7477 | yvonne.wang@pse.com | ON JANUARY 6, 2022, CLE ELUM FIRE DEPARTMENT CALLED PSE AT 14:41 NOTIFYING OF A FIRE AT A COMMERCIAL METER SET THAT PROVIDED TWO PSIG TO A LAUNDRY BUSINESS. PSE'S GAS FIRST RESPONSE (GFR) PERSONNEL ARRIVED ONSITE AT 15:30 AND FOUND THAT THE OUTLET VALVE AT THE METER SET HAD BEEN TURNED OFF PRIOR TO THEIR ARRIVAL. THE FIRE HAD ALREADY BEEN EXTINGUISHED BY CLE ELUM FIRE DEPARTMENT. PSE'S GFR MADE THE SITUATION SAFE AND LOCKED OFF THE MSA VALVE AT 19:30 ON JANUARY 6, 2022. PSE'S CONTRACTOR INFRASOURCE (IFS) CUT AND CAPPED THE SERVICE ON JANUARY 7, 2022 AT 19:41. ONE CUSTOMER LOST SERVICE AND NO EVACUATION WAS REQUIRED. NO INJURIES OR FATALITIES OCCURRED IN CONNECTION TO THIS INCIDENT. A FIRE OF UNKNOWN SOURCE AND ORIGIN IN THE BUILDING MELTED SNOW NEAR THE PEAK OF THE BUILDING. A LARGE AMOUNT OF SNOW AND ICE SLID OFF THE ROOF AND BROKE THE RELIEF VALVE VENT PIPING ON THE GAS METERSET. GAS LEAKING FROM THE BROKEN VENT PIPE WAS IGNITED BY THE FIRE IN THE BUILDING. PSE NOTIFIED THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION (WUTC) ON JANUARY 6, 2022 AT 17:30 DUE TO UNINTENTIONAL IGNITION OF GAS. PSE MADE FIRST TELEPHONIC NOTICE TO DOT ON JANUARY 6, 2022 AT 20:39, NRC # 1326070 WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGES EXCEEDED $ 122,000. THE SECOND TELEPHONIC NOTICE WAS MADE TO DOT WITHIN 48 HOURS ON JANUARY 7, 2022 AT 16:22, NRC # 1326135.
2023-06-30 12:35 | NO | YES | NO | 20220008 | 36717 | 2022-02-07 11:14 | SUPPLEMENTAL FINAL | 7348 | DOMINION ENERGY WEST VIRGINIA | 48 COLUMBIA BLVD | CLARKSBURG | WV | 26301 | 2022-01-08 20:00 | EASTERN | NO | 2022 | 305 POWELL STREET | GLENVILLE | GILMER | WV | 26351 | 38.9327 | -80.8371 |  | YES | [7 empty] | 2022-01-08 21:10 | 1326175 | 1326260 | NATURAL GAS |  | 7446 | 4265 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-08 11:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-08 12:00 | 2022-01-08 12:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1947 | UNKNOWN |  |  |  |  | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 116531 | 116531 | 0 | 0 | 66638 | 66638 | 0 | 0 |  | 3.361 | 25026 | 25026 | 14335 | 14335 | 222530 | 103570.8298401174115506134699853587115667 | 222530 | 51 | 0 | 111 | 0 | 0 | 111 | 51 | 2.18 | 0.5 | 0.75 | 192.623 | 1947-11-08 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE ALREADY MONITORING SYSTEM PRESSURES DUE TO COLD WEATHER AND WERE AWARE OF THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [196 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [40 empty] | YES |  | YES | [30 empty] | CHELSEA MINUTELLI | GAS PIPELINE COMPLIANCE ANALYST | chelsea.m.minutelli@dominionenergy.com | 3046769284 |  | CHELSEA MINUTELLI | chelsea.m.minutelli@dominionenergy.com | 3046769284 | CAROL HAGER | MANAGER- GAS OPERATIONS PIPELINE INTEGRITY | 3304379557 | carol.m.hager@dominionenergy.com | ON 1/8/2022, DEWV PERSONNEL WERE MONITORING SYSTEM PRESSURES BECAUSE OF COLD WEATHER. IN THE COURSE OF DOING THIS, THEY IDENTIFIED A PRESSURE INCREASE FROM 8 OUNCES TO 10 OUNCES AT 11:00 HOURS; AND ANOTHER INCREASE FROM 10 OUNCES TO 35 OUNCES AT 12:00 HOURS. THE PRESSURE RETURNED TO 8 OUNCES AT 13:00 HOURS, WHICH IS BELIEVED TO BE FROM AN INCREASE IN TEMPERATURE RELIEVING MOISTURE AND ICE FROM THE REGULATORS. DURING THE EVENT, A LEAK WAS DISCOVERED ON A MAINLINE. THREE REGULATING STATIONS THAT FEED THE SYSTEM WERE SHUT IN, CREATING AN OUTAGE FOR 162 CUSTOMERS. THE MAINLINE LEAK WAS REPAIRED, THE SYSTEM WAS LEAK SURVEYED WITH NO ADDITIONAL HAZARDOUS LEAKS FOUND, AND SAFETY CHECKS AND RESTORATION OF CUSTOMERS WERE INITIATED BEGINNING ON THE MORNING OF 1/9/2022.
2023-06-30 12:35 | NO | NO | NO | 20220009 | 36309 | 2022-02-08 12:13 | ORIGINAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2021-02-23 11:55 | EASTERN | NO | 2021 | GATEWAY BLVD. & WESLEY CHAPEL BLVD. | WESLEY CHAPEL | PASCO | FL | 33544 | 28.2382 | -82.3616 |  |  |  | YES | [5 empty] | 2022-02-08 08:10 | 1328385 |  | NATURAL GAS |  | 357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-23 11:55 |  |  |  | 2021-02-23 11:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 80 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 31000 | 31624.658469945364 | 42478 | 43333.943306010941032 | 0 | 0 |  | 9 | 3213 | 3645.313953488372093023255813953488372093 | 0 | 0 | 76691 | 35177.0619162219038171627906976744186047 | 78603.9157294446771250232558139534883721 | 50 | 0 | 821 | 0 | 0 | 821 | 50 | 45 | 45 | 60 | 192.619(A)(2) | 2004-12-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A 3RD PARTY LINE STRIKE TO OPERATOR'S SYSTEM, AND AS SUCH, THE CONTROLLER(S) OR CONTROL ROOM WERE NOT THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 028100002 | SUNSHINE STATE ONE CALL OF FLORIDA | FACILITY OWNER | YES | YES | YES | 18 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | [5 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 4074206667 | rharris@tecoenergy.com | THIRD PARTY CONTRACTOR STRUCK PEOPLES GAS SYSTEM'S MAIN DURING HDD OPERATION. UPON ARRIVAL ON SCENE AFTER THE REPORT OF THE DAMAGE, THE OPERATOR DID NOT IDENTIFY ANY PHYSICAL EVIDENCE THAT THE THIRD PARTY PERFORMED SPOT DIGGING TO IDENTIFY THE UTILITIES. PIPELINE WAS TOO DEEP TO DIG UP AND SQUEEZE, SO OPERATOR TURNED OFF CRITICAL VALVE STOPPING FLOW OF GAS. PRETESTED PIPELINE WAS INSTALLED, REPAIRS FINALIZED, AND RESTORATION COMPLETED.
2023-06-30 12:35 | NO | YES | NO | 20220010 | 36314 | 2022-02-08 16:05 | ORIGINAL | 12672 | MONROE NATURAL GAS DEPT, CITY OF | 300 W. CROWELL STREET | MONROE | NC | 28112 | 2022-01-04 17:15 | EASTERN | NO | 2022 | INTERSECTION OF ROCKY RIVER RD AND SECREST SHORT CUT RD. | MONROE | UNION | NC | 28110 | 35.0571 | -80.5936 | YES | [8 empty] | 2022-01-04 18:00 | 1325889 | 1326041, 1326048 | NATURAL GAS |  | 4266.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-04 15:09 | YES | OPERATOR | 2022-01-04 15:13 | 2022-01-04 15:30 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 127 | NO | YES |  |  |  |  | YES | CASED, BORED/DRILLED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2006 | 2004 |  |  |  |  | 6 | API 5L GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 52266 | 52266 | 0 | 0 | 0 | 0 |  | 16.8755 | 71999 | 71999 | 0 | 0 | 124265 | 64697.0034225911353219121522693997071742 | 124265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 265 | 275 | 192.619(A)(1) | 2006-03-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 5.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | BORING | WATER | YES | C213551031 | N/A | FACILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | DARWIN DE LOS SANTOS | NATURAL GAS ENGINEERING AND COMPLIANCE MANAGER | ddelossantos@monroenc.org | 7042824697 | 704-283-6492 | ROBERT MILLER | rmiller@monroenc.org | 704-282-4638 | DAVID LUCORE | DIRECTOR OF ENERGY SERVICES | 704-282-4602 | dlucore@monroenc.org | ON 01/04/2022 AT 3:09 PM - CDM SMITH STRUCK THE CITY OF MONROE'S 6-INCH STEEL 275 PSIG GAS MAIN WHILE MAKING A BORE ACROSS THE INTERSECTION OF ROCKY RIVER ROAD AND SECREST SHORTCUT ROAD IN MONROE NC. THE BORE WAS FOR THE INSTALLATION OF A 42 INCH WATER MAIN WITHIN A 54" CASING. THE GAS MAIN WAS PROPERLY LOCATED AND THE CONTRACTOR FAILED TO PERFORM DUE DILIGENCE IN ACCORDANCE WITH NORTH CAROLINA GENERAL STATUTES CHAPTER 87 ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT. THE GAS MAIN WAS RUPTURED BY THE AUGER BORE MACHINE CAUSING THE RELEASE OF NATURAL GAS AND REQUIRING THE REPAIR OF THE GAS LINE. REPAIRS TO THE CITY OF MONROE NATURAL GAS MAIN WERE FINALIZED ON 01/06/2022 AT 3:30 AM. ON 1/04/2022 AT 05:15 PM THE CITY OF MONROE DETERMINED THAT THE INCIDENT REPORTING THRESHOLD WAS GOING TO BE MET BEFORE THE FACILITIES COULD BE REPAIRED. THEREFORE A DETERMINATION OF FILING THE INITIAL INCIDENT WITH NRC WAS MADE. THE NRC NOTIFICATION WAS MADE AT APPROXIMATELY 6:00 PM ON 1/4/2022. THE ACTUAL INCIDENT THRESHOLD OF 3,000 MCF WAS NOT MET UNTIL APPROXIMATELY 1/05/2022 AT APPROXIMATELY 05:26 AM. CDM WAS NEGLIGENT IN THE FOLLOWING REQUIREMENTS: NC ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT - 87-122. EXCAVATOR RESPONSIBILITIES C) AN EXCAVATOR SHALL COMPLY WITH THE FOLLOWING: (3) PLAN THE EXCAVATION OR DEMOLITION TO AVOID DAMAGE TO OR MINIMIZE INTERFERENCE WITH FACILITIES IN OR NEAR THE CONSTRUCTION AREA. (9) AN EXCAVATOR SHALL NOT PERFORM ANY EXCAVATION OR DEMOLITION WITHIN THE TOLERANCE ZONE UNLESS THE EXCAVATOR COMPLIES WITH ALL OF THE FOLLOWING CONDITIONS: A. THE EXCAVATOR SHALL NOT USE MECHANIZED EQUIPMENT, EXCEPT, NONINVASIVE EQUIPMENT SPECIFICALLY DESIGNED OR INTENDED TO PROTECT THE INTEGRITY OF THE FACILITY, WITHIN THE MARKED TOLERANCE ZONE OF AN EXISTING FACILITY UNTIL: 1. THE EXCAVATOR HAS VISUALLY IDENTIFIED THE PRECISE LOCATION OF THE FACILITY OR HAS VISUALLY CONFIRMED THAT NO FACILITY IS PRESENT UP TO THE DEPTH OF EXCAVATION; 2. THE EXCAVATOR HAS TAKEN REASONABLE PRECAUTIONS TO AVOID ANY SUBSTANTIAL WEAKENING OF THE FACILITY'S STRUCTURAL OR LATERAL SUPPORT, OR BOTH, OR PENETRATION OR DESTRUCTION OF THE FACILITIES OR THEIR PROTECTIVE COATINGS: B. THE EXCAVATOR SHALL MAINTAIN CLEARANCE BETWEEN A FACILITY AND THE CUTTING EDGE POINT OF ANY MECHANIZED EQUIPMENT, TAKING INTO ACCOUNT THE KNOWN LIMIT OF CONTROL OF THE CUTTING EDGE OR POINT, AS MAY BE REASONABLY NECESSARY TO AVOID DAMAGE TO THE FACILITY. THE CITY OF MONROE ACCURATELY MARKED THE 6-INCH STEEL GAS LINE. CDM SMITH DID NOT COMPLY WITH THE REQUIREMENTS WITHIN THE TOLERANCE ZONE. CDM SMITH DID NOT VISUALLY INSPECT THE GAS FACILITY AT THE DEPTH OF THE EXCAVATION. CDM SMITH IS RESPONSIBLE FOR THE DAMAGE DUE TO NEGLIGENCE AND NON-COMPLIANCE WITH THE NC UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT.
2023-06-30 12:35 | NO | NO | NO | 20220011 | 36473 | 2022-02-14 15:41 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-01-28 06:38 | EASTERN | NO | 2022 | FERN HOLLOW BRIDGE | PITTSBURGH | ALLEGHENY | PA | 15221 | 40.4396 | -79.8995 | YES | [8 empty] | 2022-01-28 07:50 | 1327481 | 1327626 | NATURAL GAS |  | 871 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-28 06:38 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-28 07:30 | 2022-01-28 07:05 | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | PIPE THRU BRIDGE SUPPORT AND UNDERGROUND |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 16 | API-5L-B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 16 |  | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 22321 | 22321 | 0 | 0 |  | 10.3951 | 9054 | 9054 | 0 | 0 | 31375 | 15083.3782276884661133543191800878477306 | 31375 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 45 | 45 | 50 | 192.619(A)(1) | 1972-10-29 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCENTINEL T50 | 0.4 |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CASUAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE. PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [154 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | manager compliance | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412 258-4453 | edward.a.palombo@peoples-gas.com | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CAUSAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE AS THE EVIDENCE GATHERED TO DATE SUGGESTS THE PIPELINE WAS DAMAGED BY THE COLLAPSE. WHEN ALSO CONSIDERING THE RESPONSE TO THE RUPTURE STABILIZED THE SITUATION BEFORE ANY FIRE OR EXPLOSION EVENTS, THE NTSB SEES NO NEED TO CONDUCT ANY FURTHER EXAMINATION OF THE PIPE OR RELATED MATERIALS AND WILL NOT BE SECURING ANY SUCH MATERIALS FOR LATER TESTING. TEN PEOPLE WERE INJURED AS A RESULT OF THE BRIDGE COLLAPSE. NO INJURIES RELATED TO THE PIPELINE. THE PIPELINE WAS DAMAGED AT BOTH SIDES OF THE FERN HOLLOW BRIDGE: WEST SIDE ( 40.439536, -79.901115 ) AND EAST SIDE ( 40.439621, -79.899509 ).
2023-06-30 12:35 | NO | YES | YES | 20220013 | 36356 | 2022-02-17 21:08 | ORIGINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2022-01-18 11:10 | EASTERN | YES | 2022 | 869 FOX STREET | BRONX | BRONX COUNTY | NY | 10469 | 40.8186 | -73.8956 |  | YES |  | YES |  | YES |  |  |  | 2022-01-18 12:54 | 1326802 | 1326954 | NATURAL GAS |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2022-01-18 11:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-01-19 10:39 |  |  |  | 2022-01-18 11:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | UNKNOWN | UNKNOWN | [7 empty] | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [9 empty] | LEAK |  |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [5 empty] | CLASS 4 LOCATION | 50000 | 50000 | 0 | 0 | 2824 | 2824 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 52824 | 23303.925677937754728 | 52824 | 0 | 0 | 18 | 0 | 10 | 18 | 0 | 0.25 | 0.25 | 0.5 | 192.619(A)(2) | 1910-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO JURISDICTIONAL INVOLVEMENT | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | leono@coned.com | 7183192350 | 718-904-4607 | OSCAR LEON | leono@coned.com | 7183192350 | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 7183192350 | leono@coned.com | ON 1/18/22 AT 11:10, CON EDISON'S GERC RECEIVED A REPORT FROM THE FDNY OF AN ACTIVE BUILDING FIRE AND EXPLOSION AT 850 FOX STREET IN THE BRONX, WITH FDNY PERSONNEL ON LOCATION. NATURAL GAS WAS NOT REPORTED TO BE INVOLVED. CON EDISON GDS, GAS CONSTRUCTION, AND GAS ERG AND SUPERVISION WERE DISPATCHED TO THE LOCATION BY THE GERC. CON EDISON GAS ENGINEERING WAS NOTIFIED AND DEVELOPED AN ISOLATION PLAN INVOLVING CLOSURE OF DISTRIBUTION MAIN VALVE (MV) 94461 AND EXCAVATION OF A FIRE BANK AT INTERVALE AVENUE AND FOX STREET, OVER A 4-INCH LPPE GAS MAIN (INSTALLED IN 1988). CON EDISON GAS CONTROL WAS NOTIFIED AND REPORTED NORMAL OPERATING CONDITIONS AT NEARBY GAS REGULATOR STATION GR-128. AT 11:19, GDS ARRIVED AND BEGAN INVESTIGATING. GDS CORRECTED THE ADDRESS TO 869 FOX STREET AND CONFIRMED THAT A BUILDING EXPLOSION HAD OCCURRED AT THAT LOCATION. GDS ALSO REPORTED HAVING NO ACCESS TO THE HOS VALVE OR OUTDOOR METER SET AT 869 FOX STREET, WHICH IS SUPPLIED BY A 1 1/4-INCH LPPE GAS SERVICE LINE (INSTALLED IN 1986). GERC PROVIDED GDS WITH THE LOCATION OF MV 94461 (AT THE INTERSECTION OF TIFFANY STREET & FOX STREET). AT 11:48, GDS CLOSED MV 94461 TO BEGIN ISOLATING AND SHUTTING DOWN THE GAS MAIN. CON EDISON GAS CONSTRUCTION CREWS ARRIVED AND BEGAN EXCAVATING A FIRE BANK OVER THE 4-INCH LPPE GAS MAIN AT THE SOUTHEAST CORNER OF INTERVALE AVENUE AND FOX STREET. GDS CONDUCTED A SPECIAL SURVEY OF THE AREA AND DID NOT DETECT ANY NATURAL GAS LEAKS OR ODORS. ALL SUBSURFACE STRUCTURES AND TEST POINTS CHECKED DURING THE SPECIAL SURVEY WERE FOUND CLEAR OF NATURAL GAS READINGS. THE SPECIAL SURVEY WAS CONDUCTED WHILE THE GAS MAIN AND SERVICE LINES ON THE BLOCK WERE IN SERVICE AND BEFORE THEY WERE SHUT DOWN. GDS ALSO TOOK PRESSURE AND ODORANT READINGS AT 858 FOX STREET; BOTH WERE WITHIN ACCEPTABLE RANGE (7.9 INCHES WC FOR PRESSURE; 0.29% GAS-IN-AIR FOR ODORANT). AT 13:03, CON EDISON GAS CONSTRUCTION CREWS INSTALLED A SQUEEZE-OFF ON THE 4-INCH LPPE GAS MAIN IN THE FIRE BANK EXCAVATION, SHUTTING DOWN THE MAIN AND INTERRUPTING GAS SERVICE TO 18 SINGLE-FAMILY BUILDINGS. GAS CONSTRUCTION CREWS THEN CUT AND CAPPED THE SERVICE LINES SUPPLYING 865, 867 AND 869 FOX STREET. AT 18:48, GDS OPENED MV 94461, REINTRODUCING GAS INTO THE MAIN UP TO THE SQUEEZE-OFF. GDS CONDUCTED A DP-IR SURVEY OVER THE MAIN AND SERVICES LINES AND DID NOT DETECT ANY LEAKS. AT 19:08, GDS REMOVED THE SQUEEZE-OFF AND PERFORMED AN ADDITIONAL DP-IR SURVEY OF THE MAIN AND SERVICE LINES WITHOUT DETECTING ANY LEAKS. RESTORATION WAS COMPLETED AT 20:52. ON 1/18/22 AT 17:40, NYPD ARSON AND EXPLOSION SQUAD DETECTIVE DIMARE REPORTED THAT THE SOURCE OF THE EXPLOSION WAS UNKNOWN AND UNDER INVESTIGATION. ON 1/19/22 AT 10:39, FDNY CHIEF SAROCCO REPORTED THAT NATURAL GAS WAS BELIEVED TO BE INVOLVED WITH THE EXPLOSION. THERE IS, HOWEVER, NO INDICATION OF CON EDISON JURISDICTIONAL PIPING BEING INVOLVED AT THIS TIME. THIS INCIDENT REMAINS UNDER INVESTIGATION BY THE FDNY AND NYPD. THE EXPLOSION RESULTED IN TEN INJURIES AND ONE FATALITY, AND GREATER THAN $50,000 IN PROPERTY DAMAGE. PHSMA, DPS STAFF, AND NYCDEP WERE NOTIFIED AND UPDATED. NTSB INQUIRED AND WAS UPDATED. MEDIA WAS ON LOCATION.
2023-06-30 12:35 | NO | YES | NO | 20220015 | 36773 | 2022-02-23 19:59 | SUPPLEMENTAL FINAL | 6243 | HAWAII GAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2022-01-24 11:15 | HAWAII-ALEUTIAN | NO | 2022 | WAIAKAMILO ROAD (BETWEEN HART ST & KALANI ST) | HONOLULU | HONOLULU | HI | 96817 | 21.3224 | -157.8782 | YES | [8 empty] | 2022-01-24 12:30 | 1327229 | 1327369 and 1327376 | SYNTHETIC GAS |  | 550 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 100 | 2022-01-24 09:02 | YES | OPERATOR | 2022-01-24 10:19 | 2022-01-24 09:15 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.625 | [6 empty] | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 4 LOCATION | 100000 | 100000 | 25000 | 25000 | 20000 | 20000 | 0 | 0 |  | 46.67 | 25669 | 25669 | 0 | 0 | 170669 | 78813.6222974030155856515373352855051245 | 170669 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | 33 | 50 | 192.619(C) | 1999-03-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | AUGER | SEWER (SANITARY/STORM) | YES | 22000022 |  | UNKNOWN/OTHER | YES | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [167 empty] | YES |  |  | CHRISTOPHER HALL | IMP ENGINEER | chall@hawaiigas.com | 808-594-5553 |  | CHRIS HALL | chall@hawaiigas.com | 808-594-5553 | KEVIN NISHIMURA | VICE PRESIDENT OPERATIONS | 808-594-5573 | knishimu@hawaiigas.com | INCIDENT SUMMARY ON MONDAY, JANUARY 24, 2022, FRANK COLUCCIO CONSTRUCTION ("FCC") WAS PERFORMING A SEWER INSTALLATION ON A PORTION OF WAIAKAMILO ROAD IN HONOLULU, HAWAII, WITH AN AUGER. AT APPROXIMATELY 9:02 A.M., ON THE PORTION OF WAIAKAMILO ROAD BETWEEN HART STREET AND KALANI STREET, THE AUGER STRUCK A HAWAI'I GAS ("HG") UNDERGROUND 8-INCH PIPELINE ("SUBJECT SEGMENT"). THE AUGER CAUSED AN APPROXIMATELY 3-INCH LONG FRACTURE ALONG THE TOP OF THE PIPELINE. THE SUBJECT SEGMENT BEGAN TO LEAK GAS. HG'S FIRST RESPONDER ARRIVED ON SITE AT APPROXIMATELY 9:15 A.M. AND CONFIRMED THE DAMAGE TO THE SUBJECT SEGMENT. DUE TO THE MAGNITUDE OF THE LEAK, HG CALLED THE HONOLULU FIRE DEPARTMENT ("HFD") AT APPROXIMATELY 10:19 A.M. TO ASSIST IN SECURING THE ROADWAY AND TO HELP MONITOR THE HOT ZONE. HG'S MAINTENANCE CREW ARRIVED ON SITE AT APPROXIMATELY 10:30 A.M. AND BEGAN ASSESSING REPAIRS. AT APPROXIMATELY 11:15 A.M., HFD BEGAN EVACUATING NEARBY COMMERCIAL BUILDINGS. HG WAS ABLE TO STOP THE FLOW OF GAS TO THE SUBJECT SEGMENT AT APPROXIMATELY 5:35 P.M., JANUARY 24, 2022. FINAL REPAIRS WERE COMPLETED AT APPROXIMATELY 11:00 P.M., JANUARY 24, 2022. HAWAI'I GAS INVOLVEMENT PRIOR TO INCIDENT HG INSTALLED THE SUBJECT SEGMENT IN 1940. THE SUBJECT SEGMENT IS AN 8-INCH BARE STEEL PIPE. HG MAPS AND RECORDS CONTAIN NO INDICATION THAT THE SUBJECT SEGMENT WAS REPAIRED, ALTERED OR EXCAVATED SINCE ITS INSTALLATION. ON MONDAY, JANUARY 3, 2022, FCC SUBMITTED ONE CALL TICKET NUMBER 22000022 TO THE HAWAII ONE CALL CENTER INDICATING THAT FCC WOULD BE EXCAVATING "ON WAIAKAMILO ROAD BETWEEN DILLINGHAM BOULEVARD AND HART STREET (EWA SIDE OF ROAD)" ("EXCAVATION AREA"). IN RESPONSE TO TICKET NO. 22000022, HG REVIEWED GIS MAPS OF THE EXCAVATION AREA AND DETERMINED THAT AN UNDERGROUND MAIN LINE WAS LOCATED WITHIN THAT AREA. ON JANUARY 10, 2022, HG PERSONNEL ATTEMPTED TO PERFORM TONING ON THE UNDERGROUND MAIN LINE IN THE EXCAVATION AREA BUT NOTED THAT THE LOCATION OF THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL. ALSO, PLEASE NOTE THAT THIS INVESTIGATION IS STILL ONGOING. UPDATE 6/10/2022 UPON COMPLETION OF THE INVESTIGATION BY HG, IT WAS DETERMINED THAT TONING OF THE SUBJECT SEGMENT WAS PERFORMED INADEQUATELY BY HG. AS INDICATED IN THE "INCIDENT SUMMARY" SECTION ABOVE, THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT AND HG FAILED TO CONFIRM THE MARKINGS WERE CORRECT WHEN RESPONDING TO TICKET NO. 22000022. AS A RESULT OF THE INVESTIGATION, HG HAS INCORPORATED THE FOLLOWING MITIGATIVE ACTIONS INTO ITS TONING OPERATIONS AS OF MAY 2022: 1. REVISE "HG ONE CALL PIPE LOCATION GUIDELINES" DOCUMENT. A. ALL PAINTED UTILITY MARKINGS BY HG WILL HAVE A UNIQUE HG IDENTIFIER. B. ALL EXISTING UTILITY MARKINGS (WHETHER BY HG OR 3RD PARTY) SHALL BE REVERIFIED IN RESPONSE TO AN 811 TICKET. 2. UPDATE TRAINING REQUIREMENTS FOR ALL HG EMPLOYEES WHO CONDUCT UTILITY LOCATIONS. A. INITIAL TRAINING REQUIREMENTS (OQ & "HG ONE CALL PIPE LOCATION GUIDELINES" DOCUMENT REVIEW). B. REFRESHER TRAINING REQUIREMENTS (PIPE LOCATION REFRESHER TRAINING TO BE PROVIDED IN 2022 AND EVERY 3 YEARS AFTER OR WHEN PROBABLE CAUSE IS DETERMINED BY HG MANAGEMENT). C. DOCUMENTATION RETENTION REQUIREMENTS. HG IS CONFIDENT THE MITIGATIVE ACTIONS LISTED ABOVE WILL HELP TO FURTHER REDUCE TONING RELATED INCIDENTS GOING FORWARD. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL.
2023-06-30 12:35 | NO | YES | YES | 20220016 | 36388 | 2022-02-25 10:24 | ORIGINAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-01-27 10:58 | EASTERN | YES | 2022 | 217 BOSWELL RD | BALTIMORE | BALTIMORE COUNTY | MD | 21229 | 39.2819 | -76.7044 | [7 empty] | YES | TWO LEAKING CAST IRON JOINTS WERE ENCAPSULATED AND RENEWED ONE CAST IRON SERVICE AT INCIDENT | 2022-01-27 19:17 | 1327461 | N/A | NATURAL GAS |  | 0.003 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-01-27 10:28 | ALLOWED TO BURN OUT |  | 0 | YES | 0 | 2022-01-27 10:59 |  |  |  | 2022-01-27 11:45 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1920 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 12000 | 12000 | 1200 | 1200 | 0 | 0 | EMERGENCY RESPONSE PERSONNEL AND EQUIPMENT | 4.45 | 0 | 0 | 0 | 0 | 13200 | 5823.3344492802204 | 13200 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 10 | 10 | 10 | 192.623 | 1920-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | [145 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | LEAKING CAST IRON JOINT | [11 empty] | YES | GAS FROM A LEAKING CAST IRON JOINT IGNITED CAUSING A MANHOLE COVER TO LIFT STRIKING A BALTIMORE CITY WELDING CONTRACTOR. |  | YES |  |  |  | OTHER | PACKING MATERIAL USED TO SEAL CAST IRON JOINTS DRIED RELEASING NATURAL GAS | NO | [86 empty] | JEFFREY WEATHERHOLTZ | MANAGER - GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-470-8858 | 410-470-9549 |  |  |  | DANIEL A NORDEN | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | 410-470-6435 | daniel.a.norden@bge.com | ON 1/27/2022, A CITY OF BALTIMORE CONTRACTOR WAS WELDING ON A WATER MAIN ON FREDERICK AVENUE NEAR THE INTERSECTION OF BOSWELL ROAD. WHILE PERFORMING THE WELDING OPERATION, AN IGNITION OCCURRED WHICH CAUSED A NEARBY MANHOLE COVER TO RAISE AND STRIKE A NEARBY CONTRACTOR, CAUSING INJURY TO THE CONTRACTOR'S FOOT AND REQUIRING OVERNIGHT IN-PATIENT HOSPITALIZATION. NATURAL GAS WAS CONFIRMED IN THE LOCALIZED AREA AND SURVEYS WERE IMMEDIATELY CONDUCTED TO FIND THE SOURCE OF THE LEAK. AN ADJACENT MEDIUM PRESSURE 12" CAST IRON NATURAL GAS MAIN WAS FOUND TO HAVE TWO LEAKY JOINTS AND THEY WERE SUBSEQUENTLY REPAIRED AS WELL AS RENEWING AN INTERCONNECTED NATURAL GAS SERVICE LINE. POST-INCIDENT SURVEYS WERE COMPLETED, AND NO READINGS WERE DETECTED SUCH THAT THE JOB COULD BE CLOSED OUT.. NOTE : PART A 21C IS NOTED AS 0.0 HOWEVER ACTUAL (MCF) IS 0.003.TO MATCH PART A 7. THIS ONLINE FORM WILL NOT ACCEPT THAT NUMBER.
2023-06-30 12:35 | NO | YES | NO | 20220017 | 36393 | 2022-02-25 16:16 | ORIGINAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2022-01-27 08:10 | CENTRAL | NO | 2022 | 8500 E PARMER LANE | MANOR | TRAVIS | TX | 78653 | 30.3511 | -97.5885 | YES | [8 empty] | 2022-01-27 08:32 | 1327404 | 1327531 | NATURAL GAS |  | 25858 | 0.71 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-27 01:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-27 00:42 | 2022-01-27 01:30 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2016 | 2015 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.237 | [6 empty] | OTHER | [8 empty] | THIRD PARTY VEHICLE STRUCK ABOVE GROUND STATION PIPING AND SHEERED FABRICATION AT 2 CIRCUMFERENTIAL WELDS BETWEEN PIPE AND REDUCERS. | CLASS 1 LOCATION | 0 | 0 | 250000 | 250000 | 1115 | 1115 | 0 | 0 |  | 5.78 | 149459 | 149459 | 4 | 4 | 400578 | 197221.3907502301276392606149341142020498 | 400578 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 707 | 707 | 778 | 192.621 M | 2016-01-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE TO THE REGULATOR STATION BY THIRD-PARTY VEHICLE INITIATED SCADA ALARMS IN CONTROL ROOM. CONTROLLER FOLLOWED PROCEDURES TO INVESTIGATE ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 60 | YES |  | YES | [116 empty] | YES | [23 empty] | AMY MARK | REGULATORY COMPLIANCE SPECIALIST | amy.mark@onegas.com | 512-407-1571 |  | BRYAN WEEKS | bryan.weeks@onegas.com | 512-407-1529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 512-407-1529 | bryan.weeks@onegas.com | THIRD-PARTY VEHICLE RAN OFF THE ROADWAY TRAVELING WESTBOUND ON EAST PARMER LANE AT A HIGH SPEED AND CRASHED THROUGH FENCING, CONCRETE-FILLED STEEL BOLLARD POSTS WITH WELDED STEEL CROSSBARS, AND THE TEXAS GAS SERVICE (TGS) REGULATOR STATION AT SUBJECT LOCATION BEFORE DAMAGING AND COMING TO REST AGAINST ATMOS ENERGY'S METERING STATION, WHICH FEEDS TGS'S STATION AND DISTRIBUTION SYSTEM. THE VEHICLE'S IMPACT CAUSED THE PIPING TO SEPARATE, LEADING TO AN UNINTENTIONAL RELEASE OF GAS FROM THE INLET AND OUTLET SIDES OF TGS'S REGULATOR STATION. AFTER DAMAGING THE ATMOS ENERGY METERING STATION, THE VEHICLE CAME TO REST ON TOP OF THE ATMOS ENERGY PIPING. ATMOS ENERGY'S MEASUREMENT INSTRUMENTATION WAS DAMAGED AND COULD NOT PROVIDE A VOLUME OF GAS THAT FLOWED THROUGH THE STATION DURING AND AFTER THE INCIDENT. TGS HAS NO KNOWLEDGE OF THE DAMAGE ESTIMATES FOR ATMOS FACILITIES OR THE VEHICLE AT FAULT FOR THE INCIDENT.
2023-06-30 12:35 | NO | YES | NO | 20220018 | 36409 | 2022-03-02 10:16 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2022-02-01 07:42 | EASTERN | YES | 2022 | CUMBERLAND HILL RD BET AUGUSTINE ST AND FOUNDERS DR | WOONSOCKET | PROVIDENCE | RI | 02895 | 41.9925 | -71.4864 | [6 empty] | YES |  |  | 2022-02-02 19:28 | 1327936 | 1328004 | NATURAL GAS |  | 8500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 60 | 2022-02-02 11:00 | YES | OPERATOR | 2022-02-01 11:00 | 2022-02-01 11:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 25 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN - POSSIBLE OXYACETYLENE | 0.375 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 27 | 0.1 |  | CLASS 4 LOCATION | 0 | 0 | 300000 | 300000 | 50000 | 50000 | 0 | 0 |  | 7.21 | 61285 | 61285 | 0 | 0 | 411285 | 189849.6040308395100292825768667642752562 | 411285 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 47.9 | 50 | 60 | 192.621 M | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT CAUSE WAS A CRACK IN A WELD. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [145 empty] | BUTT WELD |  |  | PIPE | [28 empty] | YES | [11 empty] | YES |  |  |  | NO | [55 empty] | YES | [30 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | JOSEPH F. CURLEY | joseph.curley@nationalgrid.com | 4013329815 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | THIS EVENT WAS DISCOVERED IN RESPONSE TO AN ODOR CALL FROM A COMMERCIAL LOCATION AT FORTIN DRIVE IN WOONSOCKET, RI RECEIVED AT APPROX. 11:00 AM ON 2/1/2022. TWO RESPONDERS INITIALLY RESPONDED AND REQUESTED ADDITIONAL SUPPORT TO LOCATE THE LEAK WITH BLOWING GAS AT CUMBERLAND HILL ROAD. ADDITIONAL SUPPORT ARRIVED TO HELP LOCATE THE LEAK AS WELL AS MUTUAL AID PERSONNEL. ADDITIONAL CREWS WORKED OVERNIGHT INTO THE NEXT DAY TO CONTINUE WORK IN LOCATING THE LEAK. ENGINEERING REVIEWED FACILITY MAPS TO DETERMINE THE APPROPRIATE ISOLATION VALVES TO SHUT OFF GAS SUPPLY AND INITIATE REPAIRS WHILE CREWS WORKED TO LOCATE THE IDENTIFIED VALVES; HOWEVER, SIGNIFICANT SNOWFALL FROM 01/28 THROUGH 1/30/22 HINDERED THE CREWS' EFFORTS. DUE TO THE SCOPE OF THE PROJECTED CUSTOMER IMPACT, A DECISION WAS MADE TO ISOLATE THE AFFECTED MAIN USING WELDED STOPPLE FITTINGS. AT 8:00 PM ON 2/2/2022 THE LEAK WAS SECURED. TWO BUILDINGS WERE EVACUATED, WITH AN ESTIMATED 50-60 PEOPLE IN THESE COMMERCIAL PROPERTIES AS ESTIMATED BY THE FD. APPROXIMATELY 5'6" OF 12" STEEL PIPE WERE REPLACED WITH PLASTIC. WE ARE REPORTING THIS INCIDENT SOLELY BASED ON THE VOLUME OF GAS RELEASED. NO INJURIES WERE INVOLVED IN THIS INCIDENT AND RESPONSE AND RESTORATION COSTS ARE RELATED TO THE REPAIR OF THE MAIN AND RESTORATION OF TWO CUSTOMERS THAT WERE SHUT OFF DURING THE RESPONSE.
2023-06-30 12:35 | NO | YES | NO | 20220019 | 36639 | 2022-03-03 13:41 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-02-16 10:20 | EASTERN | NO | 2022 | 944 MCELHANEY ROAD | TRAVELERS REST | GREENVILLE | SC | 29690 | 34.9544 | -82.4665 | [6 empty] | YES |  |  | 2022-02-16 15:27 | 1329042 | 1329121 | NATURAL GAS |  | 8710 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-16 10:20 | NO |  |  | 2022-02-16 11:39 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | M10048 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 226000 | 226000 | 70000 | 70000 | 0 | 0 |  | 4 | 34840 | 34840 | 0 | 0 | 330840 | 150732.9117243537421610541727672035139092 | 330840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 250 | 192.619(A)(2) | 1962-06-25 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | UTILITY | BORING | WATER | YES | 2112131188 |  | CONTRACT LOCATOR | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | THE USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES. WATER COMPANY CONTRACTOR WAS ON A SITE TO INSTALL WATER SERVICE TO A CUSTOMER. TAPPING WHAT THEY BELIEVED WAS THE WATER MAIN, WAS INSTEAD AN 8" HIGH PRESSURE GAS MAIN. THE WATER CONTRACTOR STOPPED WHEN GAS WAS RELEASED AND REPORTED A GAS LEAK.
2023-06-30 12:35 | NO | YES | NO | 20220020 | 36425 | 2022-03-04 14:28 | ORIGINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2022-02-04 07:30 | EASTERN | NO | 2022 | 65 BAY 35TH STREET | BROOKLYN | KINGS | NY | 11232 | 40.6735 | -74.009 |  |  | YES | [6 empty] | 2022-02-04 08:55 | 1328059 | 1328218 | NATURAL GAS |  | 5.092 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-04 07:31 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2022-02-04 07:31 |  |  |  | 2022-02-04 07:54 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN - OEM ARRIVED ONSITE AFTER THE EVENT; NATIONAL GRID ARRIVED APPROX. 20 MINUTES LATER. CAUSE IS UNDER INVESTIGATION | CLASS 4 LOCATION | 750000 | 750000 | 7107 | 7107 | 8300 | 8300 | 0 | 0 |  | 7.47 | 38 | 38 | 0 | 0 | 765445 | 337690.2304239556017175797950219619326501 | 765445 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 9 | 9.1 | 12 | 192.623 | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | NATIONAL GRID DISPATCH WAS NOTIFIED ON 02/04/22 AT 7:23 AM FROM THE OFFICE OF EMERGENCY MANAGEMENT THAT AN EXPLOSION HAD OCCURRED AT 67 BAY 35TH STREET, BROOKLYN NY. THE EXPLOSION FULLY DESTROYED 65 BAY 35TH STREET AND PARTIALLY DAMAGED 69 BAY 35TH STREET, CAUSING IT TO PARTIALLY COLLAPSE. SERVICES AT 65, 69 AND 71 BAY 35TH STREET WERE CUT OFF AT THE MAIN. WITH RESPECT TO PART E, QUESTION 3A, THE MAOP WAS ESTABLISHED IN ACCORDANCE WITH 49 CFR 192.623, EFFECTIVE IN 1970; HOWEVER THE PIPELINE WAS PREDOMINANTLY INSTALLED IN 1965. THREE HOMES WERE DAMAGED AND/OR DEMOLISHED AS A RESULT OF THIS INCIDENT. AT THIS TIME, WE CANNOT ESTIMATE THE COST OF THIS DAMAGE, BUT LIKELY TO EXCEED THE $750,000 PROVIDED IN PART D. THIS INCIDENT IS STILL UNDER INVESTIGATION AND NATIONAL GRID HAS NOT BEEN GRANTED ACCESS AT THIS POINT.
2023-06-30 12:35 | NO | YES | NO | 20220022 | 36437 | 2022-03-08 09:39 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-02-08 07:45 | CENTRAL | NO | 2022 | 11699 NW H K DODGEN LOOP | TEMPLE | BELL | TX | 76504 | 31.1412 | -97.3446 | YES | [5 empty] | YES |  |  | 2022-02-08 18:41 | 1328466 | 1328674 | NATURAL GAS |  | 5036 | 18 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 07:45 | YES | OPERATOR | 2022-02-08 08:05 | 2022-02-08 08:05 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 65 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1985 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 11 | 1 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 104000 | 104000 | 0 | 0 | 0 | 0 |  | 8.17 | 41144 | 41144 | 147 | 147 | 145291 | 69760.6777808767708696925329428989751098 | 145291 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 168 | 168 | 200 | 192.619(A)(2) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2252816180 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 20 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY WAS NOT LOCATED OR MARKED | [170 empty] | DALE GAMBRELL | COMPLIANCE SUPERVISOR | dale.gambrell@atmosenergy.com | 512-844-8270 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-957-3295 | marlo.sutton@atmosenergy.com | AT 07:45 ON FEBRUARY 8, 2022, A THIRD PARTY CONTRACTOR DAMAGED A 6" ATMOS DISTRIBUTION LINE WITH A TRACKHOE AT 11699 NW H K DODGEN LOOP IN TEMPLE TX, CAUSING A RELEASE OF GAS. THE DAMAGE CAUSED AN INTERRUPTION IN SERVICE FOR 1 CUSTOMER; CNG WAS BROUGHT IN TO SHORE UP SERVICE FOR OTHER CUSTOMERS. GAS LOSS EXCEEDED THE REPORTING THRESHOLD. SERVICE WAS RESTORED AT 03:32 ON FEBRUARY 9, 2022. IT WAS DETERMINED THAT THE PIPELINE WAS NOT MARKED BY THE LOCATOR.
2023-06-30 12:35 | NO | YES | NO | 20220024 | 37266 | 2022-03-25 16:52 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-02-08 14:27 | EASTERN | NO | 2022 | PORTAGE | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2816 | -85.5722 | [5 empty] | YES |  | YES | SQUEEZE-OFF ISOLATION NORTH END PIPELINE SEGMENT & BAGGING OFF ISOLATION SOUTH END PIPELINE SEGMENT | 2022-02-25 09:33 | 1329679 | 1329801 | NATURAL GAS |  | 2277 | 0.007 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 14:27 | NO |  |  | 2022-02-08 14:44 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1901 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 332405 | 332405 | 318 | 318 | 0 | 0 |  | 4.48 | 10201 | 10201 | 0 | 0 | 342924 | 152684.197983722688825802342606149341142 | 342924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 192.623 | 1901-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | EROSION OF SUPPORT DUE WATER AND ROADWAY CONSTRUCTION IN THE AREA RESULTING IN LESS THAN ADEQUATE COMPACTION AND SUPPORT OF THE NATURAL GAS PIPELINE. | [154 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON TUESDAY, FEBRUARY 8, 2022, AT APPROXIMATELY 14:27 HOURS CONSUMERS ENERGY WAS NOTIFIED BY OUR LEAK SURVEY CONTRACTOR (PERFORMING A DISCRETIONARY LEAK SURVEY) OF A POSSIBLE LEAK AT/NEAR 1004 PORTAGE ROAD, (KALAMAZOO COUNTY) KALAMAZOO, MI. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 14:44 HOURS AND CONFIRMED READS WHICH REQUIRED AN IMMEDIATE RESPONSE. A DISTRIBUTION CREW (CREW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 16:39 HOURS. THE CREW HAD RECENTLY COMPLETED A LEAK REPAIR ON A 6" CAST IRON PIPELINE AND BASED ON A PRELIMINARY INVESTIGATION AT THE SITE THOUGHT THE SOURCE COULD POTENTIALLY BE RESIDUAL GAS FROM THE INITIAL REPAIR. EXTRACTION EQUIPMENT WAS MOBILIZED TO REMOVE RESIDUAL GAS BUILD UP WHILE GSW'S AND THE CREW CONTINUED PINPOINTING TO DETERMINE IF THE SOURCE COULD BE ADDITIONAL LEAKS ON THE PIPELINE. OVER SEVERAL WEEKS, MULTIPLE LEAKS WERE DISCOVERED ON THE CAST IRON PIPELINE. THE FAILURE INVESTIGATION DETERMINED, THE RECENT (2021) WATER AND ROAD CONSTRUCTION LED TO REDUCED COMPACTION AND SUPPORT OF THE CAST IRON PIPELINE CAUSING MULTIPLE LEAKS OVER TIME. ALL IDENTIFIED LEAKS WERE REPAIRED, AND EXTRACTION EQUIPMENT WAS SIMULTANEOUSLY USED TO REMOVE RESIDUAL GAS FROM THE SOIL. CONSUMERS ENERGY PERSONNEL MONITORED THE SITE UNTIL ALL GAS READS WERE ZERO. A PIPELINE REPLACEMENT PROJECT, WHICH WOULD HAVE INCLUDED RETIRING THE 6-INCH CAST IRON PIPELINE WAS SCHEDULED FOR 2023. HOWEVER DUE TO THE AGE AND CONDITION OF THE PIPELINE A PORTION OF THE REPLACEMENT PROJECT WAS EXPEDITED, AND CONSTRUCTION STARTED IN APRIL. FEBRUARY 25, 2022 CE RETIRED APPROXIMATELY 1100' OF THE CAST IRON PIPELINE THAT WAS COMPROMISED BECAUSE OF THE WATER AND ROAD CONSTRUCTION ACTIVITIES THAT OCCURRED IN 2021.
2023-06-30 12:35 | NO | YES | NO | 20220025 | 36533 | 2022-03-31 18:46 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2022-03-01 10:37 | CENTRAL | NO | 2022 | 3 MILLERS CT | O'FALLON | SAINT CHARLES | MO | 63366 | 38.7758 | -90.7291 | [5 empty] | YES |  |  |  | 2022-03-01 12:33 | 1329957 | 1330159 | NATURAL GAS |  | 104.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-01 11:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 45 | YES | 3 | 2022-03-01 10:37 | NO |  |  | 2022-03-01 10:59 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 663261 | 663261 | 0 | 0 | 500 | 500 | 0 | 0 |  | 6.12 | 641 | 641 | 0 | 0 | 664402 | 293196.6417228441988006749633967789165447 | 664402 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 39.77 | 40 | 60 | 192.621 M | 2002-12-02 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 220521245 |  | CONTRACT LOCATOR | YES | YES | YES | 9 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY TELECOMMUNICATIONS EXCAVATOR STRUCK A 2-INCH PLASTIC GAS MAIN WHILE BORING. THE EXCAVATOR HAD VALID LOCATES AND THE MAIN WAS MARKED WITHIN TOLERANCE BUT THE EXCAVATOR FAILED TO POT-HOLE THE BORE CROSSING. THE COMPANY IDENTIFIED GAS READINGS IN TWO HOMES UPON ARRIVAL AND EVACUATED BOTH RESIDENCES. WHILE CREWS WERE WORKING TO SHUT DOWN THE MAIN 3 MILLERS CT EXPLODED AND SUBSEQUENTLY CAUGHT FIRE. CREWS IMMEDIATELY SHUT DOWN THE MAIN FOLLOWING THE EXPLOSION. THE EXPLOSION CAUSED DAMAGE TO SEVERAL NEARBY HOMES AND THE FIRE SPREAD TO 5 MILLERS CT. THE DAMAGED GAS MAIN WAS REPLACED WITH A 15-FOOT SEGMENT OF 2-INCH PLASTIC. GAS SERVICE WAS INTERRUPTED AT 21 HOMES AND 2 HOMES WERE CONDEMNED. A 48 HOUR UPDATE TO THE NRC WAS MADE ON MARCH 3, 2021 AT 13:38. REPORT NUMBER 1330159.
2023-06-30 12:35 | NO | YES | NO | 20220026 | 36557 | 2022-04-06 09:33 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-03-10 09:18 | CENTRAL | NO | 2022 | ENTIRE CITY | SEGUIN | GUADALUPE | TX | 78155 | 29.5701 | -97.9641 |  | YES |  | YES | [5 empty] | 2022-03-10 09:18 | 1330725 | 1331011 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-08 10:30 | NO |  |  | 2022-03-08 13:00 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | LOSS OF GAS SUPPLY FROM SUPPLIER | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1121224 | 1121224 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1121224 | 494641.086709073169528 | 1121224 | 0 | 0 | 4300 | 0 | 0 | 4300 | 0 | 0 | 0 | 0 | 192.619(A)(1) | 2022-03-08 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | NOTIFICATION FROM SUPPLIER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOSS OF GAS SUPPLY FORM SUPPLIER | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [231 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM SUPPLIER | [47 empty] | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 |  | MICHAEL MAXWELL | mike.d.maxwell@centerpointenergy.com | 830-643-6914 | RANDALL SANDERS | REGIONAL OPERATIONS DIRECTOR TEXAS | 713-207-5728 | randall.x.sanders@centerpointenergy.com | LOSS OF GAS SUPPLY FROM ENTERPRISE PIPELINE TO CENTERPOINT ENERGY DISTRIBUTION SYSTEM IN SEGUIN, & MCQUEENEY, TEXAS, FORCED CENTERPOINT ENERGY TO PERFORM RE-LITE OF APPROXIMATELY 4300 CUSTOMERS.
2023-06-30 12:35 | NO | YES | NO | 20220027 | 36876 | 2022-04-06 09:44 | SUPPLEMENTAL FINAL | 13302 | NATIONAL GAS & OIL CORP | 1500 GRANVILLE ROAD | NEWARK | OH | 43055 | 2022-02-23 15:22 | EASTERN | YES | 2022 | 811 BLACKS RD SE | HEBRON | LICKING | OH | 43025 | 39.9878 | -82.5205 |  |  | YES | YES | [5 empty] | 2022-02-23 15:22 | 1329557 |  | NATURAL GAS |  | 7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-23 13:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7 | YES | 1 | 2022-02-23 14:10 | YES | OPERATOR | 2022-02-23 13:51 | 2022-02-23 14:17 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 1998 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 277236 | 277236 | 0 | 0 | 5000 | 5000 | 0 | 0 |  | 39 | 273 | 273 | 0 | 0 | 282509 | 124669.5980934465493731127379209370424597 | 282509 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 44 | 44 | 60 | 192.619(A)(1) | 1998-04-24 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 7 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL LEAK OF THIS KIND WAS NOT DETECTABLE ON SUCH A LARGE SYSTEM THAT IS MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | [56 empty] | TREES/VEGETATION ROOTS | [5 empty] | NO | [187 empty] | YES | [29 empty] | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | cstorts@theenergycoop.com | 740-348-1203 | 740-348-1131 |  |  |  | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | 740-348-1203 | cstorts@theenergycoop.com | ON WEDNESDAY, FEBRUARY 23, 2022, A HOMEOWNER REPORTED AN EXPLOSION AND CALLED 911. NATIONAL GAS & OIL COOPERATIVE WAS NOTIFIED APPROXIMATELY 10 MINUTES LATER. WHEN COOPERATIVE EMPLOYEES ARRIVED AT THE SCENE, THE SERVICE LINE CURB VALVE WAS SHUT AND THE FIRE DEPARTMENT EXTINGUISHED THE FLAMES. READINGS INDICATED THAT NATURAL GAS WAS PRESENT IN THE GROUND AROUND THE HOMEOWNER'S NATURAL GAS RISER. THE HOMEOWNER'S NATURAL GAS SERVICE LINE WAS TESTED AND LEAKAGE WAS FOUND AT THE RISER HEAD. ON TUESDAY, MARCH 22, 2022 AFTER ALL INSURANCE PARTIES AND FIRE AND EXPLOSION INVESTIGATORS COULD BE PRESENT, THE HOMEOWNER'S RISER WAS REMOVED AND THE SERVICE LINE CAPPED AT THE BASE OF THE RISER AND RETESTED. THE SERVICE LINE HELD THE PRESSURE TEST WITHOUT THE RISER. THE HOMEOWNER'S RISER WAS REMOVED AND SENT TO AN INDEPENDENT LABORATORY PLANNED FOR FURTHER INVESTIGATION (PLANNED FOR APRIL 21, 2022). THIS RISER WAS INSTALLED BY THE HOMEOWNER OR THE HOMEOWNER'S CONTRACTOR OR REPRESENTATIVE, NOT BY THE NATIONAL GAS & OIL COOPERATIVE. THE ROOT CAUSE OF THE EXPLOSION WAS DUE TO A PULLED RISER. A TREE ROOT APPROXIMATELY 6 FEET AWAY FROM THE BEND IN THE RISER GREW ACROSS THE SERVICE LINE. OVER TIME, THE ROOT PULLED THE SERVICE LINE MOST OF THE WAY OUT OF THE RISER CONNECTION, CAUSING A LEAK. THE HOUSE AT 811 BLACKS RD SE HAS BEEN TORE DOWN DUE TO THE DAMAGES CAUSED BY THE EXPLOSION. THE PUBLIC UTILITIES COMMISSION OF OHIO HAS COMPLETED THEIR INVESTIGATION AND WE, NATIONAL GAS AND OIL COOPERATIVE, ARE WAITING ON A COPY OF THEIR REPORT AS OF 7/19/2022.
2023-06-30 12:35 | NO | YES | NO | 20220028 | 36650 | 2022-04-08 10:32 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-03-10 14:50 | CENTRAL | NO | 2022 | 3307 89TH STREET | LUBBOCK | LUBBOCK | TX | 79412 | 33.513 | -101.8861 | [5 empty] | YES |  |  |  | 2022-03-10 16:55 | 1330768 | 1330843 | NATURAL GAS |  | 685 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-10 15:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | YES | 7 | 2022-03-10 15:09 | YES | OPERATOR | 2022-03-10 15:09 | 2022-03-10 15:09 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 2.375 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 7938 | 7938 | 13455 | 13455 | 166000 | 166000 | DAMAGE TO RESIDENCE. | 5.63 | 3857 | 3857 | 6 | 6 | 191256 | 84904.7068199632167784670571010248901903 | 191256 | 0 | 0 | 7 | 0 | 0 | 12 | 0 | 40 | 40 | 44 | 192.619(A)(2) | 2015-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 1 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [9 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2256245020 | TX811 | CONTRACT LOCATOR | YES | YES | YES | 40 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [142 empty] | YES | [26 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 8062206849 |  | MIKE CULP | mike.culp@atmosenergy.com | 8062206849 | MIKE CULP | COMPLIANCE MANAGER | 8062206849 | mike.culp@atmosenergy.com | CITY OF LUBBOCK, TX WHILE REPAIRING A SEWER SERVICE LINE TO THE ASSOCIATED ADDRESS, CUT A 2" NATURAL GAS LINE WITH A BACKHOE. THE GAS LINE WAS CORRECTLY MARKED WITH PAINT AND FLAGS BEFORE START OF EXCAVATION. ATMOS ENERGY WAS NOTIFIED OF THE DAMAGED LINE AT 15:09 AND ARRIVED ON SCENE AT 15:16. REMOTE EXCAVATIONS SITES WERE USED TO SQUEEZE THE PE LINE AND SHUT THE FLOW OF GAS OFF, AREA WAS MADE SAFE AT 16:37. ATMOS ENERGY'S INVESTIGATION OF THIS INCIDENT IS CURRENTLY ONGOING.
2023-06-30 12:35 | NO | YES | NO | 20220029 | 36565 | 2022-04-08 11:56 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2022-03-09 16:22 | PACIFIC | NO | 2022 | 3817 N CRESTLINE ST | SPOKANE | SPOKANE | WA | 99207 | 47.6928 | -117.3791 | YES | [8 empty] | 2022-03-09 16:37 | 1330648 | 1330830 | NATURAL GAS |  | 45 | 22 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2022-03-03 18:08 | NO |  |  | 2022-03-03 19:03 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1956 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2000 | 2000 | 177000 | 177000 | 0 | 0 |  | 4.63 | 208 | 208 | 102 | 102 | 179310 | 79147.2270027121772752562225475841874085 | 179310 | 41 | 1 | 1127 | 0 | 0 | 1127 | 42 | 55 | 55 | 60 | 192.619(C) | 1956-06-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A PIPE LEAK THAT REQUIRED A SYSTEM OUTAGE TO REPAIR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2018-08-15 | NO | [12 empty] | NO | YES | CITY STREET | [9 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | PREVIOUS DAMAGE | [173 empty] | JOSHUA FORT | SR. GAS ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | TIM HARDING | tim.harding@avistacorp.com | 509-495-2784 | BRIAN SCHULTZ | MANAGER - NAT. GAS COMPLIANCE AND INTEGRITY | 509-495-2162 |  | brian.schultz@avistacorp.com | THE SPOKANE CITY WATER DEPARTMENT RESPONDED TO A LEAKING WATER SERVICE AT 3817 N CRESTLINE ST. PRIOR TO EXCAVATING, THE WATER CREW SMELLED NATURAL GAS IN THE AREA THEY WERE GOING TO DIG. THEY CONTACTED AVISTA TO REPORT THE GAS ODOR. AN AVISTA FIRST RESPONDER ARRIVED AND DETERMINED THAT AN AVISTA CONSTRUCTION CREW WOULD NEED TO INVESTIGATE THE LEAK. THE AREA WAS EXCAVATED AND THE LEAK LOCATION WAS FOUND TO BE ON THE BOTTOM OF THE STEEL GAS MAIN. THE LEAK WAS COMING FROM A CRACK OR SMALL HOLE INSIDE THE DENT. THIS DENT WAS LIKELY CAUSED BY EXCAVATION DAMAGE SOMETIME IN THE PAST. TO REPAIR THE LEAK, THE CREW NEEDED TO WELD A STEEL FITTING OVER THE DENT. PRIOR TO WELDING ON THE FITTING, THE CREW ATTEMPTED REDUCE THE GAS FLOW FROM THE LEAK BY INSERTING A PLUG. UNFORTUNATELY THIS CAUSED THE LEAK RATE TO INCREASE AND IT WAS DECIDED THAT THE SYSTEM SHOULD BE SHUT DOWN TO SAFELY WELD ON THE REPAIR FITTING. TEN VALVES IN THE SYSTEM WERE CLOSED AT MIDNIGHT ON 3/4/22. THIS CAUSED AN OUTAGE FOR 1169 CUSTOMERS. THE STEEL MAIN REPAIR WAS COMPLETE AT 01:00 3/4/22. ALL GAS METERS IN THE SYSTEM WERE SHUT OFF, THE SYSTEM WAS PURGED OF ANY AIR, AND CUSTOMER RELIGHTS STARTED AT 14:00 ON 3/4/22. RELIGHTS WERE COMPLETE AT 17:00 ON 3/5/22 WITH THE EXCEPTION OF SOME CUSTOMERS WHOSE HOMES WE WERE UNABLE TO ENTER. ON 3/9/22 IS WAS DETERMINED THAT THE INCIDENT COST HAD EXCEEDED THE FEDERAL THRESHOLD AND IT WAS REPORTED TO PHMSA (NRC).
2023-06-30 12:35 | NO | YES | NO | 20220030 | 36571 | 2022-04-12 21:21 | ORIGINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-03-13 01:55 | EASTERN | YES | 2022 | 908 COLLEGE AVENUE | HOUGHTON | HOUGHTON | MI | 49931 | 47.1221 | -88.5626 |  | YES |  |  |  | YES |  |  |  | 2022-03-13 09:05 | 1330926 | NA | NATURAL GAS |  | 2000 | 0.113 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-13 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 30 | 2022-03-13 01:55 |  |  |  | 2022-03-13 03:19 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1966 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNKNOWN AT THIS TIME. | [5 empty] | CLASS 3 LOCATION | 500000 | 500000 | 50000 | 50000 | 50000 | 50000 | 0 | 0 |  | 5.6071 | 11214 | 11214 | 1 | 1 | 611215 | 271183.0013881532366032210834553440702782 | 611215 | 12 | 0 | 6 | 0 | 0 | 5 | 10 | 55 | 55 | 60 | 192.619(A)(2) | 1966-10-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RATE OF GAS VOLUME RELEASED WOULD NOT HAVE TRIGGERED ANY ALARMS OR AOCS THROUGH THE SCADA SYSTEM, AND THEREFORE THE CONTROLLERS WOULD NOT HAVE TAKEN ACTION. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | MIKE KOSHT | michael.kosht@semcoenergy.com | (906) 250-7196 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | TECH ARRIVED ON SITE, AND HOUGHTON FIRE DEPT. WAS ATTENDING TO STRUCTURE FIRE AT 908 COLLEGE AVE. ONCE FIRE WAS UNDER CONTROL, TECH WAS ABLE TO SECURE GAS TO 908 COLLEGE AVE. THROUGH THE LEAK INVESTIGATION PROCESS, TECH EVACUATED MULTIPLE BUILDINGS ON COLLEGE AVE. AND ON E LAKESHORE. TECH DETERMINED THERE WAS A PROBABLE UNDERGROUND LEAK, BASED ON LEL READINGS FOUND SURROUNDING THE SITE. GAS FLOW WAS CONTROLLED, AND THE SURROUNDING AREA WAS PURGED TO REDUCE GAS TO SAFE LEVELS. THE SOURCE OF GAS LEAK IS NOT YET DETERMINED DUE TO GROUND CONDITIONS (I.E, FROZEN GROUND, ETC). THE INCIDENT IS STILL UNDER INVESTIGATION AND SEMCO IS WORKING CLOSELY WITH MICHIGAN PUBLIC SERVICE COMMISSION THROUGHOUT THE PROCESS. A SUPPLEMENTAL REPORT WILL BE FILED WHEN FURTHER INVESTIGATIONS ARE ABLE TO BE CONDUCTED.
2023-06-30 12:35 | NO | NO | NO | 20220031 | 37336 | 2022-04-13 10:55 | SUPPLEMENTAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2022-03-14 16:20 | EASTERN | YES | 2022 | 449 FIRST ST. | NEWBURGH | ORANGE | NY | 12550 | 41.5027 | -74.0278 |  |  | YES | [6 empty] | 2022-03-14 18:31 | 1331058 | 1331191 | NATURAL GAS |  | 7.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-14 16:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7.4 | YES | 6 | 2022-03-14 16:32 |  |  |  | 2022-03-14 16:32 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1951 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL PIPE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE SERVICE PIPE TO THE BUILDING FOUNDATION IS 2" AND THE PIPE REDUCES TO 1 1/4" NEAR THE FOUNDATION WALL. | CLASS 3 LOCATION | 0 | 0 | 9073 | 9073 | 13610 | 13610 | 0 | 0 |  | 9.1644 | 68 | 68 | 0 | 0 | 22751 | 10046.1973577792795226691068814055636896 | 22751 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.31 | 0.31 | 0.5 | 192.623 | 1951-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [111 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL SERVICE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE CONTRACTOR INTENDED TO CUT THE PIPE. | [155 empty] | JERRY AMATO JR. | DIRECTOR OF GAS COMPLIANCE | jamato@cenhud.com | 845.486.5642 |  | JERRY AMATO | jamato@cenhud.com | 845-486-5642 | ERIC KISZKIEL | MANAGER OF GAS OPERATIONS AND ENGINEERING | 845-486-5472 | ekiszkiel@cenhud.com | AT 4:25 PM ON 3/14/2022, CENTRAL HUDSON WAS NOTIFIED BY THE CITY OF NEWBURGH OF A POSSIBLE GAS EXPLOSION AT 449 FIRST ST. IN NEWBURGH. THE FIRST CENTRAL HUDSON RESPONDER ARRIVED ON SITE AT 4:32 PM AND A SECOND CENTRAL HUDSON RESPONDER ARRIVED AT 4:33 PM. THE BUILDING WAS ON FIRE WHEN THE RESPONDERS ARRIVED. ADDITIONAL SUPPORTING PERSONNEL INCLUDING SUPERVISORS AND GAS CONSTRUCTION CREW WERE EN ROUTE. APPROXIMATELY 6 PEOPLE WERE EVACUATED BY THE FIRE DEPARTMENT. THE BUILDING AT 449 FIRST ST. WAS PRESENTLY BEING RENOVATED AND WAS FED BY A 4 INCH LOW PRESSURE CAST IRON MAIN AND 197 FT. LONG 2 INCH STEEL SERVICE. A CURB VALVE WAS PRESENT ON THE SERVICE. THERE WERE THREE GAS METERS LOCATED INSIDE THE BUILDING'S BASEMENT WITH VALVES THAT WERE CLOSED AND LOCKED ON OCTOBER 25TH 2021. A CENTRAL HUDSON REPRESENTATIVE ON SCENE ADVISED THE FIRE DEPARTMENT TO CONTAIN THE HOUSE FIRE BUT TO ALLOW THE NATURAL GAS TO BURN TO PREVENT A SECOND IGNITION. A POLICE OFFICER INFORMED AN ONSITE CENTRAL HUDSON SUPERVISOR OF A REPORT OF THE CUSTOMER'S CONTRACTOR CUTTING THE SERVICE LINE OR CUSTOMER PIPE INSIDE THE BUILDING. A COMMERCIAL REPRESENTATIVE STOPPED THE FLOW OF GAS TO THE HOUSE BY CLOSING THE CURB VALVE ON THE SERVICE AT APPROXIMATELY 5:00 PM. ELECTRIC TAPS FOR THIS ADDRESS WERE CUT AT APPROXIMATELY 5:05PM. BY THIS TIME, ADDITIONAL CH EMPLOYEES HAD ARRIVED ON THE SCENE TO ASSIST IN THE EMERGENCY RESPONSE. THE CENTRAL HUDSON SUPERVISOR INFORMED THE FIRE DEPARTMENT THAT THEY MAY PROCEED WITH EXTINGUISHING THE HOUSE FIRE. AFTER THE BUILDING WAS MADE ACCESSIBLE BY THE FIRE DEPARTMENT, ONE CENTRAL HUDSON PERSONNEL AND CITY OF NEWBURGH FIRE INVESTIGATOR INVESTIGATED THE BASEMENT OF THE HOUSE AND CONFIRMED THAT THE SERVICE PIPE AND CUSTOMER PIPE HAD BEEN CUT AND DISASSEMBLED IN MULTIPLE LOCATIONS INCLUDING AT LEAST ONE LOCATION OF UPSTREAM OF THE THREE LOCKED GAS METERS. CENTRAL HUDSON AND CONTRACTOR CREWS LEAK SURVEYED THE ENTIRE PROPERTY AND THE SURROUNDING AREA. NO NATURAL GAS LEAKS WERE FOUND AT 449 FIRST ST. THE AREA OF 244 VAN NESS ST. WAS ALSO LEAK SURVEYED, AS THE SERVICE TO 449 FIRST ST. WAS FED FROM THAT ROAD. NO LEAKS WERE FOUND AT EITHER ADDRESS. GAS ODORANT READINGS WERE TAKEN IN THE SURROUNDING AREA TO VERIFY APPROPRIATE ODORIZATION OF GAS. THE NATURAL GAS SERVICE TO 449 FIRST ST. WAS PERMANENTLY RETIRED THAT EVENING AND THE AREA WAS DECLARED SAFE AT 9:40 PM.
2023-06-30 12:35 | NO | YES | NO | 20220032 | 36654 | 2022-04-21 15:15 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-03-24 01:15 | EASTERN | NO | 2022 | HIGHWAY 9 | BOILING SPRINGS | SPARTANBURG | SC | 29316 | 35.059 | -81.9935 | [5 empty] | YES |  |  |  |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 0.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-24 01:52 | NO |  |  | 2022-03-24 01:52 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | IN A CREEK. | 72 | NO | YES | [6 empty] | YES | BORED/DRILLED | FAWN BRANCH TRIBUTARY 2 | 1 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | INVESTOR OWNED |  | MAIN |  | 2014 | UNKNOWN |  |  |  |  | 6 | MDPE | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 344000 | 344000 | 7200 | 7200 | 0 | 0 |  | 0.1 | 0 | 0 | 0 | 0 | 351200 | 154935.9892869101064 | 351200 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 68 | 70 | 192.619(A)(2) | 2014-07-10 | PRESSURE DID NOT EXCEED MAOP | OTHER | INJECTION |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | DUE TO LOCATION OF PIPE UNDER CREEK, DAMAGED PORTION OF PIPE WAS DEACTIVATED AND LEFT IN PLACE. | [45 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | A PASSERBY IN A VEHICLE CALLED STATING THAT THEY SMELLED GAS. ONCE INVESTIGATED, GAS WAS FOUND BLOWING THROUGH THE WATER IN THE CREEK. DUE TO THE NATURE OF THE PIPE BEING LOCATED IN THE CREEK AND BENEATH A CONCRETE BOX CULVERT, THE PIPE WAS NOT EXPOSED AND WAS LEFT IN PLACE. THE TRUE CAUSE OF THE LEAK, HOLE SIZE, AND GAS VOLUMES COULD NOT BE DETERMINED. NEW PIPE WILL BE BORED UNDER CREEK FOR REPAIR. THE NRC WAS NOT NOTIFIED AT THE TIME OF INCIDENT BECAUSE THE ESTIMATED COST WAS BELIEVED TO BE BELOW THE 122K THRESHOLD.
2023-06-30 12:35 | NO | YES | NO | 20220033 | 36728 | 2022-04-25 13:28 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-04-05 01:55 | CENTRAL | YES | 2022 | 4809 TROUP HWY | TYLER | SMITH | TX | 75703 | 32.2986 | -95.2662 |  |  |  | YES | [5 empty] | 2022-04-05 05:25 | 1332738 | 1332887 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-05 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2022-04-05 01:55 |  |  |  | 2022-04-05 02:25 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | REGULATOR BODY | [9 empty] | OTHER | [8 empty] | DURING A LOCAL STORM A PONTOON BOAT BELONGING TO TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. | CLASS 3 LOCATION | 125000 | 125000 | 300 | 300 | 676 | 676 | 0 | 0 |  | 4.72 | 5 | 5 | 0 | 0 | 125981 | 55578.6780622326418441815519765739385066 | 125981 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.619(A)(1) | 1970-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  |  | YES | THUNDER STORMS/HIGH WINDS | [177 empty] | YES |  |  | YES | [31 empty] | LESLIE DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-9325 |  | JASON SURRATT | jason.surratt@centerpointenergy.com | 7775006234 | RANDALL SANDERS | DIRECTOR OF OPERATIONS TX. REGION | 713-207-5708 | randall.x.sanders@centerpointenergy.com | DURING A LOCAL THUNDER STORM A PONTOON BOAT ON TRAILER OWNED BY TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. RESULTING IN IGNITION OF GAS DAMAGING BUILDING AND CONTENTS. (PART A, LINE #4 RESPONSE OF 0525AM WAS THE TIME OF CONFIRMED DISCOVERY THAT IT MET CRITERIA) DUE TO RESTRICTED ACCESS. DUE TO RESTRICTED ACCESS CONFIRMED DISCOVERY WAS NOT UNTIL 0525 AM THAT MORNING.
2023-06-30 12:35 | NO | YES | YES | 20220036 | 36674 | 2022-05-18 09:50 | ORIGINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-04-23 07:28 | EASTERN | YES | 2022 | 5021 HIALEAH DR | PITTSBURGH | ALLEGHENY | PA | 15239 | 40.4862 | -79.7042 |  |  | YES | YES |  |  |  | YES | SERVICE LINE WAS CUT OFF AT MAIN LINE. | 2022-04-23 07:28 | 1334232 | 1334328 | NATURAL GAS |  | 0.106 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES | 2022-04-22 23:22 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.1 | YES | 7 | 2022-04-22 23:28 |  |  |  | 2022-04-23 00:12 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIS INCIDENT IS UNDER INVESTIGATION BY CHIEF DEPUTY FIRE MARSHAL DONALD A. BRUCKER CERTIFIED FIRE & EXPLOSION INVESTIGATOR ALLEGHENY COUNTY FIRE MARSHAL'S OFFICE. | CLASS 3 LOCATION | 185000 | 185000 | 0 | 0 | 6148 | 6148 | 0 | 0 |  | 10.5425 | 1 | 1 | 0 | 0 | 191149 | 84327.7550968791465504363103953147877013 | 191149 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 8.7 | 8.7 | 10 | 192.621 M | 1961-01-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | wayne.dadig@peoples-gas.com | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412-258-4453 | edward.a.palombo@peoples-gas.com | AT THIS TIME THE INCIDENT IS UNDER INVESTIGATION BY CHIEF DEPUTY FIRE MARSHAL DONALD A. BRUCKER CERTIFIED FIRE & EXPLOSION INVESTIGATOR, ALLEGHENY COUNTY FIRE MARSHAL'S OFFICE. PEOPLES NATURAL GAS IS WORKING WITH AND ASSISTING THE INVESTIGATION TEAM.
2023-06-30 12:35 | YES | NO | NO | 20220037 | 36688 | 2022-05-20 16:22 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2022-04-22 04:18 | CENTRAL | YES | 2022 | 302 MAPLE | ONAWA | MONONA | IA | 51040 | 42.0212 | -96.0879 | [5 empty] | YES |  |  |  | 2022-04-22 06:06 | 1334144 | 1334323 | NATURAL GAS |  | 8.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-22 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.5 | NO | 1 | 2022-04-22 04:18 |  |  |  | 2022-04-22 00:50 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2000 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | 2406 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | OTHER | [8 empty] | LEAK CAUSED BY FIRE DAMAGE TO METER AND REGULATOR. | CLASS 4 LOCATION | 11200 | 11200 | 3000 | 3000 | 15000 | 15000 | 0 | 0 |  | 8.14 | 69 | 69 | 0 | 0 | 29269 | 12921.8264921541554161054172767203513909 | 29269 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 25 | 25 | 66.6 | 192.619(A)(1) | 2000-01-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [111 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [143 empty] | YES | [24 empty] | ANTHONY ENGLING | SUPERVISOR PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 15635854014 | 563-583-0850 | GARY HOGAN | gary.hogan@blackhillscorp,com | 1-402-221-2536 | TONY JOHN ENGLING | SUPERVISOR PIPE LINE SAFETY PROFESSIONAL | 15635854014 | tony.engling@blackhillscorp.com | ON 4/22/2022 AT 04:18 CENTRAL TIME BLACK HILLS ENERGY WAS NOTIFIED BY EMERGENCY RESPONDERS OF A RESIDENTIAL FIRE AND REQUESTED BHE TO RESPOND. THE LOCATION IS 302 MAPLE IN ONAWA IOWA. UPON ARRIVAL THE TECHNICIAN FOUND THE HOME ENGULFED IN FLAMES. THE FIRE HAD CAUSED DAMAGE TO THE METER AND REGULATOR. THE SERVICE LINE WAS EXCAVATED AT THE STREET AT A SAFE DISTANCE FROM THE FIRE AND CUT OFF AND CAPPED.
2023-06-30 12:35 | NO | YES | YES | 20220038 | 37230 | 2022-05-23 09:26 | SUPPLEMENTAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2022-04-24 14:33 | EASTERN | YES | 2022 | 10826 AVENUE N | BROOKLYN | KINGS | NY | 11234 | 40.641 | -73.8826 |  |  | YES | [6 empty] | 2022-04-24 19:19 | 1334317 | 1334342 | NATURAL GAS |  | 1.72 | 0 | YES | 0 | 0 | 2 | 0 | 0 | 2 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2022-04-24 14:33 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1.72 | NO | 3 | 2022-04-24 14:33 |  |  |  | 2022-04-24 15:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | AT THIS TIME, UNKNOWN PENDING INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN AT THIS TIME | CLASS 4 LOCATION | 122000 | 122000 | 0 | 0 | 1537 | 1537 | 0 | 0 |  | 6.05 | 10 | 10 | 0 | 0 | 123547 | 54505.5763286835031833631039531478770132 | 123547 | 0 | 0 | 2 | 10 | 0 | 2 | 0 | 0.29 | 0.32 | 0.43 | 192.623 | 1997-03-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 15169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 15169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 15169030596 | corinne.byrnes@nationalgrid.com | **UPDATE 10/14/2022- NO ADDITIONAL INFORMATION ON THIS INCIDENT IS AVAILABLE, AND NATIONAL GRID IS STILL AWAITING FINAL DISPOSITION.*** NATIONAL GRID WAS NOTIFIED ON 04/24/2022 AT 14:33 FROM FDNY 401 REGARDING FIRE IN PROGRESS AT 10826 AVENUE N, BROOKLYN, NY. A SERVICE PERSON WAS DISPATCHED AT 14:33 AND ARRIVED ON SITE AT 15:00. THE SERVICE WAS MADE SAFE AT 15:50 BY TURNING OFF THE CURB VALVE. IN ADDITION, THE RESIDENCE AT 10824 WAS SECURED AT THE METER BY THE FDNY AT 17:00. NATIONAL GRID CREW REMAINED ON SITE UNTIL THE FDNY WAS ABLE TO EXTINGUISH THE FIRE, BUT COULD NOT GAIN ACCESS TO THE PREMISE. NEWS RELEASES INDICATE THAT THERE WERE TWO FATALITIES, ONE RESIDENT, AND ONE FIREFIGHTER. NEWS RELEASES ALSO INDICATE THAT AT LEAST ONE FIREFIGHTER WAS HELD OVERNIGHT AT A NEARBY HOSPITAL. ESTIMATES ARE THAT AT LEAST TWO OTHER FIREFIGHTERS SUFFERED INJURIES NOT REQUIRING AN OVERNIGHT HOSPITAL STAY. AT THIS TIME, IT IS UNDETERMINED AS TO THE CAUSE AND LOCATION OF THE FIRE; HOWEVER, IF THE EVENT IS DETERMINED TO BE 'FIRE FIRST', WE WILL STILL FILE THIS REPORT DUE TO THE FATALITY AND INJURIES. NATIONAL GRID HAS MADE SEVERAL ATTEMPTS TO DETERMINE THE CAUSE AND STARTING POINT OF THE FIRE. IT IS STILL UNDER INVESTIGATION AS OF MAY 10, BUT WE WILL CONTINUE TO ATTEMPT TO GAIN MORE INFORMATION. PART A - QUESTION 22, TWO HOMES WERE SHUT OFF, ASSUMED MINIMUM OF 3 INDIVIDUALS EVACUATED. PART D - QUESTION 2B, NATIONAL GRID CANNOT MAKE REPAIRS AS OF YET, SO REPAIR COST UNKNOWN.
2023-06-30 12:35 | NO | YES | YES | 20220039 | 36740 | 2022-06-10 09:02 | ORIGINAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2022-05-13 20:10 | EASTERN | YES | 2022 | 611 WHITESTICK ST. | MABSCOTT | RALEIGH | WV | 25871 | 37.7758 | -81.2121 | [7 empty] | YES | FULL-CIRCLE BAND LEAK CLAMP | 2022-05-13 20:13 | 1335962 | 1336073 | NATURAL GAS |  | 14.887 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-05-13 14:10 | YES | OPERATOR | 2022-05-13 14:50 | 2022-05-13 14:10 | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | ALDYL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 600 | 600 | 500 | 500 | 0 | 0 |  | 6.739 | 100 | 100 | 0 | 0 | 1200 | 543.110960085211143631039531478770131772 | 1200 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 30 | 30 | 40 | 192.619(A)(4) | 2016-08-24 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PUNCTURE DIDN'T REDUCE SYSTEM PRESSURE ENOUGH TO CAUSE AN ALARM AT GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 2213316772 | N/A | FACILITY OWNER | NO | UNKNOWN/OTHER | NO |  | OTHER | EXCAVATOR CALLED IN AN "EMERGENCY" ONE CALL TICKET BUT DID NOT WAIT FOR UNDERGROUND UTILITIES TO BE MARKED BEFORE DIGGING. | [172 empty] | PHILIP KINGREY | MANAGER ENGINEERING AND COMPLIANCE | philipkingrey@mgcwv.com | 3043892714 | 3049259605 | JOHN LIVELY | johnlively@mgcwv.com | 3046674669 | THOMAS WESTFALL | VICE PRESIDENT GAS SUPPLY AND TECHNICAL SERVICES | 3045395740 | thomaswestfall@mgcwv.com | BECKLEY WATER COMPANY WERE MAKING A WATER LEAK REPAIR AND CALLED IN AN EMERGENCY ONE-CALL TICKET. THEY DID NOT WAIT FOR UNDERGROUND UTILITIES TO BE LOCATED BEFORE DIGGING AND PUNCTURED MOUNTAINEER GAS COMPANY'S 2" PLASTIC NATURAL GAS DISTRIBUTION PIPELINE OPERATING NEAR 30 PSIG. BECKLEY WATER COMPANY NOTIFIED MOUNTAINEER GAS COMPANY'S DISPATCH CENTER. MOUNTAINEER EMPLOYEES WERE DISPATCHED TO THE SCENE. WHILE INSTALLING A FULL CIRCLE BAND CLAMP, TWO OF THEM WERE OVERCOME WITH GAS AND REMOVED FROM THE LEAK AREA BY PERSONNEL ONSITE. MOUNTAINEER NOTIFIED 911 AND EMERGENCY MEDICAL PERSONNEL RESPONDED TO THE SCENE TO PROVIDE MEDICAL TREATMENT. ONE EMPLOYEE WAS TAKEN TO THE HOSPITAL IN AN AMBULANCE AND THE OTHER WAS TAKEN TO THE HOSPITAL BY ANOTHER EMPLOYEE. BOTH EMPLOYEES WERE GIVEN A MEDICAL ASSESSMENT AT THE HOSPITAL, ONE WAS ADMITTED TO INPATIENT HOSPITALIZATION FOR OBSERVATION, AND THE OTHER WAS RELEASED.
2023-06-30 12:35 | NO | NO | NO | 20220040 | 37711 | 2022-06-10 14:10 | SUPPLEMENTAL FINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-05-12 14:30 | CENTRAL | YES | 2022 | 100333 IMC ROAD | ABERDEEN | MONROE | MS | 39730 | 33.7684 | -88.5722 | YES | [5 empty] | YES |  |  | 2022-05-12 14:42 | 1335844 | 1335944 | NATURAL GAS |  | 5914 | 379 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-05-12 08:45 | YES | OPERATOR | 2022-05-12 08:45 | 2022-05-12 09:10 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | 1969 |  |  |  |  | 8 | API 5LX-1968 | REPUBLIC STEEL | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | LEAK |  |  | OTHER | 2-INCH NIPPLE SHEARED OFF PIPE | [5 empty] | CLASS 1 LOCATION | 0 | 0 | 10001 | 10001 | 12575 | 12575 | 0 | 0 |  | 7.3268 | 43331 | 43331 | 2777 | 2777 | 68684 | 36625.3473749841413413997071742313323573 | 68684 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 250 | 350 | 385 | 192.619(A)(2) | 1969-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OTHER THAN PROVIDING ALERTS TO OPERATIONS AS THE EVENT OCCURRED, THE CONTROL ROOM HAD NO INVOLVEMENT IN THIS INCIDENT. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE EASEMENT | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 22042814572130 |  | CONTRACT LOCATOR | YES | YES | YES | 11 | LOCATING PRACTICES NOT SUFFICIENT |  |  | INCORRECT FACILITY RECORDS/MAPS | [170 empty] | DEAN MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6015925360 |  | WADE SHULTICE | wade.shultice@atmosenergy.com | 6622512018 | JAMES E. MCKENZIE | VICE PRESIDENT TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | ATMOS ENERGY'S SECOND-PARTY CONTRACTOR WAS IN THE PROCESS OF REPLACING A CRITICAL VALVE ON AN 8-INCH HIGH PRESSURE DISTRIBUTION LINE NEAR ABERDEEN, MS. THE PROJECT WAS BEING WORKED UNDER MISSISSIPPI ONECALL LOCATE TICKET #2204814572130, AND PROPER LOCATE PRACTICES WERE USED PRIOR TO BEGINNING THE PROJECT USING ALL AVAILABLE INFORMATION ON THE ASSETS IN THE AREA AND LOCATE TECHNOLOGY. UNKNOWN TO ATMOS ENERGY OR THE SECOND PARTY CONTRACTOR, THERE WAS AN UNLOCATABLE AND UNMAPPED 2-INCH NIPPLE AND VALVE LOCATED IN THE VERTICAL POSITION ON THE CARRIER PIPE, AND THIS UNMAPPED AND UNLOCATABLE ASSET WAS DAMAGED DURING EXCAVATION ACTIVITIES. THE CONTRACTOR RESPONDED TO THE DAMAGE USING APPROPRIATE EMERGENCY RESPONSE PRACTICES. IN ORDER TO ELIMINATE THE HAZARDOUS CONDITION, A STOPPLE FITTING WAS WELDED ONTO THE CARRIER PIPE AND TAPPED. DURING THE REPAIR, THE UNINTENTIONAL LOSS OF GAS EXCEEDED THE REPORTABLE THRESHOLD, AND ATMOS ENERGY REPORTED THE DAMAGE AS AN INCIDENT.
2023-06-30 12:35 | NO | YES | YES | 20220042 | 36800 | 2022-06-24 16:50 | ORIGINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2022-05-27 00:36 | EASTERN | NO | 2022 | 453 & 455 E HALE STREET | POTTSTOWN | MONTGOMERY | PA | 19464 | 40.2508 | -75.6388 | [7 empty] | YES | NOT APPLICABLE | 2022-05-27 00:36 | 1337124 | 1337261 | OTHER GAS | UNKNOWN | 0 | 0 | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2022-05-26 20:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-05-26 20:11 |  |  |  | 2022-05-26 20:45 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | RESIDENTIAL HOME |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 7 | 2 | 0 | 20 | 20 | 25 | 192.619(A)(4) | 1967-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | RUSHABH SHAH |  | rushabh.shah2@exeloncorp.com | [5 empty] | MATTHEW MARINZOLI |  | 267-533-1169 | matthew.marinzoli@exeloncorp.com | THIS INVESTIGATION IS ONGOING. TO DATE, PECO HAS NO EVIDENCE THAT ITS FACILITIES CAUSED THIS INCIDENT.
2023-06-30 12:35 | NO | YES | NO | 20220044 | 36927 | 2022-07-05 18:18 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2021-01-27 12:00 | EASTERN | YES | 2021 | LOCKHART ROAD | BELPRE | WASHINGTON | OH | 45714 | 39.2913 | -81.5726 | [7 empty] | YES | DEO DETERMINED THIS LEAK TO BE NON-HAZARDOUS BASED ON THE SIZE AND REMOTE LOCATION OF THE LEAK. |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 3.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-10-23 10:00 | NO |  |  | 2020-10-23 12:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | LEGACY PIPELINE BY-PASS/FITTING | 2004 | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 1321100 | 1347720.5259562845284 | 500 | 510.075136612022 | 0 | 0 |  | 2.65 | 10 | 11.34551495016611295681063122923588039867 | 0 | 0 | 1321610 | 594794.2663798271751335548172757475083056 | 1348241.94660784671651295681063122923588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 160 | 175 | 192.619(A)(2) | 2004-06-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM DID NOT DETECT THE INCIDENT DUE TO MINIMAL SIZE OF LEAK AND MINIMAL RELEASE OF GAS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | A029702031 | OHIO811 | CONTRACT LOCATOR | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | DATA NOT COLLECTED | [173 empty] | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | AMY KONCELIK | amy.l.koncelik@dominionenergy.com | 3308109842 | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 2167899152 | a.walters-thompson@dominionenergy.com | 2ND PARTY CONTRACTOR HIT AN UNMARKED DEO HP LINE STUB THAT HAD BEEN ORIGINALLY USED AS A BY-PASS CREATING A MINIMAL LEAK IN A REMOTE HEAVY TERRAIN AREA.
2023-06-30 12:35 | NO | YES | NO | 20220045 | 36950 | 2022-07-07 14:10 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-06-07 17:07 | PACIFIC | YES | 2022 | 7015 TELEGRAPH ROAD | COMMERCE | LOS ANGELES | CA | 90040 | 33.987 | -118.1346 | YES | [8 empty] | 2022-06-07 17:53 | 1338079 | 1338306 | NATURAL GAS |  | 2357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-06-07 09:05 | YES | OPERATOR | 2022-06-07 09:08 | 2022-06-07 09:05 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 93 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.24 | [6 empty] | RUPTURE |  |  |  |  | LONGITUDINAL |  | 31.5 | 1.5 |  | CLASS 3 LOCATION | 0 | 0 | 250000 | 250000 | 150000 | 150000 | 0 | 0 |  | 6 | 14142 | 14142 | 0 | 0 | 414142 | 184643.4357717019625183016105417276720351 | 414142 | 55 | 36 | 12 | 0 | 0 | 12 | 91 | 223.58 | 115 | 125 | 192.619(C) | 1953-10-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NONE |  | 8.9 |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 18 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [196 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [61 empty] | YES | [5 empty] | YES | [5 empty] | MIGUEL GAMBOA | PIPELINE SAFETY AND COMPLIANCE ADVISOR | mgamboa@socalgas.com | 818-618-2564 |  | MIGUEL GAMBOA | mgamboa@socalgas.com | 818-618-2564 | MIGUEL GAMBOA | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 818-618-2564 | mgamboa@socalgas.com | ON 06-07-2022, SOCALGAS CREWS RESPONDED TO AN OVERPRESSURE ON A DISTRIBUTION MAIN IN THE CITY OF COMMERCE. THE OVERPRESSURE OCCURRED DURING THE PROCESS OF CONDUCTING AN IN-LINE INSPECTION RUN. THERE WERE NO INJURIES OR FATALITIES FROM THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC DUE TO ESTIMATED PROPERTY DAMAGE EXCEEDING $122,000. 8/5/22 UPDATE - AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT DURING THE ILI PIGGING OPERATION, EXCESS LIQUID DEBRIS LOCATED IN TRANSMISSION PIPELINE L-2000 WERE INADVERTENTLY DIRECTED INTO THE DISTRIBUTION SYSTEM, CAUSING A REGULATOR STATION TO STAY OPEN AND OVER PRESSURIZE A DISTRIBUTION PIPELINE. ALL REPAIRS TO THE PIPELINE HAVE BEEN COMPLETED AND NO FURTHER GAS LEAKAGE WAS FOUND. THE REGULATOR STATION WAS REBUILT, TESTED AND ALL LIQUIDS REMOVED. THERE HAVE BEEN NO FURTHER CONCERNS.
2023-06-30 12:35 | NO | NO | NO | 20220047 | 36836 | 2022-07-07 16:07 | ORIGINAL FINAL | 18508 | SOUTHERN INDIANA GAS & ELECTRIC CO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2022-05-23 15:30 | CENTRAL | YES | 2022 | 2710 WINDEMERE | EVANSVILLE | VANDERBURGH | IN | 47725 | 38.0637 | -87.5149 | [5 empty] | YES |  |  |  | 2022-05-23 18:25 | 1336798 |  | NATURAL GAS |  | 73.612 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-05-23 15:30 | OPERATOR/CONTRACTOR |  | 73.6 | NO | 12 | 2022-05-23 15:35 |  |  |  | 2022-05-23 16:15 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 60000 | 60000 | 8000 | 8000 | 500 | 500 | 10000 | 10000 | CURRENT ESTIMATED 2.B IS FOR CAPPING ENDS. 10K WOULD BE IF ENDS WERE RECONNECTED | 5.175 | 381 | 381 | 0 | 0 | 78881 | 34851.5375754673739802342606149341142021 | 78881 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 58 | 58 | 60 | 192.619(A)(2) | 1997-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INITIATED BY A THIRD PARTY EXCAVATOR HITTING A PLASTIC DISTRIBUTION MAIN WHICH IGNITED ALMOST IMMEDIATELY. GAS CONTROL WAS NOT INVOLVED, COULD NOT HAVE RESPONDED TO OR MINIMIZED THE LOSS OR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | NO |  |  | CONTRACT LOCATOR | YES | YES | YES | 2 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | SCOTT CHANDLER | LEAD OPERATION SPECIALIST | scott.chandler@centerpointenergy.com | 812-491-4117 |  | SCOTT CHANDLER | scott.chandler@centerpointenergy.com | 812-491-4117 | SHERRI BELL | MANAGER PIPELINE SAFETY AND COMPLIANCE | 812-491-4806 | sherri.bell@centerpointenergy.com | DCI WAS CONTRACTED BY CENTERPOINT INDIANA-ELECTRIC TO INSTALL UNDERGROUND ELECTRIC LINES AND A NEW JUNCTION BOX IN THE GREEN SPACE ACROSS FROM 2710 WINDEMERE DRIVE, EVANSVILLE, INDIANA 47725 (VANDERBURGH COUNTY). DCI HAD SUBCONTRACTED THE EXCAVATION WORK OUT TO EARLEY ELECTRIC. ON MAY 23, 2022, LESTER KNEPP WITH EARLEY ELECTRIC WAS OPERATING A CATERPILLAR 304E MINI EXCAVATOR TO EXPOSE UNDERGROUND ELECTRIC LINES ALONG THE SOUTH SIDE OF WINDEMERE DRIVE. DCI HAD CALLED FOR LOCATES BY CALLING INDIANA 811 AND GOT A LOCATE TICKET # 2205092040 ON MAY 9, 2022. EARLEY ELECTRIC AND MR. KNEPP WERE UNDER THE MISTAKEN IMPRESSION THEY COULD EXCAVATE UNDER DCI'S LOCATE AND THEREFORE DID NOT CALL FOR THEIR OWN LOCATE TICKET. AT APPROXIMATELY 1530HR., MR. KNEPP, WHILE OPERATING THE MINI EXCAVATOR, HIT A 2' PE UNDERGROUND GAS MAIN OWNED AND OPERATED BY SOUTHERN INDIANA GAS AND ELECTRIC COMPANY D.B.A CENTERPOINT ENERGY INDIANA ' SOUTH. THE GAS MAIN WAS OPERATING AT APPROXIMATELY 58 PSIG. EARLEY ELECTRIC EMPLOYEE AARON SCHROER WITNESSED THE EVENT, STATING MR. KNEPP UPON HITTING THE MAIN, EXITED THE EXCAVATOR LEAVING IT RUNNING. ACCORDING TO MR. SCHROER, THE GAS WAS BLOWING FOR ABOUT 25 SECONDS BEFORE IT IGNITED. MR. SCHROER NOTIFIED 911 IMMEDIATELY AT APPROXIMATELY 1530HRS. MR. SCHROER STATED THEY DID NOT NOTICE THE GAS LOCATE MARKS THAT WERE PART OF DCI'S MAY 9TH LOCATE TICKET. THE LOCATE WAS PERFORMED ON MAY 10, 2022. LOCATE PICTURES FROM THAT DATE SHOW THE GAS FACILITY WERE PROPERLY FLAGGED AND MARKED. AT THE TIME OF THE EVENT, GAS FACILITY LOCATE FLAGS HAD BEEN REMOVED AND MARKS WERE FAINT. CENTERPOINT DISPATCH WAS NOTIFIED BY 911 DISPATCH APPROXIMATELY 1535HRS. CENTERPOINT GAS CREW WAS NOTIFIED AT 1543HRS. AND ARRIVED ON SCENE AT 1615HRS. THE GAS FROM THE MAIN WAS STILL BURNING. THE PE MAIN WAS DUEL FED SO THE CENTERPOINT GAS CREW DUG UP AND EXPOSED THE MAIN ON THE EAST AND WEST SIDE OF THE DAMAGE. THE GAS CREW PERFORMED SQUEEZE OFF OPERATIONS STOPPING THE FLOW OF GAS AND EXTINGUISHING THE FIRE AT 1700HRS. PRIOR TO SQUEEZING OFF, TWO CUSTOMERS WERE TAKEN OUT OF SERVICE SO THAT GAUGES COULD BE INSTALLED. AT THE TIME OF INSTALLATION, THE EAST GAUGE READ 25PSIG WHERE THE WEST SIDE READ 4PSIG. AFTER SQUEEZE OFF, PRESSURE ON BOTH SIDES RETURN TO NEAR NORMAL PRESSURES. CENTERPOINT DISPATCH SENT OUT AN EMAIL ALERTING STAKEHOLDER, INCLUDING MEMBERS OF THE INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT OF THE INITIAL REPORT FROM 911 AT 1545HRS. CENTERPOINT PIPELINE SAFETY AND COMPLIANCE DEPARTMENT WAS IN CONTACT WITH MEMBERS OF THE INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT SHORTLY THEREAFTER. INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT, CHIEF ENGINEER RICH MEDCALF ARRIVED ON SCENE AND INVESTIGATED. LOCAL NEWS MEDIA COVERAGE AS WELL AS MEMBERS OF THE PUBLIC POSTED VIDEO OF THE FIRE ON SOCIAL MEDIA SITES. ON BOTH SIDES OF THE DAMAGE, THE MAIN WAS CUT AND CAPPED OFF A SHORT DISTANCE FROM WHERE IT WAS SQUEEZED OFF. IT HAS YET TO BE DETERMINED IF OR WHEN THE MAIN WILL BE RESTORED TO DUAL FED STATUS. CENTERPOINT PIPELINE SAFETY AND COMPLIANCE DEPARTMENT LEAD OPERATION SPECIALIST DECIDED TO CONTACT THE NRC, DESPITE THE EVENT NOT MEETING REPORT CRITERIA, DUE TO THE AMOUNT OF ATTENTION AND VIDEO.
2023-06-30 12:35 | NO | YES | NO | 20220048 | 36841 | 2022-07-11 14:07 | ORIGINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-06-13 15:09 | EASTERN | NO | 2022 | 1417 WHISPERING OAKS CIRCLE | MATTHEWS | UNION | NC | 28104 | 35.0223 | -80.7198 | [5 empty] | YES |  |  |  | 2022-06-13 17:19 | 1338656 | 1338728 | NATURAL GAS |  | 37.77 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-06-13 15:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 37.77 | NO | 1 | 2022-06-13 15:09 |  |  |  | 2022-06-13 15:37 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2007 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM GAS METER AND REGULATOR | [9 empty] | OTHER | [8 empty] | HOUSE FIRE. | CLASS 4 LOCATION | 0 | 0 | 122000 | 122000 | 4301 | 4301 | 0 | 0 |  | 6 | 227 | 227 | 0 | 0 | 126528 | 55850.4450732334600840424597364568081991 | 126528 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 60 | 60 | 75 | 192.619(A)(4) | 1995-04-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HOUSE FIRE. | [154 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | FIRE DEPARTMENT WAS DISPATCHED TO RESPOND TO A POSSIBLE STRUCTURE FIRE. CREWS ARRIVED ON THE SCENE TO FIND A TWO-STORY SINGLE FAMILY STRUCTURE WITH FLAMES SHOWING THROUGH THE ROOF. WITNESSES STATED THAT THEY HEARD A LOUD POP FOLLOWED BY A HISSING NOISE. FLAMES WERE BLOWING UP THE SIDE OF THE STRUCTURE DUE TO PIPING BEING DISCONNECTED FROM THE METER. THE INCIDENT WAS RULED ACCIDENTAL WITH AN EXACT CAUSE BEING UNDETERMINED PENDING FURTHER EXAMINATION OF THE NATURAL GAS METER AND REGULATOR. PROPERTY DAMAGE AMOUNT HAS NOT BEEN CONFIRMED AT THIS TIME.
2023-06-30 12:35 | NO | NO | NO | 20220050 | 37104 | 2022-07-15 16:00 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2022-06-16 05:34 | EASTERN | YES | 2022 | 10611 14 MILE RD NE | ROCKFORD | KENT | MI | 49341 | 43.1764 | -85.4072 | [5 empty] | YES |  |  |  | 2022-06-16 11:25 | 1338925 | 1339649 | NATURAL GAS |  | 25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-06-16 09:12 | OPERATOR/CONTRACTOR |  | 0 | NO | 7 | 2022-06-16 05:38 |  |  |  | 2022-06-16 06:17 | NO | PRIVATE PROPERTY | TRANSITION AREA | OTHER | BOTH UNDERGROUND AND ABOVEGROUND |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1981 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.625 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 3408 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 50000 | 50000 | 0 | 0 | 26452 | 26452 | 0 | 0 | PROPERTY DAMAGE COST UNKNOWN. FIRE DAMAGE FROM ELECTRIC SURGE EST. $50,000 | 4.3 | 108 | 108 | 0 | 0 | 76560 | 33790.1540786061574431215226939970717423 | 76560 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1981-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [111 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [134 empty] | YES | [8 empty] | YES | [24 empty] | JUSTIN C MORRIS | ENGINEER | justin.morris@dteenergy.com | 2484621760 |  |  |  |  | JUSTIN C MORRIS |  | 2484621760 | justin.morris@dteenergy.com | AT 05:38, FIRE DEPT NOTIFIED DTE GAS OF A RESIDENTIAL FIRE. FIRST CREW ARRIVED AT 06:17. INITIAL FIRE WAS CAUSED BY LIGHTNING OR DOWNED POWER LINE. BETWEEN 07:30 AND 11:00, SEVERAL SMALL GAS LEAKS WERE DISCOVERED. NRC WAS NOTIFIED AT 11:25, AND MICHIGAN PUBLIC SERVICE COMMISION AT 11:36. MULTIPLE HOUSES ALONG 14 MILE NE BECAME ENERGIZED BY THE LIGHTNING STRIKE OR DOWNED POWER LINE. THE ELECTRICAL SURGE LOCALLY ENERGIZED CABLES WITHIN HOMES, CAUSING FIRE DAMAGE. THE ELECTRICAL SURGE ALSO LOCALLY AFFECTED GAS SERVICE TRACER WIRES. TRACER WIRE DAMAGE TO PLASTIC GAS SERVICES RESULTED IN PINHOLE TYPE LEAKS. THE THREE AFFECTED SERVICE LINES THAT WERE COMPROMISED BY HOUSE FIRE AND SURGES TO TRACER WIRES WERE FULLY RENEWED WITHIN 24 HOURS. THE THREE AFFECTED RESIDENTIAL ADDRESSES WERE 10509 14 MILE RD NE, 10567 14 MILE RD NE, AND 10611 14 MILE RD NE. ALL THREE SERVICES WERE 5/8" HD PLASTIC INSTALLED IN 1981 OR 1988. TOTAL GAS LOSS IS MINIMAL DUE TO SIZE OF LEAKS AND ESTIMATED AT 25 MCF. AT 10611 14 MILE, A SMALL, PINHOLE LEAK WAS FOUND BURNED INTO THE SERVICE APPROXIMATELY 30' FROM THE HOME, BUT THE FIRE WAS ON THE INSIDE OF THE HOUSE, NOT THE OUTSIDE. AT 10567 14 MILE, THIS HOUSE HAD ALUMINUM SIDING THAT BECAME ENERGIZED. THE ELECTRICITY ARC'D FROM THE SIDING TO THE TRACER WIRE WHICH THEN WENT BELOW GRADE AND BURNED A SMALL HOLE IN THE SERVICE LINE. FIRE WAS ON OUTSIDE OF HOUSE INCLUDING METER MANIFOLD. AT 10509 14 MILE, SERVICE WAS ALSO RENEWED AS PRECAUTION. ALL THREE RESIDENCES HAD SERVICES RENEWED.
2023-06-30 12:35 | NO | YES | NO | 20220051 | 37524 | 2022-07-15 16:38 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-01-14 16:00 | CENTRAL | YES | 2022 | 9301 WHITE SETTLEMENT | WHITE SETTLEMENT | TARRANT | TX | 76108 | 32.7605 | -97.4754 | [6 empty] | YES |  |  | 2022-06-15 12:41 | 1338839 | 1339031 | NATURAL GAS |  | 15.369 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-14 16:00 | YES | OPERATOR | 2022-01-14 16:08 | 2022-01-14 16:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 16 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 129307 | 129307 | 32882 | 32882 | 0 | 0 |  | 7.874 | 121 | 121 | 0 | 0 | 162310 | 71621.5531133938398097935578330893118594 | 162310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1955-08-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | SEWER (SANITARY/STORM) | YES | 2251192444 | TEXAS 811 | CONTRACT LOCATOR | YES | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  |  | INCORRECT FACILITY RECORDS/MAPS | [170 empty] | JULIE CAMPBELL | COMPLIANCE ANALYST | julie.campbell@atmosenergy.com | 214-535-6117 |  | ROBERT WILLIAMS | robert.williams@atmosenergy.com | 8172072998 | JEFF KNIGHTS | SR VP TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON JANUARY 14, 2022, A THIRD-PARTY CONTRACTOR WAS DIRECTIONAL DRILLING AND BORED INTO ATMOS ENERGY'S 16-INCH STEEL GAS MAIN AT 9301 WHITE SETTLEMENT ROAD. THE INTERMEDIATE PRESSURE MAIN IS A TWO-WAY FEED. THE TECHNICIAN ARRIVED ON THE SCENE AND CONFIRMED THE LEAK AT 4:00 PM. ASSISTANCE WAS REQUESTED AT 4:20 PM. AT 4:08 PM THE TECH NOTED THAT FIRE DEPARTMENT WAS ON SITE INDICATING THEY WERE CONTACTED PRIOR TO THAT TIME. THIS IS THE TIME PROVIDED IN PART A QUESTION 15. OTHER NOTES INDICATE THE POLICE DEPARTMENT WAS ALSO ON THE SCENE, HOWEVER THERE IS NOT A TIME GIVEN. FIRE AND POLICE REMAINED ON SCENE TO PROVIDE TRAFFIC AND PERIMETER ASSISTANCE. STOPPLE FITTINGS WERE APPLIED TO CONTROL THE RELEASE OF GAS AND A SPLIT-WELD SLEEVE WAS INSTALLED TO REPAIR THE LEAK. THESE PERMANENT REPAIRS WERE COMPLETED ON JANUARY 15, 2022, AT 6:30 AM. ON JUNE 15, 2022 AT APPROXIMATELY 12:06 PM, IT WAS DETERMINED THAT REPAIRS COSTS HAD MET THE REPORTING THRESHOLD. A REPORT WAS MADE TO NRC WITHIN THE HOUR. REGARDING PART C QUESTION 5 - THE DIAMETER OF THE PUNCTURE IS 0.226 INCHES, BUT THE FORM ONLY ALLOWS WHOLE NUMBERS. SUPPLEMENTED TO PROVIDE ANSWERS IN PART C, QUESTION 2A AND PART E, QUESTION 3B. 12/19/2022 - FURTHER SUPPLEMENTED TO CHANGE THE SUB-CAUSE FROM FACILITY MARKING OR LOCATION NOT SUFFICIENT TO INCORRECT FACILITY RECORDS/MAPS.
2023-06-30 12:35 | NO | YES | YES | 20220053 | 37368 | 2022-07-21 19:22 | SUPPLEMENTAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2022-06-20 11:15 | CENTRAL | YES | 2022 | 198 BRICK PLANT RD | CORDOVA | WALKER | AL | 35550 | 33.7578 | -87.2124 | YES | [8 empty] | 2022-06-20 13:24 | 1339286 | 1339308, 1339472 | NATURAL GAS |  | 575 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-06-20 11:15 | ALLOWED TO BURN OUT |  | 575 | NO | 0 | 2022-06-20 11:15 | NO |  |  | 2022-06-20 12:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.8 | 7 | [7 empty] | CLASS 1 LOCATION | 60000 | 60000 | 23000 | 23000 | 2000 | 2000 | 119000 | 119000 | RELIGHTS AND RECONNECTS | 13.07 | 7515 | 7515 | 0 | 0 | 211515 | 94343.1436052078251888726207906295754026 | 211515 | 66 | 1 | 400 | 0 | 1 | 400 | 67 | 138 | 138 | 150 | 192.619(A)(4) | 1987-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED TO THE SCADA INFORMATION AND MADE THE APPROPRIATE NOTIFICATIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | YES | [6 empty] | OCCUPANT | UNKNOWN/OTHER | DRAINAGE | NO |  |  | UNKNOWN/OTHER | NO | UNKNOWN/OTHER | YES | 27 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [144 empty] | YES | [26 empty] | RANDY WILSON | DIRECTOR PIPELINE SAFETY AND COMPLIANCE | randy.wilson@spireenergy.com | 205-337-1337 |  | RANDY WILSON | randy.wilson@spireenergy.com | 205-337-1337 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A 4" HIGH PRESSURE STEEL MAIN WAS DAMAGED BY A FRONT END LOADER AND THE RELEASED GAS IGNITED. THE FIRE TOTALLY DESTROYED THE CONSTRUCTION EQUIPMENT, A MOTOR VEHICLE, AND SURROUNDING BRUSH. THE FRONT END LOADER OPERATOR WAS SEVERELY BURNED IN THE INCIDENT AND WAS HOSPITALIZED. THE EXCAVATOR DID NOT MAKE ANY NOTIFICATION TO THE ONE CALL CENTER FOR LINE LOCATES. HOWEVER, PIPELINE MARKER SIGNS WERE NEAR THE LOCATION THAT WAS DAMAGED. THE PIPELINE WAS SHUT DOWN TO STOP THE FIRE AND ALLOW FOR REPAIRS. 467 CUSTOMERS WERE WITHOUT SERVICE UNTIL REPAIRS WERE COMPLETED. CONFIRMATION OF THE INCIDENT CONDITION BEING MET OF INJURY LIKELY REQUIRING HOSPITALIZATION WAS DETERMINED AT 12:48 PM. THIS WAS WHEN THE OPERATOR OF THE FRONT-END LOADER WAS TRANSPORTED BY AMBULANCE TO THE HOSPITAL WITH INJURIES EXPECTED TO REQUIRE ADMITTANCE. THE NRC NOTIFICATION WAS THEN MADE SHORTLY THEREAFTER AT 1:24 PM.
2023-06-30 12:35 | NO | NO | NO | 20220054 | 36918 | 2022-07-29 12:17 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 220 OPERATION WAY MAIL CODE J48 | CAYCE | SC | 29033 | 2022-07-07 16:00 | EASTERN | YES | 2022 | 4920 AUGUSTA RD | LEXINGTON | LEXINGTON | SC | 29073 | 33.9787 | -81.1941 | YES | [5 empty] | YES |  |  | 2022-07-07 18:03 | 1340874 | 1340979 | NATURAL GAS |  | 2451 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-07-07 15:30 | YES | OPERATOR | 2022-07-07 18:03 | 2022-07-07 15:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 12872 | 12872 | 9356 | 9356 | 189 | 189 | ADMINISTRATIVE | 12.38 | 30343 | 30343 | 0 | 0 | 52760 | 27437.8161345577155799663250366032210835 | 52760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 48 | 60 | 192.621 M | 2000-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ACTIONS WERE NOT REQUIRED IN THE IDENTIFICATION OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2207050401 |  | CONTRACT LOCATOR | YES | YES | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NOTIFICATION TO ONE-CALL CENTER MADE, BUT NOT SUFFICIENT | [171 empty] | MARK NOAH | MANAGER - COMPLIANCE AND INTEGRITY | mark.noah@dominionenergy.com | 704-810-3224 |  | ASHLEY FORTE | ashley.forte@dominionenergy.com | 803-217-6105 | CYNTHIA OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-217-9245 | cynthia.ostrander@dominionenergy.com | ON JULY 7, 2022, AT APPROXIMATELY 3:30 PM, DOMINION ENERGY SOUTH CAROLINA (DESC) RESPONDED TO A BROKEN GAS MAIN NEAR THE INTERSECTION OF I-20 AND US-1 (AUGUSTA RD), IN LEXINGTON, SC. SHORTLY AFTER THE DESC FIRST RESPONDER ARRIVED, THE FIRE DEPARTMENT ARRIVED AND TOOK CONTROL OF THE AREA. THE THIRD PARTY EXCAVATOR, A SUBCONTRACTOR OF THE COMPANY DOING WORK ON THE INTERSTATE, HAD GOUGED THE 6-IN STEEL, MEDIUM PRESSURE MAIN. THE EXCAVATOR DID NOT HAVE A CLEAR LOCATE TICKET. IN ADDITION, THE EXCAVATOR STATED THEY ASSUMED THE MAIN WAS ABANDONED. THE CONTRACTOR HAD SPOTTED THE MAIN AND FULLY EXPOSED IT BEFORE PROCEEDING TO PULL IT OUT OF THE GROUND. A NEARBY VALVE WAS CLOSED TO REDUCE THE LEAK RATE, THOUGH THE LINE STILL LEAKED AS IT WAS TWO-WAY FED. THE LEAK WAS STOPPED BY INSTALLING A STOPPER FITTING AT APPROXIMATELY 11:30 PM. THE DAMAGED PORTION OF PIPE WAS ALREADY SCHEDULED TO BE ABANDONED AT A LATER DATE. AFTER THE LEAK WAS STOPPED AND REPAIRS WERE MADE ON JULY 8, THIS SECTION OF PIPELINE WAS ABANDONED. DUE TO THE LOCATION OF THE DAMAGE, AND THE AMOUNT OF GAS THAT WAS ESCAPING THE DECISION WAS MADE TO SHUT DOWN AUGUSTA RD AND I-20 (BOTH DIRECTIONS OF TRAFFIC). THE INTERSTATE WAS SHUT DOWN DUE TO CARS DRIVING BY AND SPREADING THE PLUME OF GAS. GAS BLEW FOR APPROXIMATELY 8 HOURS AND THE INTERSTATE WAS SHUT DOWN FOR APPROXIMATELY 7 HOURS. DESC MANAGEMENT DECIDED TO MAKE A PHMSA NOTIFICATION DUE TO THE CONCERN THAT OUR ESTIMATED LOST GAS WOULD EXCEED 3,000 MCF AND THAT THIS EVENT WOULD BE CONSIDERED SIGNIFICANT IN NATURE. THOUGH THIS THRESHOLD WAS NOT EXCEEDED, THE INCIDENT WAS SIGNIFICANT IN THE JUDGMENT OF DESC, BECAUSE OF THE DURATION OF STOPPING TRAFFIC FLOW ON A MAJOR ARTERY AND SIGNIFICANT GOVERNMENT AND MEDIA ATTENTION. NOTE: E.3.B DATE MAOP ESTABLISHED IS ESTIMATED AS JAN 1, 2000. DECADE OF INSTALLATION IS KNOWN, BUT NOT EXACT DATE OF THE PIPELINE TEST. LDF: 517493
2023-06-30 12:35 | NO | YES | NO | 20220055 | 36919 | 2022-07-29 13:42 | ORIGINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2022-07-03 12:05 | MOUNTAIN | YES | 2022 | 2126 S CREEKSIDE DR | WELLSVILLE | CACHE | UT | 84339 | 41.6939 | -111.8698 |  |  |  | YES | [5 empty] | 2022-07-03 14:16 | 1340511 |  | NATURAL GAS |  | 152.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-07-03 12:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 152.3 | NO | 0 | 2022-07-03 12:05 |  |  |  | 2022-07-03 12:20 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | NO | NO |  |  |  | OTHER | ALUMINUM METER/REGULATOR | [9 empty] | OTHER | [8 empty] | MELTED METER AND REGULATOR | CLASS 3 LOCATION | 283786 | 283786 | 1950 | 1950 | 0 | 0 | 0 | 0 |  | 8.045 | 1225 | 1225 | 0 | 0 | 286961 | 126764.2350561561157764802342606149341142 | 286961 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 43 | 43 | 60 | 192.619(A)(2) | 2021-03-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | STEVEN BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-324-3697 |  | STEVEN BURSETT | steve.bursett@dominionenergy.com | 8016718978 | REID HESS | MANAGER GAS OPERATIONS | 801-324-3374 | reid.hess@dominionenergy.com | ON JULY 3, 2022 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 2126 CREEKSIDE DRIVE, LOGAN, UTAH. DEU SENT A TECHNICIAN TO THE SITE. UPON ARRIVAL THE TECHNICIAN NOTED THE METER WAS DAMAGED AND MELTED DUE TO THE FIRE. THE SERVICE LINE WAS EXPOSED BY EXCAVATION AND SQUEEZE BARS WERE USED TO STOP THE FLOW OF GAS TO THE METER. THE FIRE DEPARTMENT NOTED THAT THE DAMAGE TO THE STRUCTURE WAS ESTIMATED TO BE $283,786. DEU CREWS LEAK SCREENED THE AREA WITH NO LEAKS FOUND. DEU RETIRED THE SERVICE LINE TO THE RESIDENCE. THIS EVENT IS BELIEVED TO BE A FIRE FIRST EVENT, HOWEVER THE INVESTIGATION IS STILL ONGOING.
2023-06-30 12:35 | NO | YES | YES | 20220056 | 36988 | 2022-08-18 11:36 | ORIGINAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2022-07-19 18:00 | CENTRAL | NO | 2022 | 401 MORGAN AVENUE | CHESTERTON | PORTER | IN | 46304 | 41.609 | -87.0563 | [6 empty] | YES |  |  | 2022-07-19 18:19 | 1341980 | 1342191 | NATURAL GAS |  | 2.89 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-07-19 09:45 | NO |  |  | 2022-07-19 09:45 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1928 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | SERVICE TEE | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.555 | 28 | 28 | 0 | 0 | 28 | 16.19326500732064421669106881405563689605 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 1970-12-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ISSUE DID NOT INVOLVE PRESSURE REGULATION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [221 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  |  | YES | THE INTERNAL COMPONENTS OF THE SERVICE TEE, WHICH WAS INSTALLED IN 1928, WERE NOT PRESENT. WHEN THE CAP ON THE TEE WAS REMOVED TO ACCESS THE COMPONENTS THAT WOULD SHUT OFF THE FLOW OF GAS TO THE SERVICE, THE GAS ESCAPED UNEXPECTEDLY AND CUT THE EMPLOYEES LEATHER-GLOVED HAND. | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [44 empty] | YES |  |  |  |  | RICK SMITH | MGR PIPELINE SAFETY AND COMPLIANCE | ricksmith@nisource.com | 219-252-4057 |  | RIC SMITH | ricksmith@nisource.com | 219-252-4057 | RICK SMITH | MGR PIPELINE SAFETY AND COMPLIANCE | 219-252-4057 | ricksmith@nisource.com | THE INTERNAL COMPONENTS OF THE SERVICE TEE, WHICH WAS INSTALLED IN 1928, WERE NOT PRESENT. WHEN THE CAP ON THE TEE WAS REMOVED TO ACCESS THE COMPONENTS THAT WOULD SHUT OFF THE FLOW OF GAS TO THE SERVICE, THE GAS ESCAPED UNEXPECTEDLY AND CUT THE EMPLOYEES LEATHER-GLOVED HAND. THE EMPLOYEE RECEIVED A SMALL LACERATION, BUT WAS CONCERNED IT MAY HAVE HAD GAS BLOWN INTO THE LACERATION UNDER THE SKIN. PER OUR PROCEDURES, THE EMPLOYEE WENT TO THE EMERGENCY ROOM TO HAVE THE INJURY LOOKED AT. THERE WAS NO DOCTOR PRESENT, SO HE WAS ADMITTED BASED ON THE ADMITTING NURSES RECOMMENDATION. THE EMPLOYEE RECEIVED BASIC FIRST AID, BUT WAS NOT SEEN BY A DOCTOR FOR 33HRS. UPON SEEING THE PHYSICIAN, IT WAS INDICATED THERE WAS NO EXPOSURE AND THAT THE EMPLOYEE SHOULD NOT HAVE BEEN ADMITTED. THE EMPLOYEE WAS RELEASED AND RETURNED TO WORK THE FOLLOWING DAY. THIS IS THE FINAL REPORT.
2023-06-30 12:35 | NO | YES | NO | 20220057 | 37046 | 2022-08-29 19:12 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-08-04 02:29 | PACIFIC | YES | 2022 | 667 NORTH F STREET | UPLAND | SAN BERNARDINO | CA | 91786 | 34.1016 | -117.6501 | [5 empty] | YES |  |  |  | 2022-08-04 02:29 | 1343499 | 48hr update NRC# 1343678 | NATURAL GAS |  | 8.7 | 426.9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-07-30 09:59 | NO |  |  | 2022-07-30 10:43 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | YES | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | STUB | 1930 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 14580 | 14580 | 344432 | 344432 | 0 | 0 |  | 6.3303 | 55 | 55 | 2702 | 2702 | 361769 | 159976.802765130274424907759882869692533 | 361769 | 6 | 0 | 130 | 0 | 0 | 130 | 6 | 45 | 45 | 60 | 192.621 M | 1930-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A WATER INTRUSION INCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER INTRUSION CAUSED BY A WATER MAIN LEAK | [136 empty] | YES | [17 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 07/30/2022 SOCALGAS CREWS RESPONDED TO AN UNDER PRESSURE CONDITION AT 220 A STREET, UPLAND, SAN BERNARDINO. ON INVESTIGATION COMPLETED TO DATE REGARDING THE UNDER PRESSURE CONDITION, SOCALGAS IDENTIFIED A LEAKING 3" WATER MAIN AT THE CROSS POINT OF A 3/4" STEEL GAS STUB THAT AFFECTED MULTIPLE SERVICES AND THE MAIN. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO UNDER-PRESSURE. THIS WAS REPORTED TO THE DOT DUE TO GAS RELEASE AND DAMAGE EXCEEDING $129,300.
2023-06-30 12:35 | NO | YES | NO | 20220058 | 37803 | 2022-09-02 13:00 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2022-07-16 04:00 | EASTERN | YES | 2022 | 55 RT 24 | CHESTER TOWNSHIP | MORRIS | NJ | 07930 | 40.7793 | -74.7203 |  |  |  | YES | [5 empty] | 2022-08-15 04:03 | 1344582 | 1344584 | NATURAL GAS |  | 514 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-07-16 04:00 | OPERATOR/CONTRACTOR |  | 514 | NO | 0 | 2022-07-16 04:00 |  |  |  | 2022-07-16 04:15 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1983 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 225000 | 225000 | 25000 | 25000 | 0 | 0 |  | 5.31 | 2729 | 2729 | 0 | 0 | 252729 | 111868.690183082394216691068814055636896 | 252729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 192.619(A)(1) | 1983-08-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A JCP&L POWER LINE CAME DOWN 2 MILES AWAY FROM THE PSE&G POINT OF IGNITION. TEN OTHER IGNITIONS OF VARIOUS TYPES (NO OTHER GAS) OCCURRED IN THE 2 MILE AFFECTED ZONE. THE CAUSE FOR THE POWER LINE DROP HAS NEVER BEEN DETERMINED. | [154 empty] | ROGER GUNNELS | PRINCIPAL REGULATORY SPECIALIST | roger.gunnels@pseg.com | 9739871589 |  | ROGER GUNNELS | roger.gunnels@pseg.com | 9739871589 | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON SATURDAY JULY 16TH PSE&G RECEIVED NOTIFICATION THAT A DOWNED JCP&L ELECTRIC WIRE THAT FOUND ITS WAY TO NEARBY METAL GUARD RAIL AND RESULTED IN THE IGNITION OF A 6 INCH 60 LB. STEEL MAIN LOCATED AT 55 RT 24 IN CHESTER TOWNSHIP. THE LOCATION OF THE IGNITION INVOLVES A BRIDGE. THE MAIN WAS THROTTLED AND TEMPORARY BYPASS WAS INSTALLED TO CONTINUE TO SERVICE CUSTOMERS. THE LOCATION OF THE DOWNED WIRE WAS 2 MILES AWAY FROM THE IGNITION LOCATION. THE CAUSE FOR HOW THE WIRE CAME INTO CONTACT WITH THE GUARD RAIL IS UNKNOWN AT THIS TIME. THERE ARE NO INDICATIONS AT THIS TIME THAT ANY TYPE OF DAMAGE WAS INVOLVED. A PERMANENT REPAIR PLAN IS BEING DEVELOPED AT THIS TIME.
2023-06-30 12:35 | NO | YES | NO | 20220059 | 37563 | 2022-09-02 13:54 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2022-09-01 09:50 | EASTERN | YES | 2022 | 1601 GREEN MOUNTAIN PARKWAY | WILLIAMSBURG | JAMES CITY | VA | 23185 | 37.2083 | -76.5973 | [7 empty] | YES | DRESSER REPAIR SLEEVE | 2022-09-01 09:59 | 1346111 |  | NATURAL GAS |  | 1557 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-08-31 11:12 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-08-31 11:31 | 2022-08-31 11:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 56 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1960 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75000 | 75000 | 50000 | 50000 | 0 | 0 |  | 6.9676 | 10849 | 10849 | 0 | 0 | 135849 | 61419.5244473245060395314787701317715959 | 135849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 137 | 150 | 192.619(A)(4) | 1960-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT LARGE ENOUGH TO BE IDENTIFIED BY THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | B224300196 |  | CONTRACT LOCATOR | NO | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO MAINTAIN THE MARKS | [142 empty] | YES | [26 empty] | MICHAEL SMITH | DIRECTOR- COMPLIANCE AND SYSTEM INTEGRITY | mlsmi@southernco.com | 5408943733 |  | MICHAEL SMITH | mlsmi@southernco.com | 5408943733 | MICHAEL SMITH | DIRECTOR- COMPLIANCE AND SYSTEM INTEGRITY | 5408943733 | mlsmi@southernco.com | VIRGINIA NATURAL GAS (COMPANY) WAS MADE AWARE OF A LEAK ON AUGUST 31, 2022, NEAR THE INTERSECTION OF POCAHONTAS TRAIL AND GREEN MOUNT PARKWAY AT 1601 GREEN MOUNT PARKWAY IN WILLIAMSBURG, VA. SHIRLEY CONTRACTING COMPANY (CONTRACTOR) WAS CONSTRUCTING A NEW ROAD AND SHOULDER FOR VDOT FROM THE INTERSECTION OF POCAHONTAS TRAIL AND GREEN MOUNT PARKWAY FOR A DISTANCE OF APPROXIMATELY 900 FEET EAST OF THAT INTERSECTION. THE CONTRACTOR WAS EXCAVATING DIRECTLY ABOVE THE COMPANY'S 16-INCH STEEL PIPELINE WHEN IT SCRAPED THE PIPELINE CAUSING COATING DAMAGE, DENTING, AND RIPPING OFF AN EXISTING TAP CAUSING THE LEAK. THE FACILITY WAS MARKED CORRECTLY, BUT PARTS OF THE MARKS WERE DESTROYED BY THE CONTRACTOR DURING CONSTRUCTION. THE CONTRACTOR SHOULD HAVE CONTACTED VA811 TO GENERATE A 3-HOUR TICKET TO REMARK THE FACILITY BEFORE CONTINUING ITS WORK. THE COMPANY WORKED WITH THE LOCAL FIRE DEPARTMENT AND LAW ENFORCEMENT TO SHUT DOWN ROUTE 60 AND REDUCED THE PRESSURE ON THE PIPELINE FROM APPROXIMATELY 150 PSI TO 100 PSI UNTIL REPAIRS COULD BE MADE. THE COMPANY UTILIZED A REPAIR SLEEVE TO REPAIR THE LEAK.
2023-06-30 12:35 | NO | YES | YES | 20220060 | 38223 | 2022-09-17 19:04 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-09-15 20:05 | PACIFIC | YES | 2022 | 6500 URSULA PL S. | SEATTLE | KING | WA | 98108 | 47.5459 | -122.3103 | YES | [8 empty] | 2022-09-15 18:47 | 1347398 | 1347652 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2022-09-15 14:24 | ALLOWED TO BURN OUT |  | 0.01 | NO | 0 | 2022-09-15 14:24 | NO |  |  | 2022-09-15 14:24 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1956 | UNKNOWN | [7 empty] | OTHER | WELD BETWEEN A FLANGE AND EXISTING RISER | [9 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 115000 | MEDICAL EXPENSES ONLY, NO DAMAGE TO PSE OR OTHER PROPERTY REQUIRING REPAIR. | 8.94 | 0 | 0 | 0 | 0 | 115000 | 50733.595580850405 | 115000 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 135 | 250 | 192.619(A)(3) | 2014-05-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 6 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [221 empty] | OTHER INCORRECT OPERATION | UNINTENTIONAL IGNITION WHILE WELDING ON AN OUT OF SERVICE REGULATOR STATION, AND OUR WORKING ASSUMPTION IS THAT IT WAS GAS AND WE ARE TAKING CORRECTIVE ACTIONS ON THAT BASIS. | YES |  |  |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [40 empty] | YES | [8 empty] | JUSTIN WAHLBORG | SR. COMPLIANCE PROGRAM MANAGER | justin.wahlborg@pse.com | 4257661811 |  |  |  |  | ZAKARIA MOHAMED | MANAGER COMPLIANCE | 4252476751 | zakaria.mohamed@pse.com | PUGET SOUND ENERGY (PSE) AND INFRASOURCE (IFS) WERE PERFORMING REPLACEMENT WORK ON A REGULATOR STATION FACILITY. THE FACILITY WAS ISOLATED FROM THE SURROUNDING SYSTEM BY CLOSING THE INLET AND OUTLET VALVES AND HAD BEEN BLOWN DOWN AND PURGED OUT OF SERVICE USING NITROGEN. THE IFS CREW WAS WORKING REBUILDING A STATION REGULATOR RUN BY ON WELDING A FLANGE ONTO AN OPEN PIPE RISER WHEN UNINTENTIONAL IGNITION OCCURRED. TWO CREW MEMBERS WERE TRANSPORTED TO THE HOSPITAL: AN IFS WELD HELPER WAS TREATED IN THE ER AND RELEASED, AND A PSE PRESSURE CONTROL TECHNICIAN WAS ADMITTED TO THE HOSPITAL AT 20:05 FOR BURN TREATMENT. OUR INVESTIGATION WAS INCONCLUSIVE, BUT OUR WORKING ASSUMPTION IS THAT ONE OF THE CLOSED VALVES BYPASSED A SMALL AMOUNT OF GAS. THE CONSTRUCTION PROCEDURE THAT WAS BEING FOLLOWED DURING THE PROJECT CONTAINED SEVERAL ISOLATION AND MONITORING STEPS: - THE VALVES ISOLATING THE WORK AREA FROM THE ACTIVE SYSTEM WERE SUBJECTED TO A "SHUT IN TEST" AND PASSED THE TEST. - THE PIPING IN THE WELD AREA HAD BEEN INERTED USING NITROGEN, BUT THE IGNITION OCCURRED SEVERAL HOURS AFTER INTERTING PROCESS HAD BEEN COMPLETED. - THE CREW WAS MONITORING FOR GAS READS IN THE INERTED PIPE RISERS AS PART OF THE WELDING PROCESS AND CONFIRMED 0% GAS READS. INVESTIGATION AFTER THE INCIDENT FOUND GAS READS ON THE INERTED SIDE OF THE CLOSED STATION OUTLET VALVE. THE VALVE WAS GREASED TO BRING THESE READS TO 0% GAS. AS PART OF THE FOLLOW UP FROM A SAFETY DEPARTMENT LED ROOT CAUSE ANALYSIS, PSE IS REVISING ENERGY CONTROL PROCEDURES TO ADDRESS THE POSSIBILITY THAT GAS MIGHT LEAK BY A CLOSED VALVE. PSE IS ALSO ADDRESSING MANAGEMENT OF CHANGE FOR WRITTEN CONSTRUCTION PROCEDURE UPDATES, SINCE LAST MINUTE CHANGES NEEDED TO BE MADE TO THE PROCEDURE DOCUMENT FOR THE REGULATOR STATION CONSTRUCTION PROJECT BASED ON PIPING CONDITIONS FOUND IN THE FIELD.
2023-06-30 12:35 | NO | YES | NO | 20220061 | 37148 | 2022-09-22 12:57 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2022-08-24 13:00 | EASTERN | YES | 2022 | I40 & ROCK QUARRY RD | RALEIGH | WAKE | NC | 27610 | 35.7472 | -78.594 | [6 empty] | YES |  |  | 2022-08-24 19:04 | 1345455 | 1345507 | NATURAL GAS |  | 1886 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-08-24 13:05 | NO |  |  | 2022-08-24 13:31 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 210000 | 210000 | 15000 | 15000 | 0 | 0 |  | 5.75 | 10845 | 10845 | 0 | 0 | 235845 | 105533.3811940567316617862371888726207906 | 235845 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 55 | 55 | 60 | 192.621 M | 2020-03-18 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT REQUIRED TO IDENTIFY THE FAILURE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | INTERSTATE HIGHWAY | [9 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 10 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [171 empty] | MARK NOAH | MANAGER - INTEGRITY AND COMPLIANCE | mark.noah@dominionenergy.com | 704-810-3224 |  | CURTIS RICE | curtis.rice@dominionenergy.com | 919-836-2448 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS | 704-810-3230 | scott.swindler@dominionenergy.com | ON AUGUST 24TH, 2022, AT APPROXIMATELY 1:00 PM, DOMINION ENERGY NORTH CAROLINA (DENC) RESPONDED TO A RUPTURED GAS MAIN NEAR THE INTERSECTION OF I-40 AND ROCK QUARRY ROAD, IN RALEIGH, NC. WHEN THE DENC FIRST RESPONDER ARRIVED, EMERGENCY RESPONDERS HAD ALREADY TAKEN CONTROL OF THE AREA. THE THIRD-PARTY EXCAVATOR, A SUBCONTRACTOR OF THE COMPANY DOING WORK ON THE INTERSTATE, HAD PIERCED THE 12-IN STEEL, DISTRIBUTION PRESSURE MAIN WHILE INSTALLING SOUND BARRIER PANELS ALONG THE INTERSTATE ROW. THE EXCAVATOR DID NOT HAVE A LOCATE TICKET. THE CONTRACTOR DID CALL IN A LOCATE REQUEST AFTER THE MAIN HAD BEEN DAMAGED. THE LEAK WAS STOPPED BY INSTALLING STOPPER FITTINGS AT APPROXIMATELY 12:30 AM. GAS BLEW FOR APPROXIMATELY 12 HOURS. DENC MANAGEMENT DECIDED TO MAKE A PHMSA NOTIFICATION DUE TO THE CONCERN THAT OUR REPAIR COSTS WOULD EXCEED $129,300 AND THAT THIS EVENT WOULD BE CONSIDERED SIGNIFICANT IN NATURE. REPAIRS HAVE BEEN COMPLETED AND THE LINE IS BACK IN SERVICE.
2023-06-30 12:35 | NO | YES | NO | 20220062 | 37441 | 2022-09-30 09:59 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2022-09-01 14:12 | EASTERN | NO | 2022 | 120 DEEDS DRIVE | DOVER | TUSCARAWAS | OH | 44622 | 40.5538 | -81.4983 | YES | [8 empty] | 2022-09-01 16:05 | 1346162 |  | NATURAL GAS |  | 13.208 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-01 14:12 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 13.2 | NO | 2 | 2022-09-01 14:12 | NO |  |  | 2022-09-01 14:14 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1989 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | DRISCO | PLASTIC |  |  |  |  | OTHER | DRISCO 8000 |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 2 | 1.3 | [7 empty] | CLASS 3 LOCATION | 310000 | 310000 | 800 | 800 | 5000 | 5000 | 0 | 0 |  | 10.5828 | 140 | 140 | 0 | 0 | 315940 | 139399.8314070588458210834553440702781845 | 315940 | 6 | 0 | 0 | 1 | 0 | 0 | 8 | 58 | 58 | 80 | 192.619(A)(2) | 1989-04-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | [7 empty] | YES |  |  |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | A223704353 | OH811 | CONTRACT LOCATOR | YES | YES | YES | 4 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | AMY LAURIE KONCELIK | SUPERVISOR PIPELINE COMPLIANCE | amy.l.koncelik@dominionenergy.com | 13308109842 |  | AMY LAURIE KONCELIK | amy.l.koncelik@dominionenergy.com | 13308109842 | AMY LAURIE KONCELIK | SUPERVISOR PIPELINE COMPLIANCE | 13308109842 | amy.l.koncelik@dominionenergy.com | A SUBCONTRACTOR FOR A THIRD PARTY CONTRACTOR WAS BORING TO INSTALL FIBER OPTIC LINES AND BORED THROUGH OPERATOR'S 4 INCH MAINLINE, WHICH WAS PROPERLY MARKED. THIRD PARTY CONTRACTOR ACKNOWLEDGED THAT THEIR SUB-CONTRACTOR DECIDED TO DO A PORTION OF THE JOB WITHOUT BEING INSTRUCTED TO DO SO AND FAILED TO POTHOLE, WHICH CREATED THIS EXCAVATION DAMAGE.
2023-06-30 12:35 | NO | YES | NO | 20220063 | 37556 | 2022-09-30 15:37 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-02 10:59 | EASTERN | YES | 2022 | 1631 N. JEROME ROAD (FARM FIELD WEST OF ADDRESS) | ARCADA TOWNSHIP | GRATIOT | MI | 48847 | 43.3113 | -84.6302 | YES | [8 empty] | 2022-09-02 19:44 | 1346279 | 1346357 | NATURAL GAS |  | 309 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-09-02 10:59 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-09-02 10:59 | 2022-09-02 11:32 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1944 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 12.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 250000 | 250000 | 372 | 372 | 0 | 0 |  | 8.95 | 2766 | 2766 | 0 | 0 | 253138 | 112054.2005787893156948345534407027818448 | 253138 | 220 | 18 | 1294 | 0 | 0 | 1294 | 238 | 259 | 259 | 375 | 192.619(C) | 1968-11-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO | [5 empty] | YES | 30 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [171 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON FRIDAY, SEPTEMBER 2, 2022 AT APPROXIMATELY 10:59 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE BY A THIRD-PARTY CONTRACTOR INSTALLING DRAIN TILES IN A FARM FIELD WEST OF 1631 N. JEROME ROAD, ARCADA TOWNSHIP (GRATIOT COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:32 HOURS AND CONFIRMED A 4-INCH HIGH-PRESSURE PIPELINE FEEDING CONSUMERS ENERGY'S ITHACA REGULATION STATION HAD BEEN DAMAGED RESULTING IN A SEVERED PIPELINE. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 12:00 HOURS. TO CONTROL THE GAS FLOW, THE GAS MECHANICS CLOSED THE G-VALVE AT REGULATOR STATION #63831 AT 12:00 HOURS TO ISOLATE DOWNSTREAM OF THE DAMAGE TO MAINTAIN SERVICE TO CUSTOMERS. THE H-67 VALVE WAS CLOSED AT 12:20 HOURS TO ISOLATE AND SHUT-OFF GAS AT THE DAMAGE LOCATION. A REQUEST WAS MADE TO LARGE COMMERCIAL AND INDUSTRIAL CUSTOMERS TO REDUCE GAS USAGE IN AN EFFORT TO MAINTAIN THE PRESSURE REQUIRED TO SERVE THE CITY OF ITHACA. DESPITE EFFORTS TO MAINTAIN PRESSURE, A CONTINUED PRESSURE DROP WAS OBSERVED, AND A DECISION WAS MADE AT APPROXIMATELY 15:30 HOURS TO BEGIN SHUTTING OFF METERS FOR THE 1400+ CUSTOMERS SERVED BY THIS FEED. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 62-FEET OF 4-INCH HIGH-PRESSURE PIPELINE. REPAIRS WERE COMPLETED AND GAS SERVICE RESTORED TO THE HIGH PRESSURE PIPELINE ON SEPTEMBER 3, 2022, AT APPROXIMATELY 06:30 HOURS. RESTORATION TO THE MEDIUM PRESSURE PIPELINE WAS COMPLETED AT 15:30 AND SERVICE RESTORATION BEGAN AT 18:00 HOURS.
2023-06-30 12:35 | NO | YES | NO | 20220064 | 37991 | 2022-10-07 13:07 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-08 17:52 | EASTERN | YES | 2022 | 1102 LAKE STREET | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2809 | -85.5665 | [5 empty] | YES |  |  |  | 2022-09-08 21:02 | 1346805 | 1346828 | NATURAL GAS |  | 315 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-08 17:52 | ALLOWED TO BURN OUT |  | 315 | NO | 25 | 2022-09-08 17:52 |  |  |  | 2022-09-08 17:58 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | UNKNOWN |  |  |  |  | 4 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 6.2 | [7 empty] | CLASS 3 LOCATION | 112929 | 112929 | 26190 | 26190 | 165 | 165 | 0 | 0 |  | 8.95 | 2819 | 2819 | 0 | 0 | 142103 | 63077.0811084245160639590043923865300146 | 142103 | 11 | 0 | 86 | 2 | 0 | 86 | 11 | 54 | 54 | 60 | 192.619(A)(2) | 1991-05-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 6 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 2022082304088 |  | CONTRACT LOCATOR | NO | NO | YES | 11 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY WAS NOT LOCATED OR MARKED | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON SEPTEMBER 8, 2022, AT APPROXIMATELY 17:52 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR 1102 LAKE STREET, KALAMAZOO (KALAMAZOO COUNTY), MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:58 HOURS. THE GSW CONFIRMED A 4-INCH MEDIUM-PRESSURE PLASTIC PIPELINE WAS DAMAGED BY A CONSUMERS ENERGY (2ND-PARTY) CONTRACTOR. DURING THE BORE SHOT PULL BACK, THE BORE REAMER DAMAGED THE PIPELINE CAUSING GAS TO BE RELEASED AND A SUBSEQUENT IGNITION. THE PREVIOUS NIGHT A CANDLELIGHT VIGIL WAS HELD NEAR THE DAMAGE LOCATION, CANDLES REMAINING AT THE SIGHT ARE THOUGHT TO BE THE IGNITION SOURCE. THE POLICE AND FIRE DEPARTMENT WERE ONSITE AND RESIDENTIAL AND COMMERCIAL STRUCTURES WITHIN ONE BLOCK IN ALL DIRECTIONS WERE EVACUATED AND ELECTRIC SERVICE DISCONTINUED. SEVERAL CONTRACT EMPLOYEES WORKING ON BEHALF OF THE OPERATOR SUSTAINED MINOR BURNS AND RECEIVED MEDICAL TREATMENT BUT OVERNIGHT HOSPITALIZATION WAS NOT REQUIRED. POST-ACCIDENT DRUG AND ALCOHOL TESTING WAS PERFORMED FOR ALL CONTRACT EMPLOYEES WORKING ON THIS PROJECT. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 18:40 HOURS AND SQUEEZED THE PIPELINE AT A REMOTE LOCATION WEST OF MILL STREET STOPPING GAS FROM BLOWING. ONCE THE GAS WAS CONTAINED, THE FIRE WAS ALLOWED TO EXTINGUISH BEFORE ASSESSING DAMAGE AND MAKING REPAIRS. IN ADDITION TO OPERATOR EMERGENCY RESPONSE AND REPAIRS COSTS, SIGNAGE, TRAFFIC CONTROL AND LIGHTING AND A NEARBY AUTOMOBILE WAS DAMAGED AND WILL REQUIRE REPLACEMENT AND/OR REPAIR. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 4-FEET OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE. REPAIRS WERE COMPLETED AND GAS SERVICE WAS RESTORED ON SEPTEMBER 9, 2022, AT APPROXIMATELY 04:30 HOURS. SERVICE RESTORATION TO IMPACTED CUSTOMERS BEGAN ON SEPTEMBER 9, 2022, AT APPROXIMATELY 15:30 HOURS. FURTHER INCIDENT INVESTIGATION DETERMINE THE THE CONTRACTOR PERFORMING WORK ON BEHALF OF CONSUMERS ENERGY AND RESPONSIBLE FOR LOCATING AND STAKING THE NATURAL GAS PIPELINE FAILED TO PROPERLY IDENTIFY AND MARK THE PIPELINE DOCUMENTED ON THE CONSTRUCTION PRINT. THE FAILURE RESULTED IN THE CREW UNKNOWINGLY BORING NEAR AN UNMARKED GAS FACILITY CAUSING A RELEASE OF GAS AND SUBSEQUENT IGNITION.
2023-06-30 12:35 | NO | YES | NO | 20220065 | 37666 | 2022-10-07 15:12 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-09 11:23 | EASTERN | YES | 2022 | HALL ROAD W/AVON LANE | CLINTON TOWNSHIP | MACOMB | MI | 48036 | 42.6299 | -82.8645 | [6 empty] | YES |  |  | 2022-09-09 20:03 | 1346895 |  | NATURAL GAS |  | 6068 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 12 | 2022-09-09 11:23 | YES | OPERATOR | 2022-09-09 13:15 | 2022-09-09 11:51 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1.2 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 68869 | 68869 | 183 | 183 | 0 | 0 |  | 8.95 | 54309 | 54309 | 0 | 0 | 123361 | 61871.6702313245466855812591508052708638 | 123361 | 13 | 0 | 7 | 0 | 0 | 7 | 13 | 329 | 329 | 400 | 192.619(A)(2) | 1994-10-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 2022080903891 |  | CONTRACT LOCATOR | YES | NO | YES | 24 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON SEPTEMBER 9, 2022, AT APPROXIMATELY 11:23 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE ON HALL ROAD (WEST OF AVON LANE), CLINTON TOWNSHIP (MACOMB COUNTY), MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 11:51 HOURS. THE GSW CONFIRMED THE DAMAGE WHICH WAS LATER DETERMINED TO BE A 2-INCH STUB (OFF A 6-INCH HIGH-PRESSURE PIPELINE) STRUCK BY A THIRD-PARTY CONTRACTOR INSTALLING DRAIN TILES. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 12:09 HOURS AND PROCEEDED TO EXCAVATE TWO REMOTE HOLES TO THE EAST AND WEST OF THE DAMAGE LOCATION. WHILE ATTEMPTING TO SQUEEZE THE PIPELINE ON THE WEST SIDE OF THE DAMAGE, THE PIPELINE CRACKED AND REQUIRED EXCAVATION AT A THIRD LOCATION. A MUELLER CONTROL FITTING WAS INSTALLED WEST OF THE DAMAGE TO CONTAIN THE BLOWING GAS. THE PIPELINE WAS A ONE-WAY FEED AND RESULTED IN A LOSS OF SERVICE TO 20 CUSTOMERS. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE INCIDENT. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FEET OF 6-INCH HIGH-PRESSURE PIPELINE. REPAIRS WERE COMPLETED AND GAS SERVICE WAS RESTORED ON SEPTEMBER 10, 2022, AT APPROXIMATELY 11:35 HOURS. SERVICE RESTORATION TO IMPACTED CUSTOMERS BEGAN AFTER REPAIRS TO THE PIPELINE WERE COMPLETED. AN INCIDENT INVESTIGATION DETERMINED THE A 2" NATURAL GAS STUB WAS DOCUMENTED ON THE RECORD BUT WAS NOT MARKED BY THE STAKING EMPLOYEE RESULTING IN A NATURAL GAS PIPELINE DAMAGE.
2023-06-30 12:35 | YES | NO | NO | 20220066 | 37623 | 2022-10-19 11:56 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2022-09-28 14:05 | EASTERN | YES | 2022 | 5409 INNISBROOKE PLACE | GREENWOOD | JOHNSON | IN | 46142 | 39.6189 | -86.2052 | [5 empty] | YES |  |  |  | 2022-09-28 15:22 | 1348530 | 1348695 | NATURAL GAS |  | 22.08 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-28 14:05 | OTHER | FIRE EXTINGUISHED BY OPERATOR SQUEEZING OFF THE GAS SERVICE LINE. | 22.08 | NO | 1 | 2022-09-28 14:24 | YES | OPERATOR | 2022-09-28 14:31 | 2022-09-28 14:23 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 | YES | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1992 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 400000 | 400000 | 1381 | 1381 | 2500 | 2500 | 0 | 0 |  | 6.4311 | 142 | 142 | 0 | 0 | 404023 | 178258.9518284701658169560761346998535871 | 404023 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1992-11-04 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.2 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [111 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [150 empty] | YES | [16 empty] | YES | RANDA POWERS | LEAD OPERATIONS SPECIALIST - GAS COMPLIANCE | randa.powers@centerpointenergy.com | 317-997-3939 |  | RANDA POWERS | lead operations specialist - gas compliance | 317-997-3939 | SHERRI BELL | MANAGER PIPELINE SAFETY AND COMPLIANCE | 812-4914806 | sherri.bell@centerpointenergy.com | A CREW FROM JOHNSON COUNTY REMC WAS REPAIRING A BURIED 3 PHASE ELECTRIC SERVICE 4' FROM THE HOME LOCATED AT 5409 INNISBROOKE PL, GREENWOOD IN WHEN THE GAS SERVICE CAUGHT ON FIRE, CATCHING THE HOME ON FIRE. THE REMC CREW HAD BEEN USING A BLOW TORCH TO HEAT SHRINK THE REPAIR. THE 3-PHASE ELECTRIC REPAIR WAS APPROXIMATELY 7 INCHES BELOW THE GAS SERVICE LINE. REMC CREW STATED THEY HAD SPOTTED THE GAS SERVICE, WHICH WAS CORRECTLY LOCATED, USED A SHOVEL TO PROTECT THE PLASTIC GAS LINE BEFORE INTRODUCING FLAME NEAR IT. WHILE USING THE FLAME TO SHRINK WRAP THE REPAIR, THERE WAS AN IGNITION OF THE GAS LINE.
2023-06-30 12:35 | NO | YES | NO | 20220067 | 37252 | 2022-10-20 19:35 | ORIGINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2022-09-23 16:05 | EASTERN | NO | 2022 | 418 TORRENCE COURT | CINCINNATI | HAMILTON | OH | 45202 | 39.1258 | -84.4621 |  |  | YES | YES | [5 empty] | 2022-09-23 17:45 | 1348095 | 1348214 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-23 16:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.01 | NO | 2 | 2022-09-23 16:05 |  |  |  | 2022-09-23 16:39 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1989 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | THE GAS METER WAS BROKEN OFF FROM THE SWIVELS ON THE METER BRANCH AND THE RISER HAD RUPTURED ON THE PLASTIC PORTION ABOVE GROUND DUE TO FIRE DAMAGE MELTING RISER JACKET AND THE INCASED PLASTIC. | CLASS 3 LOCATION | 0 | 0 | 129300 | 129300 | 2000 | 2000 | 0 | 0 |  | 0.1 | 0 | 0 | 0 | 0 | 131300 | 57924.5313023100711 | 131300 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 27 | 28 | 35 | 192.619(A)(2) | 2010-02-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | HOUSE FIRE WITH METER/RISER DAMAGE. CAUSE OF THE FIRE STILL UNDER INVESTIGATION.
2023-06-30 12:35 | NO | YES | YES | 20220068 | 38008 | 2022-10-26 16:13 | SUPPLEMENTAL | 40247 | TEXAS REPUBLIC UTILITY, LLC | 19926 KEENAN CUT OFF RD. | MONTGOMERY | TX | 77316 | 2022-10-03 12:30 | CENTRAL | YES | 2022 | 14020 GROVER CREEK DR | CONROE | MONTGOMERY | TX | 77303 | 30.3531 | -95.3622 |  | YES |  |  |  | YES |  |  |  | 2022-10-04 17:27 | 1349031 | 1349815 (48 Hour Update) | NATURAL GAS |  | 2 | 0 | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES | 2022-10-03 12:30 | OPERATOR/CONTRACTOR |  | 2 | NO | 0 | 2022-10-03 12:30 | YES | OPERATOR | 2022-10-03 12:33 | 2022-10-03 12:33 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE VALVE |  | 2022 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 4" |  |  | 2406 | LEAK |  |  | OTHER | ELECTROFUSION JOINT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 5000 | 0 | 0 | 0 | 0 |  | 11 | 22 | 22 | 0 | 0 | 5022 | 2218.53178316384407759882869692532942899 | 5022 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 40 | 40 | 70 | 192.619(A)(2) | 2022-01-03 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | [145 empty] | FUSION JOINT | [18 empty] | SADDLE, ELECTROFUSION |  | 2022 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [8 empty] | YES |  |  |  | OTHER | SADDLE ELECTROFUSION JOINT DID NOT SEAL COMPLETELY | YES | 2022 | 105 | [69 empty] | YES | [14 empty] | MICHAEL SWAIM | OPERATIONS ADMINISTRATOR | mswaim@ldcgas.com | 936-539-3500 | 936-539-3501 | MICHAEL SWAIM | mswaim@ldcgas.com | 936-539-3500 | BOBBY BROWN JR | CHIEF OPERATING OFFICER | 936-539-3500 | bbrown@ldcgas.com | DURING A HOT TAP PROCEDURE TO CONNECT NEW SERVICE TO A RESIDENCE, THE ELECTROFUSION JOINT DID NOT SEAL COMPLETELY, RESULTING IN A LEAK. DURING AN ATTEMPT TO SQUEEZE OFF THE GAS SUPPLY SO REPAIRS COULD BE MADE, ONE OF TWO PROPERLY GROUNDED SQUEEZERS FAILED. AN ADDITIONAL SQUEEZER (ALSO GROUNDED) WAS BROUGHT INTO THE LOCATION TO SQUEEZE OFF THE SUPPLY ON THAT SIDE OF THE FUSION THE PROCEDURES WERE ADEQUATE AND FOLLOWED FOR ELECTROFUSION AND SQUEEZE OFF. EITHER A SPARK FROM INADVERTENT CONTACT OF METAL ON METAL OR STATIC ELECTRICITY CAUSED THE LEAK TO IGNITE, BURNING TWO OF OUR EMPLOYEES. ALL EMPLOYEES INVOLVED WHERE BOTH QUALIFIED TO PERFORM EACH TASK SUCH AS ELECTROFUSION AND SQUEEZE-OFF. ANOTHER NOTE TO ADD IS THAT THE NEW SERVICE LINE WAS PRESSURE TESTED PRIOR TO TAP.
2023-06-30 12:35 | NO | YES | NO | 20220069 | 37302 | 2022-11-02 15:29 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-10-03 13:23 | EASTERN | YES | 2022 | INTERSTATE 94 & PORTAGE ROAD | PORTAGE | KALAMAZOO | MI | 49002 | 42.2463 | -85.5587 | YES | [5 empty] | YES |  |  | 2022-10-03 16:47 | 1348944 | 1349071 | NATURAL GAS |  | 7578 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-10-03 13:23 | YES | OPERATOR | 2022-10-03 13:45 | 2022-10-03 13:42 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 2 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 31896 | 31896 | 62 | 62 | 0 | 0 |  | 8.95 | 67823 | 67823 | 0 | 0 | 99781 | 53322.7817950504064798799414348462664714 | 99781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 352 | 400 | 192.619(A)(2) | 1973-08-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | INTERSTATE HIGHWAY | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2022092302752 |  | CONTRACT LOCATOR | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY WAS NOT LOCATED OR MARKED | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON OCTOBER 3, 2022, AT APPROXIMATELY 13:23 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR INTERSTATE HIGHWAY 94 (I-94) AND PORTAGE STREET, KALAMAZOO (KALAMAZOO COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 13:42 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR CUTTING IN A NEW ENTRANCE RAMP TO I-94 DAMAGED A NATURAL GAS PIPELINE, WHICH WAS LATER DETERMINED TO BE A 6-INCH STEEL HIGH PRESSURE PIPELINE. THE ROADWAY WAS ALREADY CLOSED TO TRAFFIC WHEN THE DAMAGED OCCURRED DUE TO THE ON-GOING CONSTRUCTION. POLICE AND FIRE DEPARTMENTS WERE ONSITE AND ENSURED NO CONSTRUCTION VEHICLES USED THE CONSTRUCTION ENTRANCES INTO THE AREA. AIR TRAFFIC INTO THE LOCAL AIRPORT WAS ALSO DIVERTED TO PREVENT THE POTENTIAL FOR INJURY. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE PIPELINE DAMAGE AND SUBSEQUENT GAS RELEASE. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 14:02 HOURS AND AN ISOLATION PLAN TO STOP GAS FROM BLOWING WAS DEVELOPED. TO ISOLATE, THE CREW UTILIZED AN EXISTING PRESSURE CONTROL FITTING TO THE NORTH OF THE DAMAGE LOCATION AND MULTIPLE VALVES WERE UTILIZED SOUTH OF THE DAMAGE LOCATION. GAS WAS CONTROLLED AT APPROXIMATELY 18:30 HOURS, THE DAMAGED SEGMENT WAS REMOVED AND REPLACED WITH 28-INCHES OF 6-INCH STEEL PIPELINE. REPAIRS WERE COMPLETED AND NORMAL OPERATIONS RESUMED ON OCTOBER 4, 2022, AT APPROXIMATELY 03:00 HOURS. NO LOSS OF SERVICE TO CUSTOMERS OCCURRED BECAUSE OF THE PIPELINE DAMAGE.
2023-06-30 12:35 | NO | NO | NO | 20220070 | 37834 | 2022-11-03 21:56 | SUPPLEMENTAL FINAL | 30839 | WALDEN, TOWN OF | PO BOX 489 513 HARRISON ST | WALDEN | CO | 80480 | 2022-08-31 13:00 | MOUNTAIN | YES | 2022 | 0.5 MILES EAST OF FAIR GROUNDS | WALDEN | JACKSON | CO | 80480 | 40.747 | -106.2604 | YES | [8 empty] | 2022-10-25 13:38 | 1350815 |  | NATURAL GAS |  | 6100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-09-02 05:30 | NO |  |  | 2022-09-02 09:00 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1970 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 2000 | 2000 | 0 | 0 | 0 | 0 |  | 5.3514 | 32644 | 32644 | 0 | 0 | 34644 | 19761.3570763694907789165446559297218155 | 34644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 15 | 275 | 192.619(A)(2) | 1995-04-15 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM IS OPERATED BY THE GAS SUPPLIER (COLORADO INTERSTATE GAS). THEY DID NOT HAVE REASONABLE ALARMS SET FOR OUR SYSTEM AND NOTIFIED BY TELEPHONE US A WEEK AFTER THE LEAK LIKELY STARTED. SINCE THE EVENT, WE NOW RECEIVE REALISTIC VOLUME BASED ALARMS AS WELL AS DAILY VOLUME REPORTS FROM CIG. THE ALARM VALUES WILL LIKELY BE SET SEASONALLY GOING FORWARD. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  | 2022 |  |  |  |  | YES | COLD APPLIED TAPE |  | YES | [19 empty] | 2022-05-11 | NO | [181 empty] | YES | [44 empty] | JOEL SHUTE | OPERATIONS AND COMPLIANCE MANAGER | joel@pipeline.group | 7202272026 |  | GRAHAM CREWS | graham@waldengas.com | 9703818557 | JOEL SHUTE | OPERATIONS AND COMPLIANCE MANAGER | 7202272026 | joel@pipeline.group | ON AUGUST 31, 2022 THE WALDEN PIPELINE OPERATORS RECEIVED PHONE CALLS FROM THE CIG CONTROL CENTER, ABOUT CONCERNS FOR INCREASED GAS USAGE. ONLINE FLOW RECORDS SHOWED AN APPARENT 10X FLOW INCREASE AROUND AUGUST 23. CIG HAD CHECKED ITS DELIVERY METER AND FOUND NOTHING ABNORMAL. THE 50-MILE TRANSMISSION SYSTEM WAS SYSTEMATICALLY ISOLATED AND CHECKED BY SECTION, AND CIG NOTED AN ABRUPT DROP IN FLOW. THE LAST SECTION ISOLATED WAS THE HIGH-PRESSURE DISTRIBUTION SYSTEM IN COLORADO THAT FEEDS THE TOWN SYSTEMS IN COWDREY AND WALDEN.NEXT DAY WE PINPOINTED LOW PRESSURE ON THE 2-INCH SECTION THAT HELPS FEED WALDEN. THIS WAS THE ORIGINAL SUPPLY LINE TO WALDEN, BUILT CA 1958 OF COATED STEEL 2" PIPE. WE HAD FOUND AND FIXED A CORROSION PINHOLE LEAK ON THIS SEGMENT EARLIER IN JULY, THE ONLY LEAK FOUND IN 20+ YEARS ON ANY PIPELINE IN COLORADO. THIS 17,000 FT SEGMENT WAS LOOPED CA 1979 WITH A 3" COATED STEEL LINE, PARALLEL AND ABOUT 10 FT SOUTHEAST. THE 2" SECTION WAS ISOLATED AND QUICKLY PRESSURED DOWN. LATER, GAS WAS REINTRODUCED AND A LEAK SURVEY DONE IN THE AREA AROUND THE PREVIOUS LEAK. THE NEWER LEAK WAS DETECTED ABOUT 180 FT SW OF THE PREVIOUS REPAIR, RUNNING ALONG A SHALLOW SAGEBRUSH WASH. WITH THIS SEGMENT SHUT DOWN AND THE 3" LOOP CARRYING THE LOAD, WE EXCAVATED THE NEW LEAK AREA ON NOVEMBER 2, INTENDING A REPAIR. THE PIPE AND COATING LOOKED IDENTICAL TO THAT WITH THE NEARBY LEAK REPAIR, BUT WAS VERY SHALLOW. THE EXCAVATED MATERIAL WAS MOSTLY BLACK, SMELLY LEAK DIRT INDICATIVE OF A LONG-TERM GAS LEAK. THE EXCAVATOR STRIPPED OUT THE PIPE FOR 60 FT, AND WE INTRODUCED A SMALL AMOUNT OF GAS FROM THE NEARBY BLOCK VALVE. THE EXPOSED & CLEANED-OFF PIPELINE DIDN'T LEAK. BUT THE GAS DETECTOR PICKED UP GAS NEAR THE FRONT AND NORTH SIDE OF THE BACKHOE, WELL AWAY FROM THE EXPOSED 2" AND THE SIDE AWAY FROM THE 3" LOOP. AFTER FURTHER INVESTIGATION, DIGGING OUT MORE LEAK DIRT, WE EVENTUALLY FOUND A SECOND STRING OF 2" PIPE RUNNING PARALLEL TO THE EXPOSED LINE, ABOUT 7 FT NW AND 3.5 FT DEEPER. WE STRIPPED OUT A 10-FT SECTION OF THIS NEWLY-DISCOVERED PIPE. THE COATING WAS A COLD-APPLIED YELLOW TAPE WITH THICK BLACK MASTIC, LIKELY HAND-APPLIED WITH GOOD OVERLAPS AND NO WRINKLES. WE COULD FIND NO OBVIOUS DEFECTS OR HOLES, UNTIL GAS WAS INTRODUCED. IN LESS THAN 5 SECONDS, THE SHORT SECTION APPEARED TO LEAK IN AT LEAST 4 PLACES, INCLUDING A PINKIE-SIZE HOLE IN THE TAPE AND THE PIPE ON THE BOTTOM. ALTHOUGH THE TAPE LOOKED GOOD ON FIRST INSPECTION, THERE WERE SEVERAL DEEP MARKS AND DENTS, ALTHOUGH THE SOIL WAS ROCK-FREE, MOIST CLAY. THE DEEP DENTS MAY HAVE BEEN MADE DURING INSTALLATION, WHEN THE PIPE WAS LOWERED IN WITH LOG CHAINS INSTEAD OF SOFTER PIPE SLINGS. THIS 3RD LINE IS NOT SHOWN ON ANY MAPS OR DESCRIBED IN ANY DOCUMENTS CONVEYED FROM THE ORIGINAL OWNER ROCKY MOUNTAIN NATURAL GAS TO THE TOWN IN 1995. WITH 5 CORROSION LEAKS (DESPITE GOOD CP READINGS) IN 200 FT IN A FEW MONTHS; AND WITH LITTLE HYDRAULIC VALUE, WE DECIDED TO PERMANENTLY ABANDON THE 2-INCH SEGMENT. WE CUT OUT AN 8-FT SECTION OF THE LEAKING PIPE, AND WELD-CAPPED BOTH ENDS OF THE 17,000 FT SEGMENT, WITH DOCUMENTATION THAT THIS SECTION CAN'T BE USED AGAIN. THIS LEAK WAS ABOUT 1.2 MILES FROM THE EDGE OF WALDEN. THE NEAREST PUBLIC ROAD IS THE COUNTY RODEO & FAIRGROUNDS ABOUT 1/2 MILE AWAY, AND 0.9 MILE TO THE NEAREST RESIDENCE. WE BELIEVE THIS LEAK HAS PERSISTED FOR DECADES. IT WAS NOT REPORTED BY THE PUBLIC, SINCE IT IS VERY REMOTE AND THE PREVAILING WIND GENERALLY BLOWS FROM THE SOUTHWEST, AWAY FROM ANY RESIDENCES OR ROADS. THE UTILITY HAD LEAK-SURVEYED THE 2 KNOWN PARALLEL LINES AS REQUIRED BY DOT PART 192. THE VEHICLE-MOUNTED RIG WAS ALWAYS DRIVEN BETWEEN THE 2 PIPELINES THAT ARE ONLY 8 FT APART. THE UNKNOWN LINE WAS ABOUT 12 FT OUTSIDE THE LEAK SURVEY PATH. WE BELIEVE OLD UNDETECTED PINHOLE LEAKS BLEW OUT WITH THE RE-PRESSURIZATION AFTER THE PREVIOUS REPAIR. NO INJURIES OR DEATHS RESULTED FROM THIS LEAK. THE ONLY DAMAGE WAS THE VALUE OF LOST GAS.
2023-06-30 12:35 | NO | YES | NO | 20220071 | 38113 | 2022-11-07 12:22 | SUPPLEMENTAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-10-08 15:48 | PACIFIC | YES | 2022 | 2793 RIVER PLAZA DRIVE | SACRAMENTO | SACRAMENTO | CA | 95833 | 38.6091 | -121.5247 | [5 empty] | YES |  |  |  | 2022-10-09 00:36 | 1349399 | 1349521 | NATURAL GAS |  | 39.9 | 0.006 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-10-08 16:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 39.9 | YES | 24 | 2022-10-08 21:15 |  |  |  | 2022-10-08 16:00 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE TEE CAP | 1987 | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 92151 | 92151 | 219513 | 219513 | 0 | 0 | 0 | 0 |  | 7.3 | 291 | 291 | 0 | 0 | 311955 | 137662.5145778119511889663250366032210835 | 311955 | 10 | 0 | 8 | 0 | 0 | 8 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1987-08-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA NOT IN PLACE THEREFORE GAS CONTROL INVOLVEMENT IS NOT A FACTOR. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | [145 empty] | FUSION JOINT | [18 empty] | SADDLE, HEAT FUSION |  | 1987 | 1" | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [6 empty] | YES | [9 empty] | YES |  |  |  | OTHER | CRACK ON PLASTIC TEE CAP | NO | [86 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510-298-7063 |  | SUSIE RICHMOND | gsr8@pge.com | 925-786-0267 | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | 06/01 UPDATE - THE REVISION TO THIS REPORT PROVIDES UPDATED COSTS ASSOCIATED WITH THE EVENT. PG&E WILL CONTINUE TO DOCUMENT COSTS ASSOCIATED WITH THIS INCIDENT AND WILL PROVIDE A FINAL REPORT ONCE ALL INFORMATION IS CONFIRMED. ON SATURDAY, OCTOBER 8, 2022, AT APPROXIMATELY 15:48 HOURS, PG&E WAS NOTIFIED OF AN EXPLOSION AT 2793 RIVER PLAZA DR., SACRAMENTO, CA. A PG&E GAS SERVICE REPRESENTATIVE RESPONDED TO SHUT OFF THE GAS TO THE METER. DURING A SUBSEQUENT LEAK SURVEY, A LEAK AT A SERVICE TEE NEAR THE BUILDING WAS LOCATED. THE FIRE DEPARTMENT, POLICE, AND MEDIA WERE REPORTED ON SITE. NO FATALITIES OR INJURIES WERE REPORTED. THIS INCIDENT WAS REPORTED ONCE ESTIMATED DAMAGE WAS CONFIRMED TO BE AT LEAST $129,300K. THIS INCIDENT HAS BEEN REPORTED TO CPUC AND DOT (1349399/1349521). THE CRACK WAS DISCOVERED WHEN THE TEE WAS EXPOSED BY EXCAVATION DURING THE LEAK INVESTIGATION FOLLOWING THE INCIDENT. PG&E WILL CONTINUE ITS INVESTIGATION AND WILL PROVIDE A SUPPLEMENTAL/AMENDED REPORT ONCE ALL INFORMATION IS CONFIRMED.
2023-06-30 12:35 | NO | YES | NO | 20220072 | 37520 | 2022-11-08 08:36 | SUPPLEMENTAL FINAL | 2188 | CENTRAL FLORIDA GAS CORP | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2022-10-11 15:35 | EASTERN | NO | 2022 | ADAMS ST AT BRIDGERS AVE | AUBURNDALE | POLK | FL | 33823 | 28.0627 | -81.7804 | [5 empty] | YES |  |  |  | 2022-11-01 16:25 | 1351443 | 1351654 | NATURAL GAS |  | 2187.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-10-11 15:35 |  |  |  | 2022-10-11 16:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2015 | 2015 |  |  |  |  | 6 | D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 200000 | 200000 | 47000 | 47000 | 1500 | 1500 | 0 | 0 |  | 5 | 10938 | 10938 | 0 | 0 | 259438 | 115954.4659336383654443631039531478770132 | 259438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 50 | 60 | 192.619(A)(2) | 2015-10-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 263201452 |  | CONTRACT LOCATOR | YES | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [169 empty] | YES | MICHAEL MCCARTY |  | mmccarty@fpuc.com | 863 224-0417 |  | GEORGE FREEMAN | gfreeman@fpuc.com | 863 209-5030 | MICHAEL MCCARTY |  | 863 224-0417 | mmccarty@fpuc.com | ON 10/11/22 DRILLING SMART, DIRECTIONAL BORE CONTRACTOR, HIT A 6" PE GAS MAIN OPERATED BY CENTRAL FLORIDA GAS UNDER THE PAVING AT ADAMS ST AND BRIDGERS AVE IN AUBURNDALE, FLORIDA. THE 6" PE IS IN THE AREA WHERE THERE IS AN OLD ABANDONED 4" BARE STEEL GAS MAIN. THE CONTRACT LOCATOR FOR CENTRAL FLORIDA GAS WAS OFF ON HIS MARKINGS. DRILLING SMART EXPOSED THE 4" BARE STEEL AND ASSUMED IT WAS THE ACTIVE GAS MAIN AND BORED DEEPER THAN THAT LINE AND HIT THE ACTIVE 6" PE GAS MAIN. CENTRAL FLORIDA GAS RESPONDED AND USED PIPE SQUEEZERS ON BOTH SIDES OF THE INTERSECTION TO STOP THE FLOW OF GAS IN THIS DUAL FED GAS MAIN AND DID NOT LOSE SERVICE TO ANY CUSTOMERS. THE POINT OF DAMAGE WAS UNDER THE ROADWAY PAVING AND THE ACTUAL DAMAGE COULD NOT BE SEEN. ON 10/12/22, A NEW PIECE OF 6" PE WAS INSTALLED UNDER THE INTERSECTION VIA DIRECTIONAL BORE, TESTED AND TIED IN. GAS WAS RESTORED TO THAT MAIN ON 10/14/22. ON 11/1/22, THE CITY OF AUBURNDALE PRESENTED CENTRAL FLORIDA GAS WITH COSTS TO RESTORE THE ROAD BASE AND PAVING AT THAT INTERSECTION, PUSHING THE DAMAGE COST ABOVE THE PHMSA REPORTING THRESHOLD OF $122,000. A NOTICE WAS MADE TO THE NATIONAL REPORTING CENTER VIA TELEPHONE ON 11/1/22 AND A 48 HOUR FOLLOW UP ON 11/3/22. 12/28/2022 SUPPLEMENT CORRECTION MADE TO PART A (19) - INCORRECT NRC REPORT NUMBER ENTERED INITIALLY WITH A NUMBER LEFT OUT. CORRECT NRC REPORT NUMBER OF 1351443 ENTERED. PART J - EXCAVATION DAMAGE (EXCAVATION DAMAGE BY THIRD PARTY) REMOVED AS NOT NECESSARY SINCE LISTED IN G3. CHANGED CONTRIBUTING FACTOR TO INCORRECT OPERATION (FAILURE TO FOLLOW PROCEDURES) DUE TO CONTRACT LOCATOR BEING OFF ON MARKS AND NOT LISTING THE TYPE AND SIZE OF GAS MAIN IN THE POSITIVE RESPONSE FOR THE LOCATE TICKET. THE LOCATOR WAS OFF ON THE LOCATE MARKS BY A FEW FEET. THE EXCAVATOR SPOTTED A PIPE SEVERAL FEET AWAY IN A GRASSY AREA AND ASSUMED IT WAS THE GAS MAIN AND AT A CERTAIN DEPTH. THEY BORED THE ROAD AT A DEEPER DEPTH AND HIT THE LIVE PE GAS MAIN. THE PIPE THEY DUG UP AND SPOTTED FOR DEPTH WAS AN OLD RETIRED 4" BARE STEEL GAS MAIN AND NOT THE LIVE 6" PE GAS MAIN. THE CONTRACTOR LOCATOR TECHNICIANS WERE BROUGHT IN AND INSTRUCTED AGAIN TO LIST THE SIZE AND TYPE OF PIPE ON THE POSITIVE RESPONSE TO MARKED LOCATE TICKETS, PER PROCEDURES, TO ENSURE EXCAVATORS ARE SURE WHICH PIPES THEY ARE SPOTTING. NO OTHER DAMAGE INFORMATION OR COSTS REQUIRE UPDATING.
2023-06-30 12:35 | NO | YES | NO | 20220073 | 37362 | 2022-11-16 17:36 | ORIGINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-10-17 11:06 | EASTERN | YES | 2022 | 1372 BARRON LAKE ROAD | NILES | CASS COUNTY | MI | 49120 | 41.8533 | -86.177 | [5 empty] | YES |  | YES | RETIRED SERVICE LINE. | 2022-10-17 11:06 | 1350127 | 1350718 | NATURAL GAS |  | 7.04 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-10-17 07:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7.04 | NO | 1 | 2022-10-17 07:57 |  |  |  | 2022-10-17 08:15 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | 1997 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | GAS METER | [9 empty] | OTHER | [8 empty] | CAR IMPACT DISLODGED METER FROM METER BAR AND PIPING. | CLASS 3 LOCATION | 200000 | 200000 | 990 | 990 | 2240 | 2240 | 0 | 0 |  | 8.94 | 63 | 63 | 0 | 0 | 203293 | 89693.727280146713259487554904831625183 | 203293 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1962-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | SMALL TRUCK | ROADWAY | 47 | NO | [142 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | JOHN O'BRYANT | john.obryant@semcoenergy.com | 269-506-3222 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | ON 17 OCT 2022 AT APPROXIMATELY 07:57, SEMCO WAS NOTIFIED BY THE CASS CO CENTRAL DISPATCH THAT THERE WAS A STRUCTURE FIRE AT THE REFERENCED ADDRESS. UPON ARRIVING AT 8:15 AM, THE SEMCO TECHNICIAN CHECKED WITH THE HOWARD TWP. FIRE CHIEF WHOM INFORMED HIM THAT THE VEHICLE HAD STRUCK ANOTHER VEHICLE IN THE ROAD, VEERED OFF THE ROAD, TRAVELED THRU THE YARD, STRIKING THE GAS METER SET WHICH THEN IGNITED, CAUSING THE STRUCTURE FIRE. THE GAS WAS SECURED AT 8:33 AM AND THE FIRE DEPARTMENT DISTINGUISHED THE FIRE.
2023-06-30 12:35 | NO | NO | NO | 20220075 | 37413 | 2022-12-02 15:08 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-11-04 15:29 | EASTERN | YES | 2022 | N. ELM AVENUE & ROSEHILL ROAD | JACKSON | JACKSON | MI | 49201 | 42.2766 | -84.3842 | [5 empty] | YES | YES |  |  | 2022-11-04 22:02 | 1351782 | 1351886 | NATURAL GAS |  | 3444 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-11-04 15:29 | YES | OPERATOR | 2022-11-04 15:55 | 2022-11-04 15:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 2 | 9.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 36708 | 36708 | 73 | 73 | 0 | 0 |  | 5.77 | 19872 | 19872 | 0 | 0 | 56653 | 27718.9600216114803453601756954612005857 | 56653 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 53 | 53 | 60 | 192.619(A)(2) | 2022-05-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2022083000497 |  | CONTRACT LOCATOR | NO | NO | YES | 7 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON NOVEMBER 4, 2022, AT APPROXIMATELY 15:29 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE AT THE INTERSECTION OF N. ELM AVENUE AND ROSEHILL ROAD, JACKSON (JACKSON COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 15:55 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR PERFORMING ROADWAY EXCAVATION WORK DAMAGED A NATURAL GAS PIPELINE, WHICH WAS LATER DETERMINED TO BE A 6-INCH STEEL MEDIUM PRESSURE PIPELINE. POLICE AND FIRE DEPARTMENTS WERE ONSITE AND ASSISTED THE CONTRACTOR WITH ROAD CLOSURE TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. A DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 16:15 HOURS AND DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. THE DAMAGED SEGMENT WAS ISOLATED BY INSTALLING A PRESSURE CONTROL FITTING AT A REMOTE LOCATION EAST OF THE DAMAGE AND SQUEEZING THE PIPELINE AT A LOCATION WEST OF THE DAMAGE. THE BLOWING GAS WAS CONTAINED AT APPROXIMATELY 04:30 HOURS (NOVEMBER 5, 2022) AND A PERMANENT REPAIR WAS COMPLETED BY WELDING AN ENCAPSULATED FITTING AROUND THE DAMAGED SEGMENT. REPAIRS WERE COMPLETED AND NORMAL OPERATIONS RESUMED ON NOVEMBER 5, 2022, AT APPROXIMATELY 10:30 HOURS. SERVICE RESTORATION FOR ALL IMPACTED CUSTOMERS BEGAN AFTER THE PIPELINE REPAIR.
2023-06-30 12:35 | NO | YES | NO | 20220077 | 38088 | 2022-12-15 12:18 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-11-16 11:45 | PACIFIC | NO | 2022 | EAST SIDE OF GRANT ST, ACROSS THE STREET FROM RESIDENCE 2707 GRANT ST | CONCORD | CONTRA COSTA | CA | 94520 | 37.9878 | -122.0379 | [5 empty] | YES |  |  |  | 2022-11-16 12:23 | 1352705 | 1352897 | NATURAL GAS |  | 2076 | 2.37 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-16 10:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2076 | NO | 1 | 2022-11-16 10:30 |  |  |  | 2022-11-16 10:53 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 22 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1961 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 6 | [7 empty] | CLASS 3 LOCATION | 350750 | 350750 | 48695 | 48695 | 2533 | 2533 | 0 | 0 |  | 6.3 | 13079 | 13079 | 15 | 15 | 415072 | 184909.9628397043025150483162518301610542 | 415072 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 54 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | YES | X229201521 | 811 | FACILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [169 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com |  |  | SUSIE RICHMOND | gas ops compliance and risk manager |  | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | ON NOVEMBER 16, 2022, AT APPROXIMATE 11:45 HOURS PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED THAT A DIG-IN LOCATED AT THE EAST SIDE OF GRANT STREET, ACROSS THE STREET FROM THE RESIDENCE OF 2707 GRANT STREET IN CONCORD, CA REACHED DOT REPORTABLE INCIDENT CRITERIA. THIRD-PARTY CONSTRUCTION EQUIPMENT STRUCK A 4" STEEL DISTRIBUTION MAIN RESULTING IN MULTIPLE PUNCTURES RESULTING IN A RELEASE OF GAS WITH SUBSEQUENT IGNITION. PG&E PERSONNEL RESPONDED AND STOPPED GAS FLOW APPROXIMATELY AT 12:27 HOURS. THERE WERE NO FATALITIES OR INJURIES. MEDIA, FIRE AND POLICE WERE REPORTED ON SITE. THIS INCIDENT WAS REPORTED TO THE DOT #1352705/1352897 AND CPUC 221116-15335 DUE TO MEDIA COVERAGE AND ONCE IT WAS CONFIRMED THAT THE INCIDENT RESULTED IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $129,300.
2023-06-30 12:35 | NO | YES | YES | 20220078 | 38138 | 2022-12-20 17:10 | SUPPLEMENTAL FINAL | 18704 | SULLIVAN GAS DEPT, CITY OF | 304 S HAMILTON ST | SULLIVAN | IL | 61951 | 2022-11-10 13:00 | CENTRAL | YES | 2022 | 1209 S HAMILTON ST. | SULLIVAN | MOULTRIE | IL | 61951 | 39.5875 | -88.6094 |  |  | YES | [6 empty] | 2022-11-14 08:19 | 1352505 | 1352759 | NATURAL GAS |  | 1.04 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-11-10 13:00 | YES | OPERATOR | 2022-11-10 13:00 | 2022-11-10 13:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 2 | GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 200 | 200 | 35000 | 35000 | 5000 | 5000 | CITY EMPLOYEE AND CONSULTANTS TIME AND LABOR. | 3.32 | 3 | 3 | 0 | 0 | 40203 | 17736.435360941845183308931185944363104 | 40203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 37 | 40 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 60 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [221 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ANDREW J WOODWORTH | CITY OF SULLIVAN GAS DEPARTMENT FOREMAN | gasdept@sullivanil.us | 2174339303 |  |  |  |  | ANDREW J WOODWORTH |  | 2174339303 | gasdept@sullivanil.us | ON NOVEMBER 10TH 2022, I (FOREMAN) AND THE REST OF MY CREW WERE INSTALLING A SECTION OF NEW GAS MAIN INSIDE THE CITY LIMITS OF SULLIVAN IL. AFTER I COMPLETED THE WELDING AND SUCCESSFUL PRESSURE TESTING OF TWO BOLT ON VALVE FLANGE WELDS AND ONE WELD SECURING THE 2 INCH TEE TO THE PREEXISTING 37 PSI, 2 INCH GAS MAIN, ALL FOUR OF US PROCEEDED TO COMMENCE DRILLING THE MAIN TO INTRODUCE GAS TO THE NEW MAIN BY UTILIZING ONE OF OUR MUELLER E-4 MODEL DRILLING MACHINES. UPON SUCCESSFUL COMPLETION OF THE DRILLING PROCESS TECHNICIAN 1 RAISED THE SHELL CUTTER INTO THE DRILLING MACHINE CHAMBER AND THE GATE VALVE WAS CLOSED TO STOP OFF GAS FLOW FROM THE TOP OF THE TEE. THE DRILLING MACHINE WAS DISASSEMBLED FROM THE GATE VALVE AND THE SHELL CUTTER DISASSEMBLED AND THE COMPLETION PLUG INSTALLED. ONCE TECHNICIAN 1 REASSEMBLED THE MACHINE IT WAS REATTACHED TO THE TOP OF THE GATE VALVE AND THE VALVE WAS OPENED ALLOWING THE COMPLETION PLUG TO BE LOWERED INTO THE TOP OF THE TEE AND THREADED INTO IT. ONCE THE PLUG WAS THREADED INTO THE TEE AND TIGHT THE SHAFT WAS REMOVED FROM THE COMPLETION PLUG AND THE MACHINE WAS REMOVED AGAIN FROM THE GATE VALVE. THE GATE VALVE WAS THEN REMOVED AND THE COMPLETION PLUG WRENCH WAS PUT INTO THE TOP OF THE COMPLETION PLUG BY TECHNICIAN 1. TECHNICIAN 1 PERFORMED ALL THE ASSEMBLY AND DISASSEMBLY OF THE MACHINE. TECHNICIAN 1 THEN TURNED THE PLUG TIGHTENING IT INTO THE TEE A 1/4 - 1/2 TURN AND THEN HANDED THE WRENCH TO TECHNICIAN 3 AND TOLD HIM TO FINISH TIGHTENING THE PLUG. TECHNICIAN 3 THEN FITTED THE WRENCH INTO THE TOP OF THE COMPLETION PLUG. HE IS RIGHT HANDED SO HE PUT HIS LEFT HAND ON TOP OF THE WRENCH TO SECURE IT AND HIS RIGHT HAND ON THE HANDLE TO TURN IT. AS SOON AS HE STARTED TO TURN THE PLUG IT BLEW OUT THE TOP. AT THE TIME THAT IT BLEW OUT I (FOREMAN) WAS SEATED ON THE EAST EDGE OF THE BELL HOLE, TECHNICIAN 2 WAS SEATED ON THE SOUTH EDGE, TECHNICIAN 3 WAS STANDING IN THE SOUTH WEST CORNER OF THE PREEXISTING AND NEW MAINS AND TECHNICIAN 1 WAS STANDING IN THE NORTH WEST CORNER OF THE PREEXISTING AND NEW MAINS. I ROLLED AWAY FROM THE EXCAVATION. I LOOKED TO MY LEFT AND SAW THAT TECHNICIAN 2 WAS CLEAR OF THE HOLE. I LOOKED RIGHT AND SAW TECHNICIAN 3 MOVING WEST IN THE DITCH AWAY FROM IT. I LOOKED RIGHT AND SAW TECHNICIAN 1 LOOKING AROUND ALL AROUND HIM I YELLED ARE YOU OK AND HE GAVE ME A THUMBS UP AND CONTINUED LOOKING AROUND HIM. I LOOKED AT TECHNICIAN 3 AND SAW HIS FACE WAS OBVIOUS SHOCK. I SAW HIM HOLDING HIS LEFT ARM AND THEN SAW HIS ARM STARTING TO BLEED. I THEN RAN AROUND THE NORTH SIDE OF THE HOLE AND GRABBED TECHNICIAN 3 AND PULLED HIM OUT OF THE DITCH AND TOOK HIM TO GET A FIRST AID KIT. AT THIS TIME I SAW HOW BAD HIS ARM WAS BLEEDING SO I KEYED UP ON THE CITY RADIO AND STATED SULLIVAN EMS SULLIVAN EMS YOU ARE NEEDED NOW AT THE H&R BLOCK BUILDING ON SOUTH HAMILTON STREET INJURED CITY EMPLOYEE WITH SHRAPNEL WOUNDS TO HIS LEFT FOREARM AND BICEP WITH SEVERE BLEEDING. I REPEATED THIS MESSAGE TWICE ON THE RADIO. I THEN TURNED TO TECHNICIAN 3 AND BEGAN MEDICAL TRIAGE. HE SAID IT FEELS LIKE SOMETHING IS MOVING UP MY ARM! I THEN TOOK OFF MY LEATHER BELT AND TOLD HIM IM GONNA TIE OFF YOUR ARM! I USED MY BELT JUST BELOW HIS LEFT ARMPIT TO APPLY A TOURNIQUET. I WRAPPED IT TIGHT AND GAVE HIM THE LOOSE END AND TOLD HIM TO HOLD IT AND NOT LET GO UNTIL THE EMTS TOLD HIM TO. MOMENTS LATER EMTS ARRIVED AND TOOK TECHNICIAN 3 TO ST MARYS HOSPITAL BY AMBULANCE IN DECATUR IL. I TURNED BACK TO TECHNICIANS 1 AND 2 AND THEY HAD ALREADY PUT THE GATE VALVE BACK ON AND SHUT DOWN THE GAS. TECHNICIAN 1 AND I PUT A NEW COMPLETION PLUG IN THE TEE AND THEN SECURED THE AREA AND WENT TO DO DRUG SCREENINGS PER HUMAN RESOURCES.
2023-06-30 12:35 | NO | YES | NO | 20220079 | 37670 | 2022-12-21 13:21 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2022-11-30 17:00 | PACIFIC | NO | 2022 | LA CIENEGA STREET AND PYLE AVE | LAS VEGAS | CLARK | NV | 89183 | 36.0055 | -115.1614 | [5 empty] | YES |  |  |  | 2022-11-30 17:44 | 1353841 | 1354008 | NATURAL GAS |  | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 6 | 2022-10-31 19:52 | YES | OPERATOR | 2022-10-31 23:01 | 2022-10-31 18:23 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1999 | 1998 |  |  |  |  | 2 | ASTM D-2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 180432 | 180432 | 12285 | 12285 | 0 | 0 |  | 5.4087 | 2704 | 2704 | 0 | 0 | 195421 | 86583.1662093817880547833089311859443631 | 195421 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 48 | 55 | 60 | 192.619(A)(2) | 1999-01-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [145 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | MATERIAL DEGRADATION | NO | [73 empty] | YES | [12 empty] | MICHAEL ROSS | SUPERVISOR OF ENGINEERING | michael.ross@swgas.com | 7023652361 |  |  |  |  | ANTHONY HILLS | DIRECTOR OF GAS OPERATIONS | 7023652049 | anthony.hills@swgas.com | AT 17:35 ON OCTOBER 31, 2022, SOUTHWEST GAS RECEIVED A CALL ABOUT AN ODOR/HISSING ON A DIRT LOT NEAR THE INTERSECTION OF LA CIENEGA STREET AND PYLE AVENUE IN LAS VEGAS, NEVADA. CREWS ARRIVED ONSITE AT 18:23 AND BEGAN INVESTIGATION. AT 19:52, SOUTHWEST GAS IDENTIFIED A LEAK ON ITS FACILITIES AND MADE THE AREA SECURE. THE LEAK WAS ISOLATED AND GAS SUPPLY WAS SHUT OFF TO THE AFFECTED PIPE SEGMENT BY 21:24 ON OCTOBER 31, 2022. THIS SEGMENT OF THE MAIN WILL NOT BE RETURNED TO SERVICE. SOUTHWEST GAS EVACUATED A TOTAL OF SIX PERSONS FROM THREE NEARBY HOMES. AFTER GAS WAS SHUT OFF, CREWS BEGAN AERATING THE SURROUNDING SOIL TO REMOVE RESIDUAL GAS IN THE GROUND. ALTHOUGH RESIDUAL GAS READS WERE DROPPING, SOUTHWEST GAS REMAINED ONSITE CONTINUOUSLY MONITORING THE RESIDUAL READS AND AERATING THE SOILS. ON NOVEMBER 30, 2022 SOUTHWEST GAS DETERMINED THAT THE ACCUMULATED EMERGENCY RESPONSE COSTS EXCEEDED $129,300. THE INCIDENT COSTS WERE MOSTLY ATTRIBUTED TO EMPLOYEE LABOR UTILIZED TO CONTINUOUSLY AERATE AND REMEDIATE THE RESIDUAL GAS IN THE SOIL. SOUTHWEST DISCONTINUED ITS EMERGENCY RESPONSE AND DECOMMISSIONED THE INCIDENT COMMAND STRUCTURE ON DECEMBER 8, 2022 AFTER THE RESIDUAL GAS READS WERE REMEDIATED TO SAFE NON-HAZARDOUS CONDITIONS. LABORATORY ANALYSIS COMPLETED IN JANUARY 2023 CONCLUDED: FRACTOGRAPHIC AND ANALYTICAL EXAMINATION INDICATED THAT THE THROUGHWALL AXIAL FRACTURE RESPONSIBLE FOR THE LEAK PATH OCCURRED DUE TO INTERNAL THERMAL-OXIDATIVE DEGRADATION. THE FRACTURE PROGRESSED THROUGH THE WALL OF THE PIPE FROM THE INSIDE DIAMETER TO THE OUTSIDE DIAMETER BY WAY OF HOOP STRESS AND BRITTLE FRACTURE DUE TO DEGRADATION AND LOW SLOW CRACK GROWTH RESISTANCE OF THE PIPE MATERIAL. THIS SUPPLEMENTAL REPORT UPDATES THE CAUSE OF THE LEAK IN PART G BASED ON THE LABORATORY ANALYSIS TO BE A CRACK CAUSED BY DEGRADATION. IT ALSO UPDATES PART J AND THE COSTS ASSOCIATED WITH THE INCIDENT IN PART D.
2023-06-30 12:35 | NO | NO | NO | 20220080 | 37509 | 2022-12-22 13:57 | ORIGINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-11-24 18:02 | MOUNTAIN | NO | 2022 | 1621 SAN JUAN CIRCLE | EVANS | WELD | CO | 80620 | 40.3772 | -104.7056 |  |  |  | YES | [5 empty] | 2022-11-24 18:45 | 1353337 |  | NATURAL GAS |  | 5.61 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-24 18:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4.98 | NO | 4 | 2022-11-24 18:02 |  |  |  | 2022-11-24 18:23 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1995 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | STEEL NIPPLE | [9 empty] | OTHER | [8 empty] | VEHICLE HIT | CLASS 3 LOCATION | 90000 | 90000 | 2100 | 2100 | 1400 | 1400 | 0 | 0 |  | 10.97 | 62 | 62 | 0 | 0 | 93562 | 41284.4755311082473550512445095168374817 | 93562 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 18 | 18 | 20 | 192.619(A)(2) | 1995-05-25 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [142 empty] | VONNA M SEEBER | COMPLIANCE | vonna.seeber@atmosenergy.com | 8163944940 |  | KURTIS RUTZ | kurtis.rutz@atmosenergy.com | 9705390057 | DOUGLAS L SHATAS | MANAGER COMPLIANCE | 8168630951 | doug.shatas@atmosenergy.com | DRIVER LOST CONTROL OF VEHICLE ON ROADWAY BEHIND 1621 SAN JUAN CIRCLE IN EVANS, COLORADO. VEHICLE WENT OFF THE ROAD THROUGH A PRIVATE FENCE AND HIT AN ATMOS GAS METER AND A HOUSE. THE HOUSE, THE METER, AND THE VEHICLE CAUGHT FIRE. THE DRIVER FLED THE SCENE. THE EVANS FIRE DEPARTMENT RESPONDED, PULLED THE VEHICLE AWAY FROM THE HOUSE, PUT OUT THE FIRE, AND SHUT OFF THE GAS RISER VALVE TO STOP THE RELEASE OF GAS. THREE HOMES AND FOUR PEOPLE WERE EVACUATED DURING THE INITIAL INVESTIGATION. ATMOS DETERMINED THAT THERE WAS NO DAMAGE TO UNDERGROUND PIPING.
2023-06-30 12:35 | NO | YES | YES | 20220081 | 37511 | 2022-12-22 16:15 | ORIGINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-11-22 14:29 | EASTERN | NO | 2022 | 1121 BAYARD ST | BALTIMORE | BALTIMORE CITY | MD | 21223 | 39.2799 | -76.6371 | [7 empty] | YES | UNDER INVESTIGATION | 2022-11-22 16:39 | 1353220 |  | NATURAL GAS |  | 5.6 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2022-11-22 14:29 | OPERATOR/CONTRACTOR |  | 5.6 | YES | 0 | 2022-11-22 14:29 |  |  |  | 2022-11-22 14:40 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | PENDING INVESTIGATION |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | PENDING INVESTIGATION | UNKNOWN | [8 empty] | OTHER | PENDING INVESTIGATION | [9 empty] | OTHER | [8 empty] | PENDING INVESTIGATION | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COST UNDER INVESTIGATION | 0.45 | 3 | 3 | 0 | 0 | 3 | 1.73499267935578330893118594436310395315 | 3 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0.25 | 0.25 | 0.36 | 192.623 | 1904-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JEFFREY WEATHERHOLTZ | MANAGER GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 4105981601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 3025933732 | robert.rex@delmarva.com | ON 11/22/2022 AT 14:29, BGE WAS NOTIFIED BY THE BALTIMORE CITY FIRE DEPARTMENT OF A POSSIBLE EXPLOSION AT 1121 BAYARD STREET. BGE IMMEDIATELY DISPATCHED A GAS SERVICE MECHANIC TO THE INCIDENT LOCATION. THE MARYLAND PUBLIC SERVICE COMMISSION WAS NOTIFIED AND A REPORT TO THE NATIONAL RESPONSE CENTER WAS ISSUED. BGE IS CONDUCTING A JOINT INVESTIGATION WITH THE MARYLAND PUBLIC SERVICE COMMISSION AND OTHER PARTIES INVOLVED.
2023-06-30 12:35 | NO | YES | NO | 20230001 | 37527 | 2023-01-03 13:43 | ORIGINAL FINAL | 12642 | SPIRE GULF INC. | 2828 DAUPHIN STREET | MOBILE | AL | 36606 | 2022-11-16 09:06 | CENTRAL | YES | 2022 | 1363 CREOLA AXIS LOOP RD | CREOLA | MOBILE COUNTY | AL | 36505 | 30.9317 | -88.0075 | [5 empty] | YES |  |  |  | 2022-11-16 10:12 | 1352681 | 1352863 | NATURAL GAS |  | 23 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-16 09:06 | ALLOWED TO BURN OUT |  | 23 | NO | 0 | 2022-11-16 09:06 | YES | OPERATOR | 2022-11-16 09:26 | 2022-11-16 09:26 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | OTHER | [8 empty] | LINE DAMAGED BY TRACKHOE TRACK. | CLASS 2 LOCATION | 0 | 0 | 10000 | 10000 | 500 | 500 | 125000 | 125000 | TRACKHOE DAMAGED BY FIRE | 6 | 138 | 138 | 0 | 0 | 135638 | 59857.2201085132345322108345534407027818 | 135638 | 1 | 0 | 62 | 0 | 0 | 62 | 1 | 40 | 40 | 60 | 192.619(A)(2) | 2022-04-11 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED TO THE SCADA AND MADE THE APPROPRIATE NOTIFICATIONS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE TRACK RAILS OF A TRACKHOE DUG INTO SOFT GROUND AND DAMAGED PIPE WHILE MOBILIZING FROM A JOB SITE. | [154 empty] | JUSTIN MONROE | MANAGER PIPELINE SAFETY DISTRIBUTION | justin.monroe@spireenergy.com | 205-572-2928 |  | JUSTIN MONROE | justin.monroe@spireenergy.com | 205-572-2928 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON NOVEMBER 16, 2022 AT 9:06 AM, A THIRD-PARTY CONTRACTOR DAMAGED A 2-INCH MEDIUM PRESSURE (60 PSIG MAOP) PLASTIC MAIN LOCATED AT 1363 CREOLA AXIS LOOP, CREOLA AL. THE CONTRACTOR WAS MOVING A TRACKHOE IN A SOFT AREA OF DIRT AND SUNK THE TRACKS INTO THE UNDERGROUND PIPELINE, CAUSING A RUPTURE. A FIRE IGNITED AND DAMAGED THE TRACKHOE. THIS REPORT WAS SUBMITTED BY PORTAL ON DECEMBER 16, 2022 BUT HAD TO BE RESUBMITTED DUE TO TECHNICAL ISSUES IN THE PORTAL.
2023-06-30 12:35 | NO | YES | NO | 20230002 | 37992 | 2023-01-12 16:41 | SUPPLEMENTAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2022-12-13 09:30 | EASTERN | NO | 2022 | 3204 CREST ROAD | HARRISBURG | DAUPHIN | PA | 17109 | 40.2923 | -76.848 |  | YES | [7 empty] | 2022-12-13 10:39 | 1354879 | 1355040 | NATURAL GAS |  | 42.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-12-13 09:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 42.1 | YES | 11 | 2022-12-13 09:07 |  |  |  | 2022-12-13 09:25 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | EXCAVATOR STRUCK SERVICE LINE | 42 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1958 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | GAS WAS RELEASED AT A TEAR ON THE INSIDE ELBOW OF A DEFORMATION IN THE SERVICE LINE WHERE IT WAS PULLED BY THE EXCAVATOR AND AT A COMPLETE SEPARATION WHEREBY THE 3/4" DIAMETER SERVICE PIPE FRACTURED BY SHEAR WHERE IT ENTERED THE BASEMENT WALL | CLASS 3 LOCATION | 500000 | 500000 | 25000 | 25000 | 11000 | 11000 | 0 | 0 |  | 9.17 | 386 | 386 | 0 | 0 | 536386 | 236685.9073015769694524158125915080527086 | 536386 | 0 | 0 | 14 | 2 | 0 | 23 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 1958-07-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 15.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FACILITY WAS HIT BY EXCAVATOR. GAS CONTROL DID NOT HAVE AN IMPACT ON THIS INCIDENT. | [12 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 20223461851 |  | FACILITY OWNER | NO | UNKNOWN/OTHER | YES | 12 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [169 empty] | ROMAN HIGH | SR ENGINEER STANDARDS | rhigh@ugi.com | 484-332-8402 |  | JOSH BARRELL | jbarrell@ugi.com |  | PAM JOCSAK | VP ENGINEERING | 484-824-5508 | pjocsak@ugi.com | ON 12/12/2022 AT 13:175, UGI RECEIVED AN EMERGENCY EXCAVATION TICKET ("TICKET") (SERIAL # 20223461851) THROUGH THE PENNSYLVANIA ONE CALL SYSTEM, ISSUED BY AN EXCAVATOR, PRONTO PLUMBING, WITH A PROPOSED DIG DATE OF 08:00 ON 12/13/22 AT 3204 CREST ROAD, HARRISBURG (THE "PROPERTY"). UGI RESPONDED THROUGH THE ONE CALL SYSTEM ON 12/12/22 AT 13:18 STATING: "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". THE UGI DISPATCHER MISTAKENLY ASSIGNED THE TICKET TO A CONTRACTOR THAT DOES NOT PERFORM EMERGENCY LOCATES. ON 12/13/2022 AT 9:06, THE FIRE DEPARTMENT WAS DISPATCHED TO THE PROPERTY DUE TO A LINE HIT. AT 9:07, UGI DISPATCH RECEIVED A CALL FROM DAUPHIN COUNTY 911, REGARDING A HIT GAS LINE AT THE PROPERTY. ALSO AT 9:07, EXCAVATOR PLACED A RE-NOTIFY TICKET THROUGH THE ONE CALL SYSTEM. UGI RESPONDED TO THE RE-NOTIFY TICKET AT 9:09 STATING: "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". UGI DISPATCHED THE CLOSEST AVAILABLE QUALIFIED FIRST RESPONDER BASED ON THE CALL RECEIVED BY DISPATCH, WHO ARRIVED AT 9:25. AT 9:30, AN EXPLOSION OCCURRED AT THE PROPERTY. THE LINE HIT RESULTED WHEN EXCAVATOR, WHO WAS WORKING FOR THE PROPERTY OWNER, BEGAN DIGGING WITH A BACKHOE NEAR THE FRONT WALL OF THE PROPERTY BETWEEN 8:45 AND 9:00 ON 12/13/22 TO REPAIR A BLOCKED SEWER SERVICE LINE. EXCAVATOR BEGAN DIGGING BEFORE UGI'S LOCATOR ARRIVED TO COMPLETE THE RE-NOTIFY TICKET AND BEFORE UGI WAS ABLE TO CONTACT EXCAVATOR TO DISCUSS THE FACILITY CONFLICTS. THE RESIDENTS AT THE PROPERTY WERE EVACUATED PRIOR TO THE EXPLOSION. THE EXPLOSION INJURED UGI'S FIRST RESPONDER AND A RESIDENT OF AN ADJACENT HOME. BOTH INDIVIDUALS WERE TREATED AT A HOSPITAL AND RELEASED THE SAME DAY. THE SITUATION WAS MADE SAFE BY CLOSING THE MAIN LINE VALVE AT THE END OF THE STREET, SHUTTING OFF GAS TO 14 CUSTOMERS. UGI CONDUCTED A SUBSURFACE LEAK SURVEY WITH NO INDICATIONS OF A LEAK. GAS SERVICE WAS PROMPTLY RESTORED TO AFFECTED CUSTOMERS ABLE TO ACCEPT GAS SERVICE. THE INCIDENT INVESTIGATION IS ONGOING, AND INFORMATION RELATED TO PARTS B, C, D, AND G OF THE REPORT ARE STILL BEING DETERMINED. A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN MORE INFORMATION IS AVAILABLE. *ON APRIL 28, 2023 UGI IS FILING THIS SUPPLEMENTAL AND FINAL REPORT AT THE REQUEST OF PHMSA. UGI IS CONFIRMING THE ROOT CAUSE OF THIS INCIDENT IDENTIFIED IN PART G REMAINS "EXCAVATION PRACTICES NOT SUFFICIENT". AS STATED IN THE NARRATIVE ABOVE, UGI RECEIVED AN EMERGENCY EXCAVATION TICKET ON 12/12/2022 AT 13:17. UGI RESPONDED TO THIS REQUEST THROUGH ITS TICKET MANAGEMENT SYSTEM THE SAME DAY AT 13:18 REMARKING "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". WHILE UGI AVERS THE FACILITIES WERE NOT MARKED BY THE TIME THE EXCAVATOR BEGAN DIGGING, THE EXCAVATOR WAS MADE AWARE THE DAY PRIOR OF FACILITY CONFLICTS. IN UGI'S VIEW, THE EXCAVATOR BEGAN EXCAVATION THROUGH THE USE OF MECHANICAL EXCAVATION EQUIPMENT (BACKHOE) WITHOUT EXERCISING DUE CARE, AS REQUIRED IN PENNSYLVANIA THROUGH THE 2017 UNDERGROUND UTILITY LINE PROTECTION LAW (ACT 50). THE EXCAVATOR DID NOT HAVE SUFFICIENT INFORMATION TO SAFELY USE MECHANICAL EXCAVATION EQUIPMENT TO EXCAVATE AT THIS LOCATION AND OTHERWISE DID NOT EMPLOY PRUDENT EXCAVATION TECHNIQUES SUCH AS HAND DUG TEST HOLES, VACUUM EXCAVATIONS, OR SIMILAR DEVICES. AS A RESULT, UGI'S SERVICE LINE WAS STRUCK, PUNCTURED, AND TORN FROM THE RISER AT THE WALL OF THE RESIDENCE DUE TO THE EXCAVATOR'S ACTIONS. INFORMATION RELATED TO PART C IS STILL BEING DETERMINED. A SUPPLEMENTAL AND FINAL REPORT WILL BE FILED WHEN THE INFORMATION IS AVAILABLE.
2023-06-30 12:35 | YES | NO | NO | 20230003 | 37594 | 2023-01-19 14:28 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-12-20 08:48 | EASTERN | NO | 2022 | 1014 THIRD STREET | BANGOR | VAN BUREN | MI | 49013 | 42.319 | -86.1167 | [5 empty] | YES |  |  |  | 2022-12-20 13:35 | 1355473 | 1355602 | NATURAL GAS |  | 6.6 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2022-12-20 08:48 | ALLOWED TO BURN OUT |  | 6.6 | NO | 0 | 2022-12-20 08:48 |  |  |  | 2022-12-20 09:25 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1974 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 0.09 |  |  | 2708 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 143500 | 143500 | 2147 | 2147 | 548 | 548 | 0 | 0 |  | 6.17 | 41 | 41 | 0 | 0 | 146236 | 64519.346400899818536888726207906295754 | 146236 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 48 | 48 | 60 | 192.619(A)(2) | 1974-07-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [111 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON TUESDAY, DECEMBER 20, 2022, AT APPROXIMATELY 08:48 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION FROM EMERGENCY PERSONNEL OF A HOUSE FIRE AT 1014 3RD STREET, BANGOR, (VAN BUREN COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED AT THE SITE AT APPROXIMATELY 09:25 HOURS AND CONFIRMED THE STRUCTURE FIRE WITH A RELEASE AT THE NATURAL GAS EQUIPMENT (METER/RISER). THE GSW ADVISED A DISTRIBUTION CREW WOULD BE NEEDED TO CONTAIN THE BLOWING GAS. THE GSW BEGAN EXCAVATING AT A REMOTE LOCATION NEAR THE PIPELINE IN PREPARATION FOR SQUEEZING THE 5/8-INCH PLASTIC PIPELINE, THE PLASTIC PIPELINE (SERVICE) WAS INSERTED IN A STEEL PIPELINE MAKING IT NECESSARY FOR ADDITIONAL EQUIPMENT UTILIZED BY GAS DISTRIBUTION. DISTRIBUTION ARRIVED ONSITE AT APPROXIMATELY 10:45 HOURS AND SQUEEZED THE PIPELINE STOPPING GAS FROM BLOWING AT APPROXIMATELY 10:48 HOURS. EMERGENCY RESPONDERS WERE ONSITE AND CONFIRMED ONE FATALITY AND MULTIPLE PERSONS REQUIRING MEDICAL ATTENTION WERE TRANSPORTED TO THE LOCAL HOSPITAL. FURTHER INVESTIGATION PERFORMED BY THE MICHIGAN STATE POLICE CONFIRMED THE RELEASE AT THE NATURAL GAS EQUIPMENT (METER/RISER) WAS NOT THE PRIMARY CAUSE OF THE FIRE. THE NATURAL GAS EQUIPMENT WAS COMPROMISED BY THE STRUCTURE FIRE RESULTING IN A RELEASE AT THE NATURAL GAS EQUIPMENT. THIS REPORT IS BEING SUBMITTED BECAUSE IT CANNOT BE DETERMINED IF THE SECONDARY RELEASE AT THE NATURAL GAS FACILITIES CONTRIBUTED TO THE FATALITY.
2023-06-30 12:35 | NO | YES | NO | 20230004 | 37605 | 2023-01-20 15:54 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 220 OPERATION WAY MAIL CODE J48 | CAYCE | SC | 29033 | 2022-12-15 16:08 | EASTERN | NO | 2022 | ROSEWOOD DRIVE / BELTLINE BLVD | COLUMBIA | RICHLAND | SC | 29205 | 33.9879 | -80.9832 |  |  |  | YES | [5 empty] | 2022-12-15 17:32 | 1355104 | 1355199 | NATURAL GAS |  | 1613 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-12-15 16:08 |  |  |  | 2022-12-15 16:57 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1980 | UNKNOWN | [7 empty] | STEEL |  | FURNACE BUTT WELDED |  | 0.25 | [6 empty] | OTHER | [8 empty] | BROKEN RELIEF VALVE FROM VEHICLE IMPACT | CLASS 3 LOCATION | 0 | 0 | 135265 | 135265 | 0 | 0 | 0 | 0 |  | 8.36 | 13485 | 13485 | 0 | 0 | 148750 | 67472.5295393018984286456808199121522694 | 148750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 145 | 175 | 192.621 M | 1980-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS IMPACT BY A MOTOR VEHICLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  | YES |  |  |  | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 35 | YES |  | YES | [140 empty] | JOHNNIE WALLER | ENGINEER III - COMPLIANCE | johnnie.waller@dominionenergy.com | 803-491-4644 |  | ASHLEY MCJUNKIN | ashley.mcjunkin@dominionenergy.com | 803-457-0541 | CYNTHIA OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-530-4135 | cynthia.ostrander@dominionenergy.com | AN INCIDENT WAS REPORTED AT THE INTERSECTION OF ROSEWOOD DRIVE & BELTLINE BLVD. WHERE A VEHICLE CRASHED INTO ONE OF DOMINION ENERGY REGULATING STATIONS. OPERATOR RESOURCES WERE DISPATCHED TO THE SCENE AND REPAIR PLAN WAS INITIATED. THE LEAK WAS STOPPED AND FINAL REPAIRS WERE COMPLETED APPROXIMATELY 50 MINUTES FROM INITIAL REPORT. AT THIS TIME, THERE WAS NO LOSS OF CUSTOMERS AND NO ONE WAS INJURED RELATED TO RELEASE OF GAS. THE OFFICE OF REGULATORY STAFF FOR SOUTH CAROLINA WAS NOTIFIED AROUND 4:30 P.M. THE PRELIMINARY COST ESTIMATE WAS STATED TO EXCEED THE $129K THRESHOLD, THEREFORE TRIGGERING AN INITIAL 1-HR NOTIFICATION AND 48-HR TO THE NRC. THIS CALL WAS MADE AT APPROXIMATELY 5:32 P.M. (NRC REPORT # 1355104 AND 1355199). THE COST ESTIMATE WAS APPROXIMATELY $35,000 ON 12/22/2022, BUT SUBSEQUENTLY, ADDITIONAL COST WERE COLLECTED AFTER THE INITIAL ESTIMATE WHICH PUT THE FINAL COST OVER THE FEDERAL THRESHOLD. THE DATE OF DETERMINING COST THRESHOLD BEING EXCEEDED WAS 12/22/2022, WHICH WAS THE DATE USED FOR DETERMINING THE SUBMITTAL TIMEFRAME FOR THIS REPORT. RECORDED ON OUR LDF REPORT # 548785
2023-06-30 12:35 | NO | YES | NO | 20230005 | 37961 | 2023-01-27 12:12 | SUPPLEMENTAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2022-12-29 15:09 | EASTERN | NO | 2022 | 1210 ROBBINS AVENUE | NILES | TRUMBULL | OH | 44446 | 41.1828 | -80.7425 |  |  |  | YES |  |  |  | YES | CUT AT MAIN | 2022-12-29 16:07 | 1356293 | 1356377, 1356388 (corrected 48 hour update) | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-12-29 15:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-12-29 15:49 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-12-29 15:53 | 2022-12-29 16:23 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNDER INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDER INVESTIGATION | CLASS 3 LOCATION | 176100 | 176100 | 200 | 200 | 5000 | 5000 | 5000 | 5000 | UPDATE ESTIMATED COST DUE TO JOINT SITE EXAMINATION WITH HOMEOWNER'S INSURANCE. | 6.89 | 0 | 0 | 0 | 0 | 186300 | 82188.4248409776561 | 186300 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.48 | 0.47 | 1 | 192.623 | 1926-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10.8 |  | NO |  |  |  |  | OTHER | PUBLIC UTILITIES COMMISSION STAFF MEMBER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | ALLISON S WALTERS-THOMPSON | a.walters-thompson@dominionenergy.com | 12167899152 | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 12167899152 | a.walters-thompson@dominionenergy.com | THE FIRE/EXPLOSION THAT OCCURRED ON DECEMBER 29, 2022 IS STILL CURRENTLY UNDER INVESTIGATION AS TO ITS CAUSE, SO RESPONSES TO CERTAIN SECTIONS OF THIS FORM ARE UNKNOWN OR LEFT BLANK. ALTHOUGH SECTION A21 IS CHECKED, YES, THE SOURCE OF IGNITION IS NOT YET DETERMINED. A JOINT SITE EXAMINATION TOOK PLACE ON FEBRUARY 8, 2022, AND PHYSICAL EVIDENCE FROM INSIDE THE SUBJECT PROPERTY IS BEING PRESERVED BY THE HOMEOWNER'S INSURANCE COMPANY FOR POTENTIAL LABORATORY EXAMINATION. AS OF THIS SUPPLEMENTAL REPORT, NO LABORATORY TESTING HAS BEEN CONDUCTED OR SCHEDULED FOR THE NON-JURISDICTIONAL PIPING. THE INVESTIGATION REMAINS ONGOING, AND THE APPARENT CAUSE AND CONTRIBUTING CAUSES (IF ANY) OF THIS INCIDENT ARE YET TO BE DETERMINED.
2023-06-30 12:35 | NO | NO | NO | 20230006 | 37843 | 2023-02-01 18:30 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2023-01-05 06:22 | PACIFIC | NO | 2023 | 2761 ROLLINGWOOD DRIVE | SAN PABLO | CONTRA COSTA | CA | 94806 | 37.9655 | -122.3345 | [5 empty] | YES |  |  |  | 2023-01-06 10:32 | 1356987 | 1357066 | NATURAL GAS |  | 5358 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 3 | 2023-01-05 06:22 |  |  |  | 2023-01-05 06:44 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1943 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 3 LOCATION | 0 | 0 | 13571 | 13303.766655726946816 | 596 | 584.263866097801216 | 0 | 0 |  | 6 | 32148 | 32148 | 0 | 0 | 46315 | 24719.0487164005934535065885797950219619 | 46036.030521824748032 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 54 | 54 | 60 | 192.619(A)(3) | 1966-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPE RUPTURED AS A RESULT OF NATURAL FORCE DAMAGE, EARTH MOVEMENT DUE TO HEAVY RAIN. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | HEAVY RAIN (BOMB CYCLONE + ATMOSPHERIC RIVER) | [212 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510/298-7063 |  |  |  |  | SUSIE RICHMOND | GAS REGULATORY COMPLIANCE MANAGER | 925/786-0267 | gsr8 | ON JANUARY 6, 2023, AT 09:50, PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED EXTENT OF CONDITION OF AN UNINTENTIONAL RELEASE OF GAS DUE TO A COMPLETELY SEVERED PIPE. ON JANUARY 5, AT APPROXIMATELY 06:22, A 4" STEEL MAIN NEAR OUR FACILITIES IN SAN PABLO BROKE AS A RESULT OF NATURAL FORCE DAMAGE, EARTH MOVEMENT DUE TO HEAVY RAIN, RESULTING IN A GAS LEAK. PG&E CREWS CONDUCTED REPAIRS. THIS SECTION OF MAIN CROSSES THE HAYWARD FAULT LINE, AND GEOSCIENCES EXAMINED THE AREA. AFTER THEIR INSPECTION IT WAS DETERMINED THAT CREEP HAS LOADED THE PIPE SINCE IT WAS INSTALLED. BASED ON A NEARBY USGS MONITORING STATION, THE AREA WHERE THE FAILURE OCCURRED CREEPS AT A RATE OF ABOUT 5 MM/YEAR. THE PIPE RUPTURED AT A PARTIAL PENETRATION GIRTH WELD. THE ORIENTATION OF THE PIPE RELATIVE TO THE FAULT AND THE SENSE OF MOVEMENT ON THE FAULT CAUSES THE PIPE TO BE LOADED IN EXTENSION, WHICH IS CONSISTENT WITH THE SEPARATION OF THE PIPE THAT WAS OBSERVED AT THE BREAK. GIVEN THAT NO OTHER BREAKS OCCURRED WHERE DISTRIBUTION MAINS IN THE AREA INTERSECT THE HAYWARD FAULT, PG&E CONCLUDES THAT THE BREAK WAS DUE TO A COMBINATION OF HEAVY RAIN FALL AND LONG-TERM CREEP LOADING. A DETAILED ASSESSMENT OF HISTORICAL LEAKS IN THE AREA DID NOT SHOW A CORRELATION BETWEEN LEAKS IN THE AREA AND THE HAYWARD FAULT. NO MEDIA WAS REPORTED ONSITE. THE FIRE DEPARTMENT AND POLICE WERE ONSITE. NO FATALITIES OR INJURIES WERE REPORTED. THREE HOMES WERE EVACUATED, AND GAS SERVICE WAS INTERRUPTED FOR EIGHT CUSTOMERS AS PART OF THE ISOLATION STRATEGY. THIS INCIDENT WAS REPORTED TO DOT (NRC #1356987/ 1357066) AND CPUC ONCE IT WAS CONFIRMED THAT THE UNINTENDED GAS LOSS WAS OVER 3 MILLION CUBIC FEET.
2023-06-30 12:35 | NO | YES | YES | 20230007 | 37691 | 2023-02-10 11:11 | ORIGINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2023-01-18 12:26 | CENTRAL | NO | 2023 | 4616 CORTEZ CIRCLE | MANDAN | MORTON | ND | 58554 | 46.8667 | -100.9446 | [5 empty] | YES |  |  |  | 2023-01-18 13:04 | 1357989 | 1358143 | NATURAL GAS |  | 8.21 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-01-18 11:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.21 | YES | 2 | 2023-01-18 11:57 |  |  |  | 2023-01-18 12:26 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2017 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | BROKEN STEEL FITTING BETWEEN THE VALVE AND THE REGULATOR. CAUSE STILL UNDETERMINED AND UNDER INVESTIGATION. | CLASS 3 LOCATION | 53100 | 52054.3813587134976 | 270 | 264.68329504430592 | 1100 | 1078.3393501805056 | 0 | 0 |  | 6.74 | 55 | 55 | 0 | 0 | 54525 | 23588.6977626265938439970717423133235725 | 53452.40400393830912 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1983-09-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 15 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | SAMANTHA CALDWELL | MANAGER POLICY AND PROCEDURE | samantha.caldwell@mdu.com | 208-509-2140 |  | SAMANTHA CALDWELL | samantha.caldwell@mdu.com | 208-509-2140 | JOSH SANDERS | DIRECTOR POLICY AND PROCEDURE | 701-222-7773 | josh.sanders@mdu.com | ON JANUARY 18, 2023, MDU RESPONDED TO A STRUCTURE FIRE/EXPLOSION AT 4616 CORTEZ CIRCLE IN MANDAN, ND. AN UNINTENTIONAL RELEASE AND IGNITION OF NATURAL GAS OCCURRED. MDU PERSONNEL SECURED THE RELEASE BY SQUEEZING OFF THE SERVICE LINE. THE CAUSE OF THE FIRE/EXPLOSION AND RELEASE OF NATURAL GAS IS STILL UNDETERMINED AND UNDER INVESTIGATION.
2023-06-30 12:35 | NO | YES | NO | 20230008 | 37951 | 2023-02-10 19:46 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-01-10 15:49 | CENTRAL | NO | 2023 | 1520 BIG TIMBER RD | ELGIN | KANE | IL | 60123 | 42.0585 | -88.3153 | YES | [5 empty] | YES |  |  | 2023-01-11 11:45 | 1357409 | 1357625 1357628 | NATURAL GAS |  | 1830 | 21 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 50 | 2023-01-10 15:49 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-01-10 16:03 | 2023-01-10 16:15 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 114 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 353550 | 346588.0702330161408 | 284225 | 278628.1834591401856 | 0 | 0 |  | 6.59 | 12060 | 12060 | 138 | 138 | 649973 | 282875.9460202794648091142020497803806735 | 637414.2536921563264 | 12 | 0 | 0 | 0 | 0 | 0 | 6 | 160 | 160.6 | 165 | 192.621 M | 1979-06-30 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS MAIN AT INCIDENT LOCATION IS NOT MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A22299449 | JULIE OTHER JULIE DIG #S - A223211418 A223402053 | CONTRACT LOCATOR | YES | YES | YES | 41 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | JOSE L DELREAL | MANAGER OPS QA | jdelrea@southernco.com | 630-918-4934 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | 630-514-2036 | lquezad@southernco.com | THIRD PARTY CONTRACTOR, VERITA TELECOMMUNICATIONS CORP, WAS DIRECTIONAL DRILLING ALONG THE EAST SIDE OF MCLEAN BLVD, AT/NEAR THE INTERSECTION OF BIG TIMBER RD. THE VERITA HDD CREW WAS DRILLING ACROSS BIG TIMBER RD. A VERITA CREW-PERSON CALLED A NICOR GAS EMPLOYEE AT 15:49 ON JANUARY 10, 2023, INDICATING THEY SMELLED GAS. COMPANY EMERGENCY RESPONDERS WERE DISPATCHED IN RESPONSE TO THE NOTIFICATION. UPON EVALUATION, IT WAS DETERMINED THAT A 12-INCH MAIN HAD BEEN DAMAGED AND THE SYSTEM COULD BE ISOLATED USING TWO EXISTING VALVES (EAST & WEST OF THE DAMAGE) AND A LINE STOP FITTING (NORTH OF THE DAMAGE). THE RELEASE WAS SECURED AT APPROXIMATELY 22:42 ON JANUARY 11, 2023. NICOR INSTALLED A 250-FOOT LONG, 4-INCH BYPASS TO MINIMIZE THE RISK OF ADDITIONAL GAS SERVICE INTERRUPTION TO CUSTOMERS THAT WERE NOT ALREADY IMPACTED BY THE INCIDENT. THE BYPASS WAS IN SERVICE AT APPROXIMATELY 03:00 (24-HOUR TIME) ON JANUARY 12, 2023. THE DAMAGED SECTION OF MAIN WAS EXPOSED AND EXAMINED, AND A CLAMP WAS INSTALLED TO REPAIR THE DAMAGED SECTION. THE SYSTEM WAS RETURNED TO SERVICE IN SECTIONS, WITH THE LAST SECTION RETURNING TO NORMAL OPERATION BY 21:46 ON JANUARY 12, 2023. AT THE TIME OF THE INCIDENT, THERE WAS A VALID ONE-CALL TICKET AND MARKINGS WERE ACCURATE. THE CONTRACTOR INDICATED THEY POTHOLED DOWN TO 4.5 FEET AND OBSERVED THE TOP OF WHAT THEY THOUGHT WAS A GAS MAIN. THERE WAS NO EVIDENCE THAT THE CONTRACTOR HAD EXPOSED THE 12-INCH GAS MAIN TO OBSERVE THE DRILLING EQUIPMENT PASS THE GAS MAIN DURING THEIR OPERATION. THE DAMAGE TO THE 12-INCH MAIN OCCURRED AT A DEPTH OF 9.5 FEET.
2023-06-30 12:35 | NO | YES | NO | 20230009 | 37866 | 2023-02-14 09:13 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2023-01-14 13:02 | EASTERN | NO | 2023 | 1906 PROMENADE WAY | JACKSONVILLE | DUVAL | FL | 32207 | 30.3014 | -81.6437 | [6 empty] | YES |  |  | 2023-01-14 13:02 | 1357662 | 1357780 | NATURAL GAS |  | 9.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-01-12 08:44 | YES | OPERATOR | 2023-01-13 08:16 | 2023-01-12 09:15 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 72103 | 70683.183787331813888 | 165852 | 162586.125369215649792 | 65078 | 63796.516573679039488 | 0 | 0 |  | 10 | 93 | 93 | 0 | 0 | 303126 | 131107.8496729614837675768667642752562225 | 297158.825730226503168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 220 | 250 | 192.619(A)(4) | 1999-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR HAIR-LINE CRACK WAS IDENTIFIED WITH NO IMPACT TO ALARMS WITHIN THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2022-09-27 | YES | 1999 | 250 | [10 empty] | YES | YES | CITY STREET | [9 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  | UNKNOWN/OTHER |  |  | NO |  | PREVIOUS DAMAGE | [147 empty] | YES | [25 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | 407-420-6667 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR OF SAFETY | 813-228-1784 | kjkelley@tecoenergy.com | PEOPLES GAS RECEIVED A LEAK REPORT ON 1/12/23, RESPONDED TO THE SCENE AND BEGAN AN INVESTIGATION. A DETERMINATION OF THE SOURCE AND LOCATION WAS IDENTIFIED, AND THE SCENE WAS MADE SAFE WITH FIRST RESPONDER SUPPORT. BASED ON THE LOCATION OF THE IDENTIFIED LEAK, DEPTH OF PIPELINE AND POTENTIAL CUSTOMER LOSS, THE CORRECTIVE ACTION PLAN TO MAKE THE SCENE SAFE WAS TO INSTALL A TEMPORARY BY-PASS TO REMEDIATE THE IDENTIFIED LEAK. THE DAMAGED PIPE WAS ISOLATED, AND THE LEAKAGE STOPPED. A NEW PRETESTED SECTION OF PIPE WAS INSTALLED FOR PERMANENT REPAIR, AND THE TEMPORARY BYPASS WAS CAPPED AND TAKEN OUT OF SERVICE. DURING THE ASSESSMENT, A PREVIOUS UNREPORTED LONGITUDINAL GOUGE (EXCAVATION DAMAGE) WAS IDENTIFIED ON THE 8" PIPELINE, THAT OVER TIME RESULTED IN A LEAK. LEAK SURVEY PERFORMED ON 9/27/2022 DID NOT IDENTIFY A LEAK AT THIS LOCATION. PART G, #9 IS "NO" DUE TO LIMITATIONS OF THE FORM, IN FACT IS UNKNOWN WHETHER A LOCATE TICKET WAS CALLED OR NOT AT THE TIME OF THE EXCAVATION/DAMAGE.
2023-06-30 12:35 | NO | YES | NO | 20230010 | 37778 | 2023-03-03 13:29 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-02-03 17:05 | CENTRAL | NO | 2023 | 136 E. LAKE ST | BLOOMINGDALE | DUPAGE | IL | 60108 | 41.9572 | -88.0754 | [5 empty] | YES |  |  |  | 2023-02-03 19:03 | 1359221 | 1359323 | NATURAL GAS |  | 201.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-02-03 17:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 201.4 | NO | 0 | 2023-02-03 17:17 |  |  |  | 2023-02-03 17:48 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1993 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | PE RISER- STEEL-ALUMINUM REGULATOR/METER | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 1255000 | 1230287.16770594048 | 200 | 196.0617000328192 | 2207 | 2163.540859862159872 | 0 | 0 |  | 6.12 | 1233 | 1233 | 0 | 0 | 1258640 | 544509.6275278082322549707174231332357247 | 1233879.770265835459072 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 54.8 | 58 | 60 | 192.619(A)(2) | 1993-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | DRIVEWAY | 25 | YES | YES | [141 empty] | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | lquezad@southernco.com | 6305142036 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | A BANK DRIVE-THRU CUSTOMER LOST CONTROL OF HER VEHICLE, CRASHING THROUGH THE BUILDING BRICK WALL. THE COLLISION DAMAGED THE METER SET LOCATED IN FRONT OF THE WALL, CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. THE NATURAL GAS IGNITED, AND THE FIRE SPREAD INTO THE BANK BUILDING. THE DRIVER OF THE VEHICLE WAS NOT INJURED AND EXITED THE VEHICLE PRIOR TO THE GAS IGNITION.
2023-06-30 12:35 | NO | YES | YES | 20230011 | 37940 | 2023-03-10 14:23 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2023-02-10 04:58 | MOUNTAIN | NO | 2023 | 1414 DEGEEST DRIVE | RAPID CITY | PENNINGTON | SD | 57703 | 44.0725 | -103.1423 | [5 empty] | YES |  |  |  | 2023-02-10 06:00 | 1359693 | 1359810 | NATURAL GAS |  | 22 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2023-02-10 04:24 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 22 | NO | 8 | 2023-02-10 04:58 |  |  |  | 2023-02-10 04:58 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2000 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ANODELESS SERVICE RISER | [9 empty] | OTHER | [8 empty] | VEHICLE STRUCK METER SET, SHEARING OFF RISER AT GROUND LEVEL. | CLASS 3 LOCATION | 750000 | 735231.375123072 | 500 | 490.154250082048 | 2000 | 1960.617000328192 | 0 | 0 |  | 6.284 | 138 | 138 | 0 | 0 | 752638 | 325516.9199356492285322108345534407027818 | 737820.14637348224 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 50 | 50 | 55 | 192.619(A)(2) | 2000-11-06 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 9 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | YES | 80 | SMALL TRUCK | ROADWAY | 62 | NO | [118 empty] | YES | [23 empty] | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | danny.hood@mdu.com | 7015162749 |  | TOBY BORDEWYK | toby.bordewyk@mdu.com | 6053554054 | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | 7015162749 | danny.hood@mdu.com | ON FEBRUARY 10, 2023, AT 04:24 AM, MONTANA DAKOTA UTILITIES (MDU) RECEIVED A CALL REPORTING A HOUSE FIRE AT 1414 DEGEEST DRIVE IN RAPID CITY SOUTH DAKOTA. UPON ARRIVAL THE MDU SERVICE TECHNICIAN DETERMINED A VEHICLE TRAVELING IN A RESIDENTIAL SUBDIVISION LEFT THE ROADWAY AND STRUCK AN OUTSIDE METER SET ON THE HOUSE, SHEARING OFF THE RISER AT GROUND LEVEL, CAUSING A RELEASE OF NATURAL GAS THAT IGNITED. THE DRIVER OF THE VEHICLE DID NOT SURVIVE, AND 4 RESIDENTS OF THE HOUSE WERE TRANSPORTED TO THE HOSPITAL. THE FOUR RESIDENTS OF 1414 DEGEEST DR WERE EVACUATED, OCCUPANTS AT 1426 DEGEEST DR AND 1392 DEGEEST DR WERE ALSO EVACUATED. NUMBER OF PEOPLE EVACUATED IN PART A IS AN ESTIMATE AS NUMBER OF OCCUPANTS FROM 1426 DEGEEST AND 1392 DEGEEST IS UNKNOWN AT THE TIME OF THIS REPORT. GAS SERVICE TO 1414 DEGEEST DR AND 1426 DEGEEST DR WAS LOST DURING THE INCIDENT. GAS SERVICE TO 1426 DEGEEST DR WAS RESTORED AT APPROXIMATELY 10:00 AM. GAS SERVICE TO 1414 DEGEEST DR HAS BEEN RETIRED. THE HOME AT 1414 DEGEEST WAS A TOTAL LOSS. THE HOUSE AT 1426 DEGEEST SUSTAINED DAMAGE, A CAMPER AT THIS LOCATION WAS A TOTAL LOSS. THREE 3 VEHICLES SUSTAINED DAMAGE. UPDATE: APRIL 12, 2023- THE POLICE REPORT INDICATED THE SPEED OF THE VEHICLE WAS ESTIMATED AT 80 MPH USING INFORMATION FROM A WITNESS. POLICE REPORT INDICATES THE INJURIES TO THE DRIVER OF THE VEHICLE AND THE RESULTING FIRE PROVED TO BE FATAL. NO INDICATION OF THE CAUSE OF THE FATALITY IN THE POLICE OR FIRE REPORT. THE FIRE REPORT INDICATES ACCESS TO THE VEHICLE AFTER THE GAS LINE WAS CLAMPED AND THE FIRE WAS CONTROLLED ALLOWING RECOVERY OF THE VICTIM. THE NUMBER OF REPORTED INJURIES VARIES FROM 2 TO 5 INDIVIDUALS ON THE POLICE, FIRE, AND COMPANY FIRST RESPONDER REPORTS. NO INFORMATION IN THE REPORTS COULD CONFIRM IF THE INJURIES REQUIRED HOSPITALIZATION. THE HOUSES AT 1414 DEGEEST DR, 1426 DEGEEST AND 1392 DEGEEST DR. WERE EVACUATED BY UNKNOWN PERSONS. THE NUMBER OF RESIDENTS EVACUATED IS AN ESTIMATE AS NO SPECIFIC INFORMATION ON THE NUMBER OF EVACUATIONS IS INCLUDED IN THE POLICE OR FIRE REPORTS. THE POLICE REPORT INDICATES TOTAL LOSS OR DAMAGE TO 1 CAMPER TRAILER, 1 UTILITY TRAILER, AND 6 VEHICLES. ESTIMATED VALUE OF TRAILERS AND VEHICLES - $100,000. UPDATED THE ESTIMATED PROPERTY DAMAGE INFORMATION, USING INFORMATION FROM POLICE AND FIRE REPORTS. 1414 DEGEEST DR. - $500,000 INCLUDING POSSESSIONS, 1426 DEGEEST DR. - $100,000 AND 1392 DEGEEST DR. - $50,000 TOTAL ESTIMATED LOSS TO NON-OPERATOR - $750,000
2023-06-30 12:35 | NO | YES | NO | 20230012 | 37877 | 2023-03-22 16:09 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-02-20 16:00 | CENTRAL | NO | 2023 | 2101 TEXAS AVE | COLLEGE STATION | BRAZOS | TX | 77840 | 30.612 | -96.3147 | [5 empty] | YES |  |  |  | 2023-02-21 18:07 | 1360544 | 1360697 | NATURAL GAS |  | 1058.34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 8 | 2023-02-20 16:00 | YES | OPERATOR | 2023-02-20 16:00 | 2023-02-20 16:15 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 180 | YES | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 113589 | 111352.262225139500544 | 14330 | 14047.82080735149568 | 0 | 0 |  | 7.7224 | 8173 | 8173 | 0 | 0 | 136092 | 60048.4122883752026829648609077598828697 | 133573.083032490996224 | 1 | 0 | 10 | 0 | 0 | 17 | 1 | 34 | 34 | 50 | 192.619(A)(2) | 2004-10-14 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2354567778 | TEXAS 811 | CONTRACT LOCATOR | YES | NO | YES | 24 | LOCATING PRACTICES NOT SUFFICIENT |  |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [170 empty] | LUIS CISNEROS | COMPLIANCE SUPERVISOR | luis.cisneros@atmosenergy.com | 979-324-8823 |  |  |  |  | JEFF KNIGHTS | SR VP TECHNICAL AND OPERATING SERVICES | 214-206-2701 | jeffrey.knights@atmosenergy.com | ON FEBRUARY 20, 2023, AT 4PM, A THIRD-PARTY CONTRACTOR WAS DIRECTIONAL DRILLING AT 2101 TEXAS AVENUE / RICHARDS ST, COLLEGE STATION AND BORED INTO ATMOS ENERGY'S 2-INCH POLY MAIN AT A DEPTH OF 15 FEET. THE TECHNICIAN ARRIVED ON THE SCENE AND CONFIRMED THE LEAK AT 4:30PM. COLLEGE STATION FIRE DEPARTMENT EVACUATED 8 STRUCTURES AND GAS WAS SUBSEQUENTLY TURNED OFF TO 10 HOUSES AND 1 COMMERCIAL ENTITY ON RICHARDS ST. UPON ARRIVAL ON THE SCENE, ATMOS ENERGY'S CREW WORKED CONTINUOUSLY TO CONDUCT THE NECESSARY EXCAVATION TO LOCATE AND REPAIR THE DAMAGED LINE. ON FEBRUARY 21, 2023 AT 2:30PM, A SQUEEZE TOOL WAS INSTALLED ON THE 2-INCH POLY PIPE TO STOP GAS FLOW WHERE THE PIPE WAS DAMAGED. AT 5PM, THE 2-INCH MAIN WAS REPLACED AND GAS SERVICE WAS RESTORED TO THE 11 CUSTOMERS. REGARDING PART A QUESTION 22 - THIS NUMBER REFERS TO THE 8 STRUCTURES THAT WERE EVACUATED AND NOT PEOPLE. THE TOTAL OF PEOPLE THAT WERE EVACUATED IS NOT KNOWN.
2023-06-30 12:35 | NO | YES | NO | 20230013 | 37860 | 2023-03-23 10:39 | ORIGINAL | 32013 | AMERIGAS PROPANE LP | 460 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2023-03-01 22:30 | PACIFIC | NO | 2023 | 65 HAYS STREET | BRIDGEPORT | MONO | CA | 93517 | 38.254 | -119.2268 |  |  |  | YES | [5 empty] | 2023-03-02 13:33 | 1361287 |  | PROPANE GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-03-01 22:30 |  |  |  | 2023-03-03 08:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN LOCATION - UNDER INVESTIGATION | CLASS 3 LOCATION | 130000 | 127440.10502133248 | 300 | 294.0925500492288 | 0 | 0 | 0 | 0 | ESTIMATE NOT AWARE OF AN ACTUAL DOLLAR AMOUNT | 3 | 0 | 0 | 0 | 0 | 130300 | 56351.4358385296635 | 127734.1975713817088 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 10 | 192.619(A)(3) | 1965-07-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [231 empty] | MISCELLANEOUS | ON 3/1/2023 AROUND 22:30 LOCAL TIME SYSTEM MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS THAT AN AUTO PARTS BUILDING THAT HAD L.P GAS SERVICE WAS ON FIRE. EMERGENCY RESPONDERS THEN CLOSED THE RISER SERVICE VALVE AND SECURED/LOCKED IT AT THAT TIME. CAUSE OF FIRE IS UNCLEAR, ESTIMATED COST OF DAMAGES IS UNKNOWN. THE INCIDENT IS UNDER INVESTIGATION, THIS FORM IS SUBMITTED AS A PRECAUTIONARY MEASURE. | [47 empty] | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | bill.runyans@amerigas.com | 2564591078 |  | KYLE MUIR | kyle.muir@amerigas.com | 7067090195 | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | 2564591078 | bill.runyans@amerigas.com | ON 3/1/2023 AROUND 22:30 LOCAL TIME SYSTEM MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS THAT AN AUTO PARTS BUILDING THAT HAD L.P GAS SERVICE WAS ON FIRE. EMERGENCY RESPONDERS THEN CLOSED THE RISER SERVICE VALVE AND SECURED/LOCKED IT AT THAT TIME. CAUSE OF FIRE IS UNCLEAR, ESTIMATED COST OF DAMAGES IS UNKNOWN. THE INCIDENT IS UNDER INVESTIGATION, THIS FORM IS SUBMITTED AS A PRECAUTIONARY MEASURE.
2023-06-30 12:35 | NO | YES | NO | 20230014 | 37863 | 2023-03-23 15:41 | ORIGINAL FINAL | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2022-02-02 08:59 | EASTERN | NO | 2022 | 2592 CARMEL AVE | BREWSTER | PUTMAN | NY | 10509 | 41.3993 | -73.625 |  |  |  | YES | [5 empty] | 2022-02-03 17:45 | 1328021 | 1328415 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-02 08:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 3 | 2022-02-02 08:20 | YES | OPERATOR | 2022-02-02 08:30 | 2022-02-02 07:07 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | 2X1 MECHANICAL TAPPING TEE | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 425000 | 425000 | 100 | 100 | 5000 | 5000 | 0 | 0 |  | 37.09 | 37 | 37 | 0 | 0 | 430137 | 189765.0457154259026941434846266471449488 | 430137 | 1 | 0 | 2 | 0 | 0 | 1 | 1 | 52 | 52 | 56 | 192.619(A)(2) | 1997-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | [145 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | TAPPING TEE |  | PERFECTION | UNKNOWN | PLASTIC |  | PULLED OUT | [21 empty] | YES | TEE NOT INSTALLED IN ACCORDANCE WITH MANUFACTURER INSTRUCTIONS | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | DAN BLANCE | ENGINEER | dcblance@nyseg.com | 607-240-3821 |  |  |  |  | BARRY KACHMARYK | MANAGER GAS ENGINEERING | 585-315-1227 | barry_kachmaryk@rge.com | ON THE MORNING OF FEBRUARY 2, 2022, NYSEG COMPANY PERSONNEL INVESTIGATING A GAS ODOR COMPLAINT AT 2586 CARMEL AVE, BREWSTER NOTICED SMOKE COMING FROM THE RESIDENCE NEXT DOOR AT 2592 CARMEL AVE ("THE RESIDENCE"). NYSEG PERSONNEL IMMEDIATELY SHUT OFF THE SERVICE LINE TO THE RESIDENCE AND CALLED THE FIRE DEPARTMENT. THE FIRE CONTINUED FOR SEVERAL HOURS BEFORE IT WAS EXTINGUISHED. ALL OCCUPANTS OF THE RESIDENCE ESCAPED AND, TO NYSEG'S KNOWLEDGE, NO INJURIES WERE REPORTED AT THAT TIME. AFTER THE FIRE WAS EXTINGUISHED, NYSEG CONDUCTED A LEAK SURVEY OF THE SURROUNDING AREA AND IDENTIFIED A LEAK IN THE GAS MAIN AT A PERMALOCK TAPPING TEE APPROXIMATELY 20 FT - 30 FT FROM THE FOUNDATION OF THE RESIDENCE. THE PERMALOCK TAPPING TEE WAS MANUFACTURED BY PERFECTION CORPORATION (NOW KNOWN AS EAMCO, LLC), WHICH IS TODAY A SUBSIDIARY OF HONEYWELL INTERNATIONAL, INC. AFTER THE FIRE THE COMPANY CONDUCTED PRESSURE TESTS AND CONFIRMED THAT THERE WERE NO LEAKS IN THE SERVICE LINE TO THE RESIDENCE. FACTS LEARNED THROUGH THE INCIDENT INVESTIGATION RAISE QUESTIONS AS TO THE ACTUAL CAUSE OF THE FIRE. SPECIFICALLY, NYSEG LEARNED THAT A NEW FURNACE WAS INSTALLED IN THE RESIDENCE'S BASEMENT BY A CONTRACTOR UNAFFILIATED WITH NYSEG THE DAY BEFORE THE FIRE. ACCORDING TO INVESTIGATIVE FINDINGS SHARED WITH THE COMPANY BY A REPRESENTATIVE OF THE HOMEOWNER'S INSURER, THE TENANTS OF 2592 CARMEL AVE STARTED SMELLING GAS IMMEDIATELY AFTER THE NEW FURNACE WAS INSTALLED AND THROUGHOUT THE NIGHT BEFORE THE FIRE, HOWEVER, THEY DID NOT NOTIFY NYSEG BECAUSE THE INSTALLER HAD TOLD THEM THAT THIS WAS "NORMAL." THIS MATTER IS NOW THE SUBJECT OF MULTIPLE CIVIL LAWSUITS FOR PROPERTY DAMAGE IN WHICH THE CAUSE OF THE FIRE WILL BE THE SUBJECT OF DISCOVERY AND EXPERT TESTIMONY. THE COMPANY DID NOT HAVE ADEQUATE CAUSE TO REPORT WITHIN THE REQUIRED 30 DAYS. ALTHOUGH THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION AND CURRENTLY THE SUBJECT OF LITIGATION, THE COMPANY IS MAKING THIS FILING NOW IN AN ABUNDANCE OF CAUTION AND TO THE EXTENT IT MEETS THE CRITERIA SET FORTH UNDER 49 CFR PART 191.3(3).
2023-06-30 12:35 | NO | YES | NO | 20230015 | 37871 | 2023-03-24 17:11 | ORIGINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2023-02-23 11:22 | CENTRAL | NO | 2023 | 1034 NE 11TH ST | MADISON | LAKE | SD | 57042 | 44.0172 | -97.0979 | [5 empty] | YES |  |  |  | 2023-02-23 17:24 | 1360720 | 1360808 | NATURAL GAS |  | 50 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-02-23 11:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 50 | YES | 10 | 2023-02-23 11:22 |  |  |  | 2023-02-23 11:37 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | 2020 | SINGLE FAMILY RESIDENTIAL | YES | NO | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | METER SET WAS BURIED IN 6-8FT OF SNOW AND ICE. UNSURE WHAT CAUSE HOUSE TO EXPLODE UNTIL FURTHER TESTING OF METER SET PIPING CAN BE TESTING/COMPLETED AT A LAB. | CLASS 3 LOCATION | 400000 | 392123.4000656384 | 1000 | 980.308500164096 | 5000 | 4901.54250082048 | 0 | 0 |  | 1.07 | 54 | 54 | 0 | 0 | 406054 | 175615.9033175226740995607613469985358712 | 398059.251066622976 | 0 | 0 | 1 | 3 | 0 | 8 | 0 | 40 | 40 | 50 | 192.619(A)(2) | 1989-01-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 13 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | NO | [217 empty] | MELISSA BARUTH | DOT SUPERVISOR | melissa.baruth@northwestern.com | 6053537462 |  | MELISSA BARUTH | melissa.baruth@northwestern.com | 6053537462 | MELISSA BARUTH | DOT SUPERVISOR | 6053537462 | melissa.baruth@northwestern.com | 2/23/2023 AT ABOUT 11:22 AM 911 NOTIFIED ALL VOLUNTEER FIREMAN VIA A FIRE PAGE OF A GAS EXPLOSION THAT TOOK PLACE AT 1034 NE 11TH ST, IN MADISON SD. NORTHWESTERN TECHNICIAN IS ALSO ON THE VOLUNTEER FIRE DEPARTMENT SO HE RECEIVED THE PAGE AND RESPONDED IMMEDIATELY. WHILE IN ROUTE HE CONTACTED HIS SUPERVISOR TO MAKE HIM AWARE OF SITUATION AND TO GET ADDITIONAL HELP IN ROUTE. THE TEMP OUTSIDE WAS HOVERING AROUND 0 DEGREES AND THERE WAS A 20 MPH WIND COMING OUT OF THE NORTH, WIND CHILLS WERE -15 TO -20 DEGREES. 11:37 NORTHWESTERN TECHNICIAN ARRIVE AT SITE. UPON ARRIVAL TECHNICIAN COORDINATED EFFORTS WITH FIRE CHIEF FOR SCENE ASSESSMENT AND DETERMINATION OF GAS PLUME USING CGI. UPON DETERMINING THE GASEOUS AREA IT WAS DETERMINED IT WAS SAFE TO ENTER AREA AND LOCATE GAS METER. TO ENTER THE SCENE EXTENSIVE DIGGING WAS NECESSARY DUE TO LARGE VOLUMES IN EXCESS OF 6-8FT SNOW/PACKED/ICED OVER ON THE PROPERTY, AROUND THE FOUNDATION AND ADJACENT PROPERTIES. EXTENSIVE SHOVELING EFFORTS ALLOWS US TO VIEW THE METER ENGULFED IN FLAMES. SERVICE IS 57 FT IN LENGTH. UTILIZING THE HEAT OF THE FIRE AND CONTINUOUS SHOVELING METER WAS REACHED, FIREMEN WAS ABLE TO SHUT THE GAS OFF USING THE VALVE TO EXTINGUISH THE FLAMES. GAS WAS SHUT OFF AT THE METER 1:30 PM CST 2/23/2023. DURING THIS TIME ALSO DUE TO THE EMERGENCY AND THE SNOW SITUATION THE MUNICIPAL DEPARTMENT IN MADISON HAD SHUT ELECTRIC SERVICES OFF TO ALL OF THE TWIN HOMES THAT WERE LOCATED IN THE IMMEDIATE AREA. THREE INDIVIDUALS WERE TRANSPORTED VIA EMS TO LOCAL HOSPITAL FOR OBSERVATION, ONE HAD BURNS TO THEIR ARMS. ALL WERE RELEASED SHORTLY AFTER ASSESSMENT. 1:30PM - ADDITIONAL CREW ARRIVED ON SITE TO ASSIST WITH RESPONSE. CREW BEGAN ADDITIONAL MONITORING/GAS CHECKS IN ALL THE STRUCTURES. DURING THE CHECKS THERE WAS GAS DETECTED ONLY IN 1032 NE 11TH ST, WHICH WAS THE HOME CONNECTED TO THE ONE THAT HAD THE EXPLOSION AND THERE WAS A STRONG GAS PRESENCE DETECTED IN 1038 NE 11TH ST., WHICH WAS THE STRUCTURE IMMEDIATELY TO THE EAST OF THE HOME WITH THE EXPLOSION. THE CREW IMMEDIATELY STARTED TO AIR OUT THE SERVICE AT 1032 NE 11TH ST. TO MAKE IT SAFE. NO ADDITIONAL GAS READINGS WERE FOUND IN CONTINGENT HOUSES IN THE AREA. 2:30 PM - FI READING OVER TOP OF ALL THE GAS MAIN AND SERVICES FOR ALL THE TWIN HOMES IN THE AREA. NO GAS WAS FOUND DURING THESE CHECKS. 3:15 PM - CREW STARTED TO PERFORM BAR HOLE READ IN AREAS ALONG THE GAS MAIN AND ALONG THE SERVICE TO THE HOME THAT HAD THE EXPLOSION. THERE WAS 0 GAS MEASURED IN ANY OF THE BAR HOLE LOCATIONS. 4:00 PM VALVE ON RISER WHERE FIRE/EXPLOSION OCCURRED WAS CLOSE BUT DUE TO HEAT FROM FIRE IT WAS ONLY 99% SHUT OFF, NOT 100% -- SEEPING ONLY DETECTABLE VIA BUBBLE TEST. RISER WAS INSPECTED, PICTURES TAKEN FOR DOCUMENTATION AND TO ACHIEVE 100% CLOSURE A SQUEEZE TOOL WAS USED ON THE RISER BELOW THE LOCKWING TO PREVENT ANY GAS FROM ESCAPING. AFTER THE SCENE WAS CHECKED AND ALL HOSES WERE CHECKED CITY OF MADISON TURN THE ELECTRICITY BACK ON FOR THE HOUSES EXCEPT 1034 NE 11TH ST. ALL EQUIPMENT WAS WORKING AND ADVISED THE OTHER HOME OWNERS THAT THEY COULD RETURN TO THEIR HOUSES. ODORANT READING WERE TAKEN IN THE AREA ALSO. 4:40 PM - 1038 NE 11TH ST. WAS AIRED OUT AND FREE OF GAS. AT THAT POINT EVERYONE LEFT THE RESIDENCE AND CLOSED THE GARAGE DOOR SECURING THE HOME. AFTER THAT HOME WAS SECURED WE STARTED TO PERFORM ODOROMETER MEASUREMENT IN THE AREA. ODOROMETER READING WERE TAKEN AT 1032 NE 11TH ST. AND WERE FOUND TO BE 0.14 AT 13% GAS. A READ WAS ALSO TAKEN AT 1120 CYPRESS AVE AS WAS 0.13 AT 12% GAS. 5:05 PM - THE CREW PERFORMED A SHUT IN TEST ON 1032 NE 11TH ST., WHICH WAS THE WEST HALF OF THE TWIN HOME. THE SHUT IN TEST PASSED SO GAS WAS TURNED BACK ON SO THEY COULD START REHEATING THE UNIT. ELECTRICITY HAD ALREADY BEEN TURNED BACK ON TO THE UNIT.
2023-06-30 12:35 | NO | YES | NO | 20230016 | 38043 | 2023-03-27 09:57 | SUPPLEMENTAL FINAL | 7685 | HUNTSVILLE GAS SYSTEM | P.O. BOX 2048 | HUNTSVILLE | AL | 35804 | 2023-03-11 13:43 | CENTRAL | NO | 2023 | 278 BREVARD BLV | HUNTSVILLE | MADISON | AL | 35811 | 34.8088 | -86.4832 |  | YES |  | YES |  | YES |  |  |  | 2023-03-11 13:43 | 1362057 | 1362183 | NATURAL GAS |  | 64.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-11 13:38 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 50 | YES | 7 | 2023-03-11 13:00 | YES | OPERATOR | 2023-03-11 13:43 | 2023-03-11 12:58 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 390000 | 382320.31506399744 | 5000 | 4901.54250082048 | 500 | 490.154250082048 | 0 | 0 |  | 5 | 324 | 324 | 0 | 0 | 395824 | 171231.0697246312220973645680819912152269 | 388036.011814899968 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 47 | 49 | 50 | 192.619(A)(2) | 2005-01-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT DID NOT INDICATE ANY PRESSURE ISSUES ON THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 230581806 |  | CONTRACT LOCATOR | NO | NO | YES | 24 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | TODD GENTLE | GAS OPERATIONS DIRECTOR | todd.gentle@hsvutil.org | 2563484852 |  | TODD GENTLE | todd.gentle@hsvutil.org | 2563484852 | TODD GENTLE | GAS OPERATIONS DIRECTOR | 2563484852 | todd.gentle@hsvutil.org | AT APPROXIMATELY 1245 (12:45PM CST) ON MARCH 11, 2023, HUNTSVILLE UTILITIES (HU) DISPATCH CENTER RECEIVED A TELEPHONE CALL FROM A CONTRACTOR NOTIFYING HU THAT HE HAD CUT A GAS SERVICE LINE AT 278 BREVARD BLVD. ON-CALL CREWS FROM HU GAS DEPARTMENT RECEIVED NOTIFICATION AT 1245 (12:45PM CST) OF AN OUTSIDE LEAK DUE TO A DIG IN. HU GAS DEPARTMENT HELPER ARRIVED ON SCENE AT 1258 (12:58PM CST) AND NOTICED A STRONG SMELL OF GAS. THE FIRST RESPONDER KNOCKED ON THE FRONT DOOR, BUT NO ONE ANSWERED. THE METER WAS THEN TURNED OFF AND CONTACT WAS MADE WITH ONE OF THE HOMEOWNERS THAT ARRIVED AT THE HOUSE. DUE TO THE RESIDENT NOT BEING ABLE TO SPEAK ENGLISH, HU EMPLOYEE HAD TO REQUEST HELP FROM THE CONTRACTOR FOR TRANSLATION. AFTER THE CONTRACTOR TRANSLATED THE INFORMATION, THE RESIDENT WENT INSIDE AND RETRIEVED A RESIDENT THAT COULD SPEAK ENGLISH. THE HU EMPLOYEE WENT INTO THE HOUSE AND COULD SMELL GAS IN THE LAUNDRY ROOM. HE INSTRUCTED THE RESIDENT TO GET EVERYONE IN THE HOUSE OUT AND TO NOT TURN ON ANY SWITCHES. THE RESIDENT PROCEEDED TO TURN ON SOME LIGHT SWITCHES AND THE HU EMPLOYEE REITERATED NOT TO TURN ON/OFF ANYTHING AND TO GET EVERYONE OUT OF THE HOUSE. AT APPROXIMATELY 1315 (01:15PM CST) HU LEADMAN ON-CALL ARRIVED AND NOTICED GAS WAS BLOWING OUT OF THE GROUND NEAR THE SERVICE RISER. ONE CREW MEMBER BEGAN TO ATTEMPT TO TEST THE ATMOSPHERE IN THE HOUSE WITH A GAS DETECTION UNIT. IN HIS ATTEMPT TO GET INTO THE HOUSE, THE RESIDENCE LOCKED THE DOOR THUS HE HAD TO FIND THE RESIDENT TO UNLOCK THE DOOR. ALSO, HU PERSONNEL WERE BEGINNING TO IDENTIFY THE MAINLINE VALVES THAT WOULD ISOLATE THIS SECTION OF MAIN SERVING THE RESIDENCE. AT 1333 (01:33PM CST) THE SUPERVISOR ON-CALL ARRIVED AT THE SCENE AND BEGAN ACCESS THE SCENE. DURING THIS TIME OTHER CREW MEMBERS BEGAN DIGGING A HOLE NEAR THE AREA THAT THE SERVICE LINE WAS DAMAGED TO VENT THE GAS AWAY FROM THE HOUSE. UPON GAINING ACCESS TO THE RESIDENCE TO TEST THE ATMOSPHERE WITH THE GAS DETECTION UNIT, THE CREW MEMBER IN THE HOUSE HEARD WHAT SOUNDED LIKE THE GARAGE DOOR OPENING AND HEARD A LOUD ROARING SOUND. AS HE SAW THE FLAMES, HE RAN OUT THE FRONT DOOR. THE CREW MEMBERS DIGGING IN THE YARD HEARD WHAT THEY ASSUMED WHAT THE GARAGE DOOR OPENING IMMEDIATELY FOLLOWED BY AN EXPLOSION AT 1343 (01:43PM CST). CREW MEMBERS RE-ASSEMBLED NEAR THE STREET, THE SUPERVISOR ON SCENE CALL 911 AT 1343 (01:43PM CST) WHILE THE OTHER CREW MEMBERS CHECKED ON THE HEALTH STATUS OF ALL INDIVIDUALS AT THE SCENE. UPON FINDING NO ONE WAS INJURED, THE CREWS BEGAN TO LOCATE THE NEAREST MAIN LINE VALVES TO BEGIN TO SHUT OFF GAS TO THE WHOLE AREA. AFTER THE SUPERVISOR ENDED HIS CALL WITH 911, HE BEGAN TO CALL ADDITIONAL CREWS TO BRING SOME EQUIPMENT TO DIG THE SERVICE UP AND CAP IT OFF. ADDITIONAL CREWS ARRIVED ON SCENE AT 14:00 (02:00 PM CST) TO BEGIN DIGGING THE SERVICE UP ACROSS THE STREET SQUEEZE IT OFF AND CAP BOTH ENDS OF THE CUT. DURING THIS TIME ADDITIONAL CREW MEMBERS BEGAN LEAK SURVEYING THE SURROUND AREA AND PERFORMING BAR HOLE TEST AROUND THE MAIN. ONCE THE FIRE WAS EXTINGUISHED, CREWS MOVED ONTO THE PROPERTY AND CONTINUED LEAK SURVEY THE SURROUNDING AREA AND BAR HOLING THE SCENE. THE FIRE MARSHAL INSTRUCTED US TO REMAIN AWAY FROM THE STRUCTURE TILL THEIR INVESTIGATION WAS COMPLETE. AN INVESTIGATION INTO THE CAUSE OF THE INCIDENT IS ONGOING. CONTRIBUTING FACTORS MAY HAVE BEEN THE CUT GAS SERVICE LEAKING INTO THE HOUSE WITH AN UNKNOW IGNITION SOURCE. THE LOCAL WEATHER CONDITIONS AT THE TIME OF THE INCIDENT WERE A TEMPERATURE OF 60 DEGREES FAHRENHEIT, THE WIND SPEED WAS 4 MPH, NO WIND GUST, EAST WIND AND PARTLY CLOUDY. A SUPPLEMENTAL OR SUPPLEMENTAL PLUS FINAL REPORT WILL BE FILLED AS SOON AS NEW, UPDATED AND/OR CORRECTED INFORMATION IS KNOWN. IT HAS BEEN DETERMINED THAT THE ROOT CAUSE OF THE INCIDENT WAS LOCATES NOT BEING PERFORMED WITHIN THE ALLOTTED TIME FRAME. THE CONTRACTOR CORRECTLY LOCATED THE SERVICE LINE THEMSELVES, BUT DID NOT POT-HOLE THE UTILITIES.
2023-06-30 12:35 | NO | NO | NO | 20230017 | 37903 | 2023-04-03 15:29 | SUPPLEMENTAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2023-03-06 18:12 | EASTERN | NO | 2023 | 20 TOWNSEND STREET | PEPPERELL | MIDDLESEX | MA | 01463 | 42.6654 | -71.6011 |  |  | YES | [6 empty] | 2023-03-07 11:18 | 1361691 | 1361846 | NATURAL GAS |  | 45.46 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-06 17:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 45.46 | NO | 4 | 2023-03-06 17:30 |  |  |  | 2023-03-06 18:06 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | AT THIS TIME, UNKNOWN PENDING INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | FIRE STARTED IN BASEMENT. CAUSE UNKNOWN. | CLASS 3 LOCATION | 0 | 0 | 500 | 490.154250082048 | 3500 | 3431.079750574336 | 0 | 0 |  | 2.53 | 115 | 115 | 0 | 0 | 4115 | 1796.406313292818360175695461200585651537 | 4036.234000656384 | 1 | 0 | 3 | 0 | 0 | 1 | 1 | 55.3 | 55 | 60 | 192.621 M | 1988-10-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | NATIONAL GRID WAS NOTIFIED ON 03/06/2023 AT 17:30 ABOUT A WORKING FIRE AT 20 TOWNSEND STREET, PEPPERELL, MA. A SERVICE PERSON ARRIVED ON SITE AT 18:06. FIRE DEPARTMENT WAS ON SITE. NO INJURIES WERE REPORTED. GAS WAS SHUT OFF AT 20:15, AND FIRE WAS DETERMINED AT THAT TIME TO BE NON-GAS RELATED. THE CAUSE OF FIRE WAS NOT DETERMINED BUT GAS WAS FEEDING THE FIRE AS SOME METER AND PIPING EQUIPMENT WAS MELTED. IT APPEARED THAT THE FIRE ORIGINATED IN THE BASEMENT BEHIND A CUSTOMER APPLIANCE. NOTE 1: THIS INCIDENT INVOLVED ONE BUILDING WITH 1 COMMERCIAL CUSTOMER, AND 3 RESIDENTIAL CUSTOMERS. TOTAL OF ONE BUILDING AND ESTIMATED 4 CUSTOMERS OUT OF SERVICE. NOTE 2: AT THIS TIME, BECAUSE IT IS BELIEVED THE INCIDENT INITIATED IN THE BASEMENT BEHIND A CUSTOMER APPLIANCE, AND THE METER IS LOCATED OUTSIDE, THE INCIDENT REPORT DOES NOT INCLUDE THE COST OF DAMAGE TO THE COMMERCIAL/RESIDENTIAL BUILDING INVOLVED.
2023-06-30 12:35 | NO | YES | NO | 20230018 | 37922 | 2023-04-10 20:50 | ORIGINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2023-03-11 19:20 | CENTRAL | NO | 2023 | 6619 WENTWORTH PARK DRIVE | WENTWORTH | LAKE | SD | 57075 | 43.9562 | -96.9991 |  |  |  | YES | [5 empty] | 2023-03-11 20:09 | 1362071 | 1362178 | NATURAL GAS |  | 3652 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2023-03-11 18:53 |  |  |  | 2023-03-11 19:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | 2002 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | TO BE DETERMINED - INVESTIGATION INCOMPLETE - LAB TESTING REQUIRED | CLASS 3 LOCATION | 600000 | 588185.1000984576 | 1000 | 980.308500164096 | 5000 | 4901.54250082048 | 0 | 0 |  | 1.07 | 3908 | 3908 | 0 | 0 | 609908 | 264339.7036088107370571010248901903367496 | 597974.951099442176 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 40 | 40 | 66 | 192.619(A)(2) | 2002-06-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 22 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | NO | [217 empty] | MELISSA BARUTH | DOT SUPERVISOR | melissa.baruth@northwestern.com | 605-353-7462 | 605-353-7519 | MELISSA BARUTH | melissa.baruth@northwestern.com | 605-353-7462 | MELISSA BARUTH | DOT SUPERVISOR | 605-353-7462 | melissa.baruth@northwestern.com | NARRATIVE 6619 WENTWORTH PARK DRIVE, WENTWORTH SD 6:53 PM ' TECHNICIAN RECEIVED A FIRE PAGE AS A FIREMAN DENOTING A HOME EXPLOSION AT 6625 WENTWORTH PARK DRIVE, WENTWORTH SD. GIVEN TECHNICIAN'S CLOSE PROXIMITY TO THE LOCATION, HE DROVE TO THE SCENE IN HIS PERSONAL VEHICLE TO ASSESS SITUATION. 6:59 PM -07:01PM ' AS TECHNICIAN WAS IN ROUTE TO SCENE HE PUT OTHER NORTHWESTERN'S PERSONNEL INCLUDING BROOKINGS GAS SUPERVISOR ON NOTICE OF POSSIBLE HOME EXPLOSION. . THE INITIAL CALL HAD THE INCORRECT ADDRESS ASSOCIATED WITH THE EXPLOSION, THE INITIAL CALL WAS FOR 6625 WENTWORTH PARK DR, INCIDENT OCCURRED AT 6619 WENTWORTH PARK DR. 7:05 PM ' NORTHWESTERN TECHNICIAN VERIFIED THAT IT WAS INDEED A HOUSE EXPLOSION AND NATURAL GAS WAS POSSIBLY INVOLVED. HE IMMEDIATELY REQUESTED ADDITIONAL ASSISTANCE. CONFIRMATION OF INCIDENT RELAYED TO NORTHWESTERN PERSONNEL INITIALLY CONTACTED. ADDITIONAL PERSONNEL HEADED TO OFFICE TO LOAD TRUCK AND TRAILER OF POSSIBLE NEEDED ITEMS, THEN PROCEEDED TO DRIVE FROM BROOKINGS SD TO LAKE MADISON (WENTWORTH, SD). IN ADDITION OTHER SUPERVISORY PERSONNEL NOTIFIED. EMERGENCY LOCATES CALLED IN FOR SITE BY SUPERVISORY PERSONNEL. ON SITE -- NORTHWESTERN TECHNICIAN AND FIRE DEPARTMENT SECURED THE AREA AND KEPT EVERYONE BACK WHILE NORTHWESTERN TECHNICIAN LEFT SCENE TO GET WORK TRUCK AND CGI'S. AFTER ARRIVING BACK AT THE SCENE AN IC WAS ESTABLISHED AND MONITORED AIR FOR GAS PLUME SINCE THERE WAS NO FIRE. NORTHWESTERN TECHNICIAN CHECKED ADJACENT HOUSES FOR GAS AND FOUND SMALL TRACE IN THE HOUSE TO THE NORTH. NO OTHER GAS WAS DETECTED. TECHNICIAN CONTACTED LAKE COUNTY DISPATCH AND HAD THEM GET SIOUX VALLEY ENERGY ON THE WAY TO DISCONNECT POWER TO 6619 TO ELIMINATE ANOTHER EXPLOSION. NORTHWESTERN TECHNICIAN PROCEEDED TO ESTABLISH WHERE THE GAS WAS COMING FROM AND CONFIRMED THAT IT WAS FROM THE METER LOCATION AT 6619 WENTWORTH PARK DR. TECHNICIAN LOCATED GAS METER IN RUMBLE AND SNOW (6-7FT), DUG AROUND THE VALVE TO CLEAR THE SNOW/ICE AS TO SHUT OFF THE SERVICE VALVE. THE WHOLE TIME FIRE DEPARTMENT PERSONNEL ASSISTED IN MONITORING THE AIR FOR GAS. THE TEMP OUTSIDE WAS IN THE MID 20 DEGREES AND THERE WAS A LITTLE TO NO WIND INITIALLY. . 8:02 PM ' GAS SHUT OFF AT INCIDENT SITE. TECHNICIAN LOCATED AND GAS RISER IN RUMBLE AND WAS ABLE TO TURN OFF THE GAS RISER VALVE. 8:15 PM ' ADDITIONAL PERSONNEL ARRIVED ON SCENE, MET WITH NORTHWESTERN TECHNICIAN ON SITE AND DETERMINED WHAT NEEDED TO BE ACCOMPLISHED TO ESTABLISH A SAFE PERIMETER. ADDITIONAL READS ON CGI TAKEN IN THE IMMEDIATE AREA. THEY CHECKED THE NEIGHBORING HOMES AND FOUND NO GAS ACCUMULATION. FI ALSO USE ABOVE THE GAS MAIN AND ABOVE ALL SERVICE LINES IN THE AREA. 8:47 TO 8:53 ' ODOROMETER READING AT 6613 AND 6625 WENTWORTH PARK DR. THE ODOROMETER READING AT BOTH LOCATION WERE THE SAME 0.22%. 9:30 TO 10:10 PM ' THE CREW WORKED TO UNCOVER THE GAS METER AND ASSOCIATED PIPING FROM EXCESSIVE SNOW ' 6 TO 7 FOOT SNOW. USING THE MINI BACKHOE THEY DUG UP AS CLOSE AS WE FELT SAFE WITH THE MINI. FROM THAT POINT THEY CHIPPED AWAY AT THE SNOWBANK WITH SHOVELS TO EXPOSE THE GAS METER. THE RISER AND ENTIRE METER SET WERE INTACT OTHER THAT THE INDEX AND ALL THE DIALS WERE BROKEN OFF OF THE METER. 10:15 PM - ALL RELEVANT LOCATES WERE COMPLETED SO WE COULD START MAKING BAR-HOLES AND TAKING READINGS. THE INITIAL HOLE THAT WE MADE IMMEDIATELY NEXT TO THE GAS RISER HAD A READING OF 0.3 ON AND 0.4 PK, WHICH WAS EXPECTED TO HAVE SOME READING THERE. ALL OTHER BAR HOLES WERE COMPLETED AND THERE WAS NOT GAS FOUND IN ANY LOCATION.
2023-06-30 12:35 | NO | YES | YES | 20230019 | 38071 | 2023-04-14 16:55 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2023-03-17 20:40 | MOUNTAIN | YES | 2023 | 8913 PADILLA DRIVE | EL PASO | EL PASO | TX | 79907 | 31.6878 | -106.334 | [5 empty] | YES |  |  |  | 2023-03-17 21:12 | 1362513 | 1362610 | NATURAL GAS |  | 5.772 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-03-17 16:49 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.54 | NO | 4 | 2023-03-17 17:49 |  |  |  | 2023-03-17 17:31 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | 2017 |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | DR11 |  |  | 2708 | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 129383 | 126835.254676731232768 | 5000 | 4901.54250082048 | 7895 | 7739.53560879553792 | 0 | 0 |  | 5.82 | 34 | 34 | 0 | 0 | 142312 | 61551.2794302150227208345534407027818448 | 139510.332786347250688 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 49 | 50 | 60 | 192.619(A)(2) | 2017-11-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DAMAGED DURING SEWER CLEAN OUT AT A CROSS BORE. | [149 empty] | YES |  |  |  |  | BRYAN WEEKS | DIRECTOR OF ENGINEERING | bryan.weeks@onegas.com | 5124071529 | 5124651133 | BRYAN WEEKS | bryan.weeks@onegas.com | 5124071529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 5124071529 | bryan.weeks@onegas.com | POST-INCIDENT INVESTIGATION REVEALED A 2-INCH PE PIPE WAS MOST LIKELY PUNCTURED WHEN A RESIDENT'S PLUMBER USED A MECHANICAL TOOL TO CLEAR A CLOGGED SEWER LATERAL. THE GAS PIPE HAD BEEN INADVERTENTLY CROSS-BORED THROUGH THE SEWER LATERAL BY THE ORIGINAL GAS LINE INSTALLATION CONTRACTOR IN 2017. CAMERA INSPECTIONS WERE PERFORMED ON THE REMAINDER OF THE ORIGINAL INSTALLATION PROJECT AND NO ADDITIONAL AREAS WERE DISCOVERED TO HAVE CROSS-BORES. TEXAS GAS SERVICE COMPANY'S PUBLIC AWARENESS TO THE AFFECTED PUBLIC INCLUDES OUTREACH ON THE POSSIBILITY OF CROSS-BORES. SUPPLEMENTAL INFORMATION 5/19/23 TGS SELECTED 20:40 AS THE EARLIEST LOCAL TIME THAT THE INCIDENT REPORTING CRITERIA WERE MET BASED ON ITS PRELIMINARY EVALUATION THAT NATURAL GAS FROM ITS SYSTEM WAS LIKELY TO HAVE CAUSED THE FIRE AND THE PRESUMPTION THAT ONE OF THE HOME'S OCCUPANTS COULD BE ADMITTED TO THE HOSPITAL FOR CARE OR THAT THE TOTAL COST OF DAMAGES COULD EXCEED $129,300. WHILE THE ORIGINAL TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER NOTED THE POTENTIAL THAT AN EXPLOSION HAD OCCURRED, THE INVESTIGATION MADE NO OBSERVATIONS OR FORMAL REPORTS OF AN EXPLOSION.
2023-06-30 12:35 | NO | YES | NO | 20230021 | 37964 | 2023-04-21 15:17 | ORIGINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2023-03-24 06:00 | EASTERN | YES | 2023 | 516 NORTH MAIN STREET | MAULDIN | GREENVILLE | SC | 29662 | 34.7879 | -82.3128 | [7 empty] | YES | FIRE DEPARTMENT SHUT OFF GAS. | 2023-03-24 07:12 | 1362993 | 1363089 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-24 06:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 0 | 2023-03-24 06:00 |  |  |  | 2023-03-24 06:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | STRUCTURE FIRE. | CLASS 1 LOCATION | 0 | 0 | 129300 | 126753.8890712176128 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 129300 | 55918.9612733836185 | 126753.8890712176128 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 58 | 58 | 70 | 192.619(A)(2) | 1997-01-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [111 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HOUSE FIRE. THE INVESTIGATION WAS TURNED OVER TO THE MAULDIN POLICE. CAUSE OF FIRE IS UNKNOWN AT THE TIME. | [154 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER-PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | STRUCTURE FIRE. CAUSE IS UNKNOWN AND STILL UNDER INVESTIGATION. A SUPPLEMENTAL AND FINAL REPORT WITH MORE DETAILS WILL BE FILED ONCE INVESTIGATION IS COMPLETE.
2023-06-30 12:35 | NO | YES | YES | 20230022 | 37968 | 2023-04-23 13:24 | ORIGINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2023-03-24 16:55 | EASTERN | YES | 2023 | 17 S 2ND AVENUE | WEST READING | BERKS | PA | 19611 | 40.3344 | -75.9422 |  | YES | [7 empty] | 2023-03-24 19:09 | 1363061 | 1363191 | NATURAL GAS |  | 0 | 0.09 | YES | 0 | 0 | 0 | 0 | 7 | 7 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2023-03-24 16:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2023-03-24 17:00 |  |  |  | 2023-03-24 17:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | UNKNOWN. STILL UNDER INVESTIGATION |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | STILL UNDER INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | STILL UNDER INVESTIGATION | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COSTS FOR ITEMS 2A-2D AND 2F ARE STILL BEING DETERMINED. | 2.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 4 | 11 | 7 | 0 | 18 | 7 | 53 | 53 | 60 | 192.619(A)(2) | 2021-02-16 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 9 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL DID NOT HAVE AN IMPACT ON THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ROMAN HIGH | SR ENGINEER STANDARDS | rhigh@ugi.com | 484-332-8402 |  | ANDREW ZIMMERMAN | azimmerman@ugi.com | 484-332-7318 | PAM JOCSAK | VP ENGINEERING | 484-824-5508 | pjocsak@ugi.com | ON 3/28/2023, THE NATIONAL TRANSPORTATION SAFETY BOARD OPENED AN INVESTIGATION INTO THIS INCIDENT. UGI IS COOPERATING WITH THE NTSB AND OTHER FEDERAL, STATE, AND LOCAL AUTHORITIES INVOLVED IN CONDUCTING THAT INVESTIGATION AND WILL SUBMIT A SUPPLEMENTAL REPORT AS ADDITIONAL INFORMATION ABOUT THE INCIDENT BECOMES AVAILABLE. THE NUMBER OF GENERAL PUBLIC EVACUATED IS UNKNOWN DUE TO THE ARRIVAL OF UGI UTILITIES, INC. RESPONDERS AND EMERGENCY RESPONDERS ON SITE AFTER THE INCIDENT OCCURRED, SO THE AMOUNT ENTERED IN A.22 WAS ZERO. THE ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY IS NOT AVAILABLE AT THIS TIME, SO THE AMOUNTS ENTERED IN A.7 AND A.21C WAS ZERO. THE OPERATING PRESSURE AND MAOP INFORMATION PROVIDED IN PART E IS BASED ON THE CLOSEST DISTRIBUTION ASSET (SERVICE LINE) THAT SUPPLIED GAS TO THE BUILDING INVOLVED IN THE INCIDENT. THE INCIDENT IS STILL UNDER INVESTIGATION AND THE INFORMATION IN PART E IS SUBJECT TO CHANGE.
2023-06-30 12:35 | NO | NO | NO | 20230023 | 37981 | 2023-04-26 10:26 | ORIGINAL | 32013 | AMERIGAS PROPANE LP | 460 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2023-04-01 01:30 | PACIFIC | YES | 2023 | 205 JUNIPER DRIVE | MAMMOTH LAKES | MONO | CA | 93546 | 37.6355 | -118.9959 |  | YES |  | YES | [5 empty] | 2023-04-01 16:15 | 1363726 | 1364037 | PROPANE GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-04-01 01:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 0 | 2023-04-01 01:30 |  |  |  | 2023-04-01 02:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN | CLASS 2 LOCATION | 100000 | 98030.8500164096 | 300 | 294.0925500492288 | 0 | 0 | 0 | 0 | ESTIMATED AMOUNT - COST UNKNOWN | 3 | 0 | 0 | 0 | 0 | 100300 | 43377.1988841483135 | 98324.9425664588288 | 0 | 0 | 27 | 0 | 0 | 1 | 0 | 0.51 | 0.51 | 10 | 192.619(A)(1) | 1980-07-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [231 empty] | MISCELLANEOUS | ON 4/1/2023 AT APPROXIMATELY 01:30 AM LOCAL TIME MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS, THAT A SINGLE FAMILY RESIDENCE THAT HAD GAS SERVICE WAS ON FIRE. AT THAT TIME EMERGENCY RESPONDERS, SHUT OFF GAS SERVICE TO THE RESIDENCES AND SECURED THE SCENE. THE CAUSE OF THE FIRE IS UNCLEAR, ESTIMATED COSTS AND DAMAGES IS UNKNOWN. THIS INCIDENT IS UNDER INVESTIGATION, THIS FORM IS BEING SUBMITTED AS A PRECAUTIONARY MEASURE. | [47 empty] | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | bill.runyans@amerigas.com | 2564591078 |  | KYLE MUIR | kyle.muir@amerigas.com | 7067090195 | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | 2564591078 | bill.runyans@amerigas.com | ON 4/1/2023 AT APPROXIMATELY 01:30 AM LOCAL TIME MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS, THAT A SINGLE FAMILY RESIDENCE THAT HAD GAS SERVICE WAS ON FIRE. AT THAT TIME EMERGENCY RESPONDERS, SHUT OFF GAS SERVICE TO THE RESIDENCES AND SECURED THE SCENE. THE CAUSE OF THE FIRE IS UNCLEAR, ESTIMATED COSTS AND DAMAGES IS UNKNOWN. THIS INCIDENT IS UNDER INVESTIGATION, THIS FORM IS BEING SUBMITTED AS A PRECAUTIONARY MEASURE.
2023-06-30 12:35 | NO | YES | NO | 20230024 | 38007 | 2023-05-03 16:47 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-04-04 15:21 | EASTERN | YES | 2023 | 7307 THORNAPPLE LAKE ROAD | NASHVILLE | BARRY | MI | 49073 | 42.6245 | -85.1473 | [6 empty] | YES |  |  | 2023-04-05 10:02 | 1364022 | 1364164 | NATURAL GAS |  | 4971 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-04-04 15:21 | YES | OPERATOR | 2023-04-05 10:00 | 2023-04-04 15:24 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 66 | NO | YES | [6 empty] | YES | UNCASED | THORNAPPLE RIVER | UNKNOWN | BELOW WATER, PIPE ON OR ABOVE BOTTOM | INVESTOR OWNED |  | MAIN |  | 1950 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | WILL PROVIDE ONCE THE PIPELINE IS REMOVE | 0.219 | [6 empty] | OTHER | [8 empty] | WILL PROVIDE ONCE THE PIPELINE IS REMOVED | CLASS 1 LOCATION | 3800 | 3725.1723006235648 | 3716000 | 3642826.386609780736 | 422 | 413.690187069248512 | 0 | 0 |  | 2.16 | 10737 | 10737 | 0 | 0 | 3730959 | 1615110.93049616417045266471449487554905 | 3657702.249097473549312 | 414 | 22 | 4002 | 0 | 0 | 4002 | 436 | 385 | 385 | 400 | 192.619(C) | 1969-11-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [231 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON APRIL 4, 2023, AT APPROXIMATELY 15:21 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A POSSIBLE NATURAL GAS LEAK ON THE PIPELINE THAT CROSSES THE THORNAPPLE RIVER NEAR 7307 THORNAPPLE LAKE ROAD NASHVILLE, (BARRY COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 15:24 HOURS. THE GSW CONFIRMED A LEAK INDICATION AT THE THORNAPPLE RIVER CROSSING ON A 6-INCH HIGH-PRESSURE, STEEL, SINGLE-FEED PIPELINE SERVING OVER FOUR THOUSAND DOWNSTREAM CUSTOMERS. A GAS DISTRIBUTION SUPERVISOR WAS NOTIFIED AND ARRIVED ONSITE TO ASSIST WITH THE RESPONSE. DUE TO EXTREME FLOODING CONDITIONS AND MINIMAL REMAINING DAYLIGHT, AN INITIAL RESPONSE PLAN WAS IMPLEMENTED TO CONTINUOUSLY MONITOR THE LEAK LOCATION. A CONTINGENCY PLAN ALSO WAS PREPARED FOR IMMEDIATE CONTAINMENT USING EMERGENCY VALVES TO ISOLATE THE AFFECTED SEGMENT SHOULD THE CONDITION WORSEN DURING THE NIGHT. GAS OPERATIONS AND GAS ENGINEERING ALSO EVALUATED AND ASSESSED THE SITUATION IN DEVELOPING A LONG-TERM REMEDIATION PLAN. THE FOLLOWING DAY, AN INCIDENT COMMAND STRUCTURE (ICS) WAS ACTIVATED BECAUSE OF THE POTENTIAL IMPACT TO CUSTOMERS IN HASTINGS, MI. THE REMEDIATION PLAN WAS FINALIZED, AND IMPLEMENTATION WAS ALREADY UNDERWAY WHEN OPERATIONS PERSONNEL DISCOVERED THE LEAK WAS WORSENING AND DUE TO AN ANTICIPATED TEMPERATURE DECREASE SERVICE LOSS FOR CUSTOMERS WAS LIKELY TO OCCUR. CONSEQUENTLY, ADDITIONAL COMMUNICATION WAS UNDERTAKEN WITH KEY STAKEHOLDERS AND CUSTOMERS NOTIFYING THEM OF THE POTENTIAL INTERRUPTION IN NATURAL GAS SERVICE. A HIGH-PRESSURE BYPASS WAS INSTALLED TO ALLOW FOR FASTER RESTORATION OF NATURAL GAS SERVICE TO IMPACTED CUSTOMERS ONCE THE RELEASE WAS CONTAINED. ON APRIL 6, 2023, GAS WAS SHUT-OFF AT THE LEAK LOCATION BY INSTALLING PRESSURE CONTROL FITTINGS AT THE EAST AND WEST SIDES OF THE LOCATION. CONCURRENT TO THE PRESSURE CONTROL WORK, MULTIPLE GSW'S WERE TURNING OFF AFFECTED CUSTOMERS' SERVICE-LINE VALVE PRIOR TO ADMITTING GAS BACK INTO THE SYSTEM. THE BYPASS WAS ACTIVATED AT APPROXIMATELY 07:21 HOURS. PURGING FROM AIR TO GAS OF THE PIPELINE WAS PERFORMED IN STAGES PRIOR TO TURNING SERVICE-LINE VALVES AND RELIGHTING CUSTOMERS. CONSTRUCTION FOR PERMANENT PIPELINE REPLACEMENT WAS ALSO UNDER WAY DURING THIS TIME. CUSTOMER RESTORATION STARTED ON APRIL 7, 2023, AND AS OF THIS REPORT'S DATE, SERVICE HAS BEEN RESTORED TO ALL IMPACTED CUSTOMERS OR THEY RECEIVED NOTIFICATION REQUESTING ACCESS TO THEIR PROPERTIES FOR SERVICE RESTORATION. WEEKLY RESTORATION STATUSES ARE PROVIDED TO THE MICHIGAN PUBLIC SERVICE COMMISSION STAFF. THE PERMANENT PIPELINE REPLACEMENT REQUIRED INSTALLATION OF APPROXIMATELY ONE THOUSAND FEET OF 6-INCH HIGH-PRESSURE STEEL PIPELINE. THE PIPELINE REPLACEMENT WAS COMPLETED, AND NORMAL OPERATIONS RESUMED ON APRIL 11, 2023, AT APPROXIMATELY 19:50 HOURS.
2023-06-30 12:35 | NO | YES | NO | 20230025 | 38039 | 2023-05-04 15:40 | SUPPLEMENTAL FINAL | 31044 | LOWER VALLEY ENERGY, INC. | 236 N. WASHINGTON BLVD/P.O. BOX 188 | AFTON | WY | 83110 | 2023-03-25 02:56 | MOUNTAIN | YES | 2023 | 900 SNOW KING DR | JACKSON | TETON | WY | 83001 | 43.4698 | -110.7489 |  |  |  | YES | [5 empty] | 2023-03-25 07:10 | 1363085 | 1363250 | NATURAL GAS |  | 27 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-25 03:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27 | NO | 0 | 2023-03-25 05:30 |  |  |  | 2023-03-25 03:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 2006 | 2006 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | THREADS | 0.113 | [6 empty] | OTHER | [8 empty] | METER CAIN SHEARED OFF RIGHT AT THE METER | CLASS 2 LOCATION | 3000000 | 2940925.500492288 | 100 | 98.0308500164096 | 540 | 529.36659008861184 | 0 | 0 |  | 27 | 729 | 729 | 0 | 0 | 3001369 | 1298122.08238091192414407027818448023426 | 2942281.89793239302144 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 2006-05-05 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS ON A RESIDENTIAL METER | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | NO | [217 empty] | CRAIG COLES | DIRECTOR OF GAS OPERATIONS | ccoles@lvenergy.com | 307 885 6151 | 307 885 5787 |  |  |  | CRAIG COLES | DIRECTOR OF GAS OPERATIONS | 307 885 6151 | ccoles@lvenergy.com | ON MARCH 25TH 2023 LOWER VALLEY ENERGY WAS CALLED TO A HOUSE FIRE WHERE THE METER CAIN HAD BEEN BROKEN BY SNOW AND ICE FALLING OFF THE ROOF AND BREAKING IT. THE GAS IGNITED BY AN UNKNOW SOURCE. LOWER VALLEY WAS CALLED BY THE FIRE DEPARTMENT TO THE SCENE WHERE IT WAS DECIDED TO PUT THE FLAME OUT AND TURN THE VALVE OFF WHICH DID STOP THE FLOW OF GAS. THE SITUATION WAS CONTROLLED BY 6:30 AM THAT DAY. THE HOUSE WAS A TOTAL LOSS FROM THE FIRE. THERE WERE NO INJURIES AS NO ONE WAS HOME AT THE TIME OF THE FIRE.
2023-06-30 12:35 | NO | YES | YES | 20230026 | 38016 | 2023-05-05 13:02 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2023-04-06 14:59 | EASTERN | YES | 2023 | 2027 HENDRIX DR. | GROVE CITY | FRANKLIN | OH | 43123 | 39.9156 | -83.0429 |  |  | YES | [6 empty] | 2023-04-06 15:18 | 1364142 | 1364239 | NATURAL GAS |  | 66.4 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2023-04-06 12:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 66.3 | NO | 0 | 2023-04-06 12:53 |  |  |  | 2023-04-06 13:10 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1986 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES | 1 | PE 2306 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 70000 | 68621.59501148672 | 800 | 784.2468001312768 | 4800 | 4705.4808007876608 | 0 | 0 |  | 5.04 | 335 | 335 | 0 | 0 | 75935 | 32888.8179742357311361639824304538799414 | 74446.3226124056576 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 48 | 48 | 60 | 192.619(A)(2) | 1996-08-24 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE BUSINESS | [7 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 48 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT |  | NOTIFICATION TO ONE-CALL CENTER MADE, BUT NOT SUFFICIENT | [171 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | A THIRD-PARTY FENCING EXCAVATOR DAMAGED A ONE-INCH PLASTIC SERVICE LINE WITH AN AUGER ATTACHED TO A SKID STEER. AFTER STRIKING THE SERVICE LINE THE SKID STEER OPERATOR BACKED UP SLIGHTLY AND A COWORKER BEGAN TO REMOVE SOIL FROM THE HOLE WHEN GAS IGNITED BURNING THE CONTRACTORS FACE AND HANDS. IN ADDITION, THE FIRE DAMAGED THE SKID-STEER. THE THIRD-PARTY FENCING EXCAVATOR CALLED IN A ONE CALL TICKET TO A BUILDING ONE STREET OVER. THE DAMAGE OCCURED AT A LOCATION WITHOUT A ONE CALL TICKET. THE ODORANT READING AT THE TIME OF THE INCIDENT WAS .42 AND DUE TO A SYSTEM ISSUE, I WAS UNABLE TO DOCUMENT THE READING IN SECTION E6. PLEASE CONSIDER THIS REPORT BOTH AND INITIAL AND FINAL REPORT. NO FURTHER REPORTS WILL BE FILED.
2023-06-30 12:35 | NO | YES | NO | 20230027 | 38063 | 2023-05-18 17:22 | ORIGINAL | 20050 | AMERENUE | 1901 CHOUTEAU | SAINT LOUIS | MO | 63103 | 2023-04-19 09:05 | CENTRAL | YES | 2023 | 106 STATE HWY 114 | ESSEX | STODDARD | MO | 63846 | 36.811 | -89.8615 | YES | [8 empty] | 2023-04-19 09:55 | 1365146 | 1365278 | NATURAL GAS |  | 33.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-04-19 08:27 | ALLOWED TO BURN OUT |  | 33.28 | NO | 3 | 2023-04-19 09:05 |  |  |  | 2023-04-19 09:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | FITTING | [9 empty] | OTHER | [8 empty] | VEHICLE DROVE OVER A METER SET. THE UNION BROKE OFF ABOVE THE RISER VALVE. | CLASS 3 LOCATION | 450000 | 441138.8250738432 | 1100 | 1078.3393501805056 | 65724 | 64429.795864785045504 | 0 | 0 | . | 0.94 | 31 | 31 | 0 | 0 | 516855 | 223531.1629147262375075256222547584187408 | 506677.960288808751104 | 21 | 0 | 161 | 0 | 0 | 161 | 21 | 14.98 | 15 | 18 | 192.619(A)(4) | 1998-05-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [111 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | SMALL TRUCK | ROADWAY | 15 | NO | [142 empty] | MARK BRANDT | MANAGER GAS COMPLIANCE AND PROGRAM MANAGEMENT | mbrandt2@ameren.com | 573-694-1794 |  | MARK BRANDT | mbrandt2@ameren.com | 573-694-1794 | PAM HARRISON | DIRECTOR MISSOURI GAS OPERATIONS | 573-619-3124 | pharrison@ameren.com | ON 4/19/2023, PRIOR TO 8:27AM A VEHICLE (VEHICLE 1) WAS PULLING OUT OF A PARKING LOT NEAR THE ESSEX ONE STOP CONVENIENCE STORE AND STRUCK AN ONCOMING VEHICLE (VEHICLE 2). VEHICLE 2 LOST CONTROL AND SLAMMED INTO THE GAS STATION WALL DRIVING OVER THE GAS METER, BREAKING THE GAS METER PIPING AT THE UNION ABOVE THE METER VALVE, CAUSING A LEAK. VEHICLE 2 CAME TO REST ON TOP OF THE BROKEN GAS PIPING. SHORTLY AFTER, THE GAS IGNITED LEADING TO A VEHICLE AND STRUCTURE FIRE. THE EXACT TIME OF IGNITION IS UNKNOWN. THE EXACT NUMBER OF INDIVIDUALS EVACUATED IS UNKNOWN, BUT IS ESTIMATED TO BE BETWEEN 3-5. AT 8:27 EMERGENCY RESPONSE PERSONNEL NOTIFIED THE AMEREN CALL CENTER OF THE FIRE. AT 8:30, AN AMEREN GAS FIRST RESPONDER WAS DISPATCHED. AT 9:05, THE FIRST AMEREN GAS PERSONNEL ARRIVED AT THE LOCATION. EMERGENCY RESPONSE PERSONNEL EXTINGUISHED THE STRUCTURE FIRE WHILE ALLOWING THE GAS FED FIRE TO BURN IN A CONTROLLED MANNER. AT 12:32, AMEREN PERSONNEL CLOSED AN EMERGENCY VALVE TO ISOLATE FLOW OF GAS TO SERVICE RISER. AT 12:48 THE FIRE BURNED OUT. AFTER VEHICLE 2 WAS REMOVED FROM THE SCENE, THE SERVICE WAS EXCAVATED AND PHYSICALLY ISOLATED FROM THE MAIN. AFTER WHICH, GAS SERVICE WAS RESTORED FOLLOWING ALL APPLICABLE STANDARD OPERATING PRACTICES. THE STRUCTURE AND VEHICLE 2 WERE TOTAL LOSSES. THE EXACT VALUE IS UNKNOWN, BUT IS ESTIMATED TO BE APPROXIMATELY $450,000.
2023-06-30 12:35 | NO | YES | YES | 20230028 | 38165 | 2023-06-13 13:39 | ORIGINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2023-05-02 10:00 | EASTERN | YES | 2023 | 26010 PENN STREET | INKSTER | WAYNE | MI | 48141 | 42.2854 | -83.2925 | [5 empty] | YES |  |  |  | 2023-05-02 10:40 | 1366173 | 1366323 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 1 | 2 | YES | 2023-05-02 10:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 1 | 2023-05-02 10:00 | YES | OPERATOR | 2023-05-02 10:01 | 2023-05-02 10:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | EXPLOSION ORIGINATED IN HOME CRAWL SPACE |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1952 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CORROSION | [5 empty] | CLASS 3 LOCATION | 49000 | 48035.116508040704 | 300 | 294.0925500492288 | 10000 | 9803.08500164096 | 0 | 0 |  | 3.85 | 0 | 0 | 0 | 0 | 59300 | 25645.7417131604685 | 58132.2940597308928 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 10 | 10 | 10 | 192.619(A)(1) | 1952-08-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 7 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | YES |  |  |  | YES | CORROSION APPEARS TO HAVE OCCURRED AT THE GROUND-TO-ATMOSPHERE TRANSITION AREA |  |  | YES |  |  |  | NO | [11 empty] | YES | YES | UNKNOWN |  | UNKNOWN | [19 empty] | 2022-07-22 | NO | [181 empty] | YES | YES | [43 empty] | MARINA DARLING | SUPERVISOR - CODES AND STANDARDS | marina.darling@dteenergy.com | 15868724760 |  |  |  |  | MARINA I. DARLING | SUPERVISOR - CODES AND STANDARDS | 15868724760 | marina.darling@dteenergy.com | A DTE CREW WAS IN THE PROCESS OF REPLACING THE SERVICE LINE TO 26010 PENN STREET, INKSTER, MI, 48141, WHEN THE HOUSE EXPLODED INJURING ONE (1) HOMEOWNER AND ONE (1) DTE GAS EMPLOYEE. THE INVESTIGATION IS ON-GOING, HOWEVER, DURING DTE'S INITIAL ASSESSMENT IT IS BELIEVED THAT A LEAK OCCURRED AT A CORRODED SECTION OF THE 3/4-INCH SERVICE RISER IN THE CRAWL SPACE OF THE HOUSE DURING REMOVAL OF THE METER MANIFOLD ASSEMBLY. THE CORROSION APPEARS TO HAVE OCCURRED AT THE GROUND-TO-ATMOSPHERE TRANSITION AREA AND THE DISTURBANCE OF THE PIPING DURING REMOVAL CAUSED THE LEAK. EMPLOYEES WERE UNAWARE OF THE LEAKING GAS AS IT ACCUMULATED IN THE CRAWL SPACE AND IGNITED. A SOURCE OF IGNITION HAS NOT BEEN DETERMINED. ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY (PART A.7) AND ESTIMATED VOLUME OF GAS CONSUMED BY FIRE (PART A.21C) COULD NOT BE DETERMINED DUE TO UNKNOWN SIZE AND DURATION OF THE LEAK AND IS ASSUMED TO BE MINIMAL.
2023-06-30 12:35 | NO | NO | NO | 20230029 | 38184 | 2023-06-16 16:06 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-05-20 10:29 | EASTERN | YES | 2023 | HARPER AVENUE & FIERZ STREET | CLINTON TOWN | MACOMB | MI | 48035 | 42.5674 | -82.8717 | [5 empty] | YES |  |  |  | 2023-05-20 19:29 | 1367814 | 1367873 | NATURAL GAS |  | 3360 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-05-20 10:29 | YES | OPERATOR | 2023-05-20 10:55 | 2023-05-20 10:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 4 | 9.6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 100491 | 98512.181489990171136 | 2435 | 2387.05119789957376 | 0 | 0 |  | 2.19 | 7358 | 7358 | 0 | 0 | 110284 | 48768.2358037884455323718887262079062958 | 108257.232687889744896 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 55 | 54 | 60 | 192.619(A)(2) | 1969-10-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2023031501225 |  | CONTRACT LOCATOR | YES | YES | YES | 24 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO VERIFY LOCATION BY TEST-HOLD (POT-HOLING) | [169 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON MAY 20, 2023, AT APPROXIMATELY 10:29 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR THE INTERSECTION OF HARPER AVENUE AND FIERZ STREET, CLINTON TOWNSHIP (MACOMB COUNTY) MICHIGAN. THE GAS DISTRIBUTION SUPERVISOR WAS ONSITE AT APPROXIMATELY 10:55 HOURS AND A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:02 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR DAMAGED A 4-INCH STEEL (MEDIUM PRESSURE) PIPELINE WHILE BORING TELECOMMUNICATION CONDUIT. THE GSW BEGAN MONITORING THE AREA FOR GAS MIGRATION AND SERVICE PERSONNEL MONITORED THE AREA UNTIL THE GAS WAS CONTAINED. POLICE AND FIRE PERSONNEL WERE ONSITE AND CLOSED THE ROAD TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. A DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 12:12 HOURS AND DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. BECAUSE THE PIPELINE DEPTH WAS GREATER THAN 6-FEET, SHORING EQUIPMENT WAS REQUIRED TO SAFELY ACCESS THE PIPELINE. THE DAMAGED SEGMENT WAS ISOLATED AT APPROXIMATELY 18:04 HOURS BY SQUEEZING THE 6-INCH S-MP PIPELINE TO THE NORTH AND SOUTH OF THE 4-INCH S-MP PIPELINE WHERE THE DAMAGE OCCURRED. ONCE GAS WAS CONTAINED, CONTROL FITTINGS WERE INSTALLED ON THE 6-INCH S-MP PIPELINE AND THE TWO SECTIONS USED DURING THE SQUEEZING OPERATION WERE REPLACED. THE SECTION OF THE 4-INCH S-MP PIPELINE WHERE THE INITIAL DAMAGE OCCURRED WAS REPLACED AND NORMAL OPERATIONS RESUMED ON MAY 21, 2023, AT APPROXIMATELY 10:45 HOURS. SERVICE RESTORATION FOR ALL IMPACTED CUSTOMERS BEGAN AFTER THE PIPELINE REPAIR.
2023-06-30 12:35 | NO | YES | NO | 20230030 | 38207 | 2023-06-26 21:38 | ORIGINAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2023-05-26 12:10 | EASTERN | YES | 2023 | 29920 JAMESTOWN DRIVE | CHESTERFIELD TOWNSHIP | MACOMB | MI | 48051 | 42.6832 | -82.8084 |  | YES |  |  |  | YES |  |  |  | 2023-05-26 13:19 | 1368330 | 1368665 | NATURAL GAS |  | 15.09 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-05-26 10:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15.09 | NO | 2 | 2023-05-26 10:53 |  |  |  | 2023-05-26 11:05 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 140000 | 137243.19002297344 | 3278 | 3213.451263537906688 | 14025 | 13748.8267148014464 | 0 | 0 |  | 4.5 | 68 | 68 | 0 | 0 | 157371 | 68068.8730219003810566691068814055636896 | 154273.468001312793088 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1981-07-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD PARTY DAMAGE. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2023052503098 |  | FACILITY OWNER | YES | NO | YES | 16 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  |  | FAILURE TO USE HAND TOOLS WHERE REQUIRED | [169 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | ADAM DZIEDZIC | adam.dziedzic@semcoenergy.com | (810) 887-5027 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | (810) 887-5027 | phil.lenn@semcoenergy.com | ON 05/26/23, A GAS MAIN LOCATED AT 29920 JAMESTOWN DRIVE, CHESTERFIELD TWP, MI, WAS STRUCK BY A THIRD-PARTY EXCAVATOR WHILE ATTEMPTING TO FIX A LEAKING WATER LINE. THE CONTRACTOR THEN CALLED 911 AND BEGAN EVACUATING NEARBY RESIDENTS. ACCORDING TO THE CONTRACTOR, THE GAS LEAK IGNITED WITHIN APPROXIMATELY 5 MINUTES OF THE GAS MAIN HIT. THE FIRE THEN SPREAD TO THE HOME. SEMCO DISPATCH WAS NOTIFIED OF THE INCIDENT BY THE LOCAL POLICE DEPARTMENT AT 10:53 AM. SEMCO CREWS ARRIVED, AND ONCE LOCAL FIRE PERSONNEL SECURED THE SCENE, SEMCO CREWS SECURED THE 2" PLASTIC MAIN BY 12:09 PM. REPAIRS, PURGING, AND RE-ACTIVATION OF GAS MAINS WERE COMPLETED BY 05/26/23 22:38 PM. THE FOLLOWING MORNING 05/27/23 SEMCO CREWS BEGAN RELIGHTING 26 CUSTOMERS AT 08:00 AM AND COMPLETED THE RELIGHTS BY APPROXIMATELY 11:45 AM. UPON INVESTIGATION, THE EXCAVATOR DUG USING A MINI-EXCAVATOR WITHIN THE 4' CAUTION ZONE OF THE MARKED GAS LINES WITHOUT HAND EXPOSING, RESULTING IN DAMAGE TO THE GAS LINE AND A RELEASE OF GAS. IT WAS ALSO DETERMINED THAT ALTHOUGH THE MAIN AND SERVICE LINES FEEDING THE ADDRESSED HOUSE WERE MARKED ACCURATELY, A PORTION OF MAIN LOCATED TO THE WEST OF THE SERVICE LINE WAS NOT MARKED, DUE TO A MAP ERROR. ADDITIONALLY, THE CONTRACTOR HIT AN UNDERGROUND ELECTRICAL SERVICE LINE IN THE SAME EXCAVATION WHICH WAS LIKELY THE SOURCE OF IGNITION.