## gd1986tofeb2004Fields
Gas Distribution System Incident Reports for 1986 - February 2004 (PHMSA Form 7100.1 Rev. 3-84) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | Date | Data as of date | Not on the form
SIGNIFICANT | Varchar2 | Identify if record meets the significant criteria or not: If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
RPTID | Number | PHMSA DOT assigned unique identifier for report | Top of first page
DOR | Date | Date when report was received at DOT | Top of first page
OPID | Number | Operator's OPS-issued Operator Identification number | Part 1 - General report information
NAME | Varchar2 | Operator Name | Part 1 - General report information
INADR | Varchar2 | Location of incident - Number and Street | Part 1 - General report information
ACCTY | Varchar2 | Location of incident - City | Part 1 - General report information
ACCNT | Varchar2 | Location of incident - County | Part 1 - General report information
ACCST | Varchar2 | Location of incident - State | Part 1 - General report information
ACZIP | Varchar2 | Location of incident - Zip Code | Part 1 - General report information
CLASS | Number | Class location of the incident as described in 49 CFR Section 192.5. | Part 1 - General report information
IFED | Varchar2 | Incident on Federal land (Yes/No/Null) | Part 1 - General report information
DTHH | Number | Time the incident took place | Part 1 - General report information
IDATE | Date | Date the incident occurred | Part 1 - General report information
FAT | Number | Total number of fatalities | Part 1 - General report information
INJ | Number | Total number of injured requiring inpatient hospitalization | Part 1 - General report information
TOTAL_COST | Number | Total of Property Damage/Loss | Part 1 - General report information
TOTAL_COST_IN84 | Number | Converted Property Damage to 1984 dollars uses the GDP (Chained) Price Index of FY 1984 and the year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027 | Not on the form
TOTAL_COST_CURRENT | Number | Converted Property Damage to Current Year dollars uses the GDP (Chained) Price Index of FY 2024 and the calendar year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027 | Not on the form
OPJUD | Varchar2 | Operator judgment/emergency action | Part 1 - General report information
STHH | Number | Number of hours that elapsed till area was made safe | Part 1 - General report information
STMN | Number | Number of minutes that elapsed till area was made safe | Part 1 - General report information
TELRN | Varchar2 | Report number of matching NRC telephonic report. | Part 1 - General report information
TELRT | Date | Date the incident was reported to NRC | Part 1 - General report information
INPRS | Number | Estimated pressure at point and time of incident (PSIG) | Part 1 - General report information
MXPRS | Number | Maximum allowable operating pressure (MAOP,PSIG) | Part 1 - General report information
MPEST | Varchar2 | Max allowable operating pressure was established by test or by 49 CFR, section 192.619 | Part 1 - General report information
TEST | Number | The test pressure if the MAOP was established by test | Part 1 - General report information
CAUSE | Varchar2 | Apparent cause of incident | Part 2 - Apparent cause of incident
MAP_CAUSE | Varchar2 | Cause by PHMSA for 20 year incident trending | Not on the form
MAP_SUBCAUSE | Varchar2 | SubCause by PHMSA for 20 year incident trending | Not on the form
PRTLK | Varchar2 | Part of System where incident occurred; Main, Meter Set Assembly, Service Line, Other. | Part 4 - Origin of the incident
PRTLO | Varchar2 | Text describing Other for the PRTLK field | Part 4 - Origin of the incident
PRTFL | Varchar2 | Component which failed; Body of Pipe, Valve, Joint, Regulator/meter, Fitting, Weld, Drip/Riser, Other. | Part 4 - Origin of the incident
PRTFO | Varchar2 | Text describing Other Plastic or Other for the MLKD field | Part 4 - Origin of the incident
MLKD | Varchar2 | Material involved; Steel, Cast Iron, Polyethylene plastic, Other plastic, Other | Part 4 - Origin of the incident
MLKDO | Varchar2 | Text describing Other Plastic or Other for the MLKD field | Part 4 - Origin of the incident
NMDIA | Number | Nominal Pipe Size (NPS) (diameter) in inches | Part 4 - Origin of the incident
THK | Number | Wall thickness in inches | Part 4 - Origin of the incident
SPEC | Varchar2 | Material specification | Part 4 - Origin of the incident
MANU | Varchar2 | Manufacturer | Part 4 - Origin of the incident
MANYR | Number | Year manufactured | Part 4 - Origin of the incident
PRTYR | Number | Year installed | Part 4 - Origin of the incident
LOCLK | Varchar2 | Area of Incident; Within/Under Building, Under Pavement, Above Ground, Under Ground or Under Water, Other. | Part 5 - Environment
LOCLO | Varchar2 | Text describing Other for field LOCLK | Part 5 - Environment
PNAME | Varchar2 | Incident Report Prepared by | Part 6 - Preparer and Authorized Signature
PHONE | Varchar2 | Preparer's telephone number | Part 6 - Preparer and Authorized Signature
LOC | Varchar2 | Location where corrosion occurred; Internal, External | Part A - Corrosion
ADESC | Varchar2 | Visual description of corrosion; Localized Pitting, General Corrosion, Other | Part A - Corrosion
ADESCO | Varchar2 | Text describing Other for field ADESC | Part A - Corrosion
CAUSR | Varchar2 | Cause of Corrosion; Galvanic, Other | Part A - Corrosion
CAUCO | Varchar2 | Text describing Other for field CAUCR | Part A - Corrosion
COAT | Varchar2 | Pipe Coating Information; Bare, Coated | Part A - Corrosion
PROT | Varchar2 | Was corroded part of pipeline cathodically protected? (Yes/No/Null) | Part A - Corrosion
CPYR | Number | Year Cathodic Protection Started | Part A - Corrosion
CAULK | Varchar2 | Primary cause of incident | Part B - Damage by Outside Forces
DMGO | Varchar2 | Text describing Damage by earth movement: Other for field CAULK | Part B - Damage by Outside Forces
NOTIF | Varchar2 | Did operator get prior notification that equipment would be used in the area? (Yes/No/Null) | Part B - Damage by Outside Forces
NOTDT | Date | Date when notification received | Part B - Damage by Outside Forces
MARK | Varchar2 | Was pipeline location marked either as a result of notification or by markers already in place? (Yes/No/Null) | Part B - Damage by Outside Forces
MRKTP | Varchar2 | Specify type of markers; Permanent Markers, Temporary Stakes, Other | Part B - Damage by Outside Forces
MRKTO | Varchar2 | Text describing Other for field MRKTP | Part B - Damage by Outside Forces
STAT | Varchar2 | Does a statute or ordinance require the outside party to determine whether underground facility(ies) exist? (Yes/No/Null) | Part B - Damage by Outside Forces
CAULC | Varchar2 | Cause of construction defect | Part C - Construction Defect
CAULO | Varchar2 | Text describing Other for field CAULC | Part C - Construction Defect
NARRATIVE | Varchar2 | Narrative description of factors contributing to the incident | Part 3 - Narrative description of factors contributing to the incident

## gd1986tofeb2004
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | RPTID | DOR | OPID | NAME | INADR | ACCTY | ACCNT | ACCST | ACZIP | CLASS | IFED | DTHH | IDATE | FAT | INJ | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | OPJUD | STHH | STMN | TELRN | TELRT | INPRS | MXPRS | MPEST | TEST | CAUSE | MAP_CAUSE | MAP_SUBCAUSE | PRTLK | PRTLO | PRTFL | PRTFO | MLKD | MLKDO | NMDIA | THK | SPEC | MANU | MANYR | PRTYR | LOCLK | LOCLO | PNAME | PHONE | LOC | ADESC | ADESCO | CAUSR | CAUCO | COAT | PROT | CPYR | CAULK | DMGO | NOTIF | NOTDT | MARK | MRKTP | MRKTO | STAT | CAULC | CAULO | NARRATIVE
2025-01-31 10:21 | YES | YES | 19860018 |  | 13710 | NORTHERN ILLINOIS GAS CO | 15 WEST MONROE | VILLA PARK | DU PAGE | IL | 4 | 4 | NO | 1325 | 1986-01-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 3 |  | 19860103 | 25 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | OTHER | PROCEDRE ERROR | STEEL |  | 0.75 | 0.133 | API 5L |  | 0 | 1928 | OTHER | BELL HOLE | GEORGE WALDVOGEL - GEN SUPV OPERATING | 3126292500 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION
2025-01-31 10:21 | YES | NO | 19860022 |  | 8160 | INTERMOUNTAIN GAS CO | 1925 SHOSHONE ST | BOISE | ADA | ID | 3 | 3 | NO | 135 | 1986-01-13 | 0 | 0 | 55000 | 52045.4545 | 125662.0553 | Null | 3 | 55 |  | 19860113 | 55 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1957 | UNDER PAVEMENT |  | RICHARD J COULSON - DIST OPER MGR | 2083776000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | FROST | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19860023 |  | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 2509 TULANE AVE | NEW ORLEANS | ORLEANS | LA | 3 | 3 | NO | 900 | 1986-01-13 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19860113 | 0.3 | 0.4 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 |  |  | 0 | 1938 | UNDER PAVEMENT |  | ROBERT W VAUGHAN - GAS DIST SUPT | 5045953511 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | EXPANSION & CONTRACTION | NO |  | NO | 0 |  | NO |  |  | BROKEN 6" CAST IRON MAIN - GAS MIGRATED THROUGH CRACKS IN CONCRETE AND WAS IGNITED BY SERVICE TRUCK.
2025-01-31 10:21 | YES | YES | 19860028 |  | 13840 | NORTHWEST NATURAL GAS CO | 1017 NORTH EAST BEECH ST | PORTLAND | MULTNOMAH | OR | 3 | 3 | NO | 1505 | 1986-01-01 | 1 | 0 | 800000 | 757024.7934 | 1827811.714 | Null | 0 | 20 |  | 19860102 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | METER REMOVED | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1928 | WITHIN/UNDER BUILDING |  | J F ERSPAMER - STAFF ENG | 5032264211 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE BLAST DESTROYED THIS HOME AND DID MAJOR DAMAGE TO FOUR MORE. BROKEN WINDOWSWERE PREVALENT IN A FOUR-BLOCK AREA. SEVERAL PEOPLE WERE TREATED AT LOCAL HOSPITALS, BUT NONE REQUIRED HOSPITALIZATION AS FAR AS WE KNOW. THE METER WAS FOUND SOME DISTANCE AWAY FROM ITS NORMAL LOCATION, WITH GASKETS STILL IN PLACE. THE PORTLAND FIRE AND POLICE DEPARTMENTS PRESUME THAT THE INSIDE METER WAS REMOVED BY THE DECEASED, WITH SUICIDE AS HIS MOTIVE.
2025-01-31 10:21 | NO | NO | 19860030 |  | 3500 | DOUBLE SPRINGS NATURAL GAS BOARD | HGWY 195 NORTH AND CHICKENFOOT RD |  | WINSTON | AL | 3 | 3 | NO | 1043 | 1986-01-10 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 56 |  | 19860110 | 150 | 300 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | JIMMY CHILCOAT - GAS SUPT | 2054895447 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | PART D - THE STATE HIGHWAY DEPT. WAS INSTALLING A NEW CULVERT, THEY HUNG THE GAS SERVICE LINE AND RIPPED A 1.24 HOLE IN GAS MIN AT THE TAP.
2025-01-31 10:21 | YES | NO | 19860031 |  | 13710 | NORTHERN ILLINOIS GAS CO | 1620 STRATTON POND LN | SCHAUMBURG | COOK | IL | 3 | 3 | NO | 2050 | 1986-01-27 | 0 | 0 | 150000 | 141942.1488 | 342714.6964 | Null | 3 | 10 |  | 19860127 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | F S LAWSON - GEN SUPR PRESSURE | 3127246704 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DURING THE YEAR OF 1985 A INSTALLING UNDER GROUND FACILITIES HIT AND DAMAGED A 2" GAS MAIN AT THE ABOVE ADDRESS. THIS ACCIDENT WAS NOT REPORTED TO NI-GAS AT THE TIME. SUBSEQUENTLY, A GAS LEAK RESULTED FROM THIS HIT AND IT MIGRATED INTO THEHOUSE CAUSING THE FIRE AND EXPLOSION OF 1/27/86. THIS STRUCTURE WAS NEW AND NOTOCCUPIED AT THE TIME OF THE EXPLOSION.
2025-01-31 10:21 | YES | YES | 19860034 |  | 1209 | BAY STATE GAS CO | 185 CANAL ST | LAWRENCE | ESSEX | MA | 4 | 4 | NO | 727 | 1986-01-11 | 0 | 1 | 500000 | 473140.4959 | 1142382.3212 | Null | 7 | 40 |  | 19860203 | 0.4 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | WITHIN BUILDING | OTHER | UNKNOWN | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN R SNOW - V PRES - DIV MGR | 6176871105 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE IS UNDER INVESTIGATION BY STATE AUTHORITIES, FIRE MARSHALL'S OFFICE AND LOCAL ARSON SQUAD. ORIGIN IS UNKNOWN. THE DWELLING WAS UNOCCUPIED AT THE TIME OF THE INCIDENT.
2025-01-31 10:21 | YES | YES | 19860035 |  | 4499 | ENTEX INC | 198 W GEORGRTOWN ST | CRYSTAL SPRINGS | COPIAH | MS | 3 | 3 | NO | 1510 | 1986-02-04 | 8 | 0 | 250000 | 236570.2479 | 571191.1606 | Null | 4 | 20 |  | 19860204 | 37 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | SEE PART 3 | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ALDYL-A | DUPONT | 0 | 1982 | UNDER PAVEMENT |  | J. RONALD POPE, SENIOR ENGINEER | 7136545498 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1985-07-01 | YES | 3 | YELLOW PAINT | YES |  |  | 1/2" PLASTIC SERVICE LIEN WAS CUT APPROXIMATELY 7/85 BY OUTSIDE PARTY. EXTEX PERSONNEL HAD MARKED LOCATION OF PIPE WITH YELLOW PAINT PRIOR TO EXCAVATION. OUTSIDE PARTY REPAIRED PLASTIC PIPE WITH 1/2" DRESSER TYPE COUPLING AND DID NOT NOTIFY ENTEX. SOMETIME AFTER 7/85, SERVICE LINE PULLED OUT OF COUPLING.
2025-01-31 10:21 | YES | YES | 19860036 |  | 1640 | BOSTON GAS CO | 69 LUBEC ST | EAST BOSTON | EAST BOSTON | MA | 3 | 3 | NO | 1020 | 1986-01-05 | 0 | 1 | 200000 | 189256.1983 | 456952.9285 | Null | 2 | 0 |  | 19860105 | 0.3 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 | UNK | UNK | 0 | 1935 | UNDER PAVEMENT |  | CHARLES COTTING, SUPT. DISTRIBUTION | 6173239210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | INVESTIGATION FOUND BROKEN 6" CAST IRON MAIN IN PREVIOUSLY EXCAVATED WATER TRENCH APPROXIMATELY 14 FEET FROM HOUSE #69. BROKEN CAST IRON MAIN PROBABLY DUE TO PREVIOUS EXCAVATION. GAS MIGRATED INTO CELLAR CAUSING INCIDENT. SOURCE OF IGNITION UNKNOWN.PART 2 - WE CHECKED HISTORICAL INFORMATION BACK THREE YEARS AND FOUND NO STREETOPENING PERMIT OR EXCAVATION NOTIFICATION. THE EXCAVATION MAY HAVE BEEN MADE SEVERAL YEARS AGO.
2025-01-31 10:21 | YES | YES | 19860038 |  | 18104 | SAN ANTONIO CITY PUBLIC SERVICE BOARD | 1306 W. HOLLYWOOD | SAN ANTONIO | BEXAR | TX | 3 | 3 | NO | 1117 | 1986-01-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19860113 | 7 | 33 | BY TEST | 50 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | JOINT | COMPR | STEEL |  | 1.25 | 0.14 | API 5L |  | 0 | 1947 | UNDER GROUND OR UNDER WATER |  | W. F. REICHERT JR., SENIOR ENGINEER | 5122273211 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OPERATOR'S EMPLOYEE VIOLATED SAFETY PROCEDURES CAUSING FIRE. FIRE WAS IMMEDIATELY EXTINGUISHED.
2025-01-31 10:21 | YES | YES | 19860041 |  | 8250 | IOWA ILLINOIS GAS & ELECTRIC | 2580 8TH AVENUE | MARION | LINN | IA | 3 | 3 | NO | 510 | 1986-02-13 | 0 | 2 | 47000 | 44475.2066 | 107383.9382 | Null | 7 | 35 |  | 19860213 | 28 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2.375 | 0.154 | API-5L |  | 0 | 1950 | UNDER PAVEMENT |  | RONALD R. WAIT, MANAGER, DISTRIBUTION DEPT. | 3193267105 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | AT APPROX. 5:10 A.M., THERE WAS AN EXPLOSION AND FIRE AT 2580 8TH AVENUE, MARION, IA. THERE WERE FOUR PERSONS IN THE HOUSE AT THE TIME OF THE EXPLOSION. TWO ADULTS REMAIN HOSPITALIZED AND TWO CHILDREN WERE TREATED AND RELEASED. THE APPARENT CAUSE OF THE INCIDENT WAS THE IGNITION OF GAS WHICH HAD MIGRATED INTO THE BASEMENT OF 2580 8TH AVENUE FROM A CRACK IN A 2" INTERMEDIATE PRESSURE STEEL MAIN IN26TH STREET JUST NORTH OF 8TH AVENUE. THE 2" MAIN HAD PREVIOUSLY BEEN PULLED UPAND BENT AT THE POINT OF FAILURE. IT APPEARS THAT THE PIPE WAS STRESSED BY BEING PULLED AND FAILED RECENTLY DUE TO FROST ACTION ON THE PIPE. THE ONLY OTHER UTILITY IN THE VICINITY OF THE DAMAGED PIPE WAS A WATER MAIN WHICH WAS INSTALLED IN1976.
2025-01-31 10:21 | NO | NO | 19860043 |  | 8270 | IOWA PUBLIC SERVICE CO | MAIN ST. & HWY 18 | CYLINDER | PALO ALTO | IA | 3 | 3 | NO | 2215 | 1986-01-17 | 0 | 0 | 1500 | 1419.4215 | 3427.147 | YES | 5 | 45 |  |  | 90 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | PRESSURE RECORDED LINES | STEEL |  | 0.75 | 0.154 | API-5L |  | 1967 | 1967 | ABOVE GROUND |  | THOMAS L. MITCHELL, GAS OPERATIONS ENGINEER | 7122777595 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | HIGHWAY 18 IN CYLINDER MAKES A 90 DEGREES TURN WITH FLASHING YELLOW LIGHTS. TRUCK DRIVER, DRIVING A SEMI-TRAILER TRUCK, WENT TO SLEEP. AWOKE IN TIME TO SEE FLASHING LIGHTS AND VEERED OFF TO AVOID STRIKING THEM. DRIVER STRUCK ABOVE GROUND DISTRICT REGULATING STATION. REGULATOR STATION IS APPROXIMATELY 100 FT. FROM FLASHING LIGHTS. TRUCK PASSED OVER TOP OF REGULATOR STATION AND BENT BOTH RISERS ANDSHEERED OFF THE HIGH PRESSURE AND THE INTERMEDIATE PRESSURE, PRESSURE RECORDINGLINES. THE SEMI-TRAILER STOPPED ON TOP OF REGULATOR STATION. TIME ELAPSED WAS DUE TO REMOVAL OF TRAILER AND UNTIL TEMPORARY REPAIRS COULD BE MADE.
2025-01-31 10:21 | YES | YES | 19860045 |  | 1800 | BROOKLYN UNION GAS CO | 1200 - HYLAN BLVD | STATEN ISLAND | RICHMOND | NY | 4 | 4 | NO | 1920 | 1986-02-02 | 0 | 1 | 50000 | 47314.0496 | 114238.2321 | NO | 0 | 17 |  | 19860202 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INTERIOR PIPING | OTHER |  | OTHER |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RALPH R. ROMANO, CUSTOMER SERVICE | 7184033107 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ARSON IS THE SUSPECTED CAUSE OF THE INCIDENT. A COUPLING WAS REMOVED FROM THE INTERIOR PIPING AND THE ESCAPING GAS WAS IGNITED FROM THE FIRES THAT ARE BELIEVEDTO HAVE BEEN PURPOSELY SET.
2025-01-31 10:21 | NO | NO | 19860046 |  | 792 | ATLANTA GAS LIGHT CO | 2080 COOPER LAKE DR. | SMYRNA | COBB | GA | 3 | 3 | NO | 1050 | 1986-02-20 | 0 | 0 | 45000 | 42582.6446 | 102814.4089 | YES | 0 | 34 |  | 19860221 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | BEYOND OPERATOR'S FACILIT | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL LAWSON, SUPT. | 4044249000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE SERVICE LINE TO THIS RESIDENCE WAS DISCONNECTED AND AIR TESTED WITH 62# OF PRESSURE FOR ONE HOUR AND TEN MINUTES. THERE WAS NO LEAK ON SERVICE LINE. BAR HOLES WERE DRIVEN ABOVE THE MAIN AT THIS LOCATION. THE BAR HOLES WERE CHECKED WITH A COMBUSTIBLE GAS INDICATOR. NO GAS WAS DETECTED WITH THE COMBUSTIBLE GAS INDICATOR.
2025-01-31 10:21 | YES | YES | 19860047 |  | 12684 | MONTANA - DAKOTA UTILITIES CO | EAST OF CITY | BOWMAN | BOWMAN | ND | 3 | 3 | NO | 1342 | 1986-02-11 | 0 | 2 | 20000 | 18925.6198 | 45695.2928 | Null | 1 | 30 |  | 19860211 | 38 | 40 | BY CFR 192.619(A)(3) | 1 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | K.L. LEGGATE, GAS SUPT. | 7012270141 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INCIDENT STILL UNDER INVESTIGATION - CAUSE UNKNOWN
2025-01-31 10:21 | YES | YES | 19860048 |  | 17620 | ROCKY MOUNTAIN NATURAL GAS CO | 778 SOPRIS AVE | CARBONDALE | GARFIELD | CO | 3 | 3 | NO | 1420 | 1986-02-13 | 0 | 1 | 100000 | 94628.0992 | 228476.4642 | Null | 18 | 20 |  | 19860305 | 25 | 66 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | OTHER | VALVE | VALVE |  | STEEL |  | 2 | 0 | FIG-149 | EMCO-NORDSTORM | 0 | 1961 | OTHER | VALVE W/BOX UNDER CONCRET | WILLARD CLAPPER, SAFETY DIRECTOR | 3039458618 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | FROZEN WATER IN VALVE BOX SEEMS TO HAVE ACCUMULATED AND PRESSURE DOWN ON TOP OFVALVE BROKE THE BODY NEXT TO OUTGOING FLANGE. BECAUSE OF FROZEN GROUND AND CEMENT STREET COVER, THE GAS COULD NOT COME TO THE SURFACE AND DISSIPATE. THE ORDOR ALSO WAS REMOVED FROM THE GAS FROM THE FROZEN GROUND, AND WE DID NOT RECEIVE "GAS LEAK" CALLS. ONLY AFTER ARRIVING ON THE SCENE AND SEEING WHAT HAPPENED DID WE KNOW OF A POSSIBLE GAS LEAK. ADDITIONAL INFORMATION CONTAINED IN LETTER.
2025-01-31 10:21 | YES | NO | 19860050 |  | 15469 | PHILADELPHIA GAS WORKS | 4635 NORTH 10TH ST. | PHILADELPHIA | PHILADELPHIA | PA | 4 | 4 | NO | 2315 | 1986-02-14 | 0 | 0 | 80000 | 75702.4793 | 182781.1714 | Null | 1 | 5 |  | 19860215 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 1 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | WELD | GIRTH | STEEL |  | 4 | 0.237 |  |  | 0 | 1926 | UNDER PAVEMENT |  | DANIEL VALE, MANAGER | 2159783372 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | ON FEB. 14, 1986 AT 9:45 P.M. PGW RECEIVED A CALL FROM A CUSTOMER AT 4631 NORTH10TH ST. REPORTING AN ODOR INSIDE (LIVING ROOM). A SERVICEMAN WAS DISPATCHED AT 9:53 P.M. AND FOUND FOUR HOMES WITH A READING OF 100% AT THE FRONT FOUNDATION WALLS. THE SERVICEMAN CALLED FOR ASSISTANCE AND CONTINUED HIS INVESTIGATION. ASECOND SERVICEMAN ARRIVED ON THE JOB AT 11:00 P.M. THE SERVICEMEN ATTEMPTED TOGAIN ENTERACE TO 4635 NORTH 10TH ST; HOWEVER, THERE WAS NO ONE HOME. THEY THENSTARTED TO FORCE ENTRY BY REMOVING THE BASEMENT WINDOW UNDER THE FRONT PORCH WHEN THE EXPLOSION OCCURRED.
2025-01-31 10:21 | NO | NO | 19860052 |  | 20211 | UNITED CITIES GAS CO | FIELD 600 NORTH OF ROSS RD |  | BARROW | GA | 2 | 2 | NO | 1704 | 1986-02-26 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 50 |  |  | 560 | 610 | BY CFR 192.619(A)(3) | 1 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8.62 | 0.188 | API 5LB | L.B. FOSTER | 1966 | 1966 | UNDER GROUND OR UNDER WATER |  | RICHARD SCHWARTZ, MANAGER | 4045343655 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | POULTRY FARMER WAS DIGGING A LARGE HOLE TO BURY TRASH OR ETC. THE LARGE FRONT END LOADER RAN INTO AND DAMAGED PIPE WHILE DIGGING APPROXIMATELY FOUR FEET DEEP.
2025-01-31 10:21 | YES | YES | 19860053 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | 10358 S. TRUMBULL | CHICAGO | COOK | IL | 3 | 3 | NO | 130 | 1986-02-19 | 0 | 1 | 65000 | 61508.2645 | 148509.7018 | Null | 4 | 30 |  | 19860219 | 20 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 |  |  | 0 | 1941 | WITHIN/UNDER BUILDING |  | MARTIN MCDONNELL, DISTRICT SUPT. | 3129624840 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | GAS LEAKING FROM A CRACKED 6" CAST IRON MEDIUM PRESSURE GAS MAIN MIGRATED INSIDE A BUILDING WHICH WAS DESTROYED BY AN EXPLOSION.THE SOURCE OF IGNITION IS UNKNOWN
2025-01-31 10:21 | NO | NO | 19860054 |  | 11800 | LOUISIANA GAS SERVICE CO | 4909 PONTCHARTRAIN DR. | SLIDELL | ST TAMMANY | LA | 3 | 3 | NO | 110 | 1986-02-15 | 0 | 0 | 5000 | 4731.405 | 11423.8232 | Null | 1 | 20 |  |  | 80 | 100 | BY CFR 192.619(A)(3) | 1 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | D. L. MERIWETHER, DIRECTOR OF TECHNICAL STANDARDS | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER INSTALLATION | NO |  |  | AUTOMOBILE RAN OVER GAS METER CAUSING GAS TO IGNITE. THE RESULTING FIRE COMPLETELY DESTROYED AUTOMOBILE AND CAUSED SOME DAMAGE TO SIDE OF HOUSE. METER REGULATOR INSTALLATION WAS ON PRIVATE PROPERTY AND OPERATOR OF VEHICLE DROVE OFF HIGHWAY STRIKING INSTALLATION.
2025-01-31 10:21 | NO | NO | 19860055 |  | 11800 | LOUISIANA GAS SERVICE CO | 3709 WEST METAIRIE | METAIRIE | JEFFERSON | LA | 3 | 3 | NO | 2230 | 1986-02-20 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 75 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER |  | OTHER |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | D. L. MERIWETHER, DIRECTOR OF TECHINCAL STANDARDS | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER TURNED OVEN ON AND DIDN'T LIGHT BURNER. APPROXIMATELY 2 OR 3 MINUTES LATER, THE CUSTOMER OPENED OVEN DOOR AND LIT A MATCH CAUSING EXPLOSION AND FLASHBACK. THE CUSTOMER DIDN'T DETECT ANY GAS ODOR. LATER TESTS PROVED THAT ODORANTCONCENTRATION IN THE GAS WAS INSUFFICIENT.
2025-01-31 10:21 | YES | YES | 19860061 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | EAST 4TH ST & AVENUE A | NEW YORK |  | NY | 4 | 4 | NO | 1022 | 1986-03-04 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19860304 | 0.2 | 0.4 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN - MAIN ABANDONED | CAST IRON |  | 6 | 0.375 |  |  | 0 | 1884 | OTHER | ELECTRIC MANHOLE | DOMINIC CASTELLANO - ACTING CHIEF GAS ENG | 2124604464 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS LEAKING FROM A 6" CAST IRON MAIN MIGRATED INTO AN ELECTRIC MANHOLE AND WAS IGNITED BY AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | NO | 19860062 |  | 4350 | ELIZABETHTOWN GAS CO | 512 PARK AVE | SCOTCH PLAINS | UNION | NJ | 1 | 1 | NO | 245 | 1986-02-25 | 0 | 0 | 750000 | 709710.7438 | 1713573.4819 | Null | 0 | 30 |  | 19860225 | 0.2 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD RAPOLAS - GEN MGR C&M | 2012895000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PART 2 - VALVE AT METER SET WAS DELIBERATELY OPENED BY UNKNOWN PERSON(S) TO CREAT FIRE (EXPLOSION).PART 3 - INVESTIGATION BY ARSON SQUAD UNDERWAY.
2025-01-31 10:21 | YES | YES | 19860063 |  | 13710 | NORTHERN ILLINOIS GAS CO | 204 W 14TH ST (RT 30) | CHICAGO HEIGHTS | COOK | IL | 3 | 3 | NO | 800 | 1986-03-13 | 1 | 1 | 250000 | 236570.2479 | 571191.1606 | Null | 0 | 45 |  | 19860313 | 28 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SLEEVE | STEEL |  | 0.75 | 0.118 | API STD 5L |  | 0 | 0 | UNDER PAVEMENT |  | C POWERS - GEN SUPV | 3127560450 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-03-07 | YES | 3 | YELLOW PAINT ON BLACKTOP | YES |  |  | ALPHA CONSTRUCTION WAS INSTALLING A WATER MAIN ON THE SOUTH SIDE OF 14TH ST (RTE 30), CHICAGO HEIGHTS, ILL. A BACKHOE WAS DIGGING A TRENCH IN FRONT OF 204 W 14TH ST WHEN THE 3/4" SERVICE TO 204 WAS HIT AND PULLED UP ABOUT 1 FT CAUSING THE PIPE TO PULL OUT OF A 3/4" COUPLING NEAR THE HOUSE. THE CONTRACTOR NOTIFIED NI-GAS AND NI-GAS CREWS WERE IMMEDIATLY DISPATCHED. AS THE GAS WAS BEING SHUT OFF AT204 THE BUILDING EXPLODED. ALSO DAMAGED BY EXPLOSION AND FIRE WERE THE HOUSES ON EACH SIDE. ONE PERSON, A RESIDENT AT 204, WAS KILLED. EIGHT OTHER PEOPLE WERE INJURED, THE MOST SERIOUS INJURY WAS A BROKEN LEG.
2025-01-31 10:21 | YES | YES | 19860065 |  | 22763 | WISCONSIN GAS CO | 1506 19TH ST | BRODHEAD | GREEN | WI | 3 | 3 | NO | 2257 | 1986-02-19 | 0 | 2 | 0 | 0 | 0 | Null | 25 | 45 |  | 19860221 | 58 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | 2306 |  | 0 | 1969 | UNDER PAVEMENT |  | R H HOLDER - PE VP & CHIEF ENG | 4142916700 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EXPLOSION AT 1506 19TH ST RESULTED IN INJURY REQUIRING INPATIENT HOSPITALAZATION OF TWO PERSONS. THE HOME WAS NOT SERVED BY NATURAL GAS. PROPERTY DAMAGE WASESTIMATED AT $40,000. AN INVESTIGATION OF THIS INCIDENT TO DATE, HAS REVEALED THAT A LEAK EXISTED ON THE UNDERGROUND 5/8 PLAS NATURAL GAS LINE LEADING TO 1503 19TH ST, THE PROPERTY ON THE OTHER SIDE OF THE STREET OF THE AFFECTED PROPERTY.ALSO, A LEAK HAS BEEN DISCOVERED ON THE UNDERGROUND LP GAS LINE LEADING TO 150619TH ST. FURTHER INVESTIGATION IS ONGOING IN AN EFFORT TO DETERMINE WHICH LEAKING FUEL OR IF BOTH FUELS CONTRIBUTED TO THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 19860066 |  | 20050 | UNION ELECTRIC CO | 320 EAST RAILROAD | CENTRALIA | BOONE | MO | 3 | 3 | NO | 1440 | 1986-01-03 | 0 | 0 | 53000 | 50152.8926 | 121092.5261 | Null | 0 | 15 |  | 19860103 | 47 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.76 |  |  | 1932 | 1932 | UNDER GROUND OR UNDER WATER |  | WILLIAM LUEBBERT, SUPERVISING ENGINEER | 3146350171 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19860068 |  | 17620 | ROCKY MOUNTAIN NATURAL GAS CO | MAIN & DAVIS ST. | TELLURIDE | SAN MIGUEL | CO | 3 | 3 | NO | 1100 | 1986-03-27 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 5 |  |  | 0 | 0 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | CLAMP | POLYETHYLENE PLASTIC |  | 3 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | WILLARD CLAPPER, SAFETY DIRECTOR | 3039458617 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EQUIPMENT FAILURE ALLOWED MORE GAS THAN NORMAL INTO TRENCH - L.P. HEAVIER THAN AIR AND FILLED TRENCH AND OVERCAME 2 PERSONS.NEED TO MOVE 1 - 2" P.E. LINE AND 1 - 3" P.E. LINE. THE 2" LINE CLAMPED LOWERED AND ALL O.K. 3" SQUEEZE-OFF CLAMPS FAILED TO HOLD FULL PRESSURE AND ALLOWED EXTRA GAS INTO TRENCH WHICH CAUSED THE LACK OF OXYGEN THAT OVERCAME THE TWO EMPLOYEES - BOTH ARE FINE NOW - TAKEN TO HOSPITALS AS A PRECAUTIONARY MEASURE. 1 - GRAND JUNCTION, 1 - MONTROSE - 2 OTHERS TREATED AT LOCAL CLINIC AND RELEASED. LINES WERE PLUGGED AND MADE SAFE PRIOR TO EMPLOYEES LEAVING THE AREA.
2025-01-31 10:21 | YES | NO | 19860069 |  | 13041 | NASHVILLE GAS CO | 505 DONELSON PIKE | NASHVILLE | DAVIDSON | TN | 3 | 3 | NO | 430 | 1986-03-26 | 0 | 0 | 400000 | 378512.3967 | 913905.857 | Null | 1 | 10 |  | 19860326 | 87 | 125 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.133 | API5L | US STEEL | 1968 | 1968 | WITHIN/UNDER BUILDING |  | W. RAY CULP, VICE PRESIDENT OF OPERATIONS | 6152447080 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION OF UNKNOWN ORIGIN BLEW OUT WALLS ON MIKE'S DELI AND GAME ROOM. CONCRETE ROOF FELL DOWN BREAKING GAS METER AND CRACKING SERVICE RISER PIPE AT VALVE.NO FIRE INVOLVED. SERVICE WAS SQUEEZED OFF BELOW RISER VALVE. AREA SURVEYED WITH FLAME PACK WITH NO SIGN OF GAS LEAKAGE. METRO GOVERNMENT BOMB & ARSON UNITS ARE INVESTINGATING SUSPICIOUS EXPLOSION.
2025-01-31 10:21 | NO | NO | 19860070 |  | 19641 | TRI - COUNTY NATURAL GAS | HWY 77 NORTH | UNION POINTE | GREENE | GA | 1 | 1 | NO | 1605 | 1986-03-17 | 0 | 0 | 13000 | 12301.6529 | 29701.9404 | YES | 0 | 45 |  | 19860317 | 300 | 600 | BY TEST | 900 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0.45 | 0.188 | API 5LG | PITTSBURG STEEL | 1963 | 1963 | UNDER GROUND OR UNDER WATER |  | RICHARD WARE, MANAGER | 4044864102 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-03-14 | YES | 2 |  | NO |  |  | CONSTRUCTION CO. WAS PLOWING TELEPHONE CABLE IN STATE ROUTE 77 RIGHT-OF-WAY. MAIN WAS RUPTURED BY PLOW FOOT PENETRATING 4" MAIN HIGH PRESSURE DISTRIBUTION LINE. PROPER LINE LOCATION AND VERIFICATION WAS NOT ADEQUATE. APPROXIMATELY 400' OF MAIN WAS DAMAGED WHERE PLOW FOOT SCRAPED SIDE WALL OF PIPE - ALLEN C. FOYD CONST. CO. MADE TEMPORARY AND PERMANENT REPAIRS.
2025-01-31 10:21 | YES | YES | 19860072 |  | 3170 | DAYTON POWER & LIGHT CO | MAIN & DETROIT | BELLEFONTAINE | LOGAN | OH | 3 | 3 | NO | 1030 | 1986-03-04 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 0 |  | 19860304 | 35 | 40 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.179 |  |  | 0 | 0 | UNDER PAVEMENT |  | STEPHEN P. BRAMLAGE, MANAGER | 5135931070 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | WEATHER CONDITIONS, I.E., ICING OF METER-REGULATOR ASSEMBLY, MAY HAVE ADVERSELYAFFECTED PRESSURE REGULATOR OPERATION, ALLOWING HIGH PRESSURE GAS TO ENTER COSTOMER'S GAS PIPING AND APPLICANCES. APPLIANCE REGUALTOR FAILED, RESULTING IN FIRE AND PROPERTY DAMAGE.
2025-01-31 10:21 | NO | NO | 19860073 |  | 22777 | WISCONSIN NATURAL GAS CO | 618 RANDOLPH ST | RACINE | RACINE | WI | 3 | 3 | NO | 1520 | 1986-02-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  |  | 58 | 60 | BY TEST | 102 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 | S 254 | FISHER | 1975 | 1975 | WITHIN/UNDER BUILDING |  | RONALD K ESPE - ASST V P | 4146377681 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FREEZING WEATHER, ICING OF METER ASSEMBLY, AND/OR APPLIANCE FAUILURE MAY HAVE CONTRIBUTED TO INCIDENT.
2025-01-31 10:21 | YES | YES | 19860074 |  | 4510 | EQUITABLE GAS CO | 5240 STANTON AVE | PITTSBURGH | ALLEGHENY | PA |  | 0 | NO | 1900 | 1986-03-20 | 0 | 2 | 600000 | 567768.595 | 1370858.7855 | Null | 0 | 15 |  | 19860320 | 10 | 14 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 3 | 0.216 |  |  | 0 | 1950 | WITHIN/UNDER BUILDING |  | E. F. MOSES, JR., MANAGER OF TECHNICAL SERVICES DEPT. | 4125535340 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | INVESTIGATION OF THE EXPLOSION INDICATES THAT THE CUSTOMERS' SERVICE LINE, CURBTO METER, WAS CORRODED AND LEAKING. A SECTION OF THE HOUSE LINE WAS CRACKED ANDLEAKING. THE HOUSE LINE WAS LOCATED BETWEEN THE FLOOR JOISTS SEPARTING THE FLOOR OF THE SECOND FLOOR APARTMENT AND THE CEILING OF THE FIRST FLOOR APARTMENT. CAUSE OF INCIDENT IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19860075 |  | 4020 | EAGLE PASS NATURAL GAS CORP | 600 BLK COLORADO ST. | EAGLE PASS | MAVERICK | TX | 3 | 3 | NO | 1850 | 1986-03-18 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 0 |  | 19860319 | 6 | 20 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.25 |  |  | 0 | 1946 | OTHER | SEWER MANHOLE | CARLTON E. KELLY, GEN. MANAGER | 5127739497 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EXPLOSION OCCURRED IN A SEWER MANHOLE ON MARCH 18, 1986, ABOUT 6:50 P.M. ANDA LITTLE BOY WAS BURNED ON THE FACE AND AROUND THE EYES. THE BOYS MOTHER RUSHED HIM TO THE HOSPITAL AND DIDN'T NOTIFY ANYONE. THE NEXT BY, MY OFFICE WAS NOTIFIED OF THE ACCIDENT AROUND 11:00 A.M. AND ENRIQUE GARCIA AND ARTURO CARDENAS, EMPLOYEES OF EAGLE PASS NATURAL GAS CORP. WERE SENT TO INVESTIGATE. MR. GARCIAREPORTED A SMALL AMOUNT OF GAS IN THE MANHOLE ON COLORADO ST. AND A LOT OFSTRUCK MATCHES BY THE MANHOLE, NO OTHER GAS WAS FOUND ALONG THAT AREA. THEGAS FOUND IN THE MANHOLE HAD COME FROM A LEAK ON A SIX INCH MAIN LOCATEDON FERRY ST. HALF A BLOCK AWAY FROM THE MANHOLE. THIS LEAK WAS DUGOUT ANDVENTED. I WAS IN AUSTIN AT THE TIME OF THE ACCIDENT AND I WAS NOTIFIED OFIT BY MY OFFICE MANAGER ABOUT 12:00 NOON MARCH 19, 1986. I CALLED THE RAIL-ROAD COMMISSION AT 1:00 P.M. AND REPORTED THE ACCIDENT AS REQUIRED BY LAW. IRETURNED TO EAGLE PASS THAT AFTERNOON AND MR. LEE SMITH FROM THE TEXASRAILROAD COMMISSION WAS HERE BRIGHT AND EARLY ON MARCH 20, 1986 TO INVESTI-GATE THE ACCIDENT.
2025-01-31 10:21 | NO | NO | 19860076 |  | 4473 | ENERGAS CO | 714 OAK | DALHART | DALLAM | TX | 3 | 3 | NO | 400 | 1986-03-19 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 30 |  | 19860319 | 0.5 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER LINE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE. STATE FIRE INSPECTOR DECLARED ARSON AS CAUSE.
2025-01-31 10:21 | YES | NO | 19860079 |  | 22189 | WASHINGTON NATURAL GAS CO | 1801 16 AVE. S.W. | SEATTLE | KING | WA | 3 | 3 | NO | 1530 | 1986-03-29 | 0 | 0 | 100000 | 94628.0992 | 228476.4642 | Null | 0 | 30 |  | 19860329 | 25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | COST ALUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DOUGLAS DAMM, SAFETY MANAGER | 2066226767 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TODD SHIPYARD CORP. SUBCONTRACTOR CONNECTED 100 PSI PURE OXYGEN LINE TO 25 PSI NATURAL GAS LINE IN ERROR, CREATING COMBUSTABLE MIXTURE IN SHIPYARD FUEL LINE. IGNITION PROBABLY CAUSED BY OXYGEN CONTACTING OIL IN PIPE. THREE LARGE GAS METERS OWNED BY OPERATOR WERE DESTROYED BY EXPLOSION. SEVERAL OTHER POINTS OF FAILURE/EXPLOSION OCCURRED IN SHIPYARD GRID.
2025-01-31 10:21 | YES | NO | 19860084 |  | 18532 | SOUTHERN UNION GAS CO | 11300 BLK OF JOLLYVILLE RD. | AUSTIN | TRAVIS | TX | 3 | 3 | NO | 1602 | 1986-01-21 | 0 | 0 | 300000 | 283884.2975 | 685429.3927 | YES | 3 | 18 |  | 19860121 | 225 | 0 | BY TEST | 600 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | API-5LX-42 |  | 0 | 1982 | NO DATA |  | GILES GOVER, ENGINEER | 5124475981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-01-03 | YES | 3 | PAINT | NO |  |  | CONTRACTOR TRENCHED INTO THE PIPE AND PUNCTURED IT. GAS IGNITED AND TRAFFIC WASREROUTED. LOCATION REQUEST WAS MADE BY ANOTHER CONTRACTOR WHO PLANNEDTO WORK IN THE AREA.
2025-01-31 10:21 | YES | YES | 19860085 |  | 18532 | SOUTHERN UNION GAS CO | 226 CANDELARIA | EL PASO | EL PASO | TX | 3 | 3 | NO | 530 | 1986-03-03 | 0 | 1 | 20000 | 18925.6198 | 45695.2928 | Null | 2 | 30 |  | 19860303 | 23 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | ABS | 2 | 0.9 |  |  | 0 | 1963 | UNDER PAVEMENT |  | H.E. SMITH, JR., P.E., DISTRICT ENGINEER | 9155446300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1985-11-01 | NO | 0 |  | NO |  |  | A 2" ABS PLASTIC PIPELINE FRACTURED ON THE LOWER 120' OF THE PIPE'S CIRCUMFERENCE. GAS MIGRATED THROUGH AN IMPROPERLY COMPACTED WATER MAIN TRENCH THROUGH STRATA OF CLAY AND SANDY LOAM. THE GAS MIGRATED UNDER AND INTO AN ADOBE RESIDENCE AT 226 CANDALARIA IN THE LOWER VALLEY OF EL PASO, TX. THE GAS WAS IGNITED WHEN THE OCCUPANT LIT HIS KITCHEN STOVE. THE STRUCTURE WAS COMPLETELY DESTROYED.THE RESIDENCE WAS OCCUPIED BY MR. GEORGE GANDARA, HIS WIFE, AND THREE CHILDREN. MRS. GANDARA AND HER CHILDREN WERE TREATED IN AN OUTPATIENT CLINIC AND RELEASED THE DAY OF THE INCIDENT. MR. GANDARA SUBSTAINED A BROKEN FEMUR AND FIRST AND SECOND DEGREE BURNS TO TWENTY -FIVE PERCENT OF HIS BODY. MR. GANDARA IS PRESENTLY IN STABLE CONDITION AND APPEARS TO BE RECOVERING.
2025-01-31 10:21 | YES | YES | 19860087 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 100 EAST OF 6TH & MAIN | TUPELO | COAL | OK | 3 | 3 | NO | 1930 | 1986-04-11 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 0 |  | 19860411 | 8 | 12 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN | UNKNOWN | OTHER |  | STEEL |  | 2 | 0.125 |  |  | 0 | 0 | OTHER | END OF CULVERT | JOHN NORTH, MANAGER, CONSTRUCTION & MAINTENANCE | 4054826315 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SPECIFIC LEAK WAS NOT EXPOSED. POUNDS PRESSURE GAS LINE WAS REPLACED IN ANOTHER LOCATION. OUNCE GAS LINE WAS RETIRED.
2025-01-31 10:21 | YES | YES | 19860089 |  | 11680 | LONE STAR GAS CO | MCFARLING | ANNONA | RED RIVER | TX | 1 | 1 | NO | 1400 | 1986-03-07 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 2 |  | 19860307 | 5 | 10 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR-11 | PLEXCO | 1985 | 1986 | UNDER GROUND OR UNDER WATER |  | DOYLE W. HAYS | 2147843339 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA |  | THREE MEN MAKING A SERVICE TAP AND 2 IN BELL HOLE WERE BURNED
2025-01-31 10:21 | YES | NO | 19860090 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 703 MONTROSE ST. | RIALTO | SAN BERNARDINO | CA | 3 | 3 | NO | 1640 | 1986-03-25 | 0 | 0 | 70000 | 66239.6694 | 159933.525 | Null | 0 | 40 |  | 19860326 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | AP1 STD 5L |  | 1983 | 1984 | ABOVE GROUND |  | J. L. LUCAS, MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19860091 |  | 13710 | NORTHERN ILLINOIS GAS CO | 538 NORTH AVE. | GLENDALE HEIGHTS | AURORA | IL | 3 | 3 | NO | 2118 | 1986-04-08 | 0 | 1 | 20000 | 18925.6198 | 45695.2928 | Null | 0 | 17 |  | 19860415 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | GEORGE WALDVOGEL, GENERAL SUPR OPERATING | 3126292500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ARTHUR MARTIN, DRIVER OF THE VEHICLE, APPARENTLY THOUGHT A DRIVEWAY EXISTEDOFF OF NORTH AVENUE. HE TRAVELED THROUGH THE PARKWAY AND STRUCK THE METER SETAT PORTILLO'S RESTAURANT, 538 1/2 NORTH AVENUE, GLENDALE HEIGHTS. THE ACCIDENTDAMAGED THE GAS METER SET, RESULTING IN A FIRE THAT CAUSED DAMAGE TO PORTILLO'SBUILDING. MR. MARTIN SUFFERED BURNS ON HIS LEFT FOREARM AND WAS TAKEN TOGLENDALE HEIGHTS HOSPITAL.
2025-01-31 10:21 | NO | NO | 19860092 |  | 13710 | NORTHERN ILLINOIS GAS CO | 16108 PARK AVE. | MARKHAM | COOK | IL | 3 | 3 | NO | 2023 | 1986-04-15 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 2 | 52 |  | 19860415 | 28 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | OTHER | PLASTIC/ALUMINUM COMPOSIT | 0.625 | 0.09 | TRIPLE-DEK | EATON CORP. | 1983 | 1984 | ABOVE GROUND |  | RICHARD FORSYTHE, MANAGER DIVISION MAINT. | 3127560450 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE OF UNKNOWN CAUSE COMPLETELY DESTROYED VACATED HOUSE AND DETACHED GARAGE. THE HEART OF THE FIRE CAUSED THE SERVICE TO RUPTURE BELOW THE CLOSED AND LOCKED OFF SERVICE VALVE AND IGNITED THE ESCAPING 28 PSI GAS.
2025-01-31 10:21 | YES | YES | 19860094 |  | 11680 | LONE STAR GAS CO | 100 EAST LANCASTER | FORT WORTH | TARRANT | TX | 4 | 4 | NO | 1008 | 1986-03-12 | 0 | 19 | 1000 | 946.281 | 2284.7646 | Null | 1 | 4 |  | 19860312 | 22 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0 | 0 |  |  | 0 | 1940 | UNDER PAVEMENT |  | W C DEUBLER - C & M SUPERVISOR III | 8173368381 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-02-19 | YES | 3 | PAINT ON PAVEMENT | NO
2025-01-31 10:21 | YES | YES | 19860095 |  | 14210 | OKLAHOMA NATURAL GAS CO | ANGELA DR / DOUGLAS BLVD | MIDWEST CITY | OKLAHOMA | OK | 3 | 3 | NO | 1450 | 1986-04-09 | 0 | 2 | 0 | 0 | 0 | Null | 2 | 30 |  | 19860414 | 220 | 275 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR SETTING | JOINT | THREADED | STEEL |  | 1 | 0.133 | API 5L |  | 0 | 1963 | ABOVE GROUND |  | DC WALKER - ENG OPER | 4055281401 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PART 3 - VEHICLE CAUSING DAMAGE HAD BEEN INVOLVED IN A VEHICLE ACCIDENT IMMEDIATELY PRIOR TO THIS INCIDENT. IN AN ATTEMPT TO FLEE THE SCENE OF THE ACCIDENT, THE VEHICLE RAN INTO THE REGULATOR SETTNG - RESULTING IN A FIRE.PART 1-6 - INITIAL REPORTS FROM THE FIELD WERE THAT THE TWO INJURIED PARTIES WERE TREATED AND RELEASED. NO OTHER REASON EXISTED TO REQUIRE A TELEPHONIC REPORT.UPON LEARNING ON APRIL 14, THAT THE INJURED HAD BEEN ADMITTED TO HOSPITAL CONFINEMENT, WE IMMEDIATELY MADE THE REQUIRED REPORT.
2025-01-31 10:21 | YES | NO | 19860096 |  | 8070 | INDIANA GAS CO INC | 6722 SOUTH MADISON AVE | ANDERSON | MADISON | IN | 2 | 2 | NO | 2015 | 1986-04-25 | 0 | 0 | 80000 | 75702.4793 | 182781.1714 | Null | 0 | 30 |  | 19860425 | 40 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.154 | API 5L |  | 1957 | 1957 | UNDER GROUND OR UNDER WATER |  | PHILIP A GURLEY | 3179270575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | BACKHOE STRUCK SERVICE LINE AND BROKE SERVICE AT SERVICE LINE RISER AT OUTSIDE METER SET.
2025-01-31 10:21 | YES | YES | 19860098 |  | 792 | ATLANTA GAS LIGHT CO | VERMACK RD @ CANDICE COURT | DUNWOODY | DE KALB | GA | 2 | 2 | NO | 1515 | 1986-04-18 | 0 | 3 | 185000 | 175061.9835 | 422681.4589 | Null | 6 | 12 |  | 19860418 | 60 | 60 | BY TEST | 114 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2.37 | 0.216 | PE 2306 | PLEXICO | 1986 | 1986 | UNDER PAVEMENT |  | FRANK W LAWRENCE - ENG | 4045844240 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-04-14 | YES | 0 |  | YES |  |  | CONTRACTOR MAKING ROAD BORE STRUCK GAS MAIN. ESCAPING GAS WAS APPARENTLY IGNITED BY FIRE TRUCK RESPONDING TO THE INCIDENT.
2025-01-31 10:21 | YES | YES | 19860100 |  | 2748 | CONSUMERS POWER CO | 324 WEST CAPITAL | BELLEVUE | EATON | MI | 3 | 3 | NO | 1412 | 1986-05-05 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 2 |  | 19860505 | 30 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | COMPRESSION | STEEL |  | 2 | 0.154 |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | D V VOIGT - MGR OF GAS OPER | 5177882250 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-03-25 | YES | 3 | PAINTED ON GROUND | YES |  |  | SEWER CONTRACTOR BROKE GAS MAIN WITH BACKHOE. FACILITIES WERE LOCATED. SUSPECT CIGARETTE AS SOURCE OF IGNITION.
2025-01-31 10:21 | NO | NO | 19860109 |  | 8270 | IOWA PUBLIC SERVICE CO | RR - EAST OF MAIN ST | BOYDEN | SIOUX | IA | 3 | 3 | NO | 2105 | 1986-04-11 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 25 |  |  | 50 | 50 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | DISTRICT REGULATOR STATIO | FITTING |  | STEEL |  | 4 | 0.25 | API 5L |  | 1954 | 1954 | ABOVE GROUND |  | THOMAS L MITCHELL - GAS OPER ENG | 7122777595 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | SEMI-TRUCK TRAILER BECAME DETACHED FROM TRACTOR AND TIPPED OVER ON ABOVE GROUNDREGULATOR STATION BREAKING OFF GAUGE LINES. EMERGENCY ACTION WAS NECESSARY TO CLEAR AREA.
2025-01-31 10:21 | YES | YES | 19860110 |  | 3240 | DELMARVA POWER & LIGHT CO | 116 LOCUST AVE | WILMINGTON | NEW CASTLE | DE | 3 | 3 | NO | 255 | 1986-03-28 | 0 | 1 | 75000 | 70971.0744 | 171357.3482 | Null | 1 | 10 |  | 19860328 | 30 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | GAS RANGE | OTHER | RANGE CONNECTOR | OTHER | BRASS | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  |  | 0000000000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT ABOUT 2:55 AM ON MARCH 28, 1986, MRS. CATHERINE HUBER, AGE 43, ATTEMPTED TO LIGHT A RANGE TOP BURNER WITH A MATCH. THERE WAS AN EXPLOSION AND MRS. HUBER WASBLOWN INTO THE SIDE YARD. SHE SUFFERED 2ND DEGREE BURNS OVER THE TOP PART OF HER BODY AND WAS HOSPITALIZED IN SERIOUS CONDITION. THREE OTHER PEOPLE IN THE HOUSE ESCAPED WITH NO INJURIES. MRS. HUBER HAS BEEN RELEASED FROM THE HOSPITAL. MRS.HUBER REPORTED USING A MATCH TO LIGHT THE BURNER BECAUSE THE PILOT LIGHT HAD NOT WORKED FOR SOMRTIME. THE FLEXIBLE RANGE CONNECTOR WAS FOUND TO HAVE A SMALL HOLE AND A CRACK IN IT. INVESTIGATIONS WITH COMBUSTIBLE GAS INDICATOR AND FLAME IONIZATION UNIT DID NOT DETECT ANY GAS IN THE BASEMENT, FOUNDATION WALL, AREA AROUND THE OUTSIDE OF THE HOME OR SEWER. GAS WAS NOT ENTERING THE BUILDING FROM THE UNDERGROUND DISTRIBUTION SYSTEM. TWO FITTINGS AT THE METER REGULATOR CONNECTIONSWERE BROKEN BY FALLING DEBRIS AND THE METER TOP AND REGULATOR TOP WERE MELTED BY FIRE. IT APPEARS AS THOUGH GAS WAS LEAKING FROM THE RANGE CONNECTOR AND A FAULTY RANGE AND WAS IGNITED WHEN A MATCH WAS USED TO LIGHT THE RANGE BURNER.
2025-01-31 10:21 | NO | NO | 19860111 |  | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | 1504,1506,1508 HYATT ST | COLUMBIA | RICHLAND | SC | 3 | 3 | NO | 242 | 1986-04-11 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 1 | 10 |  | 19860411 | 25 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SHERMAN J GOODWIN | 8037483781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE ORIGIN OF THE FIRE APPEARS TO HAVE BEEN WITH AN IGNITION SOURCE INSIDE OF THE BUILDING NEAR A COOK STOVE. ALTHOUGH THE FACILITIES OWNED BY THE OPERATOR DO NOT APPEAR TO HAVE BEEN THE CAUSE OF THE FIRE, NATIONAL GAS APPEARS TO HAVE BEENIGNITED BY BURNING DEBRIS WHICH FELL AROUND THE IMMEDIATE AREA OF THE GAS METERS. HEAT FROM THE BURNING DEBRIS CAUSED THE 5/8" PLASTIC SERVICE LINE TO MELT INSIDE OF OTS PROTECTIVE GAS RISER (3/4" GALVANIZED PIPE W/HEAT SHIELD) AS WELL AS MELT THE INDEXES ON THE GAS METERS.
2025-01-31 10:21 | NO | NO | 19860113 |  | 18532 | SOUTHERN UNION GAS CO | 4905 EASTDALE DR | AUSTIN | TRAVIS | TX | 3 | 3 | NO | 1708 | 1986-04-16 | 0 | 0 | 45000 | 42582.6446 | 102814.4089 | Null | 0 | 45 |  | 19860417 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | VALVE |  | OTHER | STEEL BODY-BRASS CORE | 1 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | GILES GOBER - ENG | 5124775852 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TAMPERING WITH GAS VALVE AND METER RESULTED IN LEAKING GAS WHICH IGNITED AND SET FIRE TO HOUSE.
2025-01-31 10:21 | YES | YES | 19860116 |  | 11680 | LONE STAR GAS CO | 1118 SHAW ST | DALLAS | DALLAS | TX | 3 | 3 | NO | 1239 | 1986-05-30 | 0 | 4 | 25000 | 23657.0248 | 57119.1161 | Null | 0 | 0 |  | 19860530 | 20 | 55 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | UNKNOWN | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | L. B. HULCY, JR. | 2147413711 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EXPLOSION OF UNDETERMINED ORIGIN BLEW WALLS OF HOUSE INTO YARD. NO FIRE, BUT SEVERAL PIECES OF PAPER SCORCHED IN SOUTHWEST CORNER BEDROOM. ALL METERED ANDUNMETERED LEAK INVESTIGATION PROVED NEGATIVE. (NO GAS LEAK FOUND.)
2025-01-31 10:21 | YES | YES | 19860117 |  | 11680 | LONE STAR GAS CO | FYKE RD AND MILAM WAY | CARROLLTON | DALLAS | TX | 3 | 3 | NO | 1345 | 1986-05-29 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19860529 | 20 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | OTHER | COMPRESSION COUPLING | 1 | 0 | STYLE 90 | DRESSER | 0 | 0 | UNDER PAVEMENT |  | J. A. CRAVY, C & M SUPT | 2142761171 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19860119 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2850 CONCORD BLVD. | CONCORD | CONTRA COSTA | CA | 2 | 2 | NO | 215 | 1986-04-26 | 0 | 2 | 250 | 236.5702 | 571.1912 | Null | 0 | 22 |  | 19860428 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSELINE | OTHER | HOUSELINE | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRUCE P. SADLER, MANAGER | 4159723161 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE FIRE INSPECTOR HAS NOT GIVEN A DETERMINATION AS TO THE CAUSE OF THE EXPLOSION AND SUBSEQUENT FIRE. THE GAS LEAK CAUSING THE EXPLOSION APPEARS TO HAVE ORIGINATED FROM THE CUSTOMER'S HOUSELINE LEADING TO THE WATER HEATER OR FROM THE CUSTOMER'S VALVE INSTALLED IN THE HOUSELINE FEEDING THE WATER HEATER.
2025-01-31 10:21 | YES | YES | 19860120 |  | 2488 | CLEARWATER GAS DIV, CITY OF | 701 EAST BAY DRIVE | LARGO | PINELLAS | FL | 1 | 1 | NO | 1106 | 1986-05-10 | 2 | 1 | 350000 | 331198.3471 | 799667.6249 | Null | 0 | 15 |  | 19860512 | 18 | 30 | BY TEST | 50 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE BUILDING | OTHER | UNKNOWN | OTHER | UNKNOWN SOURCE | 2 | 0.409 | D2513 | POLYETHYLENE PRODUCTS INC. | 1985 | 1986 | WITHIN/UNDER BUILDING |  | J. TERRY NEENAN, GENERAL SUPT. | 8134626630 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19860121 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 2865 RIO LEMPA DRIVE | HACIENDA HEIGHTS | LOS ANGELES | CA | 3 | 3 | NO | 330 | 1986-05-21 | 0 | 0 | 70000 | 66239.6694 | 159933.525 | Null | 3 | 0 |  | 19860521 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 | 0.113 | API STD 5L |  | 0 | 1971 | ABOVE GROUND |  | J. L. LUCAS, MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19860122 |  | 18112 | SAN DIEGO GAS & ELECTRIC CO | 2928 EAST 8TH ST. | NATIONAL CITY | SAN DIEGO | CA | 4 | 4 | NO | 2004 | 1986-06-01 | 0 | 0 | 83000 | 78541.3223 | 189635.4653 | Null | 0 | 30 |  | 19860601 | 60 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.11 | API 5L |  | 0 | 1962 | ABOVE GROUND |  | RICHARD E. LIFER, GAS CONTROL SUPERVISOR | 6196962560 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AUTOMOBILE HIT A GAS HEADER ASSEMBLY CONSISTING OF 3 GAS METER SETS SERVING THREE SMALL BUSINESSES. THE GAS IGNITED AND DID EXTENSIVE DAMAGE TO THE CONTENTS OF FOREMOST DRY CLEANERS, WHICH IS ADJACENT TO THE GAS METERS. THERE WERE NO INJURIES.
2025-01-31 10:21 | YES | YES | 19860125 |  | 1800 | BROOKLYN UNION GAS CO | 3217 CHURCH AVE | BROOKLYN | KINGS | NY | 4 | 4 | NO | 1600 | 1986-04-27 | 0 | 1 | 50000 | 47314.0496 | 114238.2321 | Null | 2 | 0 |  | 19860427 | 0.3 | 0.5 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | FITTING |  | OTHER | COPPER TUBING | 1 | 0.62 |  |  | 1965 | 1965 | WITHIN/UNDER BUILDING |  | RAYMOND T. MCLOUGHLIN | 7184032864 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | YES |  | YES | 3 | APPROVED PAINT MARKINGS | NO |  |  | A CITY CONTRACTOR UPON COMPLETION OF AN EMERGENCY SEWER DID NOT OBTAIN PROPER CONSOLIDATION DURING BACKFILLING. EXCESSIVE SETTLEMENT OCCURRED CREATING VOIDS UNDER THE PAVEMENT. THIS RESULTED IN THE FAILURE OF A 6" CAST IRON MAIN AND A COPPER SERVICE PULLING OUT OF THE MAIN CONNECTION.
2025-01-31 10:21 | YES | YES | 19860129 |  | 4473 | ENERGAS CO | 1311 3RD | LEVELLAND | HOCKLEY | TX | 3 | 3 | NO | 1400 | 1986-04-27 | 0 | 2 | 5000 | 4731.405 | 11423.8232 | Null | 0 | 10 |  | 19860427 | 10 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | J.M. FRENCH, COMPANY EMPLOYEE, WAS INFORMED OF FIRE AND EXPLOSION BY THE LEVELLAND FIRE DEPT. HE AND CLEO RANGEL MADE A SHUT-IN TEST OF CUSTOMER PIPING AND SLOW-FIRE TEST OF METER SETTING AT THE REQUEST OF THE FIRE DEPT. AND FOUND NO LEAKS AND NO PROBLEM WITH METER OR REGULATOR. THEY ALSO CONDUCTED A LEAK SURVEY OF THE CUSTOMER PIPING AND ADJACENT COMPANY PIPING WITH A FLAME IONIZATION INSTRUMENT AND FOUND NO LEAKS. ACCORDING TO THE SON OF ALAQUINEZ, HIS FATHER WAS CLEANING OUT DUST FROM THE TV SET ON THE LIVING ROOM FLOOR WITH A HOSE OR PUMP WHEN THE EXPLOSION OCCURED. THEY WERE UNABLE TO FIND THE HOSE OR PUMP AFTER THE EXPLOSION. J. M. FRENCH SAID SOME OF THE NEIGHBORS MENTIONED THEY THOUGH HE WAS USINGA HOSE FROM THE BUTANE TANK ON HIS PICKUP THROUGH A WINDOW OF THE HOUSE TO BLOWOUT THE TV SET. OFFICIALLY FROM THE FIRE DEPT. REPORT, ORIGIN OF THE FIRE AND EXPLOSION IS UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19860132 |  | 3550 | DRUMRIGHT GAS AUTH | 620 S. GRAND | DRUMRIGHT | CREEK | OK | 1 | 1 | NO | 1823 | 1986-05-29 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 12 |  | 19860530 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | STEEL |  | 1 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | VIRGIL L. ANDERSON, MANAGER | 9183522120 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | STATEMENTS ATTACHED
2025-01-31 10:21 | YES | YES | 19860133 |  | 4499 | ENTEX INC | 102 MIGNON | HOUSTON | HARRIS | TX | 3 | 3 | NO | 1410 | 1986-06-20 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19860620 | 30 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | NO DATA |  | STEEL |  | 2 | 0.375 | API-5L |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | JOE L. ARMSTRONG, DIV. OPERATIONS MANAGER | 7136545900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19860134 |  | 4499 | ENTEX INC | 7200 DECKER DRIVER, #103 | BAYTOWN | HARRIS | TX |  | 0 | NO | 1910 | 1986-06-25 | 0 | 1 | 20000 | 18925.6198 | 45695.2928 | Null | 0 | 20 |  | 19860625 | 28 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ALDYL A | DUPONT | 1982 | 1982 | WITHIN/UNDER BUILDING |  | MICHAEL T. STEWART, DISTRICT OPERATIONS MANAGER | 7134274894 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19860135 |  | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 813 FILMORE AVE | NEW ORLEANS | ORLEANS | LA | 3 | 3 | NO | 830 | 1986-06-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19860627 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | OTHER | INSULATING SLEEVE | 1.5 | 0 |  |  | 0 | 1967 | WITHIN/UNDER BUILDING |  | A. G. YAEGER, JR., DIVISION GAS MANAGER | 5045953524 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FAILED INSULATED SLEEVE AT THE BASE OF A SERVICE RISER ADJACENT TO A SLAB HOUSE HAD BEEN REPLACED. WHILE USING BUTANE TORCH TO WRAP PIPE, A POCKET OF GAS INUNDETECTED VOID UNDER HOUSE SLAB IGNITED. EMPLOYEE RECEIVED FACIAL BURNS. SHEETROCK OF INTERIOR WALL BETWEEN BATHROOMS WAS MODERATELY DAMAGED.
2025-01-31 10:21 | YES | NO | 19860137 |  | 2748 | CONSUMERS POWER CO | 121 ELM PARK BLVD. | PLEASANT RIDGE | OAKLAND | MI | 3 | 3 | NO | 1027 | 1986-05-29 | 0 | 0 | 90000 | 85165.2893 | 205628.8178 | Null | 0 | 10 |  | 19860529 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | ASTM A53 |  | 0 | 1949 | WITHIN/UNDER BUILDING |  | DAVID V. VOIGT, MANAGER, GAS OPERATIONS | 5177882250 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-05-28 | YES | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19860138 |  | 6960 | GUYMON MUNICIPAL GAS CO | 210 N.W. 6TH | GUYMON | TEXAS | OK | 1 | 1 | NO | 1530 | 1986-07-18 | 0 | 1 | 60000 | 56776.8595 | 137085.8785 | Null | 0 | 0 |  | 19860721 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JERRY MITTS | 4053385866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | REPORTED BY PHONE 7-21-86 TO PETTY OFFICER BRYAN SEE ENCLOSED STATEMENT
2025-01-31 10:21 | NO | NO | 19860140 |  | 180 | ALABAMA GAS CORP | RT 2 BOX 393 | NOTASULGA | MACON | AL | 1 | 1 | NO | 1128 | 1986-06-21 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 58 |  | 19860621 | 50 | 175 | BY TEST | 250 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1947 | UNDER GROUND OR UNDER WATER |  | JERRY L. MIZELL, MANAGER MAINTENANCE SERVICES | 2053269224 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO
2025-01-31 10:21 | YES | YES | 19860141 |  | 11680 | LONE STAR GAS CO | 5041 DUPONT | DALLAS | DALLAS | TX | 3 | 3 | NO | 1000 | 1986-06-19 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19860619 | 27 | 55 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | THREAD LEAK ON BLEEDER | NO DATA |  | 1 | 0.133 | API-SL CL.I |  | 0 | 1959 | OTHER | COMPANY MANHOLE | EDDIE WILLIAMS | 2146702472 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19860142 |  | 11680 | LONE STAR GAS CO | BRAZOS & FM 160 LOOP | N. ZULCH | MADISON | TX | 3 | 3 | NO | 1130 | 1986-06-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 25 |  | 19860617 | 6 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | M. M. COLE, SUPT. II | 8177523471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | R R STATION AND METER STRUCK BY DERAILED TRAIN. DPS REQUESTED TOWN PLANT SYSTEM BE TURNED OFF DURING RESCUE OPERATIONS.
2025-01-31 10:21 | YES | YES | 19860145 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 719 CEDAR ST, APT B | PACIFIC GROVE | MONTEREY | CA |  | 0 | NO | 950 | 1986-05-28 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19860529 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | RESIDENTIAL | OTHER | CUST. HOUSELINE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRUCE P. SADLER, MANAGER | 4159723161 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | RESIDENT ATTACHED PLASTIC BAG TO GAS HOUSELINE. TO COMMIT SUICIDE, RESIDENT THEN PLACED HIS HEAD INSIDE THE BAG. DEATH WAS BY ASPHYXIATION.
2025-01-31 10:21 | YES | YES | 19860146 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 68065 VISTA CHINO | CATHEDRAL CITY | RIVERSIDE | CA | 3 | 3 | NO | 1653 | 1986-05-31 | 1 | 0 | 130000 | 123016.5289 | 297019.4035 | Null | 0 | 48 |  | 19860602 | 40 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0.75 | 0 | ASTM B85-76 | FISHER CONTROLS | 1985 | 1986 | ABOVE GROUND |  | J. L. LUCAS, MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19860147 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 10770 LAWLER ST | LOS ANGELES | LOS ANGELES | CA | 3 | 3 | NO | 850 | 1986-06-25 | 0 | 1 | 1350 | 1277.4793 | 3084.4323 | Null | 1 | 10 |  | 19860625 | 40 | 43 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | JOINT |  | OTHER | COPPER | 3 | 0.09 |  |  | 1946 | 1947 | UNDER PAVEMENT |  | J. L. LUCAS, MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19860148 |  | 12390 | METROPOLITAN UTILITIES DISTRICT | HIGHWAY 73 SOUTH CITY LIMITS | FORT CALHOUN | WASHINGTON | NE | 2 | 2 | NO | 1540 | 1986-07-23 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 10 |  | 19860723 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0 |  |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | DONALD D. BLOCKER | 4024498211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19860149 |  | 2748 | CONSUMERS POWER CO | 5102 PORT AUSTIN ROAD | CASEVILLE | HURON | MI | 3 | 3 | NO | 1623 | 1986-07-04 | 0 | 0 | 60000 | 56776.8595 | 137085.8785 | Null | 2 | 7 |  | 19860704 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0.04 | ASTM B88 |  | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | D. V. VOIGT, MANAGER OF GAS OPERATIONS | 5177888250 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-05-29 | YES | 2 |  | YES
2025-01-31 10:21 | YES | NO | 19860154 |  | 18532 | SOUTHERN UNION GAS CO | 923 AUDREY LN | PRESCOTT | YAVAPAI | AZ | 3 | 3 | NO | 1045 | 1986-08-27 | 0 | 0 | 105000 | 99359.5041 | 239900.2875 | Null | 0 | 40 |  | 19860827 | 100 | 120 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | STEEL |  | 1 | 0.133 | APISLA25 |  | 0 | 1951 | UNDER GROUND OR UNDER WATER |  | ALLAN C BOUNDS - AREA MGR | 6024452210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON AUGUST 27, 1986, A 1" STEEL SERVICE LINE WAS HIT AND DAMAGED BY A CITY OWNEDAND OPERATED GRADER. THE GRADER PULLED THE LINE AWAY FROM THE METER AT A SCREW TYPE JOINT ( THE METER WAS LOCATED NEXT TO THE GARAGE). THE LINE WAS HIT BY THE GRADER APPROXIMATELY 45 FEET AWAY FROM THE HOUSE . AT THIS POINT NATURAL GAS PROCEEDED TO FIILL THE GARAGE AT 923 AUDREY LN AND IN A VERY SHORT TIME AN EXPLOSION AND SUBSEQUENT FIRE OCCURED.
2025-01-31 10:21 | YES | NO | 19860155 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 15513 S. VIRGINIA AVE | PARAMOUNT | LOS ANGELES | CA | 3 | 3 | NO | 1056 | 1986-03-26 | 0 | 0 | 105000 | 99359.5041 | 239900.2875 | Null | 0 | 40 |  | 19860326 | 40 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | SCREW | STEEL |  | 0.75 | 0.154 | ASTM A106 |  | 0 | 1940 | ABOVE GROUND |  | J L LUCAS - MGR OF DIST | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19860156 |  | 13170 | NAVASOTA, CITY OF | FM ROAD 379-INDUSTRIAL DR | NAVASOTA | GRIMES | TX | 1 | 1 | NO | 1500 | 1986-08-12 | 0 | 0 | 650 | 615.0826 | 1485.097 | Null | 0 | 45 |  | 19860812 | 24 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0 | SDR11ASTMD2513 | TEX TUBE | 0 | 1983 | UNDER GROUND OR UNDER WATER |  | GARY E JOHNSON - DIR OF UTIL | 4098256450 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHEN MAKING REPAIRS TO WATER LINE OPERATOR OF BACKHOE CUT THE GAS LINE.
2025-01-31 10:21 | NO | NO | 19860157 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | 4147 N RAVENSWOOD | CHICAGO | COOK | IL | 3 | 3 | NO | 1140 | 1986-07-07 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19860707 | 20 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | OTHER | BRASS | 1.5 | 0 |  |  | 1981 | 1981 | UNDER GROUND OR UNDER WATER |  | W E GRATZ - FIELD SUPT | 3127625101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1985-04-04 | YES | 3 | PAINT ON WALK | NO |  |  | AN OUTSIDE CONTRACTOR, USING HEAVY EQUIPMENT, BROKE A SERVICE TAP VALVE AT A 6"C.I. MAIN. DUE TO THE CLOSE PROXIMITY TO THE ESCAPING GAS, A NEARBY FACTORY WASEVACUATED.
2025-01-31 10:21 | NO | NO | 19860161 |  | 13790 | NORTHERN UTILITIES INC | 333 WEST 11TH | CASPER | NATRONA | WY | 3 | 3 | NO | 1510 | 1986-08-08 | 0 | 0 | 10000 | 9462.8099 | 22847.6464 | Null | 0 | 10 |  | 19860808 | 30 | 59 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | NO DATA |  | STEEL |  | 1 | 0.133 | API 5L | ENCOAT | 0 | 1986 | ABOVE GROUND |  | ROBERT F HUGHES - VP OPER | 3072351541 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | THE ATTACHED REPORT COVERS AN INCIDENT THAT OCURRED ON A 1" DISTRIBUTION STUB IN CASPER, WY ON 8/8/86. NATURAL GAS IGNITED RESULTING IN FIRST AND SECOND DEGREEBURNS TO THE FACE AND RIGHT ARM OF ONE COMPANY EMPLOYEE REQUIRING FIRST AID TREATMENT BUT NO FATALITIES OCCURRED AS A RESULT OG THE INCIDENT. THE INCIDENT WAS CAUSED WHEN A NEWLY INSTALLED MAIN AND SERVICE STUP WAS BEING PURGED AND IGNITION OCCURED. THE RESULTING FIRE CAUSED EXTERNAL DAMAGE TO TWO RESIDENCES ADJACENT TO THE INCIDENT. THE ESTIMATED PROPERTY DAMAGE WILL BE APPROXIMATELY $10,000. THERE WAS NO DAMAGE TO COMPANY PROPERTY NOR WAS SERVICE DISCONTINUED TO ANY CUSTOMER.
2025-01-31 10:21 | YES | YES | 19860162 |  | 11713 | LONG ISLAND LIGHTING CO | 120 JERICO TURNPIKE | JERICHO | NASSAU | NY | 3 | 3 | NO | 1940 | 1986-08-04 | 0 | 4 | 0 | 0 | 0 | Null | 3 | 50 |  |  | 46.5 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | JOINT | FUSION | POLYETHYLENE PLASTIC |  | 4 | 0.395 | ASTM-0-2513 | DUPONT | 0 | 1978 | WITHIN/UNDER BUILDING |  | THOMAS AMERIGE - AREA SUPV | 5169334718 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAK CAUSE IS CURRANTLY UNDER INVESTIGATION BY AN ANALYTICAL METALLURGICAL AND RESEARCH LABORATORY.
2025-01-31 10:21 | YES | YES | 19860163 |  | 22777 | WISCONSIN NATURAL GAS CO | 7739 34TH AVE | KENOSHA | KENOSHA | WI | 3 | 3 | NO | 2200 | 1986-07-20 | 1 | 0 | 70000 | 66239.6694 | 159933.525 | YES | 1 | 30 |  | 19860721 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER LINE CONNECTION | JOINT | SOLDER | OTHER | BRASS | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | G W BOMIER - VP | 4146377681 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BASED UPON INFORMATION OBTAINED, APPEARS THAT CONNECTOR BEHIND GAS APPLIANCE FAILED, ALLOWING ACCUMULATION AND IGNITION OF GAS WITHIN CUSTOMER'S RESIDENCE. NO INDICATION THAT OPERATOR'S DISTRIBUTION SYSTEM WAS INVOLVED IN CAUSE AND ORIGIN OF OCCURANCE.
2025-01-31 10:21 | YES | YES | 19860165 |  | 13782 | NORTHERN STATES POWER CO | 1000 ISLE LA PLUME | LA CROSSE | LA CROSSE | WI | 3 | 3 | NO | 1631 | 1986-08-06 | 0 | 2 | 10000 | 9462.8099 | 22847.6464 | Null | 0 | 10 |  | 19860806 | 1.9 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID F SEANOR | 7158392558 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS CUSTOMER IS THE CITY OF LA CROSSE SEWER DISPOSAL PLANT. IN THE PROCESS OF SWITCHING FROM METHANE GAS OFF OF THE DIGESTORS TO NSP SUPPLIED NATURAL GAS, THE"GAS" EXPLODED INSIDE THE BOILER. THIS CAUSED TWO INJURIES AND AN ESTIMATED $10,000 XDAMAGE TO BOILER. TO DATE, THERE HAS BEEN NO DISCOVERY OF ANY GAS LEAKAGE OR EQUIPMENT FAILURE OF ANY OF THE OPERATOR OWNED FACILITIES IN CONNECTION WITH THIS INCIDENT. BOTH PEOPLE INJURED HAVE SINCE RECOVERED FROM THEIR INJURIES.
2025-01-31 10:21 | YES | NO | 19860167 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | PALM & CAJON ST | REDLANDS | SAN BERNARDINO | CA | 3 | 3 | NO | 1030 | 1986-07-24 | 0 | 0 | 100000 | 94628.0992 | 228476.4642 | YES | 3 | 35 |  | 19860725 | 108 | 39 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REG STATION | VALVE |  | CAST IRON |  | 3 | 0 |  | NORDSTROM | 1946 | 1947 | OTHER | IN VAULT | J L LUCAS - MGR OF DIST | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A THREE INCH BY-PASS VALVE IN A REGULATOR STATION WAS OPENED BY AN UNATHORIZED PERSON. NATURAL GAS AT 175 PSI WAS ALLOWED TO ENTER A SYSTEM WITH AN MAOP OF 39 PSI.
2025-01-31 10:21 | YES | YES | 19860168 |  | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | RAVEN AVE AT HANCOCK RD | PISCATAWAY | MIDDLESEX | NJ | 4 | 4 | NO | 1438 | 1986-08-14 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 34 |  | 19860815 | 12 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PHILLIPS | 1983 | 1983 | UNDER PAVEMENT |  | R M WHITE - GEN MGR - GAS T&D | 2014307797 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-08-08 | YES | 3 | YELLOW PAINT MARKINGS | YES |  |  | CONTRACTOR DAMAGED A GAS MAIN WHILE INSTALLING SEWER LATERAL. IGNITION OCCURED CAUSING FIRST AND SECOND DEGREE BURNS TO CONTRACTOR'S EMPLOYEE.
2025-01-31 10:21 | YES | YES | 19860169 |  | 4499 | ENTEX INC | 9441 SHADY DR | HOUSTON | HARRIS | TX | 3 | 3 | NO | 1000 | 1986-08-08 | 0 | 1 | 500 | 473.1405 | 1142.3823 | Null | 0 | 30 |  | 19860808 | 23 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1946 | UNDER GROUND OR UNDER WATER |  | DAVID E GATES - OPER ENG | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CITY OF HOUSTON CREW BROKE 1" SERVICE OFF OF 2" MAIN. ONE CITY EMPLOYEE LIT A CIGARETTE CAUSING THE GAS TO IGNITE. TWO PEOPLE RECEIVED BURNS. ONE PERSON WAS HOSPITALIZED OVERNIGHT.
2025-01-31 10:21 | YES | NO | 19860172 |  | 11800 | LOUISIANA GAS SERVICE CO | 855 HOMESTEAD AVE | METAIRIE | JEFFERSON | LA | 70005 | 3 | NO | 1532 | 1986-08-04 | 0 | 0 | 150000 | 141942.1488 | 342714.6964 | Null | 0 | 18 |  | 19860804 | 65 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API-5L |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | D L MERIWETHER - DIR OF TECH STD | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE HOUSE AT 855 HOMESTEAD AVE EXPLODED AND BURNED AT 3:32PM ON 8/4/86. TWO ADJACENT HOMES ON EACH SIDE OF THE HOUSE WERE MODERATELY DAMAGED. NO ONE WAS HOME AT TIME OF THE EXPLOSION. GAS CO CREWS WERE IMMEDIATELY DISPATCHED TO THE AREA AND MAIN LINE VALVES ON HOMESTEAD AVE WERE SHUT OFF AT 3:50PM EFFECTIVELY REMOVINGTHE SOURCE OF GAS SUPPLY. INSPECTION OF THE GAS METER AND RISER AFTER THE FIRE HAD BEEN EXTINGUISHED REVEALED A FACTURE IN THE SERVICE LINE APPROXIMATELY 18" BELOW THE REGULATOR. CAUSE OF THE EXPLOSION AT THIS TIME IS UNKNOWN. A METALURGIST IS EXAMINING THE RISER TO DETERMINE IF THE FRACTURE WAS CAUSED BY THE EXPLOSION AND FALLEN DEBRIS OR THE FRACTURE ALREADY EXISTED AND CONTRIBUTED TO THE EXPLOSION. LEAK SURVEYS IN THE AREA AFTER THE INCIDENT REVEALED NO LEAKS ON SERVICE LINES OF MAINS IN THE IMMEDIATE AREA. THE SERVICE LINE TO 855 HOMESTEAD WAS PRESSURE TESTED AND FOUND TO BE FREE OF LEAKS OTHER THAN AT THE FRACTURE POINT JUST BELOW THE RISER.
2025-01-31 10:21 | YES | NO | 19860173 |  | 18112 | SAN DIEGO GAS & ELECTRIC CO | 9558 GROSSMONT BLVD | LA MESA | SAN DIEGO | CA | 3 | 3 | NO | 925 | 1986-07-28 | 0 | 0 | 176000 | 166545.4545 | 402118.5771 | Null | 0 | 30 |  | 19860728 | 0.3 | 0.3 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | HOUSELINE | JOINT | THREAD | STEEL |  | 0.75 | 0.13 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | A F HOOPER - LEAKAGE MITIGATION SUPV | 6196962474 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A D-3 CATERPILLER HIT A 3/4" SERVICE LINE BETWEEN MAIN AND METER SET ASSEMBLY. THE SERVICE RISER AND MSA WERE PULLED AWAY FROM THE HOUSE APPLING A STRESS TO THE HOUSELINE WHICH FAILED. ESCAPING GAS IGNITED BY UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 19860178 |  | 6141 | GAS CO OF NEW MEXICO | GAY CIRCLE AND SOUTHERN BLVD. | RIO RANCHO | SANDOVAL | NM | 3 | 3 | NO | 1032 | 1986-08-28 | 0 | 1 | 5400 | 5109.9174 | 12337.7291 | Null | 4 | 15 |  | 19860828 | 55 | 60 | BY TEST | 136 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | BY-PASS HOSE | OTHER | BY-PASS HOSE | 2 | 0.125 | API 5L | LONE STAR STEEL | 1974 | 1974 | UNDER GROUND OR UNDER WATER |  | AL ADAMSKO, CHIEF INSPECTOR | 5058892536 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | HE WAS CLEANING TAPE OFF OF PIPE USING TORCH TO BURN TAPE. FIRE WAS APPARENTLY OUT AND HE WAS GOING TO HOOK UP BYPASS HOSE. HE OPENED SANDWICH VALVE IN PREPARATION OF PURGING GAS; BUT 3/4" VALVE ON BY-PASS ASSEMBLY WAS OPEN. HE HEARD GAS AND WAS ATTEMPTING TO CLOSE VALVE WHEN IGNITION OCCURRED. HE RAN EAST DOWN DITCHAND WAS HELPED OUT OF THE DITCH.CONCLUSIONS: FIRE WAS THE RESULT OF SANDWICH VALVE BEING OPENED WHILE BY-PASS VALVE WAS OPEN. GAS FILLED AREA AND PROBABLY IGNITED FROM TAPE BURNING UNDER PIPE AS A RESULT OF EFFORT TO REMOVE TAPE TO CLEAN PIPE IN PREPARATION OF WELDING.
2025-01-31 10:21 | YES | YES | 19860179 |  | 22182 | WASHINGTON GAS LIGHT CO | 8912 CROMWELL DRIVE | SPRINGFIELD | FAIRFAX | VA | 3 | 3 | NO | 1500 | 1986-09-05 | 0 | 1 | 150000 | 141942.1488 | 342714.6964 | Null | 0 | 40 |  | 19860905 | 20 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW INSIDE HOUSE | STEEL |  | 0.75 | 0.113 | API 5L |  | 0 | 1962 | WITHIN/UNDER BUILDING |  | CLARENCE E GOODSON, III, SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A PRIVATE CONTRACTOR, ROSS MASONRY, WAS EXCAVATING AT 8912 CROMWELL DR TO REPAIR THE BASEMENT'S REAR BUILDING WALL. A 3/4" WRAPPED STEEL HP GAS SERVICE LINE WAS STRUCK AND BROKEN BY THEIR BACKHOE CAUSING GAS ESCAPEMENT WHICH POCKETED IN THE BASEMENT AND WAS IGNITED BY AN UNKNOWN SOURCE. A TOTAL OF FIVE PEOPLE WERE IN THE HOUSE AT THE TIME OF THE EXPLOSION, THE BACKHOE OPERATOR, A WOMAN AND TWO SMALL CHILDREN ON THE ENTRY LEVEL AND A LABORER IN THE BASEMENT. ONLY THE LABORER IN THE BASEMENT, ATTEMPTING TO TURN THE GAS OFF AT THE METER WAS INJURED. HE SUSTAINED SECOND AND THIRD DEGREE BURNS TO THE FACE, ARMS AND HANDS.WASHINGTON GAS LIGHT COMPANY WAS NOTIFIED BY THE FIRE BOARD AT 3:15 P.M. COMPANY PERSONNEL ARRIVED ON SITE AT 3;30 P.M. AND AFTER DIGGING UP THE CURB SIDE STOPCOCK GAS WAS TURNED OFF AT 3:40 P.M.NO RECORD OF CONTRACTOR EVER CALLING WGL CO OR MISS UTILITY TO ADVISE OF PROPOSED WORK.CONTRACTOR ROSS DID NOT HAVE: 1) PROPER PERMIT TO DO WORK 2) PROPER LICENSE TODO WORK 3) UNDERGROUND LINES MARKED PRIOR TO EXCAVATING
2025-01-31 10:21 | NO | NO | 19860180 |  | 13710 | NORTHERN ILLINOIS GAS CO | 7S721 RTE 53 | WOODRIDGE | DU PAGE | IL | 3 | 3 | NO | 1041 | 1986-09-06 | 0 | 0 | 15000 | 14194.2149 | 34271.4696 | Null | 2 | 5 |  | 19860906 | 150 | 230 | BY TEST | 230 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.25 |  |  | 0 | 1935 | UNDER GROUND OR UNDER WATER |  | GEORGE WALDVOGEL, GENERAL SUPV. OPERATING | 3126292500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-08-14 | YES | 2 |  | YES
2025-01-31 10:21 | YES | YES | 19860182 |  | 180 | ALABAMA GAS CORP | 600 EAST INVERNESS PKWY | BIRMINGHAM | JEFFERSON | AL | 3 | 3 | NO | 1525 | 1986-10-11 | 0 | 1 | 5000 | 4731.405 | 11423.8232 | Null | 1 | 31 |  | 19861013 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | CAST IRON |  | 1.25 | 0.166 | SDR 10 | DUPONT | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | G M WALKER - SUPT - MAIN & SERV | 2053268309 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR, USING VERMEER TRENCHING MACHINE TO CUT DITCH FOR TELEPHONE CABLE INSTALLATION, CUT 1.25" PLASTIC GAS SERVICE WITH DIGGING CHAIN. GAS IGNITED, DAMAGEING MACHINE AND INJURING OPERATOR. ALABAMA GAS CORP WAS NOTIFIED OF THE OPERATOR'S HOSPITALIZATION ON 10/13/86.
2025-01-31 10:21 | NO | NO | 19860183 |  | 2364 | CINCINNATI GAS & ELECTRIC CO | 1630 HERALD | CINCINNATI | HAMILTON | OH | 4 | 4 | NO | 525 | 1986-09-14 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 0 |  | 19860914 | 15 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.48 |  |  | 0 | 1954 | UNDER PAVEMENT |  | H J FANETTI - DIR REG CODES | 5136322671 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FULL CIRCUMFERENTIAL BREAK OCCURED IN HTE GAS MAIN. FOLLOWING THE EXCAVATION A ROCK WAS FOUND BURIED 6" BELOW THE BOTTOM OF THE MAIN. THIS IS BELIEVED TO HAVE BEEN A CONTRIBUTING CAUSE TOGETHER WITH THE PROBABILITY OF HEAVY EXTERNAL DOWNWARD FORCE CAUSED BY HEAVY VEHICULAR TRAFFIC.
2025-01-31 10:21 | NO | NO | 19860184 |  | 13660 | NORTH SHORE GAS CO | WASHINGTON ST & GREEN BAY RD | LAKE BLUFF | LAKE | IL | 3 | 3 | NO | 1952 | 1986-09-15 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 3 |  | 19860915 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | AP15LGRB |  | 0 | 1973 | UNDER GROUND OR UNDER WATER |  | R W STEGMAN - SUPT DIST | 3123367400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-09-10 | YES | 2 | & PAINT | NO |  |  | AN OUTSIDE CONTRACTOR BROKE A 2" STEEL MP MAIN, PULLING 10 FEET OUT OF THE GROUND. FOUR HOUSES WERE SHUT OFF AND EIGHT HOUSES WERE EVACUATED.
2025-01-31 10:21 | YES | YES | 19860185 |  | 13850 | NORTHWESTERN PUBLIC SERVICE CO | LAKESIDE MOBILE HOME ESTATES | ABERDEEN | BROWN | SD | 3 | 3 | NO | 30 | 1986-09-25 | 2 | 0 | 300000 | 283884.2975 | 685429.3927 | Null | 0 | 30 |  | 19860926 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 0 | ABOVE GROUND |  | HERBERT W THOMAS - GEN GAS SUPT | 6053528411 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | WIND OR TORNADO | NO |  | NO | 0 |  | NO |  |  | HIGH WINDS OR TORNADO TIPPED A NUMBER OF MOBILE HOMES, WITH SEVERAL FALLING ON METERS & REGULATORS.
2025-01-31 10:21 | YES | YES | 19860186 |  | 6769 | GREAT RIVER GAS CO | 1428 MISSOURI AVE | KEOKUK | LEE | IA | 3 | 3 | NO | 725 | 1986-09-21 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 15 |  | 19860921 | 47 | 80 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER SIDE OF METER | OTHER | SPACE HEATER | OTHER | APPLIANCE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MICHAEL CONN - OPER SUPT | 3195244752 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 9/21/86, AT APPROXIMATELY 7:25AM, THE OCCUPANT OF 1428 MISSOURI AVE., MR. LARRY EVANS, REPORTED HE AWOKE, PUT HIS DOG OUT ON A CHAIN, RE-ENTERED THE HOUSE, LIT A CIGARETTE, AND AN EXPLOSION OCCURED. THE EXPLOSION COMPLETELY DESTROYED THE DWELLING AND BURNED MR. EVANS. SEVERAL TESTS HAVE BEEN CONDUCTED ON GREAT RIVER'S FACILITIES, WHICH ALL HAVE PROVED NEGATIV OR NO INDICATION OF THE FACILITIESHAVING CONTRIBUTED TO THE INCIODENT. FURTHER TESTS CONDUCTED ON THE PROPERTY OWNER'S PIPING AND APPLIANCES HAVE DETERMINED THE LEADING SUSPECT IS THE SPACE HEATER. TESTS HAVE DETERMINED THE SPACE HEATER CONTROL VALVE TO BE FAULTY AND PASSING GAS. TESTS ALSO IDENTIFIED THE SPACE HEATER HAS A FAULTY HEAT EXCHANGER.
2025-01-31 10:21 | YES | YES | 19860188 |  | 12390 | METROPOLITAN UTILITIES DISTRICT | 7736 SOUTH 30TH ST | BELLEVUE | SARPY | NE | 3 | 3 | NO | 1023 | 1986-09-15 | 1 | 3 | 300000 | 283884.2975 | 685429.3927 | Null | 0 | 30 |  | 19860915 | 45 | 45 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION CPLG. | STEEL |  | 1 | 0 |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | DONALD D BLOCKER - CLAIMS ADJUSTER | 4024498211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-09-11 | YES | 3 | PAINTED | NO |  |  | SEWER CONTRACTOR EXCAVATING AND STRUCK 1" WRAPPED STEEL GAS SERVICE. PULLED OUTOF COMPRESSION COUPLING UNDERGROUND AT HOUSE. ESCAPING GAS ENTERED HOME AND RESULTED IN EXPLOSION.
2025-01-31 10:21 | NO | NO | 19860189 |  | 2748 | CONSUMERS POWER CO | 855 WEST EIGHT MILE RD | WHITMORE LAKE | WASHTENAW | MI | 3 | 3 | NO | 1400 | 1986-08-30 | 0 | 0 | 51000 | 48260.3306 | 116522.9968 | Null | 2 | 15 |  | 19860830 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.151 | PE-3408 | PHILLIPS | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | D V VOIGT - MGR GAS OPER | 5177882250 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | GAS MAIN HIT AND DAMAGED BY BACKHOE EXCAVATING TRENCH FOR WATER DRAIN. GAS IGNITED AND DESTROYED MOBILE HOME.
2025-01-31 10:21 | YES | YES | 19860190 |  | 4499 | ENTEX INC | 3227 WEST RIDGE | HOUSTON | HARRIS | TX | 4 | 4 | NO | 2119 | 1986-09-07 | 0 | 2 | 70000 | 66239.6694 | 159933.525 | Null | 1 | 59 |  | 19860907 | 25 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | NO DATA |  | 1.25 | 0.14 | AI 5L |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | B F BROYLES - DIR OF OPER | 7136545137 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS FROM LEAK CAUSED BY STRESS FRACTURES ON THREADED END OF 1 1/4" SERVICES, MIGRATED INTO RESIDENCE. GAS WAS IGNITED WHEN OCCUPANT TURNED ON ELECTRIC LAMP AFTER ENTERING HOUSE.
2025-01-31 10:21 | YES | NO | 19860191 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1037 REDMOND AVE | SAN JOSE | SANTA CLARA | CA | 3 | 3 | NO | 1445 | 1986-08-22 | 0 | 0 | 171000 | 161814.0496 | 390694.7539 | Null | 3 | 20 |  | 19860822 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | SERVICE TEE | STEEL |  | 0.75 | 0.113 | API5L GRA-25 |  | 0 | 1963 | UNDER PAVEMENT |  | HOWARD M MCKINLEY - VP GAS OPER | 4159723204 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | SURFACE MARKINGS | YES |  |  | A CONTRACTOR STRUCK OUR 3/4" STEEL SERVICE AND PULLED IT FROM THE 4" MAIN. GAS IGNITED AND A VACANT HOUSE WAS DESTROYED THREE BLOCKS WERE EVACUATED AS A PRECAUT
2025-01-31 10:21 | YES | NO | 19860192 |  | 6210 | GAS SERVICE INC | 152 INDIAN ROCK RD | MERRIMACK | HILLSBOROUGH | NH | 1 | 1 | NO | 1430 | 1986-09-29 | 0 | 0 | 125000 | 118285.124 | 285595.5803 | Null | 1 | 0 |  | 19860929 | 1 | 60 | BY TEST | 60 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | METER SET ASSEMBLY |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | SDR11 | DUPONT | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | RONALD A NICHOLS - VP | 6036254000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | THE CONTRACTOR INSTALLING THE NEW SERVICE DID NOT INSTALL THE SERVICE PIPE ALL THE WAY INTO THE METER RISER PLASTIC COUPLING. GAS LEAKED INTO THE BUILDING AND WAS IGNITED BY THE WATER HEATER CAUSING AS EXPLOSION AND BRIEF FIRE.
2025-01-31 10:21 | YES | YES | 19860193 |  | 4473 | ENERGAS CO | 4519 - 42ND STREET | LUBBOCK | LUBBOCK | TX | 3 | 3 | NO | 500 | 1986-10-21 | 1 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 20 |  | 19861021 | 6 | 16 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER LINE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | COMBUSTION FIRE AND EXPLOSION OCCURRED THIS MORNING ABOUT 5:00A.M. AT A HOUSE AT 4519 - 42ND ST. THE BODY OF MRS. EDGAR BRASCH WAS FOUND ADJACENT TO THE REAR DOOR IN THE KITCHEN OF THIS RESIDENCE. ACCORDING TO JOHN ANTHONY, FIRE MARSHALL FOR THE LUBBOCK FIRE DEPARTMENT, THE EXPLOSION AND SUBSEQUENT FIRE ORIGINATED IN THE VICINITY OF THE KITCHEN RANGE. HE FOUND ONE OF THE TOP BURNERS ON AND BELIEVES THERE WAS A FAULT ON THE FLEX LINE CONNECTING THE RANGE. BILL HART, SERVICE SUPERVISOR WITH ENERGAS, DID A SHUT-IN TEST ON THE CUSTOMER LINE THIS MORNING ANDFOUND NO OBSERVABLE LEAKAGE ON THE CUSTOMER LINE. LEAKAGE SURVEYS WITH C.G.I. AND F.I. UNITS WERE CONDUCTED ON COMPANY LINES IN THE AREA AND CUSTOMER LINE AS WELL. NO LEAKS WERE FOUND WITH THE EXCEPTION OF A VERY SMALL PIN-HOLE LEAK ON THECUSTOMER RISER AT THE HOUSE. SERVICE RECORDS FOR THIS ADDRESS SHOW CONSUMPTION OF 2 MCF FOR MONTHS OF JULY, AUGUST AND SEPTEMBER AND 4 MCF FOR MONTH OF OCTOBER. THESE VOLUMES COMPARES VERY CLOSELY WITH RECORDS FOR NEIGHBOR'S HOME AND OTHERS WITHIN THE CITY. THE RECORDS ALSO SHOW NO ORDERS FOR ANY TYPE OF SERVICE AT THIS ADDRESS FOR APPROXIMATELY THE LAST THREE YEARS.
2025-01-31 10:21 | YES | NO | 19860194 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 1511 4TH STREET | SAN FERNANDO | LOS ANGELES | CA | 3 | 3 | NO | 1515 | 1986-09-19 | 0 | 0 | 150000 | 141942.1488 | 342714.6964 | YES | 0 | 40 |  | 19860919 | 30 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | SCREW | STEEL |  | 0.75 | 0.113 | API STD 5L |  | 0 | 1963 | ABOVE GROUND |  | L.M. STEWART - MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | OWNER OF PROPERTY, WHILE BACKING VEHICLE OUT OF DRIVEWAY, ALLOWED THE VEHICLE TO STRIKE AND DAMAGE A METER SET ASSEMBLY LOCATED IN AN AREA NOT NORMALLY SUBJECTED TO VEHICULAR TRAFFIC. A 3/4" NIPPLE IMMEDIATELY ABOVE THE SERVICE SHUT OFF VALVE WAS BROKEN ALLOWING NATURAL GAS TO ESCAPE AT 30 PSI. GAS MIGRATED UNDER THE ADJACENT BUILDING WHERE IGNITION OCCURRED. ESCAPING GAS WAS CONTROLLED BY LOS ANGELES CITY FIRE DEPARTMENT CLOSING SERVICE SHUT OFF VALVE AT THE MSA. THE SERVICE SUPPLYING THE DAMAGED STRUCTURE WAS ABANDONED AT THE MAIN BY THE OPERATOR. THERE WERE NO INJURIES OF FATALATIES. DAMAGE IS ESTIMATED TO BE $150,000.00
2025-01-31 10:21 | YES | NO | 19860195 |  | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 72 IRVING AVE | LIVINGSTON | ESSEX | NJ | 4 | 4 | NO | 1555 | 1986-09-23 | 0 | 0 | 150000 | 141942.1488 | 342714.6964 | Null | 0 | 12 |  | 19860923 | 13.4 | 15 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | R.M. WHITE, GENERAL MANAGER - GAS T&D | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE CAUSE OF THE EXPLOSION IS UNKNOWN. AN EXPLOSION OF UNKNOWN ORIGIN OCCURRED WHICH COMPLETELY DESTROYED THE HOUSE AT 72 IRVING AVE., AND DAMAGED SURROUNDING PROPERTIES - NO PERSONAL INJURIES.
2025-01-31 10:21 | NO | NO | 19860196 |  | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 2719 FREEMONT DRIVE | DURHAM | DURHAM | NC | 3 | 3 | NO | 908 | 1986-08-14 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 16 |  | 19860814 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 | API FL GR B | UNKNOWN | 1971 | 1971 | UNDER GROUND OR UNDER WATER |  | J.F. NOON -SR. VICE PRESIDENT/ENG. & OPER. SERVICES | 7048646731 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-07-21 | YES | 1 | PAINT ON PAVEMENT | YES |  |  | SEWER CONTRACTOR WORKING FOR CITY OF DURHAM, N.C., HIT AP PREVIOUSLY LOCATED SERVICE LINE WITH BACKHOE. GAS LINE SPEARATED AT METER SITE AND NOT A CONTACT POINT. THIS INCIDENT WAS REPORTED TO N.C. UTILITIES COMMISSION ON 8-14-86. AT THE TIME OF INCIDENT THE COMPANY HAD NO KNOWLEDGE OF FACT THAT THE ESTIMATE OF DAMAGE WOULD BE IN THE $50,000-$60,000 RANGE AND DID NOT REPORT INCIDENT TO DOT IN WASHINGTON.
2025-01-31 10:21 | NO | NO | 19860197 |  | 2652 | COMMONWEALTH GAS CO |  | WESTBORO | MIDDLESEX | MA |  | 0 | NO | 0 | 1986-10-08 | 0 | 0 | 1500 | 1419.4215 | 3427.147 | Null | 0 | 30 |  | 19861008 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | 86 19786019702652COMMONWE | BODY OF PIPE | LTH GAS CO | NO DATA | OLD NOURSE | 0 | 0 |  | WESTBORO MIDDLESEX | 0 | 0 | NO DATA | MA 0N000010088600 | 00000001500.00000030100886035.0060.01100.0B0 | 0000000000 | [6 empty] | Null |  | OPERATOR ACTION |  | YES |  | YES | 1 |  | YES |  |  | CONSTUCTION WORKER WAS POURING GASOLINE INTO RUNNING WATER PUMP. ACCIDENTAL IGNITION OF GASOLINE OCCURRED. WORKER DROPPED GASOLINE CAN INTO EXCAVATION DAMAGING4" PLASTIC PIPE CAUSING ESCAPE AND IGNITION OF NATURAL GAS.
2025-01-31 10:21 | YES | NO | 19860199 |  | 15007 | PACIFIC GAS & ELECTRIC CO | W. RICHMOND AVE., & GARRARD BLVD. | RICHMOND | CONTRA COSTA | CA | 3 | 3 | NO | 1423 | 1986-09-26 | 0 | 0 | 70000 | 66239.6694 | 159933.525 | YES | 0 | 0 |  | 19860926 | 6.2 | 5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | REGULATOR/METER | REGULATOR | STEEL |  | 2 | 0 | 2"-1001 | ROCKWELL | 0 | 1965 | UNDER GROUND OR UNDER WATER | IN UNDERGROUND VAULT | D.L. GEE | 4159722064 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | REGULATOR MALFUNCTIONED ALLOWING PRESSURE TO INCREASE.
2025-01-31 10:21 | NO | NO | 19860201 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | 54TH PLACE AND UNIVERSITY AVENUE | CHICAGO | COOK | IL | 3 | 3 | NO | 915 | 1986-10-10 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19861010 | 20 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.25 | API5LGRB | UNKNOWN | 1984 | 1985 | UNDER PAVEMENT |  | MARTIN J. MCDONNELL, DISTRICT SUPERINTENDENT | 3124314840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-10-09 | YES | 3 | SPRAY PAINT ON PAVEMENT | NO |  |  | A 6" STL. MP MAIN WAS PUNCTURED BY A SEWER DEPT. BACKHOE. AS A PRECAUTION, SEVERAL BLDGS. IN THE IMMEDIATE AREA WERE EVACUATED BY THE FIRE DEPT.THERE WAS NO IGNITION.
2025-01-31 10:21 | YES | YES | 19860202 |  | 22756 | WISCONSIN FUEL & LIGHT CO | 1603 JONQUIL LANE | WAUSAU | MARATHON | WI | 3 | 3 | NO | 1712 | 1986-10-16 | 1 | 1 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 43 |  | 19861016 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION | POLYETHYLENE PLASTIC | STEEL FITTING | 0.5 | 0.09 | NONE-FITTING | CONTINENTAL | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | JOHN H. MILLER, VICE PRESIDENT | 4146828241 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | POSSIBILITY OF PROBLEM WITH COUPLING AND/OR SERVICE LINE BEING INVESTIGATED.
2025-01-31 10:21 | YES | NO | 19860203 |  | 22189 | WASHINGTON NATURAL GAS CO | 4700 11TH AVE., N.E. | SEATTLE | KING | WA | 3 | 3 | NO | 1010 | 1986-11-03 | 0 | 0 | 150000 | 141942.1488 | 342714.6964 | Null | 0 | 15 |  | 19861103 | 45 | 45 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | STEEL |  | 0.75 | 0.188 | UNKNOWN | UNKNOWN | 0 | 1972 | UNDER GROUND OR UNDER WATER |  | DOUGLAS DAMN, SAFETY MANAGER | 2066226767 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-10-14 | YES | 1 |  | YES |  |  | NARRATIVE DESCRIPTION: CONTRACTOR (AZTECA ENTERPRISES, INC) WAS REMOVING CONCRETE PAVING AS PART OF A STREET REPAIR PROJECT. DURING REMOVAL THEY STRUCK A 3/4" STEEL GAS SERVICE THAT WAS ACCURATELY MARKED; PULLING IT FROM A CURB VALVE LOCATED ABOUT 2' FROM THE BUILDING. GAS ACCUMALATED IN THE BUILDING AND WAS APPARENTLY IGNITED BY AN OIL FURNACE COMING ON. THE EXPLOSION SEVERELY DAMAGED THE BUILDING. ONE PERSON WAS TREATED FOR SHOCK ONLY. THERE WERE NO PERSONAL INJURIES.
2025-01-31 10:21 | NO | NO | 19860204 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 7594 JELLISON COURT | ARVADA | JEFFERSON | CO | 3 | 3 | NO | 300 | 1986-10-04 | 0 | 0 | 0 | 0 | 0 | Null | 2 | 21 |  | 19861006 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE | CUSTOMER FUEL PIPING | BODY OF PIPE | BROKEN THREAD | POLYETHYLENE PLASTIC |  | 0.75 | 0.95 | SDR 11 | PLEXCO/NORMAC | 0 | 1973 | WITHIN/UNDER BUILDING | UNDERGROUND | TOMY L. WILSON, ACTING SUPERVISOR | 3035713858 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PRELIMINARY INVESTIGATION REVEALED TWO POSSIBLE CAUSES OF THIS INCIDENT (1) A BROKEN 0.75 INCH FUEL PIPE APPROXIMATELY FOUR FEET REST OF THE HOT WATER HEATER IN THE BASEMENT OF 7495 JELLISON CT. THE BREAK WAS ON THE PIPE THREADS ON THE 0.75 INCH SIDE OF A 1.0 INCH BY 0.75 INCH BELL REDUCER (2) A BURIED STEEL 0.625 INCH BY 0.75 REDUCING COMPRESSION COUPLING WAS FOUND SEPARATED FROM THE 0.75 POLYETHYLENE PIPE. IT APPEARED THAT THE FORCE OF THE EXPLOSION COULD HAVE CAUSED EITHER PIPE TO SEPARATE OF BREAK. THE INVESTIGATION IS CONTINUING AN EFFORT TO DETERMINE WHICH ITEM WAS THE CAUSE AND WHICH ITEM WAS THE RESULT.
2025-01-31 10:21 | NO | NO | 19860207 |  | 4499 | ENTEX INC | 410 SOUTH MOBBERLY | LONGVIEW | GREGG | TX |  | 0 | NO | 2230 | 1986-08-27 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 1 | 10 |  | 19860827 | 11.5 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  | PITTSBURG | 0 | 1968 | ABOVE GROUND |  | C.S. LIOLLIO, ENGINEER | 7136545498 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TOMER PIPING. (PRESSURE EXCEEDED ALLOWABLE LIMITS). FURTHER LABORATORY TESTS INDLIMITS). AFTER FURTHER REVIEW OF FIELD DOCUMENTATION OF EVENTS, IT WAS DISCOVERE
2025-01-31 10:21 | YES | NO | 19860209 |  | 11032 | LACLEDE GAS CO | 250 ST. EUGENE | FLORISSANT | ST LOUIS | MO | 3 | 3 | NO | 1930 | 1986-10-03 | 0 | 0 | 100000 | 94628.0992 | 228476.4642 | Null | 13 | 55 |  | 19861003 | 13 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | API 5L |  | 0 | 1955 | UNDER PAVEMENT |  | PAUL B. HUNKER, JR./ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-07-17 | YES | 3 | SPRAY PAINT | YES |  |  | METROPOLITAN SEWER DISTRICTS' CONTRACTORS WORK IN STREET DAMAGED SERVICE LINE CAUSED LEAK AT SERVICE 'T' ON MAIN ALLOWING GAS TO MIGRATE INTO BUILDING AND IGNITE. MARKED LOCATION OF MAINS AND SERVICES ON PAVEMENT WITH SPRAY PAINT.
2025-01-31 10:21 | YES | YES | 19860212 |  | 11680 | LONE STAR GAS CO | TENNISON & CARPENTER | PLANO | COLLIN | TX | 1 | 1 | NO | 830 | 1986-09-25 | 0 | 1 | 1000 | 946.281 | 2284.7646 | Null | 1 | 30 |  | 19860925 | 20 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 8 | 0 | NE 2306 | DISCO PIPE | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | C.R. SUMMERS, SUPERINTENDENT | 2142761171 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | NO |  |  | LINE CUT INTO. LABORER WALKED TO WHERE LINE WAS CUT AND LIT A CIGARETTE CAUSING
2025-01-31 10:21 | NO | NO | 19860215 |  | 2364 | CINCINNATI GAS & ELECTRIC CO | 663 EZZARD CHARLES DR. | CINCINNATI | HAMILTON | OH | 3 | 3 | NO | 1924 | 1986-11-13 | 0 | 0 | 20000 | 18925.6198 | 45695.2928 | YES | 9 | 55 |  | 19861114 | 17 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | NO DATA |  | 12 | 0.54 |  |  | 0 | 1936 | UNDER GROUND OR UNDER WATER |  | H.J. FANTETTI, DIRECTOR, REGULATORY CODES | 5136322671 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE 12: C.I. MAIN WAS LATER CRADLED BY A CONCRETE DUC ENCASEMENT. THIS DUC WASPART OF THE ELECTRICAL SYSTEM TO CARRY THE ELECTRICAL CONDUIT TO SUPPLY THE HOUSING PROJECT, WHICH WAS OWNED BY THE HOUSING PROJECT. THIS CONDITION ALONG WITHEARTH SETTLEMENT AND PROBABLE CONSTRUCTION TRAFFIC RESULTED IN THE MAIN BREAK.THE GAS MIGRATED INTO AN ABANDONED STEAM SYSTEM.
2025-01-31 10:21 | NO | NO | 19860216 |  | 2364 | CINCINNATI GAS & ELECTRIC CO | 1416-26 LINN ST. | CINCINNATI | HAMILTON | OH | 3 | 3 | NO | 437 | 1986-11-14 | 0 | 0 | 15000 | 14194.2149 | 34271.4696 | YES | 9 | 55 |  | 19861114 | 17 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 0.12 | 0.54 |  |  | 0 | 1936 | UNDER GROUND OR UNDER WATER |  | H.J. FANTETTI, DIRECTOR, REGULATORY CODES | 5136322671 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE 12" C.I. MAIN WAS LATER CRADLED BY A CONCRETE DUC ENCASEMENT. THIS DUC WASPART OF THE ELECTRICAL SYSTEM TO CARRY THE ELECTRICAL CONDUIT TO SUPPLY THEHOUSING PROJECT, WHICH WAS OWNED BY THE HOUSING PROJECT. THIS CONDITION ALONGWITH EARTH SETTLEMENT AND PROBABLE CONSTRUCTION TRAFFIC RESULTED IN THE MAINBREAK. THE GAS MIGRATED INTO AN ABANDONED STEAM SYSTEM.
2025-01-31 10:21 | YES | NO | 19860217 |  | 2364 | CINCINNATI GAS & ELECTRIC CO | 6TH & DALTON AT CARR | CINCINNATI | HAMILTON | OH | 3 | 3 | NO | 745 | 1986-11-08 | 0 | 0 | 250000 | 236570.2479 | 571191.1606 | YES | 2 | 40 |  | 19861108 | 15 | 35 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 24 | 0.75 |  |  | 0 | 1892 | ABOVE GROUND |  | H.J. FANTETTI, DIRECTOR, REGULATORY CODES | 5136322671 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 | MARKING ON PIPE ABOVE GRO | NO |  |  | CAUSE WAS DUE TO TRAIN DERAILMENT. THE WEIGHT OF THE TRAIN CARS PUSHED RAILROAD MAINTENANCE EQUIPMENT INTO SOFT GROUND. IT APPEARS WHEEL OF CRUSHED MAINTENANCE EQUIPMENT IMPEDED ITSELF IN SOFT GROUND STRIKING AND BREAKING C.I. MAIN.
2025-01-31 10:21 | YES | YES | 19860219 |  | 4510 | EQUITABLE GAS CO | 702 SELDON ST. | VERONA BOROUGH | ALLEGHENY | PA | 3 | 3 | NO | 1900 | 1986-11-07 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19861112 | 0.4 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER |  | STEEL |  | 6 | 0 |  |  | 0 | 1914 | OTHER | OPEN EXCAVATION | E.F. MOSES, JR., MANAGER OF TECHNICAL SERVICES DEPT. | 4125535340 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE EQUITABLE GAS EMPLOYEES WERE TAPPING A 6" MAIN LINE IN A 3 1/2' DEEP EXCAVATION TO DRAIN WATER FROM THE MAIN LINE. WHILE INSTALLING A DOUBLE SADDLE, A SURGE OF WATER SQUIRTED OUT FROM UNDER THE LOOSE SADDLE AND HIT A UTILITY LIGHT ADJACENT TO THE EXCAVATION SITE. IT IS SPECULATED THAT THE UTILITY LIGHT WAS INCLOSER PROXIMITY TO THE WORK AREA THAN THE TWO INJURED EMPLOYEES CLAIM SINCE ITIS HIGHLY UNLIKELY THAT A LOW PRESSURE MAIN HAD ENOUGH PRESSURE TO FORCE WATER THE APPROXIMATE 7' DISTANCE TO THE LIGHT. THE ACTION OF THE COLD WATER ON THE HOT LAMP CAUSED THE WORK LIGHT BULB TO SHATTER THUS EXPLOSING THE HOT FILAMENT ANDCAUSING THE GASEOUS ATMOSPHERE TO IGNITE MOMENTARILY (FLASH). BOTH EMPLOYEES WERE BURNED AND TREATED AT ST. MARGARET MEMORIAL HOSPITAL. ONE EMPLOYEE WAS RELEASED AND THE OTHER EMPLOYEE WAS TRANSFERRED TO WEST PENN HOSPITAL AND WAS ADMITTED FOR OBSERVATION. THE EMPLOYEE WAS DISCHARGED FROM THE HOSPITAL ON 11/8/86.THIS ACCIDENT IS CURRENTLY UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19860220 |  | 4510 | EQUITABLE GAS CO | 2701 WEST CARSON ST. | PITTSBURGH | ALLEGHENY | PA | 3 | 3 | NO | 1045 | 1986-11-12 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19861112 | 0.4 | 0.4 | BY CFR 192.619(A)(3) | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER |  | STEEL |  | 0 | 0 |  |  | 0 | 1986 | WITHIN/UNDER BUILDING |  | E.F. MOSES, JR., MANAGER OF TECHNICAL SERVICES DEPT. | 4125535340 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EQUITABLE GAS EMPLOYEE WAS PURGING A HOUSELINE IN A SMALL UTILITY ROOM AT 2701 WEST CARSON STREET WHEN GAS IGNITED (UNKNOWN SOURCE) CAUSING A BRIEF FLASH FIRE. ONE EMPLOYEE WAS ADMITTED TO MERCY HOSPITAL ON 11/12/86 WITH BURNS TO THE FOREHEAD AND EARS. HE WAS DISCHARGED FROM THE HOSPITAL ON 11/13/86. CAUSE OF IGNITION IS CURRENTLY UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19860221 | 1986-12-10 | 12390 | METROPOLITAN UTILITIES DISTRICT | 4109 NORTH 25TH AVENUE | OMAHA | DOUGLAS | NE | 68111 | 3 | NO | 230 | 1986-11-25 | 1 | 0 | 35000 | 33119.8347 | 79966.7625 | Null | 0 | 30 |  | 19861125 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE SIDE OF METER | OTHER | OPEN LINE | OTHER | DISCONNECTED FITTING | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DONALD D. BLOCKER | 4024498211 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON ARRIVAL, FIREMAN REPORTED GAS ODOR. COMPANY SERVICEMAN SHUT OFF METER INSIDE BASEMENT. INSPECTION REVEALED OPEN FUEL LINE TO KITCHEN RANGE. AFTER FIRE, METER TURNED BACK ON MOMENTARILY TO CONFIRM SUPPLY THRU OPEN FUEL LINE. SHUT METER OFF & CAPPED LINE. METER BACK ON FOR SIX MINUTES WITH NO MOVEMENT OF TEST HAD CONFIRMING INTERIOR FUEL LINES SECURE, BUT FOR OPEN LINE TO RANGE. OUTSIDE: SERVICE BARHOLED AND CHECKED W/F.I. ALL READINGS NEGATIVE. ADJACENT STRUCTURE & MAIN CHECKED W/F.I., AGAIN ALL NEGATIVE READINGS. REPORTED EXPLOSION & ENSUING FIRE. RESIDENCE DESTROYED. OPEN FUEL LINE FOUND DURING FIRE SCENE INSPECTION.
2025-01-31 10:21 | YES | YES | 19860222 |  | 2596 | COLUMBIA GAS OF OHIO INC | 437 NORTH GARFIELD AVE. | COLUMBUS | FRANKLIN | OH | 4 | 4 | NO | 1305 | 1986-11-11 | 0 | 4 | 25000 | 23657.0248 | 57119.1161 | Null | 0 | 12 |  | 19861111 | 0.3 | 1 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1950 | WITHIN/UNDER BUILDING |  | J.D. SALTER, MANAGER, CONSTRUCTION & MAINTENANCE | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | OCUPANT WAS REMOVING OLD COAL FURNACE FROM BASEMENT OF DWELLING. LOST CONTROL OF FURNACE WHICH FELL AGAINST GAS LINE WHERE IT CAME THROUGH BASEMENT WALL AND TURNED TO ENTER THE INLET OF GAS METER. ESCAPING GAS EXPLODED. LINE BROKE AT APPROXIMATELY 1251 HOURS, EXPLOSION AT 1305 HOURS, GAS SHUT-OFF AT 1317 HOURS.
2025-01-31 10:21 | NO | NO | 19860223 |  | 11800 | LOUISIANA GAS SERVICE CO | 807 TATE LOURS DRIVE | MANDEVILLE | ST TAMMANY | LA | 3 | 3 | NO | 1520 | 1986-11-24 | 0 | 0 | 8500 | 8043.3884 | 19420.4995 | Null | 0 | 35 |  |  | 72 | 80 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.95 | PE 3408 | PLEXCO | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETEHRF, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-10-24 | YES | 0 | PAINT | NO |  |  | SERVICE LINE WAS CUT BY DIGGING MACHINE. GAS IGNITED AND BURNED DIGGING MACHINE. NO INJURY TO OPERATOR.
2025-01-31 10:21 | YES | YES | 19870002 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 178 LOCKWOOD AVE. | YONKERS | WESTCHESTER | NY | 4 | 4 | NO | 1358 | 1986-12-03 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 5 |  | 19861203 | 6 | 12 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FLEXIBLE HOSE | OTHER | FLEXIBLE HOSE | OTHER | BRASS | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DOMINIC CASTELLANO | 2124604464 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS LEAKAGE IN BASEMENT APARTMENT RESULTED FROM BROKEN FLEXIBLE TUBING CONNECTION AT CUSTOMER'S COUNTER-TOP RANGE. BREAK APPARENTLY THE RESULT OF IMPACT FROM UTENSIL DRAWER UNDER COUNTER-TOP TANGE. EXPLOSION AND FLASH FIRE OCCURRED WHEN CUSTOMER LIT CIGARETTE. CUSTOMER SUFFERED 2ND AND 3RD DEGREE BURNS AND LATER DIED.
2025-01-31 10:21 | YES | YES | 19870006 |  | 8040 | ILLINOIS POWER CO | 101 ST. THOMAS LANE | CAHOKIA | ST CLAIR | IL | 3 | 3 | NO | 331 | 1986-12-07 | 0 | 2 | 54500 | 51572.314 | 124519.673 | Null | 2 | 0 |  | 19861207 | 28 | 35 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.38 | ASA A21.7 |  | 0 | 1955 | UNDER PAVEMENT |  | B. D. MCKINNEY | 2174246511 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 3:25 A.M. ON DECEMBER 7, 1986, ILLINOIS POWER COMPANY WAS NOTIFIED BY THE CAHOKIA POLICE DEPARMENT THAT GAS WAS "SPEWING" OUT OF THE STREET AT 100 ST. THOMAS LANE ON CAHOKIA. AT 3:31 A.M., THE CAHOKIA POLICE CALLED AGAIN REPORTING THAT THE HOUSE AT 101 ST. THOMAS LANE HAD BLOWN UP. UPON INVESTIGATION, ILINOIS POWERCOMPANY FOUND THAT THE 6-INCH CAST IRON GAS MAIN THAT SERVES THIS AREA HAD A HOLE APPROXIMATELY 2 INCHES WIDE AND 5 INCHES LONG. THE MIGRATION OF GAS FROM THE HOLE IN THE GAS MAIN AND THE SOURCE OF IGNITION FOR THE EXPLOSION AT 101 ST. THOMAS LANE ARE UNDETERMINED.
2025-01-31 10:21 | NO | NO | 19870007 |  | 4060 | EAST OHIO GAS CO | 504 SIXTH ST., VAULT | MCDONALD | TRUMBULL | OH | 3 | 3 | NO | 1320 | 1986-11-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19861128 | 1.5 | 1 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | REGULATOR/METER |  | OTHER |  | 0 | 0 |  |  | 0 | 0 | OTHER | UNDERGROUND VAULT | PAU;L OLEKSA | 2164326858 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WATER FLOODED VAULT CAUSING REGULATORS AND RELIEF VALVE TO MALFUNCTION. REGULATORS WERE NOT VENTED.
2025-01-31 10:21 | NO | NO | 19870009 |  | 12396 | MIAMI PIPE LINE CO | OSAWATOMIE RD & 295 | PAOLA | MIAMI | KS | 1 | 1 | NO | 1000 | 1986-11-26 | 0 | 0 | 500 | 473.1405 | 1142.3823 | Null | 0 | 30 |  | 19861126 | 210 | 360 | BY TEST | 450 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 0 | 0 |  |  | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | FRED H. GREEN | 9138783438 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-11-17 | YES | 2 |  | YES |  |  | HOUSTON CONTRACTING SEVERED LINE WHILE LAYING TELEPHONE CABLE.
2025-01-31 10:21 | NO | NO | 19870010 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 2521 S. MARTIN | LITTLE ROCK | PULASKI | AR | 3 | 3 | NO | 1500 | 1986-11-24 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 15 |  | 19861124 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTM 2513 | NIPAK | 1979 | 1982 | UNDER GROUND OR UNDER WATER |  | JIM BREWER | 5013702700 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-09-25 | YES | 3 | YELLOW PAINT | NO |  |  | THIRD PARTY CONSTRUCTION COMPANY HAD EXCAVATED AROUND AND BENEATH THE GAS SERVICE LINE SERVING 2521 S. MARTIN. IN THE PROCESS OF BACK FILLING THE EXCAVATION, ALOAD OF DIRT FROM A FRONT END LOADER OF A BACK-HOE WAS DUMPED INTO THE EXCAVATION ON TOP OF THE GAS SERVICE LINE. THE SUDDEN IMPACT PULLED THE PLASTIC GAS SERVICE LINE, WHICH HAD BEEN INSERTED INTO THE OLD STEEL SERVICE LINE, LOOSE FROM THE COMPRESSION COUPLING AT THE BASE OF THE RISER BESIDE THE HOUSE, ALLOWING GAS TO ESCAPE AT 40 PSIG.
2025-01-31 10:21 | NO | NO | 19870011 |  | 4499 | ENTEX INC | 504 WINSLOW | BELLAIRE | HARRIS | TX | 3 | 3 | NO | 1651 | 1986-11-21 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 0 | 19 |  | 19861121 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  | FISHER | 0 | 1986 | ABOVE GROUND |  | B. F. BROYLES | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | REGULATOR WAS BROKEN BY UNKNOWN PARTY, OVERPRESSURING HOUSELINE. IGNITION UNKNOWN. DAMAGE APPARENTLY CAUSED BY CAR HITTING METER LOOP
2025-01-31 10:21 | YES | NO | 19870013 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 250 WALSH AVE. | HAMILTON | GLENN | CA | 3 | 3 | NO | 1810 | 1986-05-25 | 0 | 0 | 502600 | 475600.8264 | 1148322.7093 | Null | 3 | 5 |  |  | 35 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | JOINT | FLANGED | CAST IRON | GRAPHITED ASBESTOS GASKET | 2 | 0.154 |  |  | 0 | 1965 | ABOVE GROUND |  | HOWARD M. MCKINLEY | 4159723204 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | STRUCTURE FIRE BURNED OUT FLANGE GASKET BETWEEN SERVICE RISER VALVE AND FILTER ON METER SET. ESCAPING GAS IGNITED.
2025-01-31 10:21 | NO | NO | 19870015 |  | 4499 | ENTEX INC | 410 S MOBBERLY | LONGVIEW | GREGG | TX |  | 0 | NO | 2230 | 1986-08-21 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 1 | 10 |  | 19860827 | 11.5 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  | PITTSBURG | 0 | 1968 | ABOVE GROUND |  | C. S. LIOLLIO | 7136545498 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INITIAL FIELD TEST REPORTS INDICATED REGULATOR ALLOWED EXCESSIVE PRESSURE ON CUSTOMER PIPING. (PRESSURE EXCEEDED ALLOWABLE LIMITS.) FURTHER LABORATORY TESTS INDICATED REGULATOR FUNCTIONED PROPERLY. (NORMAL LOCK-UP PRESSURE WITHIN ALLOWABLELIMITS.) AFTER FURTHER REVIEW OF FIELD DOCUMENTATION OF EVENTS, IT WAS DISCOVERED THAT SEVERAL FIELD TESTS WERE ACTUALLY PERFORMED INDICATING MALFUNCTION OF SERVICE REGULATOR.
2025-01-31 10:21 | YES | YES | 19870019 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2609 O ST. | SACRAMENTO | SACRAMENTO | CA | 3 | 3 | NO | 900 | 1986-12-10 | 2 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19861210 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J. B. STOUTAMORE | 4159723203 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CONTRACTOR WORKING FOR THE CUSTOMER HAD REMOVED THE ORIGINAL VENT ON THE FLOORFURNACE AND COVERED THE OPENING WITH SHEET METAL. A NEW VENT WAS INSTALLED ON THE OTHER SIDE OF THE FURNACE BUT IT DID NOT EXTEND INTO THE COMBUSTION CHAMBER.THE ORIGINAL VENT BEING BLOCKED CAUSED RECIRCULATION OF THE FLUE GASES AND CARBON MONOXIDE. THE CARBON MONOXIDE CAUSED THE ASPHYXIATION DEATH OF TWO ADULTS.
2025-01-31 10:21 | YES | NO | 19870020 |  | 22525 | WESTVILLE GAS COMMISSION | 114 N. SCOTT ST. | WESTVILLE | VERMILION | IL | 2 | 2 | NO | 1145 | 1987-01-05 | 0 | 0 | 70000 | 64796.1336 | 156448.1547 | Null | 11 | 50 |  | 19870105 | 18 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | 90 DEGREES, E11 | STEEL |  | 0.75 | 0.113 |  | NATIONAL U.S.A. | 1956 | 1957 | UNDER GROUND OR UNDER WATER |  | THOMAS FRANKINO | 2172677911 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CINTRACTOR FAILED TO NOTIFY WESTVILLE GAS & WATER SYSTEMS FOR LOCATION OF UTILITIES. CONTRACTOR DID NOT HAVE THE REQUIRED BUILDING PERMIT. CONTRACTOR WAS DIGGING A FOOTING TRENCH AT REAR OF HOUSE PRIOR TO BUILDING AN ADDITION TO THE HOUSE ON SAME LOCATION. CONTRACTOR STRUCK A 3/4" SERVICE LINE WITH A BACKHOE AND BROKEA 3/4" ELBOW ALLOWING 18# OF GAS PRESSURE TO MIGRATE UNDER HOUSE. SOURCE OF IGNITION IS UNDETERMINED.
2025-01-31 10:21 | NO | NO | 19870021 |  | 9070 | JACKSONVILLE GAS & WATER BOARD | 1314 SOUTH CHURCH ST | JACKSONVILLE | CALHOUN | AL | 36265 | 3 | NO | 2030 | 1986-12-22 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 9 | 0 |  | 19861222 | 124 | 127 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN | & SERVICE LINE | BODY OF PIPE |  | STEEL |  | 1 | 0.154 |  |  | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | SARA A JOHNSON - OFF SUPR | 2054357657 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | ON DECEMBER 22, 1986 AT APPROXIMATELY 2200 HOURS I WAS NOTIFIED BY BEEPER TO CUT THE GAS OFF AT 1314 SOUTH CHURCH STREET, JACKSONVILLE ALABAMA DUE TO A FIRE ONTHE SERVICE LINE. I ARRIVED APPROXIMATELY FIFTEEN MINUTES LATER AND DUG UP THE SERVICE LINE AND CUT OFF THE VALVE. THEN WE PROCEEDED TO CHECK THE AREA FOR ANY OTHER POSSIBLE LEAKS. A LEAK WAS FOUND ON A 3" HIGH PRESSURE MAIN. THIS WAS DUG UP AND THE VALVE WAS TURNED OFF AT APPROXIMATELY 1:55 A.M. THE GAS MAIN WAS REPAIRED AT APPROXIMATELY 1:00 P.M. AND SERVICE RESTORED TO AREA CUSTOMERS.
2025-01-31 10:21 | YES | YES | 19870022 |  | 13782 | NORTHERN STATES POWER CO | 521 GREEN ST. | RED WING | GOODHUE | MN | 3 | 3 | NO | 1420 | 1986-11-25 | 0 | 1 | 1200 | 1135.5372 | 2741.7176 | Null | 0 | 40 |  | 19861125 | 56 | 66 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2.38 | 0.216 | D-2513 | ALDYL-A | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | BARBARA K. BELEW | 6122214156 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | LEAK OCCURRED WHEN CABLE TV COMPANY HIT 2" PLASTIC MAIN GAS TRAVELLED UNDERGROUND TO 3 HOUSES: ONE HOUSE EXPLODED; OTHER HOUSES EVACUATED AND MONITERED
2025-01-31 10:21 | YES | YES | 19870023 |  | 4350 | ELIZABETHTOWN GAS CO | 27 NOMAHEGAN COURT | CRANFORD | UNION | NJ | 1 | 1 | NO | 1920 | 1987-01-10 | 0 | 2 | 1000000 | 925659.051 | 2234973.638 | Null | 3 | 44 |  | 19870110 | 15 | 35 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.038 | ASA 21-7 | INNERTITE | 0 | 1954 | UNDER PAVEMENT |  | EDWARD J. RAPOLAS | 2012895000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CIRCUMFERENTIAL CRACK ON 4" CAST IRON ELEVATED PRESSURE MAIN. APPROXIMATELY 30'FROM HOUSE.
2025-01-31 10:21 | NO | NO | 19870025 |  | 11680 | LONE STAR GAS CO | 528 HARRISON LANE | HURST | TARRANT | TX | 1 | 1 | NO | 830 | 1986-12-13 | 0 | 0 | 50000 | 47314.0496 | 114238.2321 | Null | 1 | 9 |  | 19861213 | 22 | 45 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | JOINT | COMPRESSION JOINT | POLYETHYLENE PLASTIC |  | 5 | 9 | SDR-9.3 |  | 0 | 0 | WITHIN/UNDER BUILDING | 3 | W. C. DEUBLER | 2147413711 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | FOUND 1/2" POLY PIPE PULLED OUT OF COMPRESSION COUPLING AT INLET RISER WHICH SETAT THE HOUSE.
2025-01-31 10:21 | YES | YES | 19870027 |  | 7040 | HAMILTON GAS DEPT, CITY OF | 11 MAGIE AVE. | FAIRFIELD | BUTLER | OH | 3 | 3 | NO | 45 | 1986-12-22 | 1 | 2 | 100000 | 94628.0992 | 228476.4642 | Null | 2 | 0 |  | 19861222 | 33 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER | CAST IRON | 6 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | RICHARD W. THOMAS | 5138685902 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | THE CITY OF HAMILTON HAS 6" CAST IRON MAIN CARRYING APPROXIMATELY 33 P.S.I. NATURAL GAS ON RIVER RD. PAST THE MAGIE AVE. INTERSECTION. CINCINNATI GAS AND ELECTRIC HAS A 4" STEEL MAIN PARALLEL WITH OUR MAIN APPROXIMATELY 4' AWAY. AFTER DETERMINING WHERE A POSSIBLE FRACTURE WAS LOCATED, WE IMMEDIATELY CLOSED A VALVE SHUTTING DOWN OUR MAIN. WE HAD THE BREAK REPAIRED WITH A STAINLESS STEEL REPAIR BAND AT APPROXIMATELY 3:30 A.M. AND REPRESSURIZED THE MAIN TO CHECK FOR LEAKS. HAVING FOUND NO LEAKS, WE STARTED AERATING THE GROUND OF GAS AND WAITED FOR DAYLIGHT. WHEN DAYLIGHT ARRIVED AROUND 8 A.M., WE AGAIN SHUT THE MAIN DOWN AND BLED THE GAS OUT OF THE MAIN. WE REMOVED THE REPAIR BAND AND CUT THE PIPE 18" ON EACH SIDE OF THE FRACTURE. A 3' PEICE OF 6" PLASTIC PIPE (PE 2306 SDR 11.5) WAS INSTALLED WITH A DRESSER COUPLING ON EACH END. THE MAIN WAS REPRESSURIZED, CHECKED FOR LEAKS, BACKFILLED AND CONTINUED PURGING THE GROUND OF GAS.
2025-01-31 10:21 | YES | YES | 19870028 |  | 15462 | PHILADELPHIA ELECTRIC CO | 449 MONUMENT AVE. | UPPER MORELAND | MONTGOMERY | PA | 3 | 3 | NO | 300 | 1986-12-25 | 0 | 1 | 100000 | 94628.0992 | 228476.4642 | Null | 4 | 30 |  | 19861225 | 10 | 25 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.44 | ASA A21.7 |  | 0 | 1962 | UNDER GROUND OR UNDER WATER |  | T. A. ROEHRIG | 2158414962 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | SIX INCH CAST IRON MECHANICAL JOINT PIPE WAS UNDER MONOLITHIC CURB AND GUTTER INSTALLED SUBSEQUENT TO MAIN INSTALLATION. SUDDEN CIRCUMFERENTIAL BREAK IN SIX INCH CAST IRON MECHANICAL JOINT MAIN APPARENTLY LED TO GAS MIGRATION INTO 449 W. MONUMENT AVENUE, RESULTING IN EXPLOSION, FIRE, AND ONE INJURY (FAIR CONDITON).
2025-01-31 10:21 | YES | YES | 19870029 |  | 15462 | PHILADELPHIA ELECTRIC CO | 902 SUMMIT LANE | ORELAND | MONTGOMERY | PA | 3 | 3 | NO | 250 | 1986-12-15 | 3 | 0 | 300000 | 283884.2975 | 685429.3927 | Null | 1 | 40 |  | 19861215 | 15 | 25 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.41 | ASA A21.7 |  | 0 | 1962 | UNDER GROUND OR UNDER WATER |  | T. A. ROEHRIG | 2158414962 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | SUBSIDENCE OCCURRED ALONG THE SEWER LATERAL TRENCH TO 900 SUMMIT LANE UNDER THEFOUR INCH MECHANICAL JOINT CAST IRON PIPE. SUDDEN CIRCUMFERENTIAL BREAK IN A FOUR INCH MECHANICAL JOINT CAST IRON PIPE APPARENTLY LED TO GAS MIGRATION INTO3902 SUMMIT LANE, RESULTING IN AN EXPLOSION, FIRE, THREE RESIDENTS WITH MINOR INJURIES, AND THREE DEATHS.
2025-01-31 10:21 | YES | NO | 19870031 |  | 2364 | CINCINNATI GAS & ELECTRIC CO | 6004 WIEHE RD. | CINCINNATI | HAMILTON | OH | 3 | 3 | NO | 1908 | 1987-01-03 | 0 | 0 | 120000 | 111079.0861 | 268196.8366 | Null | 2 | 0 |  | 19870103 | 14 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | AGA-B&S |  | 0 | 1937 | UNDER PAVEMENT |  | HUBERT J. FANTETTI | 5136322671 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | COMPANY RECEIVED A REPORT OF GAS ODOR. COMPANY PERSONNEL RESPONDED AND FOUND BUILDING DESTROYED BY EXPLOSION. UPON INVESTIGATION COMPANY FOUND A CIRCUMFERENTIALBREAK IN A 6" C. I. MAIN AND REPAIRED SAME. CAUSE IS UNKNOWN AT THIS TIME. STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19870032 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 15013 E. WARREN | DETROIT | WAYNE | MI | 3 | 3 | NO | 2351 | 1986-12-09 | 0 | 0 | 55000 | 52045.4545 | 125662.0553 | Null | 1 | 14 |  | 19861210 | 2 | 2 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 1.25 | 0.14 | API 5L |  | 0 | 1961 | ABOVE GROUND |  | BRUCE NIEMAN | 3132566615 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AUTOMOBILE RAN INTO THE BUILDING AND SHEARED OFF THE SERVICE LINE AT THE OUTSIDE BEND, BELOW THE SERVICE LINE SHUT OFF.
2025-01-31 10:21 | YES | YES | 19870034 |  | 2596 | COLUMBIA GAS OF OHIO INC | 186 GARDEN DR. | WINTERSVILLE | JEFFERSON | OH | 4 | 4 | NO | 2040 | 1987-01-24 | 0 | 1 | 25000 | 23141.4763 | 55874.3409 | Null | 1 | 50 |  | 19870126 | 0.3 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J.D. SLATER, MANAGER-CONSTRUCION/MAINTENANCE | 6144606000 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | INLET SERVICE LINE RISER BROKEN IN 90_ ELL WHERE IT COMES THROUGH FOUNDATIONS AS A RESULT OF GROUND MOVEMINT DUE TO FROST CONDITIONS, GAS IGNITED. PERSONAL INJURY WAS TO FACE, HANDS, AND HAIR OF ROY STEELE RELEASED ON 1/26/87 FROM HOSPITAL.
2025-01-31 10:21 | YES | NO | 19870035 |  | 13480 | NIAGRA MOHAWK POWER CORP | ROUTE NY11 | ADAMS CENTER | JEFFERSON | NY | 3 | 3 | NO | 143 | 1987-01-25 | 0 | 0 | 500000 | 462829.5255 | 1117486.819 | Null | 2 | 2 |  | 19870125 | 14 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | JOINT | FUSE | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTMD-2513 | PHILIPS | 1971 | 1971 | UNDER PAVEMENT |  | E.P. ALFIERE, SYSTEMS OPERATIONS DIRECTOR | 3154286711 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19870036 |  | 792 | ATLANTA GAS LIGHT CO | 107 N. ESTES ST. | CEDARTOWN | POLK | GA | 4 | 4 | NO | 257 | 1987-01-23 | 0 | 0 | 10000 | 9256.5905 | 22349.7364 | Null | 0 | 0 |  | 19870123 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CAST ALUMINUM | 0 | 0 | 1213B | RELIANCE | 1972 | 1973 | ABOVE GROUND |  | GLENN C. WELCH, MANAGER | 4047482520 | [6 empty] | Null |  | LIGHTNING OR FIRE | ICE CLOSED VENT OPENING O | NO |  | NO | 0 |  | NO |  |  | DURING FREEZING WEATHER WATER DRIPPING FROM A CUSTOMER'S ROOF COATED THE GAS REGULATOR WITH ICE PLUGGING THE VENT. THE REGULATOR THEN MALFUNCTIONED WHICH RESULTED IN THE HOUSE FIRE. TURNED OFF BY FIRE DEPT. PRIOR TO OUR ARRIVAL ON SITE.
2025-01-31 10:21 | YES | YES | 19870037 |  | 15469 | PHILADELPHIA GAS WORKS | 3029 "F" ST. | PHILADELPHIA | PHILADELPHIA | PA | 4 | 4 | NO | 930 | 1987-02-03 | 0 | 1 | 20000 | 18513.181 | 44699.4728 | Null | 2 | 45 |  | 19870203 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4.8 | 0.38 |  |  | 1898 | 1898 | UNDER PAVEMENT |  | LEROY C. SCHLAGEL, MANAGER DISTRIBUTION DEPT. | 2159783372 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | ON FEBRUARY 3, 1987, AT 3029 "F" STREET, A FIRE OCCURRED AT THIS RESIDENCE ON WHICH MR. W. TORRANCE BURNT HIS HAND AND HAIR. EXACT DETAILS OF THIS INCIDENT PRIOR TO 9:30 A.M. RELATE TO AN OBSERVATION OF THE SITE AND STATEMENTS MADE TO CUSTOMER SERVICE SUPERVISOR DOMINIC PONTARELLI BY MR. W. TORRANCE. MR. TORRANCE STATED THAT HE SMELLED HAS AND WENT TO THE BASEMENT TO INVESTIGATE. HE LIT A MATCH NEAR THE METER AREA AND A FLASH FIRE OCCURRED. MR. TORRANCE'S HAIR WAS SINGED. THE FRONT WALL OF THE BASEMENT REMAINED ON FIRE AND IGNITED CHRISTMAS DECORATIONSSTORED THERE. MR. TORRANCE BURNT HIS RIGHT HAND WHEN HE ATTEMPTED TO TURN ON A FAUCET IN THE LAUNDRY TUBS. MR. TORRANCE STATED THAT THE FAUCET HAD BEEN HEATED BY THE FIRE. THE FIRE DEPARTMENT WAS CALLED TO EXTINGUISH THE FIRE WHICH AFFECTED 3027 AS WELL AS 3029 "F" STREET. AT 9:30 A.M. THE FIRE DEPARTMENT AT THE SCENESTOPPED PGW SERVICEMAN R. WELSH WHO WAS ENROUTE TO ANOTHER LOCATION AND REQUESTED THAT HE CHECK FOR A GAS LEAK AT 3029 "F" STREET. AT 9:47 A.M. PGW RECEIVED ANORDER FROM THE FIRE DISPATCHER REQUESTING A COMPANY MAN. AT 10:00 A.M. CUSTOMERSERVICE FOREMAN G. ALBERT REPORTED THAT THE FIRE DEPARTMENT INDICATED A FIRE HAD STARTED WHEN THE CUSTOMER IN 3029 "F" STREET WENT TO THE BASEMENT AND LIT A MATCH. AT THIS TIME THERE WAS NO INDICATION OF A GAS LEAK IN 3029 "F" STREET. A CHECK OF HOUSES IN THE AREA REVEALED A 100 READING LEL WITH A GAS DETECTION INSTRUMENT AT THE FRONT FOUNDATION WALL. AT 10:35 A.M. THE DISTRIBUTION DISPATCHER WAS NOTIFIED AND SUPERVISORS, A CREW AND AN EMERGENCY VEHICLE WERE DISPATCHED. THEY ARRIVED ON THE SCENE AT 10:45, 10:48 AND 10:55 A.M. RESPECTIVELY. AFTER AN INVESTIGATION, LEL READINGS WERE FOUND IN FIVE HOUSES AT THE FRONT FOUNDATION WALL. THE DISTRIBUTION CREW EXCAVATED OVER THE MAIN IN THE ROADWAY AND FOUND A BROKEN 4" CAST IRON MAIN 4'6" WEST OF THE EAST CURB OF "F" STREET AND 124'11" NORTH OF THE NORTH CURB OF POTTER STREET AT 12:06 P.M. A REPAIR OF THE BREAK WAS MADE WITH A MECHANICAL TAP SPLIT SLEEVE. THES OPERATION WAS COMPLETED AT 1:00 P.M. THEHOUSES WERE RECHECKED AND THE ORIGINAL LEL READINGS DISSIPATED. A 60 LEL READING031 WAS THEN RENEWED. THE ENTIRE AREA WAS THEN RECHECKED AND NO READINGS WERE FOUND. OPERATIONS WERE COMPLETED AT 6:45 P.M.
2025-01-31 10:21 | YES | YES | 19870038 |  | 12816 | MOSS POINT MUNICIPAL GAS SYSTEM, CITY OF | JEFFERSON & LANDWOOD ST. | MOSS POINT | JACKSON | MS | 2 | 2 | NO | 1300 | 1987-01-29 | 0 | 2 | 50 | 46.283 | 111.7487 | Null | 1 | 0 |  | 19870202 | 5 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.25 |  |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | JIMMY MILES, SUPT. OF PUBLIC WORKS | 6014751151 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-11-13 | YES | 2 |  | YES |  |  | CAMBELL CONSTRUCTION COMPANY WERE LAYING A 24" SEWER FORCE MAIN FOR THE REGIONALWASTEWATER AUTHORITY EAST ON JEFFERSON STREET. WHEN CROSSING OUR 2 INCH GAS MAIN, THERE BACKHOE OPERATOR PULLED UP ON THE 2" GAS MAIN TO INSTALL THEIR PIPE UNDER THE GAS MAIN. IN DOING THIS HE CAUSED A GAS LEAK APPROXIMATELY 5 FT. NORTH OFTHEIR SEWER MAIN. THE CONTRACTOR BACK FILLED HIS DITCH, NOT REPORTING THE LEAK TO THE CITY GAS CREW. A FEW DAYS LATER THE CAMPBELL CONSTRUCTION CREW OF TWO MENWERE FIXING A LEAKING RELIEF VALVE IN THEIR SEWER MANHOLE AND NO. TWO MAN WAS GIVING HIM TOOLS OUTSIDE THE MANHOLE, WHEN NO. 1 MAN IN MANHOLE LIGHTS UP A CIGARETTE WHICH CAUSED A FIRE TO BURN THE TWO MEN. THE CONTRACTOR REPORTED THE ACCIDENT THE NEXT DAY, JANUARY 30, 1987 TO THE GAS DEPARTMENT ABOUT 1:00 P.M. AT THAT TIME THE GAS DEPARTMENT REPAIRED THE GAS LEAK.
2025-01-31 10:21 | YES | YES | 19870039 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 500 GRISWOLD AVE. | DETROIT |  | MI | 48226 | 3 | NO | 1316 | 1986-12-14 | 1 | 2 | 100000 | 94628.0992 | 228476.4642 | Null | 9 | 54 |  | 19861214 | 2 | 2 |  | 2 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.35 | ANSI A21.9 |  | 0 | 1932 | UNDER GROUND OR UNDER WATER |  | BRUCE NIEMAN MANAGER CODES AND STANDARDS | 3132566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | O EVIDENCE OF EARTH MOVEMENT.
2025-01-31 10:21 | YES | YES | 19870040 |  | 12876 | MOUNTAIN FUEL SUPPLY CO | 4905 S. STATE ST. | MURRAY | SALT LAKE | UT | 3 | 3 | NO | 2040 | 1987-01-10 | 0 | 4 | 550000 | 509112.478 | 1229235.5009 | Null | 1 | 0 |  | 19870111 | 45 | 60 | BY TEST | 125 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CAST ALUMINUM | 0 | 0 | 125 #INLET | SPRAGUE | 1977 | 1977 | WITHIN/UNDER BUILDING |  | W.D. BENNETT, VICE PRESIDENT, OPERATIONS | 8015345374 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AT 2040 HOURS ON JANUARY 10, 1987, A VEHICLE THAT WAS TRAVELING SOUTH ON THE WEST SIDE OF STATE STREET AT 4905 SOUTH TURNED LEFT CROSSING A 24" WIDE X 4" HIGH MEDIAN STRIP AND THREE LANES OF ONCOMING TRAFFIC AND THEN RAN INTO A BUILDING ONEAST SIDE OF STREET. VEHICLE WENT THROUGH WALL OF BUILDING AND STRUCK NATURAL GAS METER SET LOCATED INSIDE OF BUILDING SHEARING DIAPHRAGM PORTION OF SPRAGUE #645 REGULATOR FROM REGULATOR BODY ALLOWING 45 P.S.I.G. NATURAL GAS TO ESCAPE INSIDE BUILDING. THE DAMAGED VEHICLE STOPPED OVER THE METER SET AND THE FIRECOCK LOCATED ON THE OUTSIDE OF THE BUILDING. MOUNTAIN FUEL WAS NOTIFIED BY THE MURRAY FIRE DEPARTMENT AT 2050 HOURS AND A SERVICE TECHNICIAN WAS DISPATCHED TO THE SCENEOF THE ACCIDENT. AT 2052 HOURS THE GAS IGNITED RESULTING IN AN EXPLOSION AND FIRE WHICH DESTROYED THE BUILDING AND ITS CONTENTS AND CAUSED DAMAGE TO SURROUNDING BUILDINGS. THE SERVICE TECHNICIAN ARRIVED AT 2055 HOURS AND IMMEDIATELY SHUT OFF FIRECOCKS TO METER SETS AT 18 ADJOINING BUSINESS ESTABLISHMENTS ON BOTH SIDESOF THE DESTROYED BUILDING. AT 2140 HOURS THE VEHICLE WAS MOVED OFF OF THE DAMAGED METER SET AND THE FIRECOCK WAS SHUT OFF BY THE FIRE DEPT. STOPPING THE ESCAPING GAS. CONSTRUCTION PERSONNEL KILLED THE THREE SERVICE LINES SERVING THE BUILDING AS THE AREA WAS MADE SAFE BY THE FIRE DEPT. THE EXPLOSION INJURED THREE MURRAY CITY FIREMEN, TWO MURRAY CITY POLICE OFFICERS AND TWO GOLD CROSS AMBULANCE PERS ONNEL WHO WERE TAKEN TO LOCAL HASPITALS FOR TREATMENT. TWO FIREFIGHTERS AND TWOPOLICE OFFICERS WERE CONFINED FOR TREATMENT FOR TWO DAYS, THE OTHERS WERE TREATED AND RELEASED.
2025-01-31 10:21 | YES | YES | 19870042 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 5621 SHAMROCK DR. | N. LITTLE ROCK | PULASKI | AR | 3 | 3 | NO | 515 | 1987-01-14 | 0 | 2 | 100000 | 92565.9051 | 223497.3638 | Null | 5 | 30 |  | 19870114 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2.067 | 0.154 |  |  | 0 | 1957 | UNDER GROUND OR UNDER WATER |  | WILLIAM J. CONNELL, CODE COMPLIANCE COORDINATOR | 5013702721 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JANUARY 14, 1987 AT APPROXIMATELY 5:15 A.M AN EXPLOSION OCCURRED AT 5621 SHAMROCK DRIVE NORTH LITTLE ROCK, AR DESTROYING THE RESIDENCE. A COLD BREAK WAS FOUND IN A 2" CAST IRON GAS MAIN IN FRONT OF THE HOUSE.
2025-01-31 10:21 | YES | YES | 19870043 |  | 2568 | COLORADO SPRINGS, CITY OF | CANON AVE. & LOVER'S LANE | MANITOU SPRINGS | EL PASO | CO | 3 | 3 | NO | 948 | 1987-02-06 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 45 |  | 19870211 | 35 | 30 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | WAYNE BROOK, ENGINEERING & OPERATIONS SUPERINTENDENT | 3036365722 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAKING NATURAL GAS MIGRATED INTO A WATER REGULATOR VAULT; WORKERS ENTERED THE NEWLY CONSTRUCTED VAULT TO INSPECT THE CONSTRUCTION AND WERE INJURED FROM A FLASHFIRE. THE PROBABLE CAUSE OF THE FIRE WAS A MATCH STRUCK BY ONE OF THE WORKERS. THE GAS DIVISION TRACED THE LEAK TO A GASKET BETWEEN THE SERVICE SADDLE AND THE STEEL MAIN. THE LEAK WAS REPAIRED AND ONE CUSTOMER WAS WITHOUT SERVICE DURING THEREPAIR.
2025-01-31 10:21 | YES | YES | 19870045 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 1119 W. 5TH ST. | SAN BERNARDINO | SAN BERNARDINO | CA | 3 | 3 | NO | 1456 | 1987-01-29 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19870130 | 110 | 125 | BY TEST | 194 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 0 | ABOVE GROUND |  | L.M. STEWART, MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EMPLOYEE OF THE OPERATOR SUFFERED BURNS WHEN GAS BEING USED TO PURGE AIR FROM A NEWLY REPLACED 3/4" STEEL SERVICE IGNITED. SERVICE WAS PRESSURED TO ONE HUNDRED TEN(110) PSIG.
2025-01-31 10:21 | YES | NO | 19870046 |  | 15259 | PENNSYLVANIA GAS & WATER CO | 130 W. FRONT ST. | BERWICK BORO | COLUMBIA | PA | 4 | 4 | NO | 405 | 1987-02-20 | 0 | 0 | 310000 | 286954.3058 | 692841.8278 | Null | 0 | 10 |  | 19870220 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | REGULATOR & METER GASKET | OTHER | ALUMINUM METER CASE | 0 | 0 | AL-250 | AMER.-SINGER | 1980 | 1981 | ABOVE GROUND |  | J.M. GREGOR, MANAGER, LEAK DET. & CORROSION CONTROL | 7178298866 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | ON FRIDAY, FEBRUARY 20, 1987, A FIRE, SUSPECTED TO BE ARSON, DESTROYED TWO STORES AND BADLY DAMAGED A THIRD IN THE BUSINESS DESTRICT OF BERWICK, PENNSYLVANIA. THE TOTAL MARKET VALUE OF THE THREE BUILDINGS WAS PLACED AT $310,000.00 BASED ONASSESSED VALUATIONS ON RECORD AT THE COLUMBIA COUNTY COURTHOUSE. VALUE OF THE CONTENTS IS UNKNOWN AT THIS TIME. THE FIRE WAS REPORTED BY A CLEANING LADY, WORKING IN A RESTAURANT APPROXIMATELY ONE BLOCK AWAY WHO NOTICED FLAMES SHOOTING UP FROM THE REAR OF PAUL'S CHILDREN'S SHOP LOCATED AT 130 WEST FRONT STREET, BERWICK. THE FIRE ALARM WAS TURNED IN AT 4:05 A.M. SGT. ROGER NUNKESTER, OF THE BERWICKPOLICE DEPARTMENT, BEING THE FIRST ONE ON THE SCENE, ATTEMPTED TO EXTINGUISH THE FLAMES WHICH CONSISTED OF A PILE OF BURNING TRASH WHICH WAS ENGULFING A GAS METER AT THE REAR OF THE BUILDING AT 130 WEST FRONT STREET. THE FIRE SIMPLY IGNITED. AT 4:09 A.M., CENTRAL DISPATCH OF THE PENNSYLVANIA GAS & WATER COMPANY WAS NOTIFIED THAT THERE WAS A GAS METER ON FIRE ON WEST FRONT STREET. AT 4:10 A.M., JAYSMITH, SERVICEPERSON, WAS DISPATCHED AND ARRIVED AT THE SCENE AT 4:26 A.M. AT THIS TIME THERE WAS NO FIRE AT OR AROUND THE METER. MR. SMITH FOUND THAT THE FIREMEN HAD SHUT THE GAS OFF AT THE 3/4" GAS COCK LOCATED ON THE METER RISER. AFTER MAKING SURE THERE WAS NO LIVE GAS IN THE IMMEDIATE AREA, HE STOOD BY TO ASSIST IF NEEDED. THE GAS FACILITIES SERVICING PAUL'S CHILDREN'S SHOP CONSISTED OF: - 1/2 " PLASTIC GAS SERVICE CONNECTED TO A 6" STEEL GAS MAIN AT 45 P.S.I.G. FROM REAG ANS ALLEY IN THE REAR OF THE BUILDING. - PREBENT METER RISER. - AMERICAN-SINGER 143 REGULATOR SET 7" W.C. - AMERICAN-SINGER AL250 METER #533536 (INSTALLED 8/12/81-PRESSURE TESTED AT 100 P.S.I.G. AT THE TIME OF INSTALLATION-LOCATED OUTSIDEREAR PF BUILDING). UPON INVESTIGATION BY WILLIAM J. CEASE, SUPERVISOR AND JOSEPH S. ZERBE, FOREMAN OF THE PENNSYLVANIA GAS & WATER COMPANY, TROOPER JAMES POWELL, PENNSYLVANIA STATE POLICE AND GARY BANKES, BERWICK FIRE CHIEF, IT WAS FOUND THAT THE GAS METER AND THE GAS REGULATOR WERE BADLY SCORCHED AND THE GASKETS WERE BURNED OUT FROM AN EXTERNAL SOURCE. IT WAS ALSO FOUND THAT THE INSULATED 3/4" UNION LOCATED ON THE RISER WAS BADLY BURNED AND THE INSULATED GASKET WAS DESTROYED ALLOWING 45 P.S.I. GAS TO ESCAPE INTO THE ATMOSPHERE. IT WAS DETERMINED THAT THE FIRE ORIGINATED FROM THE BOXES AND TRASH THAT WAS PILED ON AND AROUND THE GAS FACILITIES ALLEGEDLY IGNITED BY THE SUSPECTED ARSONIST. THE FIRE FROM THE TRASH IN TURN BURNED OUT THE GASKET IN THE METER AND THE GASKET AND DIAPHRAGM IN THEREGULATOR ALLOWING GAS TO ESCAPE AND IGNITE. THE RUBBER INSULATION BURNED AWAY IN THE 3/4" UNION ON THE RISER LOCATED AHEAD OF THE REGULATOR ALLOWING 45 P.S.I.GAS TO IGNITE AND CREATE A BLOW TORCH AFFECT WHICH BURNED THROUGH A SECTION OF PLYWOOD USED TO BOARD UP A WINDOW LOCATED ABOVE THE METER SET. (THE REST OF THE STRUCTURE AT THE REAR OF THE BUILDING WAS OF BRICK CONSTRUCTION). THE FIRE CONTINUED TO BURN INTO THE BUILDING. THE METER AND REGULATOR ASSEMBLY WAS REMOVED BY PENNSYLVANIA GAS & WATER COMPANY PERSONNEL AND TURNED OVER TO JAMES POWELL, FIREMARSHAL TO BE INSPECTED AND DISASSEMBLED AT A LATER DATE. WHEN REMOVING THE REGULATOR AND METER ASSEMBLY, IT WAS NOTICED THAT THE 3/4" X 2" NIPPLE CONNECTING THE WING COCK TO THE INSULATED UNION WAS FULL OF WATER INDICATING THAT IT HAD TO ENTER BACK THROUGH THE UNION FROM THE FIREMEN'S HOSES. ON WEDNESDAY, FEBRUARY 18, 1987, TWO DAYS BEFORE THE FIRE, THE LEAK DEPARTMENT OF THE PENNSYLVANIA GAS &WATER COMPANY HAD MADE A FROST PATROL SURVEY OF THE GAS LINES IN THIS IMMEDIATEAREA WITH NEGATIVE RESULTS. ON SATURDAY, FEBRUARY 21, 1987, ONE DAY AFTER THE FIRE, FURTHER TESTS WERE MADE ON THE GAS SERVICE AND AGAIN RESULTED IN NEGATIVE READINGS. ON THURSDAY, FEBRUARY 26, 1987, THE SERVICE WAS RETIRED AT THE MAIN AND
2025-01-31 10:21 | NO | NO | 19870048 |  | 11800 | LOUISIANA GAS SERVICE CO | CORNER OF FREDERICKS & METAIRIE ROAD | METAIRIE | JEFFERSON | LA | 3 | 3 | NO | 1550 | 1987-02-22 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 0.4 | 0.4 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.41 | CLASS 10 |  | 0 | 1926 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | YES |  | YES | 2 |  | NO |  |  | CRESCENT CONSTRUCTION COMPANY, SUB CONTRACTOR FOR GRADY CRAWFORD CONSTRUCTION COMPANY, DUG AND SHEETED A TRENCH APPROXIMATELY 11' DEEP AND 4' WIDE AND CROSSINGOUR 6" C.I.-L.P. GAS MAIN ON A 45 DEGREE ANGLE AT A POINT 46' SOUTH OF METAIRIEON THE WEST SIDE OF FREDERICKS AVENUE IN METAIRIE, LOUISIANA, ON 2-13-87, FOR THE PURPOSE OF INSTALLING A FIBRE OPTICS TELEPHONE CABLE FOR SPRINT. ALL OF THEIRCONSTRUCTION AT THIS LOCATION WAS OBSERVED BY L.G.S. REPRESENTATIVE N. FAUCHEUX. AT NO TIME DURING THEIR CONSTRUCTION WAS OUR MAIN DAMAGED. ON REQUEST BY FAUCHEUX, CRESCENT CONSTRUCTION INSTALLED WOOD SUPPORT UNDER OUR GAS MAIN ACROSS THE TRENCH. THE TELEPHONE CABLE WAS INSTALLED APPROXIMATELY 4' BELOW THE GAS MAIN. GRADY CRAWFORD CONSTRUCTION BACKFILLED THE TRENCH AS FOLLOWS: THE SHEETING WAS CUT OFF ABOUT 12" BELOW FINISHED GRADE AND LEFT IN PLACE. THE TRENCH WAS FILLED WITH SUGAR SAND TO THE GAS MAIN LEVEL AND PACKED UNDER THE GAS MAIN FOR SUPPORT. THE TRENCH WAS THEN FILLED TO A POINT APPROXIMATELY 2' ABOVE THE GAS MAIN WITH SUGAR SAND AND THEN TO THE SURFACE WITH SPOIL REMOVED DURING EXCAVATION. THE AREA WAS THEN DRESSED. FAUCHEUX STATED THAT HE OBSERVED NO DAMAGE TO THE GAS MAIN DURING CONSTRUCTION AND NO INDICATION OF GAS LEAKAGE FOR THE REMAINDER OF THE WEEK.THERE WAS A SEVERE RAIN STORM ON THE NIGHT OF 2-21-87, AND AREA RESIDENTS STATED THAT THE AREA FLOODED TO A DEPTH OF 1.5 FEET. THE FIRST REPORT OF NO GAS WAS RECIEVED AT 3:50 P.M., 2-22-87. I ASSUME THE DISTURBED AREA SETTLED UNDER THE FLOODED CONDITION AND CAUSED THE MAIN TO BREAK.
2025-01-31 10:21 | YES | NO | 19870049 |  | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 633 HANKEN ROAD | BOUND BROOK | SOMERSET | NJ | 4 | 4 | NO | 1134 | 1987-02-19 | 0 | 0 | 150000 | 138848.8576 | 335246.0457 | Null | 0 | 28 |  | 19870219 | 22 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | ENTIRE BLDG. DESTROYED | C.W. GREVENITZ, GENERAL MANAGER-GAS T&D | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE, OF UNKNOWN ORIGIN, DESTROYED A SINGLE FAMILY FRAME HOUSE. NO GAS LEAKAGEWAS FOUND. THERE WERE NO FATALITIES OR PERSONAL INJURIES.
2025-01-31 10:21 | NO | NO | 19870051 |  | 4473 | ENERGAS CO | 421 B CONLEN | DALHART | DALLAM | TX | 3 | 3 | NO | 1600 | 1987-02-06 | 0 | 0 | 1000 | 925.6591 | 2234.9736 | Null | 0 | 15 |  | 19870206 | 0.5 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER WAS REMOVING RANGE FROM HOUSE. HE TURNED OFF WHAT HE BELIEVED WAS THE METER SERVING THE HOUSE, BUT HE TURNED OFF THE METER TO ANOTHER CUSTOMER LEAVINGHIS GAS ON. HE WENT BACK INTO THE HOUSE AND BEGAN TO REMOVE THE COOK STOVE. WHEN HE DISCONNECTED THE APPLIANCE, THE GAS BEGAN TO ESCAPE. THIS GAS IGNITED CAUSING MINOR DAMAGE TO THE AREA AROUND THE RANGE.
2025-01-31 10:21 | NO | NO | 19870053 |  | 4499 | ENTEX INC | 3414 SAMPSON | HOUSTON | HARRIS | TX | 3 | 3 | NO | 1830 | 1987-01-30 | 0 | 0 | 5000 | 4628.2953 | 11174.8682 | Null | 0 | 30 |  | 19870130 | 20 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 | AL-175 | AMER.MTR.CO. | 0 | 0 | ABOVE GROUND |  | B.F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CAR STRUCK METER, ESCAPING GAS IGNITED AND BURNED ADJACENT BUILDING.
2025-01-31 10:21 | NO | NO | 19870054 |  | 18532 | SOUTHERN UNION GAS CO | 7620 N. LAMAR | AUSTIN | TRAVIS | TX |  | 0 | NO | 1502 | 1987-02-13 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19870213 | 0.3 | 0.3 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | GAS APPLIANCES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | GILES GOBER, ENGINEER | 5124775852 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | RAILROAD COMMISSION WAS UNDULY NOTIFIED DUE TO THIS EXPLOSION BEING DOWNSTREAM OF THE METER. RESIDENT WAS THOUGHT TO BE ATTEMPTING TO COMMIT SUICIDE BY RELEASING NATURAL GAS.
2025-01-31 10:21 | NO | NO | 19870055 |  | 22168 | WARREN GAS DEPT, CITY OF | 126 W. JOHNSON | WARREN | MARSHALL | MN |  | 0 | NO | 1430 | 1987-02-10 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19870211 | 3 | 21 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | REGULATING STATION | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MARLIN ANDERSON, GAS DEPT. | 2187455343 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | WE WERE IN THE PROCESS OF TESTING RELIEF VALVES AT THE TOWN REGULATING STATION WHEN THE MAN WE HAD HIRED ASKED ME TO SHUT DOWN THE MAIN VALVES FOR THE TOWN SO HE COULD HEAR THE RELIEF VALVE START TO OPEN. THE VALVE WOULD NOT OPERATE SO HE TOLD ME TO GET AN ASSORTMENT OF TOOLS FROM THE SHOP. I WENT FOR THE TOOLS AND FORGOT TO OPEN THE VALVES. WHEN I WAS AT THE SHOP AND REMEMBERED THE VALVES WERE CLOSED I WENT BACK TO THE STATION BUT THE PRESSURE WAS TOO LOW FOR THE SYSTEM ANDTHE TOWN WAS OUT. ALL OF THE CUSTOMERS WERE RELIGHTED IN ABOUT 8 HRS. EXCEPT FOR 12 CUSTOMERS THAT WERE NOT RELIGHTED FOR 26 HRS.
2025-01-31 10:21 | YES | YES | 19870056 |  | 2568 | COLORADO SPRINGS, CITY OF | N. UNION BLVD. & YAMPA ST. | COLORADO SPRINGS | EL PASO | CO | 3 | 3 | NO | 1845 | 1987-01-30 | 0 | 2 | 44000 | 40728.9982 | 98338.8401 | Null | 5 | 27 |  | 19870130 | 15 | 20 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4.5 | 0.375 | TUBING |  | 0 | 1947 | UNDER PAVEMENT |  | WAYNE BOOKER, ENGINEERING & OPERATIONS SUPERINTENDENT | 3036365722 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | AFTER IDENTIFYING A LEAK LOCATION ON AN UNDERGROUND GAS MAIN, GAS DIVISION PERSONNEL EXCAVATED TO PINPOINT THE LEAK ON THE PIPELINE. WHILE ATTEMPTING TO PIN POINT THE LEAK, THE LEAKING GAS WAS IGNITED BY AN UNKNOWN SOURCE. FOUR GAS DIVISION EMPLOYEES SUFFERED FIRST AND SECOND DEGREE BURNS TO THEIR HANDS AND FACE. TWO WERE TREATED AND RELEASED AT A LOCAL HOSPITAL, AND TWO WERE HOSPITALIZED FOR APPROXIMATELY ONE WEEK. TWO GAS DIVISION BACKHOES WERE ALSO DESTROYED IN THE FIRE. SINCE THE FIRE WAS UNDER CONTROL, TIME WAS TAKEN TO USE VALVES AND CONTROL FITTINGS TO ISOLATE A SMALL AREA NEAR THE INCIDENT, THIS INTERRUPTED GAS SERVICE TO ONLY TWELVE(12) CUSTOMERS
2025-01-31 10:21 | NO | NO | 19870057 |  | 2652 | COMMONWEALTH GAS CO | 310 WOOD AVE. | HYDE PARK |  | MA | 1 | 1 | NO | 1615 | 1987-02-18 | 0 | 0 | 5000 | 4628.2953 | 11174.8682 | Null | 0 | 0 |  | 19870219 | 0.3 | 60 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | DOWNSTREAM OF METER | OTHER | HOMEOWNER'S PIPING | OTHER | BLACK IRON PIPING | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | KAREN BOUJICANIAN, DEPT. SUPERVISOR, SAFETY & TRAINING | 6174817900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE DEPARTMENT INFORMED RESPONSIBLE SERVICE PERSON THAT THERE WAS A POSSIBLE EXPLOSION. COM/GAS IS INVESTIGATING. PLUMBING CONTRACTOR WORKING ON SITE.(CONTINENTAL PLUMBING COMPANY)
2025-01-31 10:21 | YES | NO | 19870058 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 18636 MURRAY HILL | DETROIT | WAYNE | MI | 3 | 3 | NO | 927 | 1987-02-19 | 0 | 0 | 75000 | 69424.4288 | 167623.0228 | Null | 4 | 30 |  | 19870219 | 2 | 2 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.35 | ANSI A21.9 |  | 0 | 1939 | UNDER GROUND OR UNDER WATER |  | BRUCE NIEMAN, MANAGER CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE CAUSE OF THE CIRCUMFERENTIAL FRACTURE IN THE 4" CAST IRON MAIN IS UNKNOWN; NO EVIDENCE OF EARTH MOVEMENT
2025-01-31 10:21 | YES | YES | 19870061 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1691 21ST AVE. | SAN FRANCISCO | SAN FRANCISCO | CA | 3 | 3 | NO | 1635 | 1987-02-08 | 1 | 1 | 150000 | 138848.8576 | 335246.0457 | Null | 0 | 25 |  | 19870208 | 7 | 9.2 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JAMES B. STOUTAMORE, VICE PRESIDENT, GAS OPERATIONS | 4159733204 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | GASOLINE IN GARAGE SPREAD TO WATER HEATER PILOT LIGHT, IGNITING GASOLINE. RESULTING FIRE SPREAD TO METER SET, DESTROYING REGULATOR AND METER, IGNITING NATURAL GAS.
2025-01-31 10:21 | NO | NO | 19870062 |  | 11800 | LOUISIANA GAS SERVICE CO | 504 N. BEAU CHENE BOULEVARD | MANDEVILLE | ST TAMMANY | LA | 3 | 3 | NO | 1632 | 1987-02-23 | 0 | 0 | 4500 | 4165.4657 | 10057.3814 | Null | 0 | 30 |  |  | 70 | 80 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE3408 | PLEXCO | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-02-12 | YES | 3 | YELLOW PAINT | NO |  |  | SERVICE LINE WAS CUT BY DIGGING MACHINE. GAS IGNITED AND BURNED DIGGING MACHINE. NO INJURY TO OPERATOR OR OTHERS. CUT 3/4" GAS SERVICE LINE WHILE INSTALLING TVCABLE.
2025-01-31 10:21 | YES | YES | 19870063 |  | 792 | ATLANTA GAS LIGHT CO | TUCKER NORCROSS ROAD & OLD NORCROSS ROAD | TUCKER | GWINNETT | GA | 2 | 2 | NO | 730 | 1987-02-16 | 0 | 3 | 0 | 0 | 0 | Null | 2 | 0 |  | 19870227 | 240 | 300 | BY TEST | 540 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | AP1 5L |  | 1959 | 1959 | UNDER PAVEMENT |  | CLAYTON H. PREBLE, MANAGER | 4044764861 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | 3/4" SERVICE CROSSED SEVERAL OTHER UTILITIES IN THE AREA.(SOUTHERN BELL TELEPHONE DUCT, 2" GALVANIZED WATER LINE, 4" TRANCITE WATER LINE, SOUTHERN BELL DIRECT BURIAL CABLE, 2 PLASTIC WATER SERVICES, 18" CONCRETE STORM DRAIN). GAS WAS LEAKING FROM A SERVICE LINE AND ENTERED A MANHOLE. THE GAS WAS SUBSEQUENTLY IGNITED BY WORKMEN WHO HAD ENTERED THE MANHOLE WITHOUT VENTING IT OR CHECKING FOR PRESENCE OF NATURAL GAS. REPORT HELD UP PENDING LAB REPORT TO ESTABLISH IF NATURAL GAS WAS ACTUALLY INVOLVED.
2025-01-31 10:21 | YES | YES | 19870064 |  | 18536 | SOUTHWEST GAS CORP | 1415 N 15TH AVE. | PHOENIX | MARICOPA | AZ | 3 | 3 | NO | 1911 | 1987-02-12 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 30 |  | 19870212 | 30 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | A.B.S. | 2 | 0.9 |  |  | 0 | 1971 | WITHIN/UNDER BUILDING |  | RICHARD BREEDLOVE, MANAGER, OPERATIONS | 6024845222 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | THE PIPE BEARS DAMAGE MARK WHICH APPEARS TO BE THE CAUSE OF THE FAILURE. IT IS NOT KNOWN IF THE DAMAGE OCCURRED UPON INSTALLATION OR WHEN A CROSSING SUBSTRUCTURE WAS SUBSEQUENTLY INSTALLED.
2025-01-31 10:21 | NO | NO | 19870065 |  | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | 5630 PINEBRANCH RD. & 2500 CUSTOMER OUTA | COLUMBIA | RICHLAND | SC | 3 | 3 | NO | 745 | 1987-02-19 | 0 | 0 | 30000 | 27769.7715 | 67049.2091 | YES | 0 | 0 |  | 19870219 | 0 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | PROPANE/AIR PLANT | OTHER | OPERATIONAL CONTROLS | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | SHERMAN J. GOODWIN | 8037483781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | ERROR IN DESIGN & OPERATI | ON FEBRUARY 19, 1987 SERVICE TO APPROXIMATELY 2,500 GAS CUSTOMERS IN COLUMBIA, SOUTH CAROLINA WAS INTERRUPTED. THE PROBLEM APPEARS TO HAVE ORIGINATED IN THE MIXING OPERATION OF A PROPANE AIR PLANT BEING CONSTRUCTED AND INSTALLED FOR US. FOR A SHORT PERIOD THE SENDOUT MIXTURE WAS NOT COMPATIBLE WITH NATURAL GAS COMBUSTION AND A NUMBER OF CUSTOMERS EXPERIENCED PILOT OUTAGES. IN AN ISOLATED INCIDENT, AN EXPLOSION OCCURRED IN A HOUSE AT 5630 PINEBRANCH RD. THE EXPLOSION IS BELIEVED TO HAVE RESULTED FROM FAILURE OF THE SAFETY VALVE TO SHUT OFF AFTER THE PILOT LIGHT WENT OUT. NO FIRE OR PERSONAL INJURIES RESULTED, BUT THERE WAS HEAVY STRUCTURAL DAMAGE.
2025-01-31 10:21 | NO | NO | 19870066 |  | 13360 | NEW ORLEANS PUBLIC SERVICE INC | ST. BERNARD AVE. & CASTIGLIONE ST. | NEW ORLEANS | ORLEANS | LA | 3 | 3 | NO | 1802 | 1987-03-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 26 |  |  | 11 | 12 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.48 |  |  | 0 | 1941 | UNDER PAVEMENT |  | ROBERT W. VAUGHN, GAS DISTRIBUTION SUPERINTENDENT | 5045953511 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 4' WIDE X 10' DEEP TRENCH CROSSING THE GAS MAIN HAD BEEN OPENED BY AN OUTSIDEPARTY FOR INSTALLATION OF A SEWER LINE AND BACKFILLED TWO DAYS PRIOR TO THE INCIDENT. THE ACTUAL BREAK IN THE GAS MAIN WAS LOCATED APPROXIMATELY 10' FROM THE CENTER OF THE AFOREMENTIONED TRENCH. THE TRENCH HAD BEEN SHEETED UP TO EACH SIDE OF THE GAS MAIN. THE GAS MAIN WAS 3'-7' DEEP.
2025-01-31 10:21 | NO | NO | 19870067 |  | 4473 | ENERGAS CO | 404 CHISOLM | FRITCH | CARSON | TX | 3 | 3 | NO | 30 | 1987-03-01 | 0 | 0 | 5000 | 4628.2953 | 11174.8682 | Null | 0 | 30 |  | 19870301 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | A-25 |  | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | DRIVER OF PICKUP LOST CONTROL OF VEHICLE. HIT METER SETTING. FIRE DESTROYED PICKUP AND METER.
2025-01-31 10:21 | NO | NO | 19870068 |  | 18532 | SOUTHERN UNION GAS CO | 4TH & NUECES | AUSTIN | TRAVIS | TX | 4 | 4 | NO | 939 | 1987-01-27 | 0 | 0 | 30000 | 27769.7715 | 67049.2091 | Null | 0 | 4 |  | 19870127 | 40 | 60 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | DRESSER COUPLING ON MAIN | FITTING |  | STEEL |  | 10 | 0.219 | API 5L B |  | 0 | 1964 | UNDER PAVEMENT |  | GILES GOBER, ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | CONTRACTOR WAS ATTEMPTING TO STOPPER OFF A SECTION OF EXPOSED MAIN DOWNSTREAM OF A DRESSER COUPLING. THE STOPPERING EQUIPMENT WAS NOT SECURELY ANCHORED AND THEPIPE PULLED LOOSE FROM THE DRESSER COUPLING AND IGNITED.
2025-01-31 10:21 | NO | NO | 19870069 |  | 18532 | SOUTHERN UNION GAS CO | 124 S. HORIZON BLVD. | EL PASO | EL PASO | TX | 3 | 3 | NO | 740 | 1987-02-27 | 0 | 0 | 1555 | 1439.3998 | 3475.384 | Null | 1 | 30 |  |  | 28 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.141 | API-5L-A25 | REPUBLIC STEEL | 1979 | 1979 | UNDER GROUND OR UNDER WATER |  | EDWARD H. SMITH, DISTRICT ENGINEER | 9155446300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A CONSTRUCTION COMPANY EMPLOYEE WAS CUTTING GRADE WITH A FRONT-END LOADER WHEN HE HIT A 4" STEEL MAIN PRODUCING A 2" HOLE. THERE WAS NO IGNITION OF GAS AND NO INJURIES.
2025-01-31 10:21 | NO | NO | 19870070 |  | 18532 | SOUTHERN UNION GAS CO | 1278 FARM ROAD 1110 | EL PASO | EL PASO | TX | 3 | 3 | NO | 36 | 1987-02-24 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  |  | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | API-5L-A25 | REPUBLIC STEEL | 1979 | 1979 | ABOVE GROUND |  | EDWARD H. SMITH, DISTRICT ENGINEER | 9155446300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER ASSEMBLY | NO |  |  | AUTOMOBILE STRUCK METER AT 1278 RARM ROAD 1110 AT 12:30 A.M. ON FEBRUARY 24, 1987. THE 3/4" SERVICE RESER WAS BROKEN ON THE INLET SIDE OF THE SERVICE VALVE, RESULTING IN THE ESCAPE OF GAS. IGNITION OCCURRED AND THE AUTOMOBILE WAS DESTROYED. NO INJURIES OR OTHER PROPERTY DAMAGE WAS EXPERIENCED.
2025-01-31 10:21 | YES | YES | 19870071 |  | 3260 | DELTA NATURAL GAS CO INC | AMERICAN GREETING ROAD | CORBIN | LAUREL | KY | 3 | 3 | NO | 1340 | 1987-03-11 | 1 | 2 | 1200 | 1110.7909 | 2681.9684 | Null | 0 | 5 |  | 19870311 | 40 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | 2306 SDR11.5 | DRISCOPIPE 6500 | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | ALAN L. HEATH, VICE PRESIDENT, OPERATIONS & ENGINEERING | 6067446171 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DELTA'S SOUTHERN CONSTRUCTION CREW CONSISTING OF CARL COX, FOREMAN, SHELBY SMITH, ELBERT BARGO, CLARENCE ABNER, HERMAN BROUGHTON, AND CHARLES LAMBDIN WAS REPLACING APPROXIMATELY FIVE HUNDRED(500) FEET OF FOUR(4) INCH STEEL MAIN WITH FOUR(4) INCH PLASTIC MAIN ON AMERICAN GREETING ROAD. DELTA'S THREE INSPECTORS, BENNY HENSLEY, LEAD INSPECTOR, ROBERT COBB AND LARRY BARTON, WERE ALL ASSISTING IN THISREPLACEMENT PROJECT. ON MARCH 11,1987, AT APPROXIMATELY 1:40 P.M. WHILE IN THE PROCESS OF BLEEDING DOWN THE ISOLATED SECTION IN PREPARATION FOR THE TIE-IN, THEEXISTING FOUR(4) INCH PLASTIC MAIN APPARENTLY BROKE. CARL COX, CLARENCE ABNER AND CHARLES LAMBDIN WERE IN THE DITCH AT THAT TIME. THE GAS FLOWED FOR APPROXIMATELY TEN(10) SECONDS AS CARL TRIED TO REALIGN THE PIPE TO SLOW THE FLOW. CARL TOLD CLARENCE AND CHARLES TO GET OUT OF THE DITCH AND HE WOULD GO CHECK THE LINE STOPPER FITTING. BEFORE THE THREE MEN COULD CLEAR THE DITCH, THE GAS IGNITED. THE HEAT FROM THE FIRE MELTED THE LIVE PLASTIC LINE THUS FEEDING THE FIRE UNTIL THE SYSTEM WAS SHUT DOWN. THERE IS NO INDICATION THAT THE LINE STOPPER FITTING WAS NOT HOLDING PROPERLY. CLARENCE RAN OUT OF THE FIRE CHARLES COLLAPSED AND WAS HELPED OUT BY CARL. THE OTHER EMPLOYEES EXTINGUISHED THE FLAMES ON THEIR CLOTHING. HARRY SOWDERS, DISTRIBUTION SUPERVISOR OF THE CORBIN SYSTEM AND TIM WALKER, A CUSTOMER SERVICE REPRESENTATIVE IN THE CORBIN SYSTEM, WERE WITH BENNY HENSLEY AT THE AMERICAN GREETING CARD METER MONITORING THE PRESSURE. THE THREE NOTICED A PRESSURE DROP ON THE MAIN AND TRIED TO MAKE RADIO CONTACT AND FAILED. HARRY IMMEDIATELY WENT TO THE TIE-IN POINT, SAW THE FIRE AND WENT TO TURN OFF THE FOUR (4) INCH MAIN LINE VALVE TO ELIMINATE THE GAS SOURCE. THE FIRE WAS EXTINGUISHED IN APPROXIMATELY FIVE (5) MINUTES AFTER IGNITION. ROBERT COBB RADIOED THE CORBIN OFFICETO DISPATCH AN AMBULANCE TO THE SCENE. THE THREE MEN WERE TAKEN TO THE BAPTIST REGIONAL MEDICAL CENTER IN CORBIN. THE WEST KNOX FIRE DEPARTMENT WAS DISPATCHED TO THE SCENE BUT THE FIRE WAS ALREADY EXTINGUESHED WHEN THEY ARRIVED. SERVICE WAS INTERRUPTED TO APPROXIMATELY EIGHTY-EIGHT (88) CUSTOMERS. EACH AFFECTED CUSTOMER WAS TURNED OFF AT THE METER. AFTER REPAIRS TO THE MAIN LINE WERE COMPLETED, DELTA'S EMPLOYEES BEGAN RELIGHTING THE CUSTOMERS. NATURAL GAS SERVICE WAS RESTORED TO MOST OF THE CUSTOMERS BY APPROXIMATELY 9:15 P.M. THAT EVENING. SOME COULD NOT BE RESTORED UNTIL THE NEXT MORNING. THE SOURCE OF IGNITION IS UNKNOWN. SOME SPECULATION IS THAT STATIC ELECTRICITY FROM SOME SOURCE MAY HAVE CAUSED IGNITION.DELTA, THE STATE FIRE MARSHALL, THE KENTUCKY PUBLIC SERVICE COMMISSION AND OSHAARE ALL CONDUCTING INVESTIGATIONS. THERE WAS NO SIGNIFICANT PROPERTY DAMAGE OR INJURIES OTHER THAN DELTA'S FACILITIES AND THE THREE EMPLOYEES. CARL COX WAS ADMITTED TO THE BAPTIST REGIONAL MEDICAL CENTER IN CORBIN, KENTUCKY. HE SUSTAINED BURNS ON HIS WRISTS AND FACE. CARL WAS RELEASED FROM THE HOSPITAL THE NEXT DAY, MARCH 12, 1987, AND RETURNED TO WORK MONDAY, MARCH 23, 1987. CLARENCE ABNER WAS TRANSFERRED TO THE UNIVERSITY OF KENTUCKY MEDICAL CENTER BURN UNIT IN LEXINGTON, KENTUCKY. HE SUSTAINED BURNS ON HIS HANDS, ARMS AND FACE. SINCE THE ACCIDENT, HIS CONDITION HAS UPGRADED FROM SERIOUS TO STABLE TO SATISFACTORY AND HE CONTINUESTO IMPROVE. CHARLES LAMBDIN WAS TRANSFERRED TO THE UNIVERSITY OF CINCINNATI MEDICAL CENTER BURN UNIT IN CINCINNATI, OHIO WITH BURNS OVER SIXTY-FIVE PERCENT (65%) OF HIS BODY. HE WAS LISTED IN CRITICAL CONDITION AND HIS CONDITION NEVER CHANGED. CHARLES DIED ON THURSDAY, MARCH 19, 1987, AT APPROXIMATELY 9 A.M. FROM INJURIES HE RECEIVED IN THE ACCIDENT.
2025-01-31 10:21 | YES | YES | 19870073 |  | 180 | ALABAMA GAS CORP | 100 3RD AVENUE SW | BIRMINGHAM | JEFFERSON | AL | 3 | 3 | NO | 2328 | 1987-05-08 | 0 | 1 | 20000 | 18513.181 | 44699.4728 | YES | 23 | 33 |  | 19870509 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMERS FUEL LINE | NO DATA |  | OTHER | APPLIANCE VALVE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JEFFREY W ELLIOT | 2053268113 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SOMEONE DISCONNECTED AN APPLIANCE AND THEN TURNED THE APPLIANCE VALVE TO THE OPEN POSITION. GAS IGNITED DESTROYING THE CUSTOMERS'S HOUSE AND INJURING THE CUSTOMER. THE BIRMINGHAM FIRE DEPARTMENT NOTIFIED ALABAMA GAS CORPORATION THAT THE CUSTOMER HAD BEEN HOSPITALIZED. WITNESSES REPORTED THIS WAS A SUICIDE ATTEMPT.
2025-01-31 10:21 | YES | YES | 19870074 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 10 CRESTLINE DRIVE | SAN FRANCISCO | SAN FRANCISCO | CA | 3 | 3 | NO | 1720 | 1987-04-17 | 0 | 1 | 50000 | 46282.9525 | 111748.6819 | Null | 0 | 30 |  | 19870417 | 32 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  |  | 0 | 1964 | WITHIN/UNDER BUILDING |  | J B STOUTAMORE | 4159733204 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE STARTED BY UNKNOWN PARTY IN BASEMENT BELOW GAS METER CABINET, DAMAGING METERS AND ALLOWING GAS TO ESCAPE AND IGNITE.
2025-01-31 10:21 | YES | YES | 19870075 |  | 12684 | MONTANA - DAKOTA UTILITIES CO | 325 E ST JOSEPH STREET | RAPID CITY | PENNINGTON | SD | 3 | 3 | NO | 1235 | 1987-04-09 | 0 | 1 | 7500 | 6942.4429 | 16762.3023 | Null | 0 | 5 |  | 19870409 | 0.3 | 1 | BY TEST | 15 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | NONE | OTHER | NONE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ZENE C PALEN | 6053420160 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | UKNOWN - RAPID CITY FIRE DEPARTMENT INVESTIGATION REPORT ATTACHED
2025-01-31 10:21 | YES | YES | 19870076 |  | 4473 | ENERGAS CO | 7605 STUYVESANT | AMARILLO | RANDALL | TX | 3 | 3 | NO | 1343 | 1987-03-01 | 0 | 1 | 100000 | 92565.9051 | 223497.3638 | YES | 1 | 0 |  | 19870301 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19870077 |  | 4473 | ENERGAS CO | 6107 N DIXIE | ODESSA | ECTOR | TX | 3 | 3 | NO | 1915 | 1987-04-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19870416 | 0.05 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CARL F BAILEY | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BURNING TRASH AND WEEDS IN CLOSE PROXIMITY TO DAMAGED METER AND IGNITED THE ESCAPING
2025-01-31 10:21 | NO | NO | 19870081 |  | 4473 | ENERGAS CO | 1509 W 4TH STREET | LITTLEFIELD | LAMB | TX | 3 | 3 | NO | 1129 | 1987-03-06 | 0 | 0 | 10000 | 9256.5905 | 22349.7364 | YES | 0 | 15 |  | 19870306 | 0.5 | 1 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R FULKERSON | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CLOTHES ON FLOOR IGNITED FROM OPEN FLAME OF SPACE HEATER.
2025-01-31 10:21 | YES | NO | 19870082 |  | 4473 | ENERGAS CO | 4640 BONHAM | AMARILLO | RANDALL | TX | 3 | 3 | NO | 540 | 1987-03-31 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 30 |  | 19870331 | 0.5 | 1 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER | UNKNOWN | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS ACCUMULATED UNDER FLOOR OF OUSE AND EXPLODED DESTROYING HOUSE AND DAMAGINGSEVERAL OTHER HOUSE NEARBY
2025-01-31 10:21 | YES | NO | 19870083 |  | 10037 | K P L GAS SERVICE | 1406 OAK FOREST RD | DERBY | SEDGWICK | KS | 3 | 3 | NO | 940 | 1987-03-17 | 0 | 0 | 150000 | 138848.8576 | 335246.0457 | Null | 1 | 50 |  | 19870317 | 20 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | JOINT | FUSION | POLYETHYLENE PLASTIC |  | 4 | 0.409 | SDR-11 | PHILLIPS | 1977 | 1978 | UNDER GROUND OR UNDER WATER |  | WARREN KENNEDY | 3162639895 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APPARENT FAILURE OF FUSION WELD THE CAUSE OF WHICH IS UNKNOWN AT THIS TIME.
2025-01-31 10:21 | NO | NO | 19870085 | 1987-04-21 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | CLOUET STREET & FLORIDA AVENUE | NEW ORLEANS | ORLEANS | LA | 3 | 3 | Null | 130 | 1987-04-12 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 |  |  | 85 | 100 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0.217 |  |  | 0 | 1945 | ABOVE GROUND |  | ROBERT W VAUGHAN | 5045953511 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | WHILE TRAVELING DOWN FLORIDA AVENUE, THE DRIVER OF AN AUTOMOBILE LOST CONTROL STRIKING AN ABOVE GROUND 3" HIGH PRESSURE GAS CANAL CROSSING, CAUSING THE PIPE TORUPTURE WHICH REQUIRED IMMEDIATE REPAIR
2025-01-31 10:21 | YES | NO | 19870086 |  | 13710 | NORTHERN ILLINOIS GAS CO | 717 SHORE LINE DRIVE | SCHAUMBURG | COOK | IL | 3 | 3 | NO | 2030 | 1987-04-14 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 3 | 45 |  | 19870414 | 60 | 60 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | NO DATA |  | OTHER | COPPER | 0.625 | 0.4 | TYPE L |  | 0 | 1974 | WITHIN/UNDER BUILDING |  | FRANK LAWSON | 3127246704 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A LEAKING SOURCE OF NATURAL GAS CAUSED AN EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | YES | 19870087 |  | 13710 | NORTHERN ILLINOIS GAS CO | 601 E MADISON | VILLA PARK | DU PAGE | IL | 3 | 3 | NO | 1515 | 1987-04-06 | 0 | 1 | 50000 | 46282.9525 | 111748.6819 | Null | 2 | 45 |  | 19870406 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | SLEEVE | STEEL |  | 2 | 0.154 |  |  | 0 | 1959 | UNDER PAVEMENT |  | GEORGE WALDVOGEL | 3126292500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-04-04 | YES | 2 |  | YES |  |  | NORTHERN ILLINOIS GAS COMPANY PERSONNEL WERE RESPONDINGTO AN EMERGENCY CALL AT THE INTERSECTION OF MADISON AND MONTEREY, VILLA PARKA SEWER CONTRACTOR WAS EXCAVATING AND PULLED AND DAMAGES ASTEEL TWO INCH GAS MAIN. THE GAS IGNITED ABOVE GROUND, RESULTING IN PERSONAL INJURY TO NI-GAS PERSONNEL AND EQUIPMENT. ADDITIONAL PROPERTY DAMMAGE TO A TELEPHONE POLE AND TREE LOCATED IN THE PARKWAY. THE BUILDING AT 601 MADISON HAD HEAT DAMAGE TO THE STORM DOOR AND SIDING
2025-01-31 10:21 | YES | YES | 19870088 |  | 13840 | NORTHWEST NATURAL GAS CO | 200 N STATE STREET | LAKE OSWEGO | CLACKAMAS | OR | 3 | 3 | NO | 1040 | 1987-03-15 | 0 | 1 | 300000 | 277697.7153 | 670492.0914 | Null | 0 | 42 |  | 19870316 | 45 | 57 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | P E 2306 | R W LYALL | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | GAYLORD F ROGERS | 5032264211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-03-12 | YES | 0 |  | NO |  |  | A SEWER CONTRACTOR LAYING A 72" STORM SEWER WAS CROSSING OUR 4" STEEL MAIN AND 1' PE SERVICE WITH A LARGE TRACK HOE. THE TRAC HOE CROSSING THE SERVICE VALVE CAUSED SOIL SUBSIDENCE, PUSHED THE VALVE BOX DOWN ENOUGH TO CREATE A CRACK IN THEBOTTOM QUADRANT OF THE FUSION OF THE 1" CTS PIPE ADJACANT TO THE VALVE BODY.
2025-01-31 10:21 | YES | YES | 19870090 |  | 18536 | SOUTHWEST GAS CORP | 59TH AVENUE AND CORONADA | PHOENIX | MARICOPA | AZ | 3 | 3 | NO | 1300 | 1987-03-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  |  | 1 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | PROCEDURE NOT FOLLOWED | CAST IRON |  | 2 | 0.216 | 3408 | PHILLIPS | 1987 | 1987 | OTHER | OPEN EXCAVATION | JOHN HANENBURG | 6024845203 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | CONTRACTOR EMPPLOYEE WAS PURGING A NEWLY INSTALLED 2" 3408 P.E. MAIN WHEN IGNITION COCCURRED CAUSING BURNS TO EMPLOYEE.THEMAIN BEING PURGED WAS BELOW GROUND AND IN A HORIZANTAL POSITION AND FLOW WASBEING CONTROLLED WITH WITH A PIPE SQUEEZING TOOL CONTROLLED BY THE EMPLOYEE WHILE STANDING IN THE EXCAVATION. A VERTICAL BLOW STACK WAS NOT INSTALLED. A VALVETO CONTROL THE PURGE WAS NOT INSTALLED. THE GROUNDING DEVICE WAS NOT PROPERLLYINSTALLED. THE GROUND AND NEAR THE PURGE WAS NOT WET DOWN. A SOAP/WATER SOLUTION WAS NOT APPLIED TO THE PIPE TO ASSIST IN REDUCING STATIC ELECTRICITY BUILDUP.CONTRACOR EMPLOYEE DID NOT UTILIZE THE STANDARD ACCEPTABLE PUGING METHOD AND ITS ASSUMED THAT THE FAILURE TO DO SO RESULTED IN A STATIC BUILDUP THAT CAUSED IGNITION.THE RESULTING FIRE WAS QUICKLY EXTINGUISHED AND THE EMPLOYEE WAS TRANPORTATED TO MEDICAL FACILITIES FOR TREATMENT OF BURNSIN ADDITION OUR PROCEDURES REQUIRE THAT THE SOUTHWEST GAS CORPATION COMPANY INSPECTOR BE NOTIFIED PRIOR TO PURGING OPERATIONS AND THAT HE BE PRESENT DURING ANYRELEASE OF NATURAL GAS. COMPANY INSPECTORS WERE NOT NOTIFIED PRIOR TO IGNITION
2025-01-31 10:21 | NO | NO | 19870096 |  | 12390 | METROPOLITAN UTILITIES DISTRICT | 102 SOUTH FORT CROOK RD | BELLEVUE | SARPY | NE | 68147 | 2 | NO | 1127 | 1987-08-04 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19870804 | 125 | 125 | BY TEST | 190 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | OTHER PLASTIC | SEMI-STEEL | 2 | 0 |  | ROCKWELL NORDSTRUM | 1969 | 1969 | ABOVE GROUND |  | D A KOCOUREK - CLAIMS ADJUSTER | 4024498211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | WILSON CONCRETE WORKERS LOADING SAND KNOCKED OVER CONCRETE SLAB WALL BURYING THE ABOVE GROUND 2# 1ST CUT REGULATOR AND SERVICE VALVE. THE PIPE REMAINED INTACT.THE SERVICE VALVE WAS SEVERED THROUGH THE BODY : 1" ROCKWELL VALVE (FLANGED). NO FIRE OR EXPLOSION OCCURED, HOWEVER, GAS WAS ESCAPING INTO THE ATMOSPHERE. THEGAS LEAK POINT WAS NOT IN CLOSE PROXIMITY TO ANY STRUCTURE AND NO EMERGENCY EXISTED, HOWEVER, OCCUPANTS OF THE PAYLESS LUMBER COMPANY WERE EVACUATED AS A PRECAUTIONARY MEASURE. A COPY OF THE LETTER SENT TO THE NEBRASKA STATE FIRE MARSHAL'SOFFICE IS ATTACHED AND MADE A PART OF THIS REPORT.
2025-01-31 10:21 | YES | YES | 19870097 |  | 8170 | INTERSTATE POWER CO | 218 NORTH 8TH ST | FULTON | WHITESIDE | IL | 61252 | 3 | NO | 1142 | 1987-07-31 | 0 | 2 | 2000 | 1851.3181 | 4469.9473 | Null | 2 | 30 |  | 19870731 | 59 | 60 | BY TEST | 95 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.216 | ASTM D2513 | PLEXCO | 1980 | 1981 | OTHER | EXPOSED IN HOLE | RAY P RICHARDS | 3195572218 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEES WERE FUSING A POLYETHELENE PUNCH-IT TEE TO A 2" POLYETHELENE GAS MAIN. DURING FUSION OF THE TWO, THE GAS BEGAN TO LEAK BENEATH THE TEE DISCHARGING THROUGH THE SERVICE CONNECTION END. THIS GAS IGNITED, BURNING BOTH EMPLOYEES.
2025-01-31 10:21 | YES | NO | 19870098 |  | 2592 | COLUMBIA GAS OF NEW YORK INC | 2613 OLD OWEGO RD | VESTAL | BROOME | NY | 13850 | 4 | NO | 1155 | 1987-06-26 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 1 | 5 |  | 19870626 | 16 | 18 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | GRADE B |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | DONALD E WILLIAMS - DISTRICT PLANT MNGR | 6077242431 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A 6" COATED STEEL MAIN OPERATING AT 17 PSIG AND 32" DEEP, LOCATED BENEATH A STREET SIGN, WAS DAMAGED BY APPROXIMATELY 12,000 VOLTS THAT TRAVELED FROM A SEVEREDOVERHEAD POWER LINE THROUGH THE STREET SIGN AND ARCED ONTO THE MAIN CAUSING THREE 1" HOLES. GAS TRAVELED UNDERGROUND AND INTO THE HOUSE AT 2613 OLD OWEGO RD AND WAS IGNITED BY AN UNKNOWN SOURCE, RESULTING IN AN EXPLOSION. THE HOUSE WAS COMPLETELY DESTROYED. THREE OTHER HOUSES RECEIVED MINOR DAMAGE. EIGHT HUNDRED FIFTH-ONE(851) CUSTOMERS WERE SHUT OFF AND SUBSEQUENTLY RESTORED. NO FATALITIES OR INJURIES REQUIRING HOSPITALIZATION.
2025-01-31 10:21 | NO | NO | 19870099 |  | 4499 | ENTEX INC | 1107 ALAMO | ROSENBERG | FORT BEND | TX | 77471 | 1 | NO | 600 | 1987-06-26 | 0 | 0 | 40000 | 37026.362 | 89398.9455 | Null | 0 | 28 |  | 19870626 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | CAST IRON |  | 0 | 0 |  | UNIVERSAL CONTROL | 1976 | 1976 | WITHIN/UNDER BUILDING |  | DAVID E GATES - OPER ENG | 7136545104 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE OUTSIDE PARTY SET A TRASH DUMPSTER DOWN ON THE REGULATOR WHICH KNOCKED THE REGULATOR OFF AND SENT LINE PRESSURE INTO THE HOUSE. A FIRE BROKE OUT AT WATER HEATER IN UTILITY ROOM RESULTING IN APPROXIMATELY $40,000.00 IN DAMAGES.
2025-01-31 10:21 | NO | NO | 19870103 |  | 4473 | ENERGAS CO | 301 TAYLOR | AMARILLO | POTTER | TX | 79189 | 0 | NO | 935 | 1987-07-01 | 0 | 0 | 500 | 462.8295 | 1117.4868 | YES | 0 | 5 |  | 19870701 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CUSTOMER CALLED INTO THE PAMPA ENERGAS OFFICE AT 9:31 A.M. SAYING HE SMELLED GAS NEAR HIS CLOTHES DRYER.THE ORDER WAS DISPATCHED TO A SERVICE TECHNICIAN BY RADIO AT 9:32 A.M.THE SERVICE TECHNICIAN ARRIVED AT 845 E. FREDERICK AT 9:35 A.M.BETWEEN THE TIME THE CUSTOMER CALLED THE ENERGAS OFFICE AND WHEN THE ENERGAS SERVICE TECHNICIAN ARRIVED, THE CUSTOMER WENT OUTSIDE THE RESIDENCE TO THE LOCATION WHERE HIS SERVICE LINE CAME OUT OF THE GROUND AND ENTERED THE HOUSE AND BEGAN TO LOOK FOR THE GAS SOURCE WITH HIS CIGARETTE LIGHTER. THE FLAME FROM THE CIGARETTE LIGHTER IGNITED THE GAS. THERE WAS A SMALL FLASH FIRE BACK THROUGH THE WALL INTO THE AREA BEHIND HIS GAS CLOTHES DRYER. THE FIRE EXTINGUISHED ITSELF WITH ONLY MINOR DAMAGE TO THE WALL BEHIND THE DRYER.
2025-01-31 10:21 | YES | YES | 19870106 |  | 18148 | SAWYER GAS INC | 7162 PHILLIPS HIGHWAY | JACKSONVILLE | DUVAL | FL | 32216 | 2 | NO | 933 | 1987-07-07 | 1 | 0 | 10 | 9.2566 | 22.3497 | NO | 0 | 15 |  | 19870707 | 10 | 60 | BY TEST | 60 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | SEE PART 3 | STEEL |  | 0.75 | 0.24 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | J.N. KICLITER GENERAL MANAGER | 9047318600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEE WAS IN PROCESS OF RELOCATING METER RISER AND REJOINING TO MAIN LINE. EMPLOYEE APPARENTLY PASSED OUT AND WAS FOUND BY RESIDENTS IN AN UNCONSCIOUS STATE. EMPLOYEE WAS HOSPITALIZED ON 7/7/87, AND WAS DECLARED DEAD ON 7/11/87
2025-01-31 10:21 | YES | YES | 19870107 |  | 15896 | PROVIDENCE GAS CO | 275 ALLENS AVE | PROVIDENCE | PROVIDENCE | RI | 02903 | 4 | NO | 1833 | 1987-06-06 | 0 | 2 | 0 | 0 | 0 | Null | 9 | 30 |  | 19870608 | 5.6 | 7 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | JOINT | B&S | CAST IRON |  | 20 | 0 |  |  | 0 | 1923 | UNDER PAVEMENT |  | LOUIS R. SCHMITT SUPT. OF CONSTRUCTION & MAINTENANCE | 4014611970 | EXTERNALLY | OTHER | CLAMP BOLT FAILURE | OTHER | GROUND WATER | NO DATA | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | BELL JOINT CLAMP BOLT CORRODED AND FAILED, CAUSING LEAKING OF INTERMEDIATE PRESSURE GAS WHICH MIGRATED TO MANHOLE.
2025-01-31 10:21 | YES | YES | 19870108 |  | 15518 | PIEDMONT NATURAL GAS CO INC | 4329 PARK ROAD | CHARLOTTE | MECKLENBURG | NC | 28209 | 3 | NO | 345 | 1987-06-02 | 0 | 1 | 5000 | 4628.2953 | 11174.8682 | Null | 0 | 50 |  | 19870602 | 60 | 75 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 1.05 | 0.113 |  | PHILLIPS | 0 | 1985 | NO DATA |  | JACK L. RIMMER SPUERINTENDENT DISTRIBUTION | 7045255585 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | FROM INFORMATION I CAN RECEIVE, LIGHTNING STRUCK TRANSFORMER AROUND 7:30 PM, JUNE 1, 1987. DUKE POWER CREW REMOVED TRANSFORMER TO INSTALL NEW ONE; IN THE PROCESS OF SPLICING IN NEW WIRES, CREWMAN USED IMPACT WRENCH TO TIGHTEN SPLIT BOLT NUTS, IGNITION SOURCE PROBABLY WASF INPACT WRENCH. THE PROBABLE CAUSE OF DAMAGE TOPIPE WAS HEATED OIL FROM TRANSFORMER RAN INTO ELECTRICAL CONDUIT, ALSO HEAT TRANSFER FROM TRANSFORMER TO CONDUIT CAUSED PIPE TO MELT WHICH WAS LAYING NEAR ELECTRICAL CONDUIT.
2025-01-31 10:21 | YES | YES | 19870109 |  | 2880 | CROCKETT PUBLIC UTIL DIST | 231 N. JOHNSON ST. | ALAMO | CROCKETT | TN | 38001 | 0 | NO | 830 | 1987-06-27 | 0 | 1 | 15000 | 13884.8858 | 33524.6046 | Null | 0 | 0 |  | 19870627 | 25 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 | 0 |  |  | 0 | 1967 | ABOVE GROUND |  | JERRY PITTMAN | 9016964149 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | MRS. FORSYTHE INFORMED ME THE CAR ROLLED INTO THE GAS METTER AND BROKE THE GAS PIPE. AT THIS TIME THEY COULD DETECT THE SMELL OF GAS AND HEAR THE GAS ESCAPING FROM THE BROKEN PIPE SO THEY ATTEMPTED TO PUSH THE CAR ASIDE BY HAND. THIS WAS IMPOSSIBLE SO MR. KENNETH FORSYTHE GOT INTO THE CAR TO MOVE IT AND WHEN HE CRANKED THE CAR GAS WAS ESCAPING FROM THE BROKEN PIPE UNDER THE HOOD OF THE CAR WHICH RESULTED IN THE CAR AND HOUSE CATCHING FIRE. THE ALAMO FIRE DEPARTMENT WAS CALLED AT 8:30 A.M. AND ARRIVED ON THE SCENE AT APPROXIMATELY 8:34 A.M. UPON ARRIVINGTHE FIREMEN EXTIGUISHED THE CAR FIRE IN ORDER TO REMOVE IT FROM THE GAS METER. THE GAS DEPARTMENT USING 3/4 INCH LINE STOPPER PLUGGED THE LINE STOPPING THE FLOW OF GAS AT APPROXIMATELY 9:00 A.M. AT THIS TIME THE FIREMEN EXTIGUISHED THE HOUSE FIRE WHICH WAS APPROXIMATELY 9:30 A.M.
2025-01-31 10:21 | YES | NO | 19870110 |  | 15007 | PACIFIC GAS & ELECTRIC CO |  | PEBBLE BEACH | MONTEREY | CA |  | 3 | NO | 2030 | 1987-05-31 | 0 | 0 | 75000 | 69424.4288 | 167623.0228 | Null | 7 | 30 |  | 19870531 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | J.B. STOUTAMORE | 4159733203 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | BRUSH FIRE DESTROYED 32 HOMES; ENSUING STRUCTURE FIRE DESTROYED METERS AND REGULATORS. 28 OTHER STRUCTURES HAD THEIR SERVICE.
2025-01-31 10:21 | YES | NO | 19870111 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2200 - 4TH STREET | BERKELEY | ALAMEDA | CA |  | 3 | NO | 1817 | 1987-06-08 | 0 | 0 | 1000000 | 925659.051 | 2234973.638 | Null | 0 | 57 |  | 19870608 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | CUSTOMER HOUSLINE | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | J.B. STOUTAMORE VICE PRESIDENT - GAS OPERATIONS | 4159733203 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE OF UNKNOWN ORIGIN DAMAGED HOUSELINE, ALLOWING GAS TO ESCAPE & IGNITE. BUILDINGS WERE EVACUATED & TRAFFIC REROUTED.
2025-01-31 10:21 | YES | YES | 19870114 |  | 4473 | ENERGAS CO | SEC 30 BLK A-1 | HALE CENTER | HALE | TX | 79041 | 1 | NO | 1135 | 1987-06-17 | 2 | 1 | 25000 | 23141.4763 | 55874.3409 | Null | 0 | 30 |  | 19870617 | 300 | 500 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL | ALUMINUM | 1 | 0.133 | API-5LA25 |  | 0 | 0 | ABOVE GROUND |  | DAVID V HAYES DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TWO PICKUPS COLLIDED AT RURAL INTERSECTION. THE VEHICLES HIT TWO METTER SETTINGS AT NW CORNER OF INTERSECTION.
2025-01-31 10:21 | YES | YES | 19870116 |  | 2416 | CITIZENS UTILITY CO | 1365 BAYZE ST. | NOGALES | SANTA CRUZ | AZ | 85621 | 3 | NO | 1521 | 1987-05-29 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 10 |  | 19870529 | 0.3 | 24 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER'S FUEL LINE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GEORGE X. LINEIRO GAS SUPERINTENDENT | 6022811212 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PART B # 3A GAS METER THAT WAS INACTIVE WAS OPENED BY PERSONS UNKNOWN. THE HOUSE WAS FILLED WITH GAS. AN UNKNOWN SOURCE OF IGNITION CAUSED THE EXPLOSION.SEE NARRATIVE!
2025-01-31 10:21 | YES | YES | 19870120 |  | 13710 | NORTHERN ILLINOIS GAS CO | 1255 N. RANDALL RD. | AURORA | KANE | IL | 60506 | 3 | NO | 908 | 1987-06-16 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 40 |  | 19870616 | 60 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | MECHANICALLY TAPPED | STEEL |  | 16 | 0.25 |  |  | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | GEORGE WALDVOGEL GENERAL SUPERVISOR | 3126292500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON JUNE 16, 1987, TWO AURORA WATER DEPARTMENT EMPLOYES MISTOOK A GAS MAIN FOR AWATER MAIN AND DRILLED INTO THE 16" MAIN ON RANDALL ROAD, AURORA, THE INCIDENT RESULTED IN A FIRE, CAUSING PERSONAL INJURY TO THE TWO CITY EMPLOYES.
2025-01-31 10:21 | NO | NO | 19870121 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 207 POLARIS DR. | PITTSBURG | CONTRA COSTA | CA | 94565 | 3 | NO | 2315 | 1987-04-09 | 0 | 0 | 50000 | 46282.9525 | 111748.6819 | Null | 2 | 15 |  | 19870409 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | OTHER | ALUMINUM | 0 | 0 | AL-150 | SPRAGUE | 1962 | 1978 | ABOVE GROUND |  | J.B. STOUTAMORE VICE PRESIDENT - GAS OPERATIONS | 4159733203 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DRIVER OF AUTOMOBILE WAS BEING PURSUED BY POLICE IN A HIGH SPEED CHASE, LOST CONTROL AND HIT A RESIDENTIAL GAS METER SET, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVAUATED & TRAFFIC REROUTED.
2025-01-31 10:21 | YES | YES | 19870122 |  | 22182 | WASHINGTON GAS LIGHT CO | 10704 STANMORE DR. | POTOMAC | MONTGOMERY | MD | 20854 | 3 | NO | 1330 | 1987-06-22 | 0 | 2 | 500000 | 462829.5255 | 1117486.819 | Null | 0 | 15 |  | 19870622 | 20 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 | API 5L |  | 0 | 1968 | ABOVE GROUND |  | CLARENCE E. GOODSON, III SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | INFORMATION PROVIDED BY COMPANY RECORDS, FIRE MARSHALL HARDING AND BACKHOE OPERATOR THOMAS. SHORTLY BEFORE 1:30 P.M. ON 6/22/87 THE VENTURE GROUP WAS DIGGING IN A FOOTING TO INSTALL A STOOP AT THE FRONT BUILDING WALL OF 10704 STANMORE DR.,MONT. CO., MARYLAND. THE BACKHOE USED TO EXCAVATE STRUCK A 3/4" W/STL HP GAS LINE CAUSING GAS TO ESCAPE. TWO WORKERS ATTEMPTED TO VENTILATE THE GAS BY HAND DIGGING OVER THE BREAK SITE. THE BACKHOE OPERATOR MOVED THE HOE AND PROCEEDED TO THE UNDERGROUND SERVICE SHUT-OFF AND BEGAN TO EXPOSE IT BY HAND DIGGING. HE ESTIMATED WITHIN FIVE MINUTES "SHE WENT OFF". THE TWO WORKERS AT THE BREAK SITE WERE HOSPITALIZED WITH BURN. THE GAS WAS TURNED OFF BY THE CONTRACTOR. THE HOME OWNER URSULA GOSNELL WAS INSIDE AT THE TIME OF THE INCIDENT BUT WAS UNINJURIED AND ESCAPED THROUGH A WINDOW.
2025-01-31 10:21 | YES | YES | 19870125 |  | 18536 | SOUTHWEST GAS CORP | 43RD AVE & TUCKEY LANE | PHOENIX | MARICOPA | AZ | 85051 | 3 | NO | 1530 | 1987-04-16 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19870416 | 25 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | ABS | 2 | 0.09 |  |  | 0 | 1960 | OTHER | BELL HOLE | JOHN HANENBURG, JR PROJECT MANAGER | 6024845203 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | A 2" WILLIAMSON 3-WAY TEE WAS BEING WELDED TO A 2" STEEL MAIN APPROXIMATELY 18"FROM AN ABS TO STEEL TRANSITION FITTING. THE FLOW OF GAS IN THE PIPELINE WAS FROM THE STEEL TO PLASTIC MAIN AND IN THIS CASE THE GAS WAS HEATED AS IT PASSED THE STEEL MAIN ON WHICH THE 3-WAY TEE WAS BEING INSTALLED. THE HEATED GAS CAUSED THE ABS PLASTIC PIPE MATERIAL TO EXPAND AND RUPTURE ALLOWING GAS TO ESCAPE AND IGNITE. THE FIRE WAS EXTINGUISHED IMMEDIATELY AND REPAIRS WERE INITIATED AFTER SHUT DOWN OF THE RUPTURED MAIN.
2025-01-31 10:21 | YES | YES | 19870126 |  | 13790 | NORTHERN UTILITIES INC | INTERSECTION OF RIVERVIEW & GALLOWAY RD. | RIVERTON | FREMONT | WY | 82501 | 3 | NO | 200 | 1987-09-05 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 45 |  | 19870905 | 30 | 59 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR SET | BODY OF PIPE |  | STEEL |  | 2 | 0.125 | GRADE B |  | 0 | 1979 | ABOVE GROUND |  | ROBERT HUGHES VICE PRESIDENT-OPERATIONS | 3072351541 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 | ABOVE GROUND APPURTENANCE | NO |  |  | THE ATTACHED REPORT COVERS AN INCIDENT THAT OCCURRED ON A 2" HIGH PRESSUREDISTRIBUTION REGULATOR SETTING IN RIVERTON, WYOMING ON SEPTEMBER 5, 1987. IGNITION DID OCCUR AND SEVERE BURN INJURIES WERE SUSTAINED BY A THIRD PARTY AS A RESULT OF THE LEAK. SERVICE WAS INTERRUPTED TO APPROXIMATELY 75 CUSTOMERS FROM SEVENTO THIRTY HOURS DUE TO THE LABOR DAY WEEKEND. THE LEAK WAS CAUSED BY AN OUTSIDE PARTY OPERATING A VEHICLE AT A HIGH RATEOF SPEED, LOSS CONTROL, LEFT THE ROADWAY, AND STRUCK A 2" HIGH PRESSURE DISTRICT REGULATOR SETTING PROTECTTED BY A 4" STEEL BARRICADE SET IN CONCRETE. THE RESULTING FIRE CAUSED THE TOTAL DESTRUCTION OF THE OUTSIDE PARTY'S VEHICLE AND NUD'SREGULATING FACILITIES. THE TOTAL ESTIMATED DAMAGE WILL BE APPROXIMATELY $25,000. TELEPHONIC NOTICE WAS GIVEN TO ENSIGN FAUREAU OF THE D.O.T. AT 10:15 A.M. MST ON SEPTEMBER 5, 1987. THE WYOMING PUBLIC SERVICE COMMISSION WAS NOTIFIED THESAME DAY. IF ADDITIONAL INFORMATION IS REQUIRED, PLEASE ADVISE.
2025-01-31 10:21 | NO | NO | 19870127 |  | 8241 | IOWA ELECTRIC LIGHT & GAS POWER CO | 100 BLK BETWEEN DOWNTOWN PLAZA & N. PARK | FAIRMONT | MARTIN | MN | 56031 | 1 | NO | 1335 | 1987-08-31 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 30 |  |  | 15 | 125 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | HIT BY BACKHOE | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | DAVID E. ROGERS MANAGER CUSTOMER SERVICES | 7128643435 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-08-03 | YES | 3 | YELLOW PAINT | YES |  |  | (THIRD PARTY) CAUSE OPERATOR HIT 1" LINE STOPPER ON TOP OF 4" GAS MAIN. EQUIPMENT (OPERATOR) LARGE BACKHOE.PART D:HODGMAN CONSTRUCTION COMPANY WAS TAKING OUT THE OLD CONCRETE SURFACE IN THE ALLEY BETWEEN 1ST & 2ND STREET, DOWNTOWN PLAZA AND N. PARK ST. FAIRMONT, MN (MARTINCOUNTY) USING LARGE BACKHOE FOR THE JOB. CONTRACTOR HIT TOP OF A 1" LINE STOPPER WELDED ON TOP OF THE 4" STEEL GAS MAIN. MAIN WAS 36" DEPTH. LINE STOPPER WAS APHES FOR NEW BASE. IOWA ELECTRIC WAS NOTIFIED AT 1335 HOURS 8/31/87. FIRE & POLICE WERE STANDING BY. NO EXPLOSION. NO FIRE. NEW BANK BUILDING WAS EVACUATED.
2025-01-31 10:21 | YES | YES | 19870129 |  | 22182 | WASHINGTON GAS LIGHT CO | 2ND ST. & G ST. N.E. | WASHINGTON |  | DC | 20013 | 3 | NO | 1500 | 1987-08-24 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19870824 | 0.2 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | NO DATA |  | CAST IRON |  | 4 | 0.4 |  |  | 0 | 1878 | OTHER | CONSTRUCTION EXCAVATION | CLARENCE E. GOODSON III SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | ON AUGUST 24, 1987 AT APPROXIMATELY 3:00 P.M. A WGLCO CONSTRUCTION CREW HAD JUSTTIED-IN A 12" WRAPPED STEEL MAIN. TWO 4" C.I. MAINS WERE TO BE ABANDONED AS PART OF THE JOB AND WERE BEING PURGED BY NITROGEN. THE NITROGEN INJECTION POINT WASLOCATED 300' +/- NORTH OF THE INSTALLATION SITE. THE TRUCK PERFORMING THE INJECTION WAS OBSTRUCTING TRAFFIC AND WHEN IT WAS MOVED, THE CONSTRUCTION FOREMAN ASSUMED THE PURGE OPERATION WAS COMPLETE AND INSTRUCTED MR. LESLIE LANIER TO ENTER THE EXCAVATION AND STRAP THE TIE-IN COUPLINGS ON THE 12" LINE. AFTER THE FIRST STRAP WAS INSTALLED, WHICH TOOK APPROXIMATELY 10 MINUTES, MR. LANIER STARTED WELDING STRAP NUMBER TWO WHEN A 3 SECOND FLASH FIRE STRUCK HIS LEFT SIDE. THE CONSTRUCTION FOREMAN ASSISTED HIM FROM THE HOLE AND EXTINGUISHED HIS BURNING COTTON POLYESTER TEE SHIRT AND RIPPED IT OFF HIM. T&D DISPATCH WAS CALLED AND MR. LANIER WAS TAKEN TO WASHINGTON HOSPITAL CENTER - BURN UNIT WITH SECOND AND THIRD DEGREEBURNS TO HIS ARMS AND LEFT SIDE.
2025-01-31 10:21 | NO | NO | 19870131 |  | 4473 | ENERGAS CO | 1926 E. AUBURN | LUBBOCK | LUBBOCK | TX | 79403 | 3 | NO | 600 | 1987-07-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19870717 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 12:46 P.M. ON JJULY 14, 1987, WE RECEIVED A CALL OF A STRONG GAS SMELL AT 1928 E. AUBURN. OUR SERVICEMAN, RONNIE SALMON TURNED THE GAS OFF AND LOCKED AND BLINDED THE METER. NO ONE WAS AT HOME.ON JULY 16, 1987, AT 2:30 A.M., THE LUBBOCK FIRE DEPARTMENT RECEIVED A CALL OF A FIRE AT THIS ADDRESS. FIRE MARSHALL, JACK CARLILE. SAID THAT GASOLINE HAD BEENPOURED IN THREE ROOMS AND SET ON FIRE.ON JULY 16, 1987 AT 6:20 P.M., OUR SERVICEMAN, ABE LARA TURNED THE GAS ON AT THIS ADDRESS. THE CUSTOMER DID NOT WANT THE WATER HEATER LIT, WHICH WAS THE ONLY GAS APPLIANCE IN THE HOUSE. ABE SAID THAT THE LINE TO THE KITCHEN RANGE WAS CAPPED OFF AT THE WALL. THE OWNER, MR. ARNOLD SAID HE TURNED THE GAS METER OFF AFTER WE LEFT.THE FIRE DEPARTMENT WAS CALLED TO THIS ADDRESS, 1928 E. AUBURN ON JULY 17, 1987AT 6:00 A.M. FOR AN EXPLOSION. THEY FOUND THAT THE GAS VALVE AT THE METER WAS BARELY TURNED ON AND THE CAP WAS GONE OFF THE LINE TO THE RANGE IN THE HOUSE. IT IS APPARENT THAT PARTIES UNKNOWN TURNED THE GAS BACK ON AND REMOVED THE GAS CAP THAT BROUGHT ABOUT DESTRUCTION OF THIS BUILDING.
2025-01-31 10:21 | NO | NO | 19870132 |  | 4473 | ENERGAS CO | 2004 EAST 47TH STREET | LUBBOCK | LUBBOCK | TX | 79404 | 3 | NO | 1003 | 1987-08-27 | 0 | 0 | 500 | 462.8295 | 1117.4868 | Null | 0 | 10 |  | 19870827 | 10 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON DIVISION ENGIREER | 8067414228 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER SETTING | YES |  |  | ASPLUNDH COMPANY WAS TRIMMING TREES AND LIMB FELL HITTING SERVICE REGULATOR. RESULTED IN BROKEN REGULATOR WITH POUNDS PRESSURE TO HOT WATER HEATER. FIRE FLAREDOUT FROM BURNER, MELTING CONTROLS AND SCORCHING PAINT IN HEATER CLOSET.LADY OF HOUSE, TINA STOKES, RECEIVED FLASH BURN TO FACE AND ARMS, BUT DID NOT REQUIRE TREATMENT. VALVE AT WATER HEATER TURNED OFF AND FIRE ELIMINATED BEFORE OUR SERVICEMAN AT SCENE.REGULATOR REPLACED AND SHUT-IN TEST INDICATED NO LEAKAGE.
2025-01-31 10:21 | NO | NO | 19870133 |  | 4499 | ENTEX INC | 1107 1/2 AVENUE G | HOUSTON | HARRIS | TX |  | 3 | NO | 1830 | 1987-07-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 |  | 19870728 | 22 | 60 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | METER SET ASSEMBLY |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | B.F. BROYLES DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PART 3 - NARRATIVE DESCRIPTION OF FACTORS CONTRIBUTING TO THE INCIDENT THE OPERATOR'S EMPLOYEES WERE EXCHANGING A METER. THEY DISCONNECTED THE INLET SIDE OF THE METER WITHOUT TURNING OFF THE LOCKWING VALVE ON THE RISER. THE ESCAPING GAS IGNITED, AND THE MEN WERE BURNED, BUT NOT HOSPITALIZED. IGNITION SOURCES BELIEVED TO BE FROM A SPARK OR FROM A NEARBY WATERHEATER. THERE WAS MINOR DAMAGE TO PROPERTY. THE OPERATORS PROCEDURE CALLS FOR TURNING OFF THE GAS AT THE METER PRIOR TOREMOVING THE METER. THE EMPLOYEE'S FAILURE TO FOLLOW THIS PROCEDURE CONTRIBUTEDTO THE INCIDENT.
2025-01-31 10:21 | YES | YES | 19870134 |  | 13580 | NORTH CAROLINA NATURAL GAS CORP | 915 SOUTH 11TH ST. | WILMINGTON | NEW HANOVER | NC | 28401 | 3 | NO | 900 | 1987-06-11 | 0 | 1 | 46000 | 42580.3163 | 102808.7873 | Null | 1 | 0 |  | 19870611 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 | API-5L |  | 0 | 1960 | ABOVE GROUND |  | PAUL J. SOBCZAK VICE-PRESIDENT OPERATIONS | 9194830315 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | AT 8:43 A.M., JUNE 11, 1987, THE WILMINGTON DISTRICT OFFICE WAS CALLED BY THE EMERGENCY SERVICE'S DISPATCHER. THE DISPATCHER REPORTED THAT A HOUSE AT 915 S. 11TH STREET WAS ON FIRE AND THEY MIGHT NEED ASSISTANCE FROM THE GAS COMPANY. OTIS PELHAM AND LARRY LEE RESPONDED AT 8:47 A.M. THEY FOUND THE HOUSE FULLY AFLAME AND A 1984 TOYOTA WAS TOTALLY DESTROYED BY FIRE. THE CAR HAD RUN OVER THE GASMETER AND BROKEN THE RISER AT GROUND LEVEL. THE CONSTRUCTION DEPARTMENT PULLED THE CAR OFF THE RISER AND THE FIRE DEPARTMENT HOSED THE FIRE FROM THE BURNING GAS AND THE HOUSE UNTIL THE GAS SERVICE WAS LOCATED AND THE GAS TURNED OFF. THE GAS WAS TURNED OFF AT 9:30 A.M. MY INVESTIGATION INTO THE MATTER REVEALED THE FOLLOWING INFORMATION: AT ABOUT 8:30 A.M., MS. SYLVIA ROWELL OF THIS ADDRESS STARTED THE TOYOTA, PREPARING TO LEAVE FOR WORK. SHE STATED THAT THE CAR WAS IN GEAR WHEN IT STARTED AND THAT IT LURCHED FORWARD ONTO THE GAS LINE. A PASSERBY, WILLIAM JOHNSON, HEARD HISSING OF THE ESCAPING GAS, AND WENT TO THE LADY'S AID. A MS. JOYCE ROWELL, OF THE ADDRESS, DROVE INTO THE YARD IN A LATE 1979 MODEL MONTE CARLO. SHE PARKED HER CAR ABOUT FIVE FEET FROM THE TOYOTA. MR. JOHNSON ADVISED THE LADIES TO CALL THE GAS COMPANY AND THE FIRE DEPARTMENT. MS. SYULVIA ROWELL WENT INTO THE HOUSE T
2025-01-31 10:21 | YES | YES | 19870136 |  | 11800 | LOUISIANA GAS SERVICE CO | 2904 GUERRA DRIVE | VIOLET | ST BERNARD | LA | 70092 | 3 | NO | 1607 | 1987-07-24 | 0 | 1 | 50000 | 46282.9525 | 111748.6819 | Null | 0 | 0 |  | 19870724 | 60 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S PIPING | NO DATA |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | D.L. MERIWETHER PIPELINE SAFETY | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER DISCONNECTED GAS DRYER CONNECTION AND FILLED THE HOUSE WITH NATURAL GAS IN AN APPARENT SUICIDE ATTEMPT. HE THEN TURNED ON CENTRAL AIR CONDITIONER CAUSING AN EXPLOSION WHICH DESTROYED THE HOUSE.
2025-01-31 10:21 | YES | YES | 19870137 |  | 2696 | CONNECTICUT LIGHT & POWER CO | SOUTH MAIN STREET |  | PLYMOUTH | CT | 06782 | 4 | NO | 1349 | 1987-07-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 16 |  | 19870721 | 45 | 45 | BY TEST | 95 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | METER SET ASSEMBLY |  | VALVE |  | STEEL |  | 4 | 0 |  | NORRIS | 0 | 1969 | ABOVE GROUND |  | RICHARD J. CARNARILI MANAGER-METERS & SERVICE OPERATIONS | 2037212932 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | TWO EMPLOYEES WERE EDGAGED IN REMOVING AN AL5000 TX GAS METER FOR PERIODIC TEST. ONE EMPLOYEE ERRONEOUSLY REMOVED THE FLANGE BOLTS FROM THE PRESSURIZED SIDE OFA BLOCKING VALVE RESULTING IN GAS LEAKAGE AND SUBSEQUENT IGNITION. SECOND EMPLOYEE RECEIVED 2ND AND 3RD DEGREE BURNS REQUIRING HOSPITALIZATION.
2025-01-31 10:21 | YES | YES | 19870138 |  | 2596 | COLUMBIA GAS OF OHIO INC | WASHINGTON ST., WEST OF STATE ST. INTERS | ALBANY | ATHENS | OH | 45710 | 4 | NO | 1100 | 1987-08-05 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 25 |  | 19870805 | 20 | 40 | BY TEST | 40 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.395 | PE 2306 | DUPONT ALDY 1-A | 0 | 1972 | UNDER GROUND OR UNDER WATER |  | J.D. SLATER, MGR. CONSTR/MAINT. | 6144606000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | COLUMBIA GAS OF OHIO, INC., EMPLOYEE, WILLIAM ALLEN WAS OVERCOME FROM BREATHINGTOO MUCH GAS WHILE ATTEMPTING REPAIR. THE EMERGENCY SQUAD WAS SUMMONED TO TRANSPORT MR. ALLEN TO THE HOSPITAL FOR CHECK-OUT. HE WAS HELD OVERNIGHT FOR OBSERVATION AND SUBSEQUENTLY RELEASED.
2025-01-31 10:21 | YES | YES | 19870139 |  | 13580 | NORTH CAROLINA NATURAL GAS CORP | 4615 MARKET ST. | WILMINGTON | NEW HANOVER | NC | 28401 | 2 | NO | 1114 | 1987-08-05 | 1 | 18 | 25000 | 23141.4763 | 55874.3409 | Null | 8 | 45 |  | 19870805 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6.625 | 0.188 | API5-GRADE B | L.B. FOSTER | 1959 | 1959 | UNDER PAVEMENT |  | WALLACE W. TODD SUPT. OF CONSTRUCTION & MAINTENANCE | 9194830315 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-07-30 | YES | 3 | PAINT (YELLOW) | YES |  |  | AUGUST 5 11:14 A.M - NORTH CAROLINA NATURAL GAS CORPORATION'S DISTRICT OFFICE WAS NOTIFIED OF A LINE BROKEN AND GAS BLOWING AT MARKET STREET AND KERR AVENUE. TWO SERVICEMEN WERE DISPATCHED TO THE SCENE.AUGUST 5 11:15 A.M - THE CONSTRUCTION OFFICE WAS NOTIFIED OF THE BREAK. DISPATCHED TO THE SCENE WERE DOUG FIELDS, ASSISTANT DIVISION SUPERINTENDENT AND A CONSTRUCTION CREW, FROM SEPARATE LOCATIONS.AUGUST 5 11:33 A.M - THE FIRE DEPARTMENT NOTIFIED THE GAS COMPANY THAT THEY WERE ENROUTE TO THE BREAK.AUGUST 5 12:15 P.M - MR. FIELDS NOTIFIED THE CONSTRUCTION OFFICE THAT A 3/4" TEE WAS PULLED FROM A 6" INTERMEDIATE PRESSURE MAIN (60 PSI) RESULTING IN A HOLE, APPROXIMATELY 1 1/4" IN DIAMETER ON THE TOP OF THE PIPE. A REQUEST WAS MADE TO NOTIFY THE CITY FOR A WATER LINE LOCATION AND TO HAVE THE WATER TURNED OFF. IN ATTEMPTING TO DIG AROUND THE GAS MAIN FOR THE PURPOSE OFINSTALLING A REPAIR CLAMP, THE GAS COMPANY EQUIPMENT OPERATOR HIT AND BROKE A CAST IRON WATER MAIN LOCATED APPROXIMATELY 32" AWAY FROM THE GAS MAIN, CENTER TO CENTER. WATER PUPS WERE PROVIDED BY THE CITY WATER DEPARTMENT AND ONE WAS BROUGHT IN B
2025-01-31 10:21 | YES | YES | 19870140 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | 4169 S. LOWE | CHICAGO | COOK | IL | 60609 | 3 | NO | 1555 | 1987-07-27 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 5 |  | 19870727 | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | TAP HOLE | CAST IRON |  | 6 | 0 |  |  | 0 | 1899 | OTHER | 4'X6' FOR SEV.RENEWAL | J.M. SKUBISZ DISTRICT SUPERINTENDENT | 3129624800 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BAGS AND STOPPERS HAD BEEN INSERTED INTO A 6" C.I.L.P. MAIN THROUGH AN EXISTING1.5" TAP HOLE, TO PREVENT THE FLOW OF GAS DURING A SERVICE RENEWAL OFF THE END OF THE MAIN. THE EMPLOYEE HAD TROUBLE GETTING THE PLUG STARTED ON THE MAIN AFTERREMOVING THE BAGS AND STOPPERS. A LARGER THAN USUAL AMOUNT OF GAS ESCAPED AND WAS IGNITED FROM AN UNKNOWN SOURCE. TWO EMPLOYEES WERE HOSPITALIZED WITH BURNS.
2025-01-31 10:21 | NO | NO | 19870141 |  | 11680 | LONE STAR GAS CO | PRESTON RD. & SPRING CREEK PARKWAY | PLANO | COLLIN | TX | 75074 | 2 | NO | 917 | 1987-07-23 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 6 |  | 19870723 | 160 | 175 | BY TEST | 275 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | AP156 GR. B |  | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | JERALD A. CRAVY - C & M SUPT. | 2144873840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-07-15 | YES | 1 |  | NO |  |  | LINE HIT BY TRACK LOADER MAKING 1" X 3" HOLE IN SIDE OF 6" MAIN.
2025-01-31 10:21 | NO | NO | 19870143 |  | 11680 | LONE STAR GAS CO | 2700 SIMPSON STUART | DALLAS | DALLAS | TX |  | 3 | NO | 1232 | 1987-07-29 | 0 | 0 | 4000 | 3702.6362 | 8939.8946 | Null | 3 | 45 |  | 19870729 | 35 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | API 5L GD. B | STEEL | 0 | 1944 | UNDER GROUND OR UNDER WATER |  | KEN BAILEY SUPERVISOR | 2146702472 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | MAIN HIT BY BILLDOZER WHILE DIGGING TO BURY TRASH.
2025-01-31 10:21 | NO | NO | 19870144 |  | 11680 | LONE STAR GAS CO | 2040 VALLEY VIEW CENTER | DALLAS | DALLAS | TX |  | 2 | NO | 1204 | 1987-07-21 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 43 |  | 19870721 | 20 | 55 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0 | 0 | SDR-11 |  | 1972 | 1972 | UNDER PAVEMENT |  | B.L. SPEARS | 2142763746 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE 3" X 4" STRAIGHT REDUCER APPEARED TO BE UNDER A STRESS CAUSING FITTING TO CRACK.
2025-01-31 10:21 | YES | YES | 19870149 |  | 11800 | LOUISIANA GAS SERVICE CO | POLK ST. & BENTON AVE. | MONROE | OUACHITA | LA | 71201 | 3 | NO | 910 | 1987-09-01 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19870901 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | FITTING |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | A TRENCHING MACHINE OPERATED BY COMPANY PERSONNEL STRUCK A SERVICE LINE AND PULLED IT FROM A COMPRESSION COUPLING CAUSING A DISCHARGE OF NATURAL GAS. A WELDER AND HIS HELPER WERE WORKING NEARBY. NATURAL GAS WAS APPARENTLY IGNITED BY THE WELDING TORCH AND CAUSED SECOND DEGREE BURNS ON BOTH FOREARMS OF THE WELDER'S HELPER. THE MAIN WAS SHUT OFF TO MAKE REPARIS AND 40 CUSTOMERS WERE WITHOUT GAS FOR 45 MINUTES.
2025-01-31 10:21 | YES | YES | 19870151 |  | 180 | ALABAMA GAS CORP | 1730-D VALLEY AVENUE | HOMEWOOD | JEFFERSON | AL | 35209 | 3 | NO | 1823 | 1987-09-11 | 0 | 1 | 1000 | 925.6591 | 2234.9736 | Null | 0 | 7 |  | 19870911 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | JOINT | FLARE | OTHER | STEEL TUBING | 58 | 0 |  |  | 0 | 0 | NO DATA |  | RONALD TAYLOR | 2053268471 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER SMELLED GAS INSIDE PREMISES AND CLIMBED ATTIC STAIRS TO INVESTIGATE. UPON REACHING ATTIC, HE TURNED ON AN ELECTRIC LIGHT SWITCH AND A FLASH OCCURRED. GAS WAS TURNED OFF AT THE METER BY THE FIRE DEPARTMENT. AFTER AN INVESTIGATION, IT WAS DETERMINED THAT THE GAS LEAK HAS OCCURRED ON CUSTOMER'S FUEL LINE AS A RESULT OF AN IMPROPER FLARE ON THE 5/8" TUBING CONNECTING THE FURNACE TO THE 3/4" BLACK PIPE. THE TUBING HAD PULLED OUT OF THE TUBING COLLAR ALLOWING GAS TO ESCAPE
2025-01-31 10:21 | NO | NO | 19870153 |  | 11680 | LONE STAR GAS CO | POE STREET AND HWY 67 | SAN ANGELO | TOM GREEN | TX |  | 2 | NO | 1125 | 1987-07-30 | 0 | 0 | 1200 | 1110.7909 | 2681.9684 | Null | 0 | 0 |  | 19870730 | 70 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0.203 | X-4.2 |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CLAYTON KUHLMANN | 9156558171 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 | TEMPORARY STAKES | YES |  |  | CUT LINE BY DITCHING CONTRACTOR.
2025-01-31 10:21 | NO | NO | 19870156 |  | 18532 | SOUTHERN UNION GAS CO | IH 35 SOUTH & LITTLE TEXAS LANE | AUSTIN | TRAVIS | TX | 78745 | 3 | NO | 859 | 1987-09-15 | 0 | 0 | 1200 | 1110.7909 | 2681.9684 | YES | 0 | 46 |  | 19870915 | 34 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 6 | 0.188 | API-5L-B |  | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX | 5124775852 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-09-03 | YES | 3 | YELLOW PAINT | NO |  |  | SOUTHERN UNION GAS LINE LOCATOR HAD MET WITH CITY CREW ON 9-8-87 AND LOCATED THE GAS MAIN AT SEVERAL POINTS. THE CITY CREW REPRESENTATIVE WAS PRESENT WHEN EACHMARK OVER MAIN WAS PLACED AND WAS SATISFIED. CITY ENG. DECIDED TO MOVE POLE LOCATION AND FAILED TO NOTIFY.
2025-01-31 10:21 | NO | NO | 19870160 |  | 18532 | SOUTHERN UNION GAS CO | WESTLAKE DR. AT LAKE PLACE | AUSTIN | TRAVIS | TX | 78746 | 3 | NO | 1019 | 1987-08-21 | 0 | 0 | 3000 | 2776.9772 | 6704.9209 | Null | 0 | 33 |  | 19870821 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L-B |  | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-07-28 | YES | 2 |  | NO |  |  | CONTRACTOR WAS EXCAVATING EXISTING STREET TO NEW SUB-GRADE WITH DOZER. FRONT BLADE OF DOZER SHIFTED TOO DEEP AFTER ENCOUNTERING LARGE ROCK. WHEN OPERATOR RAISED FRONT BLADE OF DOZER SHIFTED TOO DEEP AFTER ENCOUNTERING LARGE ROCK. WHEN OPERATOR RAISED FRONT BLADE, THE BLADE MADE CONTACT WITH 6" WS GAS MAIN AND PUNCTURED A HOLE IN THE MAIN.
2025-01-31 10:21 | NO | NO | 19870162 |  | 11680 | LONE STAR GAS CO | WYATT & KIMBROUGH | WHITE SETTLEMENT | TARRANT | TX | 76108 | 3 | NO | 131 | 1987-08-15 | 0 | 0 | 2000 | 1851.3181 | 4469.9473 | Null | 2 | 30 |  | 19870815 | 20 | 60 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | MAIN |  | NO DATA |  | STEEL |  | 3 | 0.156 | API-5L |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | W.C. HILL, JR. | 8173368381 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | PIPE COATING KNOCKED OFF | COATED | YES | 1974 | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHEN VAN HIT AND BROKE LIGHT POLE, THIS RESULTED IN A FIRE AT GATE VALVE BOX; SOURCE OF IGNITION UNKNOWN.
2025-01-31 10:21 | NO | NO | 19870163 |  | 11680 | LONE STAR GAS CO | RILEY ROAD AT I-44 | WICHITA FALLS | WICHITA | TX |  | 1 | NO | 1740 | 1987-07-13 | 0 | 0 | 10000 | 9256.5905 | 22349.7364 | Null | 4 | 30 |  | 19870713 | 130 | 175 | BY TEST | 263 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | BOBBY CLARK | 8177664151 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-05-08 | YES | 3 | FLAGS | NO |  |  | SUBCONTRACTOR LAYING A WATER LINE HIT OUR GAS MAIN WITH BACKHOE RUPTURING THE MAIN.
2025-01-31 10:21 | NO | NO | 19870165 |  | 4473 | ENERGAS CO | 300 ENNIS | PLAINVIEW | HALE | TX | 79073 | 3 | NO | 600 | 1987-09-23 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19870923 | 15 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN UNKNOWN PERSON TURNED OFF VALVE IN BLOCK GATE SETTING -- CUT GAS TO 32 RESIDENCES.
2025-01-31 10:21 | NO | NO | 19870166 |  | 4473 | ENERGAS CO | 301 TAYLOR ST. | AMARILLO | POTTER | TX | 79189 | 1 | NO | 500 | 1987-09-24 | 0 | 0 | 25000 | 23141.4763 | 55874.3409 | Null | 0 | 30 |  | 19870924 | 0.5 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN DESTROYED HOME.
2025-01-31 10:21 | NO | NO | 19870167 |  | 4473 | ENERGAS CO | 2204-20TH STREET | LUBBOCK | LUBBOCK | TX | 79411 | 3 | NO | 1400 | 1987-10-02 | 0 | 0 | 1750 | 1619.9033 | 3911.2039 | Null | 0 | 10 |  | 19871002 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES FULKERSON | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAK ON CUSTOMER PIPING-PLASTIC CONNECTION ON DRYER
2025-01-31 10:21 | NO | NO | 19870168 |  | 4473 | ENERGAS CO | 505 W. BROADWAY | TULIA | SWISHER | TX | 78088 | 3 | NO | 1645 | 1987-09-03 | 0 | 0 | 5000 | 4628.2953 | 11174.8682 | Null | 0 | 30 |  | 19870930 | 0.5 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S PREMISES | NO DATA |  | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TENANT HAD MOVED OUT OF RENTAL HOUSE. WHEN AN APPLIANCE WAS REMOVED, GAS VALVE WAS APPARENTLY LEFT PARTIALLY OPEN. GAS ACCUMULATED AND EXPLODED WHEN THE LANDLORD ENTERED THE HOUSE.
2025-01-31 10:21 | YES | YES | 19870169 |  | 4473 | ENERGAS CO | 2706 AVENUE P | LUBBOCK | LUBBOCK | TX | 79405 | 3 | NO | 800 | 1987-09-21 | 0 | 1 | 20000 | 18513.181 | 44699.4728 | Null | 0 | 30 |  | 19870921 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES FULKERSON | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | RECEIVED A CALL FROM THE FIRE DEPT. AT 8:31A.M., 9/21/87 ADVISING THAT THERE HAD BEEN AN EXPLOSION AT 2706 AVENUE P. ONE WAS WAS INJURED AND HAD BEEN TAKEN TO THE HOSPITAL. INVESTIGATION SHOWED THAT TWO UNITS OF THE QUADRUPLEX HAD BEEN DAMAGED DUE TO AN EXPLOSION AND AN ACCOMPANYING FLASH FIRE. THE SHUT-IN TEST ON THEMETER INDICATED 2/10 CFH LEAK ON THE PIPING SERVING THE QUADRUPLEX, SO THE METER WAS BLINDED. IT HAD ALREADY BEEN TURNED OFF BY THE FIRE DEPT. IT WAS REPORTED THAT CLARENCE RANDAL COY WAS ASLEEP IN THE QUADRUPLEX THAT WAS DAMAGED MOST HEAVILY AND HAD SUFFERED FIRST AND SECOND DEGREES BURNS TO THE FACE ARMS. REPORTEDLYHE HAD NOT BEEN SMOKING AND THE SOURCE OF IGNITION IS UNKNOWN. IT IS THEORIZED THAT IT COULD HAVE COME FROM THE HOT WATER HEATER OR THE UNIT OF THE REFRIGERATOR COMING ON. THEY KNOW THAT IT WAS NOT THE RANGE PILOT BECAUSE THEY HAD BEEN TURNED OFF FOR SOME TIME BECAUSE THEY DID NOT WORK. LEAK SEARCH OF ALL THE ADJACENTPIPING INDICATED NO LEAKS BOTH ON CUSTOMER PIPING AND ADJACENT COMPANY LINE. THIS ACCOUNT IS ON IN THE NAME OF E.W. HARE. THE RECORDS SHOW NO UNUSUAL AMOUNT OFGAS CONSUMPTION, ONLY 3 MCF SINCE METER READING ON 8/27, 1 MCF IN MONTH BEFORE,AND 2 EACH FOR THE PREVIOUS THREE MONTHS.
2025-01-31 10:21 | NO | NO | 19870174 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 826 SILLIMAN STREET | SAN FRANCISCO | SAN FRANCISCO | CA | 94134 | 4 | NO | 850 | 1987-04-25 | 0 | 0 | 51000 | 47208.6116 | 113983.6555 | YES | 0 | 5 |  | 19870425 | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | CAST IRON | COPPER (SERVICE) | 0 | 0 | 5B | AMERICAN | 0 | 1961 | ABOVE GROUND |  | J.B. STOUTAMORE | 4159733203 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE OF UNKNOWN ORIGIN SPREAD TO METER, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVACUATED & TRAFFIC WAS REROUTED AS A PRECAUTION.
2025-01-31 10:21 | YES | NO | 19870175 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1281 VETERANS BLVD. | REDWOOD CITY | SAN MATEO | CA | 94062 | 3 | NO | 230 | 1987-05-12 | 0 | 0 | 1000000 | 925659.051 | 2234973.638 | YES | 1 | 45 |  | 19870512 | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSELINE | NO DATA |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J.B. STOUTAMORE | 4159733203 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | STRUCTURE FIRE OF UNKNOWN ORIGIN CAUSED A ROOF-MOUNTED GAS FURNACE TO COLLAPSE ONTO HOUSELINE, ALLOWING GAS TO ESCAPE AND IGNITE. TRAFFIC WAS REROUTED AND BUILDINGS EVACUATED.
2025-01-31 10:21 | YES | NO | 19870176 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 406 MAIN STREET | WATSONVILLE | SANTA CRUZ | CA |  | 3 | NO | 1550 | 1987-07-24 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 0 |  | 19870724 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER BOILER | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J.B. STOUTAMORE | 4159733203 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A BOILER SERVICEMAN WAS WORKING ON A BOILER IN THE BASEMENT WHEN EXPLOSION OCCURRED. FIRE DEPT. STOPPED GAS FLOW PRIOR TO CO. ARRIVAL.
2025-01-31 10:21 | YES | YES | 19870177 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2550 VAN NESS AVENUE | SAN FRANCISCO | SAN FRANCISCO | CA | 94109 | 4 | NO | 1213 | 1987-08-23 | 0 | 2 | 1000 | 925.6591 | 2234.9736 | Null | 0 | 0 |  | 19870823 | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER BOILER | OTHER | CUSTOMER BOILER | OTHER | STEEL BOILER | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J.B. STOUTAMORE | 4159733203 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A CUSTOMER'S BOILER FLASHED BACK WHEN CUSTOMER IMPROPERLY TRIED TO RELIGHT IT. SERVICE WAS SHUT DOWN & BUILDING EVACUATED.
2025-01-31 10:21 | NO | NO | 19870178 |  | 18532 | SOUTHERN UNION GAS CO | 3507 JEFFERSON STREET | AUSTIN | TRAVIS | TX | 78731 | 4 | NO | 1030 | 1987-10-13 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19871013 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE | PVC | BODY OF PIPE |  | NO DATA |  | 0.75 | 0 |  | CUPPLES | 0 | 1968 | UNDER PAVEMENT |  | B.R. KNOX | 0000000000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-09-28 | NO | 0 |  | NO |  |  | CITY CREW WAS EXCAVATING TO INSTALL 4" WATER MAIN WHEN THEY DAMAGED THE PVC SERVICE LINE THAT WAS SERVING 3700 JEFFERSON STREET. DAMAGE OCCURRED 140' NORTH OF THE NORTH PROPERTY LINE OF WEST 35TH ST. AND 20' EAST OF THE WEST PROPERTY LINE OF JEFFERSON ST. CITY CREW EXCAVATING WITH RUBBER TIRE BACKHOE TO INSTALL 4" WATER MAIN STRUCK AND DAMAGED A 3/4" PVC SERVICE LINE.
2025-01-31 10:21 | NO | NO | 19870179 |  | 13660 | NORTH SHORE GAS CO | 16070 ROUTE 22 | PRAIRIE VIEW | LAKE | IL | 60069 | 3 | NO | 1338 | 1987-07-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 17 |  | 19870728 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | PE 3408 | PHILLIPS PRODUCTS | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | R.W. STEGMAN | 3123367400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR'S EQUIPMENT CUT THE 4" PLASTIC SERVICE TO A HIGH SCHOOL. FIFTY PEOPLE WERE EVACUATED FROM THE BLDG. BY THE FIRE DEPT. NO IGNITION, INJURIES OR OTHERDAMAGE OCCURRED.
2025-01-31 10:21 | YES | YES | 19870180 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 8050 LAMPSON AVENUE | STANTON | ORANGE | CA | 90680 | 3 | NO | 1053 | 1987-07-07 | 0 | 1 | 2500 | 2314.1476 | 5587.4341 | Null | 1 | 42 |  | 19870707 | 42 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PLEXCO | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | L.M. STEWART | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A CONTRACTOR, WHILE MECHANICALLY TRENCHING TO INSTALL AN ELECTRICAL CONDUIT, STRUCK AND DAMAGED A 2" PE SERVICE ALLOWING GAS TO ESCAPE AT 42 PSIG. THE CONTRACTOR EXPERIENCED FIRST AND SECOND DEGREE BURNS TO HIS UPPER BODY AS THE ESCAPING GAS IGNITED. HE WAS TRANSPORTED BY AMBULANCE TO THE UNIVERSITY OF CALIFORNIA, IRVINE, BURN CENTER WHERE HE WAS ADMITTED FOR TREATMENT. THE STANTON CITY FIRE DEPT. CONTAINED THE FIRE AS SOUTHERN CALIFORNIA GAS COMPANY (SOCAL GAS).PERSONNEL BROUGHT THE GAS UNDER CONTROL BY PINCHING THE SUPPLYING 2" MAIN ON EACH SIDE OF THE SERVICE CONNECTION. THERE WAS NO EVACUATION OR INTERRUPTION OF GAS AS THE DAMAGED SERVICE WAS IN AN AREA STILL UNDER CONSTRUCTION. TRAFFIC ON LAWSON AVENUE WAS BLOCKED AT BEACH BLVD A6D SAN MARCOS DR. SOCAL GAS PROPERTY DAMAGE IS ESTIMATED AT $2,500.00
2025-01-31 10:21 | YES | YES | 19870181 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 10632 PENROSE STREET | LOS ANGELES | LOS ANGELES | CA | 91352 | 3 | NO | 1235 | 1987-06-25 | 0 | 1 | 500 | 462.8295 | 1117.4868 | Null | 0 | 30 |  | 19870625 | 35 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | UNAUTHORIZED PIPING | JOINT | SCREW | STEEL |  | 0.5 | 0.133 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | L.M. STEWART | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A PLUMBER EXPERIENCED SECOND AND THIRD DEGREES BURNS TO HIS ARMS AND FACE WHEN HE ALLOWED GAS TO ESCAPE AND SUBSEQUENTLY IGNITE FROM AN ADJACENT WATER HEATER. WITHOUT FIRST SHUTTING OFF THE SUPPLY OF GAS, THE PLUMBER WAS ATTEMPTING TO ALTER WHAT HE SURMISED TO BE A 1/2" HOUSELINE OPERATING AT 8 TO 10 INCHES WATER COLUMN WHEN IN FACT IT WAS UP STREAM OF THE REGULATOR AND WAS PRESSURED TO 35 PSIG. AN INBESTIGATION HAS DETERMINED THAT AT SOME TIME PRIOR TO THIS INCIDENT, THE 1"STEEL SERVICE WAS ILLEGALLY EXTENDED WITH 1/2" PIPE AND ITS ATTACHED METER SET ASSEMBLY MOVED FROM ITS ORIGINAL LOCATION BY SOMEONE OTHER THAN THE SOUTHERN CALIFORNIA GAS COMPANY(SOCALGAS).
2025-01-31 10:21 | YES | YES | 19870182 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 515 PARK STREET | SALINAS | MONTEREY | CA |  | 3 | NO | 1400 | 1987-05-19 | 0 | 1 | 10300 | 9534.2882 | 23020.2285 | YES | 0 | 40 |  | 19870519 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREAD | STEEL |  | 0.75 | 0.113 | A-25 |  | 0 | 1963 | ABOVE GROUND |  | J.B. STOUTAMORE | 0000000000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | OUT OF CONTROL CAR STRUCK SIDE OF HOUSE SEVERING GAS SERVICE BELOW SHUTOFF, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED.
2025-01-31 10:21 | YES | YES | 19870185 |  | 4060 | EAST OHIO GAS CO | 637 ST. LAWRENCE BLVD. | EASTLAKE | LAKE | OH | 44094 | 3 | NO | 1150 | 1987-08-20 | 0 | 1 | 4000 | 3702.6362 | 8939.8946 | Null | 0 | 5 |  | 19870820 | 27 | 30 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 3 | 0.318 | 3406/8 | DRISCO | 1987 | 1987 | OTHER | IN EXCAVATION | PAUL E. OLEKSA | 2164326858 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEES WERE MAKING A 3-INCH HOT TAP CONNECTION TO A 4-INCH PLASTIC MAIN. AFTER THE TAP WAS MADE, THE 3-INCH CONNECTION WAS SQUEEZED OFF IN PREPARATION FOR A3-INCH VALVE TO BE BUTT FUSED ONTO THE 3-INCH OPENING. BECAUSE OF OBSTRUCTIONS FROM TELEPHONE AND ELECTRIC CABLES, THE CREW HAD DIFFICULTY PLACING THE FUSION EQUIPMENT. TO MAKE MORE ROOM THEY ATTEMPTED TO MOVE THE SQUEEZE OFF DEVICE. WHEN THE SQUEEZE OFF DEVICE WAS LOOSENED, GAS BLEW OUT OF THE OPEN END OF THE 3-INCH LATERAL AT ABOUT 27PSIG. THE GAS IGNITED EITHER FROM STATIC ELECTRICITY OR THE NEARBY GASOLINE OPERATED GENERATOR.
2025-01-31 10:21 | YES | NO | 19870187 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 4440 CADIEUX | DETROIT | WAYNE | MI | 48224 | 3 | NO | 1405 | 1987-08-18 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 20 |  | 19870819 | 2 | 2 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRUCE NIEMAN | 3132566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BASED ON THE EXTENT OF DAMAGE TO THE STRUCTURE, THE PRELIMINARY DETERMINATION OF THE CAUSE OF THE FIRE AND EXPLOSION WAS UNCONFINED NATURAL GAS INSIDE THE STRUCTURE. THE SUSPECTED SOURCE OF THE GAS LEAK IS THE GAS METER. THE CAUSE OF THE LEAK CANNOT BE DEFINITELY DETERMINED.
2025-01-31 10:21 | YES | NO | 19870188 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 600 SOUTH SANTA FE STREET | HEMET | RIVERSIDE | CA | 92343 | 3 | NO | 1515 | 1987-08-13 | 0 | 0 | 110000 | 101822.4956 | 245847.1002 | YES | 2 | 55 |  | 19870814 | 55 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | API STD. 5L |  | 1974 | 1975 | ABOVE GROUND |  | L.M. STEWART | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TWO PARKED VEHICLES WERE STRUCK BY AN OUT OF CONTROL VEHICLE. ONE VEHICLE WAS PUSHED FORWARD OVER A SMALL CURB, STRIKING THE METER ASSEMBLY (MSA), SHEARING OFFTHE SERVICE RISER SHUT OFF VALVE. ESCAPING GAS AT 55 PSIG WAS IGNITED, MOST LIKELY FROM SPARKS CREATED AS THE CARS CONTINUED ON THROUGH A STUCCO GARAGE WALL. THE SECOND VEHICLE WAS ALSO PUSHED FORWARD STRIKING ANOTHER M.S.A., BREAKING THE HOUSELINE ALLOWING GAS TO ESCAPE AND IGNITE. THE RESULTING FIRE WAS CONTROLLED BY THE HEMET CITY FIRE DEPARTMENT AS SOUTHERN CALIFORNIA GAS COMPANY(SOCALGAS) PERSONNEL BROUGHT THE ESCAPING GAS UNDER CONTROL BY PINCHING THE SERVICE.
2025-01-31 10:21 | YES | YES | 19870189 |  | 12484 | MIDWEST GAS CO | 2020 E. 25TH STREET | DES MOINES | POLK | IA | 50317 | 2 | NO | 108 | 1987-09-09 | 2 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 15 |  | 19870909 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINE | JOINT | FLARE | OTHER | COPPER | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS H. HUTCHINS | 5152423977 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE EXPLOSION AT THIS LOCATION WAS CAUSED BY LEAKAGE ON THE GAS CUSTOMER'S FUELLINE PIPING, DOWNSTREAM OF THE MIDWEST GAS COMPANY METER. THE LEAKAGE OCCURRED AT THE JUNCTION OF THE CUSTOMERS COPPER FUEL LINE WITH HIS IRON PIPE FUEL LINE. AT THIS LOCATION, THE COPPER PIPING WAS CONNECTED TO THE IRON PIPING WITH A FLARED TUBING CONNECTOR. THE TUBING INSERTED INTO THE CONNECTOR WAS NOT FLARED PROPERLY AND CONSEQUENTLY PULLED OUT OF THE CONNECTOR DUE TO SOME UNKNOWN EXTERNAL FORCE. UPON PULLOUT, NATURAL GAS LEAKED INTO THE HOUSE CRAWL SPACE AND EXPLODED UPON IGNITION. THE ULTIMATE CAUSE APPEARS TO BE A CONSTRUCTION DEFECT ON THE PART OF THE INSTALLER OF THE COPPER FUEL LINE TUBING. THIS COMMENTARY IS PRELIMINARY AND MAY BE REVISED AT SUCH TIME AS THE STATE FIRE MARSHAL'S REPORT ON THE PIPINGIS RELEASED.
2025-01-31 10:21 | YES | NO | 19870191 |  | 3240 | DELMARVA POWER & LIGHT CO | 19 PIERCE ROAD, | WILMINGTON | NEW CASTLE | DE | 19803 | 3 | NO | 1300 | 1987-10-20 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 45 |  | 19871020 | 30 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1954 | WITHIN/UNDER BUILDING |  | WALTER G. ROBBINS, JR. | 3024293559 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-10-01 | YES | 3 | YELLOW PAINT | YES |  |  | DELMARVA POWER WAS NOTIFIED BY THE FIRE BOARD AT 1:08 P.M. ON OCTOBER 20, 1987 OF AN EXPLOSION AND FIRE AT 119 PIERCE ROAD IN DEERHURST. THE SERVICE LINE TO THIS HOUSE HAD BEEN LOCATED AND MARKED WITH YELLOW PAINT ON OCTOBER 10, 1987 AS REQUESTED BY THE EXCAVATOR, WHO WAS TRENCHING FOR THE INSTALLATION OF STORM DRAINSIN THE ROADWAY ON OCTOBER 20, 1987, PULLED UP THE SERVICE WHICH CAUSED IT TO SEPARATE AT A COMPRESSION COUPLING NEAR THE HOUSE. THE EXCAVATOR DID NOT NOTIFY DELMARVA THAT HE HAD HIT THE LINE. ESCAPING GAS APPARENTLY ENTERED THE RESIDENCE WHICH LEAD TO AN EXPLOSION. ESCAPING GAS WAS ALSO IGNITED OUTSIDE OF THE RESIDENCE
2025-01-31 10:21 | NO | NO | 19870193 |  | 4473 | ENERGAS CO | 210 SMITH STREET | PLAINVIEW | HALE | TX | 79073 | 3 | NO | 210 | 1987-10-03 | 0 | 0 | 15000 | 13884.8858 | 33524.6046 | Null | 0 | 30 |  | 19871003 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN DAMAGED HOUSE.
2025-01-31 10:21 | YES | YES | 19870194 |  | 15350 | PEOPLES NATURAL GAS CO | MCMILLAN ROAD | UPPER ST CLAIR | ALLEGHENY | PA | 15241 | 3 | NO | 1330 | 1987-10-09 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 2 |  | 19871009 | 60 | 90 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | REGULATING STATION | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SUSAN G. GEORGE | 4125536635 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | PURGING OPERATION | REGULATION FACILITY WAS BEING PLACED BACK INTO SERVICE AFTER UNDERGOING REVISION. FACILITY INLET AND OUTLET TIE-INS HAD BEEN COMPLETED, AND FINAL PURGING OF EQUIPMENT WAS IN PROGRESS. ACCIDENTAL IGNITION OCCURRED, CAUSE UNKNOWN, INJURING TWO OF THE SEVEN EMPLOYEE ON THE JOB SITE. A BRIEF FIRE RESULTED THAT WAS IMMEDIATELY EXTINGUISHED. DAMAGE TO FACILITY AND SURROUNDING AREA WAS NOMINAL.
2025-01-31 10:21 | YES | YES | 19870195 |  | 11464 | LIBERAL GAS CO | HWY 54 E | LIBERAL | SEWARD | KS | 67901 | 0 | NO | 400 | 1987-10-20 | 0 | 1 | 10000 | 9256.5905 | 22349.7364 | YES | 0 | 15 |  | 19871020 | 5.5 | 8 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | BODY OF PIPE |  | STEEL |  | 12.5 | 0 | 3860998860 | 998MERKEL GAS OIL | 0 | 0 | NO DATA | 263294411 DARREN DR. | [8 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19870198 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | DETROIT | WAYNE | MI | 48223 | 3 | NO | 1047 | 1987-10-31 | 0 | 2 | 0 | 0 | 0 | YES | 0 | 19 |  | 19871031 | 14 | 2 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | OTHER | FUEL LINE UNCAPPED | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRUCE NIEMAN MANAGER CODES AND STANDARDS | 3132566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SEE PART "D".
2025-01-31 10:21 | YES | YES | 19870201 |  | 2668 | COMMONWEALTH GAS SERVICES INC | LONDON BLVD.& GREEN STREET | PORTSMOUTH |  | VA | 23704 | 2 | NO | 845 | 1987-10-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19871008 | 8.5 | 10 |  | 3 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | TELEPHONE M.H. | VALVE | B&S | CAST IRON |  | 10 | 0.7 |  |  | 0 | 1890 | UNDER PAVEMENT |  | ROBERT B. EARLY,PLANT MANAGER | 8043937222 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | C&P TELEPHONE PRIVATE CONTRACTOR EMPLOYEE LIT A CIGARETTE IN MANHOLE CAUSING FLASH FIRE FROM WHAT WAS DETERMINED TO BE GASOLINE VAPOR ON 10/8/87.VAPOR ANALYS MADE ON 10/22/87 ALSO INDICATED PRESENCE OF NATURAL GAS IN MANHOLE. MINOR JOINT LEAKAGE IN ADJACENT CAST IRON LOW PRESSURE SYSTEM WAS FOUND WHICHWAS CAUSED BY SETTLEMENT OF SURROUNFING EARTH DUE TO WATER TABLE AND WATER MAINLEAKAGE.
2025-01-31 10:21 | YES | YES | 19870202 |  | 3170 | DAYTON POWER & LIGHT CO | ONE SPECIALITY PLACE | DAYTON | MONTGOMERY | OH | 45408 | 3 | NO | 1115 | 1987-10-09 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 30 |  | 19871009 | 28 | 35 |  | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 |  |  | 0 | 1957 | WITHIN/UNDER BUILDING |  | RICHARD C.ROTH,MANAGER | 5132272145 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | CHEMICALS USED IN PAPER PROCESS ALSO STORED IN AREA OF VAULT.
2025-01-31 10:21 | YES | YES | 19870203 |  | 20010 | U G I CORP | 54 DERRY STREET | HARRISBURG | DAUPHIN | PA | 17111 | 3 | NO | 1548 | 1987-10-14 | 0 | 2 | 250000 | 231414.7627 | 558743.4095 | Null | 0 | 0 |  | 19871014 | 53 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | THREADS AT END OF STL PIP | STEEL |  | 0.75 | 0.113 | API 5L |  | 0 | 1969 | WITHIN/UNDER BUILDING |  | CHARLES W. BECKER,MANAGER-ENGINEERING SERVICES | 2153754441 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-09-30 | YES | 3 | LOC.PAINTED MACADAM | YES |  |  | CONTRACTOR PULLED MEDIUM PRESSURE SERVICE WITH BACKHOE CAUSING TO FRACTURE WITHIN BUILDING, ALLOWING UNCONTROLLED ESCAPE OF GAS.
2025-01-31 10:21 | YES | YES | 19870205 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2100 PROSPECT COURT | MENLO PARK | SAN MATEO | CA |  | 3 | NO | 1140 | 1987-10-05 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 27 |  | 19871005 | 30 | 40 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 | 2800 |  | 0 | 1941 | UNDER PAVEMENT |  | J.B.STOUTAMORE,V.P.,GAS OPERATIONS | 4159733204 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-09-21 | YES | 3 | PAIN ON STREET | YES |  |  | CONTRACTOR USING A TRENCHER TO INSTALL CABLE TV STRUCK 3/4" STEEL SERVICE, ALLOWING GAS TO ESCAPE & IGNITE.TRAFFIC WAS REROUTED AS A PRECAUTION.
2025-01-31 10:21 | YES | NO | 19870206 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 7920 EAST GOLDENROD CIRCLE | BUENA PARK | ORANGE | CA | 90620 | 3 | NO | 1306 | 1987-10-02 | 0 | 0 | 125000 | 115707.3814 | 279371.7047 | Null | 0 | 51 |  | 19871002 | 40 | 50 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER |  | VALVE |  | CAST IRON |  | 0 | 0 |  | MUELLER | 1956 | 1957 | ABOVE GROUND |  | L.M.STEWART,MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE CUSTOMER ATTEMPTED TO TURN ON THE GAS TO THE RESIDENCE AT THIS ADDRESS.IN DOING SO HE DISASSEMBLED THE SERVICE LINE VALVE AT THE INLET TO THE METER SET ASSEMBLR, PERMITTING GAS TO ESCAPE AT 40 PSIG. THE GAS IGNITED FROM AN UNKNOWN SOURCE AND THE RESIDENCE WAS DESTROYED. ESCAPING GAS WAS CONTROLLED BY PINCHING AND ABANDONING THE SERVICE LINE. THERE WERE NO INJURIES OR FATALITIES. DAMAGE TO SOUTHERN CALIFORNIA GAS FACILITIES WAS APPROXIMATELY $200. DAMAGE TO THE RESIDENCE IS ESTIMATED TO BE $125,000. GOLDENROD CIRCLE WAS BLOCKED BETWEEN STANTON AVENUE AND GARDENIA DRIVE.
2025-01-31 10:21 | YES | YES | 19870207 |  | 2392 | CITIZENS GAS & COKE UTILITY | 1671 LINCOLN ROAD | INDIANAPOLIS | MARION | IN | 46224 | 3 | NO | 1915 | 1987-11-04 | 0 | 1 | 80000 | 74052.7241 | 178797.891 | Null | 1 | 0 |  | 19871104 | 25 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.4 |  |  | 0 | 1954 | UNDER PAVEMENT |  | DAVID A. KAISER DIRECTOR OF DISTRIBUTION | 3179274628 | [6 empty] | Null |  | NO DATA | SUBSIDENCE | NO |  | NO | 0 |  | NO |  |  | AT 7:15 P.M. SPEEDWAY FIRE DEPARTMENT REPORTED AN EXPLOSION ABD FIRE AT 1671 LINCOLN ROAD. VARIOUS UTILITY PERSONNEL WERE DISPATCHED TO THE SCENE. UPON ARRIVAL, UTILITY PERSONNEL FOUND THE RESIDENCE AT 16711 LINCOLN ROAD DEMOLISHED WITH INJURIES TO ONE (1) RESIDENT, AND GAS MIGRATING THROUGH THE GROUND AND INTO ADJACENT RESIDENCES. SEVENTEEN (17) RESIDENCE WERE EVACUATED AND THE AFFECTED MAIN SECTION WAS VALVED OFF BY 8:15 P.M. THE MAIN WAS EXPOSED, THE LEAKING SECTION OF MAIN AND SERVICE TO 1671 LINCOLN ROAD WERE ABANDONED AND GAS SERVICE WAS RESTORED TO THE EVACUATED RESIDENCES BY 12:19 A.M., 11/5/87. A CIRCUMFERENTIAL STRESS CRACK WAS SUBSEQUENTLY DISCOVERED IN THE SIX INCH (6") CAST IRON MAIN WHICH ALLOWED GAS TO MIGRATE THROUGH THE GROUND AND INTO THE RESIDENCE AT 1671 LINCOLN ROAD. EXPLOSION AND FIRE RESULTED WHEN A CIGARETTE WAS LIT. THE INJURED RESIDENT, MR. JEROME DAUGHERTY, AGE 51, SUFFERED BURNS ON HIS FACE AND HANDS AND IS IN SERIOUS CONDITION AT WISHARD HOSPITAL.
2025-01-31 10:21 | YES | YES | 19870208 |  | 11680 | LONE STAR GAS CO | 3404 FLOYD | DALLAS | DALLAS | TX | 75204 | 3 | NO | 710 | 1987-10-09 | 0 | 1 | 0 | 0 | 0 | Null | 6 | 0 |  | 19871009 | 23 | 55 |  | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0 |  |  | 0 | 1941 | WITHIN/UNDER BUILDING |  | JAMES A. ROSS,SUPERINTENDENT | 2144267916 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS ACCUMULATED IN WATER METER BOX FROM LEAK ON 6"BARE STEEL IHP MAIN.
2025-01-31 10:21 | YES | YES | 19870210 |  | 4473 | ENERGAS CO | 510 40TH STREET | LUBBOCK | LUBBOCK | TX | 79404 | 3 | NO | 2025 | 1987-11-07 | 0 | 10 | 26000 | 24067.1353 | 58109.3146 | Null | 0 | 10 |  | 19871107 | 4375 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | CHARLES R. FULKERSON,DIVISION ENGINEER | 8064714228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THERE WAS AN EXPLOSION INSIDE THE HOUSE WHEN SOMEONE OPERATED A CIGARETTE LIGHTER. ACCORDING TO THE FIRE DEPARTMENT, IT WAS A NATURAL GAS EXPLOSION. THEY HADBEEN HAVING A PARTY AT THE HOUSE AND HAD BEEN THERE ALL DAY. THEY HAD NOT SMELLED THE ODOR OF GAS DURING THE DAY. ACCORDING TO THE CUSTOMER'S SON, THEY HADALL LEFT THE HOUSE. WHEN THEY ARRIVED BACK TO THE HOUSE,THEY SAW A Z28 CAMERO VEHICLE SPEEDING AWAY. HE THOUGHT SOMEONE HAD OPENED A LINE INSIDE THE HOUSE.THE FIREFIGHTERS REPORTED SMELLING HEAVY ODOR OF NATURAL GAS WHEN THEY ARRIVED AND THEY TURNED OFF THE GAS METER. PROBING AND USING A FLAME IONIZATION UNIT INDICATED NO GAS LEAKAGE ON THE CUSTOMER LINE OR ADJACENT ENERGAS DISTRIBUTIONLINES.
2025-01-31 10:21 | YES | NO | 19870211 |  | 22182 | WASHINGTON GAS LIGHT CO | 1217 GOLF COURSE DR |  | PRINCE GEORGES | MD | 20716 | 3 | NO | 1500 | 1987-11-13 | 0 | 0 | 103000 | 95342.8822 | 230202.2847 | Null | 1 | 0 |  | 19871113 | 28 | 55 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 6 | 0.581 |  | DUPONT | 0 | 1987 | UNDER GROUND OR UNDER WATER |  | CLARENCE E. GOODSON III,SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | NO REMARKS
2025-01-31 10:21 | YES | YES | 19870213 |  | 22210 | WASHINGTON WATER POWER CO | WEST 1824 FIRST AVENUE | SPOKANE | SPOKANE | WA | 99204 | 3 | NO | 1730 | 1987-11-26 | 0 | 1 | 8000 | 7405.2724 | 17879.7891 | Null | 0 | 10 |  | 19871127 | 14 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FACILITIES | OTHER | NO FAILURE | OTHER | GAS RANGE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LEN MITCHELL,GAS DISTRIBUTION ENGINEER | 5094824422 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS LETTER IS A FOLLOW-UP TO THE TELEPHONIC NOTIFICATION OF AN INCIDENT WHICH OCCURRED AT WEST 1824 FIRST AVENUE ON NOVEMBER 26, 1987. THE EXPLOSION CAUSED APPROXIMATELY $6000-$8000 DAMAGE TO ONE APARTMENT IN A 24 UNIT APARTMENT BUILDING.ONE WINDOW IN A NEIGHBORING BUILDING WAS ALSO DAMAGED. THE OCCUPANT OF THE APARTMENT WAS INJURED WITH SECOND DEGREE BURNS OVER %12 OF HER BODY. SHE IS IN SATISFACTORY CONDITION ACCORDING TO THE PRESS REPORTS. WASHINGTON WATER POWER COMPANY RECEIVED NOTIFICATION FROM THE FIRE DEPARTMENT AT 5:35 P.M. WWP SERVICEMEN ARRIVED AT THE SCENE AT APPROXMATELY 5:40P.M. GAS WAS SHUT OFF TO THE BUILDING AT5:40 P.M. BY THE FIRE DEPARTMENT AND THE BUILDING WAS ALSO EVACUATED AT THAT TIME. OCCUPANTS WERE ALLOWED TO RETURN TO THE BUILDING AT APPROXIMATELY 6:00P.M. SERVICE WAS RESTORED AND PILOT LIGHTS WERE RE-LIT TO THE BUILDING BY APPROXIMATELY 7:00P.M. AN ODORMETER READING WAS TAKEN SHOWING 0.23% GAS IN THE AIR. THE CAUSE OF THE INCIDENT WAS THE RELEASE OF GAS INTO THE APARTMENT FROM A GAS RANGE.THE IGNITION SOURCE IS STILL UNDETERMINED. THE FIRE DEPARTMENT IS INVESTIGATING THE INCIDENT FOR THE POSSIBILITY THAT IT WAS INTENTIONALLY SET.ALTHOUGH THID INCIDENT WAS ON CUSTOMER-OPWNED PIPING AND THEREFORE NOT REAUIRED TO BE REPORTED EITHER UNDER WAC 480-93-200 OR THE FEDERAL PIPELINE SAFETY REGULATIONS,WE DID FEEL THAT THE WUTC WOULD BE INTERESTED. MR LEN MITCHELL ATTEMPTED TO NOTIFY COMMISSION PERSONNAL AT APPROXIMATELY 10:30 AM, NOVEMBER 27, 1987. HE WAS SUCCESSFUL IN NOTIFYING A LADY AT MR COLBY'S RESIDENCE FRIDAY AFTERNOON, NOVEMBER 27, 1987, WHO SAID SHE WOULD GIVE THE MESSAGE TO HIM WHEN HE RETURNED FROM PORTLAND, OREGON. MR MITCHELL ALSO NOTIFIED THE NATIONAL RESPONSE CENTER AT 10:30 AM,FRIDAY, NOVEMBER 27, 1987. OUR PROCEDURES STATE THAT GAS ENGINEERING IS TO BE NOTIFIED OF GAS INCIDENTS INVOLVING COMPANY GAS FACILITIES. OUR FACILITIES WERE NOT INVOLVED. OUR SERVICEMENS WERE ADVISED THERE WERE NO INJURIES WHILE THEY WEREON THE SCENE. THE FIRST INFORMATION ON INJURIES CAME OVER THE 11:00 PM NEWS BROADCAST.
2025-01-31 10:21 | YES | YES | 19870214 |  | 4499 | ENTEX INC | FM HWY 14 | HAWKINS | WOOD | TX | 75765 | 2 | NO | 1535 | 1987-11-06 | 0 | 1 | 150 | 138.8489 | 335.246 | Null | 1 | 0 |  | 19871106 | 50 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.216 | ASTM D-1248 | DUPONT | 0 | 1987 | OTHER | IN OPEN TRENCH | B.F.BROYLES,DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PIPE WAS RUPTURED EARILER BY A HIGHWAY CONTRACTOR. RUPTURE WAS CLAMPED TO STOPBLOWING GAS. WHILE COMPANY CREW WAS PREPARING DAMAGED SECTION OF PLASTIC PIPE FOR REPLACEMENT, ESCAPING GAS WAS IGNITED BY UNKNOWN SOURCE, BUT PRESUSMED TO BESTATIC ELECTRICITY. TW0 (2) MEN WERE BURNED; ONE WAS BURNED ON RIGHT FOREARM AND ELBOW, ONE WAS BURNED OVER 50% OF HIS BODY AND REQUIRED HOSPITALIZATION.
2025-01-31 10:21 | NO | NO | 19870215 |  | 4499 | ENTEX INC | 6839 ROXBURY | HOUSTON | HARRIS | TX |  | 3 | NO | 1011 | 1987-11-16 | 0 | 0 | 10000 | 9256.5905 | 22349.7364 | Null | 0 | 29 |  | 19871116 | 21 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | BILLY F. BROYLES,DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LIGHTNING STRIKE ON METER.
2025-01-31 10:21 | YES | YES | 19870219 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 3146&3154 SPRING CREEK DRIVE | SANTA ROSA | SONOMA | CA | 95401 | 3 | NO | 130 | 1987-10-17 | 0 | 1 | 70000 | 64796.1336 | 156448.1547 | Null | 1 | 30 |  | 19871017 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUN | 0 | 0 | AM-5B | AMERICAN | 0 | 1977 | ABOVE GROUND |  | J.B. STOUTAMORE,VP-GAS OPERATIONS | 4159733204 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | SRTUCTURE FIRE SPREAD TO THE METERS AND REGULATORS, ALLOWING GAS TO ESCAPE AND IGNITE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED AS PRECAUTIONS.
2025-01-31 10:21 | YES | YES | 19870220 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 6858 KESTER AVENUE | VAN NUYS | LOS ANGELES | CA | 91405 | 3 | NO | 2300 | 1987-11-04 | 0 | 1 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 10 |  | 19871105 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUST.EQUIPMENT | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | L.M.STEWART-MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE TENANT OF APARTMENT #208, ONE C. HASJIM, MALE APPROXIMATELY 23 YEARS OLD, ATTEMPTED SUICIDE BY OPENING THE RANGE TOP BURNERS AND DISMANTLING THE WALL FURNACE CONTROLS ALLOWING NATURAL GAS TO ACCUMULATE AND IGNITE FROM A LIGHTED CIGARETTE. THE RESULTING EXPLOSION CAUSED DAMAGES TO THE BUILDING IN EXCESS OF $100,000 A STATEMENT GIVEN TO THE LOS ANGELES POLICE DEPARTMENT BY THE VICTIM WAS THAT HE WAS ATTEMPTING SUICIDE, THERE WERE FIVE OTHER OCCUPANTS OF THE BUILDING THATSUFFERED MINOR INJURIES. THE SERVICE SUPPLYING THE BUILDING AS WELL AS THE BUILDING'S HOUSELINES WERE TESTED AND FOUND TO BE LEAK FREE. GAS SERVICE TO THE BUILDING WAS TERMINATED DUE TO STRUCTURE DAMAGE TO THE BUILDING.
2025-01-31 10:21 | NO | NO | 19870221 |  | 4473 | ENERGAS CO | 1151 SOUTH OSAGE STREET | AMARILLO | RANDALL | TX | 79113 | 2 | NO | 700 | 1987-11-18 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19871118 | 90 | 150 | BY TEST | 225 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR PILOT | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SMALL AMOUNT OF WATER CONDENSED IN A CONTROL-PILOT REGULATOR SUBSEQUENTLY FREEZING CAUSING THE PRIMARY REGULATOR TO CLOSE OFF. THE PRESSURE ON THE SYSTEM FELL CAUSING A PARTIAL LOSS OF CUSTOMER SERVICE. OF THE 104 CUSTOMERS SERVED FOR THIS STATION A TOTAL OF 25 WERE WITHOUT GAS.
2025-01-31 10:21 | NO | NO | 19870222 |  | 4473 | ENERGAS CO | 1151 SOUTH WASHINGTON | AMARILLO | RANDALL | TX | 79113 | 3 | NO | 1500 | 1987-11-27 | 0 | 0 | 2000 | 1851.3181 | 4469.9473 | Null | 0 | 30 |  | 19871127 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | REGULATOR STATION | BODY OF PIPE |  | STEEL |  | 1 | 0.0153 | API5L-A25 |  | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | DRIVER OF AUTOMOBILE LOST CONTROL OF VEHICLE, STRUCK PRESSURE REDUCING STATION. DAMAGE TO STATION CAUSED 65 CUSTOMERS TO LOSE GAS SERVICE.
2025-01-31 10:21 | YES | YES | 19870223 |  | 7040 | HAMILTON GAS DEPT, CITY OF | 1841 GROVE AVENUE | HAMILTON | BUTLER | OH | 45015 | 3 | NO | 830 | 1987-11-25 | 0 | 1 | 20000 | 18513.181 | 44699.4728 | Null | 2 | 30 |  | 19871125 | 10 | 0 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 0 | 4 |  |  | 0 | 0 | UNDER PAVEMENT |  | RICHARD W. THOMAS,SUPERVISOR | 5138685902 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT PRESENT TIME THE INCIDENT APPEARS TO BE CAUSED BY A FRACTURE OF 4" CAST IRONPIPE AND THE ENTIRE INCIDENT IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 19870224 |  | 5090 | FAYETTE GAS BOARD, CITY OF | 603 5TH AVENUE NE | FAYETTE | FAYETTE | AL | 35555 | 3 | NO | 150 | 1987-11-28 | 0 | 0 | 50000 | 46282.9525 | 111748.6819 | Null | 0 | 50 |  | 19871128 | 29 | 32 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2.75 | 0.295 |  |  | 1953 | 1954 | WITHIN/UNDER BUILDING |  | JERRY GALLOWAY,MANAGER | 2059325270 | [6 empty] | Null |  | NO DATA | SUBSIDENCE | NO |  | NO | 0 |  | NO |  |  | NO REMARKS.
2025-01-31 10:21 | YES | YES | 19870226 |  | 11680 | LONE STAR GAS CO | 2904-2910 WEST DIVISION | ARLINGTON | TARRANT | TX |  | 3 | NO | 244 | 1987-11-03 | 1 | 0 | 0 | 0 | 0 | Null | 1 | 4 |  | 19871103 | 25 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | MTR.HIT BY TRUCK | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | WELDON R. EDENS,SUPT.II | 8173368381 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A PICKUP HIT METER LOOP,BREAKING RISER OFF ABOVE STOP AND THE GAS IGNITED BURNING PICKUP,DRIVER,TWO GAS METERS AND REGULATOR.
2025-01-31 10:21 | NO | NO | 19880003 |  | 18532 | SOUTHERN UNION GAS CO | 5613 AVE. F | AUSTIN | TRAVIS | TX | 78751 | 3 | NO | 1125 | 1987-12-18 | 0 | 0 | 0 | 0 | 0 | Null | 2 | 59 |  |  | 45 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L-B | N/A | 0 | 1984 | UNDER PAVEMENT |  | B.R.KNOX,REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19880004 |  | 18056 | ST JAMES PARISH UTILITIES | LA 18 60TENTHS OF A MILE S. LA. 70 | ST JAMES |  | LA | 70723 | 0 | NO | 400 | 1987-11-21 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 80 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REG.SET ASSEMBLY | NO DATA |  | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | NELWIN A. WEBER GEN. MANAGER | 5142654818 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | LA. STATE POLICE REPORT ATTACHED.
2025-01-31 10:21 | NO | NO | 19880007 |  | 4473 | ENERGAS CO | 108 S. PRAIRIE | HAPPY | SWISHER | TX | 79042 | 3 | NO | 1 | 1987-12-31 | 0 | 0 | 30000 | 27769.7715 | 67049.2091 | Null | 0 | 30 |  | 19871231 | 0.5 | 1 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA | CUSTOMER PREMISES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE STARTED AROUND FLOOR FURNACE, DAMAGING HOUSE AND CONTENTS.
2025-01-31 10:21 | YES | NO | 19880008 |  | 2364 | CINCINNATI GAS & ELECTRIC CO | 8727 WINTON ROAD | CINCINNATI | HAMILTON | OH | 45237 | 0 | NO | 435 | 1987-12-28 | 0 | 0 | 70000 | 64796.1336 | 156448.1547 | Null | 4 | 42 |  | 19871228 | 12 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | NO DATA |  | 12 | 0.48 | ASA-A21-7 | UNKNOWN | 0 | 1957 | UNDER PAVEMENT |  | HUBERT J. FANTETTI-DIRECTOR REGULATORY CODES | 5136322671 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CAUSE UNKNOWN AT THIS TIME. STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19880010 |  | 12350 | MINNEGASCO INC | 945 CHERRY LANE DRIVE | SEWARD | SEWARD | NE |  | 3 | NO | 520 | 1988-01-11 | 0 | 0 | 92000 | 82493.0201 | 199176.7109 | Null | 3 | 27 |  | 19880111 | 7 | 15 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | THREAD | STEEL |  | 0.75 | 0 | UNKNOWN | UNKNOWN | 0 | 1946 | UNDER GROUND OR UNDER WATER |  | CHARLES W. DOANE CLAIMS SPECIALIST | 6123425147 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | FREEZING AND HEAVING | NO |  | NO | 0 |  | NO |  |  | AT 0523, 01/11/88, THE SEWARD FIRE DEPARTMENT RECEIVED A CALL (911) THAT THERE HAD BEEN AN EXPLOSION AT 945 CHERRY LANE DRIVE. WHEN THEY ARRIVED AT THE SCENE,THEY FOUND THE HOME DEMOLISHED AND BURNING.UNDER THE DIRECTION OF CHIEF DEPUTY STATE FIRE MARSHALL, LAVERN D. RINHART, WE REMOVED A PORTION OF THE GAS SERVICE WHICH WAS THE SERVICE ENTRANCE INTO THE HOUSE. FIRE MARSHALL INSPECTION RESULTED IN FINDING A CRACKED THREAD ON THE PIPE GOING INTO THE INLET SIDE OF THE 3/4" THREADED ELL. AGAIN UNDER THE DIRECTION OFTHE STATE FIRE MARSHALL WE TESTED THE REMAINING PROTION OF THE GAS SERVICE AT 15PSI FOR 15 MINUTES. NO LEAKS WERE FOUND.
2025-01-31 10:21 | NO | NO | 19880014 |  | 4473 | ENERGAS CO | 800 E. HIGHWAY 60 | FRIONA | PARMER | TX | 79035 | 3 | NO | 1315 | 1987-12-17 | 0 | 0 | 15000 | 13884.8858 | 33524.6046 | Null | 0 | 30 |  | 19871217 | 0.5 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN EOMPLETELY DESTROYED MOBILE HOME.
2025-01-31 10:21 | NO | NO | 19880015 |  | 18532 | SOUTHERN UNION GAS CO | 45TH STREET AND SHOAL CREEK BLVD | AUSTIN | TRAVIS | TX | 78756 | 3 | NO | 1009 | 1987-12-22 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 1 |  | 19871222 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0 | N/A | N/A | 0 | 1953 | UNDER PAVEMENT |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-12-07 | YES | 3 | YELLOW PAINT | NO |  |  | SUG LOCATOR DAVID TWICHELL SPOTTED THIS MAIN ON DECEMBER 16, 1987. HE PICKED UPTWO SIGNALS. ONE, ON THE ASSIGNMENT INDICATED ONTHE ENGINEERING MAPS, AND A SECOND, WEAKER ONE, BEHIND THE P.L. HE MARKED THE SIGNAL ON THE INDICATED ASSIGNMENT, AND PLACED DOTS ON THE OTHER ACROSS THE CONTRACTOR'S PATH OF EXCAVATION. THE CONTRACTOR STRUCK AND DAMAGED THE 4" MAIN AT THE POINT WHERE THE DOTS WERE PLACED. BOTH CONDUCTIVE AND INDUCTIVE LOCATING METHODS WERE EMPLOYED AT THIS SITE. THE LOCATOR PLACED THE MARKS AFTER EXHAUSTING ALL AVAILABLE METHODS NORMALLY USED TO IDENTIFY THE CORRECT LOCATION OF THE GAS MAIN. THE CONTRACTOR MADE NO EFFORT IN EXPOSING UTILITIES WHERE MARKED PRIOR TO TRENCHING ACROSS THE RESPECTIVE UTILITIES.
2025-01-31 10:21 | YES | YES | 19880017 |  | 4473 | ENERGAS CO | 3808 FANNIN | MIDLAND | MIDLAND | TX | 79707 | 3 | NO | 700 | 1987-12-18 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19871213 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CARL BAILEY, P.E. - DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER ATTEMPTING TO LIGHT CENTRAL HEATING SYSTEM ALLOWED EXCESS ACCUMULATIONOF GAS TO OCCUR AND IGNITED IT CAUSING UNDETERMINED DAMAGE TO EYES AND SKIN.
2025-01-31 10:21 | NO | NO | 19880018 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | NEWPORT RD. E/O ANTELOPE RD. | SUN CITY | RIVERSIDE | CA | 92381 | 3 | NO | 1745 | 1987-12-03 | 0 | 0 | 50000 | 46282.9525 | 111748.6819 | Null | 0 | 35 |  | 19871203 | 250 | 266 | BY TEST | 700 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API STD. 5L | N/A | 1961 | 1962 | UNDER GROUND OR UNDER WATER |  | L.M. STEWART - MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-11-06 | YES | 2 |  | YES |  |  | THE L.S.I. ENGINEERING COMPANY, WHILE UTILIZING A D-9 CAT WITH A BACK RIPPER TOCONSTRUCT STORM DRAINS, STRUCK AND SEVERED A SIX-INCH SUPPLY LINE ALLOWING GAS PRESSURED TO 250 PSIG TO ESCAPE. SOCALGAS CREWS CONTROLLED THE ESCAPING GAS BY CLOSING THE REGULATOR STATION SUPPLYING THE LINE. THIS RESULTED IN THE LOSS OF GAS SUPPLY TO 6,500 METERS IN THE COMMUNITY TO SUN CITY. REPAIRS WERE ACCOMPLISHED BY WELDING IN TWENTY FEET OF SIX-INCH PIPE TO REPLACE THE DAMAGED SECTION. RESTORATION OF GAS TO THE EFFECTED CUSTOMERS CONTINUED THROUGH THE NIGHT AND WERE COMPLETED THE FOLLOWING DAY. THERE WERE NO INJURIES OR FATALITIES NOR WAS IT NECESSARY TO EVACUATE OR REROUTE TRAFFIC.
2025-01-31 10:21 | NO | NO | 19880019 |  | 4473 | ENERGAS CO | SECTION 7, BLOCK A-2 |  | HALE | TX | 79072 | 1 | NO | 130 | 1987-12-25 | 0 | 0 | 40000 | 37026.362 | 89398.9455 | Null | 0 | 30 |  | 19871228 | 20 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ENERGAS WAS NOT INFORMED OF THE OCCURRENCE. IT WAS LEARNED OF DURING CASUAL CONVERSATION ON MORING OF DECEMBER 28TH. ONE OF THE EMPLOYEES HAD LEARNED OF OCCURENCE OF THE FIRE.A SERVICEMAN WAS SENT TO CHECK ON IT. THE HOUSE WAS LOCATED 1 1/2 MILES SOUTH AND 1 MILE WEST OF HALE CENTER. THE SERVICEMAN FOUND THE HOUSE WAS BURNED AND STHE GAS METER WAS TURNED OFF.NONE OF STHE ADJACENT GAS LINES WERE LEAKING BUT CUSTOMER PIPING WAS IN SUCH CONDITION THAT A SHUT-IN TEST COULD NOT BE MADE.INQUIRY WITH THE HALE CENTER FIRE DEPT. INDICATED THEY WENT TOTHE FIRE BUT DID NOTHING BUT STAND-BY SINCE THE FIRE WAS ADVANCED BEYOND CONTROL. THEY STATED THECAUSE WAS UNKNOWN AND THEY DID NO FURTHER INVESTIGATION BECAUSE THE LOCATION WAS OUTSIDE THEIR JURISDICTION.HOUSE AND CONTENTS WERE DESTROYED IN THIS HOUSE OWNED BY KELLY THOMAS. WITNESSESWERE REPORTED TO BE KELLY THOMAS, HIS WIFE KIM, AND CHILD RAE. NONE OF THEM WERE INJURED.
2025-01-31 10:21 | YES | YES | 19880020 |  | 4473 | ENERGAS CO | 6406 25TH STREET | LUBBOCK | LUBBOCK | TX |  | 3 | NO | 1145 | 1988-01-10 | 0 | 1 | 65000 | 58283.112 | 140722.6762 | Null | 0 | 20 |  | 19880110 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE FIRE DEPT. NOTIFIED THE COMPANY OF THE EXPLOSION AND FIRE. A SERVICEMAN WASSENT OUT IN RESPONSE. THE FIRE DEPT. HAD ALREADY TURNED OFF THE METER WHEN HE ARRIVED.TED PEREZ WAS ONLY OCCUPANT IN THE HOUSE AT THE TIME OF THE EXPLOSION AND FIRE.HE WAS IN BED ASLEEP. HE WAS TREATED FOR MINOR INJURIES AT LUBBOCK METHODIST HOSPITAL AND THEN RELEASED.GAS MAINS ADJACENT TO THE PROPERTY WERE PROBED FOR LEAK WITH NONE FOUND. A SHUT-IN TEST WAS CONDUCTED ON CUSTOMER PIPING AND INITALLY WOULD NOT HOLD. WHEN CUSTOMER APPLIANCES WERE CHECKED, THE GAS OUTLET BEHIND THE ELECTRIC RANGE WAS FOUNDTO BE UNCAPPED WITH THE GAS VALVE IN THE ON POSITION. WHEN THE VALVE WAS TURNEDOFF, THE SHUT-IN ON CUSTOMER PIPING BECAME GAS TIGHT. MARLON HAMILTON WITH THEFIRE DEPARTMENT WITNESSED THE TEST.
2025-01-31 10:21 | YES | YES | 19880021 |  | 180 | ALABAMA GAS CORP | 620 AVENUE D-ENSLEY | BIRMINGHAM | JEFFERSON | AL | 35214 | 3 | NO | 1044 | 1988-01-15 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 |  |  | 135 | 175 | BY TEST | 263 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | FITTING |  | STEEL |  | 2 | 0.154 | 125 PSI MAX | NORMAC | 1987 | 1988 | OTHER | WITHIN EXCAVATION | G.M. WALKER-SUPERINTENDENT, MAIN & SERVICE DEPT. | 2053268309 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | AT 9:20 A.M. ON FRIDAY, JANUARY 15, 1988, AN ALABAMA GAS CORPORATION CONSTRUCTION CREW CLOSED THE VALVE ON A TWO INCH (2") HIGH PRESSURE MAIN TO MAKE REPARS TOA DAMAGED SECTION OF PIPE. FOLLOWING THE VALVE CLOSING, THE LINE WAS BLED DOWNAT A METER SETUP. THE DAMAGED SECTION OF PIPE WAS THEN CUT ON BOTH ENDS AND REMOVED.AT THIS TIME A NEW SECTION OF PIPE WAS INSTALLED AND CONNECTED TO THE EXISTING SECTION OF PIPE IWTH COMPRESSION COUPLINGS F FOLLOWING THSES CONNECTIONS, THE VALVE WAS PARTIALLY OPENED TO ALLOW GAS BACK ON THE LINE IN ORDER TO WELD STRAPS ACROSS THE COUPLINGS.THE WELDER WAS INSTALLING A RETAINER STRAP ON ONE COUPLING WHEN THE COUPLING ONTHE OTHER END OF THE REPAIR CAME LOOSE. THE GAS ESCAPED THROUGH THE TWO INCH OPENING AND IGNITED.THE VALVE WAS IMMEDIATELY RECLOSED TO STOP THE FLOW OF GAS AND, IN TURN, TO PUTOUT THE FIRE. DURING THE TIME OF THE FIRE AND THE CLOSING OF THE VALVE, THE FIVE EMPLOYEES EXPOSED WERE REMOVED FROM THE FIRE AREA TO A SAFE LOCATION.AN AMBULANCE AND PARAMEDICS WERE REQUESTED THROUGH THE RADIO DISPATCHER. ASSISTANCE SOON ARRIVED, AT WHICH TIME THE INJURED WERE REMOVED TO THE U.A.B. BURN CENTER FOR TREATMENT. REPLACEMENT PERSONNEL SECURED THE AREA AND COMPLETED THE CONSTRUCTION AS REQUIRED.
2025-01-31 10:21 | YES | NO | 19880022 |  | 630 | ARKANSAS WESTERN GAS CO | HWY.62E.,1,200 FT. NW OF HWY. 23 | EUREKA SPRINGS | CARROLL | AR | 72632 | 3 | NO | 1430 | 1988-01-15 | 0 | 0 | 150000 | 134499.4893 | 324744.6374 | Null | 4 | 15 |  | 19880115 | 27 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | UNKNOWN | UNKNOWN | 0 | 1951 | UNDER PAVEMENT |  | MICHAEL Z. HAYS, MGR.-ENGINEERING SERVICES | 5015215400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | MAIN WAS APPARENTLY DAMAGED BY OUTSIDE FORCES SOME TIME IN PAST. RESULTING DENT IN PIPE CAUSED STRESS RISER. THIS IN COMBINATION WITH COLD GROUND CONDITIONS IS SUSPECTED TO HAVE LED TO STRESS CRACK FAILURE.
2025-01-31 10:21 | YES | YES | 19880023 |  | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | E. CABARRUS STREET @ S. HAYWOOD STREET | RALEIGH | WAKE | NC | 27601 | 3 | NO | 1030 | 1987-10-21 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 4 |  | 19871021 | 60 | 90 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | REGULATOR VAULT | OTHER | NO FAILURE SEE NARRATIVE | STEEL |  | 0 | 0 |  |  | 0 | 0 | OTHER | REGULATORY VAULT | JERRY W. RICHARDSON, VICE PRESIDENT - ENGINEERING | 9194674156 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ABOUT 10:30 A.M., OCTOBER 21, 1987, THOMAS MOZINGO, LEADER WELDER; CLYDE SWANN,H.D. EQUIPMENT OPERATOR; RICHARD WILLIAMS, PIPE LAYER; AND JOHN EDWARDS, SERVICEMAN A. WERE WORKING AT THEIR TRUCK BOLTING A FLANGE ONTO A 2" VALVE THAT WAS TOBE INSTALLED IN THE ADJACENT REGULATOR VAULT. THEY ALL SUDDENLY HEARD AND SMELLED GAS ESCAPING INTO A MANHOLE FROM WHICH MOZINGO AND EDWARDS HAD EXITED A SHORTTIME EARLIER. MOZINGO ENTERED MANHOLE, WAS OVERCOME BY THE GAS AND WAS IN THE VAULT FOR APPROXIMATELY FOUR (4) MINUTES BEFORE BEING RETRIEVED. THE LACK OF OXYGEN CAUSED MOZINGO TO BLACK OUT, REQUIRING HOSPITALIZATION. RICHARD WILLIAMS WAS SEEN AT THE EMERGENCY ROOM FOR SHORTNESS OF BREATH AND WAS RELEASED. REPORT DID NOT CONTAIN A SECOND SHEET.
2025-01-31 10:21 | NO | NO | 19880025 |  | 12684 | MONTANA - DAKOTA UTILITIES CO | 316 E. PHILADELPHIA STREET | RAPID CITY | PENNINGTON | SD | 57701 | 3 | NO | 2300 | 1988-01-09 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19880111 | 25 | 25 | BY TEST | 25 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 1.54 | SCH.40 | UNKNOWN | 0 | 1947 | WITHIN/UNDER BUILDING |  | ZENE C. PALEN, GAS SUPERINTENDENT | 6053420160 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON SATURDAY, JANUARY 9, 1988, SHORTLY AFTER 11:00 P.M. KENNETH KNIGHT, SERVICEMAN-GENERAL, RECEIVED A FIRE CALL FROM OUR DISPATCH CENTER IN BISMARCK. THE EXPLOSION AND FIRE OCCURRED IN A PRIVATE DWELLING LOCATED AT 316 EAST PHILADELPHIA STREET IN RAPID CITY, SOUTH DAKOTA. THERE WERE TWO OCCUPANTS IN THE OCCUPANTS WERE IN BED SLEEPING AND WERE AWAKENED BY THE EXPLOSION. THEY FOUND THAT THE LIVING ROOM OF THEIR DWELLING WAS ENGULFED IN FLAMES, AND THEY ESCAPED THE HOUSE THROUGH THEIR BEDROOM WINDOW.IT HAS BEEN DETERMINED THAT THE EXPLOSION WAS A RESULT OF AN ACCCUMULATION OF NATURAL GAS THAT ORIGINATED AT A LEAK ON THE GAS MAIN IN THE ALLEY BEHIND THE RESIDENCE. APPARENTLY THE GAS TRAVELED UNDERGROUND UNDER THE FROST LINE FROM THE MAIN TO THE SERVICE LINE AT 316 EAST PHILADELPHIA AND UP TO THE DWELLING. THE NATURAL GAS PROBABLY ENTERED THE DWELLING FROM A CRAWL SPACE AT THE SERVICE ENTERANCE AND WAS IGNITED THE INTERIOR OF THE HOUSE. THE RAPID CITY FIRE DEPARTMENT HAD THE FIRE UNDER CONTROL IN ABOUT 30 MINUTES.WE IMMEDIATELY BAR TESTED IN THE ALLEY AND IN THE YARDS ABUTTING THE ALLEY AND FOUND A MAJOR CONCENTRATION OF NATURAL GAS. THROUGH BAR TESTING WE PINPOINTED ANAREA OVER OUR 2" MAIN IN THE ALLEY ABOUT 20' EAST OF THE SERVICE LINE TO 316 EAST PHILADELPHIA. WE DID NOT FIND A CONCENTRATION OF GAS UP AGAINST ANY OF THE BUILDINGS ON THIS BLOCK, WITH THE EXCEPTION OF 316 EAST PHILADELPHIA. WE UNCOVEREDTHE 2" MAIN AND FOUND A STRESS BREAK AROUND HALF THE CIRCUMFERENCE OF THE MAIN.THE MAIN SHOWED A DEEP DENT ON THE BOTTOM SIDE AND WAS PULLED IN THE DITCH DUE TO A HIT FROM SOME OUTSIDE FORCE. WE MADE A TEMPORARY REPAIR ON THIS MAIN EARLY SUNDAY MORNING AND COMPLETED PERMANENT REPAIR ON MONDAY MORNING, JANUARY 11TH.
2025-01-31 10:21 | YES | YES | 19880026 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 277 GENEVA | HIGHLAND PARK | WAYNE | MI | 48203 | 3 | NO | 1605 | 1987-12-25 | 1 | 0 | 0 | 0 | 0 | Null | 1 | 40 |  | 19871225 | 2 | 2 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | CAST IRON |  | 6 | 0.37 |  |  | 0 | 1915 | UNDER GROUND OR UNDER WATER |  | BRUCE NIEMAN - MGR CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE GAS SERVICE LINE SUPPLYING 277 GENEVA HAD BEEN CUT AND 1-1/2" THREADED PLUGINSTALLED IN THE MAIN ON NOVEMBER 13, 1987 BECAUSE OF GAS THEFT. SOME TIME PRIOR TO DECEMBER 25, 1987, A TUNNEL HAD BEEN DUG THROUGH THE FRONT BASEMENT WALL OFTHE BUILDING (277 GENEVA) TO THE 6" MAIN LOCATED BETWEEN THE PROPERTY LINE AND THE STREET. IT IS BELIEVED THE PURPOSE OF THE TUNNEL WAS TO REACH THE MAIN AND RECONNECT THE SERVICE LINE TO 277 GENEVA. IT IS BELIEVED THE MALE FATALITY VICTIM REMOVED THE 1-1/1" PLUG IN THE MAIN TO TO RECONNECT THE SERVICE LINE, LOST CONTROL OF THE GAS FLOW AND WAS ASPHYXIATED BY THE DISPLACEMENT OF AIR IN THE TUNNEL CAUSED BY THE UNCONFINED ESCAPING GAS.
2025-01-31 10:21 | YES | NO | 19880027 |  | 20010 | U G I CORP | 328-330 WEST LEHIGH DR | WEST EASTON | NORTHAMPTON | PA | 18042 | 3 | NO | 1345 | 1987-12-30 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 5 | 16 |  | 19871230 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0 |  |  | 0 | 1946 | UNDER PAVEMENT |  | CHARLES W BECKER - MGR ENGINEERING SERV | 2153754441 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A LOW-LEVEL EXPLOSION AND RESULTANT FIRE DESTROYED A DUPLEX DWELLING AT 328-330 WEST LEHIGH DR, WEST EASTON, PA. A BROKEN 12" CAST IRON MAIN WAS FOUND DIRECTLY IN FRONT OF THE DWELLING, APPROXIMATELY 45' FROM THE FRONT BUILDING WALL OF THE STRUCTURE. THE BREAK WAS MIDWAY BETWEEN TWO MECHANICALLY CLAMPED JOINTS OF AN18' SEGMENT OF PIPE. THE CAUSE OF THE BREAK IS UNDETERMINED AT THIS TIME.
2025-01-31 10:21 | YES | NO | 19880028 |  | 18532 | SOUTHERN UNION GAS CO | 701 6TH ST | PRESCOTT | YAVAPAI | AZ | 86301 | 3 | NO | 1345 | 1987-12-27 | 0 | 0 | 400000 | 370263.6204 | 893989.4552 | Null | 2 | 30 |  | 19871227 | 95 | 100 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 34 | 0.113 | API-5L-25 |  | 1973 | 1973 | UNDER PAVEMENT |  | JIM STEPHENS - DIST SUPT | 6024452210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-12-15 | YES | 2 | PAINT | YES
2025-01-31 10:21 | YES | NO | 19880029 |  | 3240 | DELMARVA POWER & LIGHT CO | ROCKLAND RD NEAR RT 202 | WILMINGTON | NEW CASTLE | DE | 19803 | 3 | NO | 1358 | 1988-01-19 | 0 | 0 | 150000 | 134499.4893 | 324744.6374 | Null | 0 | 20 |  | 19880120 | 30 | 45 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 |  | DUPONT CO | 1980 | 1980 | UNDER GROUND OR UNDER WATER |  | HAMILTON TAYLOR - SUPT GAS DIST | 3024293375 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-12-23 | NO | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19880030 |  | 7040 | HAMILTON GAS DEPT, CITY OF | 870 BISHOP AVE. | HAMILTON, | BUTLER | OH | 45015 | 3 | NO | 2022 | 1988-01-19 | 0 | 1 | 40000 | 35866.5305 | 86598.57 | Null | 1 | 0 |  | 19880119 | 10 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | NO DATA |  | 6 | 0 |  |  | 0 | 1960 | UNDER PAVEMENT |  | RICHARD W. THOMAS, SUPERINTENDENT | 5138685902 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT PRESENT TIME THE INCIDENT APPEARS TO BE CAUSED BY A FRACTURE OF 6" CAST IRONPIPE. THE ENTIRE INCIDENT IS STILL LUNDER INVESTIGATION. APPEARS TO BE OUTSIDENATURAL FORCE.
2025-01-31 10:21 | YES | YES | 19880031 |  | 15469 | PHILADELPHIA GAS WORKS | 936 EDGEMORE ROAD | PHILADELPHIA | PHILADELPHIA | PA | 19140 | 4 | NO | 915 | 1988-01-10 | 0 | 1 | 50000 | 44833.1631 | 108248.2125 | Null | 1 | 50 |  | 19880110 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4.8 | 0.38 | UNKNOWN | UNKNOWN | 1925 | 1925 | UNDER PAVEMENT |  | LEROY C. SCHLAGEL, MANAGER DISTRIBUTION DEPT. | 2159783372 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | DUE TO GROUND SUBSIDENCE AT A SEWER AND WATER LATERAL, THE 4" CAST IRON MAIN BROKE.
2025-01-31 10:21 | YES | NO | 19880032 |  | 15469 | PHILADELPHIA GAS WORKS | 2519 E. NORRIS STREET | PHILADELPHIA | PHILADELPHIA | PA | 19125 | 4 | NO | 1846 | 1988-01-16 | 0 | 0 | 125000 | 112082.9077 | 270620.5312 | Null | 0 | 39 |  | 19880116 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN | 1 | BODY OF PIPE |  | CAST IRON |  | 4.8 | 0.38 | UNKNOWN | UNKNOWN | 0 | 1898 | UNDER PAVEMENT |  | LEROY C. SCHLAGEL, MANAGER DISTRIBUTION DEPT. | 2159783372 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | 16'4" OF 4" CAST IRON MAIN SETTLED INTO CAVITY IN STREET. CAVITY WAS DUE TO A SEWER AND WATER FAILURE IN THE STREET.
2025-01-31 10:21 | NO | NO | 19880034 |  | 18440 | SOUTH JERSEY GAS CO | 203 STEPHEN PLACE | MAGNOLIA | CAMDEN | NJ |  | 4 | NO | 1850 | 1987-12-29 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | EDWARD J. TONIELLI, VICE PRESIDENT DIVISION OPERATIONS | 6095619000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 12-29-87 AT 6:50 P.M., THE COMPANY RECEIVED A CALL OF AN EXPLOSION AND FIRE AT 203 STEPHEN PL. MAGNOLIA. A COMPANY REPRESENTATIVE WAS DISPATCHED TO THE LOCATION AT 6:51 P.M. AND ARRIVED AT 7:10 P.M. IN WORKING WITH THE LOCAL FIRE DEPARTMENT, THE GAS WAS SHUT OFFAT THE METER AND CURB STOP. THERE WAS EXTENSIVE DAMAGE TO A RESIDENTIAL HOUSE, NO ONE WAS INJURED. THE SERVICE WAS TESTED AND NO LEAKS WERE FOUND, THE METER AND REGULATOR WERE TURNED BACK ON AND FOUND TO BE PASSING APPROXIMATELY ONE P.S.I. PRESSURE.
2025-01-31 10:21 | NO | NO | 19880035 |  | 4473 | ENERGAS CO | SECTION 43, BLOCK 4X | BROWNFIELD | TERRY | TX | 79316 | 0 | NO | 1430 | 1988-01-07 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19880107 | 6 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | OTHER PLASTIC | ABS | 2 | 0.18 | UNKNOWN |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | NICK V. FARISS, DIRECTOR ENGINEERING & MEASUREMENT | 8063789966 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA |  | INDICATION OF THE LEAK WAS FOUND UNDER THE HOUSE. RESIDENTS WERE EVACUATED ANDKEPT IN A MOTEL UNTIL THE GROUND COULD BE AERATED TO MAKE CONDITIONS SAFE. THE LEAK WAS REPAIRED AND THE PEOPLE WERE PERMITTED TO RETURN TO THE RESIDENCE THE NEXT DAY.MATERIAL DEFECT:COUPLING ON PIPE CRACKED WITH ENSUING GAS LEAKAGE. REPAIRED BY REPLACING 20 FOOT PORTION WITH 2" PVC PIPE.
2025-01-31 10:21 | NO | NO | 19880036 |  | 18532 | SOUTHERN UNION GAS CO | 9425 NORTH LAMAR BLVD. | AUSTIN | TRAVIS | TX | 78753 | 3 | NO | 952 | 1987-12-15 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 34 |  | 19871215 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 1.25 | 0.4 | API-5L-A25 | N/A | 0 | 1978 | UNDER GROUND OR UNDER WATER |  | B.R.KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-11-10 | YES | 3 | RISER AT PROPERTY LINE | NO |  |  | CONTRACTOR WAS DITCHING FOR A PORTION OF AN ON-GOING CAPITAL IMPROVEMENT PROJECT WHEN THEY STRUCK AND DAMAGED THIS GAS SERVICE LINE. THE CONTRACTOR HAD REQUESTED THAT ALL LINES IN THE AREA BE LOCATED AND MARKED. THE S.U.G. LOCATOR FAILEDTO MARK THIS PARTICULAR SERVICE LINE. PRIOR TO THE DAMAGE OCCURRING, SUG CIP CREWS HAD GONE THRU THE AREA LOWERING LINES THAT WERE DETERMINED TO BE IN THE CONTRACTOR'S WAY. THIS LINE WAS NOT LOWERED.
2025-01-31 10:21 | YES | YES | 19880037 |  | 15259 | PENNSYLVANIA GAS & WATER CO | 1141 WYOMING AVENUE | FORTY FORT | LUZERNE | PA | 18704 | 3 | NO | 542 | 1988-01-23 | 0 | 1 | 40000 | 35866.5305 | 86598.57 | Null | 1 | 24 |  | 19880125 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | METER | OTHER | ALUMINUM METER CASE | 0 | 0 | AL-250 | ROCKWELL#2848856 | 1972 | 1979 | ABOVE GROUND |  | J.M. GREGER, MGR. - LEAK DET. & CORROSION | 7178298866 | [6 empty] | Null |  | LIGHTNING OR FIRE | SUSPECTED ARSONIST | NO |  | NO | 0 |  | NO |  |  | FIRE OCCURRED AT CUSTOMER PREMISES IN REAR OF BASEMENT, SUSPECTED CAUSE BY ARSONIST. FIRE ENGULFED ENTIRE HOUSE CAUSING AN INCIDENT AT THE INSIDE GAS METER SET RESULTING IN AN IGNITION. TWO FIREFIGHTERS WERE INJURED RESULTING FROM THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 19880038 |  | 10037 | KANSAS POWER & LIGHT CO | 2513 CHIPMAN ROAD | LEE'S SUMMIT | JACKSON | MO | 64063 | 3 | NO | 1630 | 1987-10-07 | 0 | 0 | 80000 | 74052.7241 | 178797.891 | Null | 2 | 10 |  | 19871007 | 5 | 15 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0 |  |  | 0 | 1961 | WITHIN/UNDER BUILDING |  | V.E.PERCELL, SR. VICE PRESIDENT | 9132961911 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | NATURAL GAS LEAKING BELOW GROUND FROM A 1" STEEL SERVICELINE MIGRATED INTO A DUPLEX AND IGNITED, POSSIBLY FROM A PILOT ON A STOVE, CAUSING A FIRE.ALTHOUGH GAS SUPPLY WAS NOT SHUT OFF FOR TWO HOURS AND TEN MINUTES THE FIRE DEPARTMENT HAD THE BLAZE UNDER CONTROL SHORTLY AFTER THEIR ARRIVAL.
2025-01-31 10:21 | YES | NO | 19880039 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 116 WEST MILE | KALKASKA | KALKASKA | MI | 49684 | 3 | NO | 700 | 1987-11-12 | 0 | 0 | 1000000 | 925659.051 | 2234973.638 | Null | 2 | 35 |  | 19871112 | 54 | 60 | BY CFR 192.619(A)(3) | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | NO DATA |  | CAST IRON |  | 0.875 | 0.08 | M-7000 | PHILLIPS | 0 | 1974 | WITHIN/UNDER BUILDING |  | BRUCE NIEMAN, MANAGER CODES & STANDARDS | 3134566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | ON NOVEMBER 10, 1987, IN RESPONSE TO A LEAK CALL, ONE LEG OF A BURRIED COMPRESSION TEE WAS DISCOVERED TO HAVE PULLED OUT. THE PULL OUT WAS REPAIRED. THE CREWFAILED TO REPROSPECT THE AREA AFTER MAKING THE REPAIR AND THEREFORE, FAILED TO DETECT A HOLE MADE IN THE SERVICE LINE WHILE PROSPECTING THE ORIGINAL LEAK COMPLAINT.ON NOVEMBER 11, 1987 AT 7:00 A.M., AN EXPLOSION OCCURRED. PROBABLE CAUSE OF THE EXPLOSION WAS ACCUMULATION OF NATURAL GAS IN THE CINDER BLOCK WALL AND BETWEENTHE HANGING CEILING AND ROOF.
2025-01-31 10:21 | YES | NO | 19880040 |  | 15007 | PACIFIC GAS & ELECTRIC CO | VALVE 00.40,6"FEEDER MAIN,1/2MI.OF OR. | ORLAND | BUTTE COUNTY | CA | 95963 | 3 | NO | 430 | 1987-11-01 | 0 | 0 | 171600 | 158843.0931 | 383521.4763 | YES | 6 | 12 |  | 19871101 | 40 | 48 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | VALVE |  | STEEL |  | 0 | 0 | 4449.5 | NORDSTROM | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | J.B. STOUTAMORE, VICE PRESIDENT-GAS OPERATIONS | 4159373204 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | UNKNOWN PARTY GAINED FORCIBLE ENTRY TO VALVE PIT. 6" VALVE ON SINGLE FEED MAIN WAS CLOSED, TERMINATING GAS FLOW TO 2,325 CUSTOMERS.
2025-01-31 10:21 | YES | YES | 19880041 |  | 18112 | SAN DIEGO GAS & ELECTRIC CO | 1925 JADERO PLACE | ESCONDIDO. | SAN DIEGO | CA | 92025 | 3 | NO | 1100 | 1987-11-19 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 25 |  | 19871119 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE 2306 | DUPONT | 0 | 1977 | OTHER | UNKNOWN | A.F.HOOPER, LEAKAGE MITIGATION SUPERVISOR | 6196962474 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PIPE WALL FAILURE OCCURRED WHEN EXPOSED TO "ROSEBUD" TORCH. ESCAPING GAS IGNITE
2025-01-31 10:21 | NO | NO | 19880042 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 719 OCEANVIEW BOULEVARD | PACIFIC GROVE | MONTEREY | CA | 93950 | 3 | NO | 940 | 1987-11-25 | 0 | 0 | 50110 | 46384.775 | 111994.529 | Null | 0 | 12 |  | 19871125 | 25 | 29 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0.75 | 0.113 | 5LGRA25 | UNKNOWN | 0 | 1976 | ABOVE GROUND |  | J.B.STOUTAMORE-V.P.,GAS OPERATIONS | 4159733204 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | STRUCTURE FIRE OF UNKNOWN ORIGIN DESTROYED TWO METERS AND REGULATOR, ALLOWING GAS TO ESCAPE AND IGNITE.
2025-01-31 10:21 | YES | YES | 19880044 |  | 4473 | ENERGAS CO | 4515 AMARILLO BLVD. EAST | AMARILLO | POTTER | TX | 79107 | 3 | NO | 2330 | 1987-11-03 | 0 | 2 | 75000 | 69424.4288 | 167623.0228 | Null | 1 | 0 |  | 19871104 | 0.5 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER LINE | NO DATA |  | NO DATA |  | 0 | 0 | N/A |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE WAS DELIBERATELY SET AT THE BUILDING, RESULTING IN COMPLETE DESTRUCTION OF THE PREMISES.
2025-01-31 10:21 | NO | NO | 19880045 |  | 4473 | ENERGAS CO | 2ND STREET AT ALEXANDER | TURKEY | HALL | TX |  | 3 | NO | 0 | 1987-11-03 | 0 | 0 | 15000 | 13884.8858 | 33524.6046 | Null | 0 | 0 |  | 19871104 | 0.5 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WE RECEIVED NOTIFICATION AT 11:15 A.M. ON NOVEMBER 4TH THAT A HOUSE BURNED DOWNIN TURKEY. IT HAD BURNED DURING THE PREVIOUS NIGHT.WAYNE ELLISTON, ENERGAS MANAGER AT TULIA, INVESTIGATED. THE FIRE WAS AT A HOUSE ON 2ND STREET ALEXANDER. THE VOLUNTEER FIRE DEPARTMENT HAD TURNED OFF THE METER WHEN THE FIRE WAS EXTINGUISHED.THE GAS SERVICE WAS INTHE NAME OF STACY PRICE SINCE OCTOBER 19, 1987. GAS WAS ALREADY ON AT THAT TIME AND THE METER WAS READ ONLY FOR A CUSTOMER NAME CHANGE. AUGUST HAD A CONSUMPTION OF 1 MCF, SEPTEMBER AND OCTOBER, O MCF, AND 1 MCF SINCELAST METER READING.WAYNE ELLISTON PERFORMED A SHUT-IN TEST OF THE METER AND CUSTOMER LINE AND THE 20 MINUTE TEST SHOWED NO LEAKAGE. SURVEY OF ADJACENT GAS MAINS WITH A FLAME-IONZATION UNIT INDICATED NO LEAKS.WAYNE SAID THE FIRE APPEARED TO START IN THE LIVING ROOM AREA. ALTHOUGH THERE IS A PANEL-RAY HEATER PRESENT, HE THOUGHT THE FIRE WAS CAUSED BY ELECTRICAL FAULT
2025-01-31 10:21 | YES | NO | 19880046 |  | 20100 | UNION GAS SYSTEM INC | 113 N. 6TH | INDEPENDENCE | MONTGOMERY | KS | 67301 | 3 | NO | 1155 | 1987-09-20 | 0 | 0 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 25 |  | 19870920 | 20 | 28 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDETERMINED | OTHER | UNDETERMINED | OTHER | UNDETERMINED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MIKE WOOLK, RISK MANAGER | 3163314500 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EXPLOSION AT 113 N. 6TH, INDEPENDENCE, KANSAS DESTROYED A TWO STORY BRICK BUILDING AND SUBSTANTIALLY DAMAGED THREE ADJACENT STRUCTURES. THE CAUSE OF THE EXPLOSION IS UNDETERMINED AT THIS TIME PENDING FURTHER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19880047 |  | 10037 | KANSAS POWER & LIGHT CO | 317 WEST 7TH STREET | JUNCTION CITY | GEARY | KS | 66441 | 2 | NO | 2030 | 1987-12-29 | 0 | 1 | 45000 | 41654.6573 | 100573.8137 | Null | 0 | 15 |  | 19871229 | 32 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 1.25 | 0.14 | APISL SPEC | UNKNOWN | 0 | 1965 | ABOVE GROUND |  | V.E. PERCELL, SR. VICE PRESIDENT, GAS OPERATIONS | 9132961911 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | METER SETTING | NO |  |  | SERVICE REGULATOR WAS STRUCK BY HIT & RUN DRIVER, ALLOWING MAIN PRESSURE TO ENTER THE STRUCTURE, CAUSING EXPLOSION.
2025-01-31 10:21 | NO | NO | 19880048 |  | 10037 | KANSAS POWER & LIGHT CO | 7503 W. 101ST TERRACE | OVERLAND PARK | JOHNSON | KS | 66214 | 3 | NO | 1500 | 1987-12-19 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19871219 | 15 | 58 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0 |  |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | V.E.PERCELL, SR. VICE PRESIDENT, GAS OPERATIONS | 0000000000 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | COROSION LEAK AT SCREW COLLAR ON BARE STEEL YARD LINE ALLOWED GAS TO ENTER SEWERDRAIN TO HOUSE. YARD LINE WAS INSTALLED IN 1966, BY CUSTOMER. GAS WAS APPARENTLY IGNITED BY ELECTRIC FAN. CUSTOMER EXTINGUISHED FLAME BY COVERING DRAIN WITH BLANKET. SERVICE LINE WAS REPAIRED BY INSERTION OF 7/8' DRISCOPIPE. AFTER INSERTION, CGI CHECKS OF DRAINS, SERVICE LINE, MAIN, MANHOLES, TWO HOUSES ON EACH SIDE OF THIS ADDRESS, AND FOUR HOUSES ACROSS THE STREET, SHOWED NO GAS.
2025-01-31 10:21 | NO | NO | 19880049 |  | 10037 | KANSAS POWER & LIGHT CO | 12904 WOODSON | OVERLAND PARK | JOHNSON | KS | 66209 | 3 | NO | 1444 | 1987-12-18 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19871218 | 15 | 58 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2.375 | 0.216 | SDR-11 | PHILLIPS DRISCO | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | V.E.PERCELL, SR. VICE PRESIDENT, GAS OPERATIONS | 9132961911 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | YES | 3 | FLAG OVER MAIN(WOODSON) | NO |  |  | A PLUMBING CONTRACTOR (NEW COUNTRY PLUMBING), DIGGING WITH A BACKHOE IN ORDER TO INSTALL A WATER SERVICE TO A NEW HOUSE, STRUCK AND PUNCTURED OUR 2" PLASTIC MAIN. AS THE CONTRACTOR WAS DIGGING OUT THE AREA TO PREPARE FOR REPAIRS, THE BACKHOE BUCKET STRUCK A ROCK, CAUSING A SPARK IGNITING THE LEAKING NATURAL GAS.OUR CREW ARRIVED ON THE SCENE AND EXTINGUISHED THE FIRE WITHTWO DRY CHEMICAL EXTINGUISHERS. THE FIRE DEPARTMENT COOLED THE AREA WITH WATER AND REPAIRS WERE MADE WITHOUT FURTHER INCIDENT.GAS MAIN LOCATES HAD BEEN REQUESTED BY CENTURY PLUMBING ON OCTOBER 12, 1987, FOR12908 WOODSON, AND LOCATES WERE PROVIDED ON OCTOBER 14, 1987. WE DID NOT RECEIVED LOCATED REQUESTS FROM CENTURY PLUMBING FOR 12904 WOODSON.
2025-01-31 10:21 | YES | YES | 19880050 |  | 10037 | K P L GAS SERVICE | 8900 E. CENTRAL & WEST BROADWAY | WICHITA | SEDGWICK | KS | 67219 | 3 | NO | 318 | 1987-12-04 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 2 |  | 19871204 | 20 | 60 | BY TEST | 96 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | DIST REGULATOR SET | VALVE |  | OTHER | BRASS | 0.25 | 0 | 1500 PSIG | IMPERIAL EASTMAN | 1987 | 1987 | ABOVE GROUND |  | V.E.PERCELL, SR. VICE PRES, GAS OPERATIONS | 9132961911 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DISPATCHER RECEIVED A CALL FROM THE FIRE DEPARTMENT AT 0318 HOURS THAT A DISTRICT REGULATOR STATION HAD BEEN HIT AND WAS BLOWING. DUTY SUPERVISOR WIDICK WAS CALLED AT 0321 HOURS. THE DISPATCHER WAS INSTRUCTED TO CALL THE PRESSURE SUPT. QUIGGLE AT THAT TIME. MR. QUIGGLE HAD THE DISPATCHER CONTACT THE PRESSURE SUPERVISOR KEN HARTMAN AND A PRESSURE MAN ALSO WAS CONTACTED.WHEN I ARRIVED AT THE ACCIDENT AT 0355 HOURS THE PRESSURE SUPERVISOR WAS THERE.WE FOUND THE 2-1/4" TEST NIPPLES ON THE OPERATOR REGULATOR RISERS WERE BROKEN OFF AND BLOWING. THE BARRICADE OF 4" PIPE HAD BEEN HIT BY AN OLDSMOBILE CUTLASS DRIVEN BY JANET TURNER, BREAKING UP AND PUSHING THE BARRICADE INTO THE OPERATOR REGULATOR SETTING, PUSHING IT OVER AT THE TOP APPROXIMATELY 20 DEGREES. THE REGULATOR WAS PERFORMING AS IT SHOULD. THE SERVICEMAN SECURED THE LEAKS.AFTER THE VEHICLE HIT THE OPERATOR REGULATOR STATION, IT THEN HIT THE BARRICADEOF 4" PIPE AROUND THE MONITOR REGULATOR MOVING ITBUT NOT DAMAGING IT BEFORE THEVEHICLE CAME TO A STOP.THE POLICE DEPARTMENT ADVISED AT THAT TIME THEY BELIEVED THE DRIVER HAD A BROKEN LEG AND WOULD POSSIBLY BE BOOKED FOR DUI.
2025-01-31 10:21 | NO | NO | 19880051 |  | 10037 | KANSAS POWER & LIGHT CO | SOUTH KANSAS & TOWNSHIP ROAD | CARBONDALE | OSAGE | KS | 66414 | 3 | NO | 208 | 1986-06-02 | 0 | 0 | 15000 | 14194.2149 | 34271.4696 | YES | 0 | 0 |  | 19860602 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | DISTRICT REGULATOR STAT. | REGULATOR/METER |  | STEEL |  | 0.2 | 0.154 | API 5L A25 | UNKNOWN | 1968 | 1968 | NO DATA |  |  | 0000000000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | A VEHICLE FAILED TO STOP AND / OR NEGOTIATE A TURN AT A T INTERSECTION, RESULTING IN DESTRUCTION OF A DISTRICT REGULATOR AND SUBSEQUENT FIRE TOTHE STATION AND VEHICLE.
2025-01-31 10:21 | YES | YES | 19880052 |  | 10037 | K P L GAS SERVICE | 10226 MAY CT. | WICHITA | SEDGWICK | KS | 67213 | 3 | NO | 1020 | 1986-04-30 | 0 | 1 | 20350 | 19256.8182 | 46494.9605 | Null | 1 | 0 |  |  | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDRLL | PHILLIPS MFG. CO. | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  |  | 0000000000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | NO |  |  | WHILE EXCAVATING FOR INSTALLATION OF WATER LINE, CHAIN TYPE TRENCHER STRUCK 2" PLASTIC GAS MAIN. GAS MAIN WAS CUT AND ESCAPING GAS IGNITED. TRENCHER OPERATORWAS BURNED AND WAS TRANSPORTED AND ADMITTED TO HOSPITAL. DIGGER CHAIN AND ENGINE OF TRENCHER WERE BURNED.
2025-01-31 10:21 | YES | NO | 19880054 |  | 20100 | UNION GAS SYSTEM INC | 9600 121ST. TERR. | OVERLAND PARK. | JOHNSON | KS | 66213 | 3 | NO | 7 | 1987-12-19 | 0 | 0 | 300000 | 277697.7153 | 670492.0914 | Null | 2 | 25 |  | 19871219 | 55 | 57 | BY TEST | 85 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | TR 418 | PHILLIPS | 1986 | 1987 | WITHIN/UNDER BUILDING |  | MIKE WOOKF RISK MANAGER | 3163314500 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | THE PRELIMINARY INVESTIGATION INDICATES THE CAUSE OF THIS INCIDENT WAS SEPARATION OF THE SERVICE LINE FROM THE TAPPING TEE FITTING ATTACHED TO THE MAIN. THE FUSION FO THE SERVICE LINE TO THE TAPPING TEE DID NOT APPEAR TO MEET ESTABLISHED STANDARDS IN THAT A "COLD FUSIO": WAS APPARENTLY MADE DURING INSTALLATION OF THESERVICE LINE. THE "COLD FUSION" DID NOT,.OF ITSELF, CAUSE SEPARATION OF THE FITTING WHICH IS BELIEVED TO HAVE BEEN CAUSED BY AN AS YET UNDETERMINED EXTERNAL FORCE.
2025-01-31 10:21 | NO | NO | 19880055 |  | 20100 | UNION GAS SYSTEM INC | 57TH & STATE AVE. | KANSAS CITY | WYANDOTTE | KS | 66111 | 3 | NO | 2330 | 1987-10-03 | 0 | 0 | 6000 | 5553.9543 | 13409.8418 | YES | 0 | 0 |  | 19871004 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 0 | 0 | METER REGULATOR | ROCKWELL 3000 FISHER S-202 | 0 | 1977 | ABOVE GROUND |  | DALE L. ELTON / OPERATIONS MANAGER | 9137640530 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | BETWEEN 11 & 11:30 P.M. 10-3-87 A CAR HIT METER SETTING AT FASONE'S RESTAURANT AT 57TH & STATE AVE., KCK (RESULTING IN FIRE). DRIVER SAID HE WAS LEAVING LOT BUT METER SITS - 20 FEET FROM PARKING LOT ENTRANCE. THE FIRE WAS LEFT TO BURN UNTIL GAS SHUT OFF AT 1:45 AM (+) 10-4-87. DAMAGE TO CAR WAS TOTAL. REGULATOR WAS BROKEN OFF, 1: STOP WAS BENT IN NIPPLE, METER WAS CRACKED. ALL ITEMS WERE TOTAL LOSS. METER SETTING WAS BARRICADED.METER SETTING WAS MOVED UP TO BUILDING TO A LOCATION THAT IS AWAY FROM ALL VEHICLAR TRAFFIC.
2025-01-31 10:21 | NO | NO | 19880056 |  | 20100 | UNION GAS SYSTEM INC | INTER. DENNIS & KANSAS AVENUES | OLATHE | JOHNSON | KS | 66061 | 3 | NO | 210 | 1986-12-15 | 0 | 0 | 3000 | 2838.843 | 6854.2939 | YES | 0 | 50 |  |  | 55 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | NO DATA |  | STEEL |  | 6 | 0.188 | UNKNOWN | UNKNOWN | 0 | 1946 | UNDER PAVEMENT |  | MIKE WOOLF, RISK MANAGER | 3163314500 | EXTERNALLY | OTHER | 1/4" HOLE | GALVANIC |  | BARE | YES | 1980 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19880057 |  | 20100 | UNION GAS SYSTEM INC | HWY 169 & 183RD STREET | NORTH SPRING HILL | JOHNSON | KS | 66083 | 2 | NO | 1000 | 1986-08-20 | 0 | 0 | 6000 | 5677.686 | 13708.5879 | YES | 0 | 50 |  | 19860820 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.576 | PE2306-TR148 | DISCOPIPE | 1984 | 1985 | UNDER GROUND OR UNDER WATER |  | MIKE WOOLF - RISK MANAGER | 3163314500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO
2025-01-31 10:21 | NO | NO | 19880058 |  | 20100 | UNION GAS SYSTEM INC | 4 MILES SE CEDAR VALE, KS | CEDAR VALE | CHAUTAUQUA | KS | 67024 | 1 | NO | 800 | 1986-06-20 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19860620 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | APISLB | UNKNOWN | 0 | 1946 | ABOVE GROUND |  | MIKE WOOLF, RISK MANAGER | 3163314500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO
2025-01-31 10:21 | YES | NO | 19880061 |  | 630 | ARKANSAS WESTERN GAS CO | 906 & 908 WESTERN AVE. | GREEN FOREST | CARROLL | AR |  | 0 | NO | 1910 | 1987-12-16 | 0 | 0 | 64000 | 59242.1793 | 143038.3128 | Null | 0 | 15 |  | 19871217 | 29 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR AT METER LOOP | REGULATOR/METER |  | NO DATA |  | 0 | 0 | MODEL 8210 | REYNOLDS | 0 | 0 | ABOVE GROUND |  | JOHN R. KEHN, JR., VICE PRESIDENT - OPERATIONS | 5015215400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MOISTURE IN REGULATOR VENT FROZE ALLOWING HIGHER THAN NORMAL PRESSURE INTO BOTHHOMES.
2025-01-31 10:21 | NO | NO | 19880064 |  | 4473 | ENERGAS CO | 940 N. NELSON | PAMPA | GRAY | TX | 79065 | 3 | NO | 1455 | 1988-01-29 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19880129 | 25 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | THREAD | STEEL |  | 0.01 | 1.33 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAVID V. HAYES, JR. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | MATERIAL | ORIGINAL CONSTRUCTION OF THE PIPE WAS WITH THREADED PIPE ENDS AND COLLAR. THE TREADED PIPE END FAILED RESULTING IN A LEAK. THIRTY CUSTOMERS "DOWNSTREAM" OF THE LEAK WERE LOST.
2025-01-31 10:21 | NO | NO | 19880065 |  | 4499 | ENTEX INC | 410 JOHNSON | LAMARQUE | GALVESTON | TX | 77568 | 3 | NO | 945 | 1988-01-15 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19880115 | 25 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | STEEL |  | 2 | 0.154 | API-5L |  | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | B. F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CITY OF LAMARQUE WATER CREW, DIGGING WITH A BACKHOE TO REPAIR A WATER MAIN, CUTA 2" GAS SERVICE LINE AT THE TAP VALVE. GAS WAS IGNITED WHEN THE BACKHOW WAS SCRAPING DIRT AROUND THE BELL HOLE.
2025-01-31 10:21 | NO | NO | 19880066 |  | 4499 | ENTEX INC | 902 EAST AVENUE | KATY | FORT BEND | TX | 77450 | 3 | NO | 1115 | 1988-01-09 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 7 |  | 19880109 | 27 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.133 | API-51 |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | BILLY F. BROYLES, DIRECTOR OF OPERATIONS. | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | HOUSTON LIGHTING AND POWER COMPANY INSTALLED A COPPER GROUND ROD, FOR THEIR FACILITIES, IN CLOSE PROXIMITY WITH OUR SERVICE LINE. THIS RESULTED IN AN AC ARC-OVER BETWEEN THE SERVICE LINE AND THE COPPER GROUND ROD, CAUSING A TRANSFER OF METAL FROM OUR SERVICE LINE TO THE ROD, RESULTING IN A LEAK ON THE SERVICE. IT ISNOT KNOWN WHEN THE GROUND ROD WAS INSTALLED. THE SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | NO | NO | 19880070 |  | 18532 | SOUTHERN UNION GAS CO | SLAUGHTER LAND AND FM 1826 | AUSTIN | TRAVIS | TX | 78749 | 3 | NO | 1100 | 1988-01-28 | 0 | 0 | 5500 | 4931.6479 | 11907.3034 | Null | 2 | 45 |  | 19880128 | 58 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L-B | N/A | 0 | 1986 | NO DATA |  | B. R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR WAS USING AUGER TO DRILL HOLE TO SET NEW UTILITY POLE FOR NEW SUBDIVDSION. CONTRACTOR HAD NOT REQUESTED ANY UTILITY LOCATIONS. AT 11 A.M., CONTRACTOR PUNCTURED 6" WRAPPED STEEL MAIN APPROXIMATELY 1' FROM D.E. OF MAIN LINE. SECTON WAS ISOLATED WITH EXISTING SYSTEM VALVES AND DAMAGE SECTON WAS REMOVED AND MAIN WAS CAPPED AT THAT POINT. F GAS TURNED OFF AT 2:45 P.M.
2025-01-31 10:21 | YES | YES | 19880071 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 612 ADAMS W. | IRON RIVER | IRON | MI | 49935 | 3 | NO | 756 | 1988-01-13 | 0 | 5 | 0 | 0 | 0 | Null | 0 | 47 |  | 19880113 | 57 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | OTHER | BRASS | 0.625 | 0 | ANSI B16.15 | DRESSER | 0 | 1971 | UNDER PAVEMENT |  | BRUCE NIEMAN, MGR CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS LEAKING FROM 1/2" COPPEER SERVICE LINE, WHICH PULLED OUT OF A DRESSER STYLE88 COUPLING, MIGRATED INTO A SCHOOL BUILDING AND WAS IGNITED BY AN UNKNOWN SOURC
2025-01-31 10:21 | YES | NO | 19880072 |  | 12420 | MICHIGAN GAS UTILITIES CO | 132 FRANK ST. & 134 FRANK ST. | COLON | ST JOSEPH | MI | 49040 | 2 | NO | 400 | 1988-01-18 | 0 | 0 | 135000 | 121049.5403 | 292270.1736 | Null | 2 | 45 |  | 19880118 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | CAST IRON |  | 2 | 0 | 305 | NORDSTROM | 0 | 1960 | UNDER PAVEMENT |  | CHARLES F. HAUSKA, MANAGER OF ENGINEERING | 3132424400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 4:00 A.M. AN EXPLOSION AND FIRE OCCURRED AT 134 FRANK STREET, COLON. ROBERTAND DAWN WEINBERG EVACUATED THEIR HOME WITHOUT APPARENT INJURY.AT 4:27 A.M., MICHIGAN GAS UTILITIES' NIGHT ANSWERING SERVICE WAS NOTIFIED BY THE FIRE DEPARTMENT OF THE EXPLOSION. THE ORDER WAS DISPATCHED AT 4:28 A.M. JOHNLUCK, A CUSTOMER SERVICE TECHNICIAN AND A 20-YEAR VETERAN OF MICHIGAN GAS UTILITIES FROM STURGIS, MICHIGAN, ARRIVED AT THE SCENE AT 4:43 A.M. HE EVACUATED TWO HOMES ON BOWMAN STREET AND 126 FRANK STREET AND CHEACKED THE CHURCH AT 136 FRANK STREET. THE HOUSE AT 132 FRANK STREET HAD PREVIOUSLY BEEN EVACUATED BY ROBERT MILLER AND HIS WIFE.GAS ODOR WAS VERY PREVALENT IN THE AREA. AT APPROXIMATELY 6:00 A.M., MR. MILLER REENTERED HIS HOME AT 132 FRANK STREET, WITHOUT PERMISSION FRM MICHIGAN GAS UTILITIES OR THE LOCAL FIRE OFFICIALS. SOME TYPE OF IGNITION CAUSED AN ADDITIONALFIRE AND EXPLOSION. THE FIRE BURNED MR. MILLER'S HANDS AND SINGED THE HAIR ON HIS FACE.THE STREET CREW FROM MICHIGAN GAS UTILITIES ARRIVED AT 6:10 AM. THE GROUND IN THE AREA WAS FROZEN.THE MICHIGAN PUBLIC SERVICE COMMISSION WAS NOTIFIED AT 6:45 AM. OF THE EXPLOSION. A BYPASS WAS BUILT AROUND VALUVE, WHICH WAS ENCASED IN ICE, AND GAS WAS VACATED FROM THE AFFECTED VALVE AT 1:45. MR. MILLER WAS TREATED AT COLON CLINIC AND RELEASED TO HIS SON'S HOME. THE FIREES WERE PUT OUT AT 8:00 AM. THE ESTIMATED DAMAGE TO THE TWO DWELLINGS IS A TOTAL OF $125,000. LATER INVESTIGATION SHOWED THATAT APPROXIMATELY 12:00 MIDNIGHT JANUARY 18, 1988, THE PRESSURE AT A RECORDER ONTHE END OF THE COLON DISTRIBUTION SYSTEM SHOWER AN EIGHT POINT PRESSURE DROP, WHICH IS APPROXIMATELY THE TIME THE COMPANY BELIEVES THE TWO INCH SEMISTEEL NORDSTROM 305 VALVE BROKE IN FRONT OF 132 FRANK ST. WILLIAM F. ECKLES, SENIOR VICE PRESIDENT - ENGINEERING AND OPERATIONS, NOTIFIED MR. MATHESON OF THE NATIONAL DISASTER CENTER AT APPROXIMATELY 2:30 PM. THE AREA HAD PREVIOUSLY BEEN FLAME PACKED IN JULY, 1987, WITH NO LEAKS FOUND.
2025-01-31 10:21 | NO | NO | 19880073 |  | 4473 | ENERGAS CO | 1 MI. E. OF KRESS, SECTION 51 BL. M13 |  | SWISHER | TX |  | 0 | NO | 130 | 1988-02-06 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 30 |  | 19880206 | 0.5 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414228 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OUR DISPATCHER WAS NOTIFIED AT APPROXIMATELY 1:30 A.M. ON FEBRUARY 6, 1988 THATTHERE WAS AHOUSE ONFIRE ABOUT 1 1/2 MILES EAST OF KRESS. THE DISPATCHER SENT ONE OF OUR SERVIEMEN FROM TULIA TO THAT LOCATION.THE SERVCIE MAN FOUND THE HOUSE BURNED TOTHE GROUND WHEN HE ARRIVED THERE AT APPROXIMATELY 2:00 AM. HE LOCKED AND BLINDED THE METER AT THAT TIME.ON MONDAY, FEBRUARY 8TH, THE CREW CONDUCTED A LEAK SURVEY TEST USING A FLAME IONIZATION UNIT. THEY CHECKED ALL CUSTOMER PIPING AND NO LEAKS WERE FOUND.THIS HOUSE BELONGED TO MR. L. G. MAHAGAN AND WAS OCCUPIED BY A FAMILY WHO WORKED FOR HIM ON HIS FARM. THIS HOUSE IS SERVED FROM A SUCTOMER OWNED GROUP LINE CALLED THE DEAN LINE. THE PRESSURE ON THE GROUP LINE IS MAINTAINED AT 5 PSIG.NO ONE WAS HOME AT THE TIME OF THE INCIDENT AND THE FIRE DEPARTMENT OF KRESS HAVE INDICATED THE CAUSED OF FIRE IS INKNOWN.THIS CONCLUDED OUR INVESTIGATION OF THIS INCIDENT.
2025-01-31 10:21 | NO | NO | 19880074 |  | 4473 | ENERGAS CO | 3437 IRVING | AMARILLO | RANDALL | TX | 79121 | 3 | NO | 2300 | 1988-02-05 | 0 | 0 | 10000 | 8966.6326 | 21649.6425 | Null | 0 | 30 |  | 19880205 | 12 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 1.33 | API-5L | N/A | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABV. GR. METER SET. | YES |  |  | DRIVER OF AUTOMOBILE HIT METER SETTING. THE RESULTING FIRE DESTROYED AUTOMOBILE.
2025-01-31 10:21 | YES | YES | 19880075 |  | 4473 | ENERGAS CO | 107 COOPER | HEREFORD | DEAF SMITH | TX | 79045 | 3 | NO | 230 | 1988-02-08 | 1 | 0 | 10000 | 8966.6326 | 21649.6425 | Null | 0 | 30 |  | 19880208 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FAULTY VALVE IN A WALL HEATER CAUSED FIRE. A FOUR YEAR OLD GIRL WAS KILLED.
2025-01-31 10:21 | NO | NO | 19880076 |  | 11680 | LONE STAR GAS CO | 1102 32ND STREET | SNYDER | SCURRY | TX | 79549 | 1 | NO | 2200 | 1987-12-28 | 0 | 0 | 8000 | 7405.2724 | 17879.7891 | Null | 0 | 10 |  | 19871229 | 22 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR | REGULATOR/METER |  | CAST IRON |  | 0 | 0 | REGULATOR | ROCKWELL | 0 | 1956 | WITHIN/UNDER BUILDING |  | W.W.TURNER - MANAGER | 9155733594 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 1 1/4 ROCKWELL EMCO NO. 1 EJECTOR REGULATOR FAILED TO LOCK UP ALLOWING 20 OZ.TO FLOW INTO THE CUSTOMER'S HOUSE. THE EXCESS PRESSURE ESCAPED THROUGH A VALVEON THE WATER HEATER FILLING THE ATTIC WITH GAS. WHEN THE GAS IGNITED, THE CEILINGS WERE BLOWN DOWN, THE BRICK ON THE BACK WALL WAS KNOCKED DOWN AND THE ENTIRE ROOF JARRED LOOSE.
2025-01-31 10:21 | NO | NO | 19880078 |  | 11800 | LOUISIANA GAS SERVICE CO | 307 LEE AVENUE | MONROE | OUACHITA | LA | 71203 | 3 | NO | 1406 | 1988-02-12 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 57 |  |  | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | WELD | FILLET | STEEL |  | 2 | 0.154 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | BACKHOE BROKE 2" STUB TO ABANDONED SERVICE LINE OFF 6" MAIN.ELEMENTARY SCHOOL NEAR THE LEAK WAS EVACUATED.
2025-01-31 10:21 | YES | YES | 19880081 |  | 792 | ATLANTA GAS LIGHT CO | 150' E. OF JEFFERSON ST. ON BAY ST. | SAVANNAH | CHATHAM | GA | 31412 | 4 | NO | 1114 | 1988-02-03 | 0 | 2 | 0 | 0 | 0 | Null | 34 | 40 |  | 19880203 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | BELL JOINT | JOINT | BELL | CAST IRON |  | 8 | 0 | ASA SPEC. A21.8 |  | 0 | 0 | UNDER PAVEMENT |  | H.P. WELDON, S.E. GEORGIA DIVISION MANAGER | 9122382525 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CREW WAS USING AIR HAMMER TO REMOVE CONCRETE FROM UNDERNEATH BELL TO REPAIR BELL JOINT LEAK ON 8" C.I. MAIN. THE AIR HAMMER BROKE THROUGH THE DUCT AND DAMAGED THE POWER CABLE. WHEN THE CABLE WAS RE-ENERGIZED BY THE POWER COMAPNY, AS IN HOLE FLASHED RESULTING IN BURN INJURIES.
2025-01-31 10:21 | YES | NO | 19880082 |  | 22784 | WISCONSIN POWER & LIGHT CO | 614 E. MAPLE ST. | HORICON | DODGE | WI | 53032 | 0 | NO | 526 | 1988-02-13 | 0 | 0 | 76000 | 68146.4079 | 164537.2829 | Null | 5 | 0 |  | 19880217 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | WELD- END | STEEL |  | 2 | 0.154 | 150 ANSI | ASSOCIATED FLOW | 0 | 1983 | UNDER GROUND OR UNDER WATER |  | DALE G. MOODY, DIRECTOR OF GAS OPERATIONS | 6082523013 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS WAS AN OLDER HOME WITH BASEMENT WALLS OF POURED CONCRETE BUT AN EARTH FLOOR. NO ONE WAS HOME AT THE TIME OF THE EXPLOSION.
2025-01-31 10:21 | YES | YES | 19880083 |  | 22798 | WISCONSIN SOUTHERN GAS CO INC | 2921 CIRCLE DRIVE | CEDAR PARK | RACINE | WI | 53105 | 2 | NO | 1240 | 1988-02-26 | 0 | 1 | 50000 | 44833.1631 | 108248.2125 | Null | 3 | 50 |  | 19880229 | 32 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.122 |  |  | 0 | 1948 | UNDER PAVEMENT |  | ROBERT A. MEYERHOFER SAFETY & LOSS CONTROL MGR. | 4142488861 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | A 3/4 INCH GALVANIZED STEEL GAS SERVICE PIPE PROVIDING GAS SERVICE TO THE RESIDENCE AT 2921 CIRCLE DRIVE FRACTURED TWO THIRDS OF THE CIRCUMFERENCE OF THE PIPE ON TH THREADED PORTION THAT WAS SCREWED INTO A STREET EL, WHICH WAS FITTED INTO A SADDLE TEE, THAT WAS CLAMPED ON TO A TWO INCH STEEL MAIN.THE FRACTURE APPARENTLY WAS CAUSED BY STRESS FROM SOIL MOVEMENT DUE TO FROST PENETRATION.
2025-01-31 10:21 | YES | YES | 19880086 |  | 3130 | DAPHNE UTILITY DEPT, CITY OF | CORNER OF LOVETTE & CAPT. O'NEAL | DAPHNE | BALDWIN | AL | 36526 | 0 | NO | 1700 | 1988-02-15 | 0 | 1 | 0 | 0 | 0 | Null | 13 | 0 |  | 19880215 | 17 | 25 | BY TEST | 60 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 1.315 | 0.133 |  |  | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | TERRY SULLICVAN, SUPERVISOR | 2056262628 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-01-27 | YES | 3 | PAINT LINES | NO |  |  | LIT CIGARETTE IN MANHOLE NEAR GAS LEAK CAUSING FIRE AND BURNING MAN.HEAVY EQUIPMENT DRIVING OVER TAP POSSIBLY CAUSING TAP TO LEAK.
2025-01-31 10:21 | NO | NO | 19880088 |  | 12684 | MONTANA - DAKOTA UTILITIES CO | 1309 EAST DIVIDE AVE. | BISMARCK | BURLEIGH | ND | 58501 | 3 | NO | 10 | 1988-02-08 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  | 19880208 | 0.3 | 1 | BY TEST | 1 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | SCH 40 |  | 0 | 1957 | OTHER | CONCRETE SLAB | MIKE FINK/ GAS SUPERINTENDENT | 7012245814 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19880089 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1437 N. MONROE ST. | STOCKTON | SAN JOAQUIN | CA | 95201 | 3 | NO | 1625 | 1988-01-28 | 0 | 0 | 120100 | 107689.2577 | 260012.2063 | YES | 0 | 20 |  | 19880128 | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT |  | STEEL |  | 1.25 | 0.14 | API-5L A25 |  | 0 | 1937 | ABOVE GROUND |  | V.G. ROSE, V.P.-GAS & ELECTRIC TECHNICAL SERVICES | 4159736998 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | STRUCTURE FAILURE | NO |  | NO | 0 |  | NO |  |  | STRUCTURAL FAILURE OF BASEMENT WALL (CAUSE UNKNOWN) ALLOWED ENTIRE STRUCTURE TOCOLLAPSE. DEBRIS STRUCK SERVICE RISER, ALLOWING GAS TO EXCAPE TO ATMOSPHERE. BUILDINGS WERE EVACULATED AND TRAFFIC REROUTED.
2025-01-31 10:21 | NO | NO | 19880090 |  | 11680 | LONE STAR GAS CO | TOWN EAST BLVD. -VIA DEL NORTE | MESQUITE | TEXAS | TX | 75150 | 3 | NO | 1344 | 1988-01-18 | 0 | 0 | 15000 | 13449.9489 | 32474.4637 | Null | 3 | 36 |  | 19880118 | 20 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 18 | 2.5 | API-5LX | GRADE X42 | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | J.R. ROSSER - C&M SUPERINTENDENT | 2144873835 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 | SHOWN ON CONTRATORS' PLAN | NO |  |  | EXCAVATOR WAS USING LARGE FRONT-END LOADER TO REMOVE WING WALL AND STROM DRAIN. OUR 3" STEEL LINE LAY ON THE INSIDE OF THE WINGF WALL AND ON TOP OF THE DRAIN PIPE. THE FORCE AGAINST THE WING WALL AND THE 3" STEEL PIPE CAUSED A RAGGED HOLE TO BE TORN IN THE TOP OF THE 18" STEEL PIPE WHERE THE 3" WAS TIED IN. IT ALSOBROKE THE OUTLET FLANGE FROM THE 3" VALVE.
2025-01-31 10:21 | NO | NO | 19880091 |  | 3210 | DEL RIO GAS SYSTEM, CITY OF | #139 TERRY STREET | DEL RIO | VAL VERDE | TX | 78840 | 1 | NO | 345 | 1988-02-14 | 0 | 0 | 21700 | 19457.5928 | 46979.7242 | Null | 2 | 0 |  | 19880215 | 7 | 29 | BY TEST | 7 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | REGULATOR/METER | DAMAGE BY TRUCK | STEEL |  | 1 | 0.125 | TF-2-3 | GENSCO | 0 | 1982 | ABOVE GROUND |  | MANUEL RIVERA / GAS SYSTEM SUPERINTENDENT | 5127742781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE WENT OUT OF CONTROL KNOCKING DOWN FENCE AND HITTING THE GAS METER WHICHIGNITED A FIRE THAT DAMAGE A MOBILE HOME.DRIVER: RICARDO R. GOMEZ 710 W. 11TH ST. DEL RIO, TEXAS 78840
2025-01-31 10:21 | YES | NO | 19880092 |  | 20211 | UNITED CITIES GAS CO | PROPANE AIR PLANT RT 460 | BLACKSBURG | MONTGOMERY | VA | 24060 | 2 | NO | 1845 | 1988-01-07 | 0 | 0 | 60000 | 53799.7957 | 129897.855 | Null | 1 | 0 |  | 19880109 | 90 | 100 | BY TEST | 150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | PROPANE AIR PLANT | OTHER | SEPARATOR BOWL | OTHER PLASTIC | OIL SEPARATOR BOWL | 0 | 0 |  |  | 0 | 0 | OTHER | INSIDE COMPRESSOR SHED | ROBERT M. ELAM, VICE PRESIDENT/OPERATIONS | 6159267171 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 1845 HOURS OF JANUARY 7, 1988, WE INCURRED AN EXPLOSION WITHIN THE COMPRESSOR SHED DURING PEAK SHAVING OPERATIONS. SUBSEQUENT TO THE EXPLOSION, WE EXPERIENCED A NATURAL GAS FIRE EMITTING FROM A ONE-INCH STEEL LINE AT 90 PSIG. THIS STEEL LINE IS USED AS THE STARTING MECHANISM FOR BOTH #1 AND #2 COMPRESSORS.IN OUR JUDGEMENT, AS WELL AS THE OPINION OF AN OUTSIDE CONSULTANT, THE INCIDENTWAS DUE TO THE FAILURE OF THE PLASTIC SEPARATION BOWLS IN THE STARTER PIPING NETWORK. THESE PLASTIC BOWLS WERE LOCATED UPSTREAM OF THE HAND STARTER VALVE AND BETWEN A BLOCK VALVE OF THE COMPRESSOR ENGINE. THESE BOWLS WERE SUBJECT TO THE LINE PRESSURE OF 90 PSIG. WE SUSPECT THE PLASTIC BOWL FAILED AND ALLOWED THIS 90PSIG NATURAL GAS TO ESCAPE WITHIN THE COMPRESSOR SHED, THUS CAUSING THE EXPLOSION AND SUBSEQUENT FIRE. INGNITION SOURCE IS UNKNOWN AT THIS TIME.THERE WERE NO PERSONAL INJURIES OR DAMAGE TO ANY OTHER PROPERTY OTHER THAN FACILITIES OF THE COMPANY. THE COMPRESSOR ROOM WAS HEAVILY DAMAGE BY BOTH THE EXPLOSION AND SUBSEQUENT FIRE. EXTIMATED DAMAGES ARE EXPECTED TO EXCEED $50,000 DEPENDING UPON REPLACEMENT DECISIONS.
2025-01-31 10:21 | YES | NO | 19880093 |  | 2748 | CONSUMERS POWER CO | 3626 TOEPFER | WARREN | MACOMB | MI | 48091 | 3 | NO | 47 | 1988-03-10 | 0 | 0 | 90000 | 80699.6936 | 194846.7824 | Null | 0 | 36 |  | 19880310 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6.25 | 0.062 | ASTM 2513 | PHILLIPS | 0 | 1982 | ABOVE GROUND |  | K. L. ELENBAAS, GERNERAL SUPERVISOR | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AIRPLANE CRASHED INTO HOUSE AND HIT GAS SERVICE RISER.
2025-01-31 10:21 | NO | NO | 19880094 |  | 20050 | UNION ELECTRIC CO | 220 ST. FRANCIS | DEXTER | STODDARD | MO |  | 3 | NO | 1218 | 1988-02-28 | 0 | 0 | 50000 | 44833.1631 | 108248.2125 | Null | 0 | 5 |  | 19880301 | 0.2 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INTERIOR LEAK | OTHER | LACK OF PLUG | OTHER | COPPER | 0.625 | 0.049 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | F. W. COPANAS, JR. SUPV. CORROSION & METERING | 3146515724 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ABOUT 1:00 P.O., FEBRUARY 27, 1988, NATURAL GAS WAS TURNED ONTO A 5/8 INCH COPPER LINE THAT WAS OPEN INTO AN UNPROPERLY VENTED FIREPLACE.THE FIREPLACE VENTED INTO THE ATTIC SPACE BETWEEN THE CEILING AND ROOF ON A ONESTOREY DUPLEX, NOT THROUGH THE ROOF. THE DUPLEX HAD A NEW TENANT MOVING INTO THE FRONT APARTMENT AND WAS UNOCCUPIED IN THE BACK APARTMENT.THE 5/8TH INCH COPPER LINE RAN FROM THE UTILITY ROOM OF THE FRONT APARTMENT TO THE FIREPLACE OF THE BACK APARTMENT. NATURAL GAS WAS APPARENTLY ALLOWED TO EXCAPE INTO THE FIREPLACE OF THE UNOCCUPIED BACK APARTMENT FROM THE TIME GAS IN THE FRONT APARTMENT WAS TURNED ON UNTIL IT WAS SHUT OFF AFTER THE EXPLOSION AT 12:18 P.M. SUNDAY, FEBRUARY 28, 1988.NATURAL GAS DID NOT ENTER THE FRONT APARTMENT BUT IT DID FILL THE BACK APARTMENTAND VENTED OUT OF THE BUILDING BY WAY OF THE FIREPLACE FLUE AND THE RIDGE VENTSFOR THE ATTIC SPACE. THE NATURAL GAS BUILD-UP IN THE UNOCCUPIED APARTMENT WAS SLOW BECAUSE OF THE OPEN FIREPLACE FLUE.THE SOURCE OF IGNITION WAS PROBABLY THE PILOT ON THE FURNACE IN THE UNOCCUPIED REAR APARTMENT.
2025-01-31 10:21 | YES | YES | 19880096 |  | 14210 | OKLAHOMA NATURAL GAS CO | 14 STREET | WOODWARD | WOODWARD | OK | 73801 | 3 | NO | 2139 | 1988-03-30 | 2 | 0 | 20000 | 17933.2652 | 43299.285 | Null | 1 | 50 |  | 19880331 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR SETTING | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5L | N/A | 1972 | 1977 | ABOVE GROUND |  | JAMES M. WOOD, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ON MARCH 30, 1988, AT APPROXIMATELY 2139 HOURS A VEHICLE DRIVEN BY MARION HUNTER OWENS IN WOODWARD, OKLAHOMA, STRUCK A NATURAL GAS DISTRIBUTION REGULATOR SETTING. MARION OWENS AND HIS WIFE, GLENDOLA OWENS, HAD BEEN SHOPPING AT THE FLEMING'S JACK N. JILL GROCERY STORE LOCATED ON THE NW CORNER OF 14TH AND OKLAHOMA STREETS IN WOODWARD. AS THE OWENS LEFT THE PARKING LOT IN THEIR VEHICLE, WITNESSES NOTED THAT THEIR CAR SUDDENLY ACCELERATED AND SEEMED TO BE OUT OF CONTROL. ANOTHERWITNESS STATED THAT THE PASSENGER OF THE VEHICLE, MRS. OWENS, SEMED TO BE FIGHTING FOR CONTROL OF THE VEHICLE.THE OWEN'S VEHICLE RAN OVER A CURB AS IT EXITED THE PARKING LOT ON THE EAST CURB, AND TRAVELED APPROXIMATELY 27' BEFORE IT STRUCK AND CAME TO REST OVER THE REGULATOR SETTING. THE IMPACT SEVERED THE 2" INLET LINE AND THE GAS IGNITED. WITNESSES OF THE ACCIDENT RAN TO THE SITE AND PULLED THE OCCUPANTS FROM THE BURNINGVEHICLE. THE OWENS WERE THEN TRANSPORTED TO MEDICAL FACILITIES. BOTH LATERDIED. THE WOODWARD POLICE DEPARTMENT CONTACTED OKLAHOMA NATURAL GAS. ONG PERSONNEL ARRIVED AT THE SCENE AND TOOK THE NECESSARY ACTIONS TO STOP THE FLOW OF GAS
2025-01-31 10:21 | YES | YES | 19880098 |  | 2784 | CORDOVA, WATER WORKS & GAS BOARD FO THE CITY OF | 703 GREEN AVENUE | CORDOUA | WALKER | AL | 35550 | 3 | NO | 2000 | 1988-03-29 | 1 | 1 | 75000 | 67249.7446 | 162372.3187 | YES | 0 | 30 |  | 19880330 | 20 | 25 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | GALV. | 1 | 0 |  |  | 0 | 1951 | UNDER PAVEMENT |  | ELAINE STOVER, BOOKKEEPER | 2054839235 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS SERVICE WAS UNDER A LEAK HISTORY PROGRAM AND IN COMPLIANCE WITH 192.465E.
2025-01-31 10:21 | NO | NO | 19880099 |  | 11680 | LONE STAR GAS CO | 2307 ANN ARBOR | DALLAS | DALLAS | TX |  | 3 | NO | 209 | 1988-02-23 | 0 | 0 | 55000 | 49316.4794 | 119073.0337 | Null | 3 | 51 |  | 19880223 | 0 | 55 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0 |  |  | 0 | 1945 | UNDER PAVEMENT |  | L. B. HULCY, JR. SUPERINTENDENT | 2144267931 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-02-17 | YES | 3 | PAINT | YES |  |  | A CONTRACTOR INSTALLING A WATER MAIN HIT OUR STEEL SERVICE LINE AND BROKE A FITTING INSTALLED IN THE SERVICE BETWEEN THE STREET AND BUILDING STRUCTURE. POSSIBILITY OF GAS ACCUMULATION BEING IGNITED BY AN UNKNOWN SOURCE CAUSING THE EXPLOS
2025-01-31 10:21 | NO | NO | 19880100 |  | 18532 | SOUTHERN UNION GAS CO | 761 SPARKS ROAD |  | EL PASO | TX | 79927 | 3 | NO | 1200 | 1988-03-25 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19880325 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | VALVE |  | CAST IRON | BRASS VALVE CORE | 0.375 | 0 | 100G | MUELLER | 0 | 1973 | ABOVE GROUND |  | EDWARD H. SMITH, P.E., REGIONAL ENGINEER | 9155446300 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | AT 12:00 P.M. MR. JESUS MAGALLANES IGNITED SOME DEAD WEEDS AND BRUSH ON HIS PROPERTY WHICH IS APPROXIMATELY 100 FEET EAST OF HIS HOME. THE FIRE RAPIDLY SPREADTO A SHACK ON THE PROPERTY AND DESTROYED A PORTION OF THE STRUCTURE.IN ADDITION, THE FIRE SPREAD TO A STAND OF CATTAILS THAT QUICKLY IGNITED. OUR GAS METER SERVING THE PROPERTY WAS ADJACENT TO THE BRUSH. HEAT FROM THE FLAMES MELTED THE GREASE IN THE LOCKWING COCK WHICH RESULTED IN A SMALL AMOUNT OF ESCAPING GAS. THE FLAMES ALSO CAUSED GAS TO ESCAPE IN VARIOUS OTHER PLACES ON THE METER WHERE GASKETS WERE BURNED. THE FIRE AT THE METER WAS EXTINGUISHED BY THE LOCAL VOLUNTEER FIRE DEPARTMENT AND THE EXCAPE OF GAS WAS STOPPED BY TIGHTENING THE VALVE CORE AND SHUTTING THE VALVE. THE METER LOOP ASSEMBLY, INCLUDING VALVE AND VALVE METER REGULATOR, WAS REPLACED AND GAS WAS RESTORED THE SAME DAY.
2025-01-31 10:21 | NO | NO | 19880101 |  | 11800 | LOUISIANA GAS SERVICE CO | 832 PHOSPHOR STREET | METAIRIE | JEFFERSON | LA | 70005 | 3 | NO | 2042 | 1988-03-19 | 0 | 0 | 1000 | 896.6633 | 2164.9642 | YES | 1 | 10 |  |  | 70 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | N/A | N/A | 0 | 1944 | ABOVE GROUND |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PICKUP TRUCK HIT BRICK FENCE WHICH FELL ON METER INSTALLATION.ONLY ONE CUSTOMER WAS WITHOUT GAS, BUT FIRE DEPARTMENT EVACUATED 4 BLOCK AREA CONSISTING OF APPROXIMATELY 200 HOMES.
2025-01-31 10:21 | YES | YES | 19880102 |  | 17560 | ROBSTOWN GAS SYSTEM, CITY OF | 3RD STREET BETWEEN E. AVE. G. AND E. AVE | ROBSTOWN | NUECES | TX | 78380 | 0 | NO | 335 | 1988-02-17 | 0 | 3 | 0 | 0 | 0 | Null | 4 | 30 |  |  | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | FITTING | THREAD ON SERV. TAP BROKE | STEEL |  | 4 | 0.188 |  |  | 0 | 1940 | UNDER PAVEMENT |  | RICHARD ORTEGON, JR. / GAS SUPERINTENDENT | 5123873554 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | THEY WERE PREPARING TO REPLACE THE NEW LENGTH OF PIPE AND DISCOVERED THAT IT DID NOT FIT RIGHT, SO THAY USED THE TORCH TO HEAT THE PIPE SO THAT IT WOULD EXPANDAND FIT RIGHT INTO PLACE. THEY PLACED PRESSURE ON THE PIPE RUNNING NORTH AND SOUTH AND THE THREAD BROKE BEHIND 2" VALVE THAT WAS ON SERVICE TAP.THE TORCH WAS STILL LIT, THE GAS FUMES HIT THE TORCH AND THE EXPLOSION OCCURED.
2025-01-31 10:21 | NO | NO | 19880103 |  | 4473 | ENERGAS CO | YUKON RD. EAST OF WEST CO. RD. | ODESSA | ECTOR | TX | 79764 | 3 | NO | 1124 | 1988-02-24 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19880224 | 10 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.216 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | PAVING CONTRACTOR MADE AN EXCESSIVE CUT AND CUT INTO THE PIPELINE.
2025-01-31 10:21 | NO | NO | 19880104 |  | 4473 | ENERGAS CO | 3 1/2 MILES EAST OF DENVER CTY. | DENVER CITY | GAINES | TX |  | 2 | NO | 1115 | 1988-02-24 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19880224 | 15 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 2 | 0.091 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CARL F. BAILEY, P.E. DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | FARMER PLOWED INTO GAS LINE.
2025-01-31 10:21 | YES | YES | 19880105 |  | 18406 | SOUTH ALABAMA UTILITIES | LOTT ROAD BETWEEN 8 & 9 MILE MARKER | SEMMES | MOBILE | AL | 36575 | 0 | NO | 1125 | 1988-02-03 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19880204 | 20 | 45 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | FARM TAP | NO DATA |  | STEEL |  | 34 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | THOMAS E. MURPHY, OPERATIONS SUPERINTENDENT | 2056537311 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | RICHARD BLANKINCHIP WAS WORKING IN A TAP HOLE USING A PROPANE TORCH TO HOT WRAPA TAP CONNECTION AFTER INSTALLING A SERVICE TO THE RESIDENCE OF B. E. DUNN. CHRIS HURD (CREW MAN) WAS GETTING READY TO INSTALL A UNION ON THE OUTLET SIDE OF THE HIGHPRESSURE REGULATOR SET. PHILIP SCHWARTZ CAME UP ON THE JOB SITE AND INSERTED THE DISC AND HOLDER INTO THE POSITIVE LOCK VALVE. BY DOING THIS THE GAS WASALLOWED TO PASS THROUGH THE HIGH PRESSURE SET AT ABOUT 18# TO 20# PSIG. AT THISTIME THE DITCH LINE WAS OPEN FROM THE HIGH PRESSURE SET TO THE TAP HOLE ABOUT 12TO 14' AWAY WHERE RICHARD WAS WORKING. THE GAS WAS BLOWING DOWN THROUGH A U-BEND ON THE HIGH PRESSURE SET INTO THE OPEN DITCH LINE AND INTO THE TAP HOLE. THE PROPANE TORCH IGNITED THE GAS WHICH FLASH BURNED IN THE TAP HOLE AND THEN RAN BACK TOTHE HIGH PESSURE SET.THE FIRE WAS PUT OUT BY USING DRY CHEMICAL FIRE EXTINGUISHERS.THE FIRE DID NOT BURN MORE THAN A MINUTE. THE FLASH FIRE IN TAP HOLE CAUSED BURNS ON RICHARD'S FACE AND ARMS.
2025-01-31 10:21 | NO | NO | 19880107 |  | 11680 | LONE STAR GAS CO | 1800 W. SEMINARY DR. | FORT WORTH | TARRANT | TX | 76115 | 3 | NO | 2114 | 1988-01-29 | 0 | 0 | 5000 | 4483.3163 | 10824.8212 | Null | 2 | 33 |  | 19880129 | 28 | 90 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | WELDON R. EDENS - SUPT. II | 8173368381 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | FOUR TEENAGERS WERE SPEEDING IN A 1983 CHEV. CAMERO TRYING TO ELUDE THE CROWLEY, TX POLICE WHEN THEIR CAR CRASHED INTO THE METER INTALLATION AT 1800 W. SEMINARY DR. THE DAMAGE REISER BLEW GAS FOR APPROXIMATELY THREE MINUTES BEFORE IGNITING AND ENGULFING THE CAR IN FLAMES. ALL THE OCCUPANTS GOT OUR OF THE CAR BEFORE IT IGNITED.
2025-01-31 10:21 | YES | NO | 19880108 |  | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 4465 POPLAR | MEMPHIS | SHELBY | TN | 38117 | 0 | NO | 915 | 1988-02-29 | 0 | 0 | 250000 | 224165.8155 | 541241.0623 | Null | 0 | 45 |  | 19880229 | 80 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 |  | .L. B. FOSTER | 1985 | 1986 | UNDER GROUND OR UNDER WATER |  | CURTIS L. DILLIHUNT, MANAGER | 9013201452 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR WAS DRILLING HOLES FOR A STREET LIGHT AND HIT OUR 4" CWS MAIN AT APPROXIMATELY 9:15 A.M. HITTING THE LINE CAUSED AN EXPLOSION AND FIRE AND DAMAGED TWO LARGE VEHICLES OWNED BY CONTRACTOR.
2025-01-31 10:21 | YES | YES | 19880111 |  | 2596 | COLUMBIA GAS OF OHIO INC | BRIGS RD. AT HARRISBURG PK. | COLUMBUS | FRANKLIN | OH | 43223 | 4 | NO | 1252 | 1988-02-16 | 0 | 3 | 0 | 0 | 0 | Null | 1 | 5 |  | 19880211 | 45 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | GRADE "B" | N/A | 1968 | 1968 | UNDER GROUND OR UNDER WATER |  | LUTHER BEBLEY, DIVISION PLANT SUPERVISOR | 6144602103 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-01-28 | NO | 0 |  | YES |  |  | WATER LINE CONTRACTOR WAS EXCAVATING AND BROKE 1 1/4" STEEL GAS SERVICE LINE ATCURB VALVE. COMPANY CREW WAS IN PROCESS OF CUTTING LINE SO THAT THE FLOW OF GAS COULD BE CONTROLLED WHEN IGNITION OCCURRED. SUSPECTED SOURCE OF IGNITION WAS A GASOLINE DRIVEN WATER PUMP ABOUT 45FT. FROM CUT SITE. FIRE EXTINGUISHED IMMEDIATELY BY COMPANY CREW WHO WERE STANDING BY AT THE READY POSITION. THREE CONTRACTOR'S MEN BURNED REQUIRING MEDICAL ATTENTION.
2025-01-31 10:21 | YES | YES | 19880114 |  | 15518 | PIEDMONT NATURAL GAS CO INC | 380 KNOLLWOOD DRIVE | WINSTON SALEM | FORSYTH | NC | 27102 | 4 | NO | 218 | 1988-01-18 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 49 |  | 19880301 | 60 | 65 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MICHAEL N. PARROTT, SUPERINTENDENT | 7043643120 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INITIAL OFFICIAL CAUSE WAS DETERMINED BY THE INVESTIGATING WINSTON SALEM MECHANICAL INSPECTOR (IN CONCURRENCE WITH THE WINSTON SALEM FIRE DEPARTMENT) TO BEA BOILER EXPLOSION. DETERMINATION (BY THE ABOVE) WAS MADE THAT PIEDMONT NATURAL GAS CO. WAS NOT IN ANY WAY RESPONSIBLE FOR THE ACCIDENT.
2025-01-31 10:21 | YES | NO | 19880115 |  | 15518 | PIEDMONT NATURAL GAS CO INC | 1037 MADISON AVE. | WINSTON SALEM | FORSYTH | NC | 27103 | 3 | NO | 230 | 1988-03-17 | 0 | 0 | 65000 | 58283.112 | 140722.6762 | Null | 1 | 0 |  | 19880317 | 60 | 65 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MICHAEL N PARROTT - SUPT | 7043643120 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MINOR EXPLOSION AT RESIDENCE AND HOUSE DESTROYED BY FIRE. CUSTOMER HAD BEEN TURNED OFF IN FEBRUARY 1986 FOR UNAUTHORIZED USE OF GAS. THERE WAS A CONCERN THAT THE COSTOMER WAS AGAIN STEALING GAS BUT THIS WAS NOT THE CASE. THERE WAS NO METER PRESENT AND NO OTHER DEVICE TO ALLOW THE CUSTOMER ACCESS TO OUR SERVICE LINE. THE WINSTON SALEM FIRE DEPARTMENT CONCLUDED NATURAL GAS WAS NOT PRESENT.
2025-01-31 10:21 | NO | NO | 19880116 |  | 15518 | PIEDMONT NATURAL GAS CO INC | 1816 PARKER DR. (CHEM-WAY) | CHARLOTTE | MECKLENBURG | NC | 28201 | 3 | NO | 2252 | 1988-03-21 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 21 |  | 19880323 | 60 | 65 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MICHAEL N. PARROTT-SUPERINTENDENT | 7043643120 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CHEM-WAY EMPLOYEES MISHANDLED THE DISPOSITION OF CHEMICALS CAUSING FIRE. INITIALLY GAS WAS REPORTEDLY INVOLVED, BUT IT WAS NOT.
2025-01-31 10:21 | NO | NO | 19880117 |  | 15518 | PIEDMONT NATURAL GAS CO INC | 4825 HOVIS RD. | CHARLOTTE | MECKLENBURG | NC | 28201 | 3 | NO | 2322 | 1988-03-25 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 19 |  | 19880328 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MICHAEL N. PARROTT, SUPERINTENDENT | 7043643120 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION IN COMMERCIAL NATURAL GAS OVEN OF EARTH GRAINS BAKERY. EXTINGUISHED ITSELF. FIVE PERSONS INJURED.
2025-01-31 10:21 | NO | NO | 19880119 |  | 6830 | GREY FOREST UTILITIES | #9 CARRIAGE HILLS |  | BEXAR | TX | 78257 | 3 | NO | 1013 | 1988-04-20 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 7 |  | 19880420 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE3408 | PLEXCO | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | PHIL FRANCESCO, ASSISTANT GENERAL MANAGER | 5126958781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | GAS SERVICE LINE AND ELECTRIC CABLE WERE IN A COMMON TRENCH. LANDSCAPER DUG UPGAS AND ELECTRIC WITH A BACKHOE, COMPLETELY SEVERING BOTH LINES. THE ELECTRIC LINE IGNITED THE GAS. LANDSCAPER PUT OUT FIRE IMMEDIATELY.
2025-01-31 10:21 | NO | NO | 19880120 |  | 4473 | ENERGAS CO | 3007 ROBERTSON | ODESSA | ECTOR | TX | 79764 | 3 | NO | 140 | 1988-04-01 | 0 | 0 | 20000 | 17933.2652 | 43299.285 | YES | 0 | 30 |  | 19880401 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APPARENTLY THE FLOORING SUPPORTING THE WATER HEATER FAILED AND ALLOWED THE WATER HEATER TO FALL, BREAKING THE FLEXLINE SUPPLYING THE GAS.
2025-01-31 10:21 | NO | NO | 19880121 |  | 4499 | ENTEX INC | 819 COUNTRY LANE | HOUSTON | HARRIS | TX | 77024 | 3 | NO | 1029 | 1988-03-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 23 |  | 19880316 | 23 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE2306 | DUPONT | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | B. F. BROYLESS, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 2 |  | NO |  |  | CONTRACTOR APPARENTLY DAMAGED SERVICE LINE, THEN IGNITED THE EXCAPING GAS WHILEHEATING A NEARBY PIPE.
2025-01-31 10:21 | YES | YES | 19880122 |  | 4473 | ENERGAS CO | 306 COLLEGE AVENUE | LEVELLAND | HOCKLEY | TX | 79336 | 3 | NO | 1745 | 1988-04-10 | 0 | 2 | 300000 | 268998.9785 | 649489.2748 | Null | 2 | 0 |  | 19880410 | 13 | 52 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1966 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEEER | 8067414228 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS HAD APPARENTLY ACCUMULATED UNDER AND WITHIN MOTEL. IT IGNITED IN ROOM 125,POSSIBLY FROM CIGARETTE BEING LIGHTED, CAUSING FIRE INTHIS ROOM AND SPREADING TO ATTIC OF MOTEL. EXPLOSION APPEARS TO HAVE SUBSEQUENTLY OCCURRED IN MOTEL ATTICOCCUPANTS OF ROOM 125 WERE JIM ATTEBERRY, AGE 42, AND HIS WIFE, SARAH ATTEBERRY, AE 49. BOTH RECEIVED SEVERE BURNS AND WRE TRANSPORTED TO LUBBOCK GENERAL HOSPITAL, WHERE THEY REMAIN AT THIS TIME.
2025-01-31 10:21 | NO | NO | 19880123 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 968 3RD AVENUE | NEW YORK |  | NY | 10022 | 4 | NO | 506 | 1988-04-07 | 0 | 0 | 50000 | 44833.1631 | 108248.2125 | Null | 0 | 11 |  |  | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | APPLIANCE | OTHER | CONTROLS | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DOMINIC CASTELLANO, ACTING CHIEF GAS ENGINEER | 2124604464 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MALFUNCTION OF THE CONTROLS ON A WATER HEATER ALLOWED GAS TO PASS THROUGH THE APPLIANCE WITHOUT BURNING. THE APPLIANCE FLUE WAS NOT VENTED TO A CHEMNEY NOR TOTHE OUTSIDE. THE GAS ESCAPED FROM THE FLUE INTO A BASEMENT AND WAS IGNITED BYAN UNKNOWN SOURCE.
2025-01-31 10:21 | NO | NO | 19880125 |  | 6830 | GREY FOREST UTILITIES | 6500 BABCOCK ROAD | SAN ANTONIO | BEXAR | TX | 78249 | 3 | NO | 1245 | 1988-03-10 | 0 | 0 | 20000 | 17933.2652 | 43299.285 | YES | 2 | 0 |  | 19880311 | 144 | 150 | BY TEST | 300 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | API5L | DOMESTIC | 1968 | 1968 | UNDER GROUND OR UNDER WATER |  | PHIL FRANCESCO, ASSISTANT GENERAL MANAGER | 5126958781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-03-07 | YES | 3 |  | NO |  |  | THE GAS MAIN WAS DAMAGED BY A CONTRACTOR WHILE EXCAVATING FOR A ROAD WIDENING PROJECT. ALL GAS MAINS ARE SHOWN ON THE CONTRACTORS PLANS.
2025-01-31 10:21 | NO | NO | 19880130 |  | 4150 | EASTERN SHORE GAS CO | COSTAL HIGHWAY & BERING RD. | OCEAN CITY | WORCESTER | MD | 21842 | 1 | NO | 1345 | 1988-03-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19880328 | 11 | 0.3 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | NO DATA |  | STEEL |  | 0.2 | 0.216 |  | PHILLIPS | 1987 | 1988 | OTHER | OPEN EXCAVATION | GARY R. BUTTON VICE PRES. AND GENERAL MANAGER | 3015247060 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | AN EASTERN SHORE GAS CO STREET CREW, CONSISTING OF JOESPH LONOGBARDI, CLIFF GLENN AND HOWARD TAYLOR WAS REMOVING A 2 INCH STEEL GAS MAIN TO MAKE WAY FOR A 24 INCH STORM SEWER. THEY HAD INSTALLED A 2 INCH MUELLER NO-BLOW FITTING ON THE SOUTHEND OF THE MAIN AND PUT DOWN A STOPPER. MYSELF AND JIM ADKINS HAD GONE TO 118THSTREET TO TAKE A PRESSURE READING TO INSURE THAT THE STOPPER HAD NOT AFFECTED THE SYSTEM PRESSURE. WE STILL HAD 12 PUNDS OF PRESSURE ON THE SYSTEM. WHILE WE WERE OBSERVING THE PRESSURE GAUGE, I HAD THE CREW CUT THE LINE AND INSTALL A DRESSER BLANK END ON THE NORTH SIDE OF THE MAIN. THEY CUT OUT APPROXIMATELY 20 FEET OF2" MAIN. THE PRESSURE REMAINED AT 11 POUNDS.WHILE I WAS RETURNING TO THE JOB SITE, I OBSERVED A FIRE AT THE JOB SITE. I WASAT 94TH STREET. I NOTIFIED THE DISPATCHER TO CALL THE FIRE DEPARTMENT.I ARRIVED ON THE JOB SITE AND FOUND THAT ALL PERSONNEL WERE OUT OF THE EXCAVATION AND THAT JOE LONGOBARDI AND CLIFF GLENN HAD SUFFERED BURNS. THERE WAS A PIECEOF 2 " PLASTIC PIPE AND A 2 " STYLE 711 DRESSER COUPLING CONNECTED TO THE NORTHSIDE OF THE MAIN THE DRESSER COUPLING WAS NOT TIGHT AND THERE WAS FIRE AROUND THE DRESSER COUPLING. THERE WAS A SQUEEZE OFF TOOL ON THE 2" PLASTIC PIPE. THEREWAS A GASOLINE DRIVEN WATER PUMP SITTING APPROXIMATELY 25 FEET FROM THE EXCAVATION, BUT IT WAS NOT RUNNING. THERE WAS ALSO A BACKHOE IN THE INTERSECTION, BUT ITWAS NOT RUNNING. THERE WERE SEVERAL WORKERS AROUND THAT WERE NOT COMPANY EMPLOYEBOTH JOE AND CLIFF GLENN SAID THAT THEY HAD MADE SURE ALL EQUIPMENT WAS TURNED OFF AND THAT THERE WAS NOT ANYONE SMOKING AROUND THE JOB BEFORE THEY ATTEMPTED TOREMOVE THE BLANK END AND CONNECT THE PLASTIC PIPE AND DRESSER COUPLING. THEY INSTALLED THE DRESSER COUPLING AND JOE WAS HAND TIGHTENING THE BOLTS WHEN IGNITIONJOE RECEIVED SECOND DEGREE BURNS TO THE FACE AND CLIFF RECEIVED SECOND AND THIRDDEGREE BURNS TO THE RIGHT HAND AND THIRD DEGREE BURNS TO THE LEFT ARM. HOWARD SUFFERED FLASH BURNS TO THIS FACE AND WAS IN SLIGHT SHOCK.JOE AND CLIFF WERE TRANSPORTED TO PENINSULA GENERAL MEDICAL CENTER AT 66TH STREET BY THE OCEAN CITY RESCUE SQUAD, WHERE THEY WERE TREATED AND RELEASED.THE OCEAN CITY FIRE DEPARTMENT CONTROLLED THE FIRE UNTIL WE COULD STOP THE FLOWOF GAS. WE HAD TO REQUEST AN ADDITIONAL STOPPER MACHINE FROM CHESAPEAKE UTIL INSALISBURY.WE ATTEMPTED TO SQUEEZE THE 2" STEEL PIPE OFF ON THE NORTH SIDE OF THE INTERSECTION, BUT WERE UNSUCCESSFUL. WHEN THE STOPPER MACHINE ARRIVED WE WERE ABLE TO STOP THE FLOW OF GAS. THIS OCCURED AT APPROXIMATELY 5 PM. WE THEN CUT THE AFFECTEDPIECE OF MAIN AND REPLACED 40 FEET OF MAIN ACROSS THE INTERSECTION WITH PLASTICPIPE. THERE WAS A VALVE ON THE NORTH END OF THE LINE APPROXIMATELY 3 FEET NORTHOF THE INTERSECTION, BUT IT WAS USELESS, AS THERE WAS A CROSSOVER MAIN DOWN STREAM OF THE VALVE BACKFEEDING THE MAIN.
2025-01-31 10:21 | YES | NO | 19880132 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 1112 SO. SCENIC WAY | RIM FOREST | SAN BERNARDINO | CA |  | 2 | NO | 515 | 1988-05-20 | 0 | 0 | 120000 | 107599.5914 | 259795.7099 | Null | 0 | 54 |  | 19880520 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.05 | 0.84 | SMC40-00 | ALDYLA DUPONT | 0 | 1983 | ABOVE GROUND |  | ROBERT J. MAHAR | 8183072645 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE CAUSED BY ARSON AND FLAMMABLE LIQUID POURED ON FLOOR, BROKE GAS LINE. COLLAPSE OF STRUCTURE.
2025-01-31 10:21 | YES | YES | 19880133 |  | 4473 | ENERGAS CO | 309 N. GRAHAM | ODESSA | ECTOR | TX | 79763 | 3 | NO | 2100 | 1988-03-16 | 0 | 4 | 30000 | 26899.8979 | 64948.9275 | Null | 0 | 30 |  | 19880316 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | CARL F. BAILEY , P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION OF UNKNOWN ORIGIN DESTROYED THE HOUSE REQUIRING MEDICAL TREATMENT FORTHE FOUR OCUPANTS.
2025-01-31 10:21 | NO | NO | 19880134 |  | 4473 | ENERGAS CO | I-20, 1/2 MILE E. OF SYNDER HIGHWAY | BIG SPRING | HOWARD | TX | 79720 | 3 | NO | 1315 | 1988-05-02 | 0 | 0 | 10000 | 8966.6326 | 21649.6425 | YES | 0 | 15 |  | 19880502 | 10 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | PROCEDURE | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CARK F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | MEASUREMENT STATION WS BY PASSED WITH INAPPROPRIATE REGUALTOR. EXCESS PRESSUREAT CUSTOMER APPLIENCES RESULTED IN EXPLOSION & FIRE.
2025-01-31 10:21 | NO | NO | 19880135 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 909 CROCKETT ST. | MT. PLEASANT | TITUS | TX | 75455 | 1 | NO | 1232 | 1988-04-14 | 0 | 0 | 30000 | 26899.8979 | 64948.9275 | Null | 0 | 5 |  |  | 8 | 8 | BY TEST | 8 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | VALVE IN HOUSE PIPING | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | HOYLE T. ROGERS, MANAGER | 3184292523 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FLEXIBLE CONNECTOR DISCONNECTED FROM WALL VALVE. VALVE WAS FOUND IN "ON" POSITION.
2025-01-31 10:21 | YES | YES | 19880136 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 103 WHITMORE | DAINGERFIELD | MORRIS | TX | 75686 | 1 | NO | 1225 | 1988-04-06 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | CUSTOMER PIPING | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | HOYLE T. ROGERS, MANAGER | 3184292523 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PRELIMINARY INVESTIGATION REVEALED USE OF RECREATIONAL VEHICLE BUTANE APPLIANCEINSIDE 10' X 12' CINDER BLOCK STRUCTURE.
2025-01-31 10:21 | NO | NO | 19880137 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 803 SOUTH MAIN | WINNSBORO | WOOD | TX | 75494 | 1 | NO | 1155 | 1988-04-14 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 15 |  |  | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | CUSTOMER PIPING | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | HOYLE T. ROGERS, MANAGER | 3184292523 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PRELIMINARY INVESTIGATION BY LOCAL FIRE DEPARTMENT REVEALED VALVE IN CUSTOMER PIPING WAS LEAKING BEHIND OVEN.
2025-01-31 10:21 | YES | NO | 19880138 |  | 17442 | RIO GRANDE VALLEY GAS CO | 135 LINDSEY LANE | BROWNSVILLE | CAMERON | TX | 78521 | 0 | NO | 700 | 1988-03-15 | 0 | 0 | 70000 | 62766.4283 | 151547.4974 | Null | 0 | 45 |  | 19880315 | 4.2 | 24 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER | SUSPECTED ARSON | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | SUSPECTED ARSON | ROBERT J. GRANTLAND- A.V.P. DISTRICT OFC. OPERATIONS | 5125423531 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE GAS RANGE SUPPLY VALVE WAS REPORTED TO BE IN THE OPEN POSITION WITH NEITHERRANGE CONNECTOR NOR RANGE CONNECTED. TEST REVEALED 360 CFH GAS ESCAPING WITH VALVE IN OPEN POSITION. HOUSE WAS TOTALLY DEMOLISHED BY A FIRE & EXPLOSION. THERE WER NO KNOWN OCUPANTS & THE HOUSE APPEARED TO BE UNFURNISHED. POSSIBLE ARSON IS SUSPECTED. BURN DAMAGE WAS EXTENSIVE IN THE CENTE OF THE HOUSE. SERVICES WAS LOCATED WITHIN THE CITY LIMITS OF THE BROWNSVILLE DISTRIBUTION SYSTEM. METER WAS LEFT ON BY THE DISTRICT OFFICE BECAUSE THERE WAS NO DISCONNECT ORDERED ANDBILLS WERE UP TO DATE. THE ACCOUNT USED. 1.7 MCF CONSUMPTION THE PREVIOUS MONTH
2025-01-31 10:21 | YES | YES | 19880139 |  | 3170 | DAYTON POWER & LIGHT CO | 3825 E. THIRD ST. | DAYTON | MONTGOMERY | OH | 45403 | 3 | NO | 1600 | 1988-04-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19880411 | 0.3 | 1 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 |  |  | 0 | 1942 | UNDER PAVEMENT |  | R. C. ROTH , MANAGER OPERATIONS | 5132272145 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THERE WERE TWO GAS MAINS IN THE EXCAVATION. A 6" COATED LINE WAS TO HAVE ADDITIONAL ANODES INSTALLED ON IT. THE OTHER LINE, A 4" BARE WROUGHT STEEL LINE, WAS LOCATED TO THE SIDE AND APPROXIMATELY 8" BELOW THE 6" PIPE. THE CREW MEMBER DIDNOT CHECK FOR CUMBUSTIBLE GAS WITH HIS INSTRUMENT. HE STRUCK AN ARCH WITH AN IGNITOR USED TO INSTALL CADWELDS FOR ANODE INSTALLATIONS. THE GAS COMING FROM A LEAK ON THE 6" LINE IGNITED AND THE WORKER RECEIVED FIRST DEGREE BURNS ON HIS HANDS, FACE AND FOREHEAD.
2025-01-31 10:21 | NO | NO | 19880140 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 1700 BLOCK E. HWY 14 FRONTAGE ROAD | FT. COLLINS | LARIMER | CO | 80524 | 3 | NO | 1630 | 1988-04-26 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 1 |  | 19880427 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | C.C. | STEEL |  | 2 | 0.154 | API5L, GR.A-25 | N/A | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | GARY HUETT, SUPRV. OF ENGRS | 0002218542 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES |  |  | ON 4/20/88, A CONTRACTOR INSTALLING A 24" WATER LINE FOR THE CITY OF FT. COLLINS STRUCK A 2" PSC GAS LINE IN THE 1700 BLOCK ON E. HIGHWAY 14 FRONTAGE ROAD. THIS LINE HAD BEEN PREVIOUSLY INCORRECTLY LOCATED BY PSC. (DATE UNKNOWN). THE 2" GAS LINE WAS DENTED BY THE WATER LINE CONTRACTOR BY THIS 4/20/88 DAMAGE, AND IT IS SUSPECTED THAT THE PIPE WAS ALSO PARTIALLY PULLED OUT OF A 2" COMPRESSION COUPLING APPROXIMATELY 7 FEET AWAY. AT THIS SAME TIME, THE WATER LINE CONTRACTOR REQUESTED THAT THE GAS LINE BE DESTROYED SINCE IT WAS IN CONFLICT WITH THE ALIGNMENT OF THE 24" WATER LINE. ON 4/25/88, A PSC. CREW BEGAN THE RELOCATION WORK & WAS IN THE PROCESS OF COMPLETEING THIS WORK ON 4/26/88 WHEN THE 2" PIPE PULLED COMPLETELY OUT OF THE COMPRESSION COUPLING. REGULATOR STATION #H-39, LOCATED APPROX.35 FEET AWAY WAS SHUT OFF WITHIN ONE MINUTE TO STOP THE FLOW OF GAS, & SERVICE TO APPROX. 280 CUSTOMERS WAS LOST. CHARACTER OF SERVICE IN AREA IS COMMERCIAL/INDUSTRIAL AND AN 80 UNIT MOBILE HOME PARK. TWO RESTAURANTS, THE MOBILE HOME PARK, AND SOME OTHER BUSINESSES WERE RELIT THE EVENING OF 4/26/88. BUT MANY BUSINESSES WERE NOT ABLE TO BE CONTACTED UNTIL THEY OPENED THE FOLLOWING MORNING.
2025-01-31 10:21 | YES | YES | 19880141 |  | 11680 | LONE STAR GAS CO | HAYMARKET AND RYLIE ROAD | DALLAS | DALLAS | TX | 75217 | 3 | NO | 1300 | 1988-04-25 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19880425 | 36 | 55 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | VALVE |  | OTHER | PLUG VALVE | 0 | 0 |  | WALWORTH | 0 | 1987 | UNDER GROUND OR UNDER WATER |  | JAMES A. ROSS - MAINTENANCE SUPERINTENDENT | 2144267916 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA |  | EMPLOYEE FOR HAUGHT CONSTRUCTION COMPANY WAS CUTTING REINFORCEMENT RODS FROM SEWER PIPE USING A GASOLINE POWERED SAW. THERE WAS A SMALL CONCENTRATION OF NATURAL GAS THAT HAD BUILT UP IN THE STORM SEWER WHICH EXPLODED AS A RESULT FROM SPARKS CREATED FROM THE SAW THAT WAS BEING USED.THE INJURED PARTY SUFFERED MINOR BURNS TO HIS RIGHT HAND BUT WAS NOT HOSPITALIZ
2025-01-31 10:21 | YES | YES | 19880142 |  | 12390 | METROPOLITAN UTILITIES DISTRICT | 1103 SO 31ST STREET | OMAHA | DOUGLAS | NE | 68105 | 3 | NO | 725 | 1987-04-27 | 0 | 1 | 60000 | 55539.5431 | 134098.4183 | Null | 0 | 15 |  | 19870427 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE SIDE OF METER | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DONALD D. BLOCKER, CLAIMS REPRESENTATIVE | 4044498210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ORIGIN & CAUSE OF GAS ESCAPE IS UNKNOWN AT THIS TIME. PERIMETER OF HUSE, GAS SERVICE & MAINS WERE HECKED BY BAR HOCING W/FLAME IONIZATION & "CGI" MACHINES. ALL READIGS WERE NEGTIVE. BASEMENT METER SET UNDAMAGED BY FIRE OR EXPLOSION. METER SECURED, GAS SERVICE CURBED. (TO BE CUT OFF AT MAIN). ON SCENE REPORTS INDICATE VICTUM SMELLED GAS BUT PROCEDED TO LIGHT PILOT OF RANGE ON 2ND FLOOR WHEN EXPLOSION OCCURRED & WAS FOLLOWED BY FIRE.
2025-01-31 10:21 | YES | YES | 19880146 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 1245 W. ALAMEDA AVENUE | DENVER | DENVER | CO | 80223 | 3 | NO | 913 | 1988-06-01 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 30 |  |  | 15 | 15 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | AP15L,1-25 |  | 0 | 1958 | UNDER PAVEMENT |  | MICHAEL CATBAGAN, SUPERVISOR | 3035713715 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-05-03 | NO | 0 |  | YES |  |  | ON JUNE 1, 1988, GRIMM CONSTRUCTION PULLED AN 1 1/4" STEEL SERVICE OUT OF AN 1 1/4" OMPRESSION COUPLING AT THE TAP TO 1245 W. ALAMEDA AVENUE. THE CONTRACTOR WAS INSTALLLING A NEW WATER MAIN FOR THE DENVER WATER BOARD WHEN THE BACKHOE ENCOUNTERED THE STEEL WERVICE AND PULLED IT OUT OF THE COMPRESSION COUPLING . TEH LEAKING NATURAL GAS WAS THEN IGNITED BY A GASOLINE POWERED TAMPER BELONGING TO THE CONTRACTOR WHICH RESULTED IN A PSCO EMPLOYEE RECEIVING FIRST AN SECOND DEGREE BURNS AND A CONTRACTOR EMPLOYEE RECEIVING FIRST DEGREE BURN.
2025-01-31 10:21 | NO | NO | 19880147 |  | 22476 | WESTERN KENTUCKY GAS CO | 3519 FORREST CIRCLE | PADUCAH | MCCRACKEN | KY | 42301 | 3 | NO | 715 | 1988-06-02 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 25 |  | 19880602 | 20 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API SL GRA 25 | N/A | 1955 | 1955 | UNDER GROUND OR UNDER WATER |  | TOM W. HIGDON - MANAGER OF SAFETY & MAINTENANCE | 5026858057 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1955 | NO DATA |  | Null |  | Null |  |  | Null |  |  | COOROSION LEAK ON 2" MAIN IGNITED BY UNKNOWN CAUSE.
2025-01-31 10:21 | YES | NO | 19880150 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1025 ELM AVENUE | SEASIDE | MONTEREY | CA | 93955 | 3 | NO | 233 | 1988-05-18 | 0 | 0 | 70000 | 62766.4283 | 151547.4974 | YES | 0 | 37 |  | 19880518 | 0.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER-OWNED GAS RANGE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | VIRGIL G. ROSE, V.P.- GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FAULTY OPERATION OF GAS RANGE
2025-01-31 10:21 | YES | YES | 19880152 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 256 E. SHASTA | ORLAND | GLENN | CA |  | 3 | NO | 841 | 1988-03-21 | 0 | 2 | 50000 | 44833.1631 | 108248.2125 | Null | 0 | 9 |  | 19880321 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | WALL FURNACE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | INSIDE HOUSE | VIRGIL G. ROSE, V.P. -GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CHILDREN PLAYING WITH WALL FURNACE IGNITED NEWSPAPER; RESULTING FIRE SPREAD TO STRUCTURE.
2025-01-31 10:21 | YES | YES | 19880153 |  | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 4366 OLD FOREST ROAD | MEMPHIS | SHELBY | TN | 38125 | 3 | NO | 1030 | 1988-06-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 40 |  | 19880613 | 90 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D-2513 | PHILLIPS DRISCOPIPE | 1986 | 1987 | UNDER GROUND OR UNDER WATER |  | WADE STINSON, MANAGER, HICKORY HILL SERVICE CENTER | 9013673300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A CONTRACTOR, VILLAGE PLUMBING COMPANY, EXCAVATING WITH A BACKHOE TO INSTALL A SEWER LINE TO A NEW HOUSE UNDER CONSTRUCTION AT 4366 OLD FOREST RD. STRUCK AND RUPTURED A 2" POLYETHYLENE GAS MAIN. TWO EMPLOYEES OF THE PLUMBING COMPANY ENTERED THE EXCAVATION AND ATTEMPTED TO STOP THE ESCAPE OF GAS BY COVERING IT WTH DIRT. THE ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE BURNING THE TWO EMPLOYEES.ONE OF THE INJURED WAS ADMITTED TO A HOSPITAL AND THE OTHER WAS TREATED AND RELEASED. THE CONTRACTOR'S BACKHOE WAS ALSO EXTENSIVELY DAMAGED BY THE FIRE.
2025-01-31 10:21 | NO | NO | 19880154 |  | 4499 | ENTEX INC | HWY 36 & RICE ST. | ROSENBERG | FORT BEND | TX | 77471 | 3 | NO | 1530 | 1988-06-01 | 0 | 0 | 300 | 268.999 | 649.4893 | Null | 0 | 35 |  | 19880601 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | N/A | DUPONT | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | B. F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | HASSELL CONSTRUCTION WAS INSTALLING MANHOLE AND CUT 2" PLASTIC MAIN.
2025-01-31 10:21 | NO | NO | 19880155 |  | 4499 | ENTEX INC | 2436 SAWDUST ROAD | THE WOODLANDS | MONTGOMERY | TX | 77380 | 3 | NO | 830 | 1988-06-01 | 0 | 0 | 300 | 268.999 | 649.4893 | YES | 0 | 17 |  | 19880601 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | TR418 | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | B. F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-04-21 | YES | 2 |  | NO |  |  | OUTSIDE PARTY STRUCK 2" PLASTIC DISTRIBUTION MAIN WITH DOZER BLADE. GAS IGNITEE, RESULTING IN MINOR FACIAL BURNS TO BULLDOZER OPERATOR. THERE WAS NO DAMAGE TO EQUIPMENT OR PROPERTY OTHER THAN THE ACTUAL GAS MAIN BREAK. THE EQUIPMENT OPERATOR WAS TREATED IN EMERGENCY ROOM AND RELEASED.
2025-01-31 10:21 | YES | NO | 19880158 |  | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 717 E. 9TH STREET | ROCHESTER | FULTON | IN | 46975 | 3 | NO | 1220 | 1988-06-08 | 0 | 0 | 80000 | 71733.0609 | 173197.1399 | Null | 1 | 10 |  | 19880608 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION COUPLING | STEEL |  | 1.25 | 0.14 | N/A | N/A | 0 | 1955 | WITHIN/UNDER BUILDING |  | D.M. CAMPOS, MANAGER OF GAS CONTROL AND STORAGE | 2198535604 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | AN EXCAVATING CONTRACOR, WHO WAS USING A BACKHOE STRUCK AND PULLED APART THE COMPRESSION COUPLING OF THE 1 1/4 SERVICE LINE TO THE HOUSE AT 717 E. 9TH STREET CAUSING GAS TO BLOW BELOW GROUND AGAINST THE FOUNDATION. GAS ACCUMULATED WITHIN THE HOUSE AND SOMEHOW IGNITED. THE SUBSEQUENT EXPLOSION AND FIRE DESTROYED THISHOUSE. IN ADDITION, THE EXPLOSION CAUSED STRUCTURAL DAMAGE TO AN ADJACENT HOME(719 E.) AND ALSO DAMAGE TO ITS GAS METER INSTALLATION. THIS RESULTED IN GAS LEAKING AND IGNITING AND DESTROYING THIS HOUSE ALSO.
2025-01-31 10:21 | YES | YES | 19880160 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1213 LINCOLN STREET | ALAMEDA | ALAMEDA | CA | 94501 | 3 | NO | 1334 | 1988-06-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19880608 | 0.3 | 0.4 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | VALVE |  | STEEL |  | 3 | 0.216 | N/A | N/A | 0 | 1957 | UNDER GROUND OR UNDER WATER |  | V.G. ROSE, V.P. - GAS & ELEC. TECH. SERVICES | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | AT APPROXIMATELY 1334 HOURS, JUNE 8, 1988 TWO PACIFIC GAS AND ELECTRIC COMPANY EMPLOYEES WERE BURNED AS A RESULT OF GAS IGNITION IN AN EXCAVATION IN WHICH THEYWERE WORKING. THE EMPLOYEES HAD BEEN IN THE PROCESS OF CUTTING A 3" STEEL SERVICE LINE WHEN GAS BEGAN TO ESCAPE FROM THE CUT AND IGNITE. BOTH EMPLOYEES RECEIVED MINOR BURNS FROM THE RESULTING FIRE AND WERE TRANSPORTED TO A LOCAL HOSPITAL. ONE EMPLOYEE WAS TREATED AND ADMITTED FOR OBSERVATION. THE SECOND EMPLOYEE WAS TREATED AND RELEASED. OUR INVESTIGATION DISCLOSED THAT PRIOR TO CUTTING THE PIPE, THE EMPLOYEES HAD CLOSED THE SERVICE VALVE AND PURGED THE SERVICE LINE OF ALL GAS. THE SERVICE VALVE, HOWEVER, CONTINUED TO ALLOW GAS TO FLOW INTO THE LINE. THE EMPLOYEES HAD NOT INSTALLED AN ELECTRICAL BONDING WIRE ACROSS THE CUT PRIOR TO CUTTING. WHEN THE PIPE WAS CUT, GAS ESCAPED TO THE ATMOSPHERE AND WAS IGNITED. THE MOST PROBABLE SOURCE OF IGNITION IS THOUGHT TO BE STATIC ELECTRICITY
2025-01-31 10:21 | YES | YES | 19880162 |  | 12350 | MINNEGASCO INC | HWY 15 AND BARTLETT ROAD | MOUND | HENNEPIN | MN | 55364 | 3 | NO | 1220 | 1988-06-28 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19880628 | 34 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | STEEL |  | 8 | 0.025 |  |  | 0 | 1964 | OTHER |  | CHARLES W. DOANE, CLAIMS SPECIALIST | 6123425147 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE PREPARING MAIN FOR CONNECTION TO A CONTINUING MAIN AND AFTER THE TAP HAD BEEN MADE,SUDDENLY THE END OF THE TAPPED MAIN IGNITED.CONTINUED BURNING UNTIL GAS SUPPLY IN MAIN WAS TURNED OFF.
2025-01-31 10:21 | YES | YES | 19880164 |  | 3600 | DUMAS, CITY OF | 714 E. EIGHT ST. | DUMAS | MOORE | TX | 79029 | 3 | NO | 415 | 1988-04-17 | 2 | 0 | 30000 | 26899.8979 | 64948.9275 | Null | 2 | 0 |  | 19880417 | 18 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE EXPLODED | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LARRY SMITH, CITY MANAGER | 8069354102 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19880165 |  | 18104 | SAN ANTONIO CITY PUBLIC SERVICE BOARD | 722 CLARK | SAN ANTONIO | BEXAR | TX | 78210 | 3 | NO | 800 | 1988-06-24 | 0 | 0 | 140000 | 125532.8567 | 303094.9949 | Null | 0 | 40 |  | 19880624 | 7 | 33 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | SCREW | STEEL |  | 1 | 0.133 | N/A | N/A | 0 | 1965 | ABOVE GROUND |  | W.F. RIECHERT, JR. SENIOR ENGINEER | 5122273211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PICK-UP TRUCK DRIVER LOST CONTROL OF VEHICLE. HIT METER, BROKE SERVICE RISER, GAS IGNITED.
2025-01-31 10:21 | NO | NO | 19880166 |  | 4499 | ENTEX INC | PALM ROYALE BLVD & OILFIELD RD. | SUGARLAND | FORT BEND | TX | 77478 | 3 | NO | 1020 | 1988-07-08 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 27 |  | 19880708 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | DUPONT | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | B. F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DURWOOD GREEN WAS PUTTING IN NEW STREET & GOT INTO LINE WITH LIME MIXER MACHINE
2025-01-31 10:21 | NO | NO | 19880167 |  | 4499 | ENTEX INC | 5900 FM 1960 W. | HARRIS |  | TX | 77069 | 3 | NO | 1702 | 1988-05-25 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 32 |  | 19880525 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.219 | 4 PI-56 | N/A | 0 | 1957 | UNDER PAVEMENT |  | B. F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR, WHILE INSTALLING A STROM SEWER LINE, HOOKED A 2" GAS SERVICE LINEAND PULLED IT APART FROM AN 8" MAIN LINE.
2025-01-31 10:21 | NO | NO | 19880168 |  | 2432 | CITY GAS CO OF FLORIDA | 12961 S.W. 79 STREET | MIAMI | DADE | FL | 33183 | 3 | NO | 1244 | 1988-07-06 | 0 | 0 | 50000 | 44833.1631 | 108248.2125 | Null | 0 | 38 |  | 19880706 | 45 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.5 | 0 | SCHD. 40 |  | 0 | 1973 | ABOVE GROUND |  | RICHARD F. WALL, GENERAL MANAGER / OPERATIONS | 3056918710 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DRIVER OF AUTO LOST CONTROL AND HIT RISER/METER SET AND HOUSE CAUSING EXTEN. DAMAGE. CALL WAS RECEIED FROMT EH FIRE DEPARTMENT THAT A CAR HAD HIT A RISER AND FIRE WAS INVOLVED AT 12:44 P.M. OUR UNITS RESPONDED AND MADE SAFE AT 1:22 P.M. BY PINCHING AND CAPPING THE SERVICE LINE AWAY FROM THE HOUSE. THE DRIVER OF THECAR WAS UNHARMED AND NO OCCUPANTS OF THE HOUSE WERE HARMED. THE CAR WAS TOTALLY DESTROYED AND EXTENSIVE DAMAGE WAS DONT TO THE DITCHEN, GARAGE, AND ROOF OF THE HOUSE.
2025-01-31 10:21 | YES | NO | 19880172 |  | 22210 | WASHINGTON WATER POWER CO | EAST 11512 -30 SPRAGUE | SPOKANE VALLEY | SPOKANE | WA | 99206 | 3 | NO | 655 | 1988-07-20 | 0 | 0 | 100000 | 89666.3262 | 216496.4249 | Null | 0 | 20 |  | 19880721 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | GAST IRON & CAST ALUMINUM | 0 | 0 |  | FISHER | 0 | 1975 | ABOVE GROUND |  | LEN MITCHELL, GAS DISTRIBUTION ENGINEER | 5094824422 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | TRUCK BACKED INTO METER SET ASSEMBLY WHICH BROKE THE GAS SERVICE REGULATOR ANDTHE BUILDING CAUGHT ON FIRE.
2025-01-31 10:21 | YES | YES | 19880173 |  | 5110 | FAYETTEVILLE GAS SYSTEM | LOT #38 TIMBERLAKE ROAD | FAYETTEVILLE | LINCOLN | TN | 37334 | 2 | NO | 1100 | 1988-07-14 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 3 |  | 19880714 | 15 | 100 | BY TEST | 110 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | 3408SDR11 | POLY-ARK | 1988 | 1988 | ABOVE GROUND |  | KELLY PITTENGER, MANAGER | 6154334548 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | JOHNSON & JOHNSON CONSTRUCTION COMPANY EMPLOYEES, DANIEL SMITH AND DEAN HILL, WERE IN THR PORCESS OF PURGING AIR FROM A RECENTLY INSTALLED 400 FOOT SECTION OF 2 INCH POLYETHYLENE PIPE. THE EMPLOYEES HAD INSTALLED A SQUEEZE-OFF TOOL APPROXIMATELY 3 FEET FROM THE END OF THE 2 INCH EXPOSED LINE. THE POLYETHYLENE CAP WAS THEN CUT OFF OF THE LINE, AND THE SQUEEZE-OFF TOOL WAS LOSSENED TO ALLOW AIR TO BE RELEASED, SO A 100% NATURAL GAS MIXTURE COULD BE VERIFIED IN LTHE LINE. AFTER PURGING THE LINE FOR SEVERAL MINUTES, DANIEL PICKED UP THE C.G.I. (CONCENTREATED GAS INDICATOR ) AND WAS INSERTING THE BRAS PROBE ROD INTO THER END OF THE MAIN FRO THE PRUPOSE OF SAMPLING THE GAS-AIR MIXTURE. WHEN THE BRASS PROBE CA;MEINTO CONTACT WITH THE END OFTHE PIPELINE, AN APPARENT STATIC ELECTRICAL CHARGE IGNITED THE FLOWING GAS, RESULTING IN FIRST DEGREE BURNS TO DANIEL SMITH AND FIRST AND SECOND DEGREE BURNES TO DEAN HILL. THE EMPLOYEES ROLLED IN THE GRASS TO PUT OUT ANY FIRE THAT COULD POSSIBLY BE BURNING ON THEIR CLOTHING. AFTER THEYWERE SURE NO FIRE WAS ON THEM, THEY WENT BACK WHERE THE GAS WAS BURNING AND SQUEEZED THE PIPE SHUT, USING THE SQUEEZE-OFF TOOL WHICH WASALREADY ONTHE PIEPLINE. THE FAMES WENT OUT IMMEDIATELY. DANIEL THEN TOLD DEAN TO GET IN THE TRUCK, AND HEDROVE THEM TO THE LINCOLN REGIONAL HOSPITAL. THE TWO INJURED EMPLOYEES WERE RELEASED FROM THE HOSPITAL THE FOLLOWING DAY.
2025-01-31 10:21 | YES | NO | 19880174 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 2313 S. PRAIRIE AVENUE | PUEBLO | PUEBLO | CO | 81005 | 0 | NO | 745 | 1988-06-24 | 0 | 0 | 200000 | 179332.6524 | 432992.8498 | Null | 4 | 0 |  | 19880627 | 8 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | JOINT | NIPPLE | STEEL |  | 1 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | MICHAEL L. PETERSON, OPERATIONS MANAGER, PUEBLO | 0005426110 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | NATURAL GAS FROM BROKEN SERVICE APPARENTLY MIGRATED THROUGH SOIL AND INTO BUILDING THROUGH CRACKED CONCRETE SLAB FLOOR. THE SOURCE OF IGNITION IS UNKNOWN AT THIS TIME.
2025-01-31 10:21 | YES | YES | 19880175 |  | 2596 | COLUMBIA GAS OF OHIO INC | 8590 ELMFORD AVENUE | WAYNESBURG GROVE | STARK | OH | 44688 | 3 | NO | 1843 | 1988-07-09 | 1 | 0 | 35000 | 31383.2142 | 75773.7487 | Null | 0 | 32 |  | 19880709 | 38 | 38 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.119 | N/A | N/A | 0 | 1983 | UNDER GROUND OR UNDER WATER |  | ROBERT CLEVENGER | 6144328243 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | OBJECT IN BACKFILL | NO |  | NO | 0 |  | NO |  |  | SHARP METAL OBJECT WHICH WAS BURIED IN THE BACKFILL OF CUSTOMER OWNED SERVICE LINE PENETRATED 1" P.E. PIPE WALL OVER A PERIOD OF TIME FROM ORIGINAL INSTALLATION DATE FORCE CAUSING PENETRATION UNDETERMINED. CUSTOMER OWNED SERVICE LINE HAD BEEN TESTED AT 90 PSIG., 7-15-87 WITH NO LOSS OF PRESSURE.
2025-01-31 10:21 | YES | YES | 19880176 |  | 4473 | ENERGAS CO | 304 OAK STREET | PANHANDLE | CARSON | TX | 79068 | 3 | NO | 615 | 1988-06-22 | 0 | 1 | 85000 | 76216.3773 | 184021.9612 | Null | 0 | 30 |  | 19880622 | 0.5 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER LINE | OTHER | N/A | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. , DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE; OCCUPANT HAS 2ND/3RD DEGREE BURNS.
2025-01-31 10:21 | NO | NO | 19880177 |  | 4473 | ENERGAS CO | 216 WEST VIRGINIA | FLOYDADA | FLOYD | TX | 79235 | 3 | NO | 2245 | 1988-07-16 | 0 | 0 | 20000 | 17933.2652 | 43299.285 | Null | 0 | 15 |  | 19880716 | 7 | 16 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414411 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PERCY EDWARDS, ENERGAS MANAGER AT FLOYDADA, RECEIVED A CALL FROM THE SHERIFF'S DEPARTMENT ABOUT AN EXPLOSION AT 216 WEST VIRGINIA. WHEN HE AND A SERVICEMAN ARRIVED AT THIS ADDRESS, AT 11:00 PM, THE GAS METER HAD ALREADY BEEN TURNED OFF.THE EXPLOSION HAD OCCURED AT THIS ADDRESS IN THE HOUSE OF ALLEN ROY AT APPROXIMAELY 10:45 PM. NO ONE WAS HOME AT THE TIME; THEY HAD GONE TO LUBBOCK AROUND NOON.THE HOUSE WAS EXTENSIVELY DAMAGED BY THE EXPLOSION AND SUBSEQUENT SPOT FIRES.ENERGAS CO MADE A LEAK SURVEY OF ADJACENT MAINS ON MONDAY, JULY 18TH; NO LEAKS WERE FOUND. THE FIRE DEPARTMENT MADE FURTHER INVESTIGATION DURING DAY LIGHT AND REACHED THE CONCLUSION THAT LEAKS OCCURED ON CUSTOMER PIPING AND CAUSED THE EXPLOSION. PERCY EDWARDS IN DISCUSSION WITH THE FIRE DEPARTMENT BELIEIVES THAT THE GAS VALVE BEHIND THE RANGE CAME APART.OUR RECORDS INDICATE THAT GAS CONSUMPTION FOR THE MONTH PRIOR TO JUNE 20TH WAS 3MCF. THE METER READING AT TIME OF THE EXPLOSION SHOWED 13 MCF HAD REGISTERED SINCE JUNE 20TH.
2025-01-31 10:21 | NO | NO | 19880178 |  | 18532 | SOUTHERN UNION GAS CO | 7109 COOPER LANE (AT MATTHEWS LANE) | AUSTIN | TRAVIS | TX | 78751 | 3 | NO | 630 | 1988-07-07 | 0 | 0 | 1 | 0.89666 | 2.165 | Null | 2 | 47 |  | 19880707 | 34 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L-B | N/A | 0 | 1963 | UNDER PAVEMENT |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | YES | 1988-06-14 | YES | 3 | PAINT ON ALPHALT | NO |  |  | SOUTHERN UNION GAS COMPANY LINE LOCATING PERSONNEL HAD RESPONDED TO CONTRACTOR'SREQUEST TO MARK GAS FACILITIES ON JUNE 15, 1988. MARK WAS PLACED ON PAVEMENT 4'1" FROM DAMAGE SITE.
2025-01-31 10:21 | NO | NO | 19880179 |  | 18532 | SOUTHERN UNION GAS CO | EXPOSITION BLVD. @ CHERRY LANE | AUSTIN | TRAVIS | TX | 78703 | 3 | NO | 350 | 1988-07-13 | 0 | 0 | 1000 | 896.6633 | 2164.9642 | YES | 2 | 15 |  | 19880713 | 38 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.33 | N/A | N/A | 1939 | 1942 | UNDER PAVEMENT |  | B. R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SWELLING OF CLAY SOIL | NO |  | NO | 0 |  | NO |  |  | SWELLING OF CLAY SOIL BENEATH THE PIPE PUSHING UPWARD CAUSED STRESS FRACTURE.
2025-01-31 10:21 | NO | NO | 19880181 |  | 18532 | SOUTHERN UNION GAS CO | 13540 RESEARCH BLVD. | AUSTIN | TRAVIS | TX |  | 3 | NO | 1102 | 1988-06-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 28 |  | 19880617 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 2 | 0.125 | API-5L-A25 | N/A | 0 | 1986 | ABOVE GROUND |  | B. R. KNOX, RIGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | DELIVERY TRUCK BACKED OVER COMMERCIAL METER SET - CRACKING THE BIPASS LINE AND THE METER CASE.
2025-01-31 10:21 | YES | YES | 19880182 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 1291 JEWET AVENUE | PITTSBURG | CONTRA COSTA | CA | 97565 | 3 | NO | 1512 | 1988-05-26 | 0 | 1 | 4900 | 4393.65 | 10608.3248 | Null | 0 | 43 |  | 19880526 | 0.3 | 0.4 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | HOUSELINE | DRIP/RISER | WATER HEATER (TAMPERED) | OTHER | FLEX-LINE | 0 | 0 |  |  | 0 | 0 | OTHER | INSIDE HOUSE | VIRGIL G. ROSE, V.P.- GAS & ELEC. TECH. SERVICES | 4159736998 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ATTEMPTED SUICIDE INVOLVING THE ACCUMULATION OF NATURAL GAS IN THE ABOVE STRUCTURE RESULTED IN AN EXPLOSION. THIS INTENTIONAL RELEASE OF GAS ORIGINATED ON THECUSTOMER'S HOUSELINE. NEARBRY BUILDINGS WERE EVACUATED AS A PRECAUTION.
2025-01-31 10:21 | YES | YES | 19880183 |  | 15469 | PHILADELPHIA GAS WORKS | 2461 SEPVIVA STREET | PHILADELPHIA | PHILADELPHIA | PA | 19125 | 4 | NO | 2255 | 1988-06-27 | 2 | 4 | 75000 | 67249.7446 | 162372.3187 | Null | 1 | 12 |  | 19880628 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | 3/4" PLUG IN BASEMENT | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LEROY C. SHCHLAGEL, MANAGER DISTRIBUTION DEPARTMENT | 2156846372 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A RESIDENT OF 2461 SEPVIVA STREET IDENTIFIED AS MR. RICHARD LITOSTANSKY, ALLEGEDLY DESPONDENT OVER MARITAL PROBLEMS, CALLED POLICE TO HIS HOME AND WHEN THEY ARRIVED ON THE SCENE, HE WENT TO THE BASEMENT OF 2461 SEPVIVA AND REMOVED A 3/4/" ACREW PLUG FROM 1 1/4" X 3/4/" X 1" HOUSE TEE ATTACHED TO 1 1/4" LOW PRESURE GASSERVICE AT THE FRONT FOUNDATION WALL ALLOWING NATURAL GAS TO ESCAPE INTO THE BASEMENT WHICH HE ALLEGEDLY IGNITED CAUSING AN EXPLOSION AND FIRE. THIS ALOS RESULTED IN TWO FATALITIES (MR. LITOSTANSKY AND A NEIGHBOR, BERNARD FINK) AND FOUR PERSONS WERE HOSPITALIZED. THIS INCIDENT IS CURRENTLY UNDER INVESTIGATION BY THECITY OF PHILADELPHIA FIRE DEPARTMENT UNDER THE DIRECTION OF THE FIRE MARSHAL.
2025-01-31 10:21 | YES | YES | 19880184 |  | 11920 | LYNCHBURG GAS CO | EAST SPENCER RD. | HURT |  | VA |  | 2 | NO | 945 | 1988-07-19 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19880719 | 26 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2306 | PLEXCO | 1988 | 1988 | ABOVE GROUND |  | DOUGLAS WILSON, V.P. | 8048477722 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | THE NEW PLASTIC GAS PIPELINE TO ENGLISH'S SUBDIVISION IN HURT, VA. HAD BEEN COMPLETED. OUR CONTRACTOR, FALWELL CORP., HAD LOADED SOME GAS TO THE LINE IN PREPARATION TO PURGE THE LINE OF AIR. JEFF MYERS (CONTRACTOR) AND ROBERT STONE (LYNCHBURG GAS) WENT TO THE END OF THE 4" MAIN (LOCATION # 1) AND REMOVED THE END CAP, OPENED THE 4" VALVE AND PURGED THAT PART OF THE MAIN. NEXT THAY WENT TO THE END OF THE 2" MAIN ON EAST SPENCER RD(LOCATION # 2). JOHN GOWEN AND KENNY (CONTRACTORS) HAS INSTALLED A SQUEEZE-OFF TOOL ON THE 2" PIPE, REMOVED THE ENF CAP AND PURGED THE LINE. THEY CLOSED DOWN ON THE SQEUEEZE-OFF TOOL AND BEGAN PREPARATIONS TOBUTT FUSE THE PIPE BACK TOGETHER. THE END OF THE 2" PLASTIC GAS LINE AND THE PIPE WITH THE END CAP WERE PLACED IN THE BUTT FUSION MACHINE. THE BUTT FUSION MACHINE. THE BUTT FUSION MACHINE WAS ABOVE GROUND, NOT IN THE DITCH. THE ELECTRIC GENERATOR, LOCATED APPROXIMATELY 15 FEET FROM THE PIPE, WAS STARTED TO FURNISH POWER TO RUN THE BUTT FUSION MACHINE. THE PIPE WAS TRIMMED AND TRIED FOR PROPER FIT.WHEN THE PIPE WAS PULLED APART, SOME GAS WAS DETECTED. JEFF MYERS WENT TO ADJUSTTHE SQUEEZE-OFF TOOL TO GET A BETTER SEAL (THE TIME WAS APPROXIMATELY 9:45AM). JEFF LOOSENED THE SQUEEZE-OFF TOOL SLIGHTLY AND TIGHTENED IT BACK DOWN AFTER ADJUSTING. AT THIS TIME THERE WAS A FLASH AT THE END OF THE PIPE. ONE OF THE CONTRACTOR'S MEN, JOHN GOWEN, WAS BURNED BY THE RESULTING FLASH. ROBERT STONE IMMEDIATELY WENT TO THE REGULATOR (LOCATION # 3) AND TURNED OFF THE GAS SUPPLY. AT THE SAME TIME, JEFF MYERS HAD THE LADY ACROSS THE STREET CALL THE ALTAVISTA LIFE SAVING CREW. ON RETURNING TO THE SITE OF THE INCIDENT, ROBERT STONE MET GARY RICE OFTHE HURT WATER DEPARTMENT. THE END OF THE PLASTIC PIPE WAS STILL BURNING AND ALSO THE WHEELS ON THE BUTT FUSING MACHINE. MR RICE USED A FIRE EXTINGUISHER AND EXTINGUISHED THE FIRES. AT 10:20 AM, ROBERT STONE REPORTED THE INCIDENT TO THE MAIN OFFICE OF THE LYNCHBURG GAS CO. VERLA LAYNE, CHIEF DISPATCHER, RECEIVED THE REPORT FROM ROBERT STONE. AT 12:45PM, DAVID CARTER OF LYNCHBURG GAS MADE A TELEPHONE REPORT TO RYLAND BAILEY OF THE VIRGINIA STATE CORP COMM. A TELEPHONE REPORT WAS MADE BY MR CARTER AT 12:53 PM TO THE DEPARTMENT OF TRANSPORTATION.IT WAS LATER LEARNED THAT MR GOWEN, THE INJURED PERSON HAD RECEIVED FIRST DEGREEBURNS OF THE ARMS. AT 4:00 PM ON THE SAME DAY, JANES HOTTINGER OF THE VIRGINIAS.C.C. ARRIVED IN LYNCHBURG TO INVESTIGATE THE INCIDENT. MR CARTER AND MR HOTTINGER WENT TO MR HURT, WHICH IS APPROXIMATELY 30 MILES SOUTH OF LYNCHBURG, TO MEETROBERT STONE. AN INVESTIGATION WAS CONDUCTED AT THIS TIME. THE INVESTIGATION REVEALED THAT THE SPARK-PLUG WIRE ON THE ELECTRIC GENERATOR WAS NOT FIRMLY ATTACHEDTO THE SPARK-PLUG. THE SPARK-PLUG WOULD ARC WHEN THE GENERATOR WAS RUNNING. THEAPPARENT SOURCE OF IGNITION WAS THIS ARCING.JOHN GOWEN WAS RELEASED FROM THE HOSPITAL ON JULY 25, 1988, WITH COMPLETE RECOVERY EXPECTED. JOHN SHOULD RETURN TO WORK IN SIX TO EIGHT WEEKS.
2025-01-31 10:21 | NO | NO | 19880185 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 1243 WEST 101ST STREET | LOS ANGELES | LOS ANGELES | CA | 90044 | 3 | NO | 1730 | 1988-07-31 | 0 | 0 | 40000 | 35866.5305 | 86598.57 | Null | 0 | 10 |  | 19880801 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | APISTD5L | N/A | 0 | 1973 | WITHIN/UNDER BUILDING |  | L.M. STEWART-MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE INCIDENT OCCURRED ON JULY 31, 1988 AT 1243 WEST 101ST STREET, LOS ANGELES,LOS ANGELES COUNTY. DUE TO EXTENSIVE DAMAGE TO A HOUSE RESULTING FROM AN EXPLOSION, A TELEPHONIC REPORT WAS MADE TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION. A 3/4 INCH THREADED FITTING INTO A PIPE ELBOW, BETWEEN THE SERVICE RISER VALVE AND THE METER SET ASSEMBLY, WAS BROKEN BY EXTERNAL FORCES. ESCAPING GAS EXPLODED, POSSIBLY IGNITED BY A WATER HEATER, CAUSING EXTENSIVE DAMAGE TO THE STRUCTURE. THE FACILITY WAS NOT SUBJECT TO BEING HIT BY VEHICULAR TRAFFIC, FIELD INVESTIGATION COULD NOT IDENTIFY THE CAUSE; HOWEVER, THE POSSIBILITY THAT CHILDREN HAD BEEN JUMPING ON THE METER SET WAS INDICATED. THERE WERE NO INJURIES. DAMAGETO THE STRUCTURE WAS ESTIMATED TO BE $40,000.
2025-01-31 10:21 | NO | NO | 19880186 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | MATIE ROAD &SPYGLASS DRIVE | PISMO BEACH | SAN LUIS OBISPO | CA | 93449 | 3 | NO | 1345 | 1988-08-01 | 0 | 0 | 12850 | 11522.1229 | 27819.7906 | Null | 0 | 40 |  | 19880801 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM-D2513 | DUPONT | 1987 | 1988 | UNDER GROUND OR UNDER WATER |  | L.M. STEWART-MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THE INCIDENT THAT OCCURRED ON AUGUST 1, 1988, AT THE INTERSECTION OF MATIE ROADAND SPYGLASS DRIVE, PISMO BEACH, SAN LUIS OBISPO COUNTY. DUE TO EXTENSIVE DAMAGE TO THE EQUIPMENT OF A THIRD PARTY OPERATOR,A TELEPHONIC REPORT WAS MADE TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION. THE SOUTH COAST BUILDERS COMPANY, EXCAVATING WITH A TRENCHER TO INSTALL A SPRINKLER SYSTEM, STRUCK AND DAMAGED A TWO INCH PLASTIC MAIN, ALLOWING GAS TO ESCAPE AND IGNITE. GAS WAS CONTROLLED BY PINCHING THE PLASTIC MAIN AND REPAIR WAS MADE BY REPLACING THREE FEET OF PIPE. DAMAGE TO SOUTHERN CALIFORNIA GAS COMPANY FACILITIES WAS $850 AND $12,000 TO THE CONTRACTOR'S TRENCHER. THERE WERE NO INJURIES AND NO CUSTOMER OUTAGES. IT WAS NECESSARY TO TEMPORARILY REROUTE TRAFFIC ON MATIE ROAD.
2025-01-31 10:21 | NO | NO | 19880187 |  | 18532 | SOUTHERN UNION GAS CO | 2405 WILLOW STREET | AUSTIN | TRAVIS | TX | 78751 | 3 | NO | 2037 | 1988-07-01 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 23 |  | 19880701 | 0.3 | 0.5 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | N/A | N/A | 0 | 1945 | UNDER PAVEMENT |  | B. R. KNOX REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-11-12 | YES | 0 |  | NO |  |  | CONTRACTOR DAMAGED SERVICE LINE WHILE BACKFILLING A DITCH THAT WAS CUT TO FACILITATE THE INSTALLATION OF A 66" WATER TRANSMISSION MAIN.HE BUILDING WAS OF DOUBLE BRICK WALL CONSTRUCTION WITH WOOD RAFTERS AND SHEETING, AND ASPHALT ROOF. THE BUILDING FIRE DAMAGED INSTRUMENT LINES AND FITTINGS ENTERING THE SOUTH GABLE, CAUSING GAS TO ESCAPE FROM THESE LINE AND FUELING THE FIRE. THE HEAT FROM THE BLAZE EXPANDED THE FLANGE BOLTS IN THE REGULATOR RUNS AND DESTROYED THE GASKET MATERIAL, ALLOWING MORE GAS TO ESCAPE AND FUEL THE FIRE FURTHER. ULTIMATELY, A 6" WELDED ELBOW ON AN INLET STUB RUPTURED, BLOWING OUT THE SOUTH WALL OF THE BUILDING AND GREATLY INTENSIFYING THE FIRE. FLAME AND HEAT FROM THE REGULATOR STATION FIRE WERE DIRECTED TOWARD METERING FACILITIES OWNED AND OPERATED BY TEXAS GAS TRANSMISSION CORP (TGT), CAUSING A 10" RISER TO FAIL AND RUPTURE. THE HEAT FROM THE METER STATION FIRE CAUSED AN 8" RUN-AROUND PIPE ON A TGTBLOCK VALVE TO FAIL AND ALLOW ADDITIONAL GAS TO ESCAPE. THE CONFLAGRATION COMPLETELY DESTROYED THE STATION'S METERING AND REGULATING FACILITIES AND ASSOCIATED INSTRUMENTATION EQUIPMENT. THERE WERE NO INJURIES OR FATALITIES.
2025-01-31 10:21 | YES | YES | 19880188 |  | 17570 | ROCHESTER GAS & ELECTRIC CORP | 105 JERSEY STREET | ROCHESTER | MONROE | NY | 14609 | 4 | NO | 1050 | 1988-08-01 | 1 | 3 | 300000 | 268998.9785 | 649489.2748 | Null | 0 | 59 |  |  | 3 | 3 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | CAP REMOVED | OTHER | BLACK IRON | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT C. NESBITT- UTILIZATION ENGINEER | 7167248464 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GENTLEMAN AT 105 JERSEY ST. CALLED HIS GIRLFRIEND AT KODAK WHERE SHE WORKED ANDSAID HE WAS GOING TO COMMIT SUICIDE. SHE CALLED KODAK SECURITY WHO THEN CALLED911. THE POLICE AND FIRE DEPARTMENTS RESPONDED AND THE FIRE DISPATCHER NOTIFIED R.G.&E. ALL OF THE ABOVE WERE AT THE SCENE WHEN THE EXPLOSION OCCURRED. THE POLICEMAN AND FIREMEN WERE AT THE DOOR, THE MAN TOLD THEM TO GET BACK BECAUSE HEWAS GOING TO BLOW UP THE HOUSE AND HE LIT A MATCH. AN EXPLOSION RESULTED WHICHDESTROYED THE HOUSE AND THE RESULTING FIRE DESTROYED THE TWO ADJACENT HOUSES. WINDOWS IN OTHER BUILDINGS WERE BROKEN. SUBSEQUENT INVESTIGATION REVEALED THE ONE INCH CAP HAD BEEN REMOVED FROM THE TEE IN THE BASEMENT WHICH IS AHEAD OF THE STOPCOCK AND THE SERVICE REGULATOR. THE FIRE DEPARTMENT INVESTIGATION REVEALED GASOLINE HAD BEEN POURED IN THE HOUSE AND TWO ACETELYNE TANKS AND ONE OXYGEN TANK WEE IN THE HOUSE AND APPEARED TO BE LEAKING. NO TELEPHONIC NOTIFICATION WAS MADE BECAUSE IT WAS A KNOWN SUICIDE ATTEMPT AND NO GAS FACILITIES FAILED.
2025-01-31 10:21 | YES | YES | 19880189 |  | 20211 | UNITED CITIES GAS CO | ROUTE 11 | DUBLIN | PULASKI | VA | 24084 | 2 | NO | 1200 | 1988-07-22 | 0 | 1 | 10000 | 8966.6326 | 21649.6425 | YES | 1 | 15 |  | 19880722 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE-2306 | EXTRON | 1968 | 1968 | WITHIN/UNDER BUILDING |  | ROBERT M. ELAM, DIVISION VICE PRESIDENT OF OPERATIONS | 6159267172 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER
2025-01-31 10:21 | NO | NO | 19880190 |  | 4473 | ENERGAS CO | FM 1936 AND WEST 10TH STREET | ODESSA | ECTOR | TX | 79764 | 3 | NO | 1750 | 1988-07-22 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19880722 | 10 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | DISTRICT REGUALTOR STA. | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | ARL F. BAILEY, P.E. | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE SERVICING DISTRICT REGULATOR STATION MAINTENANCE MAN INADVERTENTLY LEFT VALVE CLOSED RESULTING IN OUTAGE.
2025-01-31 10:21 | YES | NO | 19880192 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 732 26TH STREET | OAKLAND | ALAMEDA | CA |  | 3 | NO | 1608 | 1988-07-15 | 0 | 0 | 85000 | 76216.3773 | 184021.9612 | Null | 0 | 37 |  | 19880715 | 15 | 15 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | OTHER | ALUMINUM | 0 | 0 | 1A ALUMINUM | ROCKWELL | 0 | 1977 | ABOVE GROUND |  | VIRGIL G. ROSE, V.P. - GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | FIRE BEGAN IN A PILE OF CARDBOARD BOXES NEAR THE METER SET. THE HOUSE IGNITED, WHICH THEN IGNITED THE METER SET.
2025-01-31 10:21 | YES | YES | 19880193 |  | 11192 | LANCASTER COUNTY NATURAL GAS AUTH | HWY 341 3 MILES SOUTH OF KERSHAW, SC | KERSHAW | LANCASTER | SC | 29067 | 1 | NO | 1030 | 1988-07-21 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 20 |  | 19880725 | 19 | 50 | BY TEST | 75 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | WRONG FITTING | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | OTHER | CONNECTION HOLE | TROY C. ELMORE, MANAGER | 8032852045 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THEY HAD PUT A 2" X 1/2 IPS PLASTIC SADDLE ON 2" PLASTIC LINE. WHEN THEY HAD FOUND OUT IT WAS WRONG, THEY WERE GOING TO REPLACE IT WITH A 2" X 5/8" PLASTIC SADDLE. DURING THIS CHANGEOVER, SOMETHING CAUSED A FLASH FIRE AND BURNED THESE TWO MEN. THE FLASH LASTED FOR ONLY A SECOND OR LESS.
2025-01-31 10:21 | YES | YES | 19880194 |  | 22798 | WISCONSIN SOUTHERN GAS CO INC | 130 S. MARINO DRIVE | DELAVAN | WALWORTH | WI | 53115 | 3 | NO | 1700 | 1988-08-01 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 15 |  | 19880801 | 0.3 | 2.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | BUILT IN RANGE TOP UNIT | OTHER | FLEXIBLE METAL | OTHER | CORRUGATED COPPER/BRASS | 0.75 | 0 | 965-55-6M | COBRA METAL HOSE INC. | 0 | 1963 | WITHIN/UNDER BUILDING |  | ROBERT A. MEYERHOFER SAFETY & LOSS CONTROL MGR. | 4142488861 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE BRAZING/SOLDERING THAT CONNECTED AN END FITTING TO THE TUBING DETERIORATED AND THE FITTING SEPERATED FROM THE TUBING.
2025-01-31 10:21 | NO | NO | 19880195 |  | 5230 | FLEMINGSBURG UTILITIES SYSTEM | BETWEEN WEST WATER ST. + MILLS AVE. | FLEMINGSBURG | FLEMING | KY | 41041 | 0 | NO | 1340 | 1988-07-25 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19880725 | 22 | 28 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.125 | N/A | N/A | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | ROBERT L. HITT, SUPT OF UTILITIES | 6068456862 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS LINE NOT MARKED ON CONSTRUCTION MAP. CONTRACTORS DID NOT KNOW GAS LINE WASTHERE.
2025-01-31 10:21 | YES | YES | 19880196 |  | 15350 | PEOPLES NATURAL GAS CO | INTERSECTION BEECH RD.-CENTER NEW TEXAS | PITTSBURGH | ALLEGHENY | PA | 15239 | 3 | NO | 940 | 1988-08-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 50 |  | 19880802 | 35 | 35 | BY TEST | 110 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0.216 | ASTML-2513 | PLEXCO | 0 | 1979 | ABOVE GROUND |  | D.T. AMBLOD, GENERAL MANAGER, OPERATING SERVICES | 4125536657 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | A PIPELINE CONSTRUCTION CREW WAS TIEING-IN A NEWLY LAID PLASTIC LINE T THE EXISTING DISTRIBUTION SYSTEM USING A 2-INCH HIGH VOLUME TAPPING TEE. THE EXISTING LINE, ALSO PLASTIC, WAS OPERATING AT 35 PSIG. THE CREW, USING A MCELROY SIDEWINDER, WAS IN THE PROCESS OF HEAT FUSING TAPPING TEE TO THE TOP OF THE PIPELINE WHEN THE LINE RUPTURED UNDER THE TEE SENDING GAS THROUGH THE TAPPING TEE TO ATMOSPHERE. THE GAS IGNITED ALMOST IMMEDIATELY FROM AN UNKNOWN SOURCE OF IGNITION. ONE CREW MEMBER RECEIVED FIRST AND SECOND DEGREE BURNS OF BOTH ARMS AND REQUIRED HOSPITALIZATION.
2025-01-31 10:21 | NO | NO | 19880198 |  | 4473 | ENERGAS CO | PLANTATION FARMS-RURAL SYSTEM | AMARILLO | RANDALL | TX | 79118 | 3 | NO | 1045 | 1988-08-12 | 0 | 0 | 1000 | 896.6633 | 2164.9642 | Null | 0 | 30 |  | 19880812 | 0 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 2 | 0.91 | 1120 TYPE 1 | N/A | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A SOUTHWESTERN PUBLIC SERVICE COMPANY CREW WAS INSTALLING A CUSTOMER SERVICE LINE DROP. THE LOCATION OF THEIR NEW POLE WAS IN A PUBLIC UTILITY EASEMENT WHERE AN ENERGAS MAIN WAS LOCATED. THEY DRILLED A HOLE IN THE MAIN. 42 CUSTOMERS WERE OUT OF GAS SERVICE.
2025-01-31 10:21 | YES | NO | 19880199 |  | 2748 | CONSUMERS POWER CO | 1565 NORTH WOODWARD AVENUE | BLOOMFIELD HILLS | OAKLAND | MI | 48013 | 3 | NO | 1151 | 1988-08-06 | 0 | 0 | 672000 | 602557.712 | 1454855.9755 | Null | 1 | 4 |  | 19880806 | 30 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0 | 0 | N/A | FLAGG FITTING | 0 | 1950 | UNDER GROUND OR UNDER WATER |  | P.D. MILLER, MANAGER OF GAS OPERATIONS | 5177882250 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-08-02 | YES | 2 |  | YES |  |  | AN EXPLOSION AND FIRE OCCURRED AT AN ABANDONED BUILDING DUE TO A THIRD PARTY DAMAGE. AN EXCAVATING CONTRACTOR HIT AND DAMAGED A 3/4" STEEL GAS SERVICE WITH A BACKHOE BUCKET. THE GAS SERVICE BROKE AT A 3/4" STEEL STREET ELBOW LOCATED INSIDE THE BUILDING ALLOWING GAS TO ENTER THE BUILDING. THE FIRE SPREAD TO ANOTHER BUILDING CAUSING EXTENSIVE PROPERTY DAMAGE. THE GAS FACILITIES WERE NOT HAND EXPOSED BY CONTRACTOR.
2025-01-31 10:21 | YES | YES | 19880202 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 6741 STOCKTON BOULEVARD, NO. 8 | SACRAMENTO | SACRAMENTO | CA |  | 3 | NO | 920 | 1988-07-14 | 0 | 1 | 50000 | 44833.1631 | 108248.2125 | Null | 0 | 8 |  | 19880714 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER EQUIPMENT | NO DATA |  | NO DATA |  | 0 | 0 | N/A |  | 0 | 0 | WITHIN/UNDER BUILDING |  | VIRGIL G. ROSE, V.P.-GAS & ELEC. SVS. | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ATTEMPTED SUIDICE BY THIRD PARTY OCCUPANT OF UNIT #8. EXTINGUISHED PILOTS ON GAS RANGE ALLOWING GAS TO ACCUMULATE IN THE APARTMENT. THE OCCUPANT IGNITED GAS WITH A CIGARETTE LIGHTER CAUSING STRUCTURAL DAMAGE TO THE BUILDING.
2025-01-31 10:21 | NO | NO | 19880204 |  | 12762 | MORAN UTILITIES CO | #12 HAWTHORNE DR. | WILLIS | MONTGOMERY | TX | 77378 | 3 | NO | 1710 | 1988-08-05 | 0 | 0 | 3000 | 2689.9898 | 6494.8927 | Null | 1 | 30 |  |  | 10 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0 | PE2306 | PLEXCO | 1972 | 1972 | UNDER GROUND OR UNDER WATER |  | R.D. KELLDORF, VICE-PRESIDENT | 4097564431 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR WAS INSTALLING WATER LINE AT #12 HAWTHORNE DRIVE WITH A SMALL WALK BEHIND TRENCHER AND CUT A TWO INCH POLY GAS MAIN. GAS IGNITED, OPEATOR REFUSE TREATMENT FOR 1ST DEGREE BURNS ON ARM AND FACE OFFERED BY FIRE DEPARTMENT. FIRE DESTROYED TRENCHER BUT WAS NO DANGER TO OTHER PROPERTY OR DWELLINGS. GAS LINE HAD 2-WAY FEED AND WAS DUG UP AND SQUEEZED OFF ON EACH SIDE OF DAMAGE. MORAN HAD TO WAIT ON OTHER UTILITIES TO LOCATE LINES BEFORE EXPOSING GAS LINE. DAMAGED SECTION WAS THEN CUT OUT AND A NEW SECTION WAS FUSED IN. NO GAS CUSTOMERS WERE TURNED OFF.
2025-01-31 10:21 | YES | NO | 19880205 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 495 W. MAIN | VANDERBUILT | OTSEGO | MI | 49795 | 3 | NO | 723 | 1988-08-16 | 0 | 0 | 60000 | 53799.7957 | 129897.855 | Null | 0 | 31 |  | 19880816 | 58 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 | AL-250 | AMERICAN | 0 | 1965 | ABOVE GROUND |  | BRUCE J. NIEMAN, MANAGER CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | LIGHTNING STRUCK DWELLING AND CAUSED A FAILURE AT AN OUTSIDE HARDCASE METER. LEAKING GAS THEN IGNITED. A TWO STORY DWELLING AND CONTENTS WERE DESTROYED.
2025-01-31 10:21 | NO | NO | 19880209 |  | 18532 | SOUTHERN UNION GAS CO | 107 W. 3D STREET | WINSLOW | NAVAJO | AZ | 86047 | 0 | NO | 1249 | 1988-09-26 | 0 | 0 | 5000 | 4483.3163 | 10824.8212 | YES | 0 | 20 |  | 19880926 | 45 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | 1" LINE PLUG | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | ROBERT L ERNEST - MANAGER | 6022893386 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NORTHERN PIPELINE CONSTRUCTION CREW WAS WELDING A 12" X 1" EXTENSION. TOP OF RISER HAD BEEN BENT IN PREVIOUS ACCIDENT AND NORTHERN PIPELINE WAS HIRED TO REPAIR IT. A LEAVE-IN 1" LINE PLUG WAS PUT IN AND THE DAMAGED RISER WAS CUT - WHILE WELDING, THE PLUG BLEW OUT AND GAS IGNITED. FLAME BURNT SEVERAL ELECTRICAL METERS, TELEPHONE LINES AND ELECTRICAL LINES TO BUILDING. THE WELDER RECEIVED 2ND DEGREE BURNS ON RIGHT ARM. HE WAS TREATED AND RELEASED FROM THE EMERGENCY ROOM TO RETURN TO WORK AT 3:00 PM. THE SAME DAY.
2025-01-31 10:21 | YES | NO | 19880210 |  | 2748 | CONSUMERS POWER CO | 2979 SAND0VAL | LAKE ORION | OAKLAND | MI | 48035 | 3 | NO | 39 | 1988-09-23 | 0 | 0 | 95000 | 85183.0099 | 205671.6037 | Null | 1 | 36 |  | 19880923 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.062 | ASTM 2513 | PHILLIPS | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | P.D. MILLER, MANAGER OF GAS OPERATIONS | 5177882250 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | LIGHTNING HIT PLASTIC GAS SERVICE LOCATING WIRE CAUSING GAS LEAK. DAMAGE TO SINGLE FAMILY DWELLING DUE TO FIRE FROM LIGHTNING STRIKE AND LOW LEVEL EXPLOSION.
2025-01-31 10:21 | NO | NO | 19880212 |  | 4499 | ENTEX INC | 6100 DIXIE DR. | HOUSTON | HARRIS | TX |  | 3 | NO | 1443 | 1988-09-10 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 52 |  | 19880910 | 60 | 0 | BY TEST | 275 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 18 | 0.281 | API5LX | N/A | 0 | 1973 | UNDER GROUND OR UNDER WATER |  | B F BROYLES - DIRECTOR OF OPERATIONS | 7136545137 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1973 | NO DATA |  | Null |  | Null |  |  | Null |  |  | PASSING TRAIN CAUSED SPARKS WHICH STARTED A SMALL GRASS FIRE. GRASS FIRE SPREAD OVER MAIN AND IGNITED GAS ESCAPING FROM ISOLATED CORROSION LEAK ON 18" MAIN.
2025-01-31 10:21 | NO | NO | 19880213 |  | 4473 | ENERGAS CO | 8110 SANTA FE & 4313 SCOTTY DRIVE | AMARILLO | RANDALL | TX | 79110 | 3 | NO | 2130 | 1988-09-14 | 0 | 0 | 1000 | 896.6633 | 2164.9642 | YES | 0 | 45 |  | 19880914 | 12 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API-5L CW | N/A | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR. DIV. ENG. | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A TORNADO DAMAGED 68 RESIDENCES IN SOUTHWEST AMARILLO. THE ONLY ENERGAS DAMAGEWAS A RISER BROKEN BELOW THE STOP AT 8110 SANTA FE AND A BROKEN REGULATOR AT 4313 SCOTTY DRIVE.
2025-01-31 10:21 | YES | YES | 19880215 |  | 22763 | WISCONSIN GAS CO | 2324 NORTH FARWELL AVENUE | MILWAUKEE | MILWAUKEE | WI | 53211 | 3 | NO | 20 | 1988-04-24 | 0 | 12 | 1500000 | 1344994.8927 | 3247446.3739 | Null | 5 | 0 |  | 19880426 | 10 | 15 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GREGORY B. SCHROEDER, P.E., ENGINEER III | 4142916729 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WISCONSIN GAS COMPANY FACILITIES WERE NOT A CAUSE OF THIS EXPLOSION AND FIRE. AN EXPLOSION AND FIRE BEGAN AT ABOUT 11:20 PM. ON SUNDAY NIGHT IN THE PAINT STORE AT 2324 NORTH FARWELL. THE FIRE SPREAD THROUGHOUT THIS BUILDING, 2334 AND 2340 NORTH FARWELL AVENUE, A BAR A 2022 WEST NORTH AVENUE AND TWO GARAGES. A FIVE ALARM FIRE RESULTED. THE INCIDENT IS BEING INVESTIGATED BY LOCAL POLICE AND THEU.S. TREASURY BUREAU OF ALCOHOL, TOBACCO AND FIREARMS.
2025-01-31 10:21 | YES | YES | 19880217 |  | 1800 | BROOKLYN UNION GAS CO | 44 EAST 57TH STREET | BROOKLYN | KINGS | NY | 11203 | 4 | NO | 1805 | 1987-11-26 | 0 | 1 | 100000 | 92565.9051 | 223497.3638 | Null | 0 | 30 |  | 19871126 | 0.3 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | N/A | N/A | 0 | 1923 | UNDER PAVEMENT |  | J.R. SHEID, MANAGER, DISTRIBUTION CENTRAL DISPATCH | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A BROKEN 6" - C.I.B.S. MAIN WAS FOUND IN FRONT OF #44 EAST 57TH STREET O NOVEMBER 26, 1987. MOBILE LEAK SURVEY HAD BEEN PERFORMED ON NOVEMBER 6, 1987 BUT NO LEAK WAS DETECTED AT THAT TIME. CAUSE OF BROKEN MAIN UNKNOWN.
2025-01-31 10:21 | YES | YES | 19880220 |  | 13660 | NORTH SHORE GAS CO | BUCKLEY RD., BET ST.MARY'S RD.&O'PLAINE | GREEN OAKS | LAKE | IL | 60031 | 3 | NO | 1059 | 1988-08-31 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 31 |  | 19880831 | 35 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | N/A | PHILLIPS MFG. CO | 0 | 1982 | UNDER GROUND OR UNDER WATER |  | R.W. STEGMAN, MANAGER, OPERATIONS | 3123367400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | COMPANY CREW PUNCTURED 4" PL/STL TRANSITION FITTING. WHILE EXCAVATING TO SHUT OFF LINE, BROKE A COMMONWEALTH EDISON COMPANY CABLE. IGNITION OCCURRED.
2025-01-31 10:21 | YES | YES | 19880221 |  | 14210 | OKLAHOMA NATURAL GAS CO | 6110 SOUTH 28TH WEST AVENUE | TULSA | TULSA | OK | 74132 | 3 | NO | 1655 | 1988-09-11 | 1 | 0 | 68000 | 60973.1018 | 147217.5689 | Null | 1 | 0 |  | 19880912 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE PIPING | OTHER | CONNECTION OF RANGE | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES M. WOOD, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INCIDENT OCCURRED AT APPROXIMATELY 16:55 HOURS ON SEPTEMBER 11, 1988, CRITICALLY INJURING THE EMPLOYEE. A LEAK REPORT WAS CALLED IN BY A REAL ESTATE SALESPERSON WHO WAS SHOWING A HOUSE NEXT DOOR TO THE HOUSE WHICH EXPLODED. THE CALLWAS RECEIVED AT 16:35 HOURS SUNDAY AFTERNOON (SEPTEMBER 11, 1988), THE MOBILE DISPATCH SYSTEM RECORDED A SERVICEMAN TO BE ON THE PREMISES AT 16:52 HOURS,AND COMPANY RECEIVED A CALL FROM THE FIRE DEPARTMENT AT 16:58 REPORTING THE EXPLOSION. THE HOUSE EXPLODED AS THE EMPLOYEE WAS APPROACHING, THE HOUSE WAS COMPLETELY DESTROYED AND NEARBY HOUSES SUSTAINED DAMAGE. THE EMPLOYEE DIED AT 17:00 HOURS ONSEPTEMBER 13, 1988, OF INJURIES. THE INVESTIGATION BY THE TULSA FIRE AND POLICE DETERMINED THE VACANT HOUSE HAD BEEN BURGLARIZED AND THE KITCHEN APPLIANCES HAD BEEN REMOVED BY THIEVES SOMETIME SATURDAY NIGHT OR SUNDAY MORNING. INVESTIGATION INDICATED THAT THE RANGE WAS REMOVED FROM THE CABINETS WITHOUT TURNING OFF THE GAS SUPPLY. A BROKEN RANGE CONNECTOR WAS FOUND TO INDICATE THIS TO BE THE CAUSE. SOURCE OF IGNITION HAS NOT BEEN DETERMINED. THE TULSA POLICE DEPARTMENT ISINVESTIGATING THE FATALITY AS A HOMICIDE.
2025-01-31 10:21 | NO | NO | 19880223 |  | 4473 | ENERGAS CO | 116 SE 2ND STREET | TULIA | SWISHER | TX | 79088 | 3 | NO | 2245 | 1988-09-18 | 0 | 0 | 20000 | 17933.2652 | 43299.285 | Null | 0 | 15 |  | 19880919 | 702 | 10 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414411 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INCIDENT APPARENTLY OCCURRED ABOUT 10:45 PM ON SUNDAY, SEPTEMBER 18TH. WAYNE ELLISTON DID NOT LEARN OF ITS OCCURRENCE UNTIL THE NEXT MORNING. THE TULIA FIRE DEPARTMENT RESPONDED TO THE FIRE AND TURNED THE GAS METER OFF THAT SERVES THE BUILDING. BECAUSE OF TEH POSSIBILITY OF ARSON, THEY WILL NOT PERMIT THE BUILDING TO BE ENTERED OR A SHUT-IN TEST OF THE CUSTOMER PIPING. REPORTEDLY THE LOCATION OF THE HOTTEST PART OF THE FIRE INDICATES IT WAS PROBABLY NOT NATURAL GAS RELATED. THE CONSTRUCTION CREW FOR ENERGAS CONDUCTED A LEAK SURVEY OF GAS PIPINGADJACENT TO THE BUILDING AND FOUND NO LEAK INDICATIONS. WE DO NOT ANTICIPATE ANY FURTHER REPORT OF THIS INCIDENT WILL BE NECESSARY.
2025-01-31 10:21 | NO | NO | 19880224 |  | 4473 | ENERGAS CO | 703 - 10 STREET | SHALLOWATER | LUBBOCK | TX | 79363 | 3 | NO | 223 | 1988-09-21 | 0 | 0 | 3000 | 2689.9898 | 6494.8927 | Null | 0 | 20 |  | 19880921 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414411 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OUR DISPATCHER WAS CALLED AT 2:23 AM. THIS MORNING, SEPTEMBER 21ST BY SANDRA CODY OF THE SHALLOWATER POLICE DEPARTMENT REPORTING A FIRE. OUR SERVICEMAN IN TURN WAS DISPATCHED TO THE LOCATION AT 703 10TH STREET IN SHALLOWATER. HE FOUND THE STORAGE HOUSE AT THE REAR OF THE PROPERTY BEHIND THE RESIDENCE AT THIS LOCATION HAD BURNED. THE METER SETTING WAS ADJACENT TO THIS STORAGE HOUSE AND THE FIREHAD MELTED THE REGULATOR AND DAMAGED THE METER. HE TURNED OFF THE GAS VALVE BUT WAS UNABLE TO MAKE A SHUT-IN TEST. THERE WERE NO INJURIES FROM THE FIRE AND NO GAS PIPING WITHIN THE STORAGE BUILDING. ESTIMATED DAMAGE WAS $3,000.00. THE METER SETTING WAS REBUILT AND LEAK SURVEY MADE OF GAS LINES IN THE ADJACENT ALLEY. NO LEAKS WERE FOUND WITH THE SURVEY. NO LEAK INDICATION WAS FOUND ON THE SHUT-IN TEST.
2025-01-31 10:21 | YES | YES | 19880226 |  | 6141 | GAS CO OF NEW MEXICO | 915 SOUTH ADAMS ST. | TUCUMCARI | QUAY | NM | 88401 | 3 | NO | 220 | 1988-09-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 25 |  | 19880914 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 1.25 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | ROBERT R. SUMRULD | 5054612714 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | N/A | YES |  |  | ON SEPTEMBER 11,1988, AT APPROXIMATELY 2:20 A.M. A CAR HIT A RESIDENTIAL METER SET LOCATED AT 915 S. ADAMS STREET, TUCUMCARI, NEW MEXICO. THE ACCIDENT RESULTED IN THE FAILURE OF THE STEEL SERVICE LINE, IMMEDIATELY UPSTREAM OF THE INLET VALVE. THE CAR AND EXCAPING GAS CAUGHT FIRE WITH BOTH PROPERTY DAMAGE AND BODILY INJURY REPORTED. THE DRIVER OF THE VEHICLE WAS HOSPITALIZED WITH BURNS TO THE FACE, ARM AND HAND. THE FIRE DEPARTMENT EXTINGUISHED THE FIRE TO BOTH THE CAR AND THE GAS; THE GAS FLOW WAS STOPPED BY 2:45 AM.
2025-01-31 10:21 | YES | YES | 19880230 |  | 11680 | LONE STAR GAS CO | 100 E. EMERALD | IOWA PARK | WICHITA | TX | 76367 | 0 | NO | 654 | 1988-08-16 | 1 | 1 | 35000 | 31383.2142 | 75773.7487 | Null | 0 | 26 |  | 19880816 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | H.R. BURCH - SUPERINTENDENT | 8177664151 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19880231 |  | 11680 | LONE STAR GAS CO | 2201 RAPER | PANTEGO | TARRANT | TX | 76013 | 1 | NO | 1350 | 1988-08-08 | 0 | 0 | 5000 | 4483.3163 | 10824.8212 | Null | 1 | 15 |  | 19880808 | 16 | 35 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 1.5 | 0.14 | API5L CLASS | NIPAK | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | JACK L. JENNINGS, SUPERVISOR IV | 8177944230 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PIPELINE HAD BEEN EXPOSED BY PARTY CAUSING DAMAGE TO COMPLETE WORK ON PHONE CABLES.
2025-01-31 10:21 | NO | NO | 19880232 |  | 1704 | BRAZOS RIVER GAS CO | BUNGER | GRAHAM | YOUNG | TX | 76046 | 1 | NO | 1500 | 1988-07-01 | 0 | 0 | 50000 | 44833.1631 | 108248.2125 | Null | 1 | 15 |  | 19880701 | 300 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CITY GATE | BODY OF PIPE |  | STEEL |  | 4 | 0.237 | API 5B | LONE STAR | 0 | 1969 | ABOVE GROUND |  |  | 0000000000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | APPROXIMATELY AT THE DATE AND TIME INDICATED, A TRUCK OWNED AND OPERATED BY L-M-S POLE LINE CONSTRUCTION CO WAS SOUTHBOUND ON FM 1287 PULLING A LOADED POLE TRAILER. L-M-S WAS DOING SOME WORK IN THE BUNGER AREA FOR FORT BELKNAP ELECTRIC COOP. THE TRAILER CAME LOOSE FROM THE TRUCK AND DRIFTED TO THE WEST LEAVING THE PAVEMENT APPROXIMATELY 500 FEET NORTH OF THE SOUTH END OF THE BRAZOS RIVER GAS CO SOUTH CITY GATE SUPPLYING GAS TO THE TOWN OF GRAHAM, TX. THE TRAILER TRAVERSED THEBAR DITCH, WENT THROUGH A NINE STRAND BARBED WIRE FENCE BREAKING OFF CEDAR POSTSAT GROUND LEVEL. ITS COURSE WAS ALTERED SLIGHTLY, TO MORE NEARLY SOUTH, BY THE FENCE, CAUSING IT TO HEAD DIRECTLY TO THE INLET STAGES OF THE CITY GATE. WHEN THETRAILER IMPACTED THE EQUIPMENT/PIPING, THE FILTER WAS COMPLETELY DISPLACED, TWISTING THE PIPING AND SHEARING OFF THE INLET PIPING SUPPLYING GAS FROM DAMSON GAS,SUPPLIED AT 300 PSIG, WAS DISCHARGED DIRECTLY INTO THE ATMOSPHERE; HOWEVER NO IGNITION RESULTED. THE L-M-S PERSONNEL IN THE TRUCK WERE QUICK TO SECURE THE AREAAROUND THE ACCIDENT WHILE BRG WAS BEING NOTIFIED. ALTHOUGH THE SITE WAS SOMEWHAT REMOTE, THE GAS WAS TURNED OFF IN 20 MINUTES. THE TRAILER AND POLES WERE MOVEDAND THE AREA CLEARED WITHIN AN HOUR AND 15 MINUTES AFTER THE INCIDENT. THE GAS DISTRIBUTION SYSTEM OF GRAMAM HAS TWO CITY GATES; THEREFORE NO CUSTOMERS LOST SERVICE AS A RESULT OF THIS ACCIDENT.
2025-01-31 10:21 | NO | NO | 19880233 |  | 18532 | SOUTHERN UNION GAS CO | CANNON RD | AUSTIN | TRAVIS | TX | 78749 | 3 | NO | 1610 | 1988-09-12 | 0 | 0 | 6000 | 5379.9796 | 12989.7855 | YES | 2 | 5 |  | 19880912 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L-B | N/A | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR INITIATED EXCAVATION THE AFTERNOON OF SEPTEMBER 12,1988 (SAME DAY ASINCIDENT) WITHOUT NOTIFYING LOCAL UTILITIES OF PROPOSED EXCAVATION EITHER BY PHONE OR THROUGH LOCAL ONE-CALL SYSTEM.CONTRACTOR WAS INITIATING EXCAVATION WITH TRACKHOE TO PLACE LARGE WATER MAIN WHEN THEY STRUCK AND DAMAGED A 6" WS GAS MAIN.
2025-01-31 10:21 | NO | NO | 19880234 |  | 18532 | SOUTHERN UNION GAS CO | NORTHLAND DR AND MARYLAND DR. | AUSTIN | TRAVIS | TX | 78756 | 3 | NO | 1156 | 1988-09-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19880914 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L-B | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-09-07 | YES | 3 | PAINT ON SIDEWALK | NO |  |  | WHILE DRILLING TO REPLACE UTILITY POLE, CONTRACTOR DAMAGED A 6" WS GAS MAIN.
2025-01-31 10:21 | YES | NO | 19880235 |  | 18532 | SOUTHERN UNION GAS CO | 10100 RR 2222 | AUSTIN | TRAVIS | TX | 78730 | 3 | NO | 1304 | 1988-08-18 | 0 | 0 | 130000 | 116566.224 | 281445.3524 | Null | 0 | 59 |  | 19880818 | 180 | 230 | BY TEST | 600 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.218 | X-52 | N/A | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-03-31 | YES | 1 |  | NO |  |  | EXCAVATOR WAS CUTTING BAR-DITCH FOR STATE HIGHWAY DEPT ROAD PROJECT USING A CATAPILLER 933 LOADER WHEN EQUIPMENT STRUCK AND PUNCTURED A 12" WS HIGH PRESSURE MAIN.IN MARCH, 1988, SOUTHERN UNION GAS COMPANY WAS NOTIFIED BY THE TEXAS STATE HIGHWAY DEPARTMENT OF PLANS TO INSTALL A LEFT TURN LANE ON RR 2222 FOR THE NEW 3M PLANT. ON MARCH 31, 1988, SOUTHERN UNION GAS COMPANY CREWS EXPOSED THE 12" MAIN AND SHOT GRADES TO DETERMINE CLEARANCE OF PROPOSED ROAD WORK. HOWEVER, SOUTHERN UNION GAS WAS NOT NOTIFIED BY THE STATE HIGHWAY DEPARTMENT OR BY CAPITOL EXCAVATING OF PROPOSED GRADE CUT SCHEDULE OR OF WORK IN PROGRESS PRIOR TO DATE OF INCIDENT.
2025-01-31 10:21 | YES | YES | 19880236 |  | 11800 | LOUISIANA GAS SERVICE CO | 105 OLLIE DRIVE | OLLIE | PLAQUEMINES | LA | 7037 | 3 | NO | 435 | 1988-09-04 | 0 | 1 | 50000 | 44833.1631 | 108248.2125 | Null | 0 | 10 |  | 19880904 | 60 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | UNKNOWN | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS SERVICEMAN TURNED ON GAS FOR NEW CUSTOMER AT 105 OLLIE DRIVE ON FRIDAY, SEPTEMBER 2, 1988. AT 0435 HOURS CDT, SEPTEMBER 4, 1988 THE PLAQUEMINES PARISH FIRE DEPARTMENT CALLED THE LOUISIANA GAS SERVICE COMPANY NIGHT DISPATCHER NOTIFYINGHIM OF AN EXPLOSION AT 105 OLLIE DRIVE. CAUSE OF THE EXPLOSION IS UNKNOWN AT THIS TIME. A FLAME IONIZATION SURVEY PROVED THAT GAS COMPANY MAINS AND A SERVICETO THE HOUSE WERE NOT LEAKING. AN ODORMETER TEST ALSO SHOWED THAT ODORIZATION LEVELS WERE ABOVE MNIMUM REQUIREMENTS.
2025-01-31 10:21 | YES | NO | 19880239 |  | 2592 | COLUMBIA GAS OF NEW YORK INC | 7 SHIPMAN ROAD | BINGHAMTON | BROOME | NY | 13903 | 4 | NO | 917 | 1988-09-28 | 0 | 0 | 75000 | 67249.7446 | 162372.3187 | Null | 1 | 13 |  | 19880928 | 14 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREAD | STEEL |  | 1 | 0.154 | GRADE B | N/A | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | JOHN J. MRVA, DISTRICT SERVICE MANAGER | 6077242431 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A 1" COATED STEEL CUSTOMER-OWNED SERVICE LINE WAS BROKEN BY A CONTRACTOR DIGGING FOR A SEPTIC TANK. THE GAS MIGRATED INTO THE HOUSE AND WAS IGNITED BY AN UNKNOWN SOURCE. THE HOUSE EXPLODED AND BURNED. NO INJURIES OF FATALITIES OCCURRED.
2025-01-31 10:21 | YES | YES | 19880240 |  | 11680 | LONE STAR GAS CO | 4015 E. BERRY | FORT WORTH | TARRANT | TX | 76119 | 3 | NO | 2300 | 1988-09-29 | 3 | 4 | 30000 | 26899.8979 | 64948.9275 | Null | 12 | 0 |  | 19880930 | 18 | 16 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | STEEL |  | 2 | 0.154 | API 51 CLAMS | N/A | 0 | 1962 | NO DATA |  | JACK L. JENNINGS, SUPERVISOR IV | 8177944232 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CURRENTLY UNDER IVESTIGATION.
2025-01-31 10:21 | NO | NO | 19880241 |  | 4473 | ENERGAS CO | 405 S. SHERIDAN | FRITCH | HUTCHINSON | TX | 79036 | 3 | NO | 1600 | 1988-10-22 | 0 | 0 | 45000 | 40349.8468 | 97423.3912 | Null | 0 | 30 |  | 19881022 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER | UNKNOWN | NO DATA |  | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR., DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN DESTROYED HOUSE.
2025-01-31 10:21 | NO | NO | 19880242 |  | 4499 | ENTEX INC | 7000 BLOCK OF PLEAK RD. | PLEAK | FORT BEND | TX | 77469 | 3 | NO | 1110 | 1988-10-06 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19881006 | 350 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | FARMER CUTTING DRAINAGE DITCH PUNCTURED 8" PIPE LINE.
2025-01-31 10:21 | NO | NO | 19880243 |  | 18532 | SOUTHERN UNION GAS CO | 610 CENTER DRIVE | CACTUS | MOORE | TX | 79013 | 3 | NO | 1415 | 1988-10-17 | 0 | 0 | 10000 | 8966.6326 | 21649.6425 | Null | 14 | 35 |  | 19881017 | 15 | 20 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | OTHER PLASTIC | ABS | 3 | 0 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DWIGHT D. REESE | 8063965681 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT A DISTANCE OF EIGHT FEET WEST OF TEH METER, A TRANSITION ( STEEL TO ABS PLASTIC) WAS CRACKED AND LEAKING.
2025-01-31 10:21 | YES | YES | 19880244 |  | 11680 | LONE STAR GAS CO | INTER. OF HWY. NO. 16 & NO. 8 | DE LEON | COMANCHE | TX | 76444 | 3 | NO | 1430 | 1988-09-28 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19880928 | 10 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | STEEL POST DR. THRU 2"PIP | POLYETHYLENE PLASTIC |  | 2 | 0 | N/A | NIPAK | 0 | 1970 | UNDER GROUND OR UNDER WATER |  | PORTER GRIMES-SUPERVISOR IV | 8179653918 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19880245 |  | 4499 | ENTEX INC | 1413 GALE | HOUSTON | HARRIS | TX | 77009 | 3 | NO | 1006 | 1988-10-04 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 9 |  |  | 25 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S HOUSE LINE | NO DATA |  | NO DATA |  | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS LEAKING FROM OPEN HOUSE LINE IGNITED AND EXPLODED A VACANT HOUSE. TELEPHONIC REPORT MADE BECAUSE OF THE SIGNIFICANCE OF THE EVENT.
2025-01-31 10:21 | NO | NO | 19880247 |  | 18532 | SOUTHERN UNION GAS CO | ARNOLD DRIVE & NORTHEAST DRIVE | AUSTIN | TRAVIS | TX | 78723 | 3 | NO | 817 | 1988-09-29 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 43 |  | 19880929 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 | N/A | N/A | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SOIL SHRINKAGE DUE TO DRY WEAHER CAUSED STRESS FRACTURE IN CAST IRON MAIN.
2025-01-31 10:21 | NO | NO | 19880248 |  | 4499 | ENTEX INC | 7403 WIDMORE CT. | HOUSTON | HARRIS | TX | 77379 | 3 | NO | 1136 | 1988-10-04 | 0 | 0 | 5000 | 4483.3163 | 10824.8212 | YES | 1 | 20 |  | 19881004 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE2306 | DUPONT | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMONETTI, ASSISTAT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-08-28 | NO | 0 |  | NO |  |  | CONTRACTOR WAS INSTALLING UNDERGROUND CABLE WITH SMALL TRENCHER AD CUT SERVICE LINE. GAS IGNITED, BURNING TRENCER AND BRICK WALL. ONE EMPLOYEE OF CONTRACTOR WAS TREATED FOR A MINOR BURN AND RELEASED.
2025-01-31 10:21 | NO | NO | 19880249 |  | 4473 | ENERGAS CO | 1226 S. TEXAS | ODESSA | ECTOR | TX | 79761 | 3 | NO | 500 | 1988-09-30 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19881004 | 10 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CARL R. BAILEY, P.E. | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | THREAD LEAK | LEAKING GAS ACCUMULATION IN WATER METER BOX. CUSTOMER IGNITED THE GAS WITH LIGHTER AND RECEIVED MINOR FLASH BURNS TO FACE.
2025-01-31 10:21 | YES | YES | 19880250 |  | 11680 | LONE STAR GAS CO | 4411 SOUTH BELTLINE RD | MESQUITE | DALLAS | TX | 75181 | 2 | NO | 1135 | 1988-09-11 | 0 | 1 | 500 | 448.3316 | 1082.4821 | YES | 2 | 55 |  | 19880911 | 12 | 55 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0 | PE 3306 | NIPAK | 1970 | 1970 | UNDER GROUND OR UNDER WATER |  | J. R. ROSSER, C&M SUPERINTENDENT | 2144873835 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A TRANSVERSE CRACK OCCURRED IN A 2" POLYETHYLENE MAIN, EXTENDING ABOUT ONE-HALFTHE CIRCUMFERENCE OF THE PIPE. IT WAS LOCATED AT THE BASE OF A SERVICE TAP.
2025-01-31 10:21 | NO | NO | 19880251 |  | 18104 | SAN ANTONIO CITY PUBLIC SERVICE BOARD | 6742 SPRING LARK DR. | SAN ANTONIO | BEXAR | TX | 78249 | 3 | NO | 758 | 1988-09-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 35 |  | 19880919 | 7 | 33 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | N/A | N/A | 0 | 1973 | ABOVE GROUND |  | WM. F. REICHERT, SENIOR ENGINEER | 5122273211 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | LIGHTNING STRUCK RISER, ESCAPING GAS IGNITED.
2025-01-31 10:21 | YES | NO | 19880256 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 21496 FIRWOOD | EL TORO | ORANGE | CA | 92630 | 3 | NO | 1740 | 1988-09-11 | 0 | 0 | 100000 | 89666.3262 | 216496.4249 | Null | 1 | 31 |  | 19880911 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D2513 | NIPAC | 0 | 1983 | ABOVE GROUND |  | L.M. STEWART - MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19880257 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 876-878 VALENCIA STREET | SAN FRANCISCO | SAN FRANCISCO | CA | 94110 | 3 | NO | 1755 | 1988-09-20 | 0 | 0 | 1001000 | 897559.9251 | 2167129.2135 | Null | 0 | 20 |  | 19880920 | 0.3 | 0.4 | BY TEST | 2 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | WILLIAM R. MAZOTTI - GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A STRUCTURE FIRE OF AN UNKNOWN ORIGIN DESTROYED TWO GAS METERS, ALLOWING GAS TOESCAPE & IGNITE. BUILDINGS WERE EVACUATED & TRAFFIC REROUTED.
2025-01-31 10:21 | YES | NO | 19880259 |  | 1640 | BOSTON GAS CO | 390 NORTH AVENUE | WESTON | MIDDLESEX | MA | 02193 | 3 | NO | 1140 | 1988-10-31 | 0 | 0 | 200000 | 179332.6524 | 432992.8498 | Null | 1 | 30 |  | 19881031 | 53 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | N/A | N/A | 0 | 1950 | WITHIN/UNDER BUILDING |  | LAWRENCE P. MCCARTHY, SUPERINTENDENT | 6173239210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR DID NOT NOTIFY DIG SAFE AS REQUIRED BY MASSACHUSETTS LAW. CONTRACTOR EXCAVATING TO REPLACE SEPTIC TANK COVERS, PULLED AND BROKE A 3/4 INCH H.P. STEEL GAS SERVICE CAUSING FIRE AND EXPLOSION.
2025-01-31 10:21 | YES | YES | 19880260 |  | 2596 | COLUMBIA GAS OF OHIO INC | R.D. 1, STARR ROAD | GREENWICH | HURON | OH | 44837 | 4 | NO | 1910 | 1988-10-10 | 0 | 1 | 90000 | 80699.6936 | 194846.7824 | Null | 0 | 15 |  | 19881010 | 34 | 38 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | NO DATA |  | 0.125 | 0.14 | N/A | N/A | 0 | 1954 | WITHIN/UNDER BUILDING |  | ROBERT P. MONROE, DIVISION SERVICE SUPV. | 4195294911 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION AND FIRE OCCURRED AT THIS ADDRESS. OCCUPANTS REPORTEDLY HAD SMELLED GAS. THE SON INVESTIGATED ODOR ABOUT 5:00 PM. AND THE FATHER ABOUT 7:00 PM. WHEN THE FATHER, RETURNING FROM THE BASEMENT, TURNED LIGHT OUT, THE EXPLOSION OCCURRED. INVESTIGATION REVEALED THE CUSTOMER OWNED SERICE LINE WOULD NOT WITHSTANDA PRESSURE TEST. FURTHER EXCAVATION REVEALED 1 1/4" PIPE CRACKED IN THE THREADS AT AN ELL IN THE GROUND UNDER THE ADD-ON DINING ROOM AND UPSTREAM OF THE METER.IT HAS NOT BEEN DETERMINED WHETHER THE CRACKED THREADS WERE THE CAUSE OF THE EXPLOSION OR WERE AS A RESULT OF IT.
2025-01-31 10:21 | YES | NO | 19880261 |  | 13710 | NORTHERN ILLINOIS GAS CO | 124 N. SCHMALE ROAD | CAROL STREAM | DU PAGE | IL | 60188 | 3 | NO | 2049 | 1988-10-25 | 0 | 0 | 150000 | 134499.4893 | 324744.6374 | Null | 1 | 11 |  | 19881025 | 60 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1.25 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | C. OVERGAARD, MANAGER DIVISION MAINTENANCE | 3126292500 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CAR ENTERED THE DRIVEWAY OF THE COMMERCIAL BUILDING AT 124 SCHMALE RD, AND DROVE INTO THE SIDE OF THE STRUCTURE DAMAGING THE METER SET AND REGULATOR, CAUSINGFIRE AND WATER DAMGE.
2025-01-31 10:21 | YES | YES | 19880262 |  | 13710 | NORTHERN ILLINOIS GAS CO | 711 MILL STREET | SOUTH ELGIN | KANE | IL |  | 3 | NO | 1230 | 1988-10-21 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 45 |  | 19881022 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | R. MAGILL, AREA MANAGER OPERATING | 8154550271 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-10-12 | NO | 0 |  | YES |  |  | LOUIS RUFFOLO AND SONS, BOLINGBROOK , ILLINOIS, WERE INSTALLING WATER SERVICE STUBS ON MILL STREET. AT 11:52 AM. NI-GAS RECEIVED A REPORT OF A HIT GAS MAIN AT711 MILL STREET. AT 12:08 A NI-GAS EMPLOYEE ARRIVED AND MADE A LEAK INVESTIGATION. THE MAIN IN FRONT OF 711 MILL HD BEEN HIT BUT HAD NOT BEEN PUNCTURED. THE EMPLOYEE TOOK READINGS WITH A COMBUSTIBLE GAS INDICATOR AND FOUND 40% GAS READINGS EAST AND WEST OF THE EXCAVATION. HE ALSO FOUND GAS BLOWING OUT OF SOL ALONG THE MAIN FROM THE EAST. HE TOLD THE CONTRACTOR EMPLOYEE TO STAY OUT OF THE HOLE UNTIL A STREET CREW COULD FIND AND REPAIR THE LEAK. THE EMPLOYEE LEFT THE SCENE TO NOTIFY A NEARBY STREET CREW OF THE INCIDENT.AT APPROXIMATELY 12:30 PM THE CONTRACTOR EMPLOYEE RE-ENTERED THE HOLE AND SPARKES FROM HIS TOOLS APPARENTLY IGNITED THE GAS. HE WAS BURNED ABOUT THE FACE ANDHANDS. THE ACTUAL BREAK IN THE MAIN WAS FOUND 13 FEET EAST OF THE EXCAVATION WHERE THE FIRE OCCURRED. THE MAIN APPEARED TO HAVE BEEN HIT PREVIOUSLY BY CONSTRUCTION EQUIPMENT AND HAD NOW CRACKED ABOUT 3/4 OF THE CIRCUMFERENCE OF THE PIPE.
2025-01-31 10:21 | YES | YES | 19880265 |  | 11713 | LONG ISLAND LIGHTING CO | 2758 NATTA BLVD. | BELLMORE, | NASSAU | NY | 11710 | 4 | NO | 553 | 1988-10-18 | 0 | 1 | 200000 | 179332.6524 | 432992.8498 | Null | 0 | 34 |  | 19881018 | 44 | 60 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.075 | 0.113 | N/A | N/A | 1932 | 1932 | UNDER GROUND OR UNDER WATER |  | M.A. FORSTMANN, ASSOCIATE ENGINEER | 5164364324 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19880266 |  | 15462 | PHILADELPHIA ELECTRIC CO | 1842 SHALLCROSS AVENUE | FOLCROFT | DELAWARE | PA | 19032 | 3 | NO | 614 | 1988-11-03 | 0 | 2 | 300000 | 268998.9785 | 649489.2748 | Null | 2 | 45 |  | 19881103 | 20 | 50 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | PIPE AT SERVICE ADAPTER | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D-2513 | DUPONT | 1972 | 1972 | OTHER | OUTDR. SERV. RISER AT WAL | T.A. ROEHRIG, SUPERINTENDENT, GAS DISTRIBUTION | 2158414962 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 06:14 ON NOVEMBER 3, 1988, AN EXPLOSION OCCURRED AT 1842 SHALLCROSS AVE. FOLCORFT. THE FORCE OF THE EXPLOSION PUSHED OUT THE FRONT FOUNDATION WALL, BENDINGTHE GAS SERVICE RISER SLEEVE AT THE SERVICE HEAD ADAPTER. THE METER ASSEMBLY WAS COVERED BY THE REST OF THE FRONT WALL. AFTER THE FIRE WAS EXTINGUISHED, THEMETER ASSEMBLY WAS EXCAVATED AND THE 1/2" PLASTIC SERVICE PIPE WAS FOUND TO HAVE FRACTURED BELOW THE COMPRESSION FITTING OF THE SERVICE HEAD ADAPTER. THIS FRACTRUE IS BELIEVED TO HAVE BEEN CAUSED BY THE FORCE OF THE HOUSE IMPACTING ON THEMETER ASSEMBLY. THE CAUSE OF THE EXPLOSION IS OF SUSPICIOUS ORIGIN AND IS STILL UNDER INVESTIGATION. ALL ADJACENT GAS FACILITIES WERE TESTED INT HE PRESENCE OF NTSB REPRESENTATIVES, AND NO OTHER GAS LEAKS WERE FOUND.
2025-01-31 10:21 | YES | NO | 19880276 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2196 DELNO STREET | FRESNO | FRESNO | CA | 93706 | 3 | NO | 100 | 1988-11-04 | 0 | 0 | 65500 | 58731.4436 | 141805.1583 | Null | 0 | 35 |  | 19881104 | 53 | 53 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | RISER | BODY OF PIPE |  | NO DATA |  | 0.75 | 0 | N/A | POWELL | 0 | 1976 | ABOVE GROUND |  | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SVC. | 4159736998 | [6 empty] | Null |  | NO DATA | SUSPECTED ARSON RELATED | NO |  | NO | 0 |  | NO |  |  | SUSPECTD ARSON, NATRUAL GAS EXPLOSION IN VACANT DUPLEX CAUSED WALL TO FALL ON RISER AND METER SET.
2025-01-31 10:21 | YES | YES | 19880277 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 24139 MISSION BOULEVARD, UNIT 25 | HAYWARD | ALAMEDA | CA | 94545 | 3 | NO | 1242 | 1988-11-03 | 2 | 0 | 0 | 0 | 0 | Null | 12 | 42 |  | 19881103 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER-OWNE | OTHER | VENTILATION SYSTEM | NO DATA |  | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | WILLIAM R. MAZOTI-V.P., GAS & ELECL. TECH . | 0000000000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INSUFFICIENT VENTALIATION OF THE CUSTOMER-OWNED GAS WASTER HEATER ALLOWED CUMBUSTION BYPORDUCTS TO COLLECT IN THE LIVING SPACE RESULTING IN CARBON MONIXIDE POISONING.
2025-01-31 10:21 | YES | NO | 19880278 |  | 11713 | LONG ISLAND LIGHTING CO | TULIP AVENUE | FLORAL PARK | NASSAU | NY | 11001 | 4 | NO | 820 | 1987-01-25 | 0 | 0 | 300000 | 277697.7153 | 670492.0914 | Null | 10 | 9 |  | 19870125 | 33 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0.004 | 0.25 | N/A | N/A | 1916 | 1916 | UNDER PAVEMENT |  | R.R. MORABITO, DIVISION MANAGER | 5169334470 | [6 empty] | Null |  | NO DATA | SUBSIDENCE | NO |  | NO | 0 |  | NO |  |  | PIPE FRACTURED DUE TO IMPROPER BACKFILLING DURING SERWER CONSTRUCTION.
2025-01-31 10:21 | NO | NO | 19880279 |  | 11713 | LONG ISLAND LIGHTING CO | COMMACK ROAD, NORTH SERVICE ROAD | COMMACK | SUFFOLK | NY | 11787 | 4 | NO | 841 | 1987-02-17 | 0 | 0 | 30000 | 27769.7715 | 67049.2091 | Null | 2 | 18 |  | 19870217 | 57.4 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 2 | 0 | ASTMD 2513 | DUPONT | 1976 | 1976 | UNDER GROUND OR UNDER WATER |  | R.R. MORABITO, DIVISION MANAGER | 5169334470 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1986-12-26 | NO | 0 |  | YES |  |  | EXCAVATOR PROVIDED INCORRECT INFORMATION ON THE LOCATION RESULTING IN MARKOUT OF WRONG LOCATION.
2025-01-31 10:21 | YES | NO | 19880280 |  | 18536 | SOUTHWEST GAS CORP | 2104 SPRING MOUNTAIN ROAD, SPACE 37 | LAS VEGAS | CLARK | NV | 89109 | 3 | NO | 1459 | 1988-03-04 | 0 | 0 | 64685 | 58000.6631 | 140040.7125 | Null | 1 | 18 |  | 19880308 | 43 | 43 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 0.5 | 0.052 | PVC | N/A | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | JOHN P. HAZARD, SUPERINTENDENT OF CONSTRUCTION | 7023652175 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CRACKIN A 1/2" PVC SERVICE TO SPACE 37 WORLD WIDE MOBILE HOME PARK LEAKED ANDWAS APPARENTLY IGNITED BY THE WATER HEATER. THE MOBIL HOME ( SPACE 37) AND ITSCOTENTS WAS DESTROYED BY FIRE. THE SERVICE WAS ABANDONED.
2025-01-31 10:21 | NO | NO | 19880281 |  | 18532 | SOUTHERN UNION GAS CO | VINTON ROAD AT I-10 EAST | EL PASO | EL PASO | TX | 79932 | 3 | NO | 1248 | 1988-11-01 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 22 |  |  | 130 | 175 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4.5 | 0.188 | N/A | N/A | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | EDWARD H. SMITH, P.E. REGIONAL ENGINEER | 9155446300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-09-16 | YES | 0 | PAINT | NO |  |  | ON NOVEMBER 1, 1988 AT 12:48 PM. A CONTRACTOR WORKING FOR 3EL PASO ELECTRIC COMPANY DAMAGED OUR 4" H.P. PIPELINE WITH AN AUGER WHILE INSTALLING POWER POLES. THE ELECTRIC COMPANY HAD REQUESTED THAT OUR LINES BE SPOTTED ON SEPTEMBER 16, 1988, AT WHICH TIME THE LINES WERE LOCATED AND SPOTTED USING YELLOW MARKER PAINT. AT THAT TIME OUR REPRESENTATIVE WAS INFORMED THAT A PORPOSED INSTALLATION WAS GOING TO BE APPROXIMATELY 100' TO THE WEST OF OUR PIPELINE. THE ELECTRIC COMPANY CHANGED THEIR DESIGN PLACING A POWER POLE DIRECTLY OVER THE PIPELINE. WE WERE NOT NOTIFIED OF ANY DESIGN CHANGE AND THE ELECTRIC COMPANY INSPECTOR THAT REQUESTED THE ORIGINAL LINESPOT DID NOT INFORM HE CONTACTOR OF THE CONFLICT WITH OUR PIPELIN AND, AS MENTIONED ABOVE, THE CONTRACTOR DRILLED THROUGH THE PIPELINE WHICHRESULTED IN AN OUTAGE INVOLVING APPROXIMATELY 100 NATURAL GAS CUSTOMERS AND THEESCAPE OF NATURAL GAS UNTIL ;THE LINE WAS SHUT-IN. TWO ELECTRIC COMPANY REPRESENTATIVES CONFIRMED THE FACT THAT THERE WAS INTERNAL MISCOMMUNICATION REGARDING THE LINE LOCATION IN RELATION TO THE REDESIGNED ELECTRIC COMPANY STRUCTURE. WE WILL PURSUE FULL REIMBURSEMENT FOR THE DAMAGE. THE NEWS MEDIA DID NOT COVER THEINCIDENT AND SERVICE WAS RESTORED TO CUSTOMERS BEFORE 9:00 PM. OF THE SAME DAY.
2025-01-31 10:21 | YES | YES | 19880282 |  | 10037 | K P L GAS SERVICE | 1157 NORTH ESTELLE | WICHITA | SEDGWICK | KS | 67214 | 3 | NO | 1445 | 1988-10-09 | 0 | 2 | 41000 | 36763.1937 | 88763.5342 | Null | 0 | 26 |  | 19881009 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES W. INGRAM, IVCE PRESIDENT, GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CAUSE HAS BEEN LISTED AS INCENDIARY BY THE LOCAL FIRE DEPARTMENT. FOUND NO INDICATION OF GAS LEAKAGE ON ANY KPL GAS SERVICE FACILIITIES. INITIAL SHUTIN TESXTREVEALED LEAKAGE TOO SMALL TO ESTIMATE.
2025-01-31 10:21 | NO | NO | 19880283 |  | 4473 | ENERGAS CO | 8822 LAMAR | ODESSA | ECTOR | TX |  | 3 | NO | 1013 | 1988-11-11 | 0 | 0 | 20000 | 17933.2652 | 43299.285 | YES | 0 | 15 |  | 19881111 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CARL F. BAILEY, P.E. | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A KITCHEN FIRE OCCURRED FOR REASONS UNKNOWN. FIRE DAMAGE TO KITCHEN AREA RESULTED. INCIDENT ON CUSTOMER'S PREMISES.
2025-01-31 10:21 | NO | NO | 19880284 |  | 4473 | ENERGAS CO | 1511 ALPINE | ODESSA | ECTOR | TX | 79760 | 3 | NO | 1155 | 1988-11-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19881121 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CARL F. BAILEY, P.E. | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19880285 |  | 4473 | ENERGAS CO | 600 SANTA ROSA | ODESSA | ECTOR | TX | 79760 | 3 | NO | 1131 | 1988-11-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19881121 | 0.5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CARL F. BAILEY, P.E. | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OCCUPANT LIGHTED THE WALL FURNANCE AND IGNITED GAS ESCAPING A FAULTY CONNECTION. FIRE DAMAGE TO WALL RESULTED.
2025-01-31 10:21 | NO | NO | 19880286 |  | 4473 | ENERGAS CO | FM 2394 1 MILE SOUTH OF 1-40 | AMARILLO | RANDALL | TX | 79112 | 3 | NO | 1330 | 1988-11-15 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19881115 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.02 | 0.216 | PE3408 | PHILLIPS | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | A TEXAS HIGHWAY DEPARTMENT CREW REPLACING CULVERT HIT 2" GAS LINE. 28 CUSTOMERSWERE OUT OF GAS FOR 4 HOURS.
2025-01-31 10:21 | NO | NO | 19880287 |  | 18532 | SOUTHERN UNION GAS CO | 10805 SCHOOL HOUSE LANE | AUSTIN | WILLIAMSON | TX | 78750 | 4 | NO | 848 | 1988-11-11 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 22 |  | 19881111 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | APPLIANCE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | CUSTOMER APPLIANCE | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE LIGHTNING AND CHECKING HEATING FURNACES, THE SCHOOL MAINTENANCE PERSONNELWERE PURGING THE LINE TO A FURNACE. THE BLOWER WAS RUNNING AND DREW THE PURGEDGAS INTO THE DUCT SYSTEM AND THEN WAS BLOWN INTO THE SCHOOL MAIN BUILDING.
2025-01-31 10:21 | NO | NO | 19880288 |  | 18532 | SOUTHERN UNION GAS CO | 2603 JONES ROAD | AUSTIN | TRAVIS | TX | 78745 | 3 | NO | 1633 | 1988-10-19 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19881019 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.102 | PE 3408 | PLEXCO | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR WAS USING PORTABLE ELECTRIC AUGER TO DRILL HOLES FOR PLACEMENT OF PARK BENCHES WHEN A 1" POLY SERVICE WAS STRUCK DAMAGED.
2025-01-31 10:21 | NO | NO | 19880289 |  | 18532 | SOUTHERN UNION GAS CO | CHERRY LAND @ EXPOSITION | AUSTIN | TRAVIS | TX | 78703 | 3 | NO | 1233 | 1988-10-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19881028 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0 | N/A | N/A | 0 | 0 | UNDER PAVEMENT |  | B.R. KNOX REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | SHIFT IN SOIL WITH HIGH CLAY CONTENT CAUSED CAST IRON MAIN TO SEPARATE.
2025-01-31 10:21 | YES | YES | 19880290 |  | 18532 | SOUTHERN UNION GAS CO | 6712 NORTH LAMAR | AUSTIN | TRAVIS | TX | 78752 | 3 | NO | 928 | 1988-09-20 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 22 |  | 19880920 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APARTMENT OCCUPANT ALLEGELY AN INTENTIONALLY TURNED ON GAS WITHOUT PROVIDING FOR SAFE AND PROPER IGNITION. ESCAPING GAS WAS FROM OUTLET ON CUSTOMER PIPING. NO GAS ESCAPED FROM SYSTEM PRIOR TO THE METER. INCIDENT WAS REPORTED DUE TO NEWSMEDIA ATTENTION.
2025-01-31 10:21 | NO | NO | 19880291 |  | 18532 | SOUTHERN UNION GAS CO | 708 VARGAS ROAD | AUSTIN | TRAVIS | TX | 78741 | 3 | NO | 912 | 1988-10-18 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 14 |  | 19881018 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19880292 |  | 18532 | SOUTHERN UNION GAS CO | 2321 HARTFORD ROAD | AUSTIN | TRAVIS | TX | 78703 | 3 | NO | 1033 | 1988-10-06 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 36 |  | 19881006 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.75 | 0 |  |  | 0 | 1951 | UNDER PAVEMENT |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-08-24 | YES | 3 | PAINT | NO |  |  | EXCAVATOR HAD EXPOSED 1 1/4" STEEL PIPE AT DEPTH OF APPROX. 18" WHICH WAS WITHIN 18" OF GAS MARK. THE EXCAVATOR, THERE FORE, ASSUMED THIS PIPE WAS THE GAS SERVICE TO 2321 HARTFORD ROAD AND PROCEEEDED TO EXCAVATE PAST THE EXPOSED PIPE. EXCAVATOR STUCK AND DAMAGED THE ACTURAL 3/4" COPPER GAS SERVICE AT A DEPTH OF APPROXIMATELY 5' AND WAS 8" PAST THE LOCATION MARK PLACED BY SUG LOCATOR. THE DIFFERENCE IN THE ACTUAL POSITION OF THE 3/4" COPPER GAS SERVICE VX. THE 1 1/4" STEELPIPE WAS 42" VERTICALLY AND 24" HORIZONTALLY. INCIDENT DID NOT MEET REPORTING CRITERIA. IT WAS REPORTED DUE TO NEWS MEDIA ATTENTION.
2025-01-31 10:21 | YES | YES | 19880293 |  | 20050 | UNION ELECTRIC CO | 400 BLOCK OF JEFFERSON STREET | JEFFERSON | COLE | MO | 65101 | 3 | NO | 530 | 1988-10-30 | 0 | 2 | 400000 | 358665.3047 | 865985.6997 | Null | 0 | 15 |  | 19881030 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 0.0006 | 0.41 | N/A | N/A | 1955 | 1955 | UNDER PAVEMENT |  | WILLIAM J. LUEBBERT, SUPERVISING ENGINEER | 3146350171 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT ABOUT 5:30 AM. (CST) ON SUNDAY, 10/30/88 AN EXPLOSION OCCURRED IN A TWO-STORY OFFICE BUILDING AT 410-412 JEFFERSON STREET, IN JEFFERSON CITY, MISSOURI. TWOADDITINAL BUILDINGS IN THE 400 BLOCK OF JEFFERSON STREET WERE ALSO DAMAGED. UNION ELECTRIC REPORTED THIS INCIDENT BY TELEPHONE TO THE MISSOURI PUBLIC SERVICE COMMISSION - PIPELINE SAFETY PROGRAM OFFICE, AT ABOUT 6:16 AM. (CST), AND TO THEFEDERAL INFORMATION SYSTEMS OFFICE ( REPORT 14784) AT ABOUT 6:21 AM. (CST). WHILE THE INVESTIGATION OF THIS INCIDENT IS NOT YET COMPLETE, EARLY FINDINGS INDICATE THAT THE EXPLOSION OCCURRED WHEN A WATER HEATER PILOT LIGHT IN THE BASEMENT OF THE BUILDING AT 410-412 JEFFERSON STREET IGNITED NATURAL GAS WHICH HAD ACCUMULATED. THE CAUSE OF SUCH GAS BUILD UP HAS NOT BEEN DETERMINED; HOWEVER, IT IS SPECULATED THAT IT MAY HAVE RESULTED FROM A LAK IN A SIX INCH CAST IRON MAIN WHICH WAS FOUND TO HAVE A CIRCUMFERENTIAL CRACK OR FRACTURE. SUCH FINDING WAS MADE AFTER THE EXPLOSION WHEN THE SECTION OF THE MAIN INVOLVED IN THE INCIDENT WAS ISOLATED BY VALVING (AT ABOUT 7:00 AM.) AND THE DEBRIS CLEARED. NO RECORD OF THEMAIN'S WALL THICKNESS IS AVAILABLE, BUT IT IS BELIEVED TO BE 0.41 INCH.
2025-01-31 10:21 | NO | NO | 19880294 |  | 4499 | ENTEX INC | W. LOOP 287 AT BORDEN RD. | LUFKIN ' | ANGELINA | TX | 75901 | 2 | NO | 2055 | 1988-10-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19881017 | 90 | 133 | BY TEST | 200 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | AUTO LEFT ROADWAY TO AVOID COLLISION WITH TRACTOR TRAILER RIG. AUTO STRUCK CYCLONE FENCE AND ENTEX REGULATOR STATION.
2025-01-31 10:21 | YES | YES | 19880295 |  | 11336 | LEBANON GAS DEPT, CITY OF | 222 LIGON DRIVE | LEBANON | WILSON | TN | 37087 | 1 | NO | 2032 | 1988-10-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19881025 | 30 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | NOT YET DETERMINED | DON COZART | 6154440825 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19880296 |  | 18532 | SOUTHERN UNION GAS CO | 6100 DERBY COVE | AUSTIN | TRAVIS | TX | 78723 | 3 | NO | 630 | 1988-11-09 | 0 | 2 | 40000 | 35866.5305 | 86598.57 | Null | 0 | 20 |  | 19881109 | 35 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PLUMBING | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | B.R. KNOX, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19880300 |  | 17620 | ROCKY MOUNTAIN NATURAL GAS CO | #24 CLARK | EL JEBEL | EAGLE | CO | 81628 | 3 | NO | 330 | 1988-11-20 | 0 | 0 | 45000 | 40349.8468 | 97423.3912 | Null | 1 | 0 |  |  | 25 | 66 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | A-120L | N/A | 1963 | 1963 | UNDER GROUND OR UNDER WATER |  | JOHN WILSON, DIRECTOR OF DISTRIBUTION | 3039458618 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | 1 1/4" MAIN CRACKED. PREVIOUS THIRD PARTY DAMAGE HAD NOT BEEN REPORTED.
2025-01-31 10:21 | YES | YES | 19880301 |  | 6141 | GAS CO OF NEW MEXICO | 340 BETHEL SE | ALBUQUERQUE | BERNALILLO | NM | 87102 | 3 | NO | 630 | 1988-11-06 | 1 | 4 | 60000 | 53799.7957 | 129897.855 | Null | 4 | 45 |  | 19881106 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | PIPE WAS PULLED FROM TREE | STEEL |  | 0.5 | 0.019 | GRADE A25 | REPUBLIC STEEL | 1971 | 1971 | UNDER GROUND OR UNDER WATER |  |  | 0000000000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | TREE ROOTS | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19880302 |  | 11713 | LONG ISLAND LIGHTING CO | 255 JERICHO TPKE | SMITHTOWN | SUFFOLK | NY | 11787 | 4 | NO | 1315 | 1988-11-19 | 1 | 1 | 1000000 | 896663.2618 | 2164964.2492 | Null | 0 | 55 |  | 19881121 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.075 | 0.113 | ASTM A53 | N/A | 1964 | 1964 | WITHIN/UNDER BUILDING |  | M.A. FORSTMANN, ASSOCIATE ENGINEER | 5164364324 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A CONCRETE CONTACTOR WHILE EXCAVATING FOR FOOTINGS WITH A BACKHOE AT THE BUILDING WALL, HIT A 3/4 INCH STEEL SERVICE PULLING AND BREAKING A FITTING ON HE INSIDE PIPING. THE EXCAPING GAS FILLED THE BASEMENT, SHICH ULTIMATELY AUSED AN EXPLOSION. IGNITION OCCURRED PRIOR TO LILCO'S ARRIVAL CAUSING MASSIVE EXPLOSION AND RESULTING IN ONE FATILITY, SEVERAL INJURIES AND EXTENSIVE PROPERTY DAMAGE. THESURROUNDING AREA WAS SECURED BY VARIOUS FIRE AND POLICE DEPARTMENTS WITH MULTIPLE MEDIA COVERAGE.
2025-01-31 10:21 | YES | YES | 19880304 |  | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 3611 COTTONWOOD DRIVE | DURHAM | DURHAM | NC | 27707 | 3 | NO | 1600 | 1988-11-15 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 4 |  | 19881115 | 60 | 90 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | SDR 11 IPS | PHILLIPS DRISCOPIPE | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | JERRY W. RICHARDSON, VICE PRESIDENT - ENG. AND GEN. SUPV. | 9194674156 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | GTE SERVICEMAN WAS REPAIRING A PHONE CABLE WITH A HEAT SHRINK SLEEVE WHEN HE SET HIS PROPANE TORCH DOWN AND BURNED THROUGH THE GAS SERVICE.
2025-01-31 10:21 | NO | NO | 19880305 |  | 13180 | NEBRASKA CITY UTILITIES | 4TH AVENUE & 14TH STREET | NEBRASKA | OTOE | NE | 64810 | 3 | NO | 700 | 1988-11-06 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 17 |  | 19881106 | 100 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR SET | WELD | GIRTH | STEEL |  | 0.2 | 0.154 | N/A | N/A | 0 | 1981 | UNDER GROUND OR UNDER WATER |  | TOM LANT | 4028733354 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | INCIDENT WAS A RESULT OF VEHICLE ACCIDENT. VEHICLE LEFT STREET AND RAN OVER DSTRIBUTION REGULATOR SET. SET WAS COMPLETELY REBUILT AFTER ACCIDENT.
2025-01-31 10:21 | YES | YES | 19880306 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 40613 VERNE STREET | FREMONT | ALAMEDA | CA | 94536 | 3 | NO | 938 | 1988-10-15 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 23 |  | 19881015 | 0.3 | 0.3 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | WIRE | NO DATA |  | 0 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | W. R. MAZOTTI, V.P. - GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN ELECTRIC SURGE RESULTED WHEN DAMIEN P. LEE, THIRD PARTY, CLIMBED A 115 KV ELECTRIC TRANSMISSION TOWER AND TOUCHED THE CONDUCTOR. MR. LEE RECEIVED A SHOCK AND FELL APPROXIMATELY SIXTY (60) FEET. AS A RESULT OF INJURIES CAUSED BY THE SHOCK AND HIS FALL, MR. LEE WAS HOSPITALIZED. THE ELECTRIC SURGE CAUSED CURRENT TO ARC FROM THE TRANSMISSION TOWER TO AN ADJACENT METALLIC FENCE AN FROM THE FENCE TO ADJACENT HOUSES. AT 40601 VERNE STREET CURRENT ARCED FROM THE HOUSE TO THEREGULATOR, CAUSING GAS IGNITION. AT 40613 VERNE STREET, CURRENT CAUSED IGNITION OF THE GAS AND FAILURE OF THE 3/4-INCH INSULATING BUSHING. AT 40736 SUNDALE DRIVE, CURRENT CAUSED FAILURE OF THE 3/4-INCH INSULATING BUSHING, ALLOWING GAS TOESCAPE AND FLASH.
2025-01-31 10:21 | YES | NO | 19880307 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 851 WEST ATCHINSON STREET | FRESNO | FRESNO | CA | 93706 | 3 | NO | 455 | 1988-10-31 | 0 | 0 | 65000 | 58283.112 | 140722.6762 | Null | 0 | 30 |  | 19881107 | 0.3 | 0.3 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSELINE | VALVE |  | NO DATA |  | 0.75 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | WILLIAM R. MAZOTTI, V.P. - GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | UNKNOWN PERSON ENTERED VACANT DUPLEX AT 851 W. ATCHINSON STREET, OPENED AN APPLIANCE VALVE, ALLOWING GAS TO ACCUMULATE IN THE BUILDING AND EXPLODE. THE SOURCEOF IGNITION IS BELIEVED TO BE AN APPLIANCE PILOT LIGHT. PACIFIC GAS AND ELECTRIC COMPANY FACILITIES WERE NOT INVOLVED.
2025-01-31 10:21 | YES | YES | 19880308 |  | 11800 | LOUISIANA GAS SERVICE CO | 11TH STREET | SLIDELL | ST TAMMANY | LA | 70460 | 2 | NO | 1400 | 1988-12-08 | 0 | 1 | 5000 | 4483.3163 | 10824.8212 | Null | 0 | 25 |  | 19881208 | 80 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0.001 | 0.133 | API-5L | N/A | 0 | 0 | ABOVE GROUND |  | D.L. MERIWETHER, PIPELINE SAFETY | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER WAS VISIBLE | YES |  |  | TRACTOR STRUCK RISER AND CAUSED BLOWING GAS TO IGNITE. FIRE BURNED TRACTOR ANDCAUSED INJURY TO OPEATOR.
2025-01-31 10:21 | YES | NO | 19880310 |  | 4060 | EAST OHIO GAS CO | HART RD. & LITTLE MOUNTAIN RD. | KIRTLAND HILLS | LAKE | OH |  | 3 | NO | 520 | 1988-02-08 | 0 | 0 | 84000 | 75319.714 | 181856.9969 | Null | 12 | 0 |  | 19880209 | 115 | 260 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | STEEL |  | 0.2 | 0.25 | GRADE B | N/A | 1961 | 1961 | UNDER GROUND OR UNDER WATER |  | PAUL E. OLEKSA, ENVIRONMENTAL & CODES ENGINEER | 2164326858 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A FILLET WELD ON THE TOP OF A PAD SADDLE CRACKED FROM ABOUT THE 10:30 O'CLOCK POSITION TO ABOUT THE 1:30 O'CLOCK POSITION. THE WELD WAS MADE BETWEEN JANUARY 19 AND 28, 1988 AS PART OF A NEW 4 INCH BY 20 INCH SIDE CONNECTION ON AN EXISTING20 INCH MAIN THAT HAD BEEN INSTALLED IN 1961. THE SIDE CONNECTION IS LOCATED IN THE BERM OF THE ROADWAY. OUTSIDE FORCE DUE TO IMPROPER BACKFILL CAUSED THE 4 INCH PIPE TO BE LOWERED, RESULTING IN THE CRACK AT THE TOP OF THE PAD SADDLE.
2025-01-31 10:21 | YES | NO | 19880313 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 863 ATCHISON STREET | FRESNO | FRESNO | CA | 93706 | 3 | NO | 215 | 1988-11-04 | 0 | 0 | 65500 | 58731.4436 | 141805.1583 | Null | 3 | 3 |  | 19881104 | 53 | 53 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | RISER | DRIP/RISER |  | NO DATA |  | 0.75 | 0 | N/A | POWELL | 0 | 1976 | ABOVE GROUND |  | W.R. MOZOTTI-V.P. GAS& ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | SUSPECTED ARSON RELATED NATURAL GAS EXPLOSION IN VACANT DUPLEX CUSED BUILDING WALL TO FALL ON METER SET AND RISER.
2025-01-31 10:21 | YES | YES | 19880314 |  | 10037 | K P L GAS SERVICE | 5611 WEST 98TH TERRACE | OVERLAND PARK | JOHNSON | KS | 66207 | 3 | NO | 156 | 1988-09-16 | 0 | 1 | 300000 | 268998.9785 | 649489.2748 | Null | 0 | 0 |  | 19880916 | 16 | 16 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0 | N/A | N/A | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | JAMES W. INGRAM, VP GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NTSB HAS A SECTION OF THE SERVICE LINE FOR LABORATORY ANALYSIS, PLUS THERE IS ONGOING INVESTIGATION OF PROBABLE CAUSE OF INCIDENT.
2025-01-31 10:21 | NO | NO | 19890001 |  | 16667 | ENERGY NORTH NATURAL GAS INC | 12-22 GLEN STREET | FRANKLIN | MERRIMACK | NH | 03235 | 3 | NO | 1319 | 1988-12-13 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 42 |  | 19881213 | 53 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 0.04 | 0.25 | N/A | N/A | 1929 | 1931 | UNDER PAVEMENT |  | RICHARD G. MACDONALD, DISTRIBUTION MANAGER | 6032241993 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19890002 |  | 4499 | ENTEX INC | 6730 LA PUENTE | HOUSTON | HARRIS | TX | 77083 | 3 | NO | 935 | 1988-12-22 | 0 | 0 | 7000 | 6276.6428 | 15154.7497 | Null | 1 | 10 |  | 19881222 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE 2406 | DUPONT | 1980 | 1981 | UNDER GROUND OR UNDER WATER |  | B.F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19890003 |  | 18532 | SOUTHERN UNION GAS CO | EAST 3RD. AND PLEASANT VALLEY ROAD | AUSTIN | TRAVIS | TX | 78734 | 3 | NO | 1425 | 1988-12-19 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 20 |  | 19881219 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | DRIP/RISER |  | STEEL |  | 1.25 | 0 | N/A | N/A | 0 | 1944 | UNDER GROUND OR UNDER WATER |  | DENNIS WORLEY, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19890004 |  | 18104 | SAN ANTONIO CITY PUBLIC SERVICE BOARD | 101 FLORANCE | SAN ANTONIO | BEXAR | TX | 78202 | 3 | NO | 1945 | 1989-01-09 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 25 |  | 19890110 | 7 | 33 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | FITTING |  | OTHER | NYLON | 1 | 0 | N/A | N/A | 0 | 1963 | ABOVE GROUND |  | WM. F. REICHERT, SENIOR ENGINEER | 5122273211 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19890005 |  | 6830 | GREY FOREST UTILITIES | OLD FREDERICKSBURG RD | SAN ANTONIO | BEXAR | TX | 73256 | 1 | NO | 1520 | 1989-01-10 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19890110 | 203 | 214 | BY TEST | 300 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0.6 | 0.156 | API5L | DOMESTIC | 1968 | 1968 | UNDER GROUND OR UNDER WATER |  | PHIL FRANCESCO, ASSISTANT GENERAL MANAGER | 5126958781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-06-01 | YES | 3 |  | NO |  |  | THE GAS MAIN WAS DAMAGED BY A CONTRACTOR WHILE BACKFILLING A SEWER MAIN. A CORNER OF A BACKHOE LOADER STRUCK THE PIPE. ALL GAS MAINS WERE SHOWN ON THE CONTRACTOR'S PLANS. OPERATORS PERSONNEL ATTENDED PRECONSTRUCTION MEETINGS.
2025-01-31 10:21 | YES | YES | 19890007 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 214 W. ALAMOS, APT. 105B | CLOVIS | FRESNO | CA | 93612 | 3 | NO | 1500 | 1988-08-12 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19881107 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE-2306 | N/A | 0 | 1972 | WITHIN/UNDER BUILDING |  | WILLIAM R. MAZOTTI, V.P. - GAS & ELEC. TECH. SVS. | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A PG&E SERVICEMAN RESPONDED TO A NATURAL GAS LEAK INCIDENT T 214 W. ALAMOS ON OCTOBER 25, 1988. A TREE ROOT WAS FOUND TO HAVE DAMAGED A PLASTIC GAS MAIN, RESULTING IN TE ESCAPE OF GAS TO THE ATMOSPHERE. WHILE INVESTIGATING THE OCTOBER 25, 1988 INCIDENT, THE SERVICEMAN NOTICED AN APARTMENT IN THE SAME BUILDING THAT HAD BEEN BURNED OUT BY FIRE. THE FIRE HAD OCCURRED ON AUGUST 12, 1988 AND HAD SEVERELY BURNED THE OCCUPANT OF THE BUILDING. THE INVESTIGATION AT THE TIME OF THE AUGUST 13, 1988 INCIDENT HAD NOT INDICATED NATURAL GAS INVOLVEMENT AND THE CAUSE OF THAT INCIDENT HAD TENTATIVELY BEEN IDENTIFIED AS THE EXPLOSION OF A "BIC" LIGHTER. AS A RESULT OF THE OCTOBER 25, 1988 INCIDENT, NATURAL GAS IS SUSPECTEDTO HAVE CONTRIBUTED TO THE AUGUST 12, 1988 INCIDENT, NECESSITATING THIS REPORT.
2025-01-31 10:21 | NO | NO | 19890008 |  | 2652 | COMMONWEALTH GAS CO | HURON AVE. AT APPLETON ST. | CAMBRIDGE |  | MA |  | 1 | NO | 1300 | 1989-01-09 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 5 |  | 19890109 | 0.4 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NONE | CAST IRON |  | 8 | 0 | N/A | N/A | 0 | 1901 | OTHER | IN TRENCH | BRIAN HAWKESWORTH | 5084817900 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | PAINTED ROAD MARKINGS | NO |  |  | THE CAMBRIDGE WATER DEPARTMENT STRUCK AND BROKE AN 8" LP CI GAS MAIN WHILE EXCAVATING FOR A WATER LEAK IN A LOCATION THAT WAS WELL MARKED WITH UNDERGROUND GASLOCATIONS. WATER ENTERED THE GAS MAN AND BEGAN CAUSING OUTAGES IN THE AREA. AT APPROXIMATELY 1:00 P.M. AN ACCIDENTAL IGNITION OF GAS OCCURRED WHILE THE WATER DEPARTMENT PUMPED WATER FROM THE EXCAVATION. THE CAMBRIDGE FIRE DEPARTMENT BELIEVES THAT THE PROBABLE CAUSE OF IGNITION WAS THE GASOLINE FIRED PUMP USED BY THE WATER DEPARTMENT. SIX PERSONS WERE INJURED. ALL WERE TREATED AND RELEASED FORM MT. AUBURN HOSPITAL. AFFECTED AREAS OF GAS PIPING WERE ISOLATED, REPAIRED AND SERVICE RESTORATION BEGAN AT APPROXIMATELY 6:00 PM.
2025-01-31 10:21 | NO | NO | 19890009 |  | 909 | AUSTELL NATURAL GAS SYSTEM, CITY OF | 1755 BENNINGFIELD DRIVE | MARIETTA | COBB | GA | 30060 | 3 | NO | 1605 | 1989-01-04 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19890105 | 40 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT | FUSION | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM | PHILLIPS | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | DOYLE E. WEST, DISTRIBUTION MANAGER | 4049481842 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | POOR BONDING IN FUSION JOINT DUE TO SUSPECTED CONTAMINATION.
2025-01-31 10:21 | NO | NO | 19890010 |  | 12876 | MOUNTAIN FUEL SUPPLY CO | VIRGIN RIVER CROSSING ON HIGHWAY #9 | ST. GEORGE | WASHINGTON | UT | 84770 | 1 | NO | 23 | 1989-01-01 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 27 |  | 19890101 | 200 | 720 | BY TEST | 2132 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0.863 | 0.219 | API 5L-X42 | IPSCO | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | DOYCE L. COATES, MANAGER DISTRIBUTION OPERATIONS | 8018968210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DIKE ON QUAIL CREEK DAM OWNED BY WASHINGTON COUNTY WATER CONSERVANCY DISTRICT FAILED. THE ENSUING WATER RELEASE WASHED THE PIPELINE FROM THE TRENCH, CAUSING THE PIPE TO RUPTURE.
2025-01-31 10:21 | YES | NO | 19890012 |  | 1209 | BAY STATE GAS CO | 77 1/2 HADLEY STREET | SOUTH HADLEY |  | MA | 01075 | 3 | NO | 1455 | 1988-12-29 | 0 | 0 | 100000 | 89666.3262 | 216496.4249 | Null | 0 | 55 |  | 19881229 | 45 | 66 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 1958 | OTHER | IN BUILDING WALL | CARL A. TYBURSKI | 4137819200 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | BUILDING CONTRACTOR WAS EXCAVATING FOR THE INSTALLATION OF A SEWER LINE TO THE HOUSE ADDITION WHEN HIS BACKHOE OPERATOR BROKE THE NATURAL GAS SERVICE PIPE TO THE EXISTING STRUCTURE COUSING NATURAL GAS TO BLOW INTO CELLAR AREA AND EVENTUALLY WAS IGNITED AND EXPLODED. THE GAS COMPANY WAS NOTIFIED BY SOUTHE HADLEY POLICE
2025-01-31 10:21 | YES | YES | 19890013 |  | 2728 | CONSUMERS GAS CO | 600 WEST CHURCH ST. | WEST SALEM | EDWARDS | IL | 62476 | 3 | NO | 250 | 1988-03-29 | 1 | 0 | 60000 | 53799.7957 | 129897.855 | Null | 1 | 5 |  | 19880329 | 42 | 42 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESS | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ALDYL A | DUPONT | 1965 | 1966 | UNDER GROUND OR UNDER WATER |  | DONALD HARPER, SUPERINTENDENT | 6184453012 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-03-08 | YES | 3 | SERV. RISER APPARENT MARK | NO |  |  | B-1 : THE CAUSE OF THE INCIDENT HAS NOT BEEN DETERMINED. THE COLLAPSE OF A WALL, FALLING OF A ROOF AND /OR FALLING OF A KITCHEN RANGE ON THE METER SETTING ANDRISER EXERTED AND DAMAGING OUTSIDE FORCE. B-2: EXCAVATION BY THE OWNER AND ANOTHER PARTY. ATTACHED EXHIGIT B EXPLAINS PART B-2 ABOVE. MARCH 8, 1988, RECEIVED PHONE CALL FORM MARION BOEWE, EXCAVATOR OF WEST SALEM WANTING GAS SERVICE LOCATED AT 600 WEST CHURCH ST. I TOLD MR. BOEWE I WOULD BE THERE AROUND 9:30 OR 10:00 AM. THE NEXT DAY. ARRIVED AT LOCATION AROUND 9:45 AM. ON MARCH 9GH. MR. BOEWE AND MR. CARBONE ( HOMEOWNER) HAD ALREADY UNCOVERED RISER AND APPROS. 4FT. OFPLASTIC PIPE. THE RISER AND APPROX. 1FT. OF PLASTIC WERE UNDERCUT ABOUT 2FT. BELOW LINE. MR. BOEWE WAS LEAVING TO GET A LARGER BACKHOE, AS HIS TRENCHER-HOE COMBINATION WOULD NOT REACH DEPTH NEEDED TO REPLACE SEWER. I RETURNED AROUND 11:15 AM. AND LOCATED LINE FURTHER BACK TOWARD ALLEY AND GAS MAIN. AT THIS TIME MR. BOEWE HAD DUG 6-7 FEET DEEP UNDER RISER AND METER AGAIN. EVERYTHING SEEMED OK, SO AT 12:15 I RETURNED HOME (ALBION) FOR LUNCH.
2025-01-31 10:21 | NO | NO | 19890014 |  | 18536 | SOUTHWEST GAS CORP | 1771 SHAMROCK | MINDEN | DOUGLAS | NV | 89423 | 1 | NO | 745 | 1988-12-29 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19890104 | 43 | 43 | BY TEST | 43 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.6 | 0.09 | 3406 | PHILLIPS | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | RON BASSLER, DISTRICT MANAGER | 7028825770 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THE INCIDENT OCCURRED AT 7:45 AM. ON DECEMBER 29, 1988 AS MR. HATT BUTLER OF HICKEY CONSTRUCTION COMPANY, 1420 MAHOGANY DRIVE, MINDEN, DEVEADA 89423, WAS USINGA TORCH TO THAW OUT SOME FROZEN WATER LINES LYING NEAR THE NATURAL GAS SERVICE LINE STUBBED TO THE EDGE OF THE LOT. MR. BUTLER'S TORCH ACCIDENTLY BURNEDA SMALL HOLE IN THE P.E. SERVICE LINE AND IGNITED THE ESCAPING NATURAL GAS. THE FIRE WAS EXTINGUISHED AND PIPE REPAIRED BY A SOUTHWEST GAS CONSTRUCTION CREW AT 8:05 AM. THERE WERE NO INJURIES; ONLY MINOR DAMAGE TO THE SERVICE LINE. PLEASE CONTACT ME AT 702-8825769 IF YOU REQUIRE ANY FURTERE INFORMATION OR HAVE ANY QUESTIONS CONCERING THIS REPORT.
2025-01-31 10:21 | YES | YES | 19890015 |  | 12582 | MISSISSIPPI VALLEY GAS | 2811 ARBOR HILL DRIVE | JACKSON | HINDS | MS | 39212 | 3 | NO | 1155 | 1988-12-31 | 0 | 1 | 75000 | 67249.7446 | 162372.3187 | Null | 2 | 30 |  | 19881231 | 35 | 40 | BY TEST | 60 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | API5L | U.S. STEEL | 1959 | 1960 | WITHIN/UNDER BUILDING |  | JOE J. POWELL, JR. -VICE PRESIDENT-TECHNICAL SERVICES. | 6019616854 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1962 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS ACCIDENT IS STILL UNDER INVESTIGATION BUT IT APPEARS THAT GAS FROM A CORROSION LEAK ON A SERVICE LINE ENTERED THE SANITARY SEWER SYSTEM AND MIGRATED UNDERTHE SLAB FOUNDATION OF 2811 ARBOR HILL DRIVE BY A ROUTE AS YET UNDERTERMINED. GAS APPARETLY ENTERED THE HOUSE THROUGH UNSEALED HOLES DRILLED IN SLAB BY A TERMITE CONTROL COMPANY. THE GAS IGNITED AND EXPLODED DAMAGING THE HOUSE AND STARTING A FIRE. ONE ADULT MALE WAS BURNED AND REMAINS HOSPITALIZED BUT THE INJURIES ARE NOT LIFE-THREATENING. FURTHER TESTS WILL BE MADE TO DETERMINE THE CONDITIONOF THE SEWER LINE IN THE VICINITY OF THE LEAK AND NEAR AND/OR UNDER THE SLAB AND TO ATTEMPT TO DETERMINE IF SEWER GAS WAS ALSO INVOLVED.
2025-01-31 10:21 | YES | YES | 19890016 |  | 11800 | LOUISIANA GAS SERVICE CO | 3600 NEYREY DRIVE | METAIRIE | JEFFERSON | LA | 70002 | 3 | NO | 1655 | 1989-01-02 | 0 | 1 | 20000 | 17234.9476 | 41613.2199 | Null | 1 | 58 |  | 19890102 | 80 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API-5L | N/A | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | WHILE TIGHTENING BUSHING ON RISER, SERVICEMAN HEARD RISER CRACK AND START LEAKING BELOW GROUND. GAS BLEW FOR APPROXIMATELY ONE HOUR UNTIL GAS WAS TURNED OFF AT HOT TAP. UNKNOWN TO REPAIR CREW, GAS ACCUMULATED IN VOID UNDER HOUSE SLAB INTO AN EXPLOSIVE MIXTURE. A BELL HOLE WAS DUG AROUND THE RISER TO FACILITATE REPLACING IT. WHEN THE WELDER FLASHED THE HOLE WITH HIS TORCH THERE WAS A MINOR EXPLOSION IMMEDIATELY FOLLOW BY A GREATER EXPLOSION CAUSING DAMAGE TO THE HOSE; AND MONOR INJURY TO A COMPANY EMPLOYEE.
2025-01-31 10:21 | NO | NO | 19890017 |  | 11800 | LOUISIANA GAS SERVICE CO | ROUTE 1, BOX 804, HIGHWAY 11 | PORT SULPHUR | PLAQUEMINES | LA | 70083 | 2 | NO | 1525 | 1988-12-24 | 0 | 0 | 5000 | 4483.3163 | 10824.8212 | Null | 0 | 55 |  | 19881230 | 40 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC PIPE | 1 | 0.119 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | HOUSE TRAILER CAUGHT FIRE CAUSING METER INSTALLATION TO BURN. NATURAL GAS WAS FOUND TO BE ESCAPING FROM A BROKEN PLASTIC SERVICE LINE AT THE METER INSTALLATION. IT IS NOT KNOWN IF THE SERVICE LINE WAS LEAKING BEFOE OR AFTER THE FIRE START
2025-01-31 10:21 | YES | NO | 19890018 |  | 20061 | UNION GAS CO | EIGHTH AND MONROE STREET | STOUDSBURG | MONROE | PA | 18360 | 4 | NO | 1943 | 1988-12-15 | 0 | 0 | 250000 | 224165.8155 | 541241.0623 | Null | 2 | 0 |  | 19881216 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.5 | N/A | N/A | 1930 | 1930 | UNDER PAVEMENT |  | LOUIS D. WALTER, DISTRICT MANAGER | 7174212066 | [6 empty] | Null |  | NO DATA |  | YES | 1988-11-23 | YES | 3 | PAINT | NO |  |  | GROUND SUBSIDENCE DUE TO SEWER CONSTRUCTION ACTIVITY.
2025-01-31 10:21 | YES | YES | 19890019 |  | 180 | ALABAMA GAS CORP | 629 4TH AVENUE WEST | BIRMINGHAM | JEFFERSON | AL | 35204 | 3 | NO | 647 | 1988-12-07 | 0 | 1 | 75600 | 67787.7426 | 163671.2972 | Null | 0 | 18 |  | 19881207 | 2 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUST. FUEL LINE | VALVE |  | OTHER | FUEL LINE VALVE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RAYMOND E. WALLACE, JR., DISTRUBUTION ENGINEER | 2053269219 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 1/2" FUEL LINE VALVE (WITH NO APPLIANCE CONNECTED) WAS FOUND IN THE OPEN POSITION INSIDE THE HOUSE. THIS ALLOWED GAS TO ESCAPE INSIDE THE HOUSE CREATING AN EXPLOSIVE CONDITION. WE HAVE BEEN UNABLE TO DETERMINE THE REASON THE CUSTOMER WOULD HAVE REMOVED THE CAP FROM THE FUEL LINE CREATING THE HAZARDOUS CONDITON WHICH CAUSED THE EXPLOSION.
2025-01-31 10:21 | NO | NO | 19890027 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 926 SOUTH 15TH. | CHICKASHA | GRADY | OK | 73018 | 3 | NO | 1800 | 1989-01-13 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 55 |  | 19890118 | 8 | 12 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | N/A | N/A | 0 | 1940 | OTHER | WATER METER BOX | JOHN NORTH, MGR., CONSTRUCTION & MAITENANCE | 4054826315 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 1986 | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 6:00 PM. ON FRIDAY, JANUARY 13, 1989, A LINDA SCOTT WHO RESIDES AT 926 SOUTH 15TH IN CHICKASHA SAYS SHE OPENED THE WATER METER VALVE BOX LOCATED NEXT TO THE STREET IN FRONT OF HER HOUSE, LIT A MATCH TO SEE INSIDE AND GOT FLASHED. SHE SAYS SHE RECEIVED A BURNED HAND AND BURNS TO PART OF HER FACE. SHEDID NOT NOTIFY ARKLA. THEY CALLED ARKLA ON MONDAY JANUARY 16, 1989 TO REPORT THAT THEY THOUGHT THEY SMALLED GAS AROUND THE WATER METER BOX. OUR SERVICEMAN VERIFIED THAT GAS WAS PRESENT AND TURNED IT OVER TO OUR MAINTENANCE CREW. ARKLA MAINTENANCE CREW DISCOVERED A COMPANY SERVICE LINE LEAKING IN THE STREET IN FRONTOF THIS LOCATION ON JANUARY 18, 1989 AND REPLACED IT. REPORT DELAYED BECAUSE ARKLA DID NOT BECOME AWARE OF ALLEGED FLASH FIRE UNTIL DAYS LATER.
2025-01-31 10:21 | YES | YES | 19890030 |  | 15693 | PLEASANT GROVE MUNICIPAL GAS SYSTEM, CITY OF | 500 BROOKLAND DRIVE | HUEYTOWN | JEFFERSON | AL | 35023 | 3 | NO | 718 | 1989-01-14 | 2 | 0 | 90000 | 77557.2644 | 187259.4895 | Null | 1 | 55 |  | 19890114 | 40 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | JOINT | THREADED | OTHER | GALVANIZED PIPE | 1 | 0.156 | N/A | N/A | 1949 | 1949 | UNDER GROUND OR UNDER WATER |  | LESLIE M. ANTHONY | 2057447221 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | DAMAGE CAUSED BY TREE ROOT GROWING AGAINST SERVICE LINE. TREE ROOT MOVED SERVICE LINE AT ELL CAUSING PIPE TO BREAK TO ELL.SUPPLEMENT : MR E J LITTLETON & MRS VIRGINIA LITTLETON DIES FRIDAY, FEBRUARY 17,1989.
2025-01-31 10:21 | NO | NO | 19890032 |  | 11680 | LONE STAR GAS CO | 100 & 200 BLK. HOUSTON STREET | DALLAS | DALLAS | TX |  | 1 | NO | 350 | 1988-12-08 | 0 | 0 | 15000 | 13449.9489 | 32474.4637 | Null | 1 | 0 |  | 19881208 | 18 | 55 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0 | SDR 11.5 | DRISCOPE | 0 | 1988 | UNDER PAVEMENT |  | KEN BAILEY - SUPERVISOR IV | 2146701471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | 2" POLY SERVICE WAS PULLED OFF 8" WR ST IHP MAIN BY JIM BOWMAN COMPANY REPLACING CURBS UNDER CONTRACT FOR THE CITY OF DALLAS. THIS GAS WAS IGNITED BY A CAR WHICH BURNED UP IN THE 100 BLOCK OF HOUSTON STREET BETWEEN ELM AND MAIN STREET APPROXIMATELY 1 A 1/1 BLOCKS AWAY FROM WHERE THIS LINE WAS PULLED OUT.
2025-01-31 10:21 | NO | NO | 19890033 |  | 4473 | ENERGAS CO | 118 W. ALBERT | PAMPA | GRAY | TX | 79065 | 3 | NO | 1525 | 1989-01-12 | 0 | 0 | 30000 | 25852.4215 | 62419.8298 | Null | 1 | 0 |  | 19890112 | 0.6 | 1 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER |  | OTHER |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 1517 HOURS ON JANUARY 12, 1989 ENERGAS RECEIVED A GAS ODOR COMPLAINT FROM A PERSON LEVING AT 118 W. ALBERT. THE ORDER WAS DISPATCHED, AND OUR SRERVICEMAN ARRIVED AT 118 W. ALBERT AT 1525 HOURS. HE MET THE OCCUPANT AT THE DOOR WHERE HEWAS DIRECTED TO A WALL HEATER WHERE THE GAS ODOR WAS REPORTED STRONGEST. WHEN HE ENTERED THE HOUSE HE COULD SMELL GAS AT THAT TIME. HE PROCEEDED TO THE WALL HEATER WHERE HE OBSERVED FLAMES UNDER THE HOUSE THROUGHT THE OPENING WHERE GAS PIPING CAME THROUGH THE FLOOR; HE COULD ALSO FEEL THE HEAT IN THE FLOOR AND WALL. HE ADVISED EVERY ONE TO VACATE THE HOUSE AND CALL THE FIRE DEPARTMENT. HE WENTIMMEDATELY TO THE ALLEY TO TURN OFF THE METER, HE RETURNED TO THE HOUSE WITH A SMALL FIRE EXTINGUISHER HE CARRIED IN HIS VEHICLE. HE WAS UNABLE TO CONTROL THEFIRE AND LEFT THE HOUSE. THE FIRE DEPARTMENT ARRIVED BUT WAS UNABLE TO SAVE ANY OF THE HOUSE. ESTIMATED LOSS WAS $30,000.
2025-01-31 10:21 | NO | NO | 19890034 |  | 4473 | ENERGAS CO | 1 1/2 MILES S. OF FM. 700, ON US. 87 S | BIG SPRINGS | HOWARD | TX | 79720 | 3 | NO | 1145 | 1989-01-12 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 25 |  | 19890112 | 17 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 5 | 0.258 |  |  | 0 | 0 | ABOVE GROUND |  | CARL R. BAILEY, P.E. DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | AT CREEK CROSSING PIECES OF BROKEN CONCRETE WERE DUMPED ON GAS LINE CAUSING A FRACTURE.
2025-01-31 10:21 | NO | NO | 19890036 |  | 13710 | NORTHERN ILLINOIS GAS CO | 1914 9TH AVE | MAYWOOD | COOK | IL | 60104 | 3 | NO | 113 | 1989-01-18 | 0 | 0 | 30000 | 25852.4215 | 62419.8298 | Null | 1 | 45 |  | 19890118 | 58 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | CAR HIT | CAST IRON |  | 0.625 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | STANLEY VIK, CONST./MAINT. SUPV. | 3125445707 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | OPERATOR OF VEHICLE LOST CONTROL AND RAN INTO METER & REG. AT 1914 S. 9TH AVE. IN MAYWOOD. THE SERVICE WAS BROKEN AND SET HOUSE ON FIRE. THE FIRE DEPARTMENT ON THE SCENE CONTROLLED THE FIRE UNTIL STREET CREW ARRIVED. STREET CREW EXTINGUISHED FIRE AND SQUEEZED OFF PLASTIC SERVICE AT GROUND LEVEL.
2025-01-31 10:21 | YES | NO | 19890037 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 828 SAPPHIRE LANE | CORONA | RIVERSIDE | CA | 91719 | 3 | NO | 1930 | 1988-12-24 | 0 | 0 | 140000 | 125532.8567 | 303094.9949 | Null | 87 | 0 |  | 19881226 | 45 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 3 | 0.307 | ASTMD2513 | DUPONT | 0 | 1983 | UNDER PAVEMENT |  | L. M. STEWART-MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION
2025-01-31 10:21 | NO | NO | 19890038 |  | 13782 | NORTHERN STATES POWER CO | 5776 BALD EAGLE BLVD. | WHITE BEAR | RAMSEY | MN | 55110 | 1 | NO | 1107 | 1989-01-11 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 0 | 33 |  | 19890111 | 45 | 66 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.318 | D-2513 | PLEXCO | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | B.K. BELEW - STANDARDS ENGINEER | 6122292261 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | NO |  |  | TWIN CITY TESTING DRILL TRUCK DRILLED THROUGH 3" IPS PLASTIC MAIN WITH AUGER. IGNITION OF ESCAPING GAS RESULTED, AND DRILL TRUCK WAS SET ABLAZE. DUE TO FIRE NO GAS LINE LOCATING MARKS WERE VISIBLE AT SITE OF DRILL HOLD BUT OTHER LOCATINGMARKS WERE WITHIN 6" OF ACTUAL MAIN LOCATION.
2025-01-31 10:21 | YES | YES | 19890043 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 823 WOLFF STREET | DENVER | DENVER | CO |  | 3 | NO | 810 | 1988-12-27 | 0 | 2 | 50000 | 44833.1631 | 108248.2125 | Null | 17 | 20 |  | 19881228 | 7 | 15 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | JOINT | COMP CPL THREADED JOINT | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1959 | UNDER PAVEMENT |  | CHRIS HARTIG, ENGINEER | 3035713750 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | GROUND MOVEMENT | NO |  | NO | 0 |  | NO |  |  | PRELIMINARY INVESTIGATION OF THE EARTH AROUND THE 2" STEEL GAS MAIN IN THE 800 N. BLOCK OF WOLFF STREET AND PHYSICAL EXAMINATION OF THE SERVICE TAP TO 812 N.WOLFF STREET AND THE ADJACENT COUPLING ON THE 2" STEEL GAS MAIN INDICATED DAMAGE TO THESE FACILITIES WAS CAUSED BY OUTSIDE FORCES, AS DESCRIBED IN PART B ABOVE. THE DAMAGE RESULTED IN THE LEAKAGE OF NATURAL GAS FROM THESE FACILITIES.
2025-01-31 10:21 | YES | NO | 19890046 |  | 20110 | UNION LIGHT HEAT & POWER CO | RT. #455 AND I-71 | WARSAW | GALLATIN | KY |  | 3 | NO | 1300 | 1989-02-10 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | YES | 4 | 5 |  | 19890210 | 0 | 360 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | GRADE B | N/A | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | HUBERT J. FANTETTI, FIRECTOR-REGULATIONS | 5136322671 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-01-28 | YES | 2 |  | NO |  |  | WHILE EXCAVATING TO INSTALL A WATER LINE, CONTRACTOR DAMAGED GAS MAIN DIGGING PARRELL TO GAS MAIN. GAS MAIN IGNITED, FIRE DESTROYED CONTRACTOR'S EQUIPMENT
2025-01-31 10:21 | YES | NO | 19890047 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 5 MILES FROM HOT SPRINGS, | HOT SPRINGS | GARLAND | AR | 0 | 3 | NO | 1300 | 1989-01-31 | 0 | 0 | 77168 | 66499.322 | 160560.4476 | Null | 6 | 0 |  | 19890208 | 900 | 1000 | BY TEST | 1500 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | 1" CROSS OVER | NO DATA |  | NO DATA |  | 0 | 0.179 | N/A | N/A | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | RAUL G. ESPINOSA, SUPERVISOR OF CONSTRUCTION | 3184293924 | [6 empty] | Null |  | OPERATOR ACTION |  | YES | 1989-01-31 | YES | 1 |  | NO |  |  | 1" CROSS OVER LINE WAS ACCIDENTALLY STRUCK WHILE DIGGING, 1" LINE CRACKED ABOVETAP VALVE CAUSING LEAK.
2025-01-31 10:21 | YES | YES | 19890048 |  | 18112 | SAN DIEGO GAS & ELECTRIC CO | 913 TOURMALINE STREET | SAN DIEGO | SAN DIEGO | CA | 92109 | 3 | NO | 540 | 1989-01-28 | 1 | 1 | 12500 | 10771.8423 | 26008.2624 | Null | 3 | 50 |  | 19890128 | 60 | 60 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.145 | API5LB.W | N/A | 0 | 1960 | UNDER PAVEMENT |  | M.G. NASH, SR. CLAIMS REPRESENTATIVE | 6196995009 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1974 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE GAS IS BELIEVED TO HAVE MIGRATED FROM BENEATH A CONCRETE ALLEYWAY,TO THE FOUNDATION OF A GARAGE CONVERTED FOR USE AS AN APARTMENT. THE GAS ENTERED A WALL AT THE BEDROOM TO A MIXTURE APPROPRIATE FOR COMBUSTION. THE TENANT LIT A CIGARETTE CAUSING IGNITION AND RESULTING IN AN EXPLOSION IN THE BEDROOM. THE TWO OCCU
2025-01-31 10:21 | YES | NO | 19890049 |  | 12484 | MIDWEST GAS CO | 871 38TH LANE | ANOKA | ANOKA | MN | 55303 | 1 | NO | 1414 | 1989-01-22 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | Null | 5 | 30 |  | 19890123 | 50 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | COMPRESSION | NO DATA |  | 0.5 | 0.109 | PE3408 | ORANGBURG | 1966 | 1966 | UNDER PAVEMENT |  | ROBERT R. KAIN - OPERATIONS COORDINATOR | 6126901761 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | SERVICE LINES WERE INSTALLED IN MAY OF 1966. OTHER UTILITIES WERE INSTALLED IN1971. SERVICE LINES WERE CUT TO ACCOMODATE OTHER UTILITY DITCHES. CUT SERVICELINES WERE RECONNECTED USING A COMPRESSION COUPLING. IMPORPER TAMPING OF BACKFILL CAUSING SETTLEMENT OF SERVICE LINE RESULTED IN PULLOUT OF PIPE FROM COUPLING.
2025-01-31 10:21 | NO | NO | 19890050 |  | 14210 | OKLAHOMA NATURAL GAS CO | WEST OF SAPULPA ON HIGHWAY 66 | SAPULPA | CREEK | OK |  | 2 | NO | 517 | 1989-01-16 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | YES | 1 | 0 |  | 19890116 | 46 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D 2513 | DUPONT | 1970 | 1970 | NO DATA |  | J. M. WOOD, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 0517 HOURS ON JANUARY 16,1989, AN EXPLOSION DEMOLISHED A CONCRETE BLOCK BUILDING NEAR THE INTERSECTION OF HIGHWAY 117 AND HIGHWAY 66, WEST OF SAPULPA, OKLAHOMA. THE BUILDING WAS BEING RENOVATED AND WAS TO OPEN SOMETIME IN THE SPRING AS A BAR. THERE WERE NO UTILITIES CONNECTED TO THE SITE=--NO GAS, WATER, ELECTRICITY, OR TELEPHONE. THE BUILDING WAS TOTALLY DOMOLISHED. THE SAPULPA FIRE DEPT. AND POLICE DEPT. ARRIVED ON THE SCENE AT 0522 HOURS. THEY DID NOT RECEIVED A CALL BUT HAD RESPONDED TO THE SOUND OF THE EXPLOSION. THE EXPLOSION WAS HEARD OVER A WIDE AREA. DEAN WISE, SAPULPA FIRE MARSHAL, ARRIVED ON THE SCENE AT 0555 HOURS. HE WAS INFORMED THAT THE POLICE DEPT. HAD CONTACTED THE FEDERAL ALCOHOL. TABACCO, AND FIREARMS DIVISION. DEAN WISE CONTACTED AHT STATE FIRE MARSHAL FIELD AGENT. THE WEATHER DATA AT 0448 HOURS FROM THE NATIONAL WEATHER SERVICE INDICATED THE WEATHER CONDITIONS WERE "FOG, 24 DEGREES, HUMIDITY 96 PERCENT, WIND SOUTH TO SOUTHEAST AT 9.5 MILES PER HOUR, THE BAROMETRIC PRESSURE AT 30.37." THE FIRST OKLAHOMA NATURAL GAS COMPANY EMPLOYEE ARRIVED ONT EH SITE AT APPROXIMATELY 0630 HOURS. HIGHWAY66 WAS TOTALLY BLOCKED BY DEBIRS FROMTHE BLAST. INITIAL OBSERVATION UPON ARRIVING WAS A SLIGHT ODOR OF NATURAL GAS, AND THERE WERE SEVERAL SMALL FIRES BURING AROUND THE SOUTHWEST CORNER OF THE BUILDING SLAB. AN INITIAL FLAME-PACK SURVEY OF THE BLAST SITE INDICATED GAS AROUND THE BUILDING SLAB. A FLAME PACK OF THE GAS LINE ALONG THE FRONT OF THE BUILDING INDICATED ONE LEAK NEAR THE EAST EDGE OF THE EDGE OF THE PROPERTY. A 2-INCH PLASTIC LINE THAT SERVED THE AREA WAS CLAMPED OF NEAR THE NORTHEAST EDGE OF THE PROPERTY, APPROXIMATELY 300 FEET AWAY. STATE OF OK FIRE MARSHALL AGENT SHELLY PHILLIPS AND A GROUPOF DEFERAL ALCOHOL, TOBACCO, AND FIREARMS DIVISION (ATF) EMPLOYEES LED BY LOU JOBSON, ARRIVED ON THE SCENE AROUND 0830 HOURS. THEIR INITIAL REACTION WASA "CLASSIC DYNAMITE CASE." THE PRESENCE OF GAS WAS ORIGINALLYY THOUGHT TO BE THE RESULT OF THE BLAST. LOU JOHNSON OF THE ATF DIVISION APPARENTLY SSUMEDJURISDICTION OF THE INVESTIGATION ALONG WITH FIRE MARSHALL AGENT SHELLY PHILLIPS BECAUSE THEY ASSUMED IT WAS A DELIBERATELY CAUSED EXPLOSIVE USED. THE DOZER ARRIVED AND STARTED CLEARING THE SITE AT APPROXIMATELY 1000 HOURS. OKLAHOMA NATURAL GAS EMPLOYEES MET WITH DEAN WISE AND SHELLY PHILLIPS AND WERE UPDATED ON THE SITUATION. GAS WAS STILL NOT BEING CONSIDERED AS THE SOURCE OF EXPLOSION AT THIS TIME. OKLAHOMA NATURAL GAS CONTINUED TO TAKE CGI READINGS AROUNT THE SITE. THE READINGS VARIED FROM 20 PERCENT TO 100 PERCENT GAS AROUND THE FILL AREA. WE SUSPECTED THE GAS WAS FROM SOME OTHER SOURCE DUE TO THE IDISTANCE FROM OUR GAS LINE. AT ATF TEAM COMPLETED CLEARING THE BUILDING SLAB AND FOUND NO EVIDENCE OF HIGH EXPLOSIVES. AT THIS TIME LOU JOBSONN OF THE ATF TEAM MADE A PRELIMIANARY REPORT RULING OUT THE USE OF EXPLOSIVES IN THEE BLAST AND INDICATED THE BLAST WAS PROBABLY DUE TO NATURAL GAS FROM AN UNKNOWNSOURCE. THE OKLAHOMA STATE FIRE MARSHAL REQUESTED A CHECK OF ODORANT LEVEL IN OUR GAS LINE. AN ODOR OF MERCAPTAN AT THE BLAST SITE WAS NOT APPARENT EVEN THOUGH WE WERE PICKING UP VOLUME GAS READINGS ALL AROUND THE AREA. AN ODORANT LEVEL IN OUR GAS LINE. AN ODOR OF MERCAPTAN AT THE BLAST SITE WAS NOT APPARENT EVEN THOUGH WE WERE PICKING UP VOLUME GAS READINGS ALL AROUND THE AREA. AN ODORANT TEST USING A HEATH ODOR TESTER, MODEL 5637, WAS RUN AT A GAS METER NEXT TO THE BLAST SITE; THE ODORANT LEVEL INDICATED WAS 0.40 PERCENT OF GAS WHICH IS CONSIDERED TO BE NORMAL. ONE OF THE REASONS GAS HAD NOT BEEN SUPPECTED AS THE PREMARY SOURCE OF THE EXPLOSION WAS A LACK OF AN IGNITION SOURC
2025-01-31 10:21 | YES | YES | 19890051 |  | 11680 | LONE STAR GAS CO | 2103 EL DORADO | CARROLLTON | DALLAS | TX | 75006 | 3 | NO | 918 | 1988-12-26 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 30 |  | 19881226 | 18 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | MAIN CUT | POLYETHYLENE PLASTIC |  | 2.375 | 0.216 | PE 1206 | N/A | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | MR. RON COX | 2142486671 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-12-26 | YES | 3 | FLAGGED | NO |  |  | ON DECEMBER 26, 1988, 6:00 AM., THE CITY OF CARROLLTON WATER DEPARTMENT REQUESTED LINE LOCATION AT THE SUBJECT ADDRESS. LINE WAS MARKED BY FLAGS. THE CITY THEN CUT THE 2" POLY GAS MAIN AND A TV CABLE. BEFORE LONE STAR GAS ARRIVED ON THE SCENE, STORER CABLE REPAIRMAN ARRIVED AND ATTEMPTED TO REPAIR TV CABLE IN HOLEWITH BLOWING GAS AND GAS IGNITED. CABLE TV EMPLOYEE SUFFERED SEVERE BURNS AND WAS TRANSPORTED TO PARKLAND HOSPITAL.
2025-01-31 10:21 | YES | YES | 19890052 |  | 19520 | TOMBALL GAS DEPT, CITY OF | 302 OXFORD STREET | TOMBALL | HARRIS | TX | 77375 | 1 | NO | 900 | 1988-09-28 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 25 | 50 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | STATIC ELECTRICITY | CAST IRON |  | 0.4 | 0.062 | ASTM2513 | PLEXCO | 1988 | 1988 | OTHER | OPEN BELL HOLE | COY E. LIPHAM, GAS SUPT. | 7133515484 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | POLY PIPE WAS NOT GROUND | THERE WERE 2-4" MAINS WITH CAPS IN DITCH THAT WE HAD DUG OUT FOR THE TIE IN. THE DITCH WAS 23' IN LENGTH AND 5' IN WIDTH AT POINT OF STIE IN. THE REMAINDER OF THE SQUEEZER ALREADY ON THE PIPE AND SQUEEZED OFF, WITH THE CAP REMOVED. THE STUB ON THE EAST SIDE DID NOT. SO WE PUT THE HYDRAULIC SQUEEZER ON THE PIPE APPROXIMATELY 12' FROM 1ST SQUEEZER AND STARTED SQUEEZING OFF 4" MAIN/ WE HAD CUT ASMALL GASH ON THE TOP OF TH WELD OF THE COP SO IT WOULD PURGE THAT WAS COMPLETED, THE CAP WAS CUT OFF. (NOTE) FROMSTART TO THIS POINT, TOMMY AND MIKE WERE THE2 MEN IN THE HOLE. AT THAT TIME TOMMY GOT OUT OF THE HOLE AND WENT TO THE TRUCK. MILE PICKED UP THE END OF THE 4" AMIN AND HELD IT AT AN ANGLE FACING UPWARD FROM THE DITCH. I OPENED THE VALVE A LITTLE BIT TO PURGE SOME CHALKY SUBSTANCE FROM THE MAIN. AS SOON AS I CRACKED OPEN THE VALVE, I STARTED JACKING THE LEVERON THE HYDRAULIC JACK CLOSED. WHEN THE GAS HAD ALMOST STOPPED BLOWING, I SAW A FLASH FIRE RIGHT BELOW ME AT THE SIDE OF THE JACK AND SAW IT START TO FOLLOW THE MAIN TOWARD MIKE. AT THAT INSTANT I LEANED BACK SHOUTING AT MIKE, WIT MY HAND STILL ON THE JACK, BUT THE FLASH HAD ALREADY GOT ME ON THE LEFT SIDE OF MY FACE, HAIR AND ARM. AT THAT TIME MIKE TURNED TOWARD ME AND FELT SOMETHING HOT ON HIS BACK. THAT'S WHENMIKE DROPPED THE HOT PIPE, THE FLAME HITTING THE BANK AND ENGULFING HIM AS HE WAS GETTING OUT OF THE HOLE. WHEN THE FLASH FIRE STATRED IMADE APPROXIMATELY 2 MORE JACKS ON THE LEVER AND THE GAS WAS COMPLETELY SHUTOFF. BY THAT TIME THE FIRE WAS OUT. MIKE ROLLED ON THE GROUND AS TOMMY CAME OVER FROM THE MIDDLE OF THE ROAD AND THE 2 OF US PULLED OFF HIS SHIRT. AT NO TIME WAS ANYOF HIS CLOTHES ON FIRE. I PUT HIM IN MY TRUCK AND TOOK HIM DIRECTLY TO TOMBALL REGIONAL HOSPITAL. WITHIN 5 MINUTES OF THE ACCIDENT WE WERE AT THE HOSPITAL. HIS FACE HAD LIGHT FIRST DEGREE BURNS AND HIS ARMS AROUND THE ELBOWS HAD LIGHT 3RD DEGREE BURNS. AT 9:50 AM I CALLED THE RAILROAD COMMISSIONAND REPORTED THE ACCIDENT TO BUZZ FANT. AT 9:55 AM I CALLED AUSTIN TO THE RAILROAD COMMISSION AND REPORTED THE ACCIDENT TO THEM. TO THE BEST OF MY KNOWLEDGE THIS IS EXACTLY WHAT HAPPENED.
2025-01-31 10:21 | NO | NO | 19890053 |  | 18104 | SAN ANTONIO CITY PUBLIC SERVICE BOARD | 1300 BLOCK OF SOUTH LAREDO STREET | SAN ANTONIO | BEXAR | TX | 78207 | 3 | NO | 813 | 1989-01-10 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 30 |  | 19890110 | 8 | 33 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 | API-5L | N/A | 0 | 1950 | UNDER PAVEMENT |  | WM. F. REICHERT, SENIOR ENGINEER | 5122273211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | HOLE DRILLING MACHINE OPERATOR DRILLING HOLES FOR PIERS DRILLED INTO 8" STEEL GA
2025-01-31 10:21 | NO | NO | 19890054 |  | 4499 | ENTEX INC | 1049 CRAIG | ALICE | JIM WELLS | TX | 78272 | 1 | NO | 1717 | 1988-12-30 | 0 | 0 | 5000 | 4483.3163 | 10824.8212 | Null | 1 | 5 |  | 19881230 | 18 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | API-5L | N/A | 0 | 0 | NO DATA |  | B.F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | ACCIDENT BY OUTSIDE FORCE | NO |  | NO | 0 |  | NO |  |  | VEHICLE RAN OVER GAS METER IN ALLEY AND GAS IGNITED ON IMPACT.
2025-01-31 10:21 | YES | NO | 19890055 |  | 15462 | PHILADELPHIA ELECTRIC CO | 357 HAWARDEN ROAD | SPRINGFIELD | DELAWARE | PA | 19064 | 4 | NO | 455 | 1988-12-17 | 0 | 0 | 200000 | 179332.6524 | 432992.8498 | Null | 3 | 35 |  | 19881217 | 18 | 33 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.41 | ASA A21.7 | N/A | 1952 | 1952 | UNDER PAVEMENT |  | THEODORE A. ROEHRIG, SUPT., GAS DISTRIBUTION | 2158414962 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOT | NO |  | NO | 0 |  | NO |  |  | AT 0455 AM. ON DECEMBER 17, 1988, AN EXPLOSION OF LOW MAGNITUDE OCCURRED AT 357HAWARDEN ROAD IN SPRINGFIELD, AND A SMALL FIRE WAS EXTINGUISHED. THE FORCE OF THE EXPLOSION DAMAGED THE STRUCTURE OF THE HOUSE BEYOND REPAIR, ALTHOUGH THE HOUSE REMAINED STANDING WITH LITTLE WINDOW DAMAGE. AN EXCAVATION WAS MADE OVER THEMAIN ON NORWINDEN ROAD AND A CRACK WAS EXPOSED ON THE 4" CAST IRON MAIN. THE CAUSE OF THE CRACKED MAIN IS PRESUMED TO HAVE BEEN LARGE, 6" WIDE, TREE ROOT GROWING ALONG AND AROUND THE 4" CAST IRON MAIN. THE ESCAPING GAS APPARENTLY FOLLOWED THE WATER SERVICE TO THE HOUSE. THE WATER SERVICE CROSSED OVER THE MAIN WITHIN 4' OF THE CRACK. A TEMPORARY CLAMP WAS INSTALLED AND THE MAIN HAS NOW BEEN REPLACED.
2025-01-31 10:21 | YES | NO | 19890056 |  | 13710 | NORTHERN ILLINOIS GAS CO | 1277 MULBERRY | CRYSTAL LAKE | MCHENRY | IL | 60014 | 3 | NO | 1553 | 1989-01-14 | 0 | 0 | 200000 | 172349.4764 | 416132.199 | Null | 2 | 17 |  | 19890114 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.2 | N/A | N/A | 0 | 1947 | UNDER GROUND OR UNDER WATER |  | ARTHUR W. SWANSON, GENERAL SUPERVISOR SYSTEM OPERATING | 8154550271 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | USE AT 1277 MULBERRY AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING AN EXPLOSION AND FIRE, THE STRUCTURE AT 1277 MULBERRY WAS COMPLETELY DESTROYED WITH MINOR DAMAGE TO THE HOMES AT 1271 AND 1281.
2025-01-31 10:21 | YES | NO | 19890057 |  | 13710 | NORTHERN ILLINOIS GAS CO | 293 MILLARD AVE. | CRYSTAL LAKE | MCHENRY | IL | 60014 | 3 | NO | 1006 | 1989-01-12 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | Null | 2 | 4 |  | 19890112 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.2 | N/A | N/A | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | AUTHUR W. SWANSON, GENERAL SUPERVISOR SYSTEM OPERATING | 8154550271 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | NATURAL GAS FROM A GAS MAIN DAMAGED BY EXCAVATION EQUIPMENT MIGRATED INTO THE HOUSE AT 293 MLLARD AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING AN EXPLOSION. THE STRUCTURE AT 293 MILLARD WAS COMPLETELY DESTROYED WITH MINOR DAMAGE TO THE HOUSES ON EITHER SIDE.
2025-01-31 10:21 | NO | NO | 19890058 |  | 12390 | METROPOLITAN UTILITIES DISTRICT | 84TH & VALLEY STREET | OMAHA | DOUGLAS | NE | 68124 | 3 | NO | 800 | 1989-02-05 | 0 | 0 | 10000 | 8617.4738 | 20806.6099 | Null | 2 | 30 |  | 19890206 | 100 | 125 | BY TEST | 187 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | NO DATA |  | STEEL |  | 0.7 | 0.113 | N/A | N/A | 0 | 1962 | UNDER PAVEMENT |  | D. A. KOCOUREK, CLAIMS ADJUSTER | 4024498211 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | BREAK CAUSED BY THE WEATHER. FROST CAUSED STREET TO HEAVE, BREAKING 3/4" DRIPSTEM.
2025-01-31 10:21 | NO | NO | 19890067 |  | 12438 | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | OLD DAYTON PIKE (AREA OF EUSTICE RD.) | SODDY-DAISY | HAMILTON | TN | 37379 | 2 | NO | 530 | 1989-02-06 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  | 19890206 | 289 | 385 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 |  |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | JAMES E. HODGES, CHIEF ENGINEER | 6155974300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PIPE SPLIT LONGITUDINALLY FOR FULL LENGTH OF PIPE JOINT.
2025-01-31 10:21 | YES | YES | 19890068 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 8253 UTE HIGHWAY (HWY 66) | BOULDER |  | CO | 80501 | 1 | NO | 1345 | 1989-02-15 | 0 | 1 | 300000 | 258524.2147 | 624198.2984 | Null | 0 | 25 |  | 19890215 | 130 | 150 | BY TEST | 225 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.133 | API-5L | N/A | 0 | 1961 | ABOVE GROUND |  | MIKE IKELER, SUPERVISOR ENGINEERING GEN. DIST. | 3039382366 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | DURING REGUALTOR CHANG-OUT, THREADS ON NIPPLE UPSTREAM OF SERVICE VALVE WERE CRACKED. TWENTY FIVE MINS. LATER GAS WAS IGNITED FROM UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 19890069 |  | 4510 | EQUITABLE GAS CO | 2723 PALMGREEN AVENUE | MCKEESPORT | ALLEGHENY | PA | 15132 | 3 | NO | 1000 | 1989-02-01 | 1 | 1 | 300000 | 258524.2147 | 624198.2984 | Null | 0 | 35 |  | 19890201 | 0.4 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | E. F. MOSES, JR., MANAGER OF TECH. RESOURCE DEPT. | 4125535340 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INVESTIGATION OF THE EXPLOSION INDICATES NO EVIDENCE FO COMBUSTIBLES OVER THE COMPANY'S SERVICE LINE OR AROUND PERIMETER OF THE BUILDING. CUSTOMER'S SERVICE LINE (CURB TO METER) WAS PRESSURE TESTED AT 13" WATER COLUMN AND FOUND TO BE NOT LEAKING. HOUSE LINE COULD NOT BE TESTED DUE TO THE TOTAL DESTRUCTION OF THE BUILDING BY THE EXPLOSION. THE CAUSE OF THE EXPLOSION IS UNKNOWN AT THIS TIME AND IS CURRENTLY UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19890070 |  | 10037 | K P L GAS SERVICE | 10819 BENNINGTON | KANSAS CITY | JACKSON | MS |  | 3 | NO | 2205 | 1988-11-25 | 1 | 5 | 52000 | 46626.4896 | 112578.141 | Null | 3 | 57 |  | 19881125 | 28 | 58 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | OTHER | PIPE AT COLLAR | STEEL |  | 1 | 0 |  |  | 0 | 1955 | UNDER PAVEMENT |  | JAMES W. INGRAM, VP GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | A CIRCUMFERAL CRACK IN A 1" SERVICE LINE WAS FOUND AT A 1" COLLAR. THIS PIPE WASTAKEN BY CLINT C TRORPE II, WITH NTSB. WHILE A SPECIFIC CAUSE FOR THE FRACTURE IS NOT READILY AVAILABLE, A PROBABLE CAUSE WOULD BE GROUND SHIFT AND SETTLEMENT,COMBINED WITH TRAFFIC ON THE DRIVEWAY DIRECTLY OVER THE SERVICE. THE ENTIRE AREA SHOWS EVIDENCE OF GROUND SETTLEMENT OVER A PERIOD OF TIME.
2025-01-31 10:21 | YES | YES | 19890071 |  | 10037 | KANSAS POWER & LIGHT CO | 1306 HARDING | OAK GROVE | JACKSON | MS | 64075 | 3 | NO | 620 | 1989-02-10 | 2 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 2 | 30 |  | 19890210 | 15 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE | THREAD | STEEL |  | 1.24 | 0 | N/A | N/A | 0 | 1963 | UNDER GROUND OR UNDER WATER |  | JAMES W. INGRAM, VP GAS OEPRATIONS | 9132961959 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER |  | NO |  | NO | 0 |  | NO |  |  | VISUAL INSPECTION OF THE SERVICE LINE REVEALED A CIRCUMFERENTIAL CRACK, APPROXIMATELY 20' - 6" EAST OF THE METER RISER. THE CRACK WAS APPROXIMATELY TWO-THIRDSAROUND THE DIAMETER OF THE PIPE, AND HAD AN OPENING ON THE BOTTOM SIDE OF A NOMINAL AMOUNT. THERE WAS SOME DEFLECTION OF THE PIPE, BUT THE REASON IS UNKNOWN AT THIS TIME.
2025-01-31 10:21 | NO | NO | 19890073 |  | 12876 | MOUNTAIN FUEL SUPPLY CO | 500 EAST 100 NORTH | SANTAQUIN | UTAH | UT | 84655 | 3 | NO | 2000 | 1989-02-08 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19890209 | 0 | 93 | BY TEST | 140 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | OTHER | TEE STRAINER | OTHER | STATION EQUIPMENT | 0 | 0 | 300 ANSI | STRAINERS INC. | 1986 | 1986 | WITHIN/UNDER BUILDING |  | ROBERT L. REED, MANAGER DISTRIBUTION OPERATIONS | 8013706533 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN INLET STRAINER ON THE STATION OF A DEAD-END SYSTEM PLUGGED WITH GREASE CAUSING THE STATION WHICH FED THE TOWN OF SANTAQUIN, UTAH, TO SHUTDOWN. (659 METERS).
2025-01-31 10:21 | YES | YES | 19890079 |  | 22182 | WASHINGTON GAS LIGHT CO | 14TH AND S STREET, NW. | WASHINGTON |  | DC | 20005 | 3 | NO | 1115 | 1989-03-10 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19890310 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | DRIP/RISER |  | STEEL |  | 2 | 0.154 | API5L | N/A | 0 | 1989 | UNDER GROUND OR UNDER WATER |  | CLARENCE E. GOODSON, III - SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | UTILITY CONSTRUCTION,INC. WORKING FOR WASHNGTON GAS LIGHT COMPANY INSTALLING A VALVE GAUGE RISER ON A LIVE MAIN, HAD AN EMPLOYEE BURNED WHEN NATURAL GAS IGNITED. A CIVILIAN MOTORIST STOPPED AT A TRAFFIC SIGNAL ADJACENT TO THE WORK TRENCH,LIT A CIGARETTE AND THREW THE MATCH OUT OF THE WINDOW. THE GAS IGNITED BUT WASQUICKLY EXTINGUISHED. THE WORKMAN, JIMMY ROGER BRIMMER, RECEIVED SECOND DEGREEBURNS TO HIS FACE AND RIGHT WRIST. HE WAS TRANSPORTED BY PRIVATE VEHICLE TO HOWARD UNIVERSITY HOSPITAL AND RELEASED 48 HOURS LATER.
2025-01-31 10:21 | NO | NO | 19890080 |  | 8170 | INTERSTATE POWER CO | SOUTH OF AUTUM STREET | ALBERT LEA | FREEBORN | MN | 56007 | 3 | NO | 1655 | 1989-03-14 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19890315 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | JOINT | DRESSER | CAST IRON |  | 3 | 0.307 | ASTMD2513 | DUPONT | 1973 | 1973 | UNDER PAVEMENT |  | RAY P. RICHARDS, DIRECTOR, GAS OPERATIONS | 3195572218 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | DRESSER FITING (STYLE 38); APPARENTY LOOSENED OVER THE YEARS. INSTALLED TO CONNECT TWO SECTIONS OF DUPONT ALDYL "A" IN A RELINING INSTALLATION IN 1973. PART3 - TIME AND CONSTANT FLEXONG OF THE PLASTIC PIPE.
2025-01-31 10:21 | NO | NO | 19890081 |  | 4473 | ENERGAS CO | 502 HOWARD | MIDLAND | MIDLAND | TX | 79703 | 3 | NO | 200 | 1989-03-04 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19890304 | 10 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | VEHICLE RAN OVER METER SETTING. ESCAPING GAS IGNITED, BURNING CAR & NEARBY FENCE
2025-01-31 10:21 | NO | NO | 19890082 |  | 4499 | ENTEX INC | 5215 TEVEY STREET | LONGVIEW | GREGG | TX | 75605 | 3 | NO | 935 | 1989-02-18 | 0 | 0 | 6000 | 5170.4843 | 12483.966 | Null | 0 | 30 |  | 19890218 | 20 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | SDR 9.3 | DUPONT | 1982 | 1982 | UNDER GROUND OR UNDER WATER |  | B.R. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19890083 |  | 13782 | NORTHERN STATES POWER CO | 845 COUNTRYSIDE COURT SOUTH | FARGO | CASS | ND | 58100 | 3 | NO | 328 | 1989-03-02 | 0 | 0 | 7000 | 6032.2317 | 14564.627 | Null | 1 | 2 |  | 19890302 | 14 | 25 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ASTM D2513 | ALDYL "A" | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | BARBARA K. BELEW, GAS STANDARDS ENGINEER | 6120292261 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE FIRE AND SLIGHT EXPLOSION AT 845 COUNTRYSIDE TRAILER COURT SOUTH FARGE, ND, MARCH 2, 1989, WAS CAUSED BY A CUT IN THE 5/8" PE IDLE GAS SERVICE SERVING 847COUNTRYSIDE COURT SO., WHICH RUNS UNDER THE SOUTH EAST CORNER OF 845 CONTRYSIDECOURT SO. NSP WAS NOT CALLED FOR LOCATIONS WHEN BERNIE'S CAMPER CORREL INSTALLED THE TIEDOWN ANCHORS TO HOLD 845 CONTRYSIDE COURT SO, OCTOBER OF 1985. WHEN THE 5/8" PE SERVICE WAS CUT, THE SERVICE TEE EXCESS FLOW VALVE (PHUSE) CLOSED, ALTHOUGH SOME GAS DID ESCAPE AROUND THE PHUSE WITH THE SNOW BANKED AROUND THE MOBILE HOME, THE CONCENTRATION BUILT UP IN THE LOWER EXPLOSIVE LIMIT AND IGNITED. IGNITION IS NOT CONCLUSIVE.
2025-01-31 10:21 | YES | NO | 19890084 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 6228 MURIETTA AVENUE | VAN NUYS | LOS ANGELES | CA | 91401 | 3 | NO | 931 | 1989-03-07 | 0 | 0 | 150000 | 129262.1073 | 312099.1492 | Null | 1 | 2 |  | 19890307 | 40 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 | 0.113 | APISTD5L | N/A | 0 | 0 | ABOVE GROUND |  | L.M. STEWART, MANAGER IS DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TREE TRIMMING RESULTED IN LIMB FALLING ON AND BREAKING METER SET FITTING.
2025-01-31 10:21 | YES | NO | 19890086 |  | 11032 | LACLEDE GAS CO | 5217 PATTERSON RAOD | MEHLVILLE | ST LOUIS | MO |  | 3 | NO | 1700 | 1989-04-02 | 0 | 0 | 150000 | 129262.1073 | 312099.1492 | Null | 0 | 15 |  | 19890402 | 15 | 60 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0.04 | ASTMB-88 | N/A | 0 | 1970 | WITHIN/UNDER BUILDING |  | PAUL B. HUNKER, JR. / ASSOCIATE GENERAL COUNSEL | 3143420528 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | DE-ICING SALT | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19890087 |  | 10037 | K P L GAS SERVICE | 3202-04 EAST 6TH STREET | KANSAS | JACKSON | MO | 64106 | 3 | NO | 434 | 1989-04-02 | 0 | 0 | 75000 | 64631.0537 | 156049.5746 | Null | 1 | 43 |  | 19890402 | 0.3 | 2 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | METERS | OTHER | ALUMINUM & TIN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD H. TANGEMAN, ASS'T VP, GAS OPERATIONS | 9132966377 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | KPL GAS SERVICE WAS CALLED TO THE SCENE OF THE FIRE AT THIS APARTMENT BUILDING TO SHUT OFF THE FLOW OF GAS TO THE BUILDING. THERE WERE SEVEN METERS LOCATED INTHE BASEMENT OF THE BUILDING, WHICH APPARENTLY MELTED,DUE TO THE EXTENSIVE HEATOF THE FIRE, AND NATURAL GAS SUBSEQUENTLY IGNITED AT THE METER LOCATION. THE GAS WAS SHUT OFF AT THE CURB VALVE. THE KANSAS CITY FIRE DEPARTMENT HAS INDICATEDTHAT THE POINT OF ORIGIN OF THE FIRE WAS IN A STORAGE AREA IN THE BASEMENT, IN A LOCATION NORTH OF THE GAS METERS. THE FIRE DEPARTMENT ALSO INDICATED THE FIRE WAS DELIBERATELY SET AND THE POLICE HAD A SUSPECT.
2025-01-31 10:21 | NO | NO | 19890089 |  | 10037 | K P L GAS SERVICE | 155 & 71 HIGHWAY | KANSAS CITY | JACKSON | MO | 64030 | 2 | NO | 1410 | 1989-03-08 | 0 | 0 | 9400 | 8100.4254 | 19558.2134 | Null | 3 | 56 |  | 19890308 | 100 | 125 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.172 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JAMES W. IMGRAM, V.PV GAS OPERATIONS. | 9132961959 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-01-12 | YES | 1 |  | YES |  |  | WRITTEN REPORT WAS NOT SUBMITTED WITHIN THE 20 DAY TIME PERIOD, SINCE COMPANY WAS NOT AWARE THAT THE ACCUMULATED TOTAL COSTS WOULD EXCEED $5,000. DAMAGE OCCURRED OUTSIDE OF AREA OF LOCATES.THIRD PARTY WAS REMOVING DIRT WITH BULLDOZER AND STRUCK GAS MAIN.
2025-01-31 10:21 | NO | NO | 19890090 |  | 4473 | ENERGAS CO | 2707 CALDERA | MIDLAND | MIDLAND | TX | 79707 | 3 | NO | 1236 | 1989-03-25 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19890325 | 10 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | SERVICE RISER WAS DAMAGED WHILE FIRE DEPT. ATTENDED TO NEARBY GRASS FIRE. EXCAPING GAS WAS IGNITED BY FIRE.
2025-01-31 10:21 | NO | NO | 19890091 |  | 18532 | SOUTHERN UNION GAS CO | 3306 BEE CAVES ROAD | WESTLAKE HILLS | TRAVIS | TX | 78746 | 3 | NO | 1038 | 1989-03-24 | 0 | 0 | 250 | 215.4368 | 520.1652 | YES | 0 | 57 |  | 19890324 | 42 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | YARD LINE | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 3408 | PLEXCO | 0 | 1989 | UNDER GROUND OR UNDER WATER |  | DENNIS WORLEY, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | WHILE EXCAVATING WITH CASE 480 BACKHOE TO INSTALL ELECTRIC CONDUCT AT NEW SHOPPING CENTER,CONTRACTOR DAMAGED 2" PE SERVICE LOCATED ON WEST SIDE OF PRIVATE PROPERTY.
2025-01-31 10:21 | YES | YES | 19890092 |  | 1048 | BAINBRIDGE GAS DEPT, CITY OF | 710 GORDON ST. | BIANBRIDGE |  | GA | 31717 | 2 | NO | 1245 | 1988-11-13 | 0 | 1 | 15000 | 13449.9489 | 32474.4637 | Null | 5 | 0 |  | 19881113 | 20 | 20 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2306 | PLOYETHYLENE PROD. | 0 | 1988 | OTHER | LEAK UNDER BUILDING | RONALD STARLING, GAS SUPERINTENDENT | 9122482000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1988-07-15 | YES | 3 | PAINT | YES |  |  | EXPLOSION OCCURRED ON 11/13/88 IN LANDMARK APTS. - D16. AFTER GAS PERSONNEL WERE NOTIFIED AREA WAS MADE SAFE BY CHECKING FOR AREA OF POSSIBLE LEAK AND AFTER VERIFICATION OF A LEAK, THE MAIN VALVE SUPPLYING APARTMENTS WAS SHUT DOWN. NEXT, TELEPHONE CALLS WERE MADE TO AUTHORIZED PERSONNEL WITHIN HOURS TO THE SITE AND PROCEEDED WITH ALL NECESSARY INSPECTIONS.
2025-01-31 10:21 | YES | YES | 19890093 |  | 10037 | K P L GAS SERVICE | 3030 KENTUCKY | TOPEKA | SHAWNEE | KS | 66605 | 3 | NO | 420 | 1989-03-29 | 1 | 1 | 100000 | 86174.7382 | 208066.0995 | Null | 4 | 20 |  | 19890329 | 15 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.25 | N/A | N/A | 0 | 1951 | UNDER GROUND OR UNDER WATER |  | JAMES W. INGRAM, VP GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON WEDNESDAY, MARCH 29, 1989, A COMPANY DISPATCHER RECEIVED A CALL FROM THE FIRE DEPARTMENT, INDICATING THAT AN EXPLOSION AND FIRE HAD OCCURRED AT 3030 KENTUCKY. COMPANY PERSONNEL RESPONDED, CONFIRMED THE DAMAGE, AND TOOK STEPS TO CONTROLTHE EMERGENCY. DURING THE LEAK INVESTIGATION,SUBSEQUENT TO THE EXPLOSION AND FIRE, A 2" CAST IRON NATURAL GAS MAIN IN FRONT OF 3030 KENTUCKY, WAS FOUND TO BE BROKEN, APPROXIMATELY 8' SOUTH OF THE DRIVEWAY. THE CAUSE OF THE EXPLOSION AND FIRE HAS YET TO BE DETERMINED. A SECTION OF THE BROKEN CAST IRON WAS TAKEN TO WASHINGTON, DC, BY THE NTSB, FOR TESTS. ALTHOUGH THE TESTS ARE COMPLETE, THE RESULTS ARE NOT AVAILABLE TO COMPANY AT THIS TIME.
2025-01-31 10:21 | YES | NO | 19890094 |  | 15359 | PEOPLES NATURAL GAS | PROPANE/AIR PEAK SHAVING PLANT | COUNCIL BLUFFS | POTTAWATTAMIE | IA | 51502 | 1 | NO | 2103 | 1989-03-27 | 0 | 0 | 120000 | 103409.6859 | 249679.3194 | Null | 1 | 57 |  | 19890328 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | PLANT CONTROL ROOM | VALVE |  | NO DATA |  | 0 | 0 |  |  | 1975 | 1975 | WITHIN/UNDER BUILDING |  | JIM NOVACEK, DIRECTOR, IOWA AREA OPERATION ENGINEERING | 5152236010 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS SAMPLES WERE TAKEN AND ANALYZED AT STRATEGIC LOCATIONS IN THE PLANT. THE NATURAL GAS LINE FEEDING A FURNACE IN THE ROOM WHERE THE EXPLOSION TOOK PLACE HADNO LEAKS. THEREFORE, IT IS CURRENTLY BELIEVED THAT PROPANE WAS IGNITED. TWO VALVES ON THE PROPANE SYSTEM ARE STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19890095 |  | 22763 | WISCONSIN GAS CO | 521 NORTH STREET | NEKOOSA | WOOD | WI | 54457 | 3 | NO | 2035 | 1989-03-22 | 1 | 2 | 75000 | 64631.0537 | 156049.5746 | Null | 3 | 0 |  | 19890323 | 56 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | D2513 | CONTINENTAL IND. | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | GREGORY B. SCHROEDER, P.E. - PLANNING ENGINEER | 4142916729 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | PIPE OUT OF COUPLING | ON MARCH 22, 1989 AT APPROXIMATELY 8:35 P.M. THERE WAS AN EXPLOSION AT 521 NORTH STREET, IN THE CITY OF NEKOOSA, WOOD COUNTY, WI. MR. GORDON KRUBSACK, DIED ASA RESULT OF THE EXPLOSION. OLGA KRUBSACK AND KATHY DAVIS SUFFERED SECOND AND THIRD DEGREE BURNES AND WERE HOSPITALIZED. A 5/8" PE COMPRESSION COUPLING WAS FOUND SEPARATED FROM THE 5/8" PE GAS SERVICE PIPE TO THE HOUSE APPROXIMATELY 30 FEET FROM THE HOUSE.
2025-01-31 10:21 | YES | NO | 19890096 |  | 1088 | BALTIMORE GAS & ELECTRIC CO | 4300 FAIRVIEW AVENUE | BALTIMORE |  | MD | 21216 | 3 | NO | 1837 | 1989-03-18 | 0 | 0 | 150000 | 129262.1073 | 312099.1492 | Null | 2 | 37 |  | 19890324 | 0.3 | 0.3 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | NO DATA |  | 0 | 0 |  | AMERICAN METER | 1951 | 1967 | WITHIN/UNDER BUILDING |  | EDWIN L. POFFENGERGER, GENERAL SUPERVISOR | 3015612790 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 1830 HOURS ON 3/18/89 BALTIMORE CITY FIRE DEPARTMENT RECEIVED A NOTIFICATION OF FIRE AT THE ABOVE ADDRESS. A BALTIMORE CITY POLICE OFFICER WAS THE FIRST TO ARRIVED ON THE SCENE. HE OBSERVED HEAVY FIRE COMING FROM FRONT BASEMENT WINDOW. SHORTLY THEREAFTER HE HEARD AN EXPLOSION WITH FIRE ENGULFING THEHOUSE. BOTH SIDE WALLS AND THE REAR WALL OF THE STRUCTURE WERE BLOWN OUT. IT APPEARS THAT THERE WAS A FIRE IN THE FRONT RIGHT CORNER OF THE BASEMENT WHICH MELTED THE METER THUS FILLING THE HOUSE WITH GAS WHICH SUBSEQUENTLY IGNITED AND EXPLODED. THE ABOVE GROUND STRUCTURE WAS COMPLETELY DESTROYED AND THE BASEMENT WAS FILLED WITH WATER. THE FLAMES WERE EXTINGUISHED BY 2115 HOURS. THE GAS SERVICE TO THE BUILDING WAS CUT OFF BY 2345 HOURS. NO ONE WAS IN THE HOUSE AT THE TIME OF THE FIRE AND EXPLOSION.
2025-01-31 10:21 | YES | NO | 19890097 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 8010 FLINT RIDGE RD | LITTLE ROCK | PULASKI | AR | 72210 | 3 | NO | 1445 | 1989-03-30 | 0 | 0 | 85000 | 73248.5275 | 176856.1846 | Null | 1 | 15 |  | 19890330 | 35 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER SERVICE | OTHER | PIPE THREAD BROKE | STEEL |  | 1 | 0.133 |  |  | 0 | 0 | OTHER | UNDER CONCRETE WALK | JIM BREWER - CODES & PROCEDURES CORRDINATOR | 5013774771 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | BACKHOE OPERATOR WAS INSTALLING SEWER SERVICE LINE. BACKHOE BUCKET HOOKED CUSTOMERS GAS SERVICE LINE. GAS LINE WAS PULLED AND BROKEN OUT OF 1" ELL AT BASE OF METER RISER NEXT TO HOUSE.
2025-01-31 10:21 | YES | YES | 19890098 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 1007 EDDIEMEE STREET | HOT SPRINGS | GARLAND | AR | 71901 | 3 | NO | 2100 | 1989-03-06 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19890307 | 34 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | JOINT | COMPRESSION | STEEL |  | 1 | 0.4 | STYLE 90 | DRESSER | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | JIM BREWER/ CODES & PROCEDURES COORDINATOR | 5013774771 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER ATTEMPTING TO READ HIS WATER METER LIT MATCH SO HE COULD SEE DOWN IN WATER METER BOX. NATURAL GAS HAD COLLECTED BENEATH WATER METER BOX LID. GAS IGNITED AND FLASH BURNED CUSTOMER.
2025-01-31 10:21 | YES | YES | 19890099 |  | 18536 | SOUTHWEST GAS CORP | 250 VINE STREET | FERNLEY | LYON | NV | 89408 | 2 | NO | 1037 | 1989-03-01 | 0 | 1 | 65000 | 56013.5798 | 135242.9647 | Null | 0 | 10 |  | 19890301 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC-SCH DM | 0.5 | 0.062 | DM-TYPE2 | KRALOY CONTROL | 1964 | 1964 | WITHIN/UNDER BUILDING |  | LARRY GIBSON - DISTRICT MANAGER | 7024235594 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | 1/8'' HOLE IN PVC | NO |  | NO | 0 |  | NO |  |  | 1/8" HOLE IN PVC PIPE NEXT TO COUPLING. CUSTOMER CONSTRUCTED ROOM ADDITIONOVER OPERATOR'S 1/2" PVC LINE.
2025-01-31 10:21 | YES | YES | 19890100 |  | 21190 | VERMONT GAS SYSTEMS INC | 47 GREENWOOD AVENUE | ESSEX JUNCTION | CHITTENDEN | VT | 05452 | 3 | NO | 920 | 1989-03-09 | 0 | 1 | 175000 | 150805.7919 | 364115.6741 | Null | 0 | 40 |  | 19890309 | 60 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | JOINT | COMPRESSION | STEEL |  | 0.75 | 0.113 | STYLE 90 | DRESSER | 1978 | 1979 | UNDER GROUND OR UNDER WATER |  | MICHAEL E. SULLIVAN, VICE PRESIDENT - OEPRATIONS | 8028634512 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | FROST ACTION PULLED A 3/4" STEEL SERVICE FROM A COMPRESSION OUTLET SERVICE TEE. TOP OF MAIN WAS 2' 10" IN DEPTH AT THIS LOCATION.
2025-01-31 10:21 | NO | NO | 19890101 |  | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 723 FLOWE STREET | GASTONIA | GASTON | NC | 28054 | 3 | NO | 1710 | 1989-02-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19890302 | 42 | 90 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 | 043 | ROCKWELL | 1965 | 1966 | ABOVE GROUND |  | JOHN WISTER BROWN - V.P. ENGINEERING | 7048647732 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A ROCKWELL 043 3/4"X1" RIGHT ANGLE BODY WITH IRV REGULATOR FAILED AT THE CUSTOMER'S METER SET ALLOWING 42 PSIG PRESSURE INTO THE HOUSE FUEL LINE, WITH A RESULTING FIRE. ESTIMATED DAMAGE TO HOUSE CAUSED BY FIRE IS $30,000.00.
2025-01-31 10:21 | YES | NO | 19890117 |  | 1088 | BALTIMORE GAS & ELECTRIC CO | 3610, 12, 14, 18 EASTERN AVENUE | BALTIMORE |  | MD | 21224 | 3 | NO | 2106 | 1989-06-05 | 0 | 0 | 150000 | 129262.1073 | 312099.1492 | Null | 2 | 20 |  | 19890606 | 0.3 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | HOUSE LINE | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWIN L. POFFEBERGER, GENERAL SUPERVISOR | 3015612790 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | ORIGIN OF THE FIRE WAS LIGHTNING OR ELECTRICAL FAILURE IN 3618 EASTERN AVENUE.SUBSEQUENT FIRE DESTROYED 3618, 3614, 3612 EASTERN AVENUE AND DAMAGED 3610 EASTERN AVENUE. WHEN THE ROOF OF 3618 COLLAPSED, A HOUSE LINE WAS BROKEN ON THE SECOND FLOOR WHICH FUELED THE FIRE. GAS METER WAS TURNED OFF BY BALTIMORE CITY FIRE DEPT.
2025-01-31 10:21 | YES | YES | 19890124 |  | 13782 | NORTHERN STATES POWER CO | 1720 CASE (CASE & FLANDRAU) | ST PAUL | RAMSEY | MN | 55117 | 2 | NO | 745 | 1989-05-25 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 30 |  | 19890525 | 0.2 | 0.28 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 |  |  | 0 | 1912 | UNDER GROUND OR UNDER WATER |  | BARBARA K. BELEW, GAS STANDARDS ENGINEER | 6122292261 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-05-22 | YES | 3 | PAINT | YES |  |  | AS A RESULT OF SEWER WORK IN THIS AREA, A 4" CI MAIN WAS DAMAGED. NATURAL GAS MIGRATED FROM THE LOCATION OF THE DAMAGED PIPE AND FITTINGS, TO A MANHOLE. THE NATURAL GAS WAS IGNITED BY AN UNKNOWN SOURCE, SERIOUSLY BURNING A SEWER WORKER IN THE MANHOLE.
2025-01-31 10:21 | YES | YES | 19890125 |  | 4473 | ENERGAS CO | 1510 WEIDEL | LITTLEFIELD | LAMB | TX | 79339 | 3 | NO | 1210 | 1989-04-03 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19890403 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GARY C. AXTON, ENGINEER | 8067414200 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE WAS REPORTED AT 1510 WEIDEL ON APRIL 3, 1989. ROBERT HOGUE OWNER OF THIS RENT HOUSE WAS DOING SOME REPAIR WORK UNDER THE HOUSE, WHEN HE THOUGHT HE SMELLED GAS AND THEN LIT A MATCH. HE DROVE HIMSELF TO THE HOSPITAL, AND THE FIRE WAS REPORTED FROM THE HOSPITAL. HE WAS HOSPITALIZED WITH 1ST AND 2ND DEGREE BURNS. THE FIRE DEPARTMENT TOOK THE CALL ABOUT 12:00 NOON. A SMALL EXPLOSION OCCURRED DURING THE FIRE WHICH WAS THOUGHT TO HAVE BEEN CAUSED BY A GAS CAN OR A MOWERGAS TANK. THIS INJURY WAS REPORTED TO ENERGAS AT ABOUT 8:00 P.M. THE RAILROAD COMMISSION WAS NOTIFIED OF THE INCIDENT AT ABOUT 9:30 P.M. WE DO NOT ANTICIPATE ANY FURTHER REPORT PERTAINING TO THIS INCIDENT.
2025-01-31 10:21 | NO | NO | 19890126 |  | 18532 | SOUTHERN UNION GAS CO | 6001 WESTCREEK DRIVE | AUSTIN | TRAVIS | TX | 78749 | 3 | NO | 917 | 1989-05-19 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 33 |  |  | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER'S YARD LINE | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PLEXCO | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | DENNIS WORLEY, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR TRENCHING WITH BACKHOE IN SCHOOL YARD FOR MODIFICATION TO SCHOOL BLDG. STRUCK AND DAMAGED 2" P.E. LINE SERVING IND. METER AT SCHOOL.
2025-01-31 10:21 | NO | NO | 19890127 |  | 18532 | SOUTHERN UNION GAS CO | OLD JOLLYVILLE ROAD AT BUSINESS PARK DR. | AUSTIN | TRAVIS | TX | 78759 | 3 | NO | 1525 | 1989-04-12 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 31 |  | 19890412 | 200 | 346 | BY TEST | 600 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | STEEL |  | 12.75 | 0.25 | API-5L-B | N/A | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | DENNIS WORLEY, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER |  | YES | 1989-03-30 | YES | 3 | PAINT | NO |  |  | RECEIVED ONE-CALL FROM CONTRACTOR ON 3/30/89 REQUESTING LOCATORS TO MEET WITH CONTRACTOR ON 4/3/89 AT 10 A.M. ON LOCATION. LOCATOR MET WITH CONTRACTOR AND PROVIDED LOCATIONS AS REQUESTED ON 4/3/89.
2025-01-31 10:21 | YES | YES | 19890128 |  | 5670 | FULTON BOARD OF PUBLIC WORKS | 312 W. 4TH STREET | FULTON | CALLAWAY | MO | 65251 | 3 | NO | 1617 | 1989-01-07 | 2 | 0 | 21000 | 18096.695 | 43693.8809 | Null | 0 | 30 |  | 19890108 | 25 | 0 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | SCHEDULE 40 | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | BYRON DYSART, GENERAL SUPERINTENDENT | 3146426655 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19890129 |  | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | TANGLEWOOD AT DILL COURT | COLUMBIA | RICHLAND | SC | 29206 | 1 | NO | 1150 | 1989-05-17 | 0 | 2 | 500 | 430.8737 | 1040.3305 | Null | 0 | 30 |  | 19890517 | 17 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | CUT | POLYETHYLENE PLASTIC |  | 20 | 0.216 | SDR 11-2306 | PLEXCO | 1988 | 1989 | UNDER GROUND OR UNDER WATER |  | REBECCA L. HOLT, MANAGER | 8037483907 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 | PAINT | YES
2025-01-31 10:21 | YES | YES | 19890130 |  | 12684 | MONTANA - DAKOTA UTILITIES CO | 5400 SOUTHGATE DR. | BILLINGS | YELLOWSTONE | MT | 59102 | 3 | NO | 111 | 1989-04-09 | 0 | 2 | 1000000 | 861747.3822 | 2080660.9948 | Null | 1 | 0 |  | 19890409 | 54 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | IN LAUNDRY ROOM | HENRY A. MEYERS, GAS SUPERINTENDENT | 4062551350 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION & FIRE OCCURRED AT SUPER 8 LODGE, 5400 SOUTHGATE DR., BILLINGS, MT, AT APPROXIMATELY 1:11 A.M., 4/9/89. AFTER THOROUGH INVESTIGATION, THE BILLINGS FIRE DEPARTMENT DETERMINED NATURAL GAS EXPLOSION OCCURRED IN BUILDING LAUNDRY ROOM AS A RESULT OF EITHER LEAKING HOUSE PIPING OR DRYER MALFUNCTION.
2025-01-31 10:21 | YES | NO | 19890131 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2727 E. STREET | FRESNO | FRESNO | CA | 93705 | 3 | NO | 2109 | 1989-03-01 | 0 | 0 | 100500 | 86605.6119 | 209106.43 | Null | 3 | 5 |  |  | 60 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | RV FIRE SET HOUSE ON FIRE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | W.R. MAZOTTI, V.P., GAS & ELEC. TECH. SVS. | 4159737000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | RV CAUGHT FIRE, SETTING THE HOUSE ON FIRE. OUR METER CAUGHT ON FIRE AFTER THE HOUSE WAS ALMOST COMPLETELY BURNED. THE FIREMEN WERE UNABLE TO TURN OFF THE GASAT THE METER BECAUSE THE SERVICE VALVE BROKE. THE METER FIRE OCCURRED AFTER THE HOUSE WAS ALMOST COMPLETELY BURNED.
2025-01-31 10:21 | NO | NO | 19890132 |  | 11800 | LOUISIANA GAS SERVICE CO | 59 AND ORLEANS AVENUE | MANDEVILLE | ST TAMMANY | LA | 70448 | 3 | NO | 1255 | 1989-05-09 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 5 |  |  | 65 | 80 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | MUELLER HOT TAP 2" | STEEL |  | 4 | 0.219 | API-5L | N/A | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-04-07 | YES | 2 |  | YES |  |  | CONTRACTOR BROKE 2" HOT TAP OFF 4" STEEL MAIN WHILE DIGGING A DRAINAGE DITCH. OPERATOR'S EMPLOYEE HAD PREVIOUSLY BEEN ON SITE AND MARKED THE SITE WITH STAKES. STAKES WERE IN PLACE AT TIME OF BREAK.
2025-01-31 10:21 | YES | YES | 19890133 |  | 1800 | BROOKLYN UNION GAS CO | 8908 - 103RD AVENUE | OZONE PARK | QUEENS | NY | 11417 | 1 | NO | 1930 | 1988-11-17 | 0 | 2 | 0 | 0 | 0 | Null | 9 | 0 |  | 19881117 | 0.3 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | N/A | N/A | 0 | 1924 | UNDER PAVEMENT |  | JOSEPH J. MARAZZO, SECTION MANAGER, DISTRIBUTION | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TWO PEOPLE WERE INJURED WHEN VAPORS FROM GLUE IGNITED IN THE BASEMENT OF 8908 -103RD AVENUE, QUEENS, NEW YORK ON NOVEMBER 17, 1988. NATURAL GAS READINGS WEREPRESENT AT THE FRONT WALL OF THE BASEMENT. A BROKEN 6" C.I.B.S. LP GAS MAIN WAS FOUND ON 103RD AVENUE AT 132' WEST OF THE WEST CURB LINE OF 90TH STREET. A MOBILE LEAK SURVEY WAS PERFORMED ON NOVEMBER 9,1988 AND A WALKING SURVEY OF THE AREA WAS COMPLETED ON AUGUST 10, 1988. NO LEAKS WERE DETECTED AT THAT TIME.
2025-01-31 10:21 | YES | YES | 19890134 |  | 7040 | HAMILTON GAS DEPT, CITY OF | 2039 DIXIE HIGHWAY | HAMILTON | BUTLER | OH | 45011 | 3 | NO | 357 | 1989-05-20 | 0 | 2 | 60000 | 51704.8429 | 124839.6597 | Null | 1 | 0 |  | 19890520 | 0.36 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER |  | OTHER |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JOHN W. LIVER, GAS & WATER DIST. SUPT. | 5138685902 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 1" VALVE IN THE KITCHEN OF THE DOWNSTAIRS APARTMENT WAS OPENED BY TENANT IN AN ATTEMPT TO COMMIT SUICIDE. EXPLOSION WAS CAUSED BY TENANT LIGHTING CIGARETTE.
2025-01-31 10:21 | YES | NO | 19890135 |  | 8240 | IOWA ELECTRIC LIGHT & POWER CO | 203 WATER STREET | CAMBRIDGE | STORY | IA | 50046 | 3 | NO | 710 | 1989-02-24 | 0 | 0 | 75000 | 64631.0537 | 156049.5746 | Null | 14 | 30 |  | 19890225 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | SCH 40 - API 5L | N/A | 1966 | 1966 | UNDER PAVEMENT |  | RON ESTABROOK, ASST. MGR OF GAS OPERATIONS | 5157545843 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-11-04 | YES | 3 | PAINTED | NO |  |  | WHEN OUR CREWS ARRIVED ON THE SCENE THEY WERE UNABLE TO DETECT ANY GAS IN THE GROUND. IT WAS OVER AN HOUR LATER THAT ANY GAS WAS DETECTED AND THE SEARCH FOR A LEAK WAS THEN INITIATED. THE CUSTOMER HAD BEEN HAVING FURNACE TROUBLE DURING THE DAY, AND THERE WAS A POSSIBILITY THAT A MALFUNCTION OF THE FURNACE CAUSED THE EXPLOSION AND THE SHOCK IN THE GROUND CAUSED THE GAS PIPE TO BREAK WHERE IT HAD BEEN DAMAGED. INVESTIGATION OF THE FURNACE WAS VERY DIFFICULT BECAUSE OF DAMAGE.
2025-01-31 10:21 | YES | NO | 19890137 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | CHAGAL AVE. & TRUMAN STREET | LANCASTER | LOS ANGELES | CA | 93534 | 3 | NO | 1424 | 1989-03-25 | 0 | 0 | 150000 | 129262.1073 | 312099.1492 | Null | 0 | 0 |  | 19890325 | 40 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | DUPONT | 0 | 1984 | UNDER PAVEMENT |  | L.M. STEWART , MANAGER OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | INCIDENT WAS THE RESULT OF IMPORPER ALIGNMENT AND POOR FUSION OF A 2" BRANCHINGSADDLE CONNECTION TO A 2" POLYETHYLENE PLASTIC MAIN.
2025-01-31 10:21 | YES | YES | 19890138 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | MORRIS AVENUE/ EAST 167 STREET | BRONX |  | NY | 10456 | 4 | NO | 855 | 1989-03-28 | 0 | 4 | 0 | 0 | 0 | Null | 0 | 5 |  |  | 0.3 | 0.4 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER |  | CAST IRON |  | 16 | 0.6 | N/A | N/A | 0 | 1904 | UNDER GROUND OR UNDER WATER |  | DOMINIC N. CASTELLANO, ACTING CHIEF GAS ENGINEER | 2124604464 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS IGNITION CAUSED NO DAMAGE TO COMPANY OR OUTSIDE PARTY PROPERTY.
2025-01-31 10:21 | YES | YES | 19890139 |  | 18532 | SOUTHERN UNION GAS CO | 1012 SOUTH HILLS STREET | EL PASO | EL PASO | TX | 79901 | 3 | NO | 350 | 1989-06-17 | 0 | 1 | 35000 | 30161.1584 | 72823.1348 | Null | 0 | 15 |  | 19890617 | 20 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RAPHAEL N. CONFER , DISTRIBUTION OFFICE SUPRV. | 9155446300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS ESCAPING FROM DISCONNECTED SPACE HEATER SUPPLY LINE AND TWO (2) OPEN RANGE BURNER VALVES APPARENTLY ACCUMULATED INSIDE THE PRIVATE RESIDENCE RESULTING IN AN EXPLOSION WHICH DESTROYED APPROXIMATELY 75% OF THE STRUCTURE. AUTHORITIES SUSPECT THE INCIDENT WAS THE RESULT OF AN ATTEMPTED SUICIDE. THE GAS COMPANY'S INVOLVEMENT WAS STRICTLY ASSISTING THE FIRE MARSHALL IN THE INVESTIGAT
2025-01-31 10:21 | YES | YES | 19890140 |  | 4473 | ENERGAS CO | 409 SE 3RD | DIMMITT | CASTRO | TX | 79027 | 3 | NO | 1510 | 1989-03-27 | 1 | 0 | 20000 | 17234.9476 | 41613.2199 | Null | 0 | 30 |  | 19890327 | 5 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID H. DOGGETTE, P.E. | 8063783381 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE OF UNKNOWN ORIGIN RESULTING IN ONE FATALITY. SUBSEQUENTLY, FIRE MARSHALL DETERMINED FIRE WAS CAUSED BY COMBUSTIBLES PLACED NEAR SPACE HEATER.
2025-01-31 10:21 | NO | NO | 19890141 |  | 4473 | ENERGAS CO | FM 1151 AT FM 1541 | AMARILLO | RANDALL | TX | 79118 | 3 | NO | 1200 | 1989-04-18 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19890418 | 90 | 150 | BY TEST | 225 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | UNKNOWN | STEEL |  | 2 | 0.154 | API5L-A25 | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN UNDERGROUND VALVE SERVED TWO CHECK METERS. THE EMPLOYEE WAS UNAWARE OF THIS AND THOUGHT THIS VALVE TURNED OFF THE BYPASS FOR ONLY THE METER HE WAS TESTING.
2025-01-31 10:21 | YES | YES | 19890143 |  | 4473 | ENERGAS CO | 736 N. ZIMMERS | PAMPA | GRAY | TX | 79065 | 3 | NO | 2100 | 1989-01-26 | 0 | 2 | 2000 | 1723.4948 | 4161.322 | Null | 0 | 30 |  | 19890126 | 0.5 | 1 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FLASH FIRE OF UNKNOWN ORIGIN CAUSED MAJOR DAMAGE TO HOME. A MAN AND WOMANOCCUPING HOUSE WERE BURNED. A SHUT IN OF CUSTOMER PIPING AFTER INCIDENT SHOWED LEAK OF 3 CFH.
2025-01-31 10:21 | NO | NO | 19890144 |  | 4473 | ENERGAS CO | 101 S. LINCOLN | AMARILLO | POTTER | TX | 79101 | 3 | NO | 519 | 1989-01-20 | 0 | 0 | 30000 | 25852.4215 | 62419.8298 | Null | 0 | 56 |  | 19890120 | 0 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNKNOWN ORIGIN STARTED IN BASEMENT OF VACANT WAREHOUSE. THE GAS METER HAD BEEN REMOVED IN JUNE 1986.
2025-01-31 10:21 | NO | NO | 19890145 |  | 4473 | ENERGAS CO | 905 WOOD STREET | AMHERST | LAMB | TX |  | 3 | NO | 2245 | 1989-01-20 | 0 | 0 | 10000 | 8617.4738 | 20806.6099 | Null | 0 | 30 |  | 19890121 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414411 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE FIRE HAD ORIGINATED IN THE HOT WATER HEATER CLOSET. DEBRIS WAS FOUND ONTHE FLOOR AROUND THE HOT WATER HEATER. IT HAD APPARENTLY CAUGHT FIRE CAUSING THE HOUSE TO CATCH FIRE. THE FIRE HAD MELTED THE ALUMINUM TUBING ATTACHED TO THE HOT WATER HEATER AND THE FIRE DEPARTMENT HAD TURNED OFF THE GAS METER.
2025-01-31 10:21 | NO | NO | 19890147 |  | 2580 | COLEMAN NATURAL GAS CO | 22402 MAIN BLVD. | TOMBALL | HARRIS | TX | 77375 | 1 | NO | 1230 | 1988-11-12 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  |  | 0 | 25 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 1970 | ABOVE GROUND |  | JACKIE SMITH | 4093729471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | CAR BACKED OVER METER, REG. SET & MAIN LINE.
2025-01-31 10:21 | NO | NO | 19890148 |  | 2580 | COLEMAN NATURAL GAS CO | FAITH OUR REACH CHURCH, HWY 6 | NAVASOTA | GRIMES | TX | 77868 | 1 | NO | 2000 | 1988-06-13 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  |  | 28 | 28 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | VALVE |  | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | JACKIE SMITH | 4093729471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | MOWING GRASS WITH TRACTOR, TAIL WHEEL WENT THROUGH METER PIN BROKE OFF REGULA
2025-01-31 10:21 | NO | NO | 19890149 |  | 2580 | COLEMAN NATURAL GAS CO | 16008 LUTHERAN SCHOOL RD. | TOMBALL | HARRIS | TX | 77373 | 1 | NO | 1145 | 1988-10-27 | 0 | 0 | 0 | 0 | 0 | Null | 2 | 0 |  |  | 25 | 25 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | JACKIE SMITH | 4093729471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | CUT TREES DOWN, DOWN ON MAIN LINE TAP, BROKE OFF METER & REG . SET ON MAIN LINE TAP.
2025-01-31 10:21 | NO | NO | 19890150 |  | 2580 | COLEMAN NATURAL GAS CO | 14702 HERMIT THURSH | TOMBALL | HARRIS | TX | 77375 | 1 | NO | 830 | 1988-11-03 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  |  | 40 | 40 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | 1" | STEEL |  | 0 | 0 |  |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | JACKIE SMITH | 4093729471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DOGS PLAYING IN BACKYARD BROKE OFF RISER GOING TO BAR-Q PIT.
2025-01-31 10:21 | NO | NO | 19890151 |  | 2580 | COLEMAN NATURAL GAS CO | 30014 DRAGON FLY | TOMBALL | HARRIS | TX | 77375 | 1 | NO | 1245 | 1988-09-17 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19880917 | 40 | 40 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JACKIE SMITH | 4093729471 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES |  |  | MOVING TRUCK BACKED OVER METER, REG SET & MAIN.
2025-01-31 10:21 | NO | NO | 19890152 |  | 4473 | ENERGAS CO | 1/4 MILE EAST OF LOOP 338 ON SPUR 191 | ODESSA | ECTOR | TX | 79760 | 3 | NO | 1045 | 1989-04-26 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 15 |  | 19890426 | 90 | 150 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 | UNKNOWN | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | A CONTRACTOR DRILLING POST HOLES HIT THE GAS MAIN.
2025-01-31 10:21 | NO | NO | 19890153 |  | 4473 | ENERGAS CO | 50TH & UPLAND | LUBBOCK | LUBBOCK | TX |  | 2 | NO | 1350 | 1989-04-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19890427 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | ABS | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414411 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | YES | 0 | PIPELINE MARKERS & METERS | NO |  |  | RANGER CONSTRUCTION CO. RUPTURED GAS LINE WHILE DIGGING DITCH FOR TELEPHONE LINE.
2025-01-31 10:21 | NO | NO | 19890157 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 14414 SHANNON RIDGE | HOUSTON | HARRIS | TX | 77062 | 3 | NO | 940 | 1989-04-11 | 0 | 0 | 4000 | 3446.9895 | 8322.644 | Null | 0 | 12 |  | 19890411 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE2306 | DUPONT | 0 | 1989 | UNDER GROUND OR UNDER WATER |  | B.F. BROYLES, DIRECTOR OF OPERATIONS | 7136545137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TELEPHONE COMPANY CUT PLASTIC SERVICE LINE WITH TRENCHER WHILE INSTALLING DROP. GAS IGNITED & DESTROYED MACHINE. NO INJURIES.
2025-01-31 10:21 | NO | NO | 19890158 |  | 18104 | SAN ANTONIO CITY PUBLIC SERVICE BOARD | 1601 S. GEN MCMULLEN DRIVE | SAN ANTONIO | BEXAR | TX | 78237 | 3 | NO | 2330 | 1989-04-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19890415 | 7 | 33 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 1.25 | 0.14 | N/A | N/A | 0 | 1976 | ABOVE GROUND |  | WM. F. REICHERT, SENIOR ENGINEER | 5122273211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE RAN INTO GAS METER, ESCAPING GAS IGNITED.
2025-01-31 10:21 | YES | NO | 19890159 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 2359 PARADISE DRIVE | TIBURON | MARIN | CA | 94920 | 3 | NO | 329 | 1989-04-24 | 0 | 0 | 150000 | 129262.1073 | 312099.1492 | Null | 1 | 6 |  | 19890424 | 0.25 | 0 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINIUM | 0 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | CAUSE OF FIRE BELIEVED TO BE WOOD BURNING STOVE OR WALL HEATER WITH INSUFFICIENT CLEARANCE.
2025-01-31 10:21 | YES | NO | 19890160 |  | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 1233 S. TELEMACHUS STREET | NEW ORLEANS |  | LA | 70125 | 3 | NO | 33 | 1989-06-15 | 0 | 0 | 80000 | 68939.7906 | 166452.8796 | Null | 0 | 57 |  | 19890615 | 0.25 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | ALBERT A. GABRIEL, JR./ENGINEER | 5045953561 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON THURSDAY, JUNE 15, 1989 AT APPROXIMATELY 12:33 AM., THERE WAS AN EXPLOSION APPARENTLY CAUSED BY THE ACCUMULATION AND SUBSEQUENT IGNITION OF NATURAL GAS IN THE MULTI-FAMILY DWELLING AT 1233 SOUTH TELEMACHUS STREET IN NEW ORLEANS, LOUISIANA. THE EXPLOSION DESTROYED THE BUILDING AND CAUSED SEVERE DAMAGE TO THE ADJACENT BUILDINGS; HOWEVER, THERE WERE ONLY MINOR INJURIES TO THREE PEOPLE IN THE VICINITY. THE NEW ORLEANS FIRE DEPARTMENT (NOFD) NOTIFIED THE GAS DISPATCHER AT NEW ORLEANS PUBLIC SERICE (NOPSI) AT 12:33 AM. A GAS SERVICEMAN WAS IMMEDIATELY DISPATCHED AND ARRIVED ON THE SCENE AT APPROXIMATELT 12:45AM. UPON ARRIVAL THE SERVICEMAN NOTED A SMALL LEAK AT THE INSULATED UNION IN THE SERVICE RISER. THE SERVICE RISER WAS LOCATED OUTSIDE THE BUILDING NEAR THE GROUND APPROXIMATELY THREE INCHES FROM THE BUILDING FOUNDATION. THE LEAK WAS OBVIOUSLY CAUSED BY THE EXPLOSION WHICH BENT THE SERVICE RISER THEREBY CRACKING THE INSULATOR. THE RISER WAS IMMEDIATELY REMOVED AND THE SERVICE WAS CAPPED-OFF. THE ADJACENT AREA WAS THEN CHECKED FOR THE PRESENCE OF NATURAL GAS WITH A COMBUSTIBLE GAS INDICATOR (CGI) AND NO MEASURABLE QUANTITY OF GAS WAS FOUND. AT THAT TIME THE AREA WAS DEEMED SAFE. NOPSI RECORDS INDICATE THAT THE RESIDENCE IS SERVED BY ONE (1) GAS SERVICE WITH A THREE (3) METER SET AND THREE(3) METER SHUT-OFF VALVES WHICH, ACCORDING TO MOPSI RECORDS, WERE OFFAND LOCKED AT THE TIME OF THE EXPLOSION. HOWEVER, THE SERVICEMAN NOTED THATTHE METER VALVE TO APARTMENT A WAS NOT LOCKED AND THE VALVE WAS IN THE OPEN POSITION. THE READING ON THE METER IMMEDIATELY FOLLOWING THE EXPLOSION WAS 0342. NOPSI RECORDS INDICATE THAT THE READING TAKEN WHEN THE METER WAS SHUT (I.E. VALVE TURNED-OFF AND LOCKED) WAS 0331. THEREFORE, AN UNAUTHORIZED CONSUMPTION OF APPROXIMATELY 11 CCF WAS INDICATED. JOSEPH F. RICKS JR., ANOPSI REPRESENTATIVE, INVESTIGATED THE INCIDENT AND FOUND THAT THE EXPLOSIONAPPARENTLY RESULTED WHEN NATURAL GAS ACCUMULATED IN APARTMENT A FROM AN OPENOR FAILED CUSTOMER FUEL LINE AND WAS IGNITED. THE SOURCE OF IGNITION IS UNKNOWN AT THE PRESENT TIME.
2025-01-31 10:21 | YES | YES | 19890161 |  | 10037 | KANSAS POWER & LIGHT CO | 1930 MURPHY BOULEVARD | JOPLIN | JASPER | MO | 64804 | 3 | NO | 450 | 1989-04-02 | 0 | 1 | 16000 | 13787.9581 | 33290.5759 | Null | 0 | 45 |  | 19890402 | 6 | 8 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | DISTRIC REGULATOR STATION | JOINT | SCREW | STEEL |  | 2 | 0.154 | API5LA25 | N/A | 1957 | 1957 | ABOVE GROUND |  | JAMES W. INGRAM, VICE PRES. GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | DARRYL G. JONES LOST CONTROL OF HIS 1976 JEEP CJ-5, ALONG MURPHY BLVD, TRAVELING AIRBORNE INTO DISTRICT REGULATOR STATION #45 AT 1930 MURPHY BLVD. STATION PIPING AND BARRICADE WERE DESTROYED, AND THE JEEP LANDED ON ITS TOP, PINING MR JONES. HE SUSTAINED A BROKEN ARM, FRACTURED PELVIS, AND HIS SPLEEN RUPTURED DURING TRANSPORTATION TO FREEMAN HOSPITAL IN JOPLIN. THE POLICE REPORT INDICATES ACCIDENT WAS ATTRIBUTED TO SPEED AND DRINKING. THERE WAS NO IGNITION OF NATURAL GAS RELEASE, AND NO CUSTOMERS WERE LOST AS THIS STATION IS WITHIN AN INTEGRATED DISTRIBUTION SYSTEM.
2025-01-31 10:21 | NO | NO | 19890162 |  | 18444 | SOUTH RUSK COUNTY GAS CO | COUNTY ROAD 317 |  | RUSK | TX | 75681 | 0 | NO | 2200 | 1989-03-28 | 0 | 0 | 10172 | 8765.6944 | 21164.4836 | Null | 9 | 0 |  | 19890329 | 26 | 59 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | OTHER | UNKNOWN | OTHER PLASTIC | PVC | 2.25 | 0 | N/A | JET STREAM | 0 | 1970 | UNDER GROUND OR UNDER WATER |  | MAE GREEN, PRESIDENT | 2148223955 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | TERRIBLE STORM AND HIGH WATER WASHED OUT A CREEK CROSSING.
2025-01-31 10:21 | NO | NO | 19890163 |  | 18532 | SOUTHERN UNION GAS CO | 1015 NOBLE STREET | EL PASO | EL PASO | TX | 79902 | 3 | NO | 1502 | 1989-05-17 | 0 | 0 | 24000 | 20681.9372 | 49935.8639 | YES | 0 | 15 |  | 19890517 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD H. SMITH, P.E. REGIONAL ENGINEER | 9155446300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FAILURE OF CUSTOMER'S EQUIPMENT RESULTED IN FIRE THAT DESTROYED A PRIVATE RESIDENCE. GAS COMPANY'S INVOLVEMENT WAS STRICTLY ASSISTING FIRE MARSHALL IN THE INVESTIGATION.
2025-01-31 10:21 | NO | NO | 19890167 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 1909 AVENUE D | ROSENGERG | FORT BEND | TX | 77469 | 3 | NO | 1240 | 1989-05-12 | 0 | 0 | 6500 | 5601.358 | 13524.2965 | Null | 1 | 25 |  | 19890512 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | SERVICE RISER | DRIP/RISER |  | STEEL |  | 1 | 0.12 | API 5L | N/A | 0 | 0 | ABOVE GROUND |  | LANNY W. CARGILE, P.E. , OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A CAR HIT A VACANT RISER CAUSING A LEAK AND IGNITION OF GAS. THE CAR BURNED.
2025-01-31 10:21 | NO | NO | 19890169 |  | 22182 | WASHINGTON GAS LIGHT CO | 11707 GOODLOE ROAD | ROCKVILLE | MONTGOMERY | MD | 20906 | 3 | NO | 1840 | 1989-06-11 | 0 | 0 | 55000 | 47396.106 | 114436.3547 | Null | 0 | 39 |  | 19890612 | 20 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.133 | ASTMA 120 | N/A | 0 | 1960 | WITHIN/UNDER BUILDING |  | CLARENCE E. GOODSON,III, SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE CUSTOMER SMELLED SMOKE FROM HIS BASEMENT AND INVESTIGATED. HE FOUND THEGAS METER,IN AN ENCLOSED METER CABINET, ON FIRE. HE CALLED THE FIRE DEPARTMENT WHO CALLED WGL AND GAS WAS TURNED OFF OUTSIDE. THE FIRE MARSHALL'S INVESTIGATION COULD NOT DETERMINE THE EXACT CAUSE OF THE FIRE; HE FELT THE GAS METER ASEMBLY MUST HAVE BEEN LEAKING AND FOUND AN UNKNOWN SOURCE OF IGNITION. THE CUSTOMER STATED HE HAD NOT PREVIOUSLY SMELLED GAS AT ANY TIME. SYSTEM ODORANT CHECKS WERE MADE AND FOUND TO BE IN THE ACCEPTABLE RANGE. WGL IS CONTINUING TO INVESTIGATE THIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19890170 |  | 329 | ALL PRO GAS CO | 1110 N.W. 44 STREET | FT LAUDERDALE | BROWARD | FL | 33309 | 3 | NO | 1830 | 1989-07-01 | 0 | 1 | 20000 | 17234.9476 | 41613.2199 | Null | 93 | 0 |  | 19890702 | 5 | 10 | BY TEST | 30 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 0.05 | 0 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ATHUR E. BLAU,PRESIDENT | 3057765961 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | WEAKENED JOINT IN PIPE | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | YES | NO | 19890171 |  | 2652 | COMMONWEALTH GAS CO | 22 HARRINGTON RIDGE RD. | SHERBORN | MIDDLESEX | MA | 01770 | 1 | NO | 1059 | 1989-04-27 | 0 | 0 | 200000 | 172349.4764 | 416132.199 | Null | 0 | 26 |  | 19890428 | 54 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 0 | N/A | N/A | 0 | 1961 | WITHIN/UNDER BUILDING |  | BRIAN J. HAWKESWORTH | 5084817900 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | NO | NO | 19890172 |  | 19200 | TERRE HAUTE GAS CORP | 2228 NORTH 31ST STREET | TERRE HAUTE | VIGO | IN | 47804 | 3 | NO | 1009 | 1989-06-07 | 0 | 0 | 25000 | 21543.6846 | 52016.5249 | Null | 0 | 15 |  | 19890608 | 18 | 67 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | W.C. COTTRELL, VICE PRESIDENT ENGINEERING | 8122341561 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AUTOMOBILE HIT GAS METER AND BROKE RISER ELBOW BELOW GROUND LEVEL, ALLOWING GAS TO ESCAPE ADJACENT TO HOUSE BELOW GRADE.
2025-01-31 10:21 | NO | NO | 19890174 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | FM 1374 AND IH-45 | HUNTSVILLE | WALKER | TX | 77340 | 3 | NO | 640 | 1989-05-22 | 0 | 0 | 47500 | 40933.0007 | 98831.3973 | Null | 0 | 40 |  | 19890522 | 26 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATORY STATION | DRIP/RISER |  | STEEL |  | 4 | 0.237 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | LANNY W. CARGILE, P.E. - OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A TRUCK WAS LEFT UNATTENDED IN A SERVICE STATION PARKING LOT. THE TRUCK ROLLED OUT OF THE PARKING LOT, ACROSS A HIGHWAY, DOWN AN EMBANKMENT, AND STRUCK A RELIEF VALVE RISER. THE RISER WAS BROKEN OFF RESULTING IN GAS ESCAPING AND IGNITION OF GAS. THE TRUCK WAS DESTROYED BY THE FIRE.
2025-01-31 10:21 | NO | NO | 19890175 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 2141 WHITE FEATHER TRAIL | CROSBY | HARRIS | TX | 77532 | 3 | NO | 945 | 1989-04-28 | 0 | 0 | 100 | 86.1747 | 208.0661 | YES | 0 | 45 |  | 19890428 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 | N/A | N/A | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE, P.E. - OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-04-20 | YES | 2 |  | NO |  |  | PRIVATE CONTRACTOR PULLED 3/4" STEEL SERVICE TAP FROM 4" STEEL MAIN. INDIANSHORES DRIVE WAS BLOCKED OFF AD ONE HOUSE EVACUATED AS A SAFETY PRECAUTION.
2025-01-31 10:21 | NO | NO | 19890176 |  | 4473 | ENERGAS CO | INTERSTATE 20,HILLSIDE MOBILE HOME PARK | BIG SPRING | HOWARD | TX | 79720 | 3 | NO | 1800 | 1989-06-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19890614 | 10 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | YES | 1 |  | NO |  |  | DRIVER LOST CONTROL OF VEHICLE AND RAN OVER A METER SETTING INTERRUPTING SERVICE TO ABOUT 22 HOUSES.
2025-01-31 10:21 | NO | NO | 19890178 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 4406 36TH STREET | DICKINSON | GALVESTON | TX | 77539 | 1 | NO | 1409 | 1989-05-03 | 0 | 0 | 400 | 344.699 | 832.2644 | YES | 0 | 49 |  | 19890503 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2306 | DUPONT | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE, P.E. - OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | LIGHTNING STRUCK A UTILITY POLE AND FOLLOWED THE BROUNG WIRE TO THE GROUND ROD BURNING A HOLE IN A 2" PLASTIC MAIN AND RESULTING IN IGNITION OF NATURAL GAS.
2025-01-31 10:21 | NO | NO | 19890179 |  | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 445 DELAINE DR | CORPUS CHRISTI | NUECES | TX | 78411 | 4 | NO | 1042 | 1989-05-22 | 0 | 0 | 5000 | 4308.7369 | 10403.305 | Null | 1 | 8 |  | 19890522 | 17 | 60 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NONE | STEEL |  | 2 | 0.167 | N/A | N/A | 0 | 1946 | UNDER GROUND OR UNDER WATER |  | FRANK SACKY, ASSISTANT GAS SUPT. | 5128544396 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS CREW, WHILE REPAIRING A SMALL GAS LEAK ON THE WELD OF A 1" TAP TEE ON A 2" WRAPPED STEEL MAIN, HAD SET A PUNCH INTO THE TAP TEE TO STOP THE FLOW OF GAS. THE CAP OF THE TAP TEE HAD BEEN REMOVED AND THE PUNCH SET INTO THE TAP OF THE GAS MAIN. WHILE THE FOREMAN WAS REWELDING THE DEFECTIVE WELD ON THE TAP TEE, THE GAS PRESSURE BLEW OUT THE PUNCH AND THE NATURAL GAS WAS IGNITED BYTHE TORCH.
2025-01-31 10:21 | NO | NO | 19890180 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | LAKE CHEROKEE | LONGVIEW | GREGG | TX |  | 3 | NO | 413 | 1989-05-05 | 0 | 0 | 2150 | 1852.7569 | 4473.4211 | YES | 0 | 30 |  | 19890505 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | OTHER | REGULATOR STATION | DRIP/RISER |  | STEEL |  | 2 | 0.125 | API 5L | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE, P.E. - OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | FALLING TREE | NO |  | NO | 0 |  | NO |  |  | DURING A STORM A LARGE TREE FELL ON A REGULATOR STATION RUPTURING A 2" RISER, RESULTING IN THE LOSS OF GAS SERVICE TO 150 CUSTOMER.
2025-01-31 10:21 | NO | NO | 19890182 |  | 4473 | ENERGAS CO | WILLOW CREEK RD. | AMARILLO | POTTER | TX | 79108 | 3 | NO | 1640 | 1989-06-26 | 0 | 0 | 2000 | 1723.4948 | 4161.322 | YES | 0 | 30 |  | 19890626 | 16 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | VALVE |  | STEEL |  | 4 | 0.188 | API-5L GRD B |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAVID V. HAYES, JR. DIVISION ENGINEER | 8063783380 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | AN EXTENSION WAS BEING INSTALLED ON AN EXISTING VALVE TO ALLOW FOR EASIER ACCESS TO GREASE TO VALVE. AS THE EXTENSION WAS BEING THREADED ONTO THE VALVE THE COMPANY EMPLOYEE CONTINUE TO TURN THE EXTENSION UNTIL IT BEGAN TO CLOSE THE VALVE. THIS PROCEDURE WAS CONTINUED UNTIL THE VALVE WAS COMPLETED CLOSED SHUTING OFF GAS FLOW TO A ONE WAY FEED SYSTEM.
2025-01-31 10:21 | NO | NO | 19890184 |  | 11800 | LOUISIANA GAS SERVICE CO | 1182' SOUTH OF MUSIC ROAD | SWARTZ | OUACHITA | LA | 71281 | 3 | NO | 1230 | 1989-07-10 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 |  |  | 30 | 80 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | ASTM D2513 | PLEXCO | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | CONTRACTOR'S BACKHOE SEVERED GAS MAIN. APPROXIMATELY 40 CUSTOMERS WERE WITHOUT GAS FOR A 5 HOUR PERIOD.
2025-01-31 10:21 | NO | NO | 19890185 |  | 12484 | MIDWEST GAS CO | 112 E. 10TH STREET | YANKTON | YANKTON | SD | 57078 | 3 | YES | 1015 | 1989-07-05 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 |  |  | 95 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | STEEL |  | 1.25 | 0.14 | API5L |  | 1965 | 1965 | UNDER GROUND OR UNDER WATER |  | ALLAN L. GATES, AREA MANAGER | 6056657846 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | OPERATOR WAS NOT CALLED FOR LOCATION OF FACILITIES.
2025-01-31 10:21 | YES | NO | 19890187 |  | 11032 | LACLEDE GAS CO | #1 ST. ALFRED ROAD | CREVE COEUR | ST LOUIS | MO | 63132 | 3 | NO | 915 | 1989-07-11 | 0 | 0 | 125000 | 107718.4228 | 260082.6243 | Null | 0 | 52 |  | 19890711 | 12.5 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | T & C | STEEL |  | 0.75 | 0.113 | N/A | N/A | 0 | 1953 | WITHIN/UNDER BUILDING |  | PAUL B. HUNKER, JR./ ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | NO | NO | 19890189 |  | 10037 | KANSAS POWER & LIGHT CO | 24 HWY. & OSAGE VILLAGE DRIVE | INDEPENDENCE | JACKSON | MO | 64050 | 3 | NO | 124 | 1989-07-08 | 0 | 0 | 5000 | 4308.7369 | 10403.305 | Null | 0 | 45 |  | 19890708 | 4 | 44 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5LA25 | N/A | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | JAMES W. INGRAM, VP GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | PICKUP TRUCK HIT & BROKE OUTLET PIPE TO REGULATOR STATION.
2025-01-31 10:21 | NO | NO | 19890191 |  | 18532 | SOUTHERN UNION GAS CO | 1917 N. WEST ST. | FLAGSTAFF | COCONINO | AZ | 86001 | 3 | NO | 2035 | 1989-06-03 | 0 | 0 | 10000 | 8617.4738 | 20806.6099 | YES | 0 | 20 |  | 19890603 | 0.25 | 0.25 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES R. WARREN, AREA MANAGER | 6027744591 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | HOUSE SETTLED DOWN ONTO HOUSEPIPING BREAKING PIPE UNDER HOUSE. BREAK WAS DOWNSTREAM OF OPERATORS METER.
2025-01-31 10:21 | NO | NO | 19890192 |  | 18532 | SOUTHERN UNION GAS CO | 1600 W. NORTH LOOP | AUSTIN | TRAVIS | TX | 78756 | 3 | NO | 2152 | 1989-07-21 | 0 | 0 | 500 | 430.8737 | 1040.3305 | YES | 3 | 45 |  |  | 20 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 | N/A | N/A | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | DENNIS WORLEY, REGIONAL ENGINEER | 5124775981 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | GROUND SURROUNDING STORM DRAIN HAD SETTLED CAUSING CI MAIN TO BREAK.
2025-01-31 10:21 | NO | NO | 19890193 |  | 4473 | ENERGAS CO | WHITNEY AND MAXWELL STREET | MIDLAND | MIDLAND | TX | 79705 | 3 | NO | 905 | 1989-07-26 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 |  | 19890726 | 10 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | STEEL |  | 2 | 0 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | REMOVAL OF BACKFILL ALLOWED PIPE TO SLIP OUT. | MAINTENANCE CREW UNCOVERED A LEAKING DRESSER COUPLING. PIPE SLIPPED OUT OF DRESSER. SERVICE LOSS TO 78 HOUSES.
2025-01-31 10:21 | NO | NO | 19890194 |  | 4473 | ENERGAS CO | 2550 W. 8TH | ODESSA | ECTOR | TX | 79760 | 3 | NO | 1045 | 1989-07-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19890714 | 0.05 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | YARD LINE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CARL F. BAILEY, P.E., DIVISION ENGINEER | 9156888849 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEE OF CUSTOMER ATTEMPTED TO LOCATE YARD LINE LEAK WITH CIGARETTE LIGHTER AND IGNITED GAS.
2025-01-31 10:21 | NO | NO | 19890196 |  | 11713 | LONG ISLAND LIGHTING CO | GIN LANE C/O FAIRLEA | SOUTHAMPTON | SUFFOLK | NY | 11968 | 4 | NO | 1326 | 1989-07-22 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 19 |  | 19890723 | 49 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | ASTM D2513-2406 | DUPONT | 1979 | 1980 | UNDER GROUND OR UNDER WATER |  | ANNE M. OSTLING, SUPERVISOR QC&R | 5169334400 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | UNDER THE DIRECTION OF THE ARSON SQUAD,GAS C&M PERSONNEL UNEARTHED A FAULTEDSECONDARY ELECTRIC CABLE (INSTALLED BY AN ELECTICIAN) WHICH HAD BURNED THE PLASTIC GAS SERVICE AT THE BUILDING.
2025-01-31 10:21 | YES | YES | 19890199 |  | 15875 | PRODUCERS GAS EQUITIES INC | NW/4 4-12-17 | ELLIS |  | KS |  | 1 | NO | 1100 | 1989-07-31 | 0 | 2 | 2676 | 2306.036 | 5567.8488 | Null | 0 | 30 |  | 19890731 | 55 | 200 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | TAP | DRIP/RISER |  | OTHER | UNKNOWN | 3 | 0.0625 | N/A | N/A | 1937 | 1937 | ABOVE GROUND |  | LUCY M. CROWELL, SAFETY SUPERVISOR | 9136257353 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO
2025-01-31 10:21 | YES | YES | 19890200 |  | 7348 | HOPE GAS INC | MILL FALL ROAD & U.S. RT. 19 | MONONGAH | MARION | WV |  | 1 | NO | 925 | 1989-07-24 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 8 |  | 19890724 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | EDMUND L. FLINT | 3046238650 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-07-10 | YES | 1 | PAINT SPRAYED ROAD | NO |  |  | THIS WAS THE THIRD OF THREE (3) LINE BREAKS CAUSED BY THE SAME THIRD PARTY WHILE LAYING 1,000 FT OF NEW WATER LINE. MAY 31, 1989, JULY 12, 1989, AND JULY 24, 1989. HOPE WAS INFORMED THEY WOULD NOT BE DIGGING ON THE SIDE OF THE ROAD OF THIS LAST DIG-IN. THE FIRST TWO (2) LINE BREAKS WERE ADJACENT TO PERMANENT MARKERS, HOWEVER, HOPE DID NOT MARK EXACTLY THE LOCATION OF THE LINE.AT 10:55 AM, PRODUCERS GAS UTILITES, INC. WAS NOTIFIED BY PHONE AS TO A NATURAL GAS EXPLOSION IN SEC 4, TWNSHIP 12, RANGE 17, IN ELLIS COUNTY, KS. THE CALL WAS MADE BY KEN ROHLEDER TO ALAN HOFFMAN, VP OF PRODUCERS GAS EQUITIES. LUCY CROWELL, SAFETY SUPERVISOR FOR PGE NOTIFIED THE ELLIS COUNTY SHERIFF'S DEPT AT 11:00 AM. WILFRED LEIKER, FIELD REPRESENTATIVE FOR PGE, WAS DISPATCHED TO THE SCENE AT 11:01 AM BY RADIO. MR LEIKER ARRIVED AT THE SCENE OF THE INCIDENT AT 11:20 AM ELMER STAAB, SUPERINTENDENT, WAS ENROUTE TO THE SCENE OF THE INCIDENT AT 11:15AM AND ARRIVED AT 11:35AM. GAS AT THE SCENE OF THE INCIDENT WAS SHUT AT 11:30AM BY COMPANY EMPLOYEE W. LEIKER. REPAIRS TO THE GAS LINE WERE MADE BY COMPANY EMPLOYEES AND COMPLETED BY 1:30PM. ONE FARM RESIDENCE AND TWO OIL FIELDS INDUSTRIALS WERE WITHOUT GAS SERVICE FOR A PERIOD OF TWO HOURS.A TELEPHONIC REPORT OF THE INCIDENT WAS MADE BY LUCY CROWELL AT 11:37AM TO BARRY FLOHRSCHUTZ, OF THE KANSAS PIPELINE SAFETY DEPT. ANOTHER TELEPHONIC REPORT OF THE INCIDENT WAS MADE BY L. CROWELL TO THE DEPT OF TRANS AT 11:53AM.AFTER SURVEYING THE SCENE OF THE INCIDENT, A COMPANY EMPLOYEE, W. LEIKER INDICATED THAT A TAP HAD BEEN TORN OFF OF A 3" DISTRIBUTION LINE (OWNED BY PGE, INC) BY A 1973 CHEVROLT PICKUP DRIVEN BY KEN ROHLEDER. THE DRIVER OF THE PICKUP WAS TREATED AND RELEASED AT A LOCAL HEALTH CARE CENTER. TWO PASSENGERS OF THE PICKUP WERE TAKEN TO A LOCAL HOSPITAL FOR TREATMENT OF MINOR BURNS. THE TWO PASSENGERS WERE KEPT OVERNIGHT FOR OBSERVATIONS ONLY. DESTROYED IN THE INCIDENT WAS A 1973 CHEVROLT (A FARM PIKUP VALUED AT $1,500.00), $500.00 IN FENCING MATERIAL ALSO ON THE PICKUP. ESTIMATED GAS LOSS FOR 45 MINUTES WAS 215 MCF, OR $676.18 (FIGURED AT A CURRENT RATE OF $3.1450 PER MCF). TOTAL DAMAGES IN THIS INCIDENT AMOUNT TO $2,676.18.
2025-01-31 10:21 | YES | YES | 19890201 |  | 4483 | ENSTAR NATURAL GAS CO | 5640 RABBIT CREEK ROAD | ANCHORAGE |  | AK | 9516 | 3 | NO | 1036 | 1989-07-28 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 30 |  | 19890728 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.409 | SDR 11 IPS' | PHILLIPS DRISCOPIPE INC. | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | DREW SMITH - CHIEF ENGINEER | 9072643744 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-05-30 | YES | 3 | YELLOW SPRAY PAINT | YES |  |  | TAB ELECTRIC EMPLOYEES DAMAGED A 4" PLASTIC GAS MAIN WITH POST HOLE AUGER. THE ESCAPING GAS IGNITED AND THREE OF THEIR EMPLOYEES WERE INJURED (ONE WAS AMINOR BURN). THE TAB CREW WAS USING AN ELECTRIC DRILL NEAR THE DAMAGED, THIS SEEMS TO BE THE APPARENT IGNITION SOURCE.
2025-01-31 10:21 | YES | YES | 19890202 |  | 22763 | WISCONSIN GAS CO | N68 W14195 MEMORY LANE | MENOMONEE FALLS | WAUKESHA | WI | 53051 | 3 | NO | 1517 | 1989-08-01 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 0 |  | 19890801 | 30 | 35 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION | STEEL |  | 0 | 0 |  | DRESSER | 1959 | 1959 | UNDER GROUND OR UNDER WATER |  | GREGORY B. SCHROADER, P.E. | 4142916729 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-06-16 | YES | 2 | PAINT | YES |  |  | ON TUESDAY, AUGUST 1, A CONTRUCTION WORKER FOR MAINLINE SEWER & WATER, INC. WAS ON A SEWER MANHOLE WHICH WAS UNDER CONSTRUCTION. HE LIT A LIGHTER TO SMOKE A CIGARETTE. THE LIGHTER IGNITED AN EXPLOSIVE NATURAL GAS AND AIR MIXTUREAT THE MANHOLE. THE WORKER WAS INJURED AND REQUIRED HOSPITALIZATION WITH SECOND & THIRD DEGREE BURNS. THE SOURCE OF THE NATURAL GAS, WHICH WAS LATER IDENTIFIED, WAS A GAS SERVICE AT N68W14065 MEMORY LINE. THE GAS SERVICE HAD BEEN DAMAGED BY THE PRESSURE OF BACKFILL IN THE MAINLINE SEWER & WATER TRENCH.THE SERVICE WAS NOT PROPERLY SUPPORTED DURING BACKFILLING OPERATIONS BY MAINLINE SEWER & WATER. THE PRESSURE OF THE BACKFILL ON THE STEEL GAS SERVICE CAUSED THE 3/4" STEEL PIPE TO PULL OUT OF A DRESSER COMPRESSION COUPLING. THE GAS APPARENTLY MIGRATED ALONG THE SEWER TRENCH AND ENTERED THE SEWER BETWEEN VERTICAL SEGMENTS OF THE PRECAST MANHOLE. THE GAS SERVICE WAS REPAIRED IMMEDIATELY AFTER THE INCIDENT INVESTIGATION DISCOVERED THE LEAK.
2025-01-31 10:21 | YES | YES | 19890204 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 60 PARK TERRACE WEST | NEW YORK |  | NY | 10034 | 4 | NO | 448 | 1989-07-28 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 21 |  | 19890728 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | METER | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS COWAN, MANAGER, MANHATTAN DIVISION-GAS ENGINEERING | 2125762443 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A TRASH FIRE UNDERNEATH A GAS METER MELTED THE SOLDER THAT SEALED THE METER. THIS ACTION ALLOWED GAS TO ESCAPE WHICH WAS THEN IGNITED BY THE FIRE.
2025-01-31 10:21 | YES | YES | 19890205 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 430 WEST 154 STREET | NEW YORK |  | NY | 10032 | 4 | NO | 1536 | 1989-07-15 | 1 | 1 | 100000 | 86174.7382 | 208066.0995 | Null | 0 | 9 |  | 19890715 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE PIPING | OTHER | OUTLET FOUND OPEN-ENDED | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT C. GREIS, DIVISION MGR, MANHATTAN GAS CONSTRUCTION | 2125762439 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE PROBABLE CAUSE OF THE EXPLOSION WAS GAS LEAKING THROUGH AN OPEN-ENDED PIPE, ESCAPING THROUGHOUT THE HOUSE, AND BEING IGNITED BY AN UNKNOWN SOURCE.
2025-01-31 10:21 | NO | NO | 19890206 |  | 11680 | LONE STAR GAS CO | BENNIE STREET | ROWENA | RUNNELS | TX |  | 4 | NO | 1250 | 1989-02-05 | 0 | 0 | 5200 | 4481.0864 | 10819.4372 | Null | 0 | 0 |  |  | 0.2 | 0.5 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | C.D. JENNINGS - MANAGER I | 9153652116 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19890209 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 101 E. 6TH STREET, APT. B | BAKERSFIELD |  | CA |  | 3 | NO | 1105 | 1989-07-13 | 1 | 4 | 500 | 430.8737 | 1040.3305 | Null | 0 | 31 |  | 19890713 | 0.25 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE LINE | OTHER | FLEX LINE | OTHER | FLEX LINE TO RANGE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | W.R. MAZOTTI - V.P., GAS & ELEC. TECH. SVS. | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SMALL GAS STOVE TOPPLED ON INFANT CAUSING THIRD-PARTY FATALITY. THE OTHER OCCUPANTS WERE OVERCOME BY GAS AND WERE TREATED AT A LOCAL HOSPITAL. NO IGNITION OR EXPLOSION, AND BUILDING WAS EVACUATED. GAS ESCAPED FROM BROKEN FLEX LINE, CAUSED BY FALLING STOVE SEVERING THE LINE.
2025-01-31 10:21 | YES | YES | 19890210 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 804 40TH STREET | OAKLAND | ALAMEDA | CA | 94069 | 3 | NO | 1223 | 1989-07-27 | 0 | 1 | 25800 | 22233.0825 | 53681.0537 | YES | 0 | 7 |  | 19890727 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | SERVICE RISER | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | N/A | N/A | 0 | 1959 | ABOVE GROUND |  | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SVS. | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AN OUT OF CONTROL VEHICLE STRUCK AND DAMAGED THE SERVICE RISER AT THE ABOVE ADDRESS, ALLOWING GAS TO ESCAPE TO THE ATMOSPHERE. NEARBY BUILDINGS WERE EVACUATED AS A PRECAUTION.
2025-01-31 10:21 | YES | YES | 19890211 |  | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 176 MALVERN STREET | NEWARK | ESSEX | NJ | 07101 | 4 | NO | 1250 | 1989-08-18 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19890818 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NONE | CAST IRON |  | 6 | 0.43 | AGLA STDS. | N/A | 0 | 1906 | UNDER PAVEMENT |  | C.W. GREVENITZ, V.P. - GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON AUGUST 18, 1989, AT APPROXIMATELY 12:50 P.M., WILLIAM ELMER, STREET MECHANIC, WAS WORKING ON A GAS SERVICE REPLACEMENT. WHILE PULLING A 2" PLUG ON A SADDLE OFF A 6" CAST IRON UTILIZATION PRESSURE MAIN, AN IGNITION OCCURRED FROM AN UNKNOWN SOURCE. W. ELMER RECEIVED BURNES ON THE FACE AND ARM. HE WAS TRANSPORTED TO THE COMPANY DISPENSARY AND THEN REFERRED TO ST. BARNABAS HOSPITAL. HE REMAINED OVERNIGHT FOR OBSERVATIONS AND WAS RELEASED THE FOLLOWING DAY.
2025-01-31 10:21 | NO | NO | 19890212 |  | 17442 | RIO GRANDE VALLEY GAS CO | 103 E. JEFFERSON | PORT ISABEL | CAMERON | TX |  | 3 | NO | 1600 | 1989-07-27 | 0 | 0 | 1000 | 861.7474 | 2080.661 | YES | 1 | 55 |  | 19890728 | 45 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | MICHAEL L. MYERS, DISTRIBUTION ENGINEER | 5125423531 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE JULY 27 INCIDENT WAS THE RESULT OF A TRUCK RUNNING OVER OUR METER. THE METER SET ASSEMBLY WAS REPLACED THE SAME DAY OF THE INCIDENT.
2025-01-31 10:21 | YES | YES | 19890214 |  | 18536 | SOUTHWEST GAS CORP | 612 MINNESOTA | LAS VEGAS | CLARK | NV | 89107 | 3 | NO | 409 | 1989-07-23 | 0 | 2 | 75000 | 64631.0537 | 156049.5746 | Null | 1 | 53 |  | 19890723 | 43 | 43 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER | PVC | 0.5 | 0.062 | N/A | N/A | 1960 | 1960 | UNDER GROUND OR UNDER WATER |  | JOHN P. HAZARD, MANAGER OF CONSTRUCTION | 7023652175 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOT | NO |  | NO | 0 |  | NO |  |  | A 1/2" PVC SERVICE WAS APPARENTLY SQUEEZED BY A LARGE TREE ROOT RESULTING INA LEAK, EXPLOSION, AND FIRE TO THE HOUSE.
2025-01-31 10:21 | NO | NO | 19890215 |  | 12350 | MINNEGASCO INC | 9051 FLYING CLOUD DRIVE | EDEN PRAIRIE |  | MN |  | 2 | NO | 1625 | 1989-08-24 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  |  | 55 | 60 | BY TEST | 60 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | HIT BY EXCAVATOR | STEEL |  | 6 | 0.56 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CHARLES W. DOANE | 6123425147 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | CONTRACTOR DIGGING WHILE WORKING ON STATE HWY PROJECT WAS UNCOVERING NATURALGAS TRANSMISSION LINE WHEN HE CAUGHT THE LINE ON ITS PARTS WITH HIS BUCKET CAUSING A HOLE OR BREAK.
2025-01-31 10:21 | YES | YES | 19890216 |  | 13710 | NORTHERN ILLINOIS GAS CO | 21694 W. ELM ST. | LAKE VILLA | LAKE | IL |  | 3 | NO | 858 | 1989-08-20 | 0 | 1 | 30000 | 25852.4215 | 62419.8298 | Null | 1 | 55 |  | 19890820 | 60 | 60 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.625 | 0 |  |  | 0 | 1974 | WITHIN/UNDER BUILDING |  | ARTHUR W. SWANSON, SUPERVISOR SYSTEM OPERATING | 8154550271 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | YES | 1974 | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER AT 21694 ELM ST. IN LAKE VILLA CONSTRUCTED A GARAGE OVER OUR GAS SERVICE. N.I. GAS WAS NOT CALLED TO RELOCATE SERVICE. CORROSION OCCURRED ON COPPER SERVICE UNDER CEMENT FLOOR OF GARAGE WHICH CAUSED FAILURE. THE GARAGE WASBADLY DAMAGED WHEN IGNITION OCCURRED. CAUSE OF IGNITION IS NOT KNOWN AT THIS TIME.
2025-01-31 10:21 | YES | YES | 19890222 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 121 S. 4TH STREET | BENTON | SALINE | AR | 72015 | 3 | NO | 433 | 1989-09-02 | 3 | 1 | 150000 | 129262.1073 | 312099.1492 | Null | 0 | 45 |  | 19890902 | 25 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0 | PE 3406 | POLY ARK | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | JIM BREWER, CODES & PROCEDURES COORDINATOR | 5013774771 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | RESIDENTS REPORTED LIGHTENING STRIKE IN IMMEDIATE AREA. IT APPEARS THAT CURRENT FROM ELECTRICAL STORM ENTERED THE LOCATOR WIRE. THE CURRENT TRAVELED ALONG THE LOCATOR WIRE TO AN AREA WHERE THE INSULATION ON THE LOCATOR WIRE HAD AVOID. AT THIS POINT, THE CURRENT LEFT THE LOCATOR WIRE CAUSING EXTREME HEATTO BE GENERATED. THIS HEAT, CAUSED THE PLASTIC GAS LINE TO PARTIALLY MELT, RESULTING IN A RUPTURE IN THE PLASTIC LINE.
2025-01-31 10:21 | YES | YES | 19890223 |  | 12420 | MICHIGAN GAS UTILITIES CO | 8140 EAST M-60 | UNION CITY | CALHOUN | MI | 49094 | 2 | NO | 830 | 1989-07-13 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 36 |  | 19890713 | 30 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | STEEL |  | 0.75 | 0 |  |  | 0 | 1969 | UNDER PAVEMENT |  | CHARLES F. HAUSKA, MANAGER OF ENGINEERING | 3132424400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | PRIOR TO 7:55 AM. ON THURSDAY, JULY 13, 1989, A CONTRACTOR USING A BACKHOE BEGAN EXCAVATION FOR SEWER LINES IN CLOSE PROXIMITY TO THE BACK OF THE TASTEE FREEZ BUILDING. DURING EXCAVATION THE BACKHOE BUCKETT STRUCK AND PULLED A 3/4" STEEL NATURAL GAS SERVICE PIPE. THE "PULLING" OF THE GAS SERVICE RESULTEDIN A 9" SEPARATION OF THE 3/4" STEEL PIPE FROM A COMPRESSION COUPLING ADJACENT TO THE SIDE BUILDING WALL. NATURAL GAS AT 30 PSIG ESCAPED FROM THE SERVICE LINE SEPARATION INTO THE LIGHT SAND/GRAVEL SOIL. AT 7:55 AM. THE CONTRACTOR NOTIFIED MICHIGAN GAS UTILITIES, MONROE EMERGENCY CALL CENTER OF THE "BADLYBENT SERVICE". HOWEVER, "DID NOT SMELL NATURAL GAS". THE MONROE EMERGENCY CALL CENTER (CIC) NOTIFIED THE COLDWATER DISTRICT AT 8:01 AM. COLDWATER DISPATCHED A STREET CREW FROM ITS OPERATIONS DEPARTMENT TO INVESTIGATE THE DAMAGEDSERVICES. AT APPROXIMATELY 8:30 AM. AN EXPLOSION AND FIRE ERUPTED IN THE TASTEE FREEZ BUILDING, INJURING THE OWNER AND TWO CONTRACTOR EMPLOYEES. FIRE, POLICE,AND MEDICAL PERSONNEL WERE ON THE SCENE WHEN MGU PERSONNEL ARRIVED AT 8:42 AM. THE THREE INJURED RECEIVED SERIOUS BURNS AND WERE AIR LIFTED FROM THE SCENE TO THE BRONSON METHODIST BURN CENTER IN KALAMAZOO. THE BUILDING RECEIVED MODERATE DAMAGE FROM THE EXPLOSION AND MINOR DAMAGED FROM THE RESULTINGFIRE.
2025-01-31 10:21 | YES | YES | 19890224 |  | 1088 | BALTIMORE GAS & ELECTRIC CO | 3031 ST. PAUL ST., 1ST FL. APT. | BALTIMORE |  | MD | 21218 | 3 | NO | 2158 | 1989-09-25 | 0 | 2 | 20000 | 17234.9476 | 41613.2199 | Null | 0 | 15 |  | 19890926 | 0 | 0 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | GAS RANGE | OTHER | UNKNOWN | OTHER | GAS RANGE | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | E.L. POFFENBERGER, GENERAL SUPERVISOR | 3015612790 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OVEN OF GAS RANGE WAS TURNED ON AND PASSING GAS FOR AN EXTENDED PERIOD OF TIME. WHEN A NEIGBOR COMPLAINED ABOUT THE ODOR OF GAS, OCCUPANT TRIED TO LIGHTTHE OVEN. AN EXPLOSION AND FIRE RESULTED.
2025-01-31 10:21 | YES | YES | 19890227 |  | 15359 | PEOPLES NATURAL GAS | 209 N. 3RD STREET | GRIMES | POLK | IA | 50111 | 3 | NO | 730 | 1989-09-07 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 90 |  | 19890907 | 6 | 6 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREWED | STEEL |  | 1 | 0.133 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JAMES P. NOVACEK, DIRECTOR, OPERATIONS ENGINEERING | 5152236010 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-08-30 | YES | 3 | PAINT | NO |  |  | ON AUGUST 30, 1989, PEOPLES NATURAL GAS LOCATED GAS TRANSMISSION LINES AT 209 N. 3RD STREET, GRIMES, IOWA, IN PREPARATION FOR THE CITY'S INSTALLATION OF SEWER LINES. ON SEPTEMBER 7, 1989, AFTER INSTALLATION OF THE SEWER LINES, VANCE MARSH, AN EMPLOYEE OF NELSON DEVELOPMENT SERVICES, THE CITY'S CONTRACTOR,ENTERED A MANHOLE AND APPARENTLY STRUCK A MATCH OR LIT A CIGARETTE LIGHTER.THERE WAS A FLASH RESULTING IN INJURIES TO MR. MARSH.
2025-01-31 10:21 | YES | YES | 19890228 |  | 18440 | SOUTH JERSEY GAS CO | KELLY & MEDITERRANEAN ROADS | SWEDESBORO, | GLOUCESTER | NJ | 08085 | 1 | NO | 1325 | 1989-09-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19890911 | 35 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | DUPONT | 1989 | 1989 | OTHER | UNKNOWN | EDWARD J. TONIELLI - V.P. DEVISION OPERATIONS | 6095619000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE PURGING AIR FROM THE END OF A NEW 2" PLASTIC MAIN, THE GAS-AIR MIXTUREIGNITED, BURNING THE ARM, BACK AND FACE OF AN EMPLOYEE WORKING IN THE HOLE ATTHE TIME.
2025-01-31 10:21 | NO | NO | 19890229 |  | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 8292 MARION | DETROIT | WAYNE | MI | 48213 | 3 | NO | 1857 | 1989-08-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 57 |  | 19890829 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | TIN | 0 | 0 | 10 LT. | SUPERIOR | 0 | 1969 | WITHIN/UNDER BUILDING |  | BRUCE J. NIEMAN, MANAGER, CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A BULLET FIRED BY AN UNKNOWN PERSON PIERCED THE INSIDE METER. LEAKING GAS, IGNITED BY AN UNKNOWN SOURCE, CAUSED AN EXPLOSION. THE DWELLING AND CONTENTSWERE DAMAGED.
2025-01-31 10:21 | YES | YES | 19890231 |  | 11800 | LOUISIANA GAS SERVICE CO | 3230 BOYOU RD | TOCA | ST BERNARD | LA | 70085 | 3 | NO | 1000 | 1989-09-22 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 29 |  | 19890922 | 70 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTM D2513 | PLEXCO | 1986 | 1986 | OTHER | IN OPEN DITCH | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | SOUTH CENTRAL BELL EMPLOYEE WAS REPAIRING TELEPHONE CABLE IN A BELL HOLE AT 3230 BAYOU ROAD, TOCA, LOUISIANA. SOUTH CENTRAL BELL EMPLOYEE LIT PROPANE TORCH TO REMOVE THERMO PLASTIC SHEATHING FROM THE TELEPHONE CABLE. WHILE USINGTHE TORCH, EMPLOYEE BURNED THROUGH NEARBY 3/4" PLASTIC NATURAL GAS SERVICE LINE WHICH WAS EXPOSED AND CLEARLY IN SIGHT. SOUTH CENTRAL BELL EMPLOYEE SUFFERED FIRST AND SECOND DEGREE BURNS AS A RESULT OF THE FIRE. LOUISIANA GAS SERVICE COMPANY WAS NOT NOTIFIED TO LOCATE ANY GAS LINES IN THE VICINITY PRIORTO THE ACCIDENT.
2025-01-31 10:21 | NO | NO | 19890232 |  | 49 | ADAMSVILLE GAS DEPT, TOWN OF | HWY.22N | ADAMSVILLE | MCNAIRY | TN | 38310 | 1 | NO | 930 | 1989-09-30 | 0 | 0 | 5000 | 4308.7369 | 10403.305 | Null | 0 | 45 |  |  | 200 | 225 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | JOINT | WELD | STEEL |  | 3 | 0.216 | ASTH API-5L | REPUBLIC STEEL | 1977 | 1978 | UNDER GROUND OR UNDER WATER |  | E. GEORGE LECKNER, JR. , GAS SYSTEM ANALYST | 9016324214 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | THE BANK TO SHIFT ADD EXERT PRESSURE AGAINST LINE.
2025-01-31 10:21 | NO | NO | 19890233 |  | 49 | ADAMSVILLE GAS DEPT, TOWN OF | HWY. 22N | ADAMSVILLE | MCNAIRY | TN | 38310 | 1 | NO | 1100 | 1989-10-01 | 0 | 0 | 2000 | 1723.4948 | 4161.322 | Null | 0 | 45 |  |  | 200 | 225 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | JOINT | WELD | STEEL |  | 3 | 0.216 | ASTM API-5L | REPUBLIC STEEL | 1977 | 1978 | UNDER GROUND OR UNDER WATER |  | E. GEORGE LECKNER, JR. , GAS SYSTEM ANALYST | 9016324214 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | DUE TO HEAVY RAINFALL, THE SLOPE OF FILL DIRT WAS UNDERMINED BY WATER CAUSING THE BANK TO SHIFT AND EXERT PRESSURE AGAINST LINE.
2025-01-31 10:21 | YES | NO | 19890237 |  | 10037 | KANSAS POWER & LIGHT CO | 4104 WARWICK | KANSAS CITY | JACKSON | MO |  | 3 | NO | 203 | 1989-09-11 | 0 | 0 | 125000 | 107718.4228 | 260082.6243 | Null | 0 | 45 |  | 19890911 | 0.25 | 2 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | TIN METER | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES W. INGRAM, VICE PRESIDENT GAS OPERATIONS | 9132961959 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | FIRE OF UNKNOWN ORIGIN IN BASEMENT, MELTED SOLDER ON METER, AND IGNITION OCCURRED.
2025-01-31 10:21 | YES | YES | 19890238 |  | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | ROUTE 5 & 20 | CANANDAIGUA | ONTARIO | NY | 14424 | 3 | NO | 840 | 1989-10-02 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 10 |  | 19891002 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | NO FAILURE | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | WALTER C. JAUTZ, SUPER-CORP. GAS OPERATOR | 6077292551 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS INCIDENT OCCURRED ON CUSTOMER-OWNED FACILITIES. THE INJURED PARTY TURNED ON AN ELECTRICAL SWITCH WHICH WAS FOLLOWED BY AN EXPLOSION AND FIRE. SUBSEQUENT INVESTIGATION DETERMINED THAT A GAS LINE INSIDE THE CUSTOMER'S BUILDING HAD BEEN DISCONNECTED FROM THE APPLIANCE IT SUPPLIED AND THE PIPE LEFT OPEN. IN ADDITION, AN ACETYLENE GAS TANK WAS FOUND OPEN AND PIPING ORIGINATING FROM AN AUTOMOTIVE TRANSMISSION FLUID STORAGE TANK WAS FOUND TO BE CUT. THE INCIDENT APPEARS TO BE NON-ACCIDENTAL IN ORIGIN AND IS STILL UNDER INVESTIGATION BY LOCAL AUTHORITIES.
2025-01-31 10:21 | YES | YES | 19890239 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | VIA LIDO & RANCHO NIGUEL ROAD | LAGUNA NIGUEL | ORANGE | CA | 92677 | 3 | NO | 1105 | 1989-09-14 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 8 |  | 19890914 | 43 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D2513 | PHILLIPS DRISCO | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | RICHARD M. MOROW-MGR. OF DISTRIBUTION | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | KENNEDY PIPELINE CO. EMPLOYEE, USING PROPANE TORCH TO MAKE WELDED REPAIR TO 2 INCH COPPER WATER LINE, MELTED 1/2 INCH PLASTIC GAS SERVICE. GAS LINE WAS EXPOSED IN THE EXCAVATION AT THE TIME OF THE INCIDENT.
2025-01-31 10:21 | NO | NO | 19890240 |  | 22189 | WASHINGTON NATURAL GAS CO | 1003 SW 317 COURT | FEDERAL WAY | KING | WA | 98023 | 3 | NO | 300 | 1989-10-09 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 0 | 45 |  | 19891009 | 45 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | PE 3406 | UNKNOWN | 0 | 1981 | UNDER GROUND OR UNDER WATER |  | DOUGLAS DAMM, SAFETY MANAGER | 2066226767 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NATURAL GAS ESCAPED THROUGH A PINHOLE LEAK IN A 5/8" PLASTIC GAS SERVICE LYING ADJACENT TO THE HOUSE. GAS MIGRATED INTO THE GARAGE WHERE IT WAS IGNITED.THE RESULTING EXPLOSION AND FIRE RESULTED IN DAMAGED ESTIMATED TO EXCEED $50,000. THE CAUSE OF THE LEAK AND THE SOURCE OF IGNITION ARE UNKNOWN AT THIS TIM
2025-01-31 10:21 | YES | YES | 19890241 |  | 11800 | LOUISIANA GAS SERVICE CO | 934 WEST HALL STREET | SLIDELL | ST TAMMANY | LA | 70460 | 3 | NO | 2135 | 1989-10-03 | 0 | 1 | 40000 | 34469.8953 | 83226.4398 | Null | 0 | 20 |  | 19891003 | 60 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER'S PIPING | FITTING |  | STEEL |  | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CUSTOMER DISCONNECTED COPPER TUBING FROM 1/2" GALVANIZED LINE SUPPLYING WALLHEATHER IN AN APPARENT SUICIDE ATTEMPT. NATURAL GAS FILLED HOUSE CAUSING AN EXPLOSION AND FIRE. SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | NO | NO | 19890244 |  | 15359 | PEOPLES NATURAL GAS | HWY 370 & HWY 75 | BELLEVUE | SARPY | NE | 68005 | 3 | NO | 1328 | 1989-10-09 | 0 | 0 | 0 | 0 | 0 | YES | 14 | 20 |  | 19891009 | 245 | 260 | BY TEST | 572 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.156 | N/A | N/A | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | EDWIN M. HATTER, PE, DIRECTOR, OPERATION ENGINEERING | 4025927670 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | A SUBCONTRACTOR, WORKING FOR THE DEPARTMENT OF ROADS, STRUCK THE OPERATOR'S LINE WITH A BULLDOZER. THE RESULTING LOSS OF PRESSURE TEMPORARILY AFFECTED GAS SERVICE TO PORTIONS OF THE CITY OF BELLEVUE, NEBRASKA.
2025-01-31 10:21 | YES | YES | 19890245 |  | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | ALA. HWY 215 AND WESTERN BY-PASS (HWY275 | TALLADEGA | TALLADEGA | AL | 35160 | 3 | NO | 845 | 1989-09-28 | 0 | 1 | 110000 | 94792.212 | 228872.7094 | Null | 1 | 36 |  | 19890928 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | NIPAK TR418 | 1985 | 1986 | UNDER GROUND OR UNDER WATER |  | RAYMOND E. WALLACE, JR., P.E. SUPV. GAS MEASUREMENT AND CON. | 2053268381 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-09-20 | YES | 1 |  | NO |  |  | AT 8:45 AM. ON SEPTEMBER 28, 1989, TALLADEGA POLICE REPORTED A GAS MAIN BREAK AND FIRE AT THE INTERSECTION OF WESTERN BY-PASS (HIGHWAY 275) AND ALABAMA HIGHWAY 21 SOUTH. AN ALAGASCO SERVICEMAN ARRIVED ON THE SCENE AT 8:53 A.M. THE FOLLOWING INFORMATION WAS REPORTED TO US IMMEDIATELY AFTER THE INCIDENT. A SUBCONTRACTOR FOR SOUTH CENTRAL BELL WAS OPERATING A CHAIN TRENCHER AT THE ABOVE LOCATION AND CUT A 2" PLASTIC MAIN WITH APPROXIMATELY 50 PSIG PRESSURE ON IT. THE MAOP OF THE SYSTEM IS 50 PSIG. THE MAOP OF THIS PARTICULAR SECTION OF MAIN IS 60 PSIG. WHEN THE OPERATOR REALIZED THAT NATURAL GAS WAS BLOWING, HE GOT OFF HIS TRACTOR AWAY FROM THE BLOWING GAS. HIS SUPERVISOR, ALLEN HANDLEY, TOLD HIM TO GET BACK ON HIS TRACTOR AND TRY TO RAISE THE TRENCHER BOOM. HE REFUSED, SO MR. HANDLEY GOT ON THE TRACTOR AND TRIED TO RAISE THE BOOM. WHEN HE ATTEMPTED THIS, THE GAS IGNITED. SUBSEQUENT TO THE ACCIDENT, A REPRESENTATIVE OF LEE ENGINEERING INFORMED US THAT MR. HANDLEY WAS THE ONLY PERSON OPERATING THE TRENCHER AT THE TIME OF THE ACCIDENT. THE GAS MAIN WAS "SQUEEZED OFF" AT 10:21 A.M. MR. HANDLEY SUFFERED FIRST AND SECOND DEGREE BURNESON HIS FACE, HANDS, ARMS, AND PORTIONS OF HIS UPPER BODY ACCORDING TO UNOFFICIAL REPORTS. HE WAS THE ONLY PERSON INJURED AS A RESULT OF THIS INCIDENT.THE TRACTOR/TRENCHER, VALUE AT $110,000 BY THE OWNER, WAS DESTROYED. THE VALUE OF THE NATURAL GAS LOST IS VALUED AT UNDER $200. ALSO, APPROXIMATELY 10 FEET OF 2 INCH PLASTIC HAD TO BE REPLACED. SERVICE WAS INTERRUPTED TO APPROXIMATELY 40 - 45 CUSTOMERS. ALL BUT ONE CUSTOMER HAD SERVICE RESTORED BY MID AFTERNOON FRIDAY, SEPTEMBER 29. PRIOR TO THE ACCIDENT, ON AUGUST 24 AND 25, 1989, A LINE LOCATION TECHNICIAN FROM ALAGASCO HAD BRIEFED THE JOB FOREMAN AS TO THE LOCATION OF THE MAINS AND HAD STRESSED THE NEED TOHAND DIG WHEN WORKING CLOSE TO OR CROSSING GAS PIPING. THE ALAGASCO LOCATION TECHNICIAN HAD MARKED THE LINE WITH PAINT AND WITH PERMANENT PIPELINE MARKERS PRIOR TO THE ACCIDENT. ADDITIONALLY, HE HAD PERSONALLY WALKED THE LOCATION OF THE LINE WITH MR.HANDLEY PRIOR TO THE ACCIDENT.
2025-01-31 10:21 | YES | YES | 19890246 |  | 12350 | MINNEGASCO INC | 50TH AVE. NORTH & SCHMIDT LAKE ROAD | PLYMOUTH | HENNEPIN | MN | 55442 | 2 | NO | 1457 | 1989-10-19 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19891020 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.242 | N/A | PLEXCO | 0 | 1978 | UNDER GROUND OR UNDER WATER |  | CHARLES W. DOANE, CLAIMS SPECIALIST | 6123425147 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-09-13 | YES | 3 | PAINTED | YES |  |  | NORTHERN STATES POWER COMPANY (UTILITY) WHILE DIGGING, HIT MINNEGASCO, INC. (UTILITY) NATURAL GAS MAIN, CUTTING THE LINE. NORTHERN STATES POWER CALLED FOR LOCATION OVER A MONTH PRIOR, BUT NEVER SHOWED UP TO DIG UNTIL A MONTH LATER, WITHOUT CALLING FOR RELOCATE.
2025-01-31 10:21 | YES | NO | 19890248 |  | 22420 | WEST OHIO GAS CO | BRIARCLIFF DR., ROLLING HILLS ESTATES | ST. MARYS | AUGLAIZE | OH | 45885 | 2 | NO | 1202 | 1989-09-29 | 0 | 0 | 350000 | 301611.5838 | 728231.3482 | Null | 1 | 50 |  | 19890930 | 230 | 275 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.28 | APL 5L | UNKNOWN | 0 | 1951 | UNDER GROUND OR UNDER WATER |  | THOMAS J. WIESE, ENGINEERING SUPERVISOR | 4192264859 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-09-28 | YES | 2 |  | YES |  |  | WEST OHIO GAS COMPANY'S 8" HIGH PRESSURE DISTRIBUTION PIPELINE WAS HIT BY A CONTRACTORS EARTH GRADING FOR A NEW STREET, BRIARCLIFF DRIVE, IN A NEW SUBDIVISION, ROLLING HILLS ESTATES IN ST. MARYS, OHIO. THE HOLE IN THE DAMAGED PIPERESULTED IN THE LOSS OF SERVICE TO APPROXIMATELY 8,000 CUSTOMERS FED OFF THIS LINE. RELIGHTING PROCEDURES WERE COMPLETED TO ALL BUT A FEW HUNDRED CUSTOMERS IN ABOUT 80 HOURS OF THE INCIDENT.
2025-01-31 10:21 | NO | NO | 19890249 |  | 3200 | DE KALB - CHEROKEE COUNTY GAS DEPT | 38TH ST. N.E. | FORT PAYNE | DE KALB | AL | 35967 | 3 | NO | 1745 | 1989-10-19 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 55 |  | 19891020 | 42 | 53 | BY TEST | 80 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | LNG SATELLITE FACILITY | VALVE |  | OTHER | CRYOGENIC STEEL STEM PCKG | 0 | 0 | ANSI B31-3 | TBV INC. | 1988 | 1988 | ABOVE GROUND |  | JAMES A. DAWSON, GENERAL MANAGER | 2058453731 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAK AROUND CRYOGENIC VALVE STEM PACKING. LEAK REPAIRED BY ADJUSTING PACKINGSTEM NUT.ON OCTOBER 19,1989, EMPLOYEE MR. JOE DOVER WAS OPERATING THE LNG SATELLITE FACILITY. AT APPROCIMATELY 5:45 P.M. LOCAL TIME, THE OPERATOR RECEIVED, THROUGH THE CONTROL PANEL, AN INDICATION THAT GAS DETECTOR NO. 4 HAD SENSED THE PRESENCE OF ESCAPING GAS AT THE STORAGE CONTAINER. MR. DOVER INVESTIGATED AND FOUND ESCAPING GAS AT VALVE NO. FVO2 (LIQUIFIED FLOW VALVE). VALVE NO. FVO2 CONTROLS THE FLOW OF GAS FROM THE STORAGE CONTAINER TO THE VAPORIZER. MR. DOVER IMMEDIATELY SHUT DOWN THE LNG SYSTEM AND NOTIFIED MR. JAMES A. DAWSON, GENERAL MANAGER, OF THE SITUATION. MR DAWSON ARRIVED AT THE LNG SATELLITE FACILITY AT APPROXIMATELY 6:05 P.M. LOCAL TIME. UPON INVESTIGATING THE LEAKING VALVE, THE CAUSE AND LOCATION OF WHICH WAS UNDERTERMINED AT THE TIME, MR. DAWSON CALLED THE FORT PAYNE POLICE DEPARTMENT (EMERGENCY PLAN) AND REQUESTED THAT 38TH STREET BE CLOSED TO TRAFFIC AND THAT THE FIRE DEPARTMENT BE NOTIFIED TO REPORT TO THE LNG SATELLITE FACILITY. MR. DAWSON FURTHER REQUESTED THAT SOUTHERN RAILWAY BE CALLED AND ADVISED OF THE SITUATION AND REQUESTED TO STOP ALL NORTH AND SOUTHBOUND TRAFFIC ON THE ADJACENT SINGLE TRACK MAIN LINE. AT APPROXIMATELY 6:10 PM. LOCAL TIME, MR. DAWSON CALLED ROGER STEBBING, LNG SYSTEM DESIGN ENGINEER, AND WAS INFORMED THAT MR. STEBBING WAS IN EUROPE. MR. DAWSON THEN CALLED JIM MAVITY OF MAVITY CONTROLS, TO ASSIST IN LOCATING AND REPAIRING THE LEAK AT VALVE NO. FVO2. THE RESPONSE TIME OF MAVITY CONTROLS TO THE LNG SATELLITE FACILITY WAS CONSIDERED TO BE ONE AND ONE-HALF HOURS. UPON ARRIVAL OF FIRE DEPARTMENT PERSONNEL, AFTER DISCUSSING THE SITUATION WITH CHIEF HARRISON, THE CHEROKEE TRAILER PARK AND DEERFIELD APARTMENTS WERE EVACUATEDAND POWER WAS DISCONNECTED BY THE FORT PAYNE IMPROVEMENT AUTHORITY (ELECTRICDEPARTMENT). UPON MAVITY CONTROL'S ARRIVAL AT THE LNG SATELLITE FACILITY, IT WAS DETERMINED THAT THE NORMAL OPERATING TANK PRESSURE OF 42 LBS SHOULD BE REDUCED TO SLOW THE FLOW OF LNG AT VALVE NO. FV02. THE STORAGE CONTAINER PRESSURE WAS REDUCED BY INJECTING LNG INTO THE DISTRIBUTION SYSTEM, THERBY LOWERING THE PRESSURE TO APPROXIMATELY 28 LBS. DURING THE TIME THE PRESSURE WAS BEING LOWERED ON THE STORAGE CONTAINER, THE FOLLOWING BUSINESSES WERE CLOSED AND ELECTRIC POWER DISCONNECTED BY FORT PAYNE IMPORVEMENT (ELECTRIC DEPARTMENT). UPON REDUCTION OF THE STORAGE CONTAINER PRESSURE FROM 42 LBS TO 28 LBS, IT WAS DETERMINED THAT THE VALVE PACKING NUT HAD LOOSENED DURING OPERATION ANDALLOWED THE PACKING TO LOOSEN, CAUSING VALVE NO. FV02 TO LEAK AROUND THE VALVE STEM. JIM MAVITY OF MAVITY CONTROLS, TIGHTENED THE PACKING NUT ON VALVE FV92 AND STOPPED THE ESCAPING GAS. AFTER ALLOWING SUFFICIENT TIME FOR THE GASTO DISSIPATE, ALL VALVES, FLANGES, AND ABOVE GROUND PIPING WERE CHECKED WITHA SOUTHERN CROSS MODEL 400 FLAME IONIZATIO DETECTOR. NO LEAKS WERE LOCATED. THE AREA AND FACILITY WERE SECURED AND THE FACILITY PLACED BACK IN SERVICE. MR. JIM MAVITY, OF MAVITY CONTROLS, ESTIMATED THE LOSS OF LNG NOT TO EXCEEDFIVE (5) GALLONS. THE FORT PAYNE FIRE DEPARTMENT, POLICE DEPARTMENT AND FORT PAYNE IMPROVEMENT AUTHORITY (ELECTRIC DEPARTMENT) WERE NOTIFIED AT 9:40 P.M. LOCAL TIME, THAT THE AREA WAS SECURED. MR. CHRIS HARVEY, ALABAMA PUBLIC SERVICE COMMISSION, WAS NOTIFIED, BY PHONE, OF THE INCIDENT ON OCTOBER 19, 1989, AT 10:00 P.M. LOCAL TIME BY GENERAL MANAGER, JAMES A. DAWSON. THE DEPARTMENT OF TRANSPORTATION WAS NOTIFIED, BY PHONE, OF THE INCIENT BY MR. JERALD MITCHELL OF DEKALB-CHEROKEE COUNTIES GAS DISTRICT AT 9:50 A.M. LOCAL TIME, OCTOBER 20, 1989. MR. MITCHELL SUBMITTED THE INCIDENT REPORT TO PETTY OFFICER BRANTLEY WHO RECORDED THE INFORMATION ON NCR REPORT NO. 18545.
2025-01-31 10:21 | NO | NO | 19890254 |  | 4473 | ENERGAS CO | 1600 NORTH AUSTIN STREET | PLAINVIEW | HALE | TX | 79073 | 3 | NO | 1841 | 1989-10-14 | 0 | 0 | 2200 | 1895.8442 | 4577.4542 | YES | 0 | 15 |  | 19891014 | 0 | 0 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067414411 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | OUR DISPATCHER RECEIVED A CALL FROM THE PLAINVIEW FIRE DEPARTMENT SATURDAY AT 6:41 P.M. THEY REPORTED THAT A CAR HAD HIT ONE OF OUR GAS METERS, WITH ENSUING FIRE ON THE METER SETTING AND ON THE CAR. BRAD HERRINGTON OF THE FIRE DEPT. CALLED ENERGAS'S DISPATCHER WHO CALLED PETE LOWRIE, DIST. SUPT. OF ENERGAS. A SERVICEMAN WAS SENT TO THE SCENE AND CAPPED THE SERVICE, STOPPING THEFLOW OF GAS. WHEN THE CAR HIT THE METER, THE DRIVER LEFT THE SCENE. THERE WERE NO INJURIES. DAMAGE IS ESTIMATED AS $200.00 FOR COMPANY FACILITIES AND $2,000 TO THE CAR.
2025-01-31 10:21 | NO | NO | 19890255 |  | 2268 | CHARLOTTESVILLE, CITY OF | 813 ELLIOTT AVENUE | CHARLOTTESVILLE |  | VA | 22901 | 3 | NO | 955 | 1989-11-02 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 0 | 10 |  | 19891102 | 0.32 | 0.61 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | JOINT | TEE | STEEL |  | 1.25 | 0.14 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | KENT MCELHENY, GAS SUPERINTENDENT | 8049713340 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A NEW GAS SERVICE LINE WAS BEING INSTALLED BY A CONTRACTOR WORKING FOR THE CITY OF CHARLOTTESVILLE. THE BACKHOE BUCKET SNAGGED THE EXISTING SERVICES LINEAND PULLED THE SERVICE LINE FROM A THREADED TEE IN THE BASEMENT OF THE HOUSE. THE BASEMENT FILLED WITH GAS WHICH WAS IGNITED, PROBABLY BY THE WATER HEATER, RESULTING IN AN EXPLOSION AND FIRE WHICH DESTROYED THE HOUSE.
2025-01-31 10:21 | YES | YES | 19890258 |  | 22658 | WILLMUT GAS & OIL CO - MAIN OFFICE | J.C. BRYANT ROAD | HATTIESBURG | FORREST | MS | 39401 | 1 | NO | 1545 | 1989-10-27 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19891030 | 150 | 100 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | MEASURING METER | REGULATOR/METER |  | CAST IRON |  | 0 | 0 | 500B | AMERICAN | 0 | 1980 | ABOVE GROUND |  | JOHN M. TATUM, JR./VICE PRESIDENT OF OPERATIONS & ENGINEER | 6015446001 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OPERATOR WAS PURGING A LINE INCLUSIVE OF METER THROUGH AN OPEN 2" VALVE. METER LOCKED UP, PRESSURE ONLY FILLED ON SIDE OF THE METER PUTTING EXCESSIVE PRESSURE DIFFERENTIAL ACROSS THE INNER WALL OF THE METER. THE INTERNAL WALL FAILED, IMPACTED INTERNAL PARTS AGAINST CAST IRON OUTER CASE. OUTER CASE FAILED AND INJURED ONE EMPLOYEE. CHART ON METER DID NOT RECORD ANY PRESSURE RISE.
2025-01-31 10:21 | NO | NO | 19890259 |  | 6830 | GREY FOREST UTILITIES | 17000 BLOCK OF IH10 WEST IN LEON CREEK | SAN ANTONIO | BEXAR | TX | 78023 | 1 | NO | 1045 | 1989-10-23 | 0 | 0 | 5000 | 4308.7369 | 10403.305 | YES | 5 | 0 |  | 19891024 | 214 | 214 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.156 | N/A | N/A | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | KIM A. MANN, OPERATIONS MANAGER | 5126958781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-08-29 | YES | 1 |  | NO |  |  | DAMAGE WAS CAUSED BY A LARGE EXCAVATOR.
2025-01-31 10:21 | YES | NO | 19890260 |  | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 745 WATER STREET | HOBART | LAKE | IN | 46342 | 3 | NO | 435 | 1989-10-13 | 0 | 0 | 65000 | 56013.5798 | 135242.9647 | Null | 0 | 55 |  | 19891019 | 47 | 55 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1927 | UNDER GROUND OR UNDER WATER |  | D.M. CAMPOS, MANAGER OF GAS CONTROL & STORAGE | 2198535603 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1961 | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON OCTOBER 13, 1989 AT APPROXIMATELY 4:30 A.M. THERE WAS AN EXPLOSION WHICH DESTROYED THE GARAGE AT THE ABOVE LOCATION. THE EXPLOSION ALSO CAUSED DAMAGE TO SEVERAL ADJACENT STRUCTURES. INVESTIGATION INDICATED THAT GAS LEAKING FROM THE 2" DISTRIBUTION MAIN (LOCATED IN THE ALLEY) ENTERED THE GARAGE AND SET OFF THE EXPLOSION.
2025-01-31 10:21 | YES | YES | 19890261 |  | 15007 | PACIFIC GAS & ELECTRIC CO | LINCOLN WAY SOUTH OF RUSSELL ROAD | AUBURN | PLACER | CA | 95603 | 3 | NO | 1750 | 1989-10-20 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 53 |  | 19891023 | 58 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT | BUTT FUSION | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE 2306 | PHILLIPS-DRISCO PIPE | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | W.R. MOZOTTI, V.P.-GAS & ELEC. TECH. SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | WHILE THE CREW WAS BACKFILLING A TRENCH, FUSION JOINT FAILED, GAS IGNITED, AND BURNED ONE EMPLOYEE. STATIC ELECTRICITY IS SUSPECTED AS SOURCE OF IGNITION
2025-01-31 10:21 | YES | YES | 19890264 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 411 4TH STREET | TAFT | KERN | CA | 93268 | 3 | NO | 339 | 1989-10-21 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 15 |  | 19891025 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER APPLIANCE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | W.R. MAZOTTI, V.P., GAS & ELEC. TECH. SVS. | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OCCUPANT ACCIDENTALLY TURNED ON STOVE WITHOUT PILOT LIGHTS, ALLOWING GAS TO ACCUMULATE IN THE BUILDING. SOURCE OF IGNITION IS SUSPECTED TO BE A CIGARETTE LIGHTER.
2025-01-31 10:21 | NO | NO | 19890265 |  | 15007 | PACIFIC GAS & ELECTRIC CO | HARIS ROAD, 1/4 MILE S/O ABBOTT ST. | SALINAS | MONTEREY | CA | 93901 | 1 | NO | 115 | 1989-10-17 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 5 | 15 |  | 19891017 | 310 | 313 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | DAMAGE BY 3RD PARTY. | STEEL |  | 0.75 | 0.13 | ASTM GRADE B | N/A | 0 | 0 | ABOVE GROUND |  | W.R. MAZOTTI-V.P., GAS & ELEC. TECH. SVS. | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | OVERTURNED TRACTOR TRAILER DAMAGED REGULATOR SET, ALLOWING GAS TO ESCAPE TO THE ATMOSPHERE. TRAFFIC WAS REROUTED.
2025-01-31 10:21 | NO | NO | 19890266 |  | 15007 | PACIFIC GAS & ELECTRIC CO | 57 RANCHO DRIVE | SAN JOSE |  | CA |  | 3 | NO | 900 | 1989-10-17 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 0 | 40 |  | 19891017 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 0.5 | 0 | TR 418 | N/A | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | W.R. ;MAZOTTI-V.P., GAS & ELEC. TECH. SVS. | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | PROPERTY OWNER DROVE STAKE INTO 1/2-INCH PLASTIC LINE AND LEAKING GAS ENTERED BUILDING, CAUSING AN EXPLOSION.
2025-01-31 10:21 | YES | YES | 19890267 |  | 2200 | CENTRAL ILLINOIS LIGHT CO | 2008 S. WHITTIER | SPRINGFIELD | SANGAMON | IL | 62794 | 3 | NO | 840 | 1989-11-01 | 0 | 1 | 45000 | 38778.6322 | 93629.7448 | YES | 0 | 3 |  | 19891101 | 40 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | CUSTOMER FUEL LINE | OTHER | OVER PRESSURE | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | E.H. SIMANEK SENIOR CODE COMPLIANCE ADMINISTRATOR | 3096934871 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OPERATOR CONNECTED A 40 P.S.I.G. SERVICE TO A SERVICE WITH 6" W.C. WITHOUT FIRST TURNING OFF GAS COCK AT METER. GAS ENTERED CUSTOMERS FUEL LINE.
2025-01-31 10:21 | NO | NO | 19890275 |  | 3260 | DELTA NATURAL GAS CO INC | 1804 NORTH MAIN STREET | LONDON | LAUREL | KY | 40741 | 3 | NO | 607 | 1989-11-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 38 |  | 19891117 | 20 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | WELD | PLASTIC FUSION BUTT | POLYETHYLENE PLASTIC |  | 4.5 | 0.395 | ASTM D 2513 | PHILLIPS DRISCOPIPE | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | ALAN L. HEATH - VICE PRESIDENT-OPERATIONS & ENGINEERING | 6067446171 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | AT APPROXIMATELY 4:58 AM NOVEMBER 17, 1989, THE LAUREL COUNTY DISPATCH CENTER RECEIVED A CALL FROM AN EMPLOYEE AT THE MCDONALDS RESTAURANT LOCATED ON NORTH MAIN ST REPORTING A STRONG GAS ODOR OUTSIDE. THE DISPATCH CENTER NOTIFIED THE LAUREL COUTY FIRE DEPT. OF A POSSIBLE LEAK AND DISPATCHED THEM TO THE SCENE. STANLEY ALTIZER, LEAD CUSTOMER SERVICE REPRESENTATIVE IN THE LONDON SYSTEM, HEARD THE DISPATCH ON HIS HOME SCANNER. HE CALLED DAVID PHIPPS, SENIOR CUSTOMER SERVICEREPRESENTATIVE IN THE LONDON SYSTEM, AND CURTISS CHESNUT, A CUSTOMER SERVICE REP IN THE LONDON SYSTEM, AND TOLD THEM TO MEET HIM AT THE SCENE. HE THEN CALLED THE DISPATCH CENTER AND ADVISED THEM THAT DELTA EMPLOYEES WERE ENROUTE TO THE SCENE. ALTIZER, PHIPPS AND CHESTNUT ARRIVED AT THE SCENE AT APPROXIMATELY 5:15 AM. A 4" PLASTIC PIPE WAS LEAKING NEAR THE MCDONALDS EXIT DRIVEWAY. ALTIZER WENT TO DELTA'S LONDON OFFICE AND CALLED GERALD BAKER, DELTA'S SOUTHERN DIV MGR, TO ADVISE HIM OF THE BROKEN LINE. BAKER INSTRUCTED ALTIZER TO SQUEEZE OFF THE LINE BELOW THE CROSSING GOING TO KERNS BAKERY AND SOUTH OF CHINOOK DR. BAKER THEN CALLED BENNY HENSLEY, DELTA'S LEAD INSPECTOR, TO ADVISE HIM OF THE BROKEN LINE. HENSLEY TOLD BAKER HE WOULD DO HIS BEST TO HAVE A CONSTRUCTION CREW THERE BY 7 AM TO MAKE REPAIRS. IMMEDIATLY FOLLOWINGHIS CONVERSATION WITH HENSLEY, BAKER RECEIVED A CALL FROM THE DISPATCH CENTER ADVISING HIM OF A GAS FIRE AND MINOR INJURIES AT MCDONALDS RESTAURANT. ENROUTE TO THE SCENE, BAKER MADE RADIO CONTACT WITH ALTIZER TO CHECK ON THE SEVERITY OF THE INJURIES AND THE FIRE. ALTIZER INFORMED BAKER THAT THE INJURIES WERE MINOR AND THE FIRE WAS STILL BURNING. HE STATED THAT THEY WERE IN THE PROCESS OF DIGGING OUT THE LINE SOUTH OF CHINOOK DR AND NORTH OF KERNS BAKERY SO SERVICE WOULD NOT BE INTERRUPTED TO CUSTOMERS ON THE NORTH END OF LONDON. TO SAVE TIME, BAKER INSTRUCTED ALTIZER TO DIG OUT AND SQUEEZE OFF ONLY THE LINE NORTH OF KERNS BAKERY AND TO SHUT-IN THE CHINOOK DR REGULATOR STATION. THIS ACTION EXTINGUISHED THE FIRE BUT RESULTED IN DISRUPTING NATURAL GAS SERVICE TO63 CUSTOMERS. BAKER ARRIVED AT THE SCENE AT APPROXIMATELY 6:30A. BAKER DISPATCHED 9 CUSTOMER SERVICE REP TO THE SCENE, 3 FROM THE CORBINE SYSTEM, 3 FORMTHE BEREA SYSTEM, 1 FROM THE MANCHESTER SYSTEM, 1 FROM THE PINEVILLE SYSTEM AND 1 FROM THE MIDDLESBORO SYSTEM IN ORDER TO EXPEDITE RESTORATION OF NATURALGAS SERVICE TO THE AFFECTED CUSTOMERS. THE CUSTOMER SERVICE REP TURNED THE GAS OFF AT EACH METER. THE LEAK WAS REPAIRED BY A CREW FROM STANLEY PIPELINE CO AND BENNY HENSLEY, DELTA'S LEAD INSPECTOR. A 12 FOOT SECTION OF 4" PLASTICPIPE WAS REPLACED. REPAIRS WERE COMPLETE BY 3 PM. THE PIPELINE WAS THEN PURGED AND ENERGIZED. NATURAL GAS SERVICE WAS RESTORED TO THE 63 AFFECTED CUSTOMERS BY 3:30 PM THAT AFTERNOON. THE GAS LEAK WAS CONFINED TO A PLASTIC FUSION BUTT WELD THAT HAD FAILED. ALTIZER ATTEMPTED TO CONTROL THE LEAK WITH THE USEOF A FULL SEAL LEAK CLAMP. THE GAS IGNITED DURING INSTALLATION OF THE CLAMP.THE SOURCE OF IGNITION IS NOT POSITIVELY KNOWN. HARRY SOWDERS, LONDON'S DISTRIBUTION SUPERVISOR, TOOK ALTIZER, PHIPPS AND CHESTNU TO THE MARYMONUT HOSPITAL IN LONDON WHERE THEY WERE TREATED FOR MINOR BURNS ON THIER FACE AND HANDSTHEN RELEASED. THE LONDON POLICE DEPT, LONDON FIRE DEPT, LAUREL COUNTY FIREDEPT AND THE LAUREL COUNTY RESCUE SQUAD WERE AT THE SCENE FIGHTING THE FIRE,DIRECTING TRAFFIC AND MAINTAINING SAFETY PRECAUTIONS. THERE WAS NO SIGNIFICANT PROPERTY DAMAGE OR INJURIES ATTRIBUTABLE TO THIS INCIDENT. A KENTUCKY UTILITIES POWER POLE AND A MCDONALDS EXIT SIGN AND SHRUBS WERE DAMAGED BY THE FIR
2025-01-31 10:21 | YES | NO | 19890276 |  | 2652 | COMMONWEALTH GAS CO | 100 GOODALE ROAD | MARLBORO | MIDDLESEX | MA | 01752 | 2 | NO | 40 | 1989-11-27 | 0 | 0 | 275000 | 236980.5301 | 572181.7736 | Null | 0 | 40 |  | 19891127 | 55 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S PROPERTY | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | BRIAN J. HAWKESWORTH - SAFETY MANAGER | 5084817900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE DESTROYED A SINGLE FAMILY HOME AT 100 GOODALE ROAD, MALBORO, MASS. THE FIRE IS BELIEVED TO HAVE STARTED IN OR NEAR THE BOILER ROOM IN THE CELLAR.NODETERMINATION HAS BEEN MADE AS TO THE CAUSE OF THE FIRE. AN INVESTIGATION BY THE TOWN FIRE DEPARTMENT AND THE STATE FIRE MARSHAL'S OFFICE IS STILL UNDERWA
2025-01-31 10:21 | YES | YES | 19890277 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 228 FRONT STREET | NAPLES | MORRIS | TX | 75568 | 3 | NO | 1055 | 1989-10-30 | 0 | 2 | 10000 | 8617.4738 | 20806.6099 | Null | 0 | 0 |  | 19891031 | 5.3 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE PIPING | OTHER | UNCAPPED LINE | STEEL |  | 0.5 | 0 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | ROY T. LILLY, CONSTRUCTION SUPERVISOR | 2145723461 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER HAD UNCAPPED LINE IN BATHROOM DURING REMODELING.
2025-01-31 10:21 | YES | YES | 19890278 |  | 11680 | LONE STAR GAS CO | INTERSTATE 30 & F.M. 549 | ROCKWALL | ROCKWALL | TX | 75087 | 1 | NO | 1155 | 1989-10-10 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19891010 | 15 | 55 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 1.25 | 0 | N/A | NIPAK | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | DALE BAUGHMAN, C&M SUPT. I | 2144873834 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19890279 |  | 12350 | MINNEGASCO INC | 322 EAST COMMON | WATERVILLE | LE SUEUR | MN | 56096 | 2 | NO | 1220 | 1989-11-30 | 0 | 0 | 45000 | 38778.6322 | 93629.7448 | Null | 1 | 0 |  | 19891130 | 50 | 60 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.149 | GRADE B | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES W. DOANE | 6123425147 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-06-22 | YES | 3 | LOCATIONS MARKED W/ PAINT | YES |  |  | FROM OUR INVESTIGATION OF THE INCIDENT AT THIS TIME AND DATE, WE BELEIVE THELINE INDICATES BEING SCRAPED OR HIT BY A PIECE OF CONSTRUCTION EQUIPMENT ANDCOVERED UP BY GROUND.
2025-01-31 10:21 | YES | YES | 19890280 |  | 11800 | LOUISIANA GAS SERVICE CO | WEST ESPLANADE AND NEYREY DRIVE | METAIRIE | JEFFERSON | LA | 70002 | 3 | NO | 1145 | 1989-11-24 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19891124 | 60 | 100 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | VALVE |  | STEEL |  | 3 | 0.216 | API-5L | UNKNOWN | 0 | 1966 | OTHER | IN BELL HOLE | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | WHILE REMOVING A 3" HIGH PRESSURE STEEL MAIN CANAL CROSSING TO FACILITATE A DRAINAGE PROJECT, IT WAS NECESSARY TO CLOSE NINE VALVES. UPON COMPLETION OF CUTTING OUT THE SECTION OF PIPE OVER THE CANAL AND CAPPING THE MAIN FROM THE NORTH SIDE, THE CREW LEADER ORDERED THREE VALVES OPENED TO RESTORE SERVICE TOCUSTOMERS THAT HAD BEEN SHUT OFF. THE WORKER ASSIGNED THE TASK OF OPENING THE VALVES OPENED A WRONG VALVE AND CAUSED GAS TO ENTER THE BELL HOLE FROM THEUNCAPPED MAIN ON THE SOUTH SIDE. THE NATURAL GAS WAS IGNITED BY A PROPANE TORCH AND BURNED THE WORKER IN THE BELL HOLE WHO WAS WRAPPING THE PIPE.
2025-01-31 10:21 | YES | NO | 19890281 |  | 1088 | BALTIMORE GAS & ELECTRIC CO | 1757 REGENTS PARK ROAD | CROFTON | ANNE ARUNDEL | MD |  | 3 | NO | 2100 | 1989-12-14 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | Null | 23 | 0 |  | 19891215 | 0.29 | 0.29 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNONW | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | E.L. POFFENBERGER, GENERAL SUPERVISOR | 3015612790 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE STARTED AT OR AROUND THE FURNACE AREA. NATURAL GAS FURNACE BECAME INVOLVED AND CONTRIBUTED TO THE FIRE. INTERIOR OF THE HOUSE WAS DESTROYED. CAUSE OF THE FIRE WAS NOT DETERMINED.
2025-01-31 10:21 | YES | YES | 19900001 |  | 15469 | PHILADELPHIA GAS WORKS | 628 E. WENSLEY STREET | PHILADELPHIA | PHILADELPHIA | PA | 19134 | 3 | NO | 42 | 1989-12-11 | 1 | 0 | 60000 | 51704.8429 | 124839.6597 | Null | 0 | 42 | 22069 | 19891211 | 0.26 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 | N/A | N/A | 1904 | 1905 | UNDER PAVEMENT |  | LEO T. MIDDLEMISS, MANAGER DISTRIBUTION DEPARTMENT | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | CAST IRON GAS MAIN FRACTURED AFTER ITS SUPPORT WAS DISTURBED BY OUTSIDE FORCES AND THE FAILURE OF OPERATOR'S PERSONNEL TO FOLLOW PROPER PROCEDURES DURINGLEAK INVESTIGATION.
2025-01-31 10:21 | NO | NO | 19900002 |  | 4350 | ELIZABETHTOWN GAS CO | BROADWAY AND SECOND STREET | ELIZABETH | UNION | NJ |  | 1 | NO | 2200 | 1989-12-23 | 0 | 0 | 0 | 0 | 0 | YES | 8 | 0 | 22916 | 19891223 | 17 | 35 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.38 | WWP-421 | INNERTITE | 0 | 1935 | UNDER PAVEMENT |  | EDWARD J. RAPOLAS, DIRECTOR OF OPERATIONS | 2012895000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE GAS COMPANY WAS WORKING ON A GAS LEAK AND IN THE PROCES OF EXCAVATING BROKE A WATER MAIN. THE WATER MAIN HAD TO BE REPAIRED AND TO DO SO A PUMP WAS BEING USED TO CLEAR THE WATER FROM THE HOLE. THE PUMP BACKFIRED CAUSING IGNITION TO THE LEAKING GAS. THE FIRE WAS IN A WIDE INTERSECTION WITH NO DANGER TOEXISTING HOUSES OR TO THE PUBLIC. THE FIRE DEPARTMENT WAS STANDING BY. RATHER THAN SHUT DOWN A LARGE NUMBER OF HOUSES IN SUB-FREEZING TEMPERATURES BY USING THE CONTROL VALVES, IT WAS DECIDED TO SHUT DOWN A SMALL SECTION USING PRESSURE CONTROL FITTINGS, CAUSING NO SHUT OFFS TO ANY CUSTOMERS.
2025-01-31 10:21 | YES | YES | 19900003 |  | 4350 | ELIZABETHTOWN GAS CO | 520 EAST THIRD AVENUE | ROSELLE | UNION | NJ | 07203 | 4 | NO | 2040 | 1989-12-29 | 0 | 2 | 200000 | 172349.4764 | 416132.199 | Null | 3 | 30 | 23584 | 19891229 | 23 | 35 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 | 0.41 | FED-WW P-421 | U.S. PIPE FOUNDRY | 0 | 1950 | UNDER PAVEMENT |  | EDWARD RAPOLAS, DIRECTOR OF OPERATIONS | 2012895000 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOTS | NO |  | NO | 0 |  | NO |  |  | ESCAPE OF GAS RESULTING FROM CRACK IN MAIN APPARENTLY CAUSED BY PRESSURE FROM TREE ROOT FROM LARGE SYCAMORE TREE LOCATED NEARBY.
2025-01-31 10:21 | YES | YES | 19900004 |  | 15462 | PHILADELPHIA ELECTRIC CO | 106 CENTER STREET (AKA 327 CENTER STREET | UPPER MERION | MONTGOMERY | PA | 19405 | 3 | NO | 837 | 1989-12-03 | 0 | 1 | 211000 | 181828.6976 | 439019.4699 | Null | 1 | 54 | 21555 | 19891203 | 15 | 25 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.41 | ASA A21.7 | N/A | 0 | 1952 | UNDER PAVEMENT |  | T.A. ROEHRIG, SUPERINTENDENT, GAS DISTRIBUTION | 2158414962 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | POSSIBLE BLASTING | NO |  | NO | 0 |  | NO |  |  | RESIDENTS AND TOWNSHIP OFFICIALS HAD BEEN COMPLAINING TO NEARBY QUARRY ABOUTHEAVY BLASTING, ESPECIALLY ON FRIDAYS. THE INJURED PARTY IS ONE OF THOSE TOWNSHIP OFFICIALS. SUDDEN CIRCUMFERENTIAL BREAK IN A 4-INCH MECHANICAL JOINT CAST IRON MAIN APPARENTLY LET TO GAS MIGRATION INTO NO. 106 (NO. 327) CENTER STREET, RESULTING IN AN EXPLOSION, FIRE, ONE SERIOUS INJURY, ONE MINOR INJURY, AND MODERATE FIRE DAMAGE TO THREE OTHER ADJACENT STRUCTURES ( # 102, 104, AND 108).
2025-01-31 10:21 | YES | NO | 19900007 |  | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 442 GARRETSON ROAD | BRIDGEWATER | SOMERSET | NJ | 08807 | 4 | NO | 1615 | 1989-12-12 | 0 | 0 | 160000 | 137879.5812 | 332905.7592 | Null | 1 | 45 | 22217 | 19891212 | 20 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.5 | ASA A21.7 | UNKNOWN | 0 | 1956 | UNDER PAVEMENT |  |  | 0 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | ON DECEMBER 12, 1989 AT 3:16 PM A LEAK ORDER WAS RECEIVED AT THE PLAINFIELD GAS DISTRICT DISPATCH OFFICE REGARDING A GAS ODOR OUTSIDE OF NUMBER 436 GARRETSON RD., BRIDGEWATER TWP., NJ. A SERVICE SPECIALIST WAS DISPATCHED AND ARRIVED ON THE SCENE AT 4:10 PM. AN EXPLOSION OCCURRED AT 442 GARRETSON RD. AT 4:15 PM; THERE WERE NO PERSONAL INJURIES. STREET DEPARTMENT PERSONNEL ARRIVED AT 4:45 PM AND INSTALLED A REPAIR CLAMP ON THE CRACKED (CIRCUMFERENTIAL) 12 INCH CAST IRON MAIN. REPAIRS WERE COMPLETED AT 9:00 PM.
2025-01-31 10:21 | YES | YES | 19900008 |  | 4473 | ENERGAS CO | 1119 S. POLK ST. | AMARILLO | POTTER | TX | 79101 | 3 | NO | 214 | 1989-11-29 | 1 | 8 | 100000 | 86174.7382 | 208066.0995 | Null | 1 | 0 |  | 19891129 | 0.5 | 1 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISES | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | N/A | N/ | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID V. HAYES, JR. - DIVISION ENGINEER | 8063789872 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN OPEN FLAME GAS HEATER SITUATED TOO CLOSE TO A WALL CAUGHT WALL ON FIRE.
2025-01-31 10:21 | YES | NO | 19900009 |  | 22182 | WASHINGTON GAS LIGHT CO | 519 ELM AVENUE | TAKOMA PARK | PRINCE GEORGES | MD | 20912 | 3 | NO | 1618 | 1989-12-13 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | Null | 1 | 55 | 22296 | 19891213 | 0.25 | 0.25 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 | UNKNOWN | N/A | 0 | 1926 | UNDER GROUND OR UNDER WATER |  | C.E. GOODSON, III - SAFETY SUPERVISOR | 7037504584 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | AT 1329 HOURS ON 12/13/89 WASHINGTON GAS WAS NOTIFIED OF NATURAL GAS ODOR NEAR 519 ELM AVENUE BY A PASSERBY. A PRIORITY 3 CODE ORDER WAS DISPATCHED AT 1350 HOURS AND THE LEAK INVESTIGATOR ARRIVED AT 1420 HOURS. HE CHECKED INSIDETHE HOUSES IN THE IMMEDIATE AREA OF 519 ELM AVE. AND REGISTERED NO GAS INDICATIONS. 519 ELM AVENUE WAS UNOCCUPIED AND HE TESTED OUTSIDE FOR GAS LEAKAGEAND DETERMINED AN UNDERGROUND LEAK EXISTED IN THE AREA. HE CALLED (1440 HOURS)FOR AN EXCAVATION CREW TO FURTHER PINPOINT THE LEAK AND MAKE A REPAIR. HE CONTINUED MONITORING THE OCCUPIED BUILDINGS,UNDER GROUND STRUCTURES AND BAR HOLES FOR POSSIBLE MIGRATION. THE EXCAVATION CREW ARRIVED AT 1500 HOURS, PINPOINTED THE LEAK AND BEGAN EXCAVATING. AT APPROXIMATELY 1610 HOURS THE HOUSE AT519 ELM AVENUE EXPLODED, SLIGHTLY INJURING THE WGL LEAK INVESTIGATOR CHECKING FOR GAS MIGRATION NEAR THE BUILDING WALL. THE ADJACENT HOUSES ON EACH SIDEWERE EXCAVATED, WGL DISPATCH AND THE FIRE DEPARTMENT WERE NOTIFIED. THE LEAKING 4" C.L. LOW PRESSURE MAIN WERE EXPOSED AND REPAIRED AT 1725 HOURS. THISINCIDENT IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19900010 |  | 792 | ATLANTA GAS LIGHT CO | 3280 TRICKUM ROAD | WOODSTOCK | CHEROKEE | GA | 30188 | 3 | NO | 130 | 1989-12-25 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | Null | 1 | 0 | 23131 | 19891225 | 45 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | REGULATOR | 0 | 0 | 1213 | SINGER | 1985 | 1987 | ABOVE GROUND |  | EARNEST F. BRAKE, DIVISION OPERATIONS ENGINEER | 4044271132 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APPARENT INCING OF REGULATOR CAUSING OVERPRSSURE AT FURNACE. SAFETY DEVICE AT FURNACE DID NOT SHUT OFF GAS.
2025-01-31 10:21 | NO | NO | 19900011 |  | 18440 | SOUTH JERSEY GAS CO | 1479 BLACKBURN COURT | VINELAND | CUMBERLAND | NJ | 08360 | 2 | NO | 1309 | 1989-12-25 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 20 | 23175 | 19891226 | 40 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | JOINT | THREAD | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1950 | UNDER PAVEMENT |  | RICHARD J. JACKSON, ASST. VICE PRESIDENT | 6095619000 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | HOUSE FIRE AND EXPLOSION WITH BUILDING AND CONTENTS TOTALLY DESTROYED. NO INJURIES. FOUND 2" BARE STEEL MAIN THREADS CRACKED AT COUPLING. GROUND FROZEN TO MAIN DEPTH OF 33 INCHES. REPAIRED WITH 2" 54C CLAMP.
2025-01-31 10:21 | YES | YES | 19900012 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 2329 ELLIS AVENUE | BRONX |  | NY | 10472 | 4 | NO | 1329 | 1989-12-20 | 0 | 1 | 50000 | 43087.3691 | 104033.0497 | Null | 8 | 31 | 22783 |  | 0.21 | 0.43 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | N/A | N/A | 0 | 1917 | UNDER PAVEMENT |  | FRANK CIMINIELLO, GENERAL MANAGER-BRONX GAS OPERATIONS | 2125791319 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CRACKED 6" CAST IRON GAS MAIN LEAKED GAS INTO BASEMENT OF TWO-FAMILY HOUSEAT 2329 ELLIS AVENUE. EXTENSIVE DAMAGE WAS CAUSED WHEN GAS IGNITED. ONE PERSON RECEIVED FACIAL BURNS AND WAS ADMITTED TO HOSPITAL.
2025-01-31 10:21 | YES | YES | 19900013 |  | 22791 | WISCONSIN PUBLIC SERVICE CORP | 1018 31ST STREET | TWO RIVERS | MANITOWOC | WI | 54241 | 3 | NO | 850 | 1989-12-27 | 0 | 3 | 100000 | 86174.7382 | 208066.0995 | Null | 1 | 0 | 23301 | 19891227 | 43 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1952 | UNDER GROUND OR UNDER WATER |  | THEODORE J. ZABEL, GAS STANDARDS ENGINEER | 4144331040 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THREE PEOPLE WERE INJURED IN A FIRE & EXPLOSION AT 1018 31ST STREET, TWO RIVERS, WI. A 2" WRAPPED STEEL GAS MAIN WAS LEAKING IN FRONT OF THE HOUSE.
2025-01-31 10:21 | NO | NO | 19900019 |  | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 191 WEXFORD BAYNE ROAD | WEXFORD BOROUGH | ALLEGHENY | PA | 15090 | 4 | NO | 2354 | 1989-12-22 | 0 | 0 | 50000 | 43087.3691 | 104033.0497 | Null | 9 | 21 |  | 19891223 | 16.5 | 18 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1947 | UNDER PAVEMENT |  | D.E. WILLIAMS, MANAGER, CONSTRUCTION & MAINTENANCE | 6144606000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-04-04 | YES | 3 | PAINT AND FLAGS | YES |  |  | WE BELIEVE THAT OUR PIPELINE WAS DAMAGED BY A THIRD PARTY AT SOME TIME IN THEPAST, PROBABLY LAST SUMMER. THIS DAMAGE WAS THE CAUSE OF A CRACK IN THE PIPELINE WHEN INFLUENCED BY THE EXTREME WEATHER CONDITIONS AT THE TIME OF THE INCIDENT, AND THE PIPE FAILED SUDDENLY AT THE POINT OF DAMAGE. GAS LEAKED FROMTHIS PIPELINE AT THE POINT OF DAMAGE AND, TAKING THE PATH OF LEAST RESISTANCE, TRAVELED THROUGH THE GROUND AND INTO THE DWELLING, BUILDING UP A CONCENTRATION THAT WAS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE WITHIN THE DWELLING.THE RESULTANT EXPLOSION AND FIRE DESTROYED A SINGLE FAMILY RESIDENCE.
2025-01-31 10:21 | YES | YES | 19900021 |  | 20211 | UNITED CITIES GAS CO | 2501 N. ECOMOMY ROAD | MORRISTOWN | HAMBLEN | TN |  | 3 | NO | 2330 | 1989-12-21 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 0 | 22901 | 19891222 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | JOINT | COMPRESS | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD2513 | PLEXCO | 1989 | 1989 | OTHER | TIE-IN BELL HOLE | DAVID A. SWECKER, DIVISION ENGINEERING MANAGER | 6154611805 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE MAIN IS PART OF A REINFORCEMENT PROJECT WHICH JOINED TWO BRANCHES OF A 25 PSIG DISTRIBUTION SYSTEM. THE PROJECT INVOLVED THE CONTRACT INSTALLATION OF 282' OF 4" P.E. PIPE AND 707' OF 2" P.E. PIPE WHICH JOINED A 2" P.E. MAIN TO A 2" COATED STEEL MAIN. UNITED CITIES PERSONNEL COORDINATED THE TIE-IN OF THIS MAIN UPON COMPLETION OF A 120 PSIG PRESSURE TEST. IT WAS DURING THIS PORTION OF THE INSTALLATION THAT THE INCIDENT OCCURRED. WHILE WORKING WITH DETERIORATING CONDITIONS, 10 MILES PER HOUR WIND, TEMPERATURE AT 7 DEGREES F ANDAPPROACHING 11:00 P.M., WE WERE ATTEMPTING TO COMPLETE THE TIE-IN OF THIS REINFORCEMENT LINE PRIOR TO THE ANTICIPATED PEAK LOAD RESULTING FROM THE "ARTICBLAST" FORECAST FOR DECEMBER 22, 1989. THE CREW PREPARED TO MAKE THE TIE-IN TO THE STEEL SECTIONS WHERE A TRANSITION FITTING HAD BEEN INSTALLED. THE INABILITY TO SECURE A COMPLETE SHUT-OFF OF GAS BY SQUEEZE-OFF ON THE TRANSITION SRESULTED IN A DECISION TO USE A 711 DRESSER COUPLING AS OPPOSED TO BUTT FUSION, WHICH WOULD HAVE REQUIRED THE USE OF THE ELECTRIC FACER IN THE HOLE, A POTENTIALLY HAZARDOUS SITUATION FOR THIS JUNCTION. HOWEVER, WHILE INSTALLING THE 711 DRESSER COUPLING GAS CONTINUED TO FILL THE BELL HOLE AND IN THE PROCESSOF SLIDING THE COUPLING INTO POSITION THERE WAS AN APPARENT DISCHARGE OF STATIC ELECTRICITY IGNITING THE GAS. TWO OF THWORKERS, ON CONTRACTOR AND ONE UCG EMPLOYEE, WERE INJURED REQUIRING HOSPITALIZATION AND ONE CONTRACTOR EMPLOYEE WAS TREATED AND RELEASED. MELVIN ESTEPP, THE CONTRACTOR EMPLOYEE REQUIRINGADMISSION, WAS TREATED FOR BURNS OF THE EYES AND HELD OVERNIGHT FOR OBSERVATION. RICK KILGORE, THE UCG EMPLOYEE, WAS ADMITTED FOR TREATMENT FOR SECOND DEGREE BURNS TO HIS FACE AND HANDS. DENNY STEFFEY WAS TREATED FOR FACIAL BURNS AND RELEASED. THE CONTRACTOR EMPLOYEE'S WERE ABLE TO RETURN TO WORK THE FOLLOWING TUESDAY, DECEMBER 27, 1989 AND THE UCG EMPLOYEE RETURNED TO WORK WEDNESDAY, JANUARY 3, 1990. TO SECURE THE AREA FOLLOWING THE ADDITIONAL UCG PEPRSONNEL USED A MUELLER LINE STOPPER TO STOP THE FLOW OF GAS AND A CAP WAS INSTALLED ON THE LINE. THE FOLLOWING DAY THE LINES WERE CONNECTED WITHOUT INCIDENT COMPLETING THE REINFORCEMENT PROJECT. PLEASE CONTACT ME AT (615) 461-1800IF YOU HAVE QUESTIONS CONCERNING THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 19900022 |  | 2596 | COLUMBIA GAS OF OHIO INC | 5702 ANGOLA ROAD, LOT 13 | TOLEDO | LUCAS | OH |  | 4 | NO | 1406 | 1989-12-29 | 0 | 0 | 64000 | 55151.8325 | 133162.3037 | Null | 0 | 23 | 23558 | 19891229 | 40 | 50 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | ASTM D25-13 | OIL CREEK | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS, MANAGER CONST/MAINT. | 6144606000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR DIGGING A TRENCH TO INSTALL A BURIED ELECTRICAL SERVICE FOR THE MOBILE HOME ON LOT 13 STRUCK THE CUSTOMER-OWNED SERVICE LINE. GAS IGNITED ANDCOMPLETELY DESTROYED THE TRENCHING MACHINE AND THE NEW UNOCCUPIED MOBILE HOME
2025-01-31 10:21 | YES | YES | 19900023 |  | 13710 | NORTHERN ILLINOIS GAS CO | 2100 MAPLEWOOD LAND | JOLIET | WILL | IL | 60433 | 3 | NO | 700 | 1989-12-19 | 1 | 1 | 75000 | 64631.0537 | 156049.5746 | Null | 1 | 30 | 22663 | 19891219 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDETERMINED | OTHER | UNDETERMINED | OTHER | UNDETERMINED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | C.F. WALSHON, MANAGER DIVISION CONSTRUCTION/MAINTENANCE | 8157404100 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION AND FIRE DESTROYED THE RESIDENCE CAUSING INJURIES TO TWO OCCUPANTS, ONE FATAL. WILL COUNTY SHERIFF'S POLICE REPORT INDICATES FURNACE AS A PROBLEM.
2025-01-31 10:21 | NO | NO | 19900024 |  | 12606 | MISSOURI PUBLIC SERVICE CO | 206 WEST ROYLE | RICHMOND | RAY | MO | 64085 | 3 | NO | 1222 | 1989-12-19 | 0 | 0 | 25000 | 21543.6846 | 52016.5249 | Null | 3 | 53 |  | 19891219 | 27 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.35 | AM.ST.A21.6 |  | 0 | 1946 | UNDER GROUND OR UNDER WATER |  |  | 0 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19900026 |  | 6920 | GULF STATES UTILITIES CO | EXXON REFINERY | BATON ROUGE |  | LA | 70805 | 3 | NO | 1330 | 1989-12-24 | 0 | 0 | 25000 | 21543.6846 | 52016.5249 | Null | 1 | 15 |  |  | 140 | 225 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0 |  |  | 0 | 1946 | ABOVE GROUND |  | ROBERT A. BORNE/ENGINEERING SECTION HEAD | 5047671802 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | EXPLOSION WITH-IN EXXON REFINERY BATON ROUGE CAUSED THIS 12" AERIAL CROSSINGTO RUPTURE. FIRE WITH-IN REFINERY WAS BROUGHT UNDER CONTROL THE NEXT DAY.
2025-01-31 10:21 | YES | NO | 19900027 |  | 3170 | DAYTON POWER & LIGHT CO | 1068 VALLEY STREET | DAYTON | MONTGOMERY | OH | 45404 | 3 | NO | 1515 | 1989-12-31 | 0 | 0 | 100000 | 86174.7382 | 208066.0995 | Null | 1 | 45 | 23697 | 19891231 | 25 | 40 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | OTHER | GRAY IRON | 0 | 0 | 4" | WALWORTH | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | RICHARD C. ROTH, MANAGER GAS OPERATIONS | 5132272145 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 4" GRAY IRON LUBIRCATED PLUG VALVE WAS FOUND TO HAVE A CRACK IN THE BODY.
2025-01-31 10:21 | NO | NO | 19900029 |  | 4473 | ENERGAS CO | HCR 2, BOX 3 | KRESS | SWISHER | TX | 79052 | 1 | NO | 800 | 1990-01-19 | 0 | 0 | 700 | 581.8971 | 1404.9716 | Null | 0 | 10 |  | 19900119 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON, DIVISION ENGINEER | 8067984477 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OUR DISPATCHER RECEIVED A CALL AT 8:12 AM. THIS MORNING, JANUARY 19TH. THEYREPORTED A FIRE AT THE HOME OF CLINT ROBERSON 1/2 MILE WEST AND 1/2 MILE SOUTH OF DRESS. OUR SERVICEMAN WAS DISPATCHED TO THE SCENE. THE SERVICEMAN FOUND THAT THE SERVICE REGULATOR AND RELIEF VALVE ON THE METER SETTING HAD A BUILD-UP OF ICE THAT CLOSED OFF THE VENTS. THIS RESULTED IN AN OVER-PRESSURE SITUATION ON THE GAS PIPING AT THE WATER HEATER AND FURNACE IN THE HEATER CLOSET. A SMALL FIRE RESULTED WHICH BURNED THE WIRING ON THE FURNACE AND WATER HEATER CONTROLS AND SMOKED UP THE HEATER CLOSET WALLS. THERE WERE NO INJURIES AND ABOUT $700 FIRE DAMAGE. THE CUSTOMER HAD TURNED OFF A VALVE OUTSIDE THE HOUSE BEFORE OUR SERVICEMAN ARRIVED AND THE FIRE WAS ALREADY EXTINGUISHED.
2025-01-31 10:21 | YES | YES | 19900031 |  | 3210 | DEL RIO GAS SYSTEM, CITY OF | 610 W. CORTINAS ST. | DEL RIO | VAL VERDE | TX | 78840 | 0 | NO | 1300 | 1989-12-15 | 1 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19891215 | 7 | 29 | BY TEST | 7 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE HOME | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MANUEL RIVERA/GAS SYSTEM SUPERINTENDENT | 5127748620 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 12/16/89 AT APPROXIMATELY 1:05 PM OFFICERS RUBID AND SANTELLANES WERE DISPATCHED TO 610 W. CONTINAS IN REFERENCE TO A DECEASED VICTIM. UPON ARRIVAL AND FURTHER INVESTIGATION SUBTAINED FROM EMS ADVISED OFFICERS RUBID AND SANTELLANES THAT THERE WAS A STRONG ODOR OF NATURAL GAS UPON ENTERING THE HOUSE IT WAS REVEALED THAT THEIR WAS A STRONG ODOR OF NATURAL GAS. THE FIRE DEPARTMENT WHO WAS AT THE SCENE TURNED OFF THE GAS AT THE ABOVE ADDRESS. AT APPROXIMATELY 1:43 PM. J.P. BEST PRONOUNCED VICTIM DEAD.
2025-01-31 10:21 | YES | YES | 19900032 |  | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 3900 KENNEDY AVENUE | EAST CHICAGO | LAKE | IN | 46312 | 3 | NO | 2033 | 1989-12-21 | 0 | 1 | 10000 | 8617.4738 | 20806.6099 | Null | 1 | 0 |  | 19891222 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API5L |  | 0 | 1942 | ABOVE GROUND |  | D.M. CAMPOS, MANAGER OF GAS CONTROL & STORAGE | 2198535603 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON DECEMBER 21,1989, AT APPROXIMATELY 8:30 PM., AN OFFICE TRAILER LOCATED AT3900 MICHIGAN AVENUE, EAST CHICAGO, INDIANA, CAUGHT FIRE AND MR. KEVIN REYESSUFFERED BURNS AND WAS HOSPITALIZED. ALTHOUGH THERE WAS NO GAS SERVICE TO THE TRAILER, GAS LEAKING FROM A DAMAGED 2" STEEL SERVICE NEARBY APPARENTLY MIGRATED UNDERGROUND DUE TO FROZEN SOIL CONDITIONS FINDING ITS WAY UNDER THE TRAILER TO THE WARMER GROUND UNTIL IT ENTERED THE TRAILER FROM UNDERNEATH AND BECAME IGNITED. BUT FOR DAMAGE TO THE STEEL SERVICE PIPE DURING CONSTRUCTION BY THE CUSTOMER OF ITS UNDERGROUND ELECTRIC SERVICE TO THE TRAILER, THERE WOULD HAVE BEEN NO LEAK AND NO RESULTING FIRE.
2025-01-31 10:21 | NO | NO | 19900033 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | 2705 SOUTH SAWYER (REAR HOUSE) | CHICAGO | COOK | IL | 60623 | 3 | NO | 1634 | 1989-12-29 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 1 | 23578 | 19891229 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INTERIOR SERVICE PIPING | OTHER | NO FAILURE | OTHER | UNKNOWN | 1 | 0.133 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | J.B. JONES , DIST. DEPT. GENERAL SUPERINTENDENT | 3124314682 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER OF RECORD FOR INCIDENT LOCATION REMOVED A SECTION OF INTERIOR SERVICE PIPE IN THE KITCHEN AREA. THIS ALLOWED GAS TO ESCAPE INTO THE BUILDING AND IT IGNITED FROM AN UNKNONW SOURCE.
2025-01-31 10:21 | NO | NO | 19900034 |  | 12642 | MOBILE GAS SERVICE CORP | 55 CLARENCE AVENUE | MOBILE | MOBILE | AL | 36610 | 3 | NO | 950 | 1989-12-25 | 0 | 0 | 5000 | 4308.7369 | 10403.305 | Null | 1 | 10 | 23136 | 19891225 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.37 | N/A | N/A | 0 | 0 | UNDER PAVEMENT |  | GERALD S. KEEN , VICE - PRESIDENT OPERATIONS | 2054762720 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | SERVICEMAN A. CAMPBELL WAS DISPATCHED TO 805 WILLJOHN STREET AT 9:00 AM. ON DECEMBER 25, 1989 TO INVESTIGATE A GAS ODOR. UPON ARRIVAL AT 9:14 AM., CAMPBELL DETECTED S STRONG GAS ODOR ON THE NORTHEAST CORNER OF WILLJOHN AND CLARENCE STREETS. HE CHECKED THE NORTHWEST CORNER BUT DID NOT SMELL GAS THERE. HETHEN REQUESTED A CONSTRUCTION FOREMAN. A. CAMPBELL SAW MR. KENNEDY PARK HISCAR ON THE WEST SIDE OF CLARENCE STREET AND GET OUT. AT 9:45 AM., DISPATCHER BOB WHITE DISPATCHED R. MUMFORD TO WILLJOHN AND CLARENCE STREETS AND DISPATCHED A. CAMPBELL TO ANOTHER GAS LEAK CALL ON CLINTON STREET. R. MUMFORD ARRIVED AT 9:50 AM. MUMFORD STATED THAT WHEN HE DROVE UP, MR. KENNEDY WAS STARTING HIS CAR AND IGNITION OCCURRED. MUMFORD IMMEDIATELY CALLED FOR THE FIRE DEPARTMENT AND THEN TRIED TO EXTINGUISH THE FIRE BUT COULD NOT. THE PRITCHARD FIRE DEPARTMENT RESPONDED AND TRIED UNSUCCESSFULLY TO PUT OUT THE FIRE WITH WATER. I WAS IN SERVICE AT ABOUT 10:00 AM. AND MR. LEE CAME IN SERVICE AT APPROXIMATELY 10:10 AM. MR. LEE REQUESTED A SERVICEMAN TO PICK UP FIRE EXTINGUISHERS; AND I PROCEEDED TO THE SITE OF THE FIRE. UPON MY ARRIVAL AT APPROXIMATELY 10:20 AM., I REQUESTED A WRECKER FROM THE PRICHARD POLICE DEPARTMENT TO MOVE THE CAR. I WAS ADVISED THAT THE CAP ON THE FUEL TANK HAD BLOWN OFF AND THERE WAS NO DANGER OF IT EXPLODING. I WAS ALSO ADVISED THAT THE METERS TO ADJACENT HOUSES HAD BEEN TURNED OFF, THE HOUSES HAD BEEN CHECKED FORGAS INSIDE AND THE PEOPLE HAD BEEN ADVISED TO KEEP ALL DOORS AND WINDOWS CLOSED. THE WRECKER ARRIVED APPROXIMATELY 20 MINUTES LATER AND PULLED THE BURNING CAR ABOUT 50 FEET UP WIND FROM THE FIRE. THE FIRE DEPARTMENT THEN PUT OUTTHE FIRE IN THE CAR. THEY THEN PULLED THE CAR 50 FEET FURTHER FROM THE BURNING NATURAL GAS. WHILE I HELD A BACK-UP FIRE EXTINGUISHER, L. DOTSON, R. MUMFORD, DALE HANNAH AND A. CAMPBELL USED FOUR DRY-CHEMICAL EXTINGUISHERS TO PUTOUT THE FIRE. AT THIS POINT, L. DOTSON AND R. MUMFORD PROCEEDED TO LOCATE THE MAIN AND THE LEAK.
2025-01-31 10:21 | NO | NO | 19900037 |  | 18456 | SOUTHEAST ALABAMA GAS DISTRICT | 1017 E. COMMERCE ST. | GREENVILLE | BUTLER | AL | 36037 | 3 | NO | 1700 | 1990-01-06 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 0 |  | 19900108 | 30 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREWED | OTHER | GALV. | 1 | 0.133 | N/A | N/A | 0 | 1955 | UNDER PAVEMENT |  | ARNIE C. COBB, JR., SUPERINTENDENT OF ENG. & GAS CONTROL | 2052224177 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | WE FOUND THAT THE SERVICE LINE HAD BEEN HIT BY EQUIPMENT ON THE OPPOSITE SIDE OF THE STREET FROM THE MAIN. THE BLOW HAD CAUSED A HAIRLINE CRACK IN THE THREADS WHERE IT WAS SCREWED INTO AN ELL NEAR THE TAP ON THE MAIN, CAUSING A GAS LEAK.
2025-01-31 10:21 | NO | NO | 19900038 |  | 18532 | SOUTHERN UNION GAS CO | 4602 CANDLETREE LANE | AUSTIN | TRAVIS | TX | 78744 | 3 | NO | 2100 | 1990-01-09 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 25 |  | 19900109 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L-B | N/A | 0 | 1975 | UNDER PAVEMENT |  | DENNIS WORLEY, REGIONAL ENGINEER | 5124651110 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-01-07 | YES | 3 | YELLOW PAINT | NO |  |  | ON THE EVENING OF JANUARY 9, 1990, A MAINTENANCE CREW FOR THE CITY OF AUSTINWATER/WASTEWATER DEPARTMENT WAS EXCAVATING TO EXPOSE A LEAKING WATER MAIN TAP LOCATED UNDER THE PAVEMENT IN FRONT FOF 4602 CANDLETREE LANE. WHILE EXCAVAITING WITHIN THE ROADWAY, THE CITY CREW UNCOVERED A 3/4" WRAPPED STEEL SERVICE THAT WAS BEING UTILIZED AS A GAS SERVICE FOR 4601 CANDLETREE LANE. THIS SERVICE HAD BEEN ACCURATELY LOCATED AND MARKED ON SUNDAY, JANUARY 7, 1990, BY ASOUTHERN UNION GAS COMPANY REPRESENTATIVE IN RESPONSE TO AN EMERGENCY REQUEST FOR UTILITY LOCATIONS RECEIVED ON THAT SAME DAY. THE CITY OF AUSTIN'S MAINTENANCE CREW PROCEDED TO FULLY EXPOSE THE GAS LINE AS IT CROSSED THEIR EXCAVATION SITE. THIS WAS ACCOMPLISHED WITHOUT ANY DAMAGE TO THE GAS FACILITY IN QUESTION. HOWEVER, THE CREWS EXCAVATION SITE BEGAN TO FILL WITH WATER FROM THE LEAKING WATER TAP AT A RATE THAT THEIR WATER PUMPS COULD NOT KEEP UP WITH THE FLOW AND EVENTUALLY COVERED THE EXPOSED GAS LINE WITH WATER. THE CITY'S MAINTENANCE CREW THEN DECIDED TO UTILIZE THE BUCKET ON THEIR BACKHOE TO DIP THE WATER FROM THE EXCAVATION SITE. WHILE IN THE PROCESS OF DIPPING THE WATERWITH THE BACKHOE BUCKET THE OPERATOR CAUGHT THE GAS SERVICE, WHICH HAD BEEN PREVIOUSLY EXPOSED, AND PROCEDED TO PULL THE SERVICE FROM THE 2" STEEL GAS MAIN WHICH WAS LOCATED APPROXIMATELY 6' NORTH OF THE EXCAVATION SITE. AT APPROXIMATELY 22:00 HOURS (10:00 PM) ON TUESDAY, JANUARY 9, 1990, THE SOUTHERN UNION GAS EMERGENCY DISPATCHER RECEIVED A PHONE CALL FROM THE CITY OF AUSTIN DISPATCHER NOTIFYING US OF A BLOWING GAS LEAK AT THE LOCATION NOTED ABOVE. OUR (SUG) DISPATCHER PROCEDED TO ROUTE A SERVICE AND INSTALLATION SPECIALIST TO THE LOCATION TO EVALUATE AND REPORT THE CONDITIONS. THEY THEN PROCEDED TO NOTIFY THE AFTER HOURS EMERGENCY MAINTENANCE CREW AND ROUTED THEM TO THE INCIDENT SITE. OUR EMERGENCY MAINTENANCE CREW ARRIVED AT APPROXIMATELY 22:46 (10:46) ON THE SAME EVENING AND, AFTER PINPOINTING THE PRECISE LOCATION OF THE DAMAGE, PROCEDED TO EXCAVATE TO EXPOSE THE DAMAGED SERVICE TAP. THE SERVICE TAP WAS LOCATED UNDER THE DRIVEWAY APPROACH TO 4602 CANDLETREE LANE. THIS REQUIRED OUR EMERGENCY MAINTENANCE CREW TO MAKE A 4' X 4' CONCRETE DRIVEWAY APPROACH CUT BEFORE THEY WOULD BE ABLE TO EXPOSE THE MAIN TAP. THE DRIVEWAY APPROACH CUT HAD BEEN COMPLETED AND THE SOUTHERN UNION GAS COMPANY EMERGENCY CREW WAS IN THE PROCESS OF EXCAVATING THE SOIL WITH A BACKHOE TO EXPOSE THE MAIN LINE WHEN AT APPROXIMATELY 23:45 HOURS (11:45 PM) THE EXCAPING GAS IGNITED. THESOURCE OF IGNITION IS STILL UNKNOWN. HOWEVER, WITNESSES STATE THAT THE IGNITION SOURCE APPEARED TO BE BELOW GROUND.
2025-01-31 10:21 | YES | YES | 19900039 |  | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 301 WEST HWY. 82 | NEW BOSTON | BOWIE | TX | 75570 | 3 | NO | 2012 | 1989-12-11 | 0 | 1 | 100000 | 86174.7382 | 208066.0995 | YES | 0 | 6 |  | 19891212 | 11 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER EQUIPMENT | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS L. CUMMINS | 2146283337 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | HOT WATER CIRCULATING BOILER EXPLODED.
2025-01-31 10:21 | YES | YES | 19900040 |  | 4060 | EAST OHIO GAS CO | 97 FOX HALL DRIVE | SOUTH RUSSELL | GEAUGA | OH | 44022 | 3 | NO | 1300 | 1989-12-19 | 0 | 1 | 300 | 258.5242 | 624.1983 | Null | 0 | 0 | 22690 | 19891219 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ASTMD2513 | PHILLIPS DRISCOPE | 0 | 1989 | UNDER GROUND OR UNDER WATER |  | PAUL E. OLEKSA, ENVIRONMENTAL & CODES ENGINEER | 2164326858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | WHILE MAKING REPAIRS TO AN ELECTRIC SERVICE LINE IN FRONT OF 97 FOX HALL DRIVE AN ELECTRIC UTILITY EMPLOYEE BURNED THROUGH A 5/8-INCH PLASTIC SERVICE LINE CAUSING A FLASH FIRE, INJURING HIMSELF AND DAMAGING THE SERVICE LINE. THEAREA WAS MADE SAFE IMMEDIATELY WHEN THE EXCESS FLOW VALVE WAS ACTIVATED & SHUT OFF THE SOURCE OF GAS.
2025-01-31 10:21 | YES | NO | 19900041 |  | 15469 | PHILADELPHIA GAS WORKS | 7423 STENTON AVENUE | PHILADELPHIA | PHILADELPHIA | PA | 19150 | 4 | NO | 2146 | 1990-01-04 | 0 | 0 | 100000 | 83128.1566 | 200710.2273 | Null | 1 | 58 | 326 | 19900105 | 0.26 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 | N/A | N/A | 1937 | 1938 | UNDER PAVEMENT |  | LEO T. MIDDLEMISS, MANAGER DISTRIBUTION DEPARTMENT | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: FROST | 24" FROST DEPTH | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19900047 |  | 4590 | EUNICE GAS DEPT, CITY OF | MAPLE AVE & 5TH EAST ST. | EUNICE |  | LA | 70535 | 1 | NO | 1449 | 1990-02-06 | 0 | 6 | 0 | 0 | 0 | YES | 4 | 30 |  | 19900206 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 3 | 0.4 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | BERNARD BERGERON , GAS SUPT. | 3184574340 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-02-01 | YES | 2 | PAINT | YES |  |  | DAMAGE DONE BY 3RD PARTY CONTRACTOR FOR UNION PACIFIC.
2025-01-31 10:21 | YES | NO | 19900048 |  | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 1117 S. ALBEMARLE STREET | SPRING GARDEN TOWNSHIP | YORK | PA | 17403 | 4 | NO | 1559 | 1990-01-11 | 0 | 0 | 150000 | 124692.2348 | 301065.3409 | Null | 0 | 35 | 807 | 19900111 | 45 | 57 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | GRADE B | N/A | 0 | 1934 | UNDER PAVEMENT |  | D.E. WILIAMS, MGR., CONSTRUCTION & MAINTENANCE | 6144606000 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | SUSBEQUENT INVESTIGATION OF THE FAILUE TO OUR 2" STEEL PIPELINE REVEALED THAT THE PIPELINE WAS SNAGGED AND DAMAGED BY A BACKHOE BUCKET, MOST LIKELY DURING PREVIOUS CONSTRUCTION OF A SEWER LINE, BY A SEWER CONTRACTOR. THE PRIOR DAMAGE EVENTUALLY RESULTED IN THE PIPE'S FAILURE. GAS LEAKED FROM THIS FAILURE, MIGRATED INTO TWO DWELLINGS, AND WAS IGNITED IN EACH BY UNKNOWN SOURCES WITHIN THE TWO BUILDINGS. THE RESULTANT EXPLOSIONS AND FIRES DESTROYED BOTH SINGLE FAMILY RESIDENCES.
2025-01-31 10:21 | NO | NO | 19900050 |  | 909 | AUSTELL NATURAL GAS SYSTEM, CITY OF |  | COBB | DOUGLAS | GA |  | 3 | NO | 510 | 1990-02-10 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 30 | 7823 | 19900210 | 42 | 58 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | OTHER | UNKNOWN | STEEL |  | 0.75 | 0.113 | API-5L-B | VARIES | 0 | 0 | WITHIN/UNDER BUILDING |  | E.G. HARMON, GENERAL MANAGER | 4049481841 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SEE CONMMENTS | NO |  | NO | 0 |  | NO |  |  | HIGH WINDS AND POSSIBLE MULTIPLE TORNADOES STRUCK JUST AFTER 5:00 AM. ON SATURDAY MORNING, FEBRUARY 10,1990. GAS SERVICE LINES WERE DAMAGED WHEN TREES WERE TOPPLED TEARING LINES FROM GROUND, WHEN HOUSES WERE DEMOLISHED AND WHEN MOBILE HOMES WERE BLOWN FROM FOUNDATIONS ONTO RISER AND METER ASSEMBLIES. NO INJURIES, FATALITIES OR PROPERTY DAMAGE WAS CAUSED BY LEAKING GAS. SOME FIRESWERE FUELED BY BROKEN GAS LINES (MOSTLY FUEL LINES INSIDE RESIDENCE) UNTIL GAS SERVICE WAS DISCONTINUED.
2025-01-31 10:21 | YES | NO | 19900051 |  | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 1521 VANDORA SPRINGS ROAD | GARNER | WAKE | NC | 27529 | 2 | NO | 836 | 1989-12-20 | 0 | 0 | 200000 | 172349.4764 | 416132.199 | Null | 0 | 15 | 22756 | 19891220 | 58 | 90 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 1984 | WITHIN/UNDER BUILDING |  | MR. JOSEPH F. NOON, SR. VICE PRES. ENG. AND OPER. SERVICES | 7048646731 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AFTER FURTHER CONSIDERATION AND INVESTIGATION OF THE INCIDENT, IT APPEARS THAT THIS MIGHT BE A NON-REPORTABLE ACCIDENT. IT APPEARS THAT THERE WAS A MALFUNCTION OF THE SERVICE REGULATOR WHICH CAUSED OVERPRESSURING OF THE FUEL LINE. WE NOW SUSPECT THAT THIS DID NOT OCCUR BUT RATHER THERE WAS A MALFUNCITON OF ONE OF TWO FURNACES WHICH MAY HAVE CAUSED THE ACCIDENT. INVESTIGATION IS CONTINUING.
2025-01-31 10:21 | YES | YES | 19900052 |  | 12684 | MONTANA - DAKOTA UTILITIES CO | HC68 - MILE DRIVE (TRACY GROW) | GLENDIVE | DAWSON | MT | 59330 | 1 | NO | 804 | 1989-12-16 | 0 | 1 | 100 | 86.1747 | 208.0661 | Null | 1 | 30 |  | 19891219 | 47 | 48 | BY TEST | 48 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.315 | 0.119 | ASTM D2513 | DUPONT | 1988 | 1989 | UNDER GROUND OR UNDER WATER |  | GORDON J. SCHMITT, ENGINEERING ASST. | 4063593100 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | EXPOSED | YES |  |  | CUSTOMER HAD DUG A WELL PIT ALONG SIDE OF HIS HOUSE WHICH REQUIRED RELOCATION OF THE GAS SERVICE LINE AND METER SETTING. THE CUSTOMER HAD THE WELL PIT EXCAVATED AND WAS PREPARING TO BUILD THE WELL HOUSE. RATHER THAN TRENCH AROUND THE WELL PIT AND A LARGE PILE OF DIRT AND SCRAP LUMBER WHICH WOULD HAVE INVOLVED ABOUT ANOTHER 80 FEET OF TRENCH AND MATERIALS, WE LAID THE GAS LINE ALONG THE BOTTOM OF THE WELL PIT HOLE OUTSIDE OF THE FOOTINGS. THE CUSTOMER SAID HE WOULD BACKFILL THIS OPENING BECAUSE HE HAD SOME ADDITONAL WORK TO DO IN THE WELL PIT HOLE AND THAT HE WOULD ALSO BACKFILL THE SHORT TRENCH WE HAD DUG TO THE HOUSE TO COMPLETE THE PROJECT. HE DID NOT GET THE BACKFILLING DONE WHICH CAUSED A WATER LINE COMING FROM THE WELL PIT TO FREEZE. WHILE TRYING TO THAW OUT THE GROUND OVER THE WATER LINE WITH A PROPANE TORCH HE INADVERTENTLY HEATED THE PLASTIC GAS LINE CAUSING IT TO RUPTURE AND IGNITE.
2025-01-31 10:21 | NO | NO | 19900053 |  | 8170 | INTERSTATE POWER CO | 410 FLOYD | RUDD | FLOYD | IA | 50471 | 3 | NO | 1555 | 1990-02-01 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 | 6702 | 19900202 | 60 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1970 | WITHIN/UNDER BUILDING |  | RAY P. RICHARDS, DIRECTOR, GAS OPERATIONS | 3195572218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | UPON EXCAVATION, IT WAS DISCOVERED THAT A 6" LONG STAINLESS STEEL LEAK REPAIR CLAMP HAD BEEN INSTALLED AROUND A SECTION OF 2" STEEL GAS MAIN THAT HAD BEEN HIT BY A BACKHOE TOOTH. THE PIPE WAS DEFORMED AND WELL OUT OF ROUND AND WAS NOT LEAKING AT THE TIME IT WAS STRUCK BY THE BACKHOE. THE CLAMP'S PURPOSE IS GENERALLY FOR USE AS A SEAL FOR VERY MINOR CORROSION PINHOLE LEAKS. THE PIPE CRACKED BENEATH THE POINT WHERE THE PAVEMENT MEETS THE BERM, WHERE THE BACHOE TOOTH CAUSED THE ORIGINAL DEFORMATION TO THE PIPE, ALLOWING NATURAL GAS AT60 PSIG TO MIGRATE TO AN AREA UNDER THE PORCH OF A RESIDENCE AT 410 FLOYD, IN RUDD, IOWA, WHERE THE EXPLOSION OCCURRED ON THE AFTERNOON OF FEBRUARY 2, 1990. IT'S BELIEVED THAT THE PIPE CRACKED AT APPROXIMATELY 11:30 A.M. THAT DAY. THE PIPE WAS ORIGINALLY INSTALLED BETWEEN 1970 AND 1977. OUR RECORDS DO NOT REVEAL WHEN THE PIPE WAS DAMAGED BY THE BACKHOE.
2025-01-31 10:21 | YES | YES | 19900054 |  | 15329 | PEOPLES GAS LIGHT & COKE CO | 2534 WEST CORTEZ STREET | CHICAGO | COOK | IL | 60622 | 3 | NO | 1155 | 1990-01-24 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 | 1742 | 19900124 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | OTHER | UNKNOWN | BODY OF PIPE |  | CAST IRON |  | 6 | 0 | N/A | N/A | 0 | 1894 | UNDER PAVEMENT |  | P.J. EGIZIO, DISTRICT SUPERINTENDENT | 3127946800 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | A 6" CAST IRON LOW PRESSURE MAIN LOCATED IN THE PARKWAY OPPOSITE A WATER METER VAULT WAS DAMAGED BY FROST. GAS FROM THE DAMAGED MAIN MIGRATED ALONG THE WATER SERVICE INTO THE VAULT AND IGNITED WHEN A WATER DEPARTMENT EMPLOYEE SMOKING A CIGARETTE LIFTED THE COVER OFF THE WATER METER VAUL
2025-01-31 10:21 | NO | NO | 19900058 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 2509 REDONDO BEACH BLVD. | GARDENA | LOS ANGELES | CA | 90249 | 3 | NO | 1315 | 1990-02-13 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 1 | 0 | 8264 | 19900213 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | DUPONT | 0 | 1979 | UNDER GROUND OR UNDER WATER |  | RICHARD M. MORROW | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | MASONRY CONTRACTOR EXCAVATED TO EXPOSE SUBTERRANEAN WALL TO DRY AND WATERPROOF IT. A 2 INCH PLASTIC SERVICE WAS ALSO UNCOVERED. A PROPANE HEATER USED IN THE DRYING PROCESS WAS LEFT UNATTENDED, MELTING THE SERVICE, IGNITING THE GAS. THREE APARTMENT UNITS WERE DAMAGED BY FIRE.
2025-01-31 10:21 | NO | NO | 19900060 |  | 11680 | LONE STAR GAS CO | 1600 BLOCK WEST HENDERSON | CLEBURNE | JOHNSON | TX | 76031 | 3 | NO | 250 | 1989-01-15 | 0 | 0 | 5000 | 4308.7369 | 10403.305 | Null | 1 | 0 |  | 19890115 | 20 | 55 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | W.L. SIMMEL, DISTRICT MANAGER | 8176456633 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | METER LOOP HIT BY VEHICLE BREAKING INLET RISER. GAS IN\GNITED CAUSING VEHICLE TO BURN. VEHICLE DESTROYED. NO ONE WAS INJURED. SERVICE WAS INTERRUPTEDTO ONE COMMERCIAL CUSTOMER.
2025-01-31 10:21 | NO | NO | 19900062 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 1810 MATAMORAS | HOUSTON | HARRIS | TX | 77023 | 3 | NO | 920 | 1989-01-19 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19890119 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.12 | API5L | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | RISER APPARENTLY STRUCK BY UNKNOWN FORCE, POSSIBLY AUTOMOBILE, CAUSING BREAKIN THREADS AT COUPLING.
2025-01-31 10:21 | YES | NO | 19900064 |  | 15469 | PHILADELPHIA GAS WORKS | 251 SOUTH 56TH STREET | PHILADELPHIA | PHILADELPHIA | PA | 19139 | 4 | NO | 1157 | 1990-02-13 | 0 | 0 | 75000 | 62346.1174 | 150532.6705 | Null | 0 | 23 | 8251 | 19900213 | 0.26 | 0.5 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.125 | 0.14 | N/A | N/A | 0 | 1908 | WITHIN/UNDER BUILDING |  | LEO T. MIDDLEMISS, MANAGER DISTRIBUTION DEPARTMENT | 2156846372 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | 1/4" STEEL BROKE | WHILE REBUILDING METER CONNECTION TO 249 S. 56TH ST., OPERATOR'S EMPLOYEE BROKE OFF 1-1/4" STEEL SERVICE BEYOND THE FRONT FOUNDATION WALL, CAUSING NATURAL GAS TO LEAK INTO THE BASEMENT OF 251 S. 56TH ST.
2025-01-31 10:21 | YES | YES | 19900065 |  | 18484 | SOUTHERN CALIFORNIA GAS CO | 1622 PALOMA STREET | PASADENA | LOS ANGELES | CA | 91104 | 3 | NO | 900 | 1990-01-31 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 | 6469 | 19900131 | 0.29 | 0.43 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD M. MORROW | 2136894930 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CONTRACTOR EMPLOYEE, ON SERVICE REPLACEMENT PROJECT, FAILED TO COMPLETELY CLOSE SERVICE RISER VALVE PRIOR TO REMOVING METER. ESCAPING GAS MIGRATED UP THROUGH KITCHEN FLOOR AND WAS IGNITED BY GAS RANGE.
2025-01-31 10:21 | NO | NO | 19900066 |  | 22189 | WASHINGTON NATURAL GAS CO | E. VALLEY HWY,E. & 24 ST. E. | SUMNER | PIERCE | WA | 98390 | 2 | NO | 2235 | 1990-01-19 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 1 | 20 | 1569 | 19900122 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | GATE STATION-CONTROL ROOM | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DOUGLAS DAMM, SAFETY MANAGER | 2062242396 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE DRIVEN BY INTOXICATED DRIVER LEFT THE ROAD AND STRUCK A POWER POLE WHICH FELL TO THE GROUND. COMMERCIAL POWER SHORTED THROUGH GROUND TO 8" STEELGAS LINE. POWER DISCHARGED IN CONTROL ROOM AT DIERINGER GATE (N. TACOMA) STATION, STARTING FIRE WHICH DESTROYED TO CONTROL ROOM.
2025-01-31 10:21 | YES | NO | 19900067 |  | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | FOLMAR PARKWAY | MONTGOMERY | MONTGOMERY | AL | 36043 | 3 | NO | 902 | 1990-03-01 | 0 | 0 | 183076 | 152187.7039 | 367452.2557 | Null | 0 | 19 | 10352 | 19900301 | 150 | 175 | BY TEST | 263 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.156 | API 5L | LTV | 1986 | 1987 | UNDER GROUND OR UNDER WATER |  | THOMAS F. TAYLOR, JR. , DISTRIBUTION ENGINEER | 2053268113 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | A CONTRACTOR, W.S. NEWELL, WAS UTILIZING A CATERPILLAR ROTOFLEX TO TILL AND COMPACT THE SOIL IN AND AROUND THE AREA OF A FOUR-INCH HIGH PRESSURE MAIN IN PREPARATION FOR THE CONSTRUCTION OF A RAILROAD SPUR. THE MACHINE STRUCK THE FOUR-INCH MAIN DURING THE TILLING PROCESS. THE ESCAPING GAS WAS IGNITED SETTING THE ROTOFLEX ON FIRE. THE MACHINE WAS TOTALLY DESTROYED. AFTER ALABAMA GAS CORPORATION WAS NOTIFIED OF THE INCIDENT AND ARRIVED AT THE SCENE, A VALVE UPSTREAM OF THE DAMAGED MAIN WAS CLOSED TO SHUT OFF THE GAS. THERE WERE NO CUSTOMERS THAT WERE INTERRUPTED AS A RESULT OF THE INCIDENT. ALSO, A LINE LOCATION REQUEST WAS NOT RECEIVED.
2025-01-31 10:21 | NO | NO | 19900069 |  | 1704 | BRAZOS RIVER GAS CO | 1/4 MILE S. OF BUNGER "Y" | GRAHAM | YOUNG | TX |  | 2 | NO | 900 | 1990-02-09 | 0 | 0 | 5000 | 4156.4078 | 10035.5114 | Null | 0 | 40 |  | 19900209 | 25 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.152 | SCH.40 |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | PAUL R. JOHNSON, VICE PRESIDENT OPERATIONS | 8173254445 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-11-27 | YES | 3 | PAINT | NO
2025-01-31 10:21 | NO | NO | 19900072 |  | 11680 | LONE STAR GAS CO | NW CORNER OF DELWOOD AT MILES | LONGVIEW | GREGG | TX | 75601 | 1 | NO | 1400 | 1989-12-24 | 0 | 0 | 7400 | 6376.9306 | 15396.8914 | Null | 6 | 0 |  | 19891224 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | GRADE A | LONE STAR STEEL | 1961 | 1961 | UNDER PAVEMENT |  | BENNETT COST, FACILITIES COORDINATOR | 2147539830 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19900073 |  | 11800 | LOUISIANA GAS SERVICE CO | 4345 COLORADO STREET | KENNER | JEFFERSON | LA | 70065 | 3 | NO | 157 | 1990-03-09 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 |  |  | 68 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | SCREWED | STEEL |  | 0.75 | 0.113 | API-5L |  | 0 | 1974 | ABOVE GROUND |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | POLICE REROUTED TRAFFIC AND EVACUATED APPROXIMATELY SIX HOUSES.
2025-01-31 10:21 | YES | NO | 19900074 |  | 16667 | ENERGY NORTH NATURAL GAS INC | 257 MESSER STREET | LACONIA | BELKNAP | NH | 03246 | 3 | NO | 1203 | 1990-03-08 | 0 | 0 | 85000 | 70658.9331 | 170603.6932 | Null | 1 | 0 | 11437 | 19900308 | 58 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.25 | UNKNOWN | UNKNOWN | 0 | 1956 | UNDER PAVEMENT |  | RICHARD G. MACDONALD, DISTRIBUTION MANAGER | 6036254000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-02-27 | YES | 3 | APWA YELLOW MARKING POINT | YES |  |  | THE CONTRACTOR WHILE DRILLING SOIL SAMPLES BORED THROUGH A 6" STEEL GAS MAINOPERATING A 58 PSIG. THE ONE CALL SYSTEM WAS NOTIFIED AND THE GAS MAIN WAS M
2025-01-31 10:21 | YES | YES | 19900076 |  | 728 | ALLIED GAS CO | 101 CENTRE STREET | ASHLAND BORO | SCHUYLKILL | PA | 17921 | 3 | NO | 935 | 1990-01-18 | 0 | 1 | 50000 | 41564.0783 | 100355.1136 | Null | 0 | 0 |  | 19900118 | 0.33 | 2 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.5 | UNKNOWN | UNKNOWN | 0 | 1930 | WITHIN/UNDER BUILDING |  | L. EDWIN LICHTEL - MGR. | 7176486837 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CIRCUMFERENTIAL CRACK ON 6" CAST IRON MAIN. UNSURE AT THIS TIME OF ACTUAL CAUSE OF CRACK. POSSIBILITY THAT CRACK COULD HAVE OCCURRED DUE TO FORCE OF EXPLOSION THAT OCCURRED WITHIN HOUSE # 101 CENTRE STREET, ASHLAND PA.
2025-01-31 10:21 | NO | NO | 19900077 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 321 BAYSHORE DRIVE | INGLESIDE | SAN PATRICIO | TX | 78362 | 2 | NO | 325 | 1989-11-11 | 0 | 0 | 8000 | 6893.9791 | 16645.288 | Null | 0 | 55 |  | 19891111 | 10 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | LANNY W. CARGILE, P.E., OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER INSTALLATION | YES |  |  | SERVICE RISER WAS BROKEN OFF AT THREADS DUE TO TRUCK DRIVING INTO IT. ESCAPING GAS WAS IGNITED. TRUCK WAS BURNED. NO INJURIES.
2025-01-31 10:21 | NO | NO | 19900078 |  | 4499 | ENTEX - DIVISION OF ARKLA INC | 6438 LONG DRIVE | HOUSTON | HARRIS | TX | 77087 | 3 | NO | 1230 | 1990-02-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 |  |  | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | OTHER | UNKNOWN | 1 | 0.133 | API5L | UNKNOWN | 0 | 1955 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE, P.E. - OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | LARGE TRUCK DROVE OFF PAVEMENT ONTO SOFT DIRT. WEIGHT OF TRUCK CAUSED SERVICE LINE TO CRACK IN THREADED JOINT. FIRE DEPARTMENT BLOCKED TRAFFIC AND EVACUATED TWO SMALL BUSINESSES UNTIL SITUATION MADE SAFE.
2025-01-31 10:21 | NO | NO | 19900079 |  | 11680 | LONE STAR GAS CO | 4003 INWOOD | COLLEYVILLE | TARRANT | TX | 76034 | 3 | NO | 1510 | 1990-02-25 | 0 | 0 | 5000 | 4156.4078 | 10035.5114 | Null | 4 | 20 |  | 19900225 | 38 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | UNKNOWN | 0.75 | 0.095 | PE2306 ASTM-251 | PLEXCO | 0 | 1989 | WITHIN/UNDER BUILDING |  | J.K. BENNETT - SUPERINTENDENT | 8179276982 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | INLET METER RISER | NO |  |  | LINE BELIEVED TO BE DAMAGED BY LANSCAPER WHILE INSTALLING A TREE.
2025-01-31 10:21 | YES | NO | 19900081 |  | 1209 | BAY STATE GAS CO | 55 EDDY STREET | SPRINGFIELD | HAMPDEN | MA | 01104 | 3 | NO | 1220 | 1987-01-05 | 0 | 0 | 75000 | 69424.4288 | 167623.0228 | Null | 13 | 12 |  | 19870105 | 0.3 | 0.54 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0 | 0 | N/A | N/A | 0 | 1923 | OTHER | IN BUILDING WALL | CARL A. TYBURSKI | 4137819200 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1987-01-05 | YES | 3 | PAINT | YES |  |  | A SEWER REPAIR CREW WAS EXCAVATING IN FRONT OF THE HOUSE WHEN THEY DAMAGED AGAS SERVICE PIPE. THERE WAS NO SMELL OUTSIDE, BUT THE PIPE WAS PULLED INTO THE WALL CAUSING THE FITTINGS INSIDE TO BREAK OFF. THIS LEAD TO GAS GOING INTO THE HOUSE AND EVENTUALLY WAS IGNITED AND EXPLODED. THE GAS COMPANY WAS NOTIFIED OF THE DAMAGED PIPE WHEN THEY RESPONDED TO THE SCENE FOR AN EXPLOSION.
2025-01-31 10:21 | NO | NO | 19900083 |  | 18440 | SOUTH JERSEY GAS CO | 118 BARTRAM LANE | OCEAN CITY | CAPE MAY | NJ | 08210 | 4 | NO | 623 | 1990-03-07 | 0 | 0 | 0 | 0 | 0 | Null | 2 | 7 | 11204 | 19900307 | 50 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | RICHARD J. JACKSON, ASST. VICE PRESIDENT | 6095619000 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | GAS SERVICE BROKE NEAR THE HOUSE FOUNDATION, RESULTING IN HIGH PRESSURE GAS ENTERING THE HOUSE. GAS WAS ACCIDENTALLY IGNITED INSIDE THE HOUSE CAUSING ANEXPLOSION AND AN ENSUING HOUSE FIRE. HOUSE AND CONTENTS WERE TOTALLY DESTROY
2025-01-31 10:21 | YES | NO | 19900084 |  | 13782 | NORTHERN STATES POWER CO | 3833 RICHTER AVE. | ST. CLOUD | STEARNS | MN | 56301 | 2 | NO | 1153 | 1990-03-08 | 0 | 0 | 90000 | 74815.3409 | 180639.2045 | Null | 13 | 50 | 11439 | 19900308 | 57 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | D2513 | PLEXCO | 0 | 1987 | UNDER GROUND OR UNDER WATER |  | MARK R. ELLSON, GAS ENGINEER | 6122292313 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | UNKNOWN | NO |  | NO | 0 |  | NO |  |  | AS A RESULT OF A 1/4" HOLE BY A POSSIBLE RODENT IN NSP'S 5/8" P.E. GAS LINE,AN EXPLOSION OCCURRED AT 3833 RICHTER AVE. A DEAD RODENT WAS DISCOVERED ADJACENT TO 5/8" P.E. PIPE.
2025-01-31 10:21 | NO | NO | 19900092 |  | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 200 WEST 54TH STREET | NEW YORK |  | NY | 10019 | 4 | NO | 1240 | 1990-02-23 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 19 | 9577 | 19900223 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS W. COWAN, DIV. MANAGER- MANHATTAN GAS OPERATIONS | 2125762443 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CONTRACTOR INSTALLED A NEW METER BAR AND CONTROL VALVE UNDER LIVE CONDITIONS. AS A RESULT, GAS BUILT UP IN UNVENTILATED ROOM. THE CONTRACTOR IGNITED THE GAS WITH A SPARCK FROM HIS ELECTRIC JACKHAMMER.
2025-01-31 10:21 | NO | NO | 19900094 |  | 5470 | FORT STOCKTON MUNICIPAL SYSTEM, CITY OF | HIGHWAY 18, NORTH GATE STATION | FORT STOCKTON | PECOS | TX | 79735 | 1 | NO | 0 | 1990-03-28 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 5 |  | 19900328 | 165 | 190 | BY TEST | 190 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | GAUGE TEST POINT | STEEL |  | 4.5 | 0.237 | GRX42 | GIBCO PIPE CO. | 1983 | 1983 | ABOVE GROUND |  | JESSE GARCIA, CITY MANAGER | 9153368525 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THIRD PARTY RAN INTO NORTH GATE AFTER RUNNING STOP SIGN, AND KNOCKING DOWN 2" GAUGE PIPE.
2025-01-31 10:21 | NO | NO | 19900095 |  | 17621 | SALGAS INC OF CRESTED BUTTE | EAST 500 BLOCK ELK AVE. | CRESTED BUTTE | GUNNISON | CO | 81224 | 3 | NO | 1630 | 1990-03-12 | 0 | 0 | 0 | 0 | 0 | YES | 12 | 30 | 13219 | 19900319 | 18 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | JOINT | COMPRESSION COUPLING | STEEL |  | 1.25 | 0.187 | SCHEDULE 40 | N/A | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | PAUL STAHLMAN | 4175323101 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | UNKNOWN | NO |  | NO | 0 |  | NO |  |  | ON MARCH 6, 1990 AT 08:55 HRS., THE CRESTED BUTTE STATE BANK WAS LEVELED BY AN EXPLOSION. THE CAUSE OF THE EXPLOSION IS AN UNKNOWN GAS. 3 PEOPLE WERE KILLED, 14 INJURED. THE BUILDING WAS DESTROYED. ON MARCH 12, 1990 AT 16:30 HRS., THIS OFFICE WAS NOTIFIED OF A POSSIBLE GAS LEAK AT ONE OF THE MAIN LINESACROSS THE STREET FROM THE BANK. CREWS WERE SENT TO THE AREA AND THE MAIN WAS CUT AND PLUGED WHERE THE LEAK READINGS WERE OCCURING. SPECIALISTS AND GOVERNMENTAL AGENTS FROM ALL OVER ARE ANALIZING THE BROKEN JOINT TO DETERMINE WHETHER OR NOT THE PIPE WAS BROKEN BEFORE THE EXPLOSION OR CAUSED BY THE EXPLOSION. NO CONCLUSIVE REPORTS HAVE BEEN MADE AVALIABLE AT THIS TIME. THE DEFECTIVE SECTION OF THE MAIN HAS BEEN REMOVED AND NEW PIPING HAS BEEN ADDED TO RESTORE THE UNDERGROUND LINE. ALL WORK IS BEING SUPERVISED BY THE PUC AREA REPRESENTATIVE. REPRESENATIVES FROM THE EPA, OSHA, THE TOWN OF CRESTED BUTTE, THE STATE ATTORNEY GENERALS OFFICE AND THE MEDIA ARE ALL MONITORING THE SITUATION. OTHER PARTIES PRESENT AT THE RECONNECTION OF THE GAS MAIN WERE: PETERSTAPP - STATE ATTORNEY GENERALS OFFICE. LOREN SWICK - PUC. LARRY ADAMS- TOWN OF CRESTED BUTTE.
2025-01-31 10:21 | NO | NO | 19900096 |  | 20050 | UNION ELECTRIC CO | 1802 JACKSON ST. | COLUMBIA | BOONE | MO | 65202 | 3 | NO | 1950 | 1990-02-16 | 0 | 0 | 30000 | 24938.447 | 60213.0682 | Null | 0 | 10 | 8725 | 19900216 | 20 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 | N/A | N/A | 1962 | 1962 | UNDER PAVEMENT |  | WILLIAM J. LUEBBERT, SUPERVISING ENGINEER | 3146350171 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CIRCUMFERENTIAL FRACTURE OF CAST IRON PIPE. NO READILY RECOGNIZABLE CAUSE.
2025-01-31 10:21 | YES | NO | 19900097 | 1990-04-13 | 20110 | UNION LIGHT HEAT & POWER CO | 643 GRAND AVENUE | TAYLOR MILL | KENTON | KY |  | 3 | NO | 1559 | 1990-03-13 | 0 | 0 | 70000 | 58189.7096 | 140497.1591 | YES | 2 | 31 | 12265 | 19900313 | 17 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 | 0.38 | ASA-A21.7 | UNKNOWN | 0 | 1957 | UNDER PAVEMENT |  | HUBERT J. FANTETTI, DIRECTOR | 5136322671 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | UNKNOWN | YES
2025-01-31 10:21 | YES | YES | 19900098 | 1990-04-19 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 155 NORTH JEFFERSON | BERNE | ADAMS | IN | 46711 | 2 | NO | 1330 | 1990-03-22 | 0 | 1 | 100000 | 83128.1566 | 200710.2273 | Null | 1 | 45 | 13919 | 19900323 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESION COUPLING | STEEL |  | 0.75 | 0.113 | N/A | N/A | 0 | 1964 | UNDER PAVEMENT |  | D.M. CAMPOS, MANAGER OF GAS CONTROL & STORAGE | 2198535603 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-03-12 | YES | 3 | MARKED IN PAINT | YES |  |  | CONSTRUCTION EQUIPMENT BEING UTILIZED BY JOHNSON BROTHERS CONSTRUCTION OF YORKTOWN, INDIANA, STRUCK AND PULLED OUR A 3/4" STEEL SERVICE FROM THE COMPRESSION COUPLING OF THE 4" DISTRIBUTION MAIN OPERATING AT 45 PSIG. THIS LINE SERVED A BUILDING AT 109 EAST MAIN. LEAKING GAS, SOMEHOW, FOUND ITS WAY INTO THE BUILDING ACROSS THE ALLEY AT 155 NORTH JEFFERSON. THE GAS, SOMEHOW, IGNITED AND SET OFF THE EXPLOSION AND FIRE.
2025-01-31 10:21 | NO | NO | 19900099 | 1990-04-12 | 8170 | INTERSTATE POWER CO | INTERSECTION OF N. WALNUT & N. BROADWAY | MANLY | WORTH | IA | 50456 | 3 | NO | 1650 | 1990-03-12 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 10 | 12131 | 19900313 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | VALVE |  | CAST IRON |  | 1 | 0 | N/A | N/A | 0 | 0 | UNDER PAVEMENT |  | RAY P. RICHARDS, DIRECTOR, GAS OPERATIONS | 3195572218 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19900105 | 1990-04-30 | 20211 | UNITED CITIES GAS CO | 110 W. SEVIER AVENUE | KINGSPORT | SULLIVAN | TN | 37662 | 4 | NO | 2112 | 1990-03-26 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 | 14457 | 19900327 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1955 | WITHIN/UNDER BUILDING |  | DAVID A. SWECKER, DIVISION ENGINEERING MANAGER | 6154611805 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-03-23 | YES | 3 | YELLOW PAINT | YES |  |  | ON MONDAY, MARCH 26, 1990 AT APPROXIMATELY 9:00 PM. A HOUSE EXPLOSION AND FIRE WAS REPORTED AT THE CORNER OF WEST SEVIER AVENUE AND BROAD STREET IN KINGSPORT, TENNESSEE. THE SITE WAS LATER IDENTIFIED AS 110 WEST SEVIER AVENUE, ANUNOCCUPIED TWO-STORY, FRAME STRUCTURE. IT WAS BORDERED BY A CHURCH, RESIDENCES OF SIMILAR STRUCTURE, AND PARKING LOTS. MANY BUILDINGS IN THE AREA SURROUNDING THE SITE HAVE REPORTED DAMAGE WHICH INCLUDE BROKEN WINDOWS, DAMAGED ROOFS AND PLASTER WALLS, AND SCRATCHED FURNITURE. THERE ARE ALSO SOME REPORTS OF PERSONAL INJURY, PRIMARILY CAUSED BY THE GLASS FROM THE BROKEN WINDOWS. THE INCIDENT SITE WAS A LOT CONTAINING TWO STRUCTURES, THE HOUSE IDENTIFIED ABOVE AND A TWO-UNIT APARTMENT COMPLEX AT 110 1/2 WEST SEVIER AVENUE. THE LATTER LOCATION HAD BEEN DEMOLISHED THAT DAY BY A CONTRACTOR EMPLOYED BY THE HOLSTON VALLEY HOSPITAL AND MEDICAL CENTER. INVESTIGATION OF THE ACCIDENT HAS REVEALED THAT A REPRESENTATIVE FROM HOLSTON VALLEY REQUESTED THE GAS SERVICE TO110 1/2 WEST SEVIER AVENUE BE TERMINATED AND THAT WE FIELD LOCATE THE GAS SERVICE LINE TO 110 WEST SEVIER AVENUE, WHICH BORDERED THE APARTMENT HOUSE. THE REQUEST WAS COMPLETED ON FRIDAY, MARCH 23, 1990. THE HOLSTON VALLEY REPRESENTATIVE REVIEWED THE SITE AND BEING SATISFIED THAT THE LINE WAS PHYSICALLY IDENTIFIED, PROCEEDED WITH THE DEMOLITION OF THE APARTMENT HOUSE. THE CONTRACTOR, WHO LATER STATED HE WAS NOT INFORMED OF THE PRESENCE OF AN UNDERGROUND GAS LINE, DEMOLISHED AND REMOVED THE STRUCTURE AND IN THE PROCESS HE HOOKED THE GAS SERVICE LINE (3/4" STEEL) WITH HIS EQUIPMENT. THE LINE DID NOT BREAK AT THIS LOCATION, HOWEVER, THE STRESS RESULTED IN A BREAK NEAR A THREADED ELBOW SOME 38' 10" AWAY. A PORCH WHICH WAS LATER ENCLOSED HAD BEEN BUILT OVER THIS POINT CAUSING THE ENTRAPMENT OF THE ESCAPING GAS. THIS OCCURRED SOME TIMEPRIOR TO 4:00 PM. ON MARCH 26, APPROXIMATELY FIVE HOURS PRIOR TO THE EXPLOSION. I HAVE ATTACHED A DRAWING OF THE SITE FOR BETTER REPRESENTATION. IN CONSLUSION, IT APPEARS THE EXCAPING GAS FROM THE DAMAGED SERVICE VENTED UNDER AND INTO THE STRUCTURE FOR A MINIMUM OF FIVE HOURS. AT APPROXIMATELY 9:00 PM. AN ELECTRICAL CONTACT FROM EITHER THE PHONE, OR THE THERMOSTAT TO THE FLOOR FURNACE MAY HAVE BEEN THE IGNITION SOURCE CAUSING THE EXPLOSION. OUR FOLLOW-UP INVESTIGATION, WHICH WAS CONDUCTED WITH THE ASSISTANCE OF THE KINGSPORT FIRE DEPARTMENT, INCLUDED A PRESSURE TEST OF THE GAS FUEL LINE WHICH REMAINED INTACT AND THE GAS SERVICE LINE. THESE TESTS CONFIRMED THE ONLY FAILURE TO EITHER OF THE SYSTEMS WAS DUE TO THE THIRD-PARTY DAMAGE.
2025-01-31 10:21 | YES | YES | 19900107 | 1990-05-01 | 4499 | ENTEX - DIVISION OF ARKLA INC | 1690 S. DAIRY ASHFORD | HOUSTON | HARRIS | TX | 77077 | 3 | NO | 700 | 1989-12-07 | 0 | 1 | 1000 | 861.7474 | 2080.661 | Null | 1 | 20 | 21965 | 19891207 | 22 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2306 | DUPONT | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE, P.E., OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OPERATOR HAD SQUEEZED OFF AND REMOVED A LEAKING SECTION OF 2" PLASTIC MAIN IN A BELL HOLE. WHILE MAKING PERMANENT REPAIRS, THE PIPE SQUEEZING TOOL WAS ADJUSTED, AND SEBSEQUENTLY, GAS FILLED THE BELL HOLE. THE GAS WAS IGNITED BY A NEARBY PORTABLE ELECTRIC SIGN. TWO MEN WERE BURNED: ONE WAS HOSPITALIZED AND THE OTHER WAS TREATED AND RELEASED. THE HOSPITALIZED MAN WAS RELEASED FROM THE HOSPITAL SEVERAL DAYS LATER.
2025-01-31 10:21 | YES | NO | 19900111 | 1990-05-07 | 12350 | MINNEGASCO INC | 1904 SOUTH 6TH STREET | MINNEAPOLIS | HENNEPIN | MN | 55454 | 3 | NO | 1204 | 1990-04-26 | 0 | 0 | 250000 | 207820.3914 | 501775.5682 | Null | 2 | 0 | 19151 | 19900426 | 10 | 15 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | N/A | N/A | 0 | 1952 | UNDER GROUND OR UNDER WATER |  | DAVID R. HENNINGSGAARD, DIR. LOCAL GOV'T RELATIONS | 6123425316 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES |  |  | SERVICE LINE WAS HIT BY A THIRD PARTY EXCAVATOR CAUSING A COUPLING PULL-OUT.
2025-01-31 10:21 | YES | YES | 19900112 | 1990-05-04 | 4350 | ELIZABETHTOWN GAS CO | 1420 ST. GEORGES AVENUE | LINDEN/ROSELLE | UNION | NJ | 07036 | 4 | NO | 1135 | 1990-04-26 | 0 | 1 | 300000 | 249384.4697 | 602130.6818 | Null | 0 | 35 | 19129 | 19900426 | 22 | 35 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.043 |  |  | 0 | 0 | UNDER PAVEMENT |  | EDWARD RAPOLAS, DIRECTOR OF OPERATIONS | 2012895000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OPERATOR DIGGING TO REPAIR MINOR LEAK DAMAGED THE MAIN, CAUSING LARGE LEAK WHICH IGNITED BY UNKNOWN SOURCE, CAUSING FIRE WHICH DAMAGED ADJACENT DWELLINGS.
2025-01-31 10:21 | NO | NO | 19900116 | 1990-06-07 | 2188 | CENTRAL FLORIDA GAS CORP |  | SAINT CLOUD | OSCEOLA | FL | 32769 | 3 | NO | 1545 | 1990-05-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 | 23150 | 19900522 | 100 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | ENTIRE SYSTEM | OTHER | ENTIRE SYSTEM | STEEL |  | 0 | 0 | N/A |  | 0 | 0 | OTHER | SYSTEM-WIDE | EDWARD C. DUNLAP, ENGINEER | 3027346787 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FGT INTRODUCED AIR INTO ITS TRANSMISSION LINE SERVING ST. CLOUD. THE AIR GOT INTO THE ST. CLOUD DISTRIBUTION SYSTEM CAUSING SEVERAL CUSTOMERS TO LOSE SERVICE. THE GAS WAS SHUT OFF TO THE TOWN BY THE GAS DISTRIBUTION COMPANY FOR SAFETY PURPOSES. THREE HUNDRED AND THIRTY-ONE CUSTOMERS TEMPORARILY LOST GAS SERVICE UNTIL THE SYSTEM COULD BE PURGED AND MADE SAFE. ON MONDAY, MAY 21, 1990, AT 3:45 PM, THE SAINT CLOUD POWER (POWER PLANT) NOTIFIED CFGC THEY DID NOT HAVE GAS TO THEIR GENERATOR ENGINES. IMMEDIATELY SEVERAL OTHER TELEPHONE CALLS FROM OTHER DISTRIBUTION CUSTOMERS IN SAINT CLOUD REPORTING THEY DID NOT HAVE GAS. AT 3:47 PM, SAINT CLOUD MAINTENANCE PERSONNEL WERE DISPATCHED. ALL AVAILABLE PERSONNEL WERE DISPATCHED FROM WINTER HAVEN TO SAINT CLOUD AT 4:20 PM. THE SAINT CLOUD DISTRIBUTION SYSTEM WAS SHUT OFF AT 4:25 PM. BETWEEN 5:10 PM AND 7:30 PM VARIOUS COMPONENTS OF THE SYSTEM WERE EXAMINED TO DETERMINE THE CAUSE OF THE OUTAGE. AT 7:25 PM, THE INDIVIDUAL METERS OR SERVICES WERE BEGUN TO BE SHUT OFF. AT 10:00 PM A COMBUSTIBLE GAS INDICATOR TEST WAS MADE OF THE LINE AT THE POWER PLANT AND AT GROUND LEVEL THERE WAS 5% GAS IN AIR. AT 10:30 PM A CGI TEST OF THE LINE AT THE POWER PLANT ROOF SHOWED THERE WAS 58% GAS IN AIR. TESTING THE LINE NEAR FGT'S SAINT CLOUD STATION, AT 11:00 PMSHOWED 65% GAS IN AIR. AT 11:30 PM,. FGT ACKNOWLEDGED THEY HAD A PROBLEM. AT 1:00 AM, TUESDAY, MAY 22, FGT BEGAN PURGING THEIR LINE AND AT 3:00 AM THISWAS COMPLETED. AT 5:35 AM, THE POWER PLANT WAS RESTARTED AFTER THE LINE WAS PURGED. AT 5:20 AM PRESSURE ON THE DISTRIBUTION SYSTEM WAS RAISED AND PURGING BEGUN. AT 7:32 AM PURGING WAS COMPLETED AND THE SYSTEM PRESSURE HELD FOR 15 MINUTES TO CHECK FOR PRESSURE LOSS. AT 7:47 AM THE LEAK TEST WAS COMPLETEDAND THE TURN-ON PROCEDURE BEGUN. BY 12:00 PM, ALL COMMERCIAL TURN-ONS WERE COMPLETED. BY 4:30 PM, ALL RESIDENTIAL TURN-ONS WERE COMPLETED OR DOOR TAGGED
2025-01-31 10:21 | YES | NO | 19900120 | 1990-06-18 | 20010 | U G I CORP | 2030 ASTER ROAD | LOWER MACUNGIE TWP |  | PA | 18062 | 3 | NO | 300 | 1990-05-16 | 0 | 0 | 200000 | 166256.3131 | 401420.4545 | Null | 4 | 30 | 22126 | 19900516 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | SCREW COUPLING | STEEL |  | 0.75 | 0.113 | API 5L |  | 1971 | 1971 | UNDER PAVEMENT |  | JAMES R. HEINTZ, DIVISION ENGINEER | 2153715490 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | THE GAS SERVICE TO 2027 ASTER ROAD WAS AFFECTED BY A SUBSIDENCE OF UNKNOWN ORIGIN WHICH RESULTED IN THE FRACTURE OF THE 0.75 INCH PIPE AT A THREADED SOCKET COUPLING AND THE PARTIAL PULLOUT OF A 0.75-INCH STEEL SERVICE FROM A COMPRESSION TEE. THE ESCAPING GAS ULTIMATELY RESULTED IN A LOW GRADE EXPLOSION AND FIRE AT 2030 ASTER ROAD.
2025-01-31 10:21 | YES | NO | 19900121 | 1990-06-19 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | BUILDING GARDENVIEW TERRACE | EAST WINDSOR | MERCER | NJ | 08520 | 3 | NO | 631 | 1990-05-19 | 0 | 0 | 1000000 | 831281.5657 | 2007102.2727 | Null | 1 | 9 | 22740 | 19900519 | 30 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | FITTING | 2" UNION | STEEL |  | 2 | 0 | N/A | GRINNELL | 0 | 1965 | WITHIN/UNDER BUILDING |  | C.W. GREVENITZ-V.P. - GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INITIAL INVESTIGATION REVEALS AN IGNITION OF ACCUMULATED NATURAL GAS RESULTING IN AN EXPLOSION & ENSUING FIRE. THE ORIGINAL DELAYED IGNITION OCCURRED ON THE SECOND FLOOR LEVEL ABOVE THE BASEMENT UTILITY ROOMS. THE SOURCE OFACCUMULATING GAS AND THE SOURCE OF IGNITION REMAIN UNDER INVESTIGATION. THEBUILDING, WHICH CONTAINS 28 APARTMENT UNITS, SUSTAINED EXTENSIVE DAMAGE AND ALL OCCUPANTS WERE DISPLACED. BASEMENT FLOODING FROM AN UNDETERMINED SOURCE AND THE FAILURE OF FLOOR DRAINS RESULTED IN A RISING WATER LEVEL DURING A PERIOD OF SEVERAL HOURS IN THE UTILITY ROOM CONTAINING THE METERS, PRESSURE REGULATOR, AND METER SET PIPING DURING THE NIGHT OF 5/18/90 AND INTO THE EARLY MORNING HOURS OF 5/19/90. THE SIZE 60A TIN CASE METERS BECAME SUBMERGED AND THEIR BUOYANT FORCES ON THE SET PIPING RESULTED IN A FAILURE OF A 2" UNION AT THE OUTLET OF THE SERVICE REGULATOR WHICH PROVIDES 6" W.C. (1/4 PSIG) UTILIZATION PRESSURE. THE 2" UNION FAILURE OCCURRED BETWEEN THE MALE AND FEMALE UNION JOINT ALLOWING NATURAL GAS TO ESCAPE INTO THE UTILITY ROOM AREA.
2025-01-31 10:21 | YES | YES | 19900122 | 1990-07-11 | 15007 | PACIFIC GAS & ELECTRIC CO | 431 W. AMADOR | FRESNO | FRESNO | CA | 93706 | 3 | NO | 2300 | 1990-05-17 | 2 | 0 | 20350 | 16916.5799 | 40844.5312 | Null | 2 | 4 | 24179 | 19900517 | 50 | 53 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.154 | N/A | N/A | 0 | 1964 | ABOVE GROUND |  | W.R. MAZOTTI, V.P.-GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DRIVER LOST CONTROL OF VEHICLE AND HIT THE FENCE, THE GAS METER SET AND THE BUILDING.
2025-01-31 10:21 | NO | NO | 19900124 | 1990-06-29 | 11800 | LOUISIANA GAS SERVICE CO | TOWN BORDER STATION | CASTOR | BIENVILLE | LA | 71016 | 3 | NO | 945 | 1990-06-19 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 45 |  |  | 45 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | PIPELINE | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | TRANSMISSION COMPANY FAILED TO OPEN ALL VALVES ON CROSS OVER LINE WHILE TAKING ONE OF TWO PIPELINES OUT OF SERVICE FOR MAINTENANCE. A TOTAL OF 161 CUSTOMERS WERE WITHOUT GAS.
2025-01-31 10:21 | YES | NO | 19900127 | 1990-07-12 | 15259 | PENNSYLVANIA GAS & WATER CO | 2825 N. MAIN AVENUE | SCRANTON | LACKAWANNA | PA | 18508 | 3 | NO | 1538 | 1990-06-21 | 0 | 0 | 113000 | 93934.8169 | 226802.5568 | Null | 0 | 17 | 27916 | 19900621 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | UNKNOWN | 6 | 0.576 | SDR 11.5 | DUPONT | 1975 | 1976 | UNDER PAVEMENT |  | JAMES M. GREGER, MGR. - SPECIAL PROGRAMS | 7178298866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-05-07 | YES | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19900128 | 1990-07-16 | 15007 | PACIFIC GAS & ELECTRIC CO | FRANKLIN BLVD. BET. 20TH & 21ST AVE. | SACRAMENTO | SACRAMENTO | CA |  | 3 | NO | 1109 | 1990-06-25 | 0 | 1 | 82500 | 68580.7292 | 165585.9375 | YES | 1 | 36 | 28346 | 19900625 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.218 | API 5L GR B | N/A | 0 | 1925 | UNDER GROUND OR UNDER WATER |  | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SVS. | 4059736999 | [6 empty] | Null |  | OPERATOR ACTION |  | YES | 1990-06-14 | YES | 3 | MARKS OF PAINT ON PAVMENT | YES |  |  | CONTRACTOR EXCAVATING WITH BACKHOE STRUCK MAIN, CAUSING GAS TO ESCAPE. COMPANY EMPLOYEE IN ATTEMPT TO GAIN ACCESS TO A VALVE TO SHUT OFF THE GAS STARTEDUP BACKHOE AND MOVED THE BUCKET OUT OF THE EXCAVATION. AN UNKNOWN SOURCE IGNITED THE GAS. THE COMPANY EMPLOYEE RECEIVED SECOND DEGREE BURNS TO HIS HANDS, ARMS, FACE AND NECK RESULTING IN ADMISSION TO THE HOSPITAL.ON JUNE 6, 1990, A CONTRACTOR WORKING FOR PENNSYLVANIA GAS & WATER COMPANY WAS RENEWING LEAD-LINED WATER SERVCIES AT 2821 N. MAIN AVENUE, SCRANTON. AFTER UNSUCCESSFUL ATTEMPTS TO PULL EXISTING WATER SERVICE BENEATH THE ROADWAY, IT WAS DECIDED TO UTILIZE A PNEUMATIC PIERCING TOOL TO BORE A HOLE ACROSS THE ROAD AT A DEPTH OF APPROXIMATELY 4.5-FEET. THE CONTRACTOR WAS TOLD THAT A SIX (6)-INCH INTERMEDIATE PRESSURE PLASTIC GAS MAIN EXISTED IN THE STREET. THEMAIN WAS INSTALLED IN 1976 APPROXIMATELY THREE-FEET IN DEPTH AND WAS MARKED OUT A MONTH PRIOR TO START OF WORK. IT WAS ASSUMED THAT "SHOOTING" THE PIERCING TOOL AT A DEPTH OF 4.5-FEET, THERE WOULD BE MINIMAL CHANCE OF THE UNIT DEFLECTING UPWARD 18-INCHES WITHIN A FEW FEET INTO THE STREET, AND THEREFORE LITTLE RISK IN STRIKING THE GAS MAIN AT ITS THREE (3)-FOOT DEPTH. AS WORK WAS CONTINUING, THE CONTRACTOR INFORMED P.G.&W.'S INSPECTOR THAT THE TOOL WAS STRUCK BENEATH THE ROAD AND THAT THEY WERE GOING TO REVERSE THE PIECE OF EQUIPMENT AND BACK IT OUT OF THE OBSTRUCTION. UPON PERFORMING THIS ACTION, THERE WAS AN IMMEDIATE ODOR OF NATURAL GAS IN THE ATMOSPHERE. IT WAS CONCLUDED THAT THE GAS MAIN WAS RUPTURED AND EMERGENCY PROCEDURES WERE PUT INTO EFFECT. PREPARATIONS WERE MADE TO SHUT DOWN THE GAS MAIN AND START EVACUATION PROCEDURESIN THE AFFECTED AREA. IT WAS DURING THIS TIME AN EXPLOSION OCCURRED AT 2825N. MAIN AVENUE, SCRANTON. APPROXIMATELY ONE MINUTE LATER, THE HOUSE BURST INTO FLAMES. FIRE, POLICE, AND EMERGENCY AGENCIES WERE NOTIFIED. AFTER EXCAVATION AT THE LEAK SITE WAS COMPLETED, IT WAS DETERMINED THAT THE CONTRACTOR'S PNEUMATIC PIERCING TOOL HAD STRUCK THE SIX (6)-INCH PLASTIC INTERMEDIATE PRESSURE (55 PSI) MAIN AND PUNCTURED A HOLE APPROXIMATELY 3/4-INCH DIAMETER INTO THE EASTERLY SIDE OF THE MAIN. APPROXIMATELY FIVE (5)-FEET OF PIPE WAS REPLAC
2025-01-31 10:21 | YES | YES | 19900129 | 1990-07-16 | 11032 | LACLEDE GAS CO | LOT 121 HORNBEAN DRIVE | CHESTERFIELD | ST LOUIS | MO |  | 3 | NO | 1515 | 1990-06-26 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 50 | 28509 | 19900626 | 13.5 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM 02513 | PHILLIPS PET | 0 | 1989 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER, JR./ ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DURING THE REPAIR OF THE DAMAGE THAT RESULTED FROM ACTION BY OUTSIDE PARTY/THIRD PARTY THERE WAS AN IGNITION FROM AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 19900130 | 1990-07-24 | 1209 | BAY STATE GAS CO | PARK PLACE | ATTLEBORO |  | MA |  | 0 | NO | 730 | 1990-07-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 | 30768 | 19900713 | 55 | 99 | BY TEST | 99 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | WELD | LONGITUDINAL | STEEL |  | 2 | 0.154 | N/A | N/A | 0 | 1927 | UNDER PAVEMENT |  | F.W. ST.CYR MANAGER/DISTRIBUTION | 5085800100 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SEWER | YES | 1990-06-27 | YES | 3 | MARKING PAINT | NO |  |  | THREE CONSTRUCTION WORKERS, EMPLOYED BY RAVOLI CONSTRUCTION (NORTH READING MASS) WERE INVOLVED IN INSTALLATION OF NEW SEWER FACILITIES. ONE PERSON APPARENTLY WAS IN A NEW SEWER MANHOLE, HE REPORTEDLY IGNITED A "BIC" TYPE CIGARETTE LIGHTER AND CAUSED IGNITION OF WHAT IS BELIEVED TO BE A-BUILD-UP OF NATURALGAS IN THE MANHOLE. THE PERSON IN THE MANHOLE AND TWO PERSONS OUTSIDE THE MANHOLE (IN CLOSE PROXIMITY) WERE BURNT.
2025-01-31 10:21 | YES | YES | 19900131 | 1990-07-30 | 10037 | K P L GAS SERVICE | 128 W. 5TH | KANSAS CITY | JACKSON | MO | 64120 | 4 | NO | 1737 | 1990-07-02 | 1 | 0 | 0 | 0 | 0 | Null | 1 | 57 | 29237 | 19900702 | 1 | 5 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | UNKNOWN | OTHER | COPPER | 1.5 | 0 |  |  | 0 | 1967 | WITHIN/UNDER BUILDING |  | HANS E. MERTENS, VICE-PRESIDENT ENGINEERING | 8163465575 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | IN CONJUNCTION WITH A MAIN INSTALLATION PROJECT FOR SYSTEM REINFORCEMENT, THE EXISTING SERVICE LINE TO 128 WEST 5TH WAS REPLACED WITH A NEW SERVICE LINE. DURING THE PROCESS OF TRANSFERRING SERVICE FROM THE OLD SERVICE LINE TOTHE NEW SERVCIE LINE, THE OLD SERVICE LINE OUTLET IN THE CUSTOMER'S BASEMENT, WAS NOT CAPPED. WHEN GAS WAS REINTRODUCED INTO THE MAIN SERVING THE OLD SERVICE LINE, GAS APPARENTLY FLOWED THROUGH THE OPEN END OF THE OLD SERVICE LINE. THE GAS SUBSEQUENTLY IGNITED AND AN EXPLOSION OCCURRED, WHICH RESULTED IN THE DESTRUCTION OF THE BUILDING AND ONE FATALITY.
2025-01-31 10:21 | YES | YES | 19900132 | 1990-07-25 | 14210 | OKLAHOMA NATURAL GAS CO | 3824 SIMS | EDMOND | OKLAHOMA | OK | 73034 | 2 | NO | 1400 | 1990-06-28 | 0 | 1 | 1500 | 1246.9223 | 3010.6534 | Null | 1 | 10 | 28951 | 19900628 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | DRISCO | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | JAMES M. WOOD, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | PAINT ON GROUND | YES |  |  | JEFF JONES WAS DIGGING POSTHOLES FOR A FENCE AT 3824 SIMS AND HIT A 2-INCH PLASTIC MAIN. THIS RESULTED IN A GAS LEAK WHICH WAS IGNITED BY A GASOLINE ENGINE FIVE FEET FROM POINT OF RUPTURE.
2025-01-31 10:21 | NO | NO | 19900136 | 1990-07-25 | 15007 | PACIFIC GAS & ELECTRIC CO | 39 BUCHANAN COURT | EAST PALO ALTO | SAN MATEO | CA | 94303 | 3 | NO | 758 | 1990-07-13 | 0 | 0 | 55150 | 45845.1783 | 110691.6903 | Null | 0 | 32 | 30800 | 19900713 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | 3RD PARTY STRUCTURE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | W.R. MAZOTTI, V.PV - GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | FIRE FROM UNKNOWN SOURCE DAMAGED HOME.
2025-01-31 10:21 | NO | NO | 19900137 | 1990-08-03 | 12684 | MONTANA - DAKOTA UTILITIES CO | 5516 LAUREL ROAD | BILLINGS | YELLOWSTONE | MT | 59101 | 3 | NO | 1920 | 1990-07-02 | 0 | 0 | 47000 | 39070.2336 | 94333.8068 | Null | 0 | 30 | 29246 | 19900702 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER | ANODELESS | STEEL |  | 0.5 | 0.113 | N/A | UNKNOWN | 1982 | 1982 | ABOVE GROUND |  | DAN FARMER, GAS ENGINEER | 4062551374 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GRD, METER VISIBLE | YES |  |  | THE OPERATOR OF A MOTOR HOME STRUCK A METER SET CAUSING RISER TO BREAK AT STOP, RESULTING IN A FIRE WHICH DESTROYED THE MOTOR HOME.
2025-01-31 10:21 | NO | NO | 19900138 | 1990-08-03 | 11032 | LACLEDE GAS CO | 4285 RINGER ROAD | MEHLVILLE | ST LOUIS | MO |  | 3 | NO | 1851 | 1990-05-15 | 0 | 0 | 60000 | 49876.8939 | 120426.1364 | Null | 0 | 0 | 23334 | 19900523 | 13.5 | 60 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0.04 | ASTM B-88 | N/A | 0 | 1963 | WITHIN/UNDER BUILDING |  | PAUL B. HUNKER, JR./ ASSOCIATE GENERAL COUNSEL | 3143420528 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | CHEMICAL | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | NO READINGS FOR NATURAL GAS BECAME EVIDENT UNTIL 5/19/90. THE ACTUAL CORROSION LEAK WAS ISOLATED ON 5/20/90 AND THE APPROPRIATE REPAIRS WERE COMPLETED AT THAT TIME.
2025-01-31 10:21 | YES | YES | 19900139 | 1990-08-02 | 22182 | WASHINGTON GAS LIGHT CO | 8737 CARROLL AVENUE | TAKOMA PARK | PRINCE GEORGES | MD | 20903 | 3 | NO | 1322 | 1990-07-12 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 42 | 30664 | 19900712 | 27 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | ASTM D2513 | DUPONT | 1981 | 1981 | UNDER GROUND OR UNDER WATER |  | C.E. GOODSON III - SENIOR SAFETY SPECIALIST | 7037504584 | [6 empty] | Null |  | OPERATOR ACTION |  | YES | 1990-06-29 | YES | 3 | MARKINGS NOT LISTED | NO |  |  | TWO EMPLOYEES WORKING FOR THE FREDERICK FENCE COMPANY INSTALLING FENCE POSTSWITH A GASOLINE AUGER, STRUCK AND DAMAGED A 1 1/4" PLASTIC HIGH PRESSURE NATURAL GAS LINE. THE ESCAPING NATURAL GAS IGNITED, INJURING BOTH WORKERS, WHO SUSTAINED FIRST, SECOND AND THIRD DEGREE BURNS. ONE WORKER WAS TREATED AND RELEASED FROM THE HOSPITAL. THE SECOND WORKER WAS ADMITTED WITH MORE SERIOUS BURNS. WASHINGTON GAS RESPONDED AND SQUEEZED THE SERVICE LINE OFF IN A SEPARATE EXCAVATION, TEMPORARILY LEAVING 51 CUSTOMERS WITHOUT NATURAL GAS SERVICE.REPAIRS WERE COMPLETED AND CUSTOMERS SERVICE WAS RESTORED ON 7/12/90. THE PROBABLE CAUSE OF IGNITION WAS THE GASOLINE AUGER.
2025-01-31 10:21 | NO | NO | 19900141 | 1990-08-09 | 15007 | PACIFIC GAS & ELECTRIC CO | 170 MAGNOLIA STREET | AUBURN | PLACER | CA | 95603 | 3 | NO | 2136 | 1990-07-10 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 29 | 30386 | 19900711 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0 | UNKNOWN | UNKNOWN | 0 | 0 | ABOVE GROUND |  | W.R. MAZOTTI, V.P. - GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | INITIALLY REPORTED AS A GAS EXPLOSION; INVESTIGATION REVEALED HOUSE COLLAPSED DUE TO DRYROT DAMAGING SERVICE LINE.
2025-01-31 10:21 | NO | NO | 19900144 | 1990-08-14 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 1517 WALTON AVENUE | THE BRONX |  | NY |  | 4 | NO | 1000 | 1990-06-18 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 0 | 0 | 27326 | 19900618 | 0.22 | 0.43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | STEEL |  | 3 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RICHARD GAULIN-PLANNING | 2124602838 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONSTRUCTION WORK ON FRONT STOOP OF RESIDENCE RUPTURED UNUSED THREE-INCH SERVICE. IGNITION OF GAS OCCURRED, POSSIBLY CAUSED BY WELDING EQUIPMENT. REPORT OF TWO PERSONS HOSPITALIZED LATER PROVED TO BE ERRONEOUS. INVESTIGATION PROVED THAT INCIDENT DID NOT MEET ANY REPORTING CRITERIA.
2025-01-31 10:21 | YES | YES | 19900145 | 1990-08-21 | 11680 | LONE STAR GAS CO | HYMEADOW & S.H. 183 | AUSTIN | TRAVIS | TX |  | 0 | NO | 1630 | 1990-07-27 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 20 |  | 19900727 | 25 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 3 | 0.307 | ASTMD-2518 | PLEXCO | 1990 | 1990 | UNDER GROUND OR UNDER WATER |  | LOIS ROSS-CLERK | 2146701566 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | A PROBLEM WITH THE TAPPING EQUIPMENT WHILE ATTEMPING TO CONNECT A 3-" POLYETHYLENE LINE TO AN 6" PLOYETHYLENE GAS MAIN.
2025-01-31 10:21 | YES | NO | 19900146 | 1990-08-21 | 14210 | OKLAHOMA NATURAL GAS CO | 712 SOUTHWEST 104 STREET | OKLAHOMA CITY | CLEVELAND | OK |  | 3 | NO | 950 | 1990-08-02 | 0 | 0 | 169200 | 140652.8409 | 339601.7045 | Null | 3 | 39 | 33761 | 19900802 | 457 | 660 | BY TEST | 1100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | STEEL |  | 2 | 0.154 | SMLS GRADE B | N/A | 1978 | 1979 | UNDER GROUND OR UNDER WATER |  | JAMES M. WOOD, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-07-20 | YES | 2 |  | YES |  |  | ATLAS PAVING (CONTRACTOR FOR CITY OF OKLAHOMA CITY) WAS EXCAVATING WITH A PULVERIZER IN PREPARATION OF A LIME STABILIZED SUBBASE FOR AN OKLAHOMA CITY STREET IMPROVEMENT PROJECT ON SOUTHWEST 104TH STREET. THE PULVERIZER CONTACTED A 2 3/8-INCH OD HIGH-PRESSURE SERVCIE LINE CARRYING 457 PSIG AT 712 SOUTHWEST104 STREET. THE PIPE WAS MANGLED AND HAD NUMEROUS HOLES RIPPED OUT OF IT. THE RESULTING ESCAPING GAS WAS IGNITED, CAUSING A FIRE. MINOR INJURIES WERE RECEIVED BY TWO OF THE CONTRACTOR'S EMPLOYEES. THE PULVERIZER, VALUED AT APPROXIMATELY $168,000, WAS A TOTAL LOSS. THE LINE HAD BEEN ACCURATELY LOCATED.
2025-01-31 10:21 | YES | NO | 19900151 | 1990-08-24 | 15007 | PACIFIC GAS & ELECTRIC CO | 2981 26TH ST | SAN FRANCISCO | SAN FRANCISCO | CA |  | 3 | NO | 401 | 1990-07-20 | 0 | 0 | 100150 | 83252.8488 | 201011.2926 | Null | 3 | 52 | 31811 | 19900720 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1.15 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | W R MAZOTTI, VP - ELEC. TECH. SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE SPREAD TO GAS METER LOCATION.
2025-01-31 10:21 | YES | YES | 19900152 | 1990-08-24 | 15518 | PIEDMONT NATURAL GAS CO INC | 2219 SENOIR DR | CHARLOTTE | MECKLENBURG | NC | 28216 | 3 | NO | 1433 | 1990-08-02 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 32 | 33804 | 19900802 | 60 | 75 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.178 | PE 3408 | PHILLIPS | 1989 | 1990 | UNDER GROUND OR UNDER WATER |  | MICHAEL N PARROTT | 7043643120 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-07-30 | NO | 0 |  | NO |  |  | ON THURSDAY, 080290, 3 PERSONS WERE BURNED AS A RESULT OF A DIG-IN TO A PIEDMONT NATURAL GAS SERVICE LINE. THE INCIDENT OCCURRED AT WEST CHARLOTTE SENOIRHIGH SCHOOL, 2219 SENIOR DR, CHARLOTTE, NC. WILLIAMS ELECTRIC CO WAS TRENCHING IN ORDER TO INSTALL UNDERGROUND CONDUIT WHEN THEY STRUCK A 1.25 PLASTIC SERVICE LINE RELEASING NATURAL GAS. IND-COM ELECTRIC CO WORKERS WERE WORKING IN THE AREA WITH AN ELECTRIC DRILL. THERE WAS AN APPARENT SHORT IN THE CORD. WHEN A WORKER WENT TO THE CORD AND STARTED THE DRILL BACK, A SPARK WAS CREATEDAND THE ESCAPING GAS IGNITED. THERE WERE THREE PEOPLE BURNED. DWIGHT HODGESHAD SECOND DEGREE BURNS ON HIS FACE AND BODY. SCOTT BARKER WAS BURNED ON HIS RIGHT ARM. BOTH WERE HOSPITILIZED AND BOTH WORKED FOR IND-COM ELECTRI. JACKIE HELM OF WILLIAMS ELECTRIC RECEIVED MINOR BURNS. WILLIAMS ELECTRIC, A SUB-CONTRACTOR FOR DUKE POWER, HAD CALLED FOR A LOCATE BUT BYERS ENGINEERING, A CONTRACTING SERVICE EMPLOYED BY PIEDMONT NATURAL GAS, HAD BEEN TO THE SITE AND LOCATED OTHER GAS PIPELINES BUT FAILED TO LOCATE THE GAS PIPLINE THAT WAS DAMAGED.
2025-01-31 10:21 | YES | YES | 19900157 | 1990-09-13 | 22791 | WISCONSIN PUBLIC SERVICE CORP | ONTARIO & FINGER ROAD | GREEN BAY | BROWN | WI | 54311 | 2 | NO | 230 | 1990-08-25 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 50 | 36890 | 19900825 | 135 | 150 | BY TEST | 225 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | PRESS. REDUCING FACILITY | WELD | GIRTH | OTHER | UNKNOWN | 2 | 0.154 | API 5L | LACLEDE | 1987 | 1988 | ABOVE GROUND |  | ROBERT L. BUBOLZ | 4144985129 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AN ABOVE GROUND REGULATORY FACILITY WAS STRUCK BY A PICK-UP TRUCK WHICH CROSSED A MEDIAN, TWO OPPOSING TRAFFIC LANES, WENT THROUGH A DITCH, AND 200 FEET THROUGH A FIELD. A 2" RISER PIPE WAS SEVERED UPON IMPACT. THE ESCAPING GAS IGNITED AND THE TRUCK WAS ENGULFED IN FLAMES. THERE WAS ONE FATILITY.
2025-01-31 10:21 | YES | NO | 19900159 | 1990-09-13 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 111 CHRISTIE STREET | LEONIA | BERGEN | NJ | 07605 | 4 | NO | 1327 | 1990-08-22 | 0 | 0 | 80000 | 66502.5253 | 160568.1818 | Null | 1 | 38 | 36579 | 19900823 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S EQUIP. RANGE | OTHER | CUSTOMER EQUIP RANGE | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | KITCHEN AREA AT RANGE | C.W. GREVENITZ | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PRELIMINARY INVESTIGATIONS INDICATES THAT THE CUSTOMER'S RANGE APPLIANCE MAYHAVE BEEN FAULTY CAUSING GAS TO ESCAPE UNDETECTED WHICH RESULTED IN THIS INCIDENT. CUSTOMER WAS ON VACATION AND UPON RETURN DETECTED A STRONG ODOR. WHILE IN THE PROCESS OF OPENING DOORS TO VENT, THE RANGE TOP BLEW AND THE EXPLOSION OCCURRED.
2025-01-31 10:21 | YES | NO | 19900160 | 1990-09-12 | 15007 | PACIFIC GAS & ELECTRIC CO | 3813 MARTIN DRIVE | SAN MATEO | SAN MATEO | CA |  | 3 | NO | 1550 | 1990-08-14 | 0 | 0 | 100000 | 83128.1566 | 200710.2273 | Null | 0 | 5 | 35433 | 19900814 | 30 | 34 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0.75 | 0 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | W.R. MAZOTTI, V.P.-GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | CUSTOMER'S GAS APPLIANCE IGNITED NEARBY GASOLINE FUMES RESULTING IN STRUCTURE FIRE WHICH SPREAD TO AND IGNITED THE GAS REGULATORY.
2025-01-31 10:21 | NO | NO | 19900161 | 1990-09-12 | 15007 | PACIFIC GAS & ELECTRIC CO | 980 IGNACIO BOULEVARD | NOVATO | MARIN | CA |  | 3 | NO | 1626 | 1990-08-13 | 0 | 0 | 1800 | 1496.3068 | 3612.7841 | YES | 0 | 2 | 35304 | 19900813 | 7 | 7 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | N/A | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | W.R. MAZOTTI-V.P., GAS & ELECTRIC TECH SERVICES | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE STRUCK CUSTOMER HOUSELINE. ONE RESIDENT WASOVERCOME BY THE SMELL OFTHE NATURAL GAS, WAS TAKEN TO THE HOSPITAL.
2025-01-31 10:21 | YES | YES | 19900162 | 1990-09-05 | 15007 | PACIFIC GAS & ELECTRIC CO | 1041 MCFARLANE AVENUE | SEBASTOPOL | SONOMA | CA | 95472 | 3 | NO | 825 | 1990-08-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 | 35267 | 19900813 | 45 | 50 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.23 | N/A | DRISCO | 1990 | 1990 | OTHER | BELL HOLE | W.R. MAZOTTI, V.P.-GAS & ELECTRIC TECH SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | EMPLOYEE WAS CUTTING A SQUEEZED OFF 2-INCH PLASTIC DEAD END MAIN WITH A PLASTIC PIPE CUTTER WHEN PIPE END BLEW OFF AND ESCAPING GAS WAS IGNITED BY ADJACENT CREW TRUCK'S GENERATOR. EMPLOYEE RECEIVED 2ND DEGREE BURNS ABOUT HANDS AND FACE.
2025-01-31 10:21 | NO | NO | 19900163 | 1990-09-12 | 15007 | PACIFIC GAS & ELECTRIC CO | 2918 "D" STREET | HAYWARD |  | CA |  | 3 | NO | 1400 | 1990-08-15 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 0 | 5 | 35886 | 19900817 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 | 5B | AMERICAN | 1935 | 1968 | ABOVE GROUND |  | W.R. MAZOTTI, V.P.-GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE OF UNKNOWN SOURCE CAUSED GAS METER TO MELT AND IGNITE.
2025-01-31 10:21 | YES | YES | 19900164 | 1990-09-12 | 15931 | PUBLIC SERVICE CO OF COLORADO | 1400 LAMAR ST. | LAKEWOOD | JEFFERSON | CO |  | 3 | NO | 1300 | 1990-08-21 | 0 | 1 | 0 | 0 | 0 | Null | 6 | 5 | 36335 |  | 5 | 15 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 2 | 0.154 | SCHEDULE 40 | N/A | 0 | 1961 | UNDER PAVEMENT |  | JAMES SHANAKER | 3035717687 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-08-16 | YES | 3 | PAINT | YES |  |  | A SEWER CONTRACTOR USING A LINK BACKHOE TO EXCAVATE A TRENCH TO INSTALL A NEW SEWER LINE HIT AND PULLED A 2" MW MAIN OUT OF A COMPRESSION COUPLING. DURING THE PROCESS OF EMERGENCY CREWS ATTEMPTING TO EXPOSE THE SECTION OF LINE THAT HAD BEEN PULLED, AN UNKNOWN IGNITION SOURCE CAUSED THE GAS TO IGNITE. FOUR (4) GAS COMPANY EMPLOYEES RECEIVED 1ST DEGREE BURNS. ONE OF THE FOUR EMPLOYEES REQUIRED INPATIENT HOSPITALIZATION AFTER THE INCIDENT. NO OTHER PERSONAL OR PROPERTY DAMAGES OCCURRED. THE LINES FEEDIN THE FIRE WERE EXPOSED AND CONTROL FITTINGS WERE INSTALLED TO STOP THE GAS.
2025-01-31 10:21 | YES | YES | 19900166 | 1990-09-19 | 22189 | WASHINGTON NATURAL GAS CO | 10907 SE 302 STREET | AUBURN | KING | WA | 98002 | 3 | NO | 1445 | 1990-08-30 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 15 | 37672 | 19900830 | 45 | 60 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | TAPPING MACHINE | OTHER | RUBBER STOPPER | 0 | 0 |  |  | 0 | 0 | OTHER | OPEN EXCAVATION | DOUGLAS DAMM, SAFETY MANAGER | 2062242396 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | FAILURE TO FOLLOW PROPER TAPPING PROCEDURE | DURING WITHDRAWAL OF A RUBBER STOPPER AFTER A HOT TAP OPERATION, THE RUBBER WAS TORN FROM THE TAPPING MACHINE SHAFT, PREVENTING CLOSURE OF THE GATE VALVE. EMPLOYEE OF OPERATOR'S SUB-CONTRACTOR REMOVED THE BARREL ALLOWING GAS TO ESCAPE AND IGNITE FROM AN UNKNOWN IGNITION SOURCE. EMPLOYEE SUFFERED SECOND DEGREE BURNS OVER FACE AND HANDS. POST-ACCIDENT DRUG TEST WAS CONDUCTED.
2025-01-31 10:21 | YES | YES | 19900167 | 1990-09-17 | 11680 | LONE STAR GAS CO | 1900 JOSEY LANE | CARROLLTON | DALLAS | TX |  | 0 | NO | 1 | 1990-08-18 | 0 | 3 | 5000 | 4156.4078 | 10035.5114 | Null | 0 | 0 |  | 19900818 | 15 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | WELD | N/A | STEEL |  | 4 | 0.25 | API-5L |  | 1960 | 1960 | UNDER GROUND OR UNDER WATER |  | LOIS ROSS - CLERK | 2146701566 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | CAR | NO |  | NO | 0 |  | NO |  |  | CAR HIT METER INSTALLATION.
2025-01-31 10:21 | NO | NO | 19900170 | 1990-09-18 | 1088 | BALTIMORE GAS & ELECTRIC CO | 507 MOUNTAIN ROAD | BEL AIR | HARFORD | MD | 21047 | 2 | NO | 133 | 1990-09-09 | 0 | 0 | 60000 | 49876.8939 | 120426.1364 | Null | 0 | 57 |  | 19900909 | 99 | 99 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | OTHER | N/A | 0.75 | 0.154 | API 5L | N/A | 1980 | 1981 | ABOVE GROUND |  | DANOLD L. SHRADER, SUPERVISOR CUSTOMER SERVICE | 3015612728 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | FIRE AT LOG CABIN CREATED PARTIAL COLLAPSE OF FRONT WALL. TIMBER FELL ON OUTSIDE METER/REGULATOR INSTALLATION CAUSING A RELEASE OF GAS AND ADDITIONAL FIRE. BEL AIR FIRE DEPARTMENT TURNED OFF VALVE AT OUTSIDE SERVICE RISER. AFTERTHE FIRE DEPARTMENT SHUT OFF THE OUTSIDE SERVICE RISER VALVE THIS BROUGHT THE INCIDENT UNDER CONTROL AND DID NOT PRESENT A SIGNIFICANT THREAT TO PUBLIC SAFETY. IT WAS NECESSARY TO UNCOVER THE SERVICE LINE 75' FROM THE LOG CABIN AND ABANDON THE SERVICE BECAUSE OF GAS LEAKING UNDER VALVE AND VALVE BODY. THE LEAK AT THE SERVICE AND VALVE WAS CAUSED BY TIMBER THAT HAD COLLAPSED ON METER INSTALLATION.
2025-01-31 10:21 | YES | NO | 19900174 | 1990-10-03 | 15007 | PACIFIC GAS & ELECTRIC CO | 512 SOUTH SANTA CRUZ AVENUE | MODESTO | STANISLAUS | CA | 95354 | 3 | NO | 2012 | 1990-08-22 | 0 | 0 | 165000 | 137161.4583 | 331171.875 | YES | 3 | 18 | 36806 | 19900823 | 45 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | UNKNOWN | OTHER | COPPER | 0.5 | 0 |  |  | 0 | 1949 | UNDER PAVEMENT |  | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FAILURE OF SERVICE PIPE ALLOWED GAS TO MIGRATE INTO BUILDING. WALL HEATER IN APARTMENT 6 IS ATTRIBUTED AS THE LIKELY SOURCE OF IGNITION. STRUCTURE FIREENSUED, CAUSING STRUCTURAL DAMAGE. BUILDINGS WERE EVACUATED AND TRAFFIC REROUTED.
2025-01-31 10:21 | NO | NO | 19900175 | 1990-10-03 | 12876 | MOUNTAIN FUEL SUPPLY CO | 2282 WEST 4400 SOUTH | ROY | WEBER | UT | 84067 | 3 | NO | 1220 | 1990-09-17 | 0 | 0 | 60000 | 49876.8939 | 120426.1364 | Null | 0 | 50 | 39662 | 19900917 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | N/A | N/A | 0 | 1971 | ABOVE GROUND |  | H. MARTELL BROWER (CENTER ENGINEER) | 8016263252 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | SERVICE RISER & METER SET | YES |  |  | ON SATURDAY, SEPTEMBER 15TH, THE HOMEOWNER OF 2282 WEST 4400 SOUTH IN ROY, UTAH CONSTRUCTED A MAKESHIFT AWNING OVER HIS CAMPER USING PINE POLES, CANVAS AND ROPE. THE POLES WERE POSITIONED SUCH THAT THEY WERE LEANING UP AGAINST THE HOUSE AND WERE HELD INPLACE BY ROPES SECURED TO VARIOUS LOCATIONS. THE HOMEOWNER'S SON GOT INTO THE CAMPER AND MOVED IT FORWARD. AS HE MOVED THE CAMPER FORWARD, THE CAMPER SHELL CAUGHT ONE OF THE ROPES WHICH PULLED THE AWNING DWOWN. IN PULLING DOWN THE AWNING,ONE OF THE POLES NEXT TO THE HOUSE CAUGHT THE METER SET AND BROKE THE RISER IMMEDIATELY BELOW THE FIRECOCK. THERE WAS AWALL VENT NEARBY WITH A WATER HEATER NEAR THE VENT. AS THE GAS WAS ESCAPINGTO THE ATMOSPHERE, IT IS VERY LIKELY THAT SOME GAS FILTERED INTO THE VENT ANDWAS IGNITED BY THE PILOT LIGHT OF THE WATER HEATER.
2025-01-31 10:21 | YES | YES | 19900176 | 1990-10-03 | 20010 | U G I CORP | 421-423 NORTH 5TH STREET | ALLENTOWN | LEHIGH | PA | 18102 | 3 | NO | 518 | 1990-08-29 | 1 | 1 | 300000 | 249384.4697 | 602130.6818 | Null | 4 | 25 | 37392 | 19900829 | 0.25 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1903 | UNDER PAVEMENT |  | J.R. HEINTZ - DIVISION ENGINEER-DISTRIBUTION OPERATION | 2153715490 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | AT 5:10 AM. ON AUGUST 29, 1990, A CALL WAS RECEIVED REPORTING AN EXPLOSION AND FIRE AT 423 AND 425 N. 5TH ST., ALLENTOWN. UPON INVESTIGATION, AN AREA OFSUBSIDENCE APROXIMATELY 10' BY 36' WAS DISCOVERED AROUND THE MAIN BREAK. THE AREA OF SUBSIDENCE WAS OVAL IN SHAPE AND EXTENDED FROM THE CURB OPPOSITE 425 N. 5TH STREET TO UNDER THE SIDEWALK IN FRONT OF 423 N. 5TH STREET. THE LONG AXIS OF THE SUBSIDENCE AREA WAS PERENDICULAR TO THE STREET. WITHIN THE AREA OF SUBSIDENCE THERE WAS A RECENT UNREPAIRED WATER MAIN BREAK ADJACENT TO THE GAS MAIN BREAK. GAS MIGRATED FROM THE BREAK IN THE CAST IRON GAS MAIN TO HOUSE 423 VIA A CAVERN CAUSED BY THIS SUBSIDENCE AND SUBSEQUENTLY FILLED THE HOUSE. THE GAS WAS THEN IGNITED BY AN UNKNOWN SOURCE WHICH RESULTED IN AN EXPLOSION WHICH COMPLETELY LEVELED 421 AND 423 AND HEAVILY DAMAGED 419 AND 425.MESSR. CHARLES H. BATTEN OF NTSB SENT THE DAMAGED SEGMENT OF THE CAST IRON MAIN TO THEIR LABORATORY. RESULTS OF THEIR ANALYSIS ARE NOT AVAILABLE AS YET.
2025-01-31 10:21 | YES | YES | 19900177 | 1990-10-03 | 14210 | OKLAHOMA NATURAL GAS CO | 526 EAST LATIMER COURT | TULSA | TULSA | OK | 74106 | 3 | NO | 1459 | 1990-08-30 | 0 | 2 | 500 | 415.6408 | 1003.5511 | Null | 0 | 46 | 37693 | 19900831 | 40 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | N/A | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2306 | PLEXCO | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | JAMES M. WOOD, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | EMPLOYEES OF A & L UNDERGROUND, A PIPELINE CONTRACTOR, HAVE BEEN INVOLVED INA DGETR 7UTION REBUILD PROJECT FOR OKLAHOMA NATURAL GAS COMPANY (ONG). ON THURSDAY, AUGUST 30, 1990, THE CONTRACTOR HAD A CREW WORKING AT 526 EAST LATIMER COURT. THEY WERE CLAMPING OFF A 2-INCH PLASTIC LINE IN ORDER TO CUT THE CAP OFF TO EXTEND THE LINE ACROSS THE STREET. GAS WAS LEAKING THROUGH THE SQUEEZE-OFF AFTER THE CAP WAS REMOVED; AS ONE EMPLOYEE ATTEMPTED TO TIGHTEN THECLAMP, THE GAS IGNITED. AT 2:59 PM., ONG RECEIVED NOTIFICATION THAT THE TULSA FIRE DEPARTMENT HAD REPORTED A FIRE INVOLVING GAS AT THIS ADDRESS. THE ORDER WAS DISPATCHED AT 3:03 PM. AND WAS ACKNOWLEDGED BY A COMPANY REPRESENTATIVE IN UNIT #149. AN ONG CONSTRUCTION INSPECTOR WAS THE FIRST COMPANY PERSONTO ARRIVE ON THE SCENE OF THE INCIDENT. THE COMPANY CREW WITH ASSISTANCE FROM THE CONTRACTOR DUG UP THE 2-INCH PLASTIC MAIN APPROXIMATELY 100 FEET NORTHOF THE SITE OF THE FIRE AND SQUEEZED OFF, STOPPED THE GAS FLOW, AND EXTINGUISHED THE FIRE. THE PIPE WAS THEN CUT AND CAPPED AT 3:45 PM. TWO EMPLOYEES OF A & L UNDERGROUND WERE TAKEN BY LIFE FLIGHT TO HILLCREST HOSPITAL. ONE A & L EMPLOYEE, BILL PARNELL, HAD SECOND AND THIRD DEGREE BURNS OVER 53 PERCENT OF HIS BODY; HE IS EXPECTED TO BE HOSPITALIZED FOR 6 TO 8 WEEKS. THE OTHER EMPLYEE, JEFF OOTS, HAD FIRST DEGREE BURNES ONHIS BACK, SHOULDERS, AND ARMS. HE SHOULD BE RELEASED IN ABOUT A WEEK. NOTE: CONDITION OF INJURED PERSONS ASOF SEPTEMBER 24, 1990: BILL PARNELL IS STILL HOSPITALIZED. HE HAS HAD FIVESKIN GRAFTS TO DATE WITH ONE MORE IN THE NEAR FUTURE. IT IS EXPECTED THAT HE WILL BE IN THE HOSPITAL AN ADDITIONAL FOUR WEEKS. HE IS PROGRESSING AS EXPECTED. JEFF OOTS WAS RELEASED FROM THE HOSPTIAL ON SEPTEMBER 2, 1990 (FOUR DAYSAFTER THE INCIDENT). SAFETY DIRECTOR KURT GOWDY AND FOREMAN RICK BLANKE WITH A & L UNDERGROUND MET WITH R.E. RICHEY, ONG SUPERINTENDENT, ON AUGUST 31, 1990, TO DISCUSS THE INCIDENT AND POSSIBLE SOURCES OF IGNITION. INVESTIGATION OFTHE INCIDENT INDICATES PROBABLE SOURCE OF IGNITION WAS STATIC ELEC. CAUSED AS THE RESULT OF GAS FLOWING THROUGH THE SQUEEZE-OFF TOOL WHEN CAP WAS CUT OFF
2025-01-31 10:21 | NO | NO | 19900181 | 1990-10-05 | 18484 | SOUTHERN CALIFORNIA GAS CO | 925 SOUTH 8TH STREET | COLTON | SAN BERNARDINO | CA | 92324 | 3 | NO | 400 | 1990-08-13 | 0 | 0 | 15300 | 12718.608 | 30708.6648 | Null | 1 | 20 |  |  | 110 | 125 | BY TEST | 190 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | UNKNOWN | 0.25 | 0 |  | FISHER | 0 | 1986 | ABOVE GROUND |  | MARSHALL B. ANDERSON, STAFF SUPERVISOR-LEAKAGE CONTROL | 2133072643 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | SHORTED ELECTRIC FUSES AT AN INDUSTRIAL COMPLEX CAUSED A GAS HOUSELINE SOLENOID VALVE TO CLOSE. GAS RELIEVING THROUGH A RELIEF VALVE IN THE MSA WAS IGNITED BY FLYING SPARKS. TWO INDUSTRIAL METER SETS WERE DESTROYED.
2025-01-31 10:21 | NO | NO | 19900182 | 1990-10-05 | 18484 | SOUTHERN CALIFORNIA GAS CO | 10TH STREET WEST AND BEECHDALE DRIVE | PALMDALE | LOS ANGELES | CA | 93550 | 3 | NO | 735 | 1990-08-29 | 0 | 0 | 39400 | 32752.4937 | 79079.8295 | Null | 6 | 9 |  | 19900829 | 220 | 230 | BY TEST | 345 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | APISTD5L |  | 0 | 1970 | UNDER GROUND OR UNDER WATER |  | RICHARD M. MORROW, MGR. OF DIST. STAFF | 2136894930 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-03-26 | YES | 3 | PAINT | YES |  |  | THE D.W. BURHOE CONSTRUCTION CO., GRADING FOR STREET IMPROVEMENT FOR THE CITY OF PALMDALE, STRUCK AND DAMAGED A 6 INCH HIGH PRESSURE MAIN, CAUSING GAS TOESCAPE.
2025-01-31 10:21 | YES | YES | 19900184 | 1990-10-04 | 15007 | PACIFIC GAS & ELECTRIC CO | 2025 NEVIN STREET | RICHMOND | CONTRA COSTA | CA | 94804 | 3 | NO | 1310 | 1990-09-05 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 20 | 38469 | 19900905 | 0.36 | 0.36 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.188 | 4" CI |  | 0 | 1911 | OTHER | OPEN EXCAVATION | W. R. MAZOTTI, V.P. GAS AND ELECTRIC TECH. SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEE ACCIDENTALLY STEPPED ON 1 1/4 INCH STUB SERVICE CAUSING GAS SERVICETO CRACK AND LEAK.
2025-01-31 10:21 | YES | YES | 19900186 | 1990-10-22 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 201 S. HARDY STREET | DERMOTT | CHICOT | AR | 71638 | 3 | NO | 1350 | 1990-09-27 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 | 41483 | 19900927 | 20 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 2 | 0.1216 | ASTM2513 | PHILIPS-DRISCOPIPE | 1990 | 1990 | UNDER GROUND OR UNDER WATER |  | ROY C. TOBEY - DIVISION MANAGER | 5013774800 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ARKLA CREW WAS IN THE PROCESS OF INSERTING A 2" PLS GAS MAIN IN AN EXISTING 4" STEEL MAIN. ALL ASPECTS OF THE JOB HAD BEEN COMPLETED WHEN THE SQUEEZE OFF WAS RELEASED, BLEEDING THE AIR OUT OF THE LINE FOR THE FINAL CONNECTION. WHILE BLEEDING THE LINE, THE GAS IGNITED FROM STATIC ELECTRICITY. ONE ALG EMPLOYEE RECEIVED SECOND AND THIRD DEGREE BURNS TO BOTH ARMS, REQUIRING HOSPITALIZATION.
2025-01-31 10:21 | YES | YES | 19900195 | 1990-10-31 | 12878 | MOUNTAINEER GAS CO | NEAR BOX 241 | CHARLESTON | KANAWHA | WV | 25312 | 3 | NO | 815 | 1990-10-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 | 42857 | 19901009 | 35 | 35 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | JOINT | THREADED | STEEL |  | 2 | 0.154 |  |  | 0 | 1941 | UNDER GROUND OR UNDER WATER |  | ROGER A. DINGESS, AREA PLANT SUPERVISOR | 3043470586 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | TWO EMPLOYEES OF ROVER CONSTRUCTION COMPANY REMOVED THE LID FROM A MAN HOLE COVER TO ENTER A SEWER LINE UNDER CONSTRUCTION. THEY WERE USING A BATTERY POWERED LAZER BEAM WHICH SPARKED AND IGNITED GAS THAT HAD ACCUMULATED. ONE EMPLOYEE, JOHN PRINGLE WAS TREATED FOR BURNS AT THE HOSPITAL AND RELEASED. THE OTHER EMPLOYEE, KEITH PAULEY WAS BURNED MORE SEVERELY AND WAS TAKEN TO THE CABELL HUNTINGTON BURN UNIT AND ADMITTED. THE GAS APPARENTLY MIGRATED FROM A LEAK IN A 2" GAS LINE WHICH PARALELLED THE SEWER LINE. THERE WAS NO DAMAGE TOANY FACILITIES. GAS LOSS WAS MINIMAL. THE TWO MEN STATED THEY THOUGHT THEYSMELLED SEWER GAS. THEY MADE NO CHECKS FOR GAS. WHEN GAS COMPANY CREW ARRIVED, THERE WAS ONLY AN 80% L.E.L. READING IN THE MAN HOLE.
2025-01-31 10:21 | NO | NO | 19900196 | 1990-10-30 | 10037 | K P L GAS SERVICE | 12TH AND WALNUT | KANSAS CITY | JACKSON | MO | 64120 | 4 | NO | 1315 | 1990-10-05 | 0 | 0 | 7000 | 5818.971 | 14049.7159 | YES | 1 | 10 | 42395 | 19901005 | 1 | 5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | BRANCH TO DRIP POT | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1901 | UNDER PAVEMENT |  | HANS E. MERTENS, V.P. ENGINEERING | 8163465575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-10-05 | YES | 3 | LOCATED BY PHONE | YES |  |  | REGARDING PIPELINE LOCATION MARKERS:CITY REQUESTED MAIN LOCATION DATA BY TELEPHONE (EMERGENCY LOCATE) AT 10:15.KANSAS CITY WATER AND POLLUTION CONTROL DEPT. BROKE A DRIP POT LOOSE FROM 24"CAST IRON MAIN WHILE EXCAVATING A SEWER LINE.
2025-01-31 10:21 | NO | NO | 19900197 | 1990-10-29 | 2116 | CARROLLTON GAS DISTRICT SYSTEM, CITY OF | 304 THIRD STREET | CARROLLTON | CARROLL | KY | 41008 | 3 | NO | 955 | 1990-09-24 | 0 | 0 | 49000 | 40732.7967 | 98348.0114 | Null | 0 | 25 | 40754 | 19900924 | 250 | 150 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | PROPANE AIR PEAK SHAVING | OTHER | FILTER | OTHER | GLASS | 1 | 0 |  | WATTS FLUID POWER | 1973 | 1973 | ABOVE GROUND | INSIDE BUILDING | PAUL ALEXANDER, SUPERINTENDENT OUTSIDE SERVICES | 5027324221 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE UTILITY WAS IN THE PROCESS OF UP-RATING A SIX INCH (6") STEEL NATURAL GAS PIPELINE TO A MAOP OF FOUR HUNDRED AND TWENTY FIVE POUNDS PER SQUARE INCH(425 PSIG). THE UTILITY'S PROPANE-AIR PEAK SHAVING PLANT IS CONNECTED TO THIS PIPELINE THROUGH APPROXIMATELY ONE THOUSAND EIGHT HUNDRED FEET (1800') OF FOUR INCH (4") STEEL MAIN. UNKNOWN TO ANYONE AND NOT DISCOVERED DURING THE SYSTEM INVESTIGATION PRIOR TO PREPARATION OF THE WRITTEN UP-RATING PLAN WAS A ONE INCH (1") PIPELINE CONNECTING THE STARTING MOTORS OF THE THREE AIR COMPRESSORS INSIDE THE PROPANE AIR PEAK SHAVING PLANT BUILDING TO THE PIPELINE BEING UP-RATED. THE ONE INCH (1") PIPE TRAIN CONTAINED VALVES, ONE (1) GLASS BOWL FILTER AND (1) GLASS BOWL LUBRICATOR ALONG WITH THE NORMAL PIPE FITTINGS. THE MAOP OF THIS COMPRESSOR STARTING ASSEMBLY WAS ONE HUNDRED AND FIFTY POUNDS PER SQUARE IN (150 PSIG). WHEN THE PRESSURE WAS INCREASED IN THE SIX INCH(6") PIPELINE TO APPROXIMATELY TWO HUNDRED AND FIFTY LBS. PER SQUARE INCH (250 PSIG) THE GLASS BOWL ON THE ONE (1") FILTER RUPTURED. IMMEDIATELY AFTER THE RUPTURE THE VALVE AT THE CONNECTION OF THE FOUR INCH (4") LATERAL PIPELINE CONNECTING THE PROPANE-AIR PLANT TO THE SIX INCH (6") PIPELINE WAS CLOSED.BEFORE THE BUILDING COULD BE VENTED OF GAS THE GAS MIGRATED INTO THE IVENTORY STORAGE AREA OF THE BUILDING. THE PILOT ON AN OVERHEAD GAS HEATER IN THIS PORTION OF THE BUILDING BECAME THE SOURCE OF IGNITION. A FLASH FIRE AND EXPLOSION OCCURRED. ACTUAL DAMAGE DUE TO FIRE WAS MINIMAL SINCE THE STRUCTURE DID NOT CATCH FIRE. THE MAJOR DAMAGE RESULTED FROM THE EXPLOSIVE FORCE. THE BUILDING WAS CONSTRUCTED OF REINFORCED CONCRETE FLOORS AND WALLS ON THE PARTIALLY UNDERGROUND (WALK OUT BASEMENT) LOWER LEVEL, CONCRETE BLOCK WALL CONSTRUCTION ON THE SECOND LEVEL AND A WOODEN ROOF SYSTEM. THE CONCRETE BLOCK WALL WAS PARTIALLY DESTROYED BY THE FORCE OF THE EXPLOSION RESULTING IN THE ROOF SYSTEM SAGGING. ALL INVENTORY AND EQUIPMENT STORED INSIDE THE STRUCTURE WAS UNHARMED AND SALVAGED. THE STRUCTURE IS PRESENTLY UNDERGOING REPAIRS.
2025-01-31 10:21 | YES | NO | 19900200 | 1990-11-02 | 22763 | WISCONSIN GAS CO | W67-N396 GRANT AVENUE | CEDARBURG | OZAUKEE | WI | 53012 | 3 | NO | 1342 | 1990-10-12 | 0 | 0 | 80000 | 66502.5253 | 160568.1818 | Null | 1 | 0 | 43374 | 19901012 | 0.23 | 35 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 0.75 | 0.113 | DRESSER 90 | DRESSER INDUSTRIES | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | GREGORY B. SCHROEDER, P.E. PLANNING ENGINEER | 4142916729 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-09-25 | YES | 3 | PAINT | YES |  |  | SERVICE PIPE WAS PULLED APART AT A COUPLING BECAUSE OF SETTLEMENT OF SOIL INTHE TRENCH OF A NEW SEWER.ON OCTOBER 12, 1990 AT 1:42 P.M. A GAS EXPLOSION OCCURED AT W67 N396 GRANT AVENUE IN CEDARBURG, WI. A SEWER CONTRACTOR WAS FLUSHING A SEWER TRENCH WITH WATER TO SETTLE THE BACKFILL. ONE OF THE WORKERS NEARBY DETECTED GAS ODOR AND CALLED WISCONSIN GAS COMPANY. THE HOUSE EXPLODED SHORTLY AFTER THE GAS COMPANY REPRESENTATIVE ARRIVED. THE GAS SERVCE TO THE HOME HAD NOT BEEN SUFFICIENTLY SUPPORTED BEFORE THE TRENCH WAS BACKFILLED. DOWNWARD PRESSURE ON THE PIPE CAUSED IT TO PULL OUT OF A COUPLING. THE LEAKING GAS MIGRATED THROUGH THE SOIL AND INTO THE HOUSE WHERE IT ACCUMULATED TO THE POINT OF IGNITION
2025-01-31 10:21 | YES | NO | 19900201 | 1990-11-02 | 22763 | WISCONSIN GAS CO | 1406 N 23RD STREET | MILWAUKEE | MILWAUKEE | WI | 53205 | 3 | NO | 1712 | 1990-10-15 | 0 | 0 | 100000 | 83128.1566 | 200710.2273 | Null | 0 | 10 | 43756 | 19901016 | 0.23 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER HOUSEPIPE | OTHER | CUSTOMER HOUSEPIPE | OTHER PLASTIC | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GREGORY B. SCHROEDER, P.E. PLANNING ENGINEER | 4142916729 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER'S BOILER OVER FLOW TANK FELL AND BROKE HOUSEPIPE WHICH LEAKED AND IGNITED ON A PILOT LIGHT.ON OCTOBER 15, 1990 AT 5:12 P.M. A GAS EXPLOSION OCCURRED AT 1406 N. 23RD STREET, AN APARTMENT BUILDING OF 10 UNITS. A HEAVY TANK USED FOR OVERFLOW OF HOT WATER ABOVE THE GAS BOILER IN THE BASEMENT FELL OFF ONTO THE GAS BOILER SHUTOFF VALVE, SHEARING THE VALVE AND ALLOWING THE GAS TO FLOW. THE NATURAL GAS PROBABLY WAS IGNITED BY THE BOILER OR WATER HEATER PILOT, EXPLODING AND CAUSING ONE MINOR INJURY, KNOCKING DOWN PART OF THE SOUTH SIDE WALL, AND LEAVINGTHE BUILDING UNFIT FOR HABITATION.
2025-01-31 10:21 | YES | YES | 19900202 | 1990-11-01 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | E. BROADWAY AND CATHERINE STREET | NEW YORK |  | NY | 10038 | 4 | NO | 1944 | 1990-10-01 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 6 | 41898 | 19901001 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | OTHER | PIPE BRANCH | STEEL |  | 6 | 0 |  |  | 0 | 1935 | UNDER GROUND OR UNDER WATER | STREET EXCAVATION | THOMAS W. COWAN, MANAGER | 2125762443 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | MECHANIC WAS LOOSENING BOLTS ON A 6" STEEL COUPLING IN EXCAVATION WHEN FIRE ERUPTED.CONSTRUCTION CREW WAS PERFORMING A GAS MAIN CUT-OUT WHEN A FIRE ERUPTED IN THE EXCAVATION. A MECHANIC WAS LOOSENING BOLTS ON A 6" STEEL COUPLING WHEN INCIDENT OCCURRED.
2025-01-31 10:21 | YES | YES | 19900203 | 1990-11-01 | 11032 | LACLEDE GAS CO | LAC TERRE COURT & DARDEEN FARMS DRIVE | O'FALLON | ST CHARLES | MO | 63366 | 3 | NO | 1115 | 1990-10-05 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 20 | 42490 | 19901005 | 24.5 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | ASTM D2513 |  | 0 | 1989 | OTHER | EXCAVATION | PAUL B. HUNKER, ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | DURING THE PROCESS OF PURGING A PROPANE GAS MAIN FOR THE CONVERSION TO NATURAL GAS, A FITTING USED IN THE TEMPORARY PURGE PIPING FAILED. IT APPEARS THATTHE NATURAL GAS WAS IGNITED BY STATIC ELECTRICITY.
2025-01-31 10:21 | YES | NO | 19900205 | 1990-11-08 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | INNER HARBOR, NAVIGATIONAL CANAL/LN RR | NEW ORLEANS |  | LA | 70160 | 3 | NO | 1600 | 1990-10-13 | 0 | 0 | 100000 | 83128.1566 | 200710.2273 | YES | 2 | 10 |  | 19901013 | 80 | 125 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | WELD | GIRTH | STEEL |  | 16 | 0.75 | UNKNOWN | UNKNOWN | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | ALBERT A. GABRIEL, JR. | 5045953561 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GIRTH WELD FAILED AS A RESULT OF EXTERNAL STRESS. CAUSE OF FAILURE IS UNDER INVESTIGATION
2025-01-31 10:21 | NO | NO | 19900206 | 1990-11-08 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 42 CENTERVIEW STREET | BELMONT | GASTON | NC | 28012 | 3 | NO | 1200 | 1990-10-16 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 | 43789 | 19901016 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | MECH. | STEEL |  | 0.75 | 0.113 | API 5L GR.B |  | 1960 | 1960 | UNDER GROUND OR UNDER WATER |  | BILL RAYNER, DIVISION ENGINEER | 7048646731 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-09-25 | YES | 0 |  | YES |  |  | A CONTRACTOR INSTALLING A WATER LINE AT RESIDENCE PULLED THE GAS SERVICE OUTOF A MECHANICAL COUPLING CAUSING A GAS LEAK. THE LEAK WAS UNREPORTED AND WAS LATER IGNITED BY A PLUMBING WORKER WHO WAS LIGHTING A CIGARETTE. THE PLUMBING WORKER WAS BURNED AROUND THE FACE AND SHOULDER. HE WAS TAKEN TO A HOSPITAL, TREATED AND RELEASED.
2025-01-31 10:21 | YES | NO | 19900209 | 1990-11-05 | 1640 | BOSTON GAS CO | 132 GRANDVIEW AVENUE | WINTHROP | SUFFOLK | MA | 02152 | 3 | NO | 1218 | 1990-10-02 | 0 | 0 | 950000 | 789717.4874 | 1906747.1591 | Null | 2 | 0 | 41977 | 19901002 | 0.25 | 0.36 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.384 |  |  | 0 | 1911 | UNDER PAVEMENT |  | LEO. T. CODY, MANAGER, DISTRIBUTION ADMINISTRATION | 6173239210 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TIDAL ACTION | NO |  | NO | 0 |  | NO |  |  | THE TOWN OF WINTHROP MAINTAINED A BRICK DRAIN MANHOLE ON GRANDVIEW AVENUE ATBILLOWS STREET. THE MANHOLE HAD A 15" DRAIN OUTFALL RUNNING INTO WINTHROP HARBOR WHICH WAS AFFECTED BY THE OPERATION OF THE TIDES. TIDAL WATER ENTERED THE MANHOLE THROUGH THE 15" DRAIN OUTFALL.THERE WAS A 4" CAST IRON MAIN IN GRADVIEW AVENUE CONNECTED TO A 1-1/2" STEELMAIN IN THE INTERSECTION AT BILLOWS STREET. THE 1-1/2" STEEL GAS MAIN WAS ENCASED BY THE BRICK DRAIN MANHOLE.THE FOLLOWING FACTORS CAUSED THE 4" CAST IRON GAS MAIN TO BREAK: 1. THERE WERE SEVERAL MISSING COURSES OF BRICK FROM THE BASE OF THE WALL OF THE DRAIN MANHOLE AND THE TIDAL ACTION ERODED THE LATERAL SUPPORT OF THECAST IRON GAS MAIN. 2. THE TIDAL ACTION AND THE COMBINATION SLAG AND GRAVEL SOIL CAUSED THEDRAIN MANHOLE TO SETTLE WHICH ADVERSELY AFFECTED THE 1-1/2" STEEL GAS MAIN AND CREATED AN ADDITIONAL DOWNWARD STRESS ON THE 4" CAS IRON GAS MAIN.AS A RESULT, THE 4" CAST IRON NATURAL GAS MAIN CRACKED OPEN AT THE BOTTOM OFTHE PIPE. THE RESULTING LEAKING GAS MIGRATED TO 132 GRANDVIEW AVENUE WHERE IT IGNITED. THE ENSUING FIRE, FANNED BY HIGH WINDS, CAUSED A LOSS OF THREE ADDITIONAL HOMES AND PROPERTY DAMAGE TO ANOTHER.
2025-01-31 10:21 | YES | NO | 19900211 | 1990-11-20 | 4060 | EAST OHIO GAS CO | 6313 SCOTLAND | MADISON | LAKE | OH | 44057 | 3 | NO | 2110 | 1990-10-15 | 0 | 0 | 102414 | 85134.8703 | 205555.3722 | Null | 3 | 30 | 43714 | 19901015 | 42 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | NONE | STEEL |  | 1 | 0.179 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | PAUL E. OLEKSA, ENVIRONMENTAL AND CODES ENGINEER | 2164326858 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE HOME OWNER, WHILE ATTEMPTING TO BY-PASS HIS NATURAL GAS METER, SAYS HE REMOVED A 1" SCREW PLUG FROM A 1" x 1" SCREW TEE UPSTREAM OF HIS SERVICE REGULATOR AND LOCATED UNDERGROUND NEAR HIS NATURAL GAS METER MANIFOLD. HE REMOVEDTHE 1" SCREW PLUG FROM THE 1" x 1" SCREW TEE AND BECAUSE OF THE 42 PSI SERVICE LINE PRESSURE, COULD NOT SCREW THE 1" SCREW PLUG BACK INTO THE SCREW TEE.THE HOME OWNER CALLED THE MADISON FIRE DEPARTMENT FOR HELP. A SHORT TIME AFTER THE MADISON FIRE DEPARTMENT ARRIVED AN EXPLOSION OCCURED.
2025-01-31 10:21 | NO | NO | 19900213 | 1990-11-15 | 15007 | PACIFIC GAS & ELECTRIC CO | 1745 SOUTH EL CAMINO REAL | SAN MATEO | SAN MATEO | CA | 94402 | 3 | NO | 735 | 1990-10-15 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 0 | 20 | 43596 | 19901015 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  | SPRAGUE | 0 | 1974 | WITHIN/UNDER BUILDING |  | W R MAZOTTI - VP GAS & ELEX TECH SVS | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE DAMAGED METER AND REGULATOR.
2025-01-31 10:21 | NO | NO | 19900217 | 1990-11-14 | 13782 | NORTHERN STATES POWER CO | 11TH AND ROBERT STREETS | ST PAUL | RAMSEY | MN | 55101 | 3 | NO | 840 | 1990-10-26 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 | 45153 | 19901026 | 20 | 20 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DANIEL J. WOEHRLE, SUPERINTENDENT, GAS ENG & STDS. | 6122292211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | YES |  |  | CONTRACTOR STRUCK 8" STEEL MAIN CROSSING INTERSTATE FREEWAY, CAUSING TRAFFICTO BE STOPPED FOR 40 MINUTES.
2025-01-31 10:21 | NO | NO | 19900219 | 1990-11-29 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 1830 LEXINGTON AVENUE | MANHATTAN |  | NY |  | 4 | NO | 1130 | 1990-10-09 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 0 | 0 | 42879 | 19901009 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | RISER TO GAS HEATER | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD C. GAULIN - PLANNING | 2124602838 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | WHILE DRILLING HOLES IN THE PROCESS OF REPLACING A CORRODED GAS RISER LEADING TO A GAS HEATER, A GENERAL CONTRACTOR CAUSED THE RISER TO LEAK. THIS ACTIONPRECIPITATED A GAS EXPLOSION BY AN UNKNOWN IGNITION SOURCE. TWO PERSONS WERE TAKEN TO THE HOSPITAL. IT WAS DETERMINED THAT THIS INCIDENT IS NOT REPORTABLE TO DOT.
2025-01-31 10:21 | YES | YES | 19900222 | 1990-12-11 | 15007 | PACIFIC GAS & ELECTRIC CO | 6159 LOIS DRIVE | PARADISE | BUTTE | CA |  | 3 | NO | 2212 | 1990-11-15 | 0 | 2 | 125000 | 103910.1957 | 250887.7841 | Null | 2 | 48 | 47845 | 19901115 | 48 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | LEAK CLAMP | POLYETHYLENE PLASTIC |  | 0.5 | 0 | N/A | ALDYL A | 0 | 1973 | UNDER PAVEMENT |  | W.R. MAZOTTI, V.P.-GAS AND ELECTRIC TECHNICAL SVS. | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DURING THE INVESTIGATION, PACIFIC GAS AND ELECTRIC COMPANY AND THE PARADISE FIRE DEPARTMENT FOUND THAT THE GAS SERVICE HAD BEEN PREVIOUSLY SEVERED BY AN UNKNOWN THIRD-PARTY. THE DAMAGED SERVICE WAS REPAIRED WITH HOSE CLAMPS AND APIECE OF AUTOMOBILE HEATER HOSE. THE GAS WAS LEAKING FROM THE MAKESHIFT CLAMP WHEN THE INCIDENT OCCURRED.
2025-01-31 10:21 | YES | YES | 19900223 | 1990-12-06 | 13710 | NORTHERN ILLINOIS GAS CO | GRASS LAKE ROAD AT ROUGE 83 | ANTIOCH | LAKE | IL | 60002 | 3 | NO | 1536 | 1990-11-02 | 0 | 3 | 0 | 0 | 0 | Null | 1 | 39 | 46195 | 19901102 | 150 | 300 | BY TEST | 450 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 6 | 0 | UNKNOWN | UNKNOWN | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | A.W. SWANSON, GENERAL SUPERVISOR SYSTEM OPERATING | 8154550271 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A SERVICE TEE WAS KNOCKED OFF A 6-INCH, 150 PSI MAIN BY THE CUSTOMER WHO WASGRADING IN A DITCH. NI-GAS PERSONNEL WERE CALLED AND RESPONDED TO STOP THE ESCAPING GAS AND MAKE REPAIRS. WHILE REPAIRS WERE UNDER WAY, ESCAPING GAS WAS IGNITED, RESULTING IN INJURY TO SEVERAL NI-GAS PERSONNEL. THE FIRE WAS EXTINGUISHED AT 1934 BY THE ANTIOCH FIRE DEPARTMENT AT THE SCENE. THE LEAK WAS STOPPED AT 2040.
2025-01-31 10:21 | NO | NO | 19900225 | 1990-12-14 | 792 | ATLANTA GAS LIGHT CO | INDIAN TRAIL - LILBURN ROAD | LILBURN |  | GA | 30247 | 1 | NO | 945 | 1990-11-29 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 1 | 55 | 49353 | 19901129 | 60 | 60 | BY TEST | 110 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0 | ASTMD2513 | DRISCO | 1979 | 1980 | UNDER GROUND OR UNDER WATER |  | CLAYTON H. PREBLE | 4044764861 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-11-19 | YES | 3 | PAINT | YES |  |  | CONTRACTOR MAKING A 30" BORE STRUCK AND DAMAGED 4" GAS MAIN LOCATED IN RIGHT-OF-WAY OF INDIAN TRAIL ROAD. FLOW OF NATURAL GAS BACK THROUGH CASING WAS IGNITED BY BORING RIG, RESULTING IN DAMAGE TO THE BORING RIG EQUIPMENT.
2025-01-31 10:21 | YES | NO | 19900226 | 1990-12-13 | 15350 | PEOPLES NATURAL GAS CO | THE DOMINION PLAN | ST CLAIR | ALLEGHENY | PA | 15241 | 3 | NO | 1546 | 1990-11-14 | 0 | 0 | 180000 | 149630.6818 | 361278.4091 | Null | 1 | 0 | 47650 | 19901114 | 64 | 90 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | STEEL |  | 12 | 0 |  |  | 0 | 1913 | UNDER GROUND OR UNDER WATER |  | HORACE P. PAYNE, JR., ESQ. | 4124976889 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-09-13 | YES | 2 |  | YES |  |  | CONTRACTOR HIT P-1156 WITH BULLDOZER. LINE HAD BEEN LOCATED & MARKED BY PNG.
2025-01-31 10:21 | NO | NO | 19900227 | 1990-12-18 | 13707 | NORTHERN MINNESOTA UTILITIES |  | DEER RIVER | ITASCA | MN | 56636 | 3 | NO | 100 | 1990-11-13 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 47782 | 19901115 | 250 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | REGULATOR/METER |  | STEEL |  | 4 | 0.395 | AFV 2" | AMERICAN METER | 1990 | 1990 | UNDER PAVEMENT |  | K.R. BERGSTEDT | 2188791571 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE TIME THAT THE PRESSURE EXCEEDED THE MAOP IS UNDEFINED. IT IS SUSPECTED THAT THE EXCESS PRESSURE MAY HAVE BEEN INITIATED ON TUESDAY, NOVEMBER 13TH. THE PRESSURE WAS REDUCED TO WITHIN MAOP BY 1055 HOURS, NOVMEMBER 15, 1990. PRESSURE IS JUDGED TO HAVE REACHED A MAXIMUM GREATER THAN 160 PSIG, BUT LESS THAN 250 PSIG FOR THE FOLLOWING REASONS: A 160# PRESSURES GAUGE INSTALLED ON THE SYSTEM SUFFERED PERMANENT DISTORTION; THIS INDICATES THAT THE SYSTEM PRESURE WAS IN EXCESS OF 110% FACE VALUE. CRITICAL PRESSURE ( THAT WHICH INDUCESYEILD) IN POLYETHYLENE IS EXPERIMENTALLY LOCATED BETWEEN 560-650 PSIG FOR 4"IPS SDR 11 PIPE. LABORATORY TESTS INDICATE THAT THE APPLICATION OF 44% OF YEIELD STRESS INDUCES DEFORMATION IN PE PIPE THAT IS ENTIRELY ELASTIC, I.E. THE PIPE WILL RETURN TO ITS ORIGINAL SIZE WITHIN 24 HOURS OF RELIEVING THE EXCESS PRESSURE. A TEST INSPECTION OF THE SYSTEM AT APRPOXIMATELY 1400 HOURS, NOVEMBER 16, 1990, INDICATED THE PIPE DIAMETER TO MATCH THAT OF THE FACTORY QUALITY CONTROL REPORT. IT IS BELIEVED THAT HIGH HUMIDITY GAS WAS RECIEVED DUE TO THE HYDRO-TESTING OF THE SUPPLIER'S STATION PIPING. THIS MOISTURE FROZE INTHE REGULATOR BODY RESTRICTING THE REGULATORY FROM FULLY SEATING. AT THIS ITME, THE MONITOR REGULATORY PROBABLY TOOK CONTROL UNTIL IT EXPERIENCED A SIMILAR FAILURE.
2025-01-31 10:21 | YES | YES | 19900228 | 1990-12-14 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 54338 IVY ROAD | SOUTH BEND | ST JOSEPH | IN | 46618 | 3 | NO | 1330 | 1990-11-27 | 0 | 1 | 50000 | 41564.0783 | 100355.1136 | Null | 4 | 0 | 50062 | 19901205 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD 2513 | DUPONT | 0 | 1981 | WITHIN/UNDER BUILDING |  | D.M. CAMPOS, MANAGER GAS CONTROL & STORAGE | 2198535603 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | ON NOVEMBER 27, 1990, AT APPROXIMATELY 1330 HRS., THE HOUSE IN QUESTION EXPLODED AND WAS GUTTED BY THE ENSUING FIRE. MS. ANN HORVATH, AGE 78 YEARS, WAS HOSPITALIZED DUE TO INJURIES CAUSED BY FALLING DEBRIS. THE CAUSE OF THE INCIDENT IS ABGRIBUTED TO LEAKING GAS FROM A 2" PLASTIC BURIED MAIN FINDING ITS WAY INTO THE BUILDING AND SOMEHOW IGNITING. THE LEAK WAS TRACED TO A CRACK, NEAR AN ELBOW, ON THE 2" MAIN. IT APPEARS THE CRACK WAS CAUSED BY STRESS DUE TO SOIL SUBSIDENCE.
2025-01-31 10:21 | YES | YES | 19900230 | 1990-12-20 | 1800 | BROOKLYN UNION GAS CO | 1270 EAST 72ND STREET | BROOKLYN | KINGS | NY | 11234 | 4 | NO | 939 | 1990-12-04 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 21 | 49946 | 19901204 | 0.25 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 1.5 | 0.145 |  |  | 0 | 1968 | OTHER | SEWER MANHOLE | JOSEPH J. MARAZZO, SECTION MANAGER, DCD | 7184032864 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | YES | 1990-07-12 | YES | 3 | STREET SURFACE PAINTED | NO |  |  | A N.Y.C. CONTRACTOR EMPLOYEE WAS INJURED WHILE WORKING IN A SEWER MANHOLE ONEAST 72ND. STREET BETWEEN AVENUE L AND AVENUE M. A BROOKLYN UNION CHEMIST CONFIRMED THE PRESENCE OF NATURAL GAS IN THE SEWER MANHOLE. UPON INVESTIGATION BY LEAK SURVEILLANCE CREWS, TWO GAS SERVCIES SUPPLYING #1256 AND #1270 EAST 72ND. STREET WERE FOUND SEPARATED AT A COUPLING DUE TO SUBSIDENCE OF RECENT SEWER CONSTRUCTION.
2025-01-31 10:21 | YES | YES | 19900232 | 1990-12-20 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 1638 YORK AVENUE | NEW YORK |  | NY |  | 4 | NO | 416 | 1990-11-17 | 0 | 1 | 1000 | 831.2816 | 2007.1023 | Null | 0 | 14 | 48011 | 19901117 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | APPLIANCE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | THOMAS COWAN - DIVISION MANAGER | 2125762441 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PERSON WAS USING COMMERCIAL BAKING OVEN WHEN AN EXPLOSION OCCURRED.
2025-01-31 10:21 | NO | NO | 19900235 | 1990-12-31 | 15007 | PACIFIC GAS & ELECTRIC CO | 2982 CUESTA WAY | CARMEL | MONTEREY | CA |  | 2 | NO | 1336 | 1990-12-04 | 0 | 0 | 25000 | 20782.0391 | 50177.5568 | Null | 0 | 20 | 49937 | 19901204 | 50 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | W.R. MAZOTTI, V.P. - GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS METER SET IN GARBAGE COLLECTION AREA CAUGHT ON FIRE.
2025-01-31 10:21 | NO | NO | 19910006 | 1991-01-07 | 4060 | EAST OHIO GAS CO | 2628 11TH STREET SW. | CANTON | STARK | OH | 44710 | 3 | NO | 1530 | 1990-12-06 | 0 | 0 | 50000 | 41564.0783 | 100355.1136 | Null | 2 | 30 | 50204 | 19901206 | 0.5 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | 8000PE 3408 | PHILLIPS DRISCOPIPE INC | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | PAUL E. OLEKSA, ENVIRONMENTAL & CODES ENGINEER | 2164326858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-11-28 | YES | 3 | PAINT ON PAVEMENT | NO |  |  | TEMPORARY LOCATION MARKING WAS INACCURATE. ANOTHER UTILITY HIT A 4-INCH PLASTIC LOW PRESSURE MAIN WITH A BORING DEVICE. GAS MIGRATED 17 FEET THROUGH SOIL TO A HOUSE. THE HOUSE EXPLODED. THERE WERE NO INJURIES OR FATALITIES.
2025-01-31 10:21 | NO | NO | 19910007 | 1991-01-03 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 4512 14 BANKS STREET | NEW ORLEANS | ORLEANS | LA | 70119 | 3 | NO | 1800 | 1990-12-15 | 0 | 0 | 0 | 0 | 0 | YES | 6 | 15 | 51225 | 19901215 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | UNSPECIFIED CORROSION | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.145 | N/A | N/A | 0 | 1916 | WITHIN/UNDER BUILDING |  | J.E. MCNAMARA, P.E., ENGINEER | 5045953576 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS ESCAPING FROM A RUSTED OUT 1 1/2 INCH CONCRETE COATED LOW PRESSURE SERVICE LINE TO 4512-14 BANKS ACCUMULATED IN THE FRONT WALL OF THE BUILDING AND MAY HAVE BEEN IGNITED BY A LIGHT SWITCH OR DOOR BELL. A SMALL AMOUNT OF SIDINGWAS BLOWN OFF THE FRONT WALL NEAR THE LIGHT SWITCH NEXT TO THE FRONT DOOR OF4512 BANKS, AND SOME MORE ALONG THE FRONT OF THE HOUSE. 4512 BANKS WAS NOT OCCUPIES. THE EXPLOSION OCCURRED SHORTLY AFTER 6:00 PM. AT THE TIME OF THE EXPLOSION, UNDERGROUND CREWMAN T. WINTERS WAS MZKING TEMPORARY REPAIRS TO THE SERVICE LINE UNDER THE HOUSE. T. WINTERS RECEIVED MINOR BURNS. HE WAS BROUGHT TO THE HOSPITAL AND WAS RELEASED AFTER TREATMENT.
2025-01-31 10:21 | YES | YES | 19910008 | 1990-01-03 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 3409 11 SHORT STREET | NEW ORLEANS | ORLEANS | LA | 70125 | 3 | NO | 1820 | 1990-12-14 | 0 | 1 | 0 | 0 | 0 | Null | 5 | 0 | 51147 | 19901214 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.375 | N/A | N/A | 0 | 1925 | WITHIN/UNDER BUILDING |  | J.E. MCNAMARA, P.E., ENGINEER | 5045953576 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | NO |  |  | GAS ESCAPING FROM A BROKEN 6 INCH LOW PRESURE CAST IRON GAS MAIN LEAKED INTOTHE SEWER LINE LEADING TO 3409 11 SHORT STREET. GAS THEN ESCAPED THROUGH BROKEN SEWER PIPES UNDER 3411 SHORT, ENTERED THE BATHROOM AND WAS IGNITED BY A WATER HEATER. MS. LEOLIA WATT WAS IN THE BATHROOM AT THE TIME AND SHE RECEIVED BURNS AND WAS BROUGHT TO CHARITY HOSPITAL. THE EXPLOSION CAUSED MEDIUM DAMAGE TO THE BATHROOM OF 3411 SHORT, AND SLIGHT DAMAGE TO BATHROOM OF 3409 SHORT. SIDING WAS BLOWN OFF 3411 SHORT AND SOME SIDING NEAR THE ROOF ON 3409 SHORT WAS LOOSE. THERE WAS NO VISIBLE DAMAGE TO THE REST OF THE HOUSE.
2025-01-31 10:21 | YES | YES | 19910013 | 1991-01-11 | 11800 | LOUISIANA GAS SERVICE CO | INTERSEC. MERAUX LN & E JUDGE PEREZ DR. | VIOLET | ST BERNARD | LA | 70092 | 3 | NO | 1215 | 1990-12-20 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 | 51828 | 19901220 | 80 | 100 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | VALVE |  | STEEL |  | 4 | 0.237 | API-5L | UNKNOWN | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | A COMPANY CONSTRUCTION CREW WAS ATTEMPTING TO REWORK AND GREASE A 4" PLUG VALVE AT THE CORNER OF MERAUX LANE AND EAST JUDGE PEREZ DRIVE. THE VALVE WAS STUCK IN THE OFF POSITION. WHEN THE CONSTRUCTION WORKER LOOSENED THE BONNET RETAINING BOLTS, THE VALVE COVER PLATE BLEW INTO THE EMPLOYEE'S FACE CAUSING MINOR FACIAL LACERATIONS. THE ESCAPING GAS ALSO CONTAINED DUST AND DEBRIS WHICH WAS BLOWN INTO BOTH EYES. THE INJURED WORKER WAS TAKEN TO THE HOSPITAL AND LATER RELEASED. ALL EMPLOYEES ON THE CONSTRUCTION CREW WERE WEARING SAFETYGLASSES BUT THE GLASSES WERE BLOWN OFF THEINJURED EMPLOYEE BY THE ESCAPING GAS PRESSURE. GAS SERVICE WAS SHUT OFF TO APPROXIMATELY 50 CUSTOMERS AS A RESULT OF THIS INCIDENT. ALSO TRAFFIC OF EAST JUDGE PEREZ DRIVE WAS BLOCKED FORONE HOUR.
2025-01-31 10:21 | NO | NO | 19910015 | 1991-01-11 | 15931 | PUBLIC SERVICE CO OF COLORADO | 4940 LOWELL BLVD | DENVER CITY | DENVER | CO |  | 3 | NO | 43 | 1990-12-31 | 0 | 0 | 30000 | 24938.447 | 60213.0682 | YES | 1 | 31 | 53084 |  | 9 | 11 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | FITTING |  | OTHER PLASTIC | CAB | 0.75 | 0 | ASTM D-2513 |  | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | TOM WILSON | 3035713858 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | CAB PLASTIC SERVICE WAS INSERTED INSIDE 1 1/4" STEEL SERVICE IN 1965. CAB PLASTIC PULLED OUT OF THE COMPRESSION COUPLING AT THE WALL OF THE STRUCTURE AT4940 LOWEL BLVD. THE ESCAPING GAS WAS IGNITED BY SOME UNKNOWN SOURCE, RESULTNG IN A STRUCTURE FIRE. ONE MALE ADULT WAS TREATED FOR SMOKE INHALATION ANDRELEASED.
2025-01-31 10:21 | YES | YES | 19910016 | 1991-01-23 | 20211 | UNITED CITIES GAS CO | 908 E MARKET STREET | JOHNSON CITY | WASHINGTON | TN | 37601 | 0 | NO | 1145 | 1990-12-15 | 0 | 1 | 35000 | 29094.8548 | 70248.5795 | Null | 2 | 0 | 51199 | 19901215 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 1.05 | 0.113 | UNKNOWN | UNKNOWN | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | DAVID A SWECKER, DIVISION ENGINEERING MANAGER | 6156411805 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ABOUT 12:05 PM. ON SATURDAY, DECEMBER 15, 1990, THE RESIDENCE AT 908 EAST MARKET STREET EXPLODED AND BURNED. THERE WERE TWO RESIDENTS AND A LANDSCAPE CONTRACTOR WITH HELPER AT THE HOME. THE CONTRACTOR AND HIS HELPER WERE NOT INJURED, HOWEVER, ONE RESIDENT WAS TREATED AND RELEASED WHILE THE OTHER RESIDENTWAS ADMITTED AND TREATED FOR BURNS TO THE UPPER BODY. THE EVENTS PRECEDING THE ACCIDENT BEGAN ON THIS DAY AT APPROXIMATELY 10:00 AM., WHEN A LANDSCAPINGCONTRACTOR, EMPLOYED BY THE RESIDENT, BEGAN DIGGING IN THE BACKYARD OF 908 EAST MARKET STREET. AS A PART OF THEIR PRE-PLANNING FOR THIS PROJECT, THE CONTRACTOR DID NOT REQUEST UTILITY LOCATION THRU THE AREA UTILITIES NOR THE "ONE-CALL" SERVICE. AS A RESULT, THE CONTRACTOR BROKE THE UNMARKED, 3/4" COATED STEEL GAS SERVICE LINE NEAR THE FOUNDATION OF THE HOUSE WHERE THE LINE HAD APPROXIMATELY 1' OF COVER. THE RESIDENT CONTACTED OUR SERVICEMAN VIA THE ANSWERING SERVICE AND UPON ARRIVAL THE SERVICEMAN IDENTIFIED THE PROBLEM TO BE A BREAK IN THE 3/4" SERVICE LINE PROBABLY AT THE THREADED CONNECTION WHERE THE LINE CHANGED FROM ITS HORIZONTAL ORIENTATION TO THE VERTICAL WHICH FUNCTIONED AS THE SERVICE RISER FOR THE METER INSTALLATION WHICH, IN THIS CASE, DID NOT EXIST BECAUSE THERE WAS PRESENTLY NO GAS EQUIPMENT INSTALLED IN THE HOUSE. THESERVICEMAN THEN DIRECTED THE EXCAVATION OF THE LINE TO A POINT WHERE IT COULDBE DISCONNECTED AND CAPPED SINCE THERE WAS NO AVAILABLE VALVE TO DO SO. THIS WAS ACCOMPLISHED SOME 50 MINUTES AFTER THE BREAK OCCURRED. IT WAS APPROXIMATELY 15 MINUTES LATER THAT THE EXPLOSION OCCURRED. THE RESIDENT WHO SUFFERED THE BURNS WAS THE ONLY ONE IN THE HOUSE AT THE TIME OF THE EXPLOSION, THEOTHER RESIDENT AND THE CONTRACTOR PERSONNEL WERE OUTSIDE AT THE TIME. IT APPEARS THE EXPLOSION WAS THE RESULT OF NATURAL GAS, FROM THE EXTERIOR LINE BREAK, TRAVELING INTO THE HOUSE THROUGH CREVICES AND AN OPEN WINDOW IN SUFFICIENT QUANTITY TO CREATE AN EXPLOSIVE MIXTURE. THE SOURCE OF IGNITION IS INDETERMINATE.
2025-01-31 10:21 | YES | YES | 19910017 | 1991-01-17 | 2668 | COMMONWEALTH GAS SERVICES INC | 306 N SIXTH STREET | HOPEWELL |  | VA | 23860 | 3 | NO | 1319 | 1990-12-18 | 0 | 2 | 75000 | 62346.1174 | 150532.6705 | Null | 0 | 21 | 51591 | 19901218 | 35 | 35 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE 2306 | DUPONT | 1971 | 1971 | UNDER PAVEMENT |  | GARY J. LAPE, DIRECTOR PLANT OPERATIONS. | 8043235413 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EXPLOSION OCCURRED IN A BUILDING UNDER CONSTRUCTION THAT DID NOT HAVE NATURAL GAS SERVICE, INJURING FOUR CONSTRUCTION WORKERS, TWO OF WHOM WERE HOSPITALIZED. ALTHOUGH THE SOURCE AND NATURE OF THE COMBUSTIBLE MATERIAL HAS NOT BEEN DETERMINED, NATURAL GAS HAS NOT BEEN RULED OUT AS A POSSIBLE SOURCE. COMMONWEALTH GAS SERVICE (COS) PRESSURE TESTED THE 2" PLASTIC GAS MAIN AND FOUR ATTACHED SERVICE LINES IN THE BLOCK IN FRONT OF 306 N. SIXTH STREET AND FOUNDA LEAK. (A SIMILAR PRESSURE TEST WAS PERFORMED ON THE GAS MAIN ON 7TH STREET WITH NO LEAKAGE FOUND.) THE LEAK WAS ON THE SERVICE LINE FOR 301 N. SIXTH STREET AT A SOCKET FUSIO JOINT ON THE OUTLET OF A 2" X 1/2" CTS SERVICE TEE. COS HAS NOT BEEN ABLE TO DETERMINE THE PATH, IF ONE EXISTED, BOTH NATURAL GASTRACES OF FERMENTATION GAS, CONTINUE TO BE ENCOUNTERED IN THE AREA AND COS CONTINUES TO MONITOR AND INVESTIGATE THESE.
2025-01-31 10:21 | YES | NO | 19910018 | 1991-01-15 | 13795 | NORTHERN UTILITIES INC (ME) | 59 COTTAGE FARMS ROAD | CAPE ELIZABETH | CUMBERLAND | ME | 04107 | 3 | NO | 950 | 1990-12-05 | 0 | 0 | 100000 | 83128.1566 | 200710.2273 | Null | 1 | 30 | 50008 | 19901205 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING | THREAD | STEEL |  | 1 | 0 |  |  | 0 | 1983 | UNDER PAVEMENT |  | DANNY G. COTE, OPERATIONS MANAGER | 2077978002 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-11-30 | NO | 0 |  | YES |  |  | THE CONTRACTOR PULLED A 1 1/4" STEEL CAUSING THAT HAD 1" PLASTIC MAIN INSIDE THIS, IN TURN, BROKE A 3/4" MALLEABLE TEE WHERE IT WAS THREADED INTO A 1 1/4 X 3/4 TEE WITH A POSI-LOCK ADAPTOR WHERE A TRANSITION HAD BEEN MADE FROM PLASTIC TO STEEL TO JOIN TO THE PLASTIC SERVICE FEEDING 59 COTTAGE FARMS ROAD.SEE ATTACHMENT TO FEDERAL INCIDENT REPORT, NORTHERN UTILITIES, DECEMBER 5, 1990.
2025-01-31 10:21 | YES | NO | 19910019 | 1991-01-15 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 190 COUNTRY RIDGE ROAD | NEW ROCHELLE | WESTCHESTER | NY | 10804 | 0 | NO | 857 | 1990-12-07 | 0 | 0 | 100000 | 83128.1566 | 200710.2273 | Null | 0 | 0 | 52534 | 19901207 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S APPLIANCE | OTHER | CUSTOMER'S APPLIANCE | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | BRUAN G. GIBBS - CHIEF GAS ENGINEER | 2124604464 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | HOSE CONNECTION MELTED AT CUSTOMER'S BARBECUE GRILL. GAS RELEASED FROM MELTED HOSE IGNITED AND THE FIRE SPREAD TO THE HOUSE.
2025-01-31 10:21 | YES | NO | 19910020 | 1990-01-16 | 11800 | LOUISIANA GAS SERVICE CO | 6601 CAMPHOR STREET | METAIRIE | JEFFERSON | LA | 70003 | 3 | NO | 1452 | 1990-12-28 | 0 | 0 | 75000 | 62346.1174 | 150532.6705 | Null | 1 | 2 | 52847 | 19901228 | 60 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | THREADED | STEEL |  | 2 | 0.154 | API-5L | UNKNOWN | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DUMP TRUCK LOADED WITH SAND ROLLED OVER VALVE BOX CAUSING VALVE NIPPLE TO CRACK IN THREADS.
2025-01-31 10:21 | NO | NO | 19910021 | 1991-01-29 | 11800 | LOUISIANA GAS SERVICE CO | ROOSEVELT BLVD. AND 25TH STREET | KENNER | JEFFERSON | LA | 70062 | 3 | NO | 1030 | 1991-01-05 | 0 | 0 | 4000 | 3210.6065 | 7751.9049 | YES | 1 | 35 |  |  | 70 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L |  | 0 | 1956 | UNDER PAVEMENT |  | D.L. MERIWETHER, PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-09-27 | YES | 2 | PAINT | YES |  |  | 2" GAS MAIN WAS RUPTURED BY A BACKHOE THAT WAS ATTEMPTING TO DIG UP AND REMOVE A PAVED STREET.
2025-01-31 10:21 | YES | YES | 19910022 | 1991-01-28 | 2748 | CONSUMERS POWER CO | 48700 GRAND RIVER AVENUE | NOVI | OAKLAND | MI | 48374 | 3 | NO | 1601 | 1991-01-02 | 0 | 1 | 75000 | 60198.8723 | 145348.217 | Null | 0 | 44 | 53429 | 19910103 | 160 | 400 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.219 | API-5LGRB | US STEEL | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | K.L. ELENBAAS, GENERAL SUPERVISOR | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-12-12 | YES | 3 | UNKNOWN | YES |  |  | CONTRACTOR AUGERING FOR WATER LINE HIT AND DAMAGED GAS MAIN. GAS IGNITED DURING REPAIR.
2025-01-31 10:21 | YES | YES | 19910023 | 1991-01-29 | 2596 | COLUMBIA GAS OF OHIO INC | 7419 NEWPORT AVENUE | PARMA | CUYAHOGA | OH | 44129 | 4 | NO | 932 | 1991-01-02 | 0 | 2 | 3000 | 2407.9549 | 5813.9287 | Null | 1 | 0 | 53283 | 19910102 | 3 | 5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | VALVE |  | OTHER | BRASS VALVE | 1.25 | 0 | UNKNOWN | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | D.E. WILLIAMS, MGR., CONSTRUCTION & MAINTENANCE | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | LINE WAS EXPOSED IN BASEM | NO |  |  | PAUL CYGAN, CUSTOMER AND PROPERTY OWNER, WAS ATTEMPTING TO REPAIR A GAS LEAKON A BRASS METER VALVE IN HIS BASEMENT WHEN THE VALVE CORE BLEW OUT. ESCAPING GAS WAS IGNITED BY A BURNING PROPANE TORCH THAT MR. CYGAN HAD IN THE BASEMENT WITH HIM. THE FIRE CAUSED DAMAGE TO THE HOUSE AND THE GAS METER. A COLUMBIA GAS SERVCIE PERSON RESPONDING TO THE FIRE DEPARTMENT'S REQUEST, MADE THESITUATION SAFE BY CLOSING THE EXTERIOR CURB VALVE. MR. CYGAN HAD NOT NOTIFIED COLUMBIA GAS OF THE LEAK, NOR DID HE ATTEMPT TO TURN OFF THE GAS AT THE CURB VALVE PRIOR TO ATTEMPTING REPAIRS HIMSELF. PART B - LINE WAS EXPOSED INBASEMENT. THIS WAS NOT AN UNDERGROUND LINE. INCIDENT OCCURRED ON EXPOSEDFACILITY IN BASEMENT.
2025-01-31 10:21 | NO | NO | 19910024 | 1991-01-29 | 1800 | BROOKLYN UNION GAS CO | 319 MCKIBBEN STREET | BROOKLYN | KINGS | NY | 11222 | 4 | NO | 219 | 1991-01-15 | 0 | 0 | 0 | 0 | 0 | Null | 7 | 15 | 54976 | 19910115 | 0.25 | 0.43 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOSEPH J. MARAZZO - SECTION MANAGER | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | N.Y.C. FIRE DEPARTMENT REPORTED THAT NATURAL GAS WAS FUELING A FIVE ALARM BLAZE INVOLVING SEVERAL LARGE INDUSTRIAL BUILDINGS WITHIN ONE SQUARE BLOCK. INVESTIGATION AS TO THE CAUSE OF THE FIRE IS STILL BEING CONDUCTED. AS PER FEDERAL REGULATION 49-CFR-199, DRUG TESTING IS NOT REQUIRED BECAUSE NO EMPLOYEE WAS INVOLVED WITH THE CAUSE OF ACCIDENT. ON JANUARY 15,1991 AT 02:19 HOURS WE RECEIVED NOTIFICATION FROM THE N.Y.C. FIRE DEPARTMENT THAT A FIVE ALARM FIRE WAS IN PROGRESS AT 319 MCKIBBEN STREET, BROOKLYN, NY. AT APPROXIMATELY 04:00 HOURS THE GETR 9. FIRE DEPARTMENT REPORTED THAT INTERNAL GAS PIPING HAD SEVERED IGNITING NATURAL GAS.AT 07:35 HOURS A TELEPHONE REPORT OF THE INCIDENT WAS MADE TO DOT PETTY OFFICER JAMES BOWMAR. THE N.Y.C. FIRE DEPARTMENT IS STILL CONDUCTING THE INVESTIGATION AND IT IS NOT KNOWN WHETHER OR NOT NATURAL GAS WAS THE CAUSE. WE ARE SUBMITTING FORM DOT-F-7100.1 IN ACOCRDANCE WITH THEREGULATIONS OF THE OFFICE OF THE SECRETARY OF TRANSPORTATION, PART 191, SECTION 191.7, EVEN THOUGH HE CAUSE OF THE FIRE HAS STILL NOT BEEN DETERMINED.
2025-01-31 10:21 | YES | NO | 19910025 | 1991-01-29 | 1088 | BALTIMORE GAS & ELECTRIC CO | 4004 FREDRICK AVENUE | BALTIMORE |  | MD | 21228 | 3 | NO | 1520 | 1991-01-08 | 0 | 0 | 275000 | 220729.1984 | 532943.4624 | Null | 3 | 0 | 54111 | 19910108 | 0.23 | 0.29 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | CUSTOMER PIPING | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | DONALD L. SHRADER - SUPERVISOR | 3015612728 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | AT 1040, BALTIMORE CITY FIRE DEPARTMENT REQUESTED SERVICE ON WORKING TWO ALARM FIRE AT 4004 FREDERICK AVENUE. ARRIVING AT 1045 THE FIRST BALTIMORE GAS AND ELECTRIC REPRESENTATIVE REPORTED TO THE BATTALION CHIEF. THE BATTALION CHEIF #4 STATED "FIRE WAS NOT GAS RELATED BUT REQUESTED OUR COMPANY TO STANDBY" MR. STEVE UGATE, BALTIMORE CITY FIRE INVESTIGATOR STATED "THE FIRE STARTEDAT THE DEEP FAT FRYER WHEN RESTAURANT EMPLOYEES WERE CHANGING THE COOKING OIL AND NATURAL GAS WAS NOT INVOLVED". THE COOKING OIL WAS SPILLED AND IGNITED. THE RESTAURANT EMPLOYEES TRIED USING WATER TO EXTINGUISH THE FLAMES, THIS ACTION ONLY SPREAD THE FLAMES. AT 1115, MR. E.C. GOODRICH, BALTIMORE GAS ANDELECTRIC CALLED FOR DISTRIBUTION CREWS TO REPORT TO THE FIRE SCENE TO CUT OFF 1 1/4" LOW PRESSURE GAS SERVICE. DISTRIBUTION CREWS WERE REQUESTED TO CUT OFF GAS SERVICE OUTSIDE THE BUILDING BECAUSE BATTALION CHIEF #4 WOULD NOT ALLOW ENTRY INTO THE BASEMENT OF THE BUILDING. DISTRIBUTION CREWS ARRIVED AT 1145, PINPOINTED AND STARTED TO UNCOVER THE GAS SERVICE IN THE STREET. THE EXCAVATION OF THE GAS SERVICE WAS DELAYED BY HEAVY GROUND SMOKE AND FIRE FIGHTINGEFFORTS. AT THIS TIME THE REAR 2ND AND 3RD FLOOR COLLAPSED INTO THE 1ST FLOOR KITCHEN. BALTIMORE CITY FIRE DEPARTMENT REPORTED THE FIRE WAS UNDER CONTROL AT 1240. ENTRANCE TO THE BASEMENT WAS IMPOSSIBLE BECAUSE OF PARTIAL COLLAPSE. OUR DISTRIBUITON CREW WAS DIGGING OUT THE GAS SERVICE. AT 1520 BALTIMORE CITY FIRE DEPARTMENT ADVISED THE UTILITY FURTHER COLLAPSE OF THE 2ND AND 3RD FLOOR MUST HAVE BROKEN THE CUSTOMER'S FUEL LINE, AND GAS WAS NOW FEEDING THE FIRE. BATTALION CHEIF #4 ALSO REPORTED A 300 GALLON FUEL OIL TANK IN REAR BASEMENT IS LIKELY FEEDING THE FIRE. DELAYED BY WATER ENTERING THE HOLE BEING DUG TO CUT OFF THE GAS SERVICE AND VERY HEAVY GROUND SMOKE, DISTRIBUTION HAD TO START ANOTHER HOLE IN THE SIDEWALK 6' IN FRONT OF THE BUILDING AT 1650.BY 1820 DISTRUBITON CUT OFF 1 1/4" LOW PRESSURE SERVICE IN THE SIDE WALK. THE FIRE DEPARTMENT HAD THE FIRE OUT AT 1930.
2025-01-31 10:21 | YES | NO | 19910026 | 1991-01-28 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 316 SPRING STREET | HOT SPRINGS | GARLAND | AR | 71901 | 4 | NO | 1928 | 1990-12-29 | 0 | 0 | 150000 | 124692.2348 | 301065.3409 | Null | 0 | 45 | 52965 | 19901229 | 28 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 | N/A | N/A | 1950 | 1950 | OTHER | UNKNOWN | TOM CONNELL | 5013774786 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 4" CAST IRON COLD BREAK.
2025-01-31 10:21 | YES | YES | 19910027 | 1991-02-04 | 15007 | PACIFIC GAS & ELECTRIC CO | 24084 MYRTLE STREET | HAYWARD | ALAMEDA | CA | 94645 | 3 | NO | 1041 | 1990-12-21 | 0 | 1 | 465000 | 386545.928 | 933302.5568 | Null | 2 | 4 | 52005 | 19901221 | 0.25 | 0.38 | BY TEST | 2 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNDER INVESTIGATION | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION AND IGNITION OF ESCAPING GAS DAMAGED STRUCTURE AT ABOVE ADDRESS. SOURCE OF THE ESCAPING GAS IS STILL UNDER INVESTIGATION. NEARBY BUILDINGS WERE EVACUATED & TRAFFIC REROUTED. THE METER WAS REMOVED & THE SERVICE PIPE WAS CAPPED.
2025-01-31 10:21 | YES | NO | 19910031 | 1991-01-31 | 11032 | LACLEDE GAS CO | 201 N. STATE STREET | DESLOGE | ST FRANCOIS | MO | 63601 | 3 | NO | 1055 | 1991-01-07 | 0 | 0 | 95000 | 76251.9049 | 184107.7415 | Null | 0 | 53 | 53906 | 19910107 | 18 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.154 | N/A | N/A | 0 | 1956 | UNDER PAVEMENT |  | PAUL B. HUNKER, JR. / ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DURING REPAIR OF WATER MAIN, WATER COMPANY'S BACKHOE PUSH/PULLED STEEL GAS SERVICE TO THIS ADDRESS, CAUSING FITTING TO PULL APART, RESULTING IN EXPLOSION AND FIRE.
2025-01-31 10:21 | NO | NO | 19910032 | 1991-02-12 | 6690 | GREAT PLAINS NATURAL GAS CO | 303 N. 12TH STREET | BRECKENRIDGE | WILKIN | MN | 56520 | 3 | NO | 2340 | 1991-01-13 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 54841 | 19910114 | 15 | 15 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | WARREN E. SATTERLEE, VICE PRESIDENT-OPERATIONS | 2187366935 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS REPORT IS A FOLLOW-UP TO THE TELEPHONIC REPORT. EXTENSIVE TESTING INDICATES THAT THERE WAS NO RELEASE OF GAS FROM THE PIPELINE.
2025-01-31 10:21 | YES | YES | 19910033 | 1991-02-07 | 13840 | NORTHWEST NATURAL GAS CO | 2245 S.W. TROY | PORTLAND | MULTNOMAH | OR | 97219 | 3 | NO | 1630 | 1991-01-06 | 1 | 0 | 0 | 0 | 0 | Null | 2 | 0 | 53879 | 19910107 | 40 | 57 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 | API 5L-A25 | UNKNOWN | 1958 | 1958 | WITHIN/UNDER BUILDING |  | J.F. ERSPAMER, STAFF ENGINEER | 5032264211 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BASEMENT FIRE AT THE RESIDENCE INVOLVED ONE FATALITY AND MELTDOWN OF A BASEMENT METER SET. FREEZING RAIN, ICY STREETS, AND TRAFFIC SNARLS CONTRIBUTED TOTHE TWO-HOUR RESPONSE TIME. INVESTIGATION BY CITY FIRE MARSHALL, STATE UTILITY COMMISSION AND NATIONAL TRANSPORTATION SAFETY BOARD IS ONGOING. THE SEQUENCE OF EVENTS AND THE CAUSE OF THE FIRE IS UNCLEAR. THE METER IS IN THE POSSESSION OF N.T.S.B. FOR ANALYSIS.
2025-01-31 10:21 | NO | NO | 19910034 | 1991-02-07 | 12606 | MISSOURI PUBLIC SERVICE CO | 1232 N. TUCKER | NEVADA | VERNON | MO | 64772 | 3 | NO | 345 | 1991-01-14 | 0 | 0 | 60000 | 48159.0978 | 116278.5736 | Null | 1 | 35 | 54809 | 19910114 | 28 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.25 | UNKNOWN | UNKNOWN | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | LARRY WRAY JONES - DIRECTOR OPERATIONS | 8167379350 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19910036 | 1991-02-11 | 9050 | JACKSON VANGAS INC | 465 FLAT CREEK DRIVE | JACKSON | TETON | WY | 83001 | 1 | NO | 1400 | 1990-12-23 | 0 | 0 | 125000 | 103910.1957 | 250887.7841 | Null | 1 | 15 | 53597 |  | 15 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.5 | ALDY-A | DUPONT | 1969 | 1969 | UNDER PAVEMENT |  | JOHN A. NORBY | 3074334699 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | 12/23/89 2:00 PM. (APPROX). A CALL WAS PLACED TO JOHN NORBY IN RUPERT IDAHOBY JOHN SLOAN, SUBURBAN PROPANE EMPLOYEE, STATING THAT THERE HAD BEEN AN EXPLOSION AT THE CORNER OF FLAT CREEK & KARNS ACROSS FROM THE RADEO GROUNDS. JOHN SLOAN ON 2-WAY MOBILE PHONE TO SHERIFF'S OFFICE. 15 MINUTE ESTIMATED TIMEOF ARRIVAL. JOHN NEEDED KEY. I STATED TO JOHN SLOAN TO SHUT OFF VALVES ON FLAT CREEK IN FRONT OF HOUSE AND ON SNOW KING DRIVE TO ISOLATE THE AREA. 2:45 PM. SHERIFF'S OFFICE CALLED-VALVE WAS SHUT OFF AT FLAT CREEK. FIRE DEPARTMENT HAD A STRONG SMELL OF PROPANE AND SMALL FLAME-UPS AS PER KEN SUTTON. 3:00 PM NOTHING TO REPORT FROM KAREN BECKETT, SHERIFF OFFICE DISPATCHER, ON 2-WAY WITH RUSTY PALMER, FIRE INSPECTOR. 3:30 PM. CALLED SHERIFF'S OFFICE. CONTROLLING FIRE. NO CONTACT UNTIL APPROX. 6:00 PM. 6:00PM. JOHN SLOAN-FIRE OUT. GEORGE HUNTER, UTILITY SPECIALIST, ON HIS WAY TO JACKSON FROM KEMMERER.BOB SHERVIN, OF SHERVIN'S EXCAVATION, TO DIG IN ON SNOW KING TO SQEEZE OF A CITY BLOCK OF 4" LINE TO FLAT CREEK VALVE. JOHN STATED HE HAD REAL ESTATE CUT OFF OF FUEL-NEEDED HELP. I HAD FUELED UP AND WAS BACK IN JACKSON BY APPROX. 6:50 AM. 12/24/89. 8:15 AM. 12/24/89-CALLED DEE ANDREWS, ACTING REGIONAL MGR., TO INFORM HIM OF THE FIRE & EXPLOSION IN FLAT CREEK DRIVE. BROUGHT HIM UP TO DATE-NO INJURIES. NO ONE OUT OF SERVICE. 9:05 AM. CALLED BOB MARTIN, SAFETY MAN-SUBURBAN, FRESON, CA. 1-800-669-2600-MR. MARTIN WAS NOT IN AND A MESSAGE WAS LEFT FRO HIM TO RETURN MY CALL. 9:15 AM. DON ROBERTS PUBLIC SERVICE COMMISSION WAS CALLED TO INFORM HIM OF THE PROBLEM-RECEIVER OF MESSAGE STATED DON ROBERTS WAS NOT IN-WILL CALL BACK.
2025-01-31 10:21 | YES | YES | 19910037 | 1991-02-05 | 10037 | K P L GAS SERVICE | 2121 STREET JOHN | KANSAS CITY | JACKSON | MO | 64124 | 3 | NO | 1342 | 1991-01-09 | 0 | 2 | 100000 | 80265.1631 | 193797.6227 | Null | 4 | 18 | 54239 | 19910109 | 1 | 5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 | UNKNOWN | UNKNOWN | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | HANS E. MERTENS, VICE PRESIDENT, ENGINEERING | 8163465575 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | A FIRE AT 2121 ST. JOHN MAY HAVE RESULTED FROM AN IGNITION OF GAS WHICH COULD HAVE MIGRATED FROM A CRACK IN A 4" CAST IRON MAIN IN THIS VICINITY. THE CRECK MAY HAVE BEEN CAUSED BY EARTH MOVEMENT POSSIBLY DUE TO FROST CONDITIONS IN THE SOIL. THE POINT OF INFILTRATION OF GAS INTO LTHE RESIDENCE WAS NOT DETERMINED NOR WAS THE SOURCE OF THE IGNITION.
2025-01-31 10:21 | YES | YES | 19910038 | 1990-10-24 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 3RD & FINDERNE AVENUE | BRIDGEWATER |  | NJ | 08807 | 4 | NO | 500 | 1990-09-21 | 0 | 1 | 100000 | 83128.1566 | 200710.2273 | Null | 2 | 0 | 40199 | 19900921 | 18 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.5 | WW-P421 | INNER-TITE | 1952 | 1952 | UNDER PAVEMENT |  | C.W. GREVENITZ, V.P. - GAS OPERATIONS | 04307797 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | LOCALIZED GRAPHITIC CORR. | NO |  | NO | 0 |  | NO |  |  | ON SEPTEMBER 21, 1990, AT 5:07 AM., A TELEPHONE CALL WAS RECEIVED BY THE COMPANY FROM BRIDGEWATER FIRE COMPANY TO REPORT A GAS LEAK ON FINDERNE AVENUE, BRIDGEWATER, IN THE VICINITY OF 3RD AVENUE. A SERVICEMAN FROM PLAINFIELD DISTRICT WAS DISPATCHED AND ARRIVED ON THE SCENE AT 5:20 AM. A FIRE TRUCK THAT HAD DRIVEN OVER A CATCH BASIN APPARENTLY VENTING GAS, CAUGHT FIRE INJURING THREE FREMEN, ONE OF WHICH REQUIRED HOSPITALIZATION. GAS ON A 12" C.I. MAIN WASTHROTTLED TO 1/4 PSIG WHILE A STREET CREW EXCAVATED TO THE MIN WHICH HAD SEVEN FEET OF COVER. REPAIR OF THE CIRCUMFERENTIAL BREAK WAS COMPLETED BY INSTALLING A FULL SEAL REPAIR CLAMP. THIS MAIN HAS BEEN SCHEDULED TO BE REPLACED IN 1990.
2025-01-31 10:21 | YES | YES | 19910039 | 1991-02-12 | 2652 | COMMONWEALTH GAS CO | 98 ELLIOT STREET | NATICK | MIDDLESEX | MA | 01760 | 1 | NO | 1400 | 1991-01-31 | 0 | 2 | 0 | 0 | 0 | Null | 14 | 19 | 57461 | 19910131 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE BUILDING | OTHER | NONE | OTHER | NONE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRIAN J. HAWKESWORTH - MANAGER OF SAFETY & TRAINING | 5084817900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TWO PERSONS WERE REMOVED FROM THE BUILDING PER ORDER OF THE NATICK FIREDEPARTMENT. BOTH PERSONS WERE ADMITTED AND TESTED FOR CARBON MONOXIDEEXPOSURE AT LEONARD MORSE HOSPITAL, FRAMINGHAM, MA. RESULTS OF THESE TESTSWERE NOT KNOWN AT THE TIME OF THE TELEPNONIC REPORT MADE AT THE EARLIESTPRACTICABLE MOMENT FOLLOWING DISCOVERY. RESULTS WERE NEGATIVE FOR BOTHPERSONS. ALL GAS EQUIPMENT WAS FUNCTIONING PROPERLY.
2025-01-31 10:21 | YES | NO | 19910040 | 1991-02-14 | 11032 | LACLEDE GAS CO | 4324 NORTH TAYLOR | ST LOUIS | ST LOUIS | MO | 63115 | 3 | NO | 1635 | 1991-01-17 | 0 | 0 | 75000 | 60198.8723 | 145348.217 | Null | 4 | 55 | 55476 | 19910117 | 0.26 | 0.34 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.388 | N/A | N/A | 0 | 1949 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER, JR., ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | UNKNOWN | NO |  | NO | 0 |  | NO |  |  | EXTERNAL STRESSES ON A 6 INCH LOW PRESSURE CAST IRON MAIN CAUSED A COMPLETE CIRCUMFERENCE BREAK.
2025-01-31 10:21 | NO | NO | 19910043 | 1991-02-26 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | WEST 38TH STREET & 7TH AVENUE | NEW YORK |  | NY | 10018 | 4 | NO | 2055 | 1991-02-05 | 0 | 0 | 0 | 0 | 0 | YES | 7 | 35 | 58214 |  | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | CAST IRON |  | 20 | 0.75 | N/A | N/A | 0 | 1896 | OTHER | EXCAVATION | THOMAS COWAN - DIVISION MANAGER | 2125762443 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CONSTUCTION CREW PERFORMING GAS MAIN TIE-IN WHEN FIRE ERUPTED IN THE EXCAVATION. THEY WERE MANIFOLDING TWO 4" PIPES FROM A 20" MAIN TO A 6" MAIN WHEN INCIDENT OCCURRED.
2025-01-31 10:21 | NO | NO | 19910044 | 1991-02-15 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 1007 EAST 217TH STREET | BRONX |  | NY | 10466 | 4 | NO | 1556 | 1991-01-06 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 53824 | 19910106 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | APPLIANCE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | RICHARD C. GAULIN - PLANNING ENGINEER | 2124602838 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NO NATURAL GAS INVOLVED.
2025-01-31 10:21 | NO | NO | 19910045 | 1991-02-26 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 1311 LONGDON LANE | MAMARONECK | WESTCHESTER | NY | 10543 | 4 | NO | 1530 | 1991-01-30 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 6 | 0 | 57299 | 19910130 | 15 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | WELD |  | OTHER | UNKNOWN | 6 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS ROGERS - DIVISION MANAGER | 9149256215 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CRACKED WELD ON A 6" MEDIUM PRESSURE STEEL MAIN CAUSED NATURAL GAS TO MIGRATE OVER 300 FEET UNDER THE GROUND AND SEWER SYSTEM. AN EXPLOSION OCCURRED AND THIS HOUSE DUE TO THE BUILD UP OF GAS IN THE HOME.
2025-01-31 10:21 | YES | YES | 19910046 | 1991-02-22 | 8040 | ILLINOIS POWER CO | 123 N. MAIN STREET | CHERRY | BUREAU | IL | 61317 | 3 | NO | 1020 | 1991-01-26 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 | 56803 | 19910128 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE2306/ASTMD251 | PLEXCO | 1976 | 1976 | WITHIN/UNDER BUILDING |  | GLEN E. CARTER, GAS ENGINEER | 2174246853 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-10-02 | YES | 3 | YELLOW PAINT | YES |  |  | ON JANUARY 26, 1991, AT APPROXIMATELY 10:20 AM., AN EXPLOSION AND RESULTING FLASH WAS REPORTED TO THE LOCAL FIRE DEPARTMENT AT 123 N. MAIN STREET IN CHERRY. A SEVEN YEAR OLD BOY, STANDING OUTSIDE OF THE GARAGE INVOLVED, WAS HOSPITALIZED DUE TO BURNS. THE EXPLOSION WAS TERMED "A TYPICAL GAS EXPLOSION" IN THAT THE ROOF AND WALLS BLEW OUT OF THE GARAGE AFTER AN IGNITION SOURCE, CREATED BY THE FATHER OF THE BOY INJURED, WHEN HE TRIED TO START HIS VEHICLE INSIDE THE GARAGE. THE FATHER WAS AT THE IGNITION POINT AND WAS BLOWN CLEAR, WITH MINOR INJURIES NOT REQUIRING HOSPITALIZATION. THE SOURCE OF NATURAL GAS WAS A HOLE WORN IN THE 5/8" PLASTIC SERVICE LINE CAUSED BY A PIECE OF CNCRETE 48" X 30" WHICH WAS IN THE GROUND, LAYING ON THE SERVICE LINE. IT WAS IN THE BACKFILL OF AN EXCAVATION SITE PERFOMRED BY STAR LINE CONSTRUCTION DURING ASEWER PROJECT CROSSING THE SUBJECT SERVICE LINE IN OCTOBER, 1990. SUBSEQUENT SETTLING OF THE SEWER BACKFILL CREATED A FRICTION POINT ON THE SERVICE, THEREBY CREATING A LEAK. NATURAL GAS, EXCAPING FROM THE HOLE, WAS TRAPPED BY FROST CONDITIONS ALLOWING IT TO MIGRATE TOWARD THE GARAGE STRUCTURE DAMAGED ANDVENTING INTO THE STRUCTURE.
2025-01-31 10:21 | YES | NO | 19910047 | 1991-02-26 | 22777 | WISCONSIN NATURAL GAS CO | 1640 NORTH SAWYER ROAD | SUMMIT | WAUKESHA | WI | 53401 | 2 | NO | 445 | 1991-01-24 | 0 | 0 | 65000 | 52172.356 | 125968.4547 | Null | 0 | 25 | 56418 | 19910124 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | API5L | UNKNOWN | 1967 | 1967 | ABOVE GROUND |  | SHELDON B. SEPSTEAD - ATTORNEY | 4146377681 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | WALL AT DWELLING COLLAPSED, DUE TO FIRE, THEREBY BREAKING RISER PIPE UPSTREAM OF METER ASSEMBLY.
2025-01-31 10:21 | YES | NO | 19910050 | 1991-02-25 | 20010 | U G I CORP | 2251 KENSINGTON STREET | HARRISBURG | DAUPHIN | PA | 17104 | 3 | NO | 2145 | 1991-01-26 | 0 | 0 | 225000 | 180596.6169 | 436044.651 | Null | 0 | 30 | 56990 | 19910129 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES R. HEINTZ - DIVISION ENGINEER | 2153715490 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ACCORDING TO THE HARRISBURG BUREAU OF FIRE INCIDENT REPORT, THE LEAK AND SUBSEQUENT IGNITION APPEARED TO ORIGINATE FROMTHE FURNACE TO HOUSE NO.2251 KENSINGTON STREET, HARRISBURG. THERE WAS NO APPARENT INVOLVEMENT WITH UGI FACILITIES AS TO CAUSE. HOWEVER, DURING THE FIRE AFTER THE EXPLOSION, THE SOLDERED METER SEAMS MELTED. THE ESCAPING GAS AT THE METER SET IGNITED AND BURNED UNTIL THE GAS WAS SHUT OFF AT THE CURB VALVE.
2025-01-31 10:21 | YES | YES | 19910051 | 1991-02-25 | 15007 | PACIFIC GAS & ELECTRIC CO | 3589 COLONY LANE | LOOMIS | PLACER | CA | 95650 | 3 | NO | 2004 | 1991-01-31 | 0 | 1 | 75500 | 60600.1981 | 146317.2051 | Null | 0 | 31 | 57636 | 19910131 | 50 | 54 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 | B-175 | ROCKWELL | 1973 | 1974 | OTHER | UNKNOWN | W.R. MAZOTTI, V.P. - GAS & ELEC. TECH. SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE OF UNKNOWN ORIGIN SPREAD TO METER/REGULATOR, ALLOWING GAS TOESCAPE AND IGNITE. ONE THIRD-PARTY INJURY REQUIRED ADMITTANCE TO LOCALHOSPITAL. SUPPLEMENTAL REPORT 8/26/94 INDICATES A REVISION IN INCIDENT CAUSE.STRUCTURE FIRE.
2025-01-31 10:21 | YES | YES | 19910053 | 1991-03-03 | 4350 | ELIZABETHTOWN GAS CO | 2065 SPRINGFIELD AVENUE | UNION | UNION | NJ | 07083 | 4 | NO | 2014 | 1991-02-19 | 0 | 6 | 300000 | 240795.4892 | 581392.868 | Null | 0 | 45 | 60585 | 19910221 | 0.22 | 0.22 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | OTHER | INSIDE OF BUILDING | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DANIEL P. MORRIS, MANAGER, CONSTRUCTION & MAINTENANCE | 9082895000 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | UNDER INVESTIGATION | NO |  | NO | 0 |  | NO |  |  | UNION COUNTY ARSON INVESTIGATION UNIT HAS RULED THE EXPLOSION AS STILL UNDERINVESTIGATION AS OF FEBRUARY 21, 1991.
2025-01-31 10:21 | YES | YES | 19910054 | 1991-03-04 | 17570 | ROCHESTER GAS & ELECTRIC CORP | 110 DELMAR STREET | ROCHESTER | MONROE | NY | 14606 | 3 | NO | 1500 | 1991-02-03 | 0 | 2 | 100000 | 80265.1631 | 193797.6227 | Null | 0 | 13 | 57821 | 19910203 | 0.36 | 0.44 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | N/A | N/A | 1910 | 1910 | UNDER GROUND OR UNDER WATER |  | ROBERT A. ROSS, ASSOCIATE GAS DISTRIBUTION | 7167248465 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CATCH BASIN RECENTLY RECONSTRUCTED IN JULY 1990, WAS DISCOVERED RESTING ON THE CAST IRON MAIN APPROXIMATELY 5' FROM WHERE THE BREAK OCCURRED IN THE MAIN.
2025-01-31 10:21 | YES | YES | 19910055 | 1991-03-05 | 14180 | OHIO VALLEY GAS CORP |  | WINCHESTER | RANDOLPH | IN | 47394 | 3 | NO | 730 | 1991-02-21 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 5 | 60627 | 19910221 | 40 | 0 | BY TEST | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | CUSTOMER PIPING | FITTING |  | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RONALD L. LOYD, CHIEF ENGINEER | 3175845501 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | APPROXIMATELY 7:30 AM., FEBRUARY 21,1991, A 2' GAS LINE BECAME DISCONNECTED,WHICH CAUSED RAW GAS TO GO INTO THE PLANT. THIS WAS IN CONJUCTION WITH HOT WORKS REMOVING BURNERS FROM THE TANK HEAT-UP. TWO ANCHOR GLASS EMPLOYEES, KENNY MCCOY AND JACK PHILLIPS, WERE INJURED. KENNY MCCOY HAS SECOND AND THIRD DEGREE BURNS ON HIS FACE, NECK, SHOULDERS AND BACK. HE ALSO HAS A FRACTURED FOREARM AND DISLOCATED WRIST. HE HAS BEEN TRANSPORTED FROM THE RANDOLPH COUNTY HOSPITAL TO MUNCIE BURN CENTER. JACK PHILLIPS HAS SECOND AND THIRD DEGREEBURNS OVER AREAS OF THE FACE. HE IS REMAINING IN THE RANDOLPH COUNTY HOSPITAL ONE TO TWO DAYS FOR OBSERVATION. THE CAUSE OF THE ACCIDENT POINTS DIRECTLY TO HUMAN ERROR. AT THIS TIME, WE DO NOT KNOW IF THE GAS LINE BECAME DISCONNECTED ON ITS OWN, OR IT IF WAS DISCONNECTED BY PERSONNEL WORKING ON THE TANKPROJECT. IF IT BECAME DISCONNECTED ON ITS OWN, THIS MEANS THE PERSON CONNECTING THE LINE ORIGINALLY, DID NOT USE THE SAFETY FEATURES DESIGNED INTO THE QUICK-DISCONNECT LINE. IF IT WAS DISCONNECTED BY PLANT PERSONNEL, OBVIOUSLY THE WRONG LINE WAS DISCONNECTED. IN UNRELATED MATTERS, YESTERDAY, (2/20/91), WE HAD A FAULTY GAS VALVE BLOW. THIS WAS REMEDIED IMMEDIATELY BY SHUTTING OFF ALL GAS TO FURNACES. THIS INCIDENT IS TOTALLY SEPARATE FROM THE ACCIDENT OCCURRING THIS MORNING. IN CONJUCTION WITH THE START-UP OF THE FURNACE, IT ISIMPORTANT TO KNOW THAT WE SOLICITED THE HELP OF OHIO VALLEY GAS CORPORATION TO COME IN WITH "GAS SNIFFERS" TO MAKE SURE ALL GAS LINES, WELDS, AND CONNECTIONS WERE LEAK-FREE. THE AETNA INSURANCE AGENCY ARE SENDING INVESTIGATORS TOTHE PLANT TODAY TO SATISFY ANY SAFETY QUESTIONS THAT THEY MAY HAVE. THE ACCIDENT THIS MORNING WAS VERY UNFORTUNATE, TO SAY THE LEAST, AND WE WILL KEEP ON-SITE WORKERS INFORMED AS TO KENNY AND JACK'S CONDITION. ANYONE WHO WISHESTO DISCUSS THIS OR ANY OTHER SAFETY CONCERN MAY FEEL FREE TO CONTACT MY OFFICE AT ANY TIME.
2025-01-31 10:21 | YES | YES | 19910059 | 1991-03-13 | 18496 | SOUTHERN CONNECTICUT GAS CO | 74 DWIGHT STREET | NEW HAVEN | NEW HAVEN | CT | 06511 | 3 | NO | 1357 | 1991-02-06 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 | 58506 | 19910207 | 0.25 | 0.65 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 |  |  | 0 | 1903 | UNDER PAVEMENT |  | AMOS F. BARNES, MANAGER=MAINS & SERVICES. | 2037866206 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-08-14 | YES | 3 | PAINTED ON ROAD | YES |  |  | ON JANUARY 17, 1991, WHILE ON ROUTINE LEAK SURVEY, A MAIN BREAK WAS DETECTEDADJACENT TO A NEWLY INSTALLED MANHOLE NEAR 74 DWIGHT STREET, NEW HAVEN. THESPREAD OF THE GAS LEAK WAS APPROXIMATELY 100 FT. IN EACH DIRECTION, WITHIN THE STREET, FROM THE BREAK. A CREW WAS DISPATCHED WHO FOUND A CIRCUMFERENTIALCRACK IN THE SIX INCH CAST IRON LOW PRESSURE MAIN ADJACENT TO THE MANHOLE. THE CREW INSTALLED A REPAIR SLEEVE, BACKFILLED AND TERMPORARILY PATCHED THE DITCH. SUBSEQUENT SURVEYS OF THE AREA SHOWED RESIDUAL GAS PRESENT BUT DIMINISHING AS TIME WENT ON. CAUSED OF THE BREAK WAS ATTRIBUTED TO IMPROPER COMPACTION OF THE BACKFILL MATERIAL DURING THE MANHOLE INSTALLATION. ON FEBRUARY 6,1991, AT APPROXIMATELY 1:30 PM. A CONTRACTOR ENTERED THE MANHOLE ON DWIGHT STREET TO INSPECT FOR THE PRESENCE OF WATER. ACCORDING THE WITNESSES, HE MAY HAVE LIT A BUTANE LIGHTER WHILE IN THE MANHOLE TO EITHER CHECK FOR ADEQUATE OXYGEN LEVELS OR TO SEE IF THERE WAS WATER IN THE MANHOLE. THERE WAS A FLASH AND THE CONTRACTOR WAS BURNED ON HIS HANDS AND FACE. A SECOND CONTRACTOR WASALSO BURNED ON THEHAND IN HELPING THE FIRST MAN OUT OF THE MANHOLE. BOTH MEN WENT TO THE HOSPITAL FOR TREATMENT. THE FIRST MAN WAS ADMITTED AND THE SECOND WAS TREATED AND RELEASED. THE NEW HAVEN FIRE DEPARTMENT NOTIFIED US AT 1:57 PM. AND WE DISPATCHED A SERVICE TECHNICIAN AND TWO SUPERVISORS. THE MANHOLE WAS CHECKED FOR THE PRESENCE OF GAS WITH A 10% READING RECORDED ON LEL SCALE. HIGHER LEVELS OF GAS WERE FOUND UNDER THE EMPORARY PATCH ADJACENT TO THE MANHOLE. A STREET CREW WAS DISPATCHED AND RECHECKED THE AREA ADJACENT TO THE MANHOLE. THE CREW BEGAN AERATING THE SOIL IN THE AREA REDUCING RESIDUAL GAS CONCENTRATIONS TO ACCEPTABLE LEVELS. WE CONTINUE TO KEEP THE AREA UNDER SURVEILLANCE. WE HAVE CONCLUDED THAT THERE IS NO SECONDARY SOURCE OF GAS AND THAT ALL TRACES OF GAS WILL DISSIPATE SHORTLY.
2025-01-31 10:21 | YES | YES | 19910061 | 1991-03-08 | 22777 | WISCONSIN NATURAL GAS CO | 6747 CROCUS COURT | GREENDALE | MILWAUKEE | WI | 53129 | 3 | NO | 758 | 1991-02-05 | 3 | 6 | 200000 | 160530.3261 | 387595.2454 | Null | 0 | 41 | 58059 | 19910205 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | 3/4" X 12" NIPPLE | STEEL |  | 0.75 | 0.154 | API5L | N/A | 1958 | 1958 | UNDER GROUND OR UNDER WATER |  | SHELDON B. SEPSTEAD, ATTORNEY | 4146377681 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-01-31 | YES | 3 | PLAG MARKERS AND PAINT | YES |  |  | THE LOCATION OF SERVICE LINE WAS REASONABLY MARKED AT THE TIME OF THE INCIDENT.
2025-01-31 10:21 | NO | NO | 19910065 | 1991-03-19 | 15350 | PEOPLES NATURAL GAS CO | RD. 3, BOX 1720, ROUTE 56 | HOMER CITY | INDIANA | PA | 15748 | 2 | NO | 1005 | 1991-02-14 | 0 | 0 | 60000 | 48159.0978 | 116278.5736 | Null | 0 | 35 | 59766 | 19910215 | 28 | 30 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | STEEL |  | 1.25 | 0.191 |  |  | 0 | 0 | ABOVE GROUND |  | HORACE P. PAYNE, JR., SENIOR ATTORNEY | 4124976889 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ED HERNANDEZ'S CAR LEFT THE HIGHWAY AND SHEARED OFF THE NATURAL GAS METER AGAINST THE GEORGE HOME, STARTING A FIRE THAT DESTROYED THE RESIDENCE.
2025-01-31 10:21 | YES | NO | 19910067 | 1991-03-19 | 20010 | U G I CORP | 310/312/314/316 N. WATER STREET | LITITZ | LANCASTER | PA | 17543 | 3 | NO | 1010 | 1991-02-19 | 0 | 0 | 500000 | 401325.8153 | 968988.1134 | Null | 1 | 1 | 60196 | 19910219 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | JAMES R. HEINTZ - DIVISION ENGINEER | 2153715490 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-11-27 | YES | 3 | PAINTING STREET | YES |  |  | AT 1011 HOURS ON FEBRUARY 19, 1991 UGI RECEIVED NOTIFICATION VIA TELEPHONE THROUGH ITS CUSTOMER INFORMATION CENTER THAT A CONTRACTOR HAD HIT A GAL LINE AT 314-316 N. WATER STREET IN LITITZ BOROUGH. TWO UGI EMPLOYEES RESPONDED, VENTILATED ONE DUPLEX TYPE HOUSE (314-316 N. WATER STREET) IGNITED AND THE RESULTING FIRE AND EXPLOSION COMPLETELY DESTROYED THE BUILDING. THE HOUSE AT 310-312 N. WATER STRET AND WAS HEAVILY DAMAGED. THE GAS MAIN SERVING THIS STREET WAS SHUT DOWN BY CLOSING TWO VALVES AT 1111 HOURS. NO INJURIES OCCURRED AND ONE RESIDENT AT 316 N. WATER STREET WAS EVACUATED.
2025-01-31 10:21 | YES | NO | 19910068 | 1991-04-09 | 6141 | GAS CO OF NEW MEXICO | 1111 AMHERST DRIVE SE. | ALBUQUERQUE | BERNALILLO | NM | 87108 | 3 | NO | 1416 | 1991-02-02 | 0 | 0 | 100000 | 80265.1631 | 193797.6227 | Null | 0 | 42 | 57882 | 19910204 | 57 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | SCHD 40 | UNKNOWN | 0 | 1977 | ABOVE GROUND |  | STEVEN C. EMRICK - CHIEF ENGINEER | 5058807903 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ON SATURDAY, FEBRUARY 2, 1991, THE ALBUQUERQUE FIRE DEPARTMENT (APD) CALLED THE GAS COMPANY OF NEW MEXICO (GCNM) DISPATCH OFFICE AT 2:16 PM TO REPORT A CAR HIT METER WITH A BLOWING GAS LINE AT 1111 AMHERST SE. THE AFD REQUESTED GCNM'S ASSISTANCE. GENERAL SERVICE TECHNICIAN, RICHARD SILVA, ARRIVED AT THE SCENE AT 2:21 PM AND REPORTED THAT A CAR WAS ON TOP OF A BLOWING LINE. HE THEN REPORTED THAT THE BLOWING GAS HAD IGNITED. RICHARD REQUESTED ASSISTANCE FROMTHE GCNM CONSTRUCTION & MAINTENANCE (C&M) DEPARTMENT. SERVICE SUPERVISOR JOHN HIGGINS ARRIVED AT 2:54 PM AND STARTED HIS INVESTIGATION. ALBUQUERQUE POLICE DEPARTMENT (APD) INVESTIGATIVE OFFICE, L.J. CAMPBELL OFFERED THE FOLLOWING STROY: 2 INDIVIDUALS WERE DRIVING EAST ON THAXTON AND TURNED INTO THE PARKING LOT FOR THE APARTMENT AT 1111 AMHERST SE. THE CAR ENTERED THE PARKING LOT AND EVENTUALLY RAN THROUGH A BARRICADE AND INTO A 4 METER HEADER. THE IMPACT BROKE THE PIPE OFF ABOVE THE MAIN STOP COCK, ALLOWING GAS TO BLOW UNDER THE CAR AND INTO A HOLE IN THE APARTMENT WALL WHICH WAS CAUSED BY THE IMPACT. THE TWO OCCUPANTS OF THE VEHICAL FLED THE SCENE ON FOOT AND HAVE NOT BEEN IDENTIFIED. THE VEHICLE WAS A SILVER 1976 CHEVROLET NOVA - LICENSE: NM LDK 845, OWNED BY ABEL MADERIZ, 222 CANNON SW. THEIS APARTMENT COMPLEX CONSISTS OFTHREE BUILDING. THE AFFECTED BUILDING WAS TOTALLY DESTROYED ALONG WITH MOSTOF ITS CONTENTS. THE DESTROYED BUILDING CONSISTED OF APARTMENTS 1, 2, 3, 4,23, 24, 25, 26 AND A STORAGE ROOM WHICH CONTAINED A WATER HEATER WHICH SERVED THE ENTIRE BUILDING AND 20 APARTMENTS IN AN ADJOINING BUILDING. ALSO DAMAGED IN THIS INCIDENT WERE TWO VEHICLES WHICH WERE PARKED FACING THE BUILDING NEXT TO THE DAMAGED METER STATION. THE FIRST VEHICLE WAS A BROWN GMC PICK-UP,LICENSE: NM LA 3976, RECEIVED DAMAGE TO THE HOOD, LEFT AND RIGHT FRONT FENDERS, CRACKED WINDSHIELD, BROKEN DRIVER'S WINDOW, SOME INTERIOR WATER DAMAGED AND A BROKEN OUTSIDE MIRROR ON THE DRIVER'S SIDE. THE SECOND VEHICLE WAS AN OFF RED TOYOTA PICK-UP, LICENSE: NM LH 4025. IT RECEIVED EXTENSION DAMAGE TOTHE LEFT SIDE, CAB TOP CAVED IN, ENTIRE HOOD DAMAGED, HOOD FRONT AND RIGHT FRONT FENDER BURNED, AMBER LIGHT LENS RIGHT FRONT SIDE BURNED AND HEAT DAMAGEDAT THE BASE OF THE WINDSHIELD. MOST OF THE ABOVE VEHICLE DAMAGE WAS CAUSED BY FALLING DEBRIS. THE OFFICE COMPLEX IS MANAGED BY THE HINES CORPORATION, 12800 LOMAS NE, PHONE: 298-4444. THE MANAGER IS MARY ANN STENER. THE RESIDENT MANAGER WAS MARIE SANCHEZ, WHO RESIDES IN APARTMENT 4. THE ALBUQUERQUE FIRE DEPARTMENT (AFD) OFFICER IN CHARGE OF THE FIRE WAS LANDJUR ABURUSUMU OF STATION NO. 4, 301 MCKNIGHT NW. GAS COMPANY OF NEW MEXICO C & M CREW PROBED UNDER GROUND, WITH THE USE OF A COMBUSTIBLE GAS INDICATOR, TO DETECT ANY POSSIBLE GAS LEAKAGE. THE PROBE WAS TAKEN AROUND THE PERIMETER OF THE ENTIRE APARTMENT COMPLEX AND ACROSS THE STREET ON AMHERST AND ACROSS THE STREET ON THAXTON. NO UNDERGROUND LEAKAGE WAS PRESENT IN THE ENTIRE PROBE. THE C & M CREW THEN CUT AND CAPPED THE SERVICE LINE, TO THE AFFECTED BUILDING, AT THE PROPERTY LINE ON THE NORTH SIDE OF THAXTON. ALL NINE GAS METERS WERE REMOVED. METER INFORMATION FOR THE NINE METERS: METER NO. 0104644, 175C SPRAQUE, READ 4741, LAUNDRY ROOM; METER NO. 3931196, 240 SPRAGUE, READ 1341, 1111 AMHERST SE, APT. 1; METER NO. 4756732, AL175 AMERICAN, INDEX BURNED - NO READING, 1111 AMHERST SE, APT. 4; METER NO 4756731, AL175 AMERICAN, INDEX BURNED - NO READING, 1111 AMHERST SE, APT. 3; METER NO. 2918847, 1A SPRAGUE, READ 8774, 1111 AMHERST SE, APT. 24; METER NO. 0897426, AL175 AMERICAN, READ 1558, 1111 AMHERST SE, APT. 23; METER NO. 2312467, 5B METRIC, READ 1889, 1111 AMHERST SE, APT. 2: METER NO. 6004854, 1A SPRAGUE, INDEX BURNED - NO READING, 1111 AMHERST SE, APT, 25; METER NO. 0405890, AC250 AMERICAN, INDEX BURNED - NO READING, 1111 AMHERST SE, APT 26.
2025-01-31 10:21 | YES | YES | 19910069 | 1991-03-26 | 15359 | PEOPLES NATURAL GAS | SW/4 SEC. 28, T8S, R43W |  | KIT CARSON | CO |  | 1 | NO | 1630 | 1991-03-14 | 0 | 1 | 100000 | 80265.1631 | 193797.6227 | Null | 0 | 20 | 63566 | 19910314 | 350 | 500 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0.125 | N/A | N/A | 0 | 1962 | UNDER GROUND OR UNDER WATER |  | GREGORY J. BENAK, ATTORNEY | 4022212021 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | FARMER OPERATING EXCAVATING EQUIPMENT STRUCK LINE WITHOUT FIRST MAKING LINE LOCATE REQUEST.
2025-01-31 10:21 | YES | YES | 19910073 | 1991-04-16 | 13840 | NORTHWEST NATURAL GAS CO | 19625 S.E. MCLOUGHLIN BLVD | GLADSTONE | CLACKAMAS | OR | 97027 | 3 | NO | 2142 | 1991-03-20 | 0 | 2 | 0 | 0 | 0 | Null | 3 | 33 | 64489 | 19910321 | 35 | 57 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API 5L-A25 | UNKNOWN | 1982 | 1982 | WITHIN/UNDER BUILDING |  | J.F. ERSPAMER, STAFF ENGINEER | 5032264211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR DOING ENVIRONMENTAL DRILLING TO TEST FOR GASOLINE CONTAMINATION OF SOIL STRUCK AN INACTIVE CURB SERVICE ON RIVER ROAD AT THE REAR OF 19625 MCLOUGHLIN. CONTRACTOR PERSONNEL STATED THAT THEY SMELLED GAS, BUT THOUGHT THATGASOLINE VAPORS WERE COMING FROM THE SOIL. TWO EMPLOYEES OF THE AUTO AGENCYAT 19505 MCLOUGHLIN ENTERED THE BUILDING AT 19625 ABOUT 9PM. AN EXPLOSION AND FIRE FROM AN UNDETERMINED IGNITION SOURCE OCCURRED ALMOST IMMEDIATELY. BOTH MEN WERE HOSPITALIZED WITH BURNS. A COMPANY SUPERVISOR ARRIVED AT 10:05 PM. AND THE FIRE WAS CONTROLLED BY 10:55 PM. A COMPANY CREW ARRIVED AT 11:15. GAS FLOW WAS STOPPED AT 12:30 AM, AND THE AREA WAS MADE SAFE (INCLUDING VENTING) AT 1:15 AM.
2025-01-31 10:21 | NO | NO | 19910075 | 1991-04-18 | 18440 | SOUTH JERSEY GAS CO | UNITED STATE AVENUE & RT. 561 | GIBBSBORO | CAMDEN | NJ | 08026 | 3 | NO | 1430 | 1991-04-02 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 | 66237 | 19910402 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D1248 | DUPONT | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | THOMAS F. BONNER, VICE PRES., DISTRIBUTION OPERATION | 6095619000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-01-23 | YES | 3 | YELLOW PAINT ON STREET | YES |  |  | ON APRIL 2, 1991, AT APPROXIMATELY 14:30 HOURS, SOUTH JERSEY GAS COMPANY RECEIVED A CALL FROM A CONTRACTOR REPORTING THAT A GAS MAIN HAD BEEN STRUCK AND WAS BLOWING. A SERVICEMAN WAS DISPATCHED AT 14:33 HOURS. HE ARRIVED AT 14:45 HOURS AND REQUESTED A STREET CREW AND REPORTED THAT THE MAIN WAS ON FIRE. POLICE AND FIRE PERSONNEL ALSO ARRIVED AT THE LOCATION. TWO STREET CREWS ARRIVED AT 15:05 HOURS. THE STREET CREWS, WITH THE ASSISTANCE OF THE CONTRACTOR, MADE AN OPENING UPSTREAM OF THE STRUCK MAIN, SQUEEZED OFF AND THE AREA WAS MADE SAFE AT 15:15 HOURS. THE STREET CREWS INTERRUPTED WAS RESTORED AT 18:45HOURS THE SAME DAY. THERE WAS NO INJURIES OR PROPERTY DAMAGE. AN INVESTIGATION REVEALED THE FOLLOWING INFORMATION. A CONTRACTOR WAS INSTALLING A SEWERLATERAL LOCATION INFORMATION BY THE FOREMAN OF ANOTHER CREW WHO INSTALLED THE MAIN SEWER LINE. ORIGINALLY, THE STREET WAS MARKED OUT SHOWING THE LOCATION OF THE 2" PLASTIC GAS MAIN WHEN THE SEWER MAIN WAS INSTALLED, BUT NO MARKS WERE VISIBLE TO THE CREW INSTALLING THE LATERALS DUE TO THE EXTENSIVE WORK DONE WHEN INSTALLING THE SEWER MAIN. THE CONTRACTOR DID NOT CALL FOR NEW MARKOUTS. WHEN THE GAS MAIN WA STRUCK, THE FOREMAN FOR THE CONTRACTOR CLEARED THEAREA OF PERSONNEL AND EQUIPMENT AND NOTIFIED SOUTH JERSEY GAS COMPANY OF THEDAMAGE. APPROXIMATELY 5 TO 10 MINUTES LATER, THE 2" PLASTIC GAS MAIN IGNITE
2025-01-31 10:21 | NO | NO | 19910076 | 1991-04-18 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 1301-03 S. SARATOGA | NEW ORLEANS | ORLEANS | LA | 70112 | 3 | NO | 321 | 1991-03-13 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 | 63377 |  | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.145 | UNKNOWN | UNKNOWN | 0 | 1917 | WITHIN/UNDER BUILDING |  | PERRY J. DUFRENE/ SUPERVISOR GAS MAINTENANCE | 5045953582 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | AN EXPLOSION AND FIRE OCCURRED AT 1301-03 S. SARATOGA DESTROYING THE BUILDING AND DAMAGED THE SERVICE RISER BELOW THE VALVE. THE SERVICE WAS IGNITED BY THE FIRE AND WAS CUT-OFF AT THE MAIN. THE EXPLOSION WAS INVESTIGATED BY AF&TAND ARSON DIVISION OF NEW ORLEANS FIRE DEPT., IT WAS DETERMINED THAT GASOLINE WAS THE CAUSE OF THE EXPLOSION. TWO INDIVIDUALS HAVE BEEN CHARGED WITH THECASE.
2025-01-31 10:21 | YES | NO | 19910077 | 1991-04-08 | 792 | ATLANTA GAS LIGHT CO | 1224 WESTMONT ROAD | ATLANTA | FULTON | GA | 30302 | 3 | NO | 1346 | 1991-03-01 | 0 | 0 | 65000 | 52172.356 | 125968.4547 | Null | 0 | 14 | 61740 | 19910301 | 30 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | C.J. SPINKS - DIVISION DISTRIBUTION MANAGER | 4045844470 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 1:46 PM. ON 3/1/91, ATLANTA GAS LIGHT'S SERVICE DISPATCH OFFICE NOTIFIED ATLANTA DISTRIBUTION DISPATCH OF AN EXPLOSION AT 1224 WESTMONT ROAD. UPON ARRIVING AT THE SCENE ATLANTA GAS LIGHT COMPANY WAS UNABLE TO COMPLETELY SURVEYTHE GAS FACILITIES DUE TO DEBRIES AND THE PRESENCE OF FIRE DEPARTMENT EQUIPMENT. WHILE USING A FRON-END LOADER TO SEARCH FOR POSSIBLE INJURED OCCUPANTS,THE FIRE DEPARTMENT SEVERED THE GAS LINE RISER AT THE GROUND LEVEL AND DESTROYED MUCH OF THE REMAINING SECTIONS OF THE HOUSE. THIS IMPAIRED ATLANTA GAS IGHT COMPANY'S ABILITY TO THOROUGHLY INVESTIGATE AND DETERMINE THE POSSIBLE CAUSE OF THE EXPLOSION. ON 3/1/91 A CHECK FOR GAS IN THE GROUND OVER THE AMIN, IN SEWER MAINHOLES AND IN THE WATER METER BOX WAS PERFORMED. NO GAS WAS DETECTED IN ANY OF THESE LOCATIONS. UPON FURTHER INVESTIGATION CONDUCTED ON 3/4/91 A SMALL LEAK ON HE UNDERGROUND SERVICE PIPE, NEAR THE RISER, WAS DETECTED. BECAUSE UNIDENTIFIED PERSONS WERE SEEN LEAVING THE BUILDING THE DAY BEFORE THE EXPLOSION, THERE IS SOME SUSPICIOUS THAT THE EXPLOSION RESULTED FROM A FUEL LINE LEAK IN THE LOWER APARTMENT. THE EXACT SOURCE OF THE LEAK CAUSING THE EXPLOSION CAN NOT BE DETERMINED AT THIS TIME.
2025-01-31 10:21 | YES | YES | 19910078 | 1991-04-08 | 4499 | ENTEX - DIVISION OF ARKLA INC | 7502 FM ROAD 646 | SANTA FE | GALVESTON | TX |  | 3 | NO | 1000 | 1991-03-25 | 1 | 0 | 150 | 120.3977 | 290.6964 | Null | 0 | 50 | 65117 | 19910325 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTMD-2513 | DUPONT, ALDYL A | 0 | 1973 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE, P.E., OPERATIONS ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-03-15 | YES | 3 | YELLOW PAINT & FLAGS | NO |  |  | A HOUSTON LIGHTING AND POWER COMPANY CONSTRUCTION CREW CUT A 3/4" PLASTIC NATURAL GAS SERVICE LINE WHILE INSTALLING AN ELECTRIC POWER POLE. AN ENTEX EMPLOYEE ATTEMPTING TO REPAIR THE LINE WAS OVERCOME BY GAS AND LOST CONSCIOUSNESS. THE EMPLOYEE WAS HOSPITALIZED IN CRITICAL CONDITION.
2025-01-31 10:21 | YES | NO | 19910080 | 1991-04-22 | 1088 | BALTIMORE GAS & ELECTRIC CO | 422 HASKELL ROAD | ARNOLD |  | MD |  | 2 | NO | 755 | 1991-04-03 | 0 | 0 | 125000 | 100331.4538 | 242247.0283 | Null | 1 | 25 | 66368 | 19910403 | 99 | 99 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.375 | 0.062 | ASD2513 | UNKNOWN | 1981 | 1982 | OTHER | EXPOSED 3/8" PLASTIC SVC. | DENNIS BLESSING - OPERATIONS ANALYST | 3015612779 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | YES | 1990-03-01 | YES | 3 | PAINTED | NO |  |  | AT APPROXIMATELY 0715 ON APRIL 3, 1991, MR. HART LIT A KEROSINE HEATER. TO WARM HOUSE. HEATER CAUGHT FIRE AND DESTROYED UNFINISHED ADDITION TO HOUSE. DURING THE FIRE SOMETHING FELL ON METER AND INSTALLATION AND GAS SERVICE, SEVERING 3/8" PLASTIC SERVICE. PLASTIC SERVICE THEN IGNITED AND BURNT FOR APPROXIMATELY 1 HOURS AND 25 MINUTES UNTIL GAS DISTRIBUTION WAS ABLE TO DIG A BELLHOLE TO CUT SERVICE OFF.
2025-01-31 10:21 | NO | NO | 19910081 | 1991-06-11 | 5200 | FITCHBURG GAS & ELECTRIC LIGHT CO | BEMIS ROAD BRIDGE APPROACH | FITCHBURG | WORCESTER | MA | 01420 | 2 | NO | 920 | 1991-05-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 | 72370 | 19910517 | 90 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | COUPLING | STEEL |  | 6 | 0.28 | A106 |  | 1980 | 1980 | ABOVE GROUND |  | BERNARD B. WOOD, SR. GAS ENGINEER | 5083436931 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-01 | YES | 3 | EXPOSED PIPE STUB | YES |  |  | CONTRACTOR HIT EXPOSED PIPE STUB.
2025-01-31 10:21 | YES | YES | 19910082 | 1991-06-11 | 13782 | NORTHERN STATES POWER CO | 1320 NILES AVENUE | ST. PAUL | RAMSEY | MN | 55116 | 3 | NO | 1645 | 1991-05-07 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 | 71200 | 19910508 | 0 | 0 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | CUSTOMER FURNACE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | NICK J. BOOSALIS, SENIOR GAS ENGINEER | 6122292317 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PART 3 (DESCRIPTION): A CONTRACT EMPLOYEE, WHILE ATTEMPTING TO RELIGHT AN OLD STYLE ("OCTOPUS TYPE") GRAVITY FURNACE, RECEIVED FIRST-DEGREE BURNS TO FACE AND SECOND-DEGREE BURNS TO ONE HAND. THE INJURED EMPLOYEE MISTAKENLY PRESSED THE MANUAL BUTTON WHICH OPENED THE MAIN GAS VALVE TO BURNER INSTEAD OF PRESSING THE MANUAL BUTTON WHICH ALLOWS GAS TO FLOW TO PILOT ONLY. NATURAL GAS,FROM THE BURNER, IGNITED WHILE EMPLOYEE'S HEAD AND HAND WERE WITHIN THE FURNACE.
2025-01-31 10:21 | YES | NO | 19910084 | 1991-05-13 | 15259 | PENNSYLVANIA GAS & WATER CO | 1003 SHOEMAKER AVENUE | WEST WYOMING | LUZERNE | PA | 18644 | 3 | NO | 1659 | 1991-04-24 | 0 | 0 | 250000 | 200662.9077 | 484494.0567 | Null | 1 | 46 | 69382 | 19910424 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | THREAD | STEEL |  | 2 | 0.154 | ASP-B36.10 | UNKNOWN | 0 | 1935 | UNDER PAVEMENT |  | JAMES M. GREGER, MANAGER SPECIAL PROGRAMS | 7178298866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-09-05 | YES | 3 | PAINT | YES
2025-01-31 10:21 | YES | NO | 19910085 | 1991-05-10 | 13840 | NORTHWEST NATURAL GAS CO | 11001 S.E. MAIN | PORTLAND | MULTNOMAH | OR | 97216 | 3 | NO | 1340 | 1991-04-11 | 0 | 0 | 100000 | 80265.1631 | 193797.6227 | Null | 0 | 55 | 67655 | 19910411 | 40 | 57 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING | DRESSER TEE | STEEL |  | 0.75 | 0.113 | API 5L-A25 | UNKNOWN | 1960 | 1960 | UNDER GROUND OR UNDER WATER |  | J.F. ERSPAMER, STAFF ENGINEER | 5032264211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | UNKNOWN | YES |  |  | PART 2a&b MARKING AND MONITORING IS ONGOING AND FREQUENT BY THE GAS COMPANYFOR THIS MAJOR SEWER PROJECT. THE SERVICE WAS EXPOSED SATISFACTORILY DURING EXCAVATION AND APPARENTLY WAS DAMAGED IN THE BACKFILL PROCESS. SEWER CONTRACTOR PULLED THE SERVICE TO 11006 S.E. MAIN, AND SHORTLY AFTER THE RESIDENCE AT11001 S.E. MAIN (ACROSS THE STREET) EXPERIENCED EXPLOSION AND FIRE. THE HOME WAS UNOCCUPIED AT THE TIME. HOMEOWNER HAD MADE AN ODOR COMPLAINT AT 1321 HOURS, BUT THE INCIDENT OCCURRED BEFORE THE LEAKAGE INVESTIGATOR ARRIVED. THE GAS WAS VENTING UPWARD FREELY AND HARMLESSLY BY 2:35 PM, AND THE FLOW WAS STOPPED AT 2:55 PM.
2025-01-31 10:21 | NO | NO | 19910087 | 1991-06-04 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | WEST 76TH STREET & COLUMBUS AVENUE | NEW YORK |  | NY | 10023 | 4 | NO | 1650 | 1991-03-30 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 55 | 71299 |  | 60 | 99 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | VALVE |  | CAST IRON |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | THOMAS COWAN - DIVISION MANAGER | 2125762443 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS BLOWING FROM 1" CONTROL LINE FOR REGULATOR STATION. STRONG ODOR OF GASIN AREA. FIRE DEPARTMENT EVACUATES BUILDING AND CLOSES OFF COLUMBUS AVENUE TO TRAFFIC.
2025-01-31 10:21 | NO | NO | 19910088 | 1991-06-12 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | IL S. HIGHWAY 65 SOUTH | DERMOTT | CHICOT | AR | 71638 | 1 | NO | 1330 | 1991-05-04 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19910504 | 45 | 300 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | JOINT | WELD | STEEL |  | 6.62 | 0.188 | SLX,X42,ERW,PE | TEXTUBE | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | JIM BREWER - CODES & PROCEDURES COORDINATOR | 5013774771 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | Very heavy rain-fall this year caused the bayou to remain at a high level for a long time. high water washed away the pipe cover at the bank, letting the pipe move and causing the failure.
2025-01-31 10:21 | NO | NO | 19910091 | 1991-06-12 | 6141 | GAS CO OF NEW MEXICO | 103 CALLE LA PENA(809 ABEYTA STREET) | SANTA FE | SANTA FE | NM | 87504 | 3 | NO | 1718 | 1991-05-03 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 2 | 13 | 70742 | 19910503 | 55 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | THREAD | STEEL |  | 1.25 | 0.131 | GRADE A-25 | N/A | 0 | 1967 | ABOVE GROUND |  | CAMPBELL MCMORDIE | 5058807182 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-04-25 | YES | 3 | YELLOW PAINT/ROOSTER TAIL | YES
2025-01-31 10:21 | YES | YES | 19910092 | 1991-06-12 | 1640 | BOSTON GAS CO | 497 COLUMBIA ROAD | DORCHESTER | SUFFOLK | MA |  | 3 | NO | 1621 | 1991-05-20 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 | 72707 | 19910520 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | CAST IRON |  | 4 | 0 |  |  | 0 | 1899 | OTHER | STREET EXCAVATION | JOHN J. BARBUTO, ASSISTANT SUPERINTENDENT | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEE WAS THREADING SERVICE TEE INTO 4" C.I. MAIN WHEN GAS ESCAPIING FROMTAP HOLE IGNITED. EMPLOYEE EXITED OPENING WITH ASSISTANCE FROM CREW MEMBERS. HE WAS BURNED ON BOTH HIS ARMS AND FACE. FIRE WAS EXTINGUISHED APPROXIMATELY 5 MINUTES AFTER IGNITION AND THE TAP HOLE WAS SECURED. SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | YES | YES | 19910093 | 1991-06-12 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 265 WOODLAWN AVENUE | HOT SPRINGS | GARLAND | AR | 71901 | 3 | NO | 1125 | 1991-05-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 | 71228 | 19910508 | 22 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.11 | PE2406 | PLEXCO | 0 | 1991 | OTHER | BELL HOLE | JIM BREWER - CODES & PROCEDURES COORDINATOR | 5013774771 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WE HAD JUST INSERTED THE 2" STEEL GAS MAIN WITH 1 1/4" PLASTIC PIPE. A 1/2"E11 HAD BEEN FUSED TO A SERVICE "T" ON THE MAIN TO TIE IN THE LAST SERVICE.THE SERVICE MEN WERE WAITING FOR THE LAST FUSION TO COOL, BEFORE TYING IN THE 1/2" PLASTIC SERVICE. THERE WAS A FLASH FIRE AND TWO EMPLOYEES RECEIVED BURNS. NO GAS HAD BEEN INTRODUCED TO THE NEW SYSTEM AT THE TIME. SOURCE OF GASAND CAUSE OF IGNITION HAS NOT BEEN DETERMINED.
2025-01-31 10:21 | YES | YES | 19910096 | 1991-06-17 | 4483 | ENSTAR NATURAL GAS CO | 7231 CLAIRBORNE CIRCLE | ANCHORAGE |  | AK | 99502 | 3 | NO | 504 | 1991-05-21 | 1 | 0 | 60000 | 48159.0978 | 116278.5736 | Null | 1 | 30 | 72544 | 19910521 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | ALUMINUM METER SET | 0.5 | 0.09 | DRISCOPIPE | PHILLIPS | 1982 | 1983 | OTHER | SIDE OF BUILDING | DREW SMITH - SENIOR ENGINEER | 9072643744 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | RESIDENTIAL STRUCTURE FIRE MELTED THE GAS METER AND REGULATOR. PRELIMINARY FIRE INVESTIGATION DETERMINED THE FIRE STARTED INSIDE THE STRUCTURE FROM A BURNING CIGARETTE IN THE CARPET OR FURNITURE.
2025-01-31 10:21 | NO | NO | 19910097 | 1991-06-21 | 22182 | WASHINGTON GAS LIGHT CO | INTER./ MARY'S WAY & JEFFERSON DAVIS HWY | WOODBRIDGE | PRINCE WILLIAM | VA | 22191 | 3 | NO | 1038 | 1991-05-30 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 1 | 13 |  | 19910530 | 20 | 24 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.118 | API 5L X42 |  | 0 | 1964 | UNDER GROUND OR UNDER WATER |  | CLARENCE E. GOODSON III - SENIOR SFAETY SPECIALIST | 7037504584 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-03-08 | YES | 3 | PAINTED | YES |  |  | SHORTLY BEFORE 1038 HOURS ON MAY 30, 1991, THE K&M ROAD BORING COMPANY STRUCK A 6" WRAPPED STEEL H.P. GAS MAIN PUSHING IT OUT OF A STRIPPED COMPRESSION COUPLING UNDERGROUND. WGL PERSONNEL RESPONDED AND FOUND ZERO PRESSURE READINGS DOWNSTREAM OF THE BREAK. THE MAIN CONTROL VALVE WAS CLOSED, POSITIVELY DISCONTINUING SERVICE TO 1,200 CUSTOMERS. THE MAIN WAS REPAIRED, PRESSURE RESTORED, AND RELIGHTING PROCEDURES STARTED ON MAY 30, 1991.
2025-01-31 10:21 | YES | YES | 19910098 | 1991-06-18 | 13850 | NORTHWESTERN PUBLIC SERVICE CO | 308 21ST AVE. N.E. | ABERDEEN | BROWN | SD | 57401 | 1 | NO | 1400 | 1991-05-14 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 0 | 71957 | 19910514 | 23 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2306 | DUPONT | 1979 | 1979 | UNDER GROUND OR UNDER WATER |  | V.B NELSON, GAS SUPERINTENDENT | 6052256300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-13 | YES | 3 | PAINT (YELLOW) | YES
2025-01-31 10:21 | NO | NO | 19910099 | 1991-06-18 | 792 | ATLANTA GAS LIGHT CO | 2732 CARLTON PLACE | CHAMBLEE | DE KALB | GA | 30319 | 1 | NO | 1256 | 1991-05-19 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 1 | 0 | 72567 | 19910519 | 30 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0 | STYLE 88 | DRESSER | 1969 | 1969 | UNDER GROUND OR UNDER WATER |  | THOMAS E. TURNER, SUPERINTENDENT | 4044573401 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ON MAY 19, 1991, AT APPROXIMATELY 12:40 P.M., AN AIRPLANE DEPARTING FROM PEACHTREE DEKALB AIRPORT STRUCK AND SEVERED AN ELECTRICAL POWER LINE. THE ELECTRICITY FROM THE DOWNED POWER LINE APPARENTLY TRAVELED THROUGH THE GROUND AND ALONG THE SERVICE LINE OF THE RESIDENCE LOCATED AT 2732 CARLTON PLACE. AT THE BUILDING WALL THE ELECTRICITY DISCHARGED FROM THE SERVICE CREATING A HOLE. GAS FILLED THE CRAWL SPACE AREA OF THE HOUSE AND AT APPROXIMATELY 12:47 P.M. WAS IGNITED BY AN UNKNOWN SOURCE, CAUSING AN EXPLOSION. AT 12:56PM. ATLANTA GAS LIGHT COMPANY RECEIVED A LEAK CALL AND DISPATCHED A SERVICE MAN TO THE SCENE. THE CAUSE OF THE LEAK WAS DISCOVERED AND THE SERVICE WAS SECURED.
2025-01-31 10:21 | YES | YES | 19910100 | 1991-06-25 | 10310 | KNOXVILLE UTILITIES BOARD | EMORY ROAD AT CLINTON HIGHWAY | KNOXVILLE | KNOX | TN |  | 4 | NO | 1630 | 1991-05-08 | 1 | 4 | 25000 | 20066.2908 | 48449.4057 | Null | 0 | 30 | 71280 | 19910508 | 30 | 60 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | JOINT |  | CAST IRON |  | 6 | 0.43 | WW-P-421 | CLOW & SONS | 1961 | 1961 | OTHER | OPEN TRENCH | PATRICK R. LUND - GAS ENGINEER | 6155947550 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | KNOXVILLE UTILITIES BOARD BUREAU OF GAS CREW HAD REMOVED SECTION OF CAST IRONPIPE TO PLACE A DROP IN THE LINE TO ALLOW FOR CONSTRUCTION OF SEWER LINE. THE DROP WAS CONSTRUCTED AND LEAK TESTED ACCORDING TO ESTABLISHED PROCEDURES.WHILE CREW WAS WRAPPING MECHANICAL COUPLINGS WITH HOT TAPE, CAST IRON JOINTFAILED RESULTING IN ESCAPE AND IGNITION OF GAS. THE ESCAPING GAS WAS IGNITEDBY A PROPANE TORCH USED TO HEAT THE WRAPPING TAPE. PART C.2 CAST IRON JOINTHAD BEEN WEAKENED DURING REMOVAL OF A PORTION OF PIPE TO INSTALL A DROP.
2025-01-31 10:21 | YES | YES | 19910102 | 1991-06-21 | 13299 | NEW JERSEY NATURAL GAS CO | 280 SUNSET LANE | SOUTH MANTOLOKING BEACH | BRICK | NJ | 08723 | 4 | NO | 1300 | 1991-06-07 | 0 | 3 | 150000 | 120397.7446 | 290696.434 | Null | 1 | 22 | 74827 | 19910607 | 38 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.15 | A25 | UNKNOWN | 0 | 1949 | UNDER PAVEMENT |  | H.R. YOUNG, MANAGER OF QUALITY CONTROL | 9089381265 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-29 | YES | 3 | PAINT | NO |  |  | ON FRIDAY JUNE 7, 1991, SANITARY CONSTRUCTION COMPANY WAS INSTALLING AN 8" CAST IRON WATER MAIN ON SUNSET LANE AT CARLTON PLACE IN THE SOUTH MANTOLOKING BEACH SECTION OF BRICK TOWNSHIP. SOMETIME BEFORE 12:18 PM. THE CONTRACTOR STRUCK THE 3/4" SERVICE TO 280 SUNSET LANE AND BROKE THE SERVICE AT THE BASE OFTHE RISER. AT 1:00 PM. THE GAS IGNITED CAUSING AN EXPLOSION AND AN ENSUING FIRE. SIX WORKERS WERE INJURED, THREE REQUIRING HOSPITALIZATION.
2025-01-31 10:21 | YES | NO | 19910103 | 1991-06-21 | 2668 | COMMONWEALTH GAS SERVICES INC | 663 DULLES-PARK COURT | HERNDON | FAIRFAX | VA | 22070 | 1 | NO | 618 | 1991-05-16 | 0 | 0 | 200000 | 160530.3261 | 387595.2454 | Null | 4 | 14 | 72214 | 19910516 | 20 | 21 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | OTHER | UNKNOWN | OTHER | BOLTED COUPLING | 4 | 0 |  | DRESSER | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS, MANAGER CONSTRUCTION & MAINTENANCE | 6144606366 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | UNKNOWN | COATED | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS COMING FROM A CORROSION LEAK IN THE BARREL OF A 4" BOLTED COUPLING CONNECTING THE RISER OF THE MEASUREMENT & REGULATION (M&R) SETTING TO A 4" PLASTICMAIN WAS IGNITED FROM AN UNDETERMINED SOURCE. THE RESULTING FIRE AT THE M&R STATION OUT SIDE A BRICK APARTMENT BUILDING CAUSED LESS THAN $1000 DAMAGE TO THE M&R FACILITY. THE RESPONDING FIRE DEPARTMENT, ARRIVING PRIOR TO OUR COMPANY, USED A WATER CANNON, SHOOTING THOUSANDS OF GALLONS OF WATER INTO THE BUILDING AND SURROUNDING AREA CAUSING WHAT THE FIRE DEPARTMENT ESTIMATES AS $200,000 IN DAMAGE TO THE APARTMENT BUILDING AND PERSONAL PROPERTY. THE WATER, WHICH ACCUMULATED AROUND THE BUILDING, AND THE RESTRICTIONS IMPOSED BY THE FIRE DEPARTMENT SEVERLY HAMPERED THE ABILITY OF PERSONNEL TO LOCATE THE UNDERGROUND MAIN AND THE SHUTTING OF THE GAS. SHUT-OFF WAS FINALLY EFFECTED AFTER FOUR HOURS VIA LOCATION AND SQUEEZING THE 4" PLASTIC MAIN.
2025-01-31 10:21 | NO | NO | 19910104 | 1991-06-01 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | W 125TH ST & ST. NICHOLAS AVENUE | NEW YORK CITY |  | NY | 10027 | 4 | NO | 1907 | 1991-05-19 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 76161 | 19910619 | 0.29 | 0.43 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | RICHARD C. GAULING - PLANNING ENGINER | 2124602838 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WELDING SLAG FROM RECENTLY INSTALLED STEEL TRAFFIC PLATES OVER EXCAVATION DROPPED DOWN ON PLASTIC GAS MAIN BELOW AND GAS FIRE ENSUED.
2025-01-31 10:21 | NO | NO | 19910106 | 1991-07-01 | 18440 | SOUTH JERSEY GAS CO | 20 NORTH HARRISBURG AVENUE | ATLANTIC CITY | ATLANTIC | NJ | 08401 | 1 | NO | 1420 | 1991-06-10 | 0 | 0 | 0 | 0 | 0 | Null | 1 | 0 | 75044 | 19910610 | 0.22 | 0.43 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMER'S RANGE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD J. JACKSON, ASST. V.P. DIVISION OPERATIONS | 6096519000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | TWO, FIVE-GALLON FUEL CANS CONTAINING SOME TYPE OF LIQUID ACCELERANT WAS PLACED IN FRONT OF THE GAS STOVE WHICH HAD STANDING PILOT LIGHTS. THE VAPORS FROMTHE ACCELERANT GATHERED NEAR THE FLOOR AND, AFTER REACHING THE HEIGHT OF 11 INCHES, CAUSED AN EXPLOSION. THE EXPLOSION WAS FUELED BY APPROXIMATELY 10 GALLONS OF FUEL WHICH CAUSED AN INTENSE FIRE TO FOLLOW.
2025-01-31 10:21 | YES | YES | 19910107 | 1991-07-15 | 2652 | COMMONWEALTH GAS CO | 25 SMITH PLACE | CAMBRIDGE | MIDDLESEX | MA |  | 1 | NO | 600 | 1991-06-22 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 10 | 76529 | 19910622 | 10 | 15 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | RISER BROKEN BY IMPACT | OTHER | UNKNOWN | 1.25 | 0 |  |  | 0 | 1989 | ABOVE GROUND |  | BRIAN J. HAWKESWORTH - SAFETY MANAGER | 5084817900 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE DRIVER OF A MOTORCYCLE WAS FATALLY INJURED WHEN HIS VEHICLE LEFT THE TRAVELED WAY AND STRUCK AN OUTSIDE METER ASSEMBLY AT 25 SMITH PLACE, CAMBRIDGE, MASS. A 1 1/4" I.P. SERVICE WAS BROKEN FROM THE IMPACT. PERMANENT REPAIRS WERE MADE TO THE PIPING AT THE CONVENIENCE OF THE CUSTOMER ON JUNE 25, 1991.
2025-01-31 10:21 | YES | NO | 19910108 | 1991-07-08 | 18536 | SOUTHWEST GAS CORP | 5040 S. RAINBOW | LAS VEGAS | CLARK | NV | 89118 | 3 | NO | 1647 | 1991-06-24 | 0 | 0 | 80000 | 64212.1304 | 155038.0981 | Null | 0 | 30 | 76872 | 19910625 | 43 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | STEEL |  | 0.75 | 0.113 | ASTM A-53 | R.W. LYALL & CO. | 1988 | 1988 | ABOVE GROUND |  | L.K. SMITH - CONSTRUCTION SUPERVISOR | 7023652030 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | SERVICE RISER WAS BROKEN OFF IN THREADS AT STOP COCK WHILE ATTEMPTING TO LOOSEN METER CONNECTION.
2025-01-31 10:21 | NO | NO | 19910111 | 1991-08-02 | 6035 | GALLAWAY GAS DEPT, CITY OF | HWY. 205 APPROX. 3 MI. N. OF ARLINGTON | UNKNOWN | SHELBY | TN | 38002 | 0 | NO | 1500 | 1991-06-27 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | WILLARD U. FLETCHER | 9018673333 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | WHILE MAKING REPAIRS TO AN EXISTING FIRE HYDRANT, MEMPHIS LIGHT GAS & WATER -- WATER MAINTENANCE CREW, CUT THE 4" POLY GAS MAIN ON MILLINGTON-ARLINGTON ROAD APPROXIMATELY 3 MILES NORTH OF ARLINGTON, TN. THE ABOVE CREW DID NOT REQUEST INFORMATION REGARDING ANY UTILITIES IN THE AREA NOR DID THEY CALL THE 800 NUMBER PRIOR TO DIGGING. CITY OF GALLOWAY RECEIVED CALL AND WENT TO FIRST AVAILABLE VALVE AND TURNED GAS OFF. A MEMPHIS LIGHT GAS & WATER - GAS CREW CAME AND MADE PROPER REPAIRS TO GAS LINE AND EVERYTHING WAS BACK IN SERVICE BY1926 HOURS.
2025-01-31 10:21 | NO | NO | 19910112 | 1991-07-26 | 18536 | SOUTHWEST GAS CORP | 48 STREET AND REOOSEVELT | PHOENIX | MARICOPA | AZ | 85034 | 3 | NO | 1030 | 1991-06-18 | 0 | 0 | 6500 | 5217.2356 | 12596.8455 | YES | 3 | 0 |  | 19910618 | 30 | 30 | BY TEST | 60 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 | API5LX42 | UNKNOWN | 1948 | 1949 | UNDER PAVEMENT |  | MIGUEL Y. JAUREGUI - MANAGER OF ENGINEERING | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-06-12 | YES | 0 |  | YES |  |  | LEONARD WAHLQUIST, FOREMAN FOR AMERICAN UNDERGROUND CONSTRUCTION, WAS BORINGWITH A 2' AUGER, WHILE PUSHING A 30" CASING, WHEN HE HIT OUR 4" DISTRIBUTON GAS MAIN
2025-01-31 10:21 | YES | YES | 19910113 | 1991-07-17 | 13710 | NORTHERN ILLINOIS GAS CO | ELA & LAKE COOK ROAD | BARRINGTON | COOK | IL | 60010 | 3 | NO | 800 | 1991-06-19 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 | 76233 | 19910619 | 0 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | PURGING | STEEL |  | 10 | 0 |  |  | 0 | 1946 | OTHER | OPEN DITCH | ARTHUR W. SWANSON - GENERAL SUPERVISOR, SYS. OPER. | 8154550271 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ACCIDENT WAS CAUSED BY A MISUNDERSTANDING BETWEEN A NI-GAS SUB-CONTRACTOR'S SUPERVISOR AND LABORER. A PURGE PROCEDURE FOR A PIPE CONTAINING A GAS/AIR MISTURE WAS STARTED BEFORE A HOT WRAPPING OPERATION WAS COMPLETED. THE RESULTING FLASH FIRE CAUSED FIRST AND SECOND DEGREE BURNS TO THE SUPERVISOR'S FACE AND HANDS.
2025-01-31 10:21 | NO | NO | 19910114 | 1991-07-25 | 12390 | METROPOLITAN UTILITIES DISTRICT | 60TH & WILLIAMS STREET | OMAHA | DOUGLAS | NE | 68106 | 3 | NO | 1130 | 1991-07-15 | 0 | 0 | 1000 | 802.6516 | 1937.9762 | YES | 0 | 5 | 79470 | 19910715 | 0.25 | 0.25 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | TAP FOR PURGE | STEEL |  | 16 | 0.25 | API5L GRADE B |  | 0 | 1991 | OTHER | OPEN EXCAVATION | DONALD D. BLOCKER - CLAIMS REP | 4024498210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | NEW MAIN INSTALLED AND WAS BEING CONNECTED TO EXISTING MAIN W/CLOSURE PIECE WHICH WAS ISOLATED FROM NEW AND EXISTING MAINS BY "BAG-OFF". CLOSURE PIECE WAS BEING PURGED. OPERATOR'S EMPLOYEE HAD FILLED "BURN BAG" FROM VENT ON PURGE CONNCECTION AND ATTEMPTED THE "BURN TEST" IN THE EXCAVATION RATHER THAN EXITING EXCAVATION. IN DOING SO, A LIGHTED MATCH WAS DROPPED, IGNITING GAS. TWO EMPLOYEE RECEIVED 1ST DEGREE BURNES. THEY WERE TREATED AND RELEASED FROM HOSPITAL. TELEPHONIC REPORT WAS MADE IN THAT SEVERITY OF INJURIES WERE UNKNOWN. BASED ON FULL INFORMATION NEW AVAILABLE, THIS WAS NOT A REPORTABLE ACCIDENT
2025-01-31 10:21 | NO | NO | 19910115 | 1991-07-29 | 13782 | NORTHERN STATES POWER CO | ALBEMARLE ST AND W MARYLAND STREET | ST. PAUL | RAMSEY | MN | 55117 | 3 | NO | 611 | 1991-04-28 | 0 | 0 | 56000 | 44948.4913 | 108526.6687 | Null | 0 | 0 | 78382 | 19910428 | 0.3 | 0.3 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | JOINT | BELL & SPIGOT | CAST IRON |  | 4 | 0 |  |  | 0 | 1913 | UNDER PAVEMENT |  | NICK J. BOOSALIS, SENIOR GAS ENGINEER | 6122292317 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | PART 1 (#5 ELAPSED TIME) - SOMETIME AFTER THE WATER MAIN BROKE AT AROUND 3:00 AM. THE LOW PRESSURE GAS MAIN FILLED WITH WATER, CUTTING OFF THE FLOW OF GAS. FIRST MADE AWARE THAT THERE WAS A PROBLEM WHEN NOTIFIED AT 6:09 AM. BY A CUSTOMER "NO GAS" CALL.PART 1 (#6 TELEPHONIC REPORT) - AT THE TIME OF THE TELEPHONIC NOTICE TO MNOPS, IT WAS TO EXPECTED THAT DAMAGES WOULD EXCEED $50,000. THEREFORE, IT WAS NOT CONSIDERED REPORTABLE BY US DOT CRITERIA. TELEPHONIC NOTIECE WAS MADE TO US DOT (MARK BRANTLEY) ON 7/8/91 AFTER DISCOVERING THAT COSTS TO REPLACE MAINAND RESTORE SERVICE TO CUSTOMERS EXCEEDED $50,000. MARK BRANTLEY SAID THAT A WRITTEN INCIDENT REPORT TO US DOT WAS NOT REQUIRED FOR THIS INCIDENT. HOWEVER, AFTER DISCUSSION WITH STEVE SWENEY OF MN OPS, IT WAS DECIDED TO SUBMIT AN INCIDENT REPORT TO US DOT ALSO.
2025-01-31 10:21 | NO | NO | 19910116 | 1991-07-30 | 8070 | INDIANA GAS CO INC | 2806 SCHAAL AVENUE | TERRE HAUTE | VIGO | IN | 47807 | 1 | NO | 1533 | 1991-06-18 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 13 | 76103 | 19910618 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | FUEL LINE TO RANGE | BODY OF PIPE |  | OTHER | COPPER | 0.625 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RONALD J. BOES | 3173210575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | RESIDENT MOVING SINK BROKE OFF FUEL LINE TO RANGE, CAUSING GAS LEAK; RESIDENT OVERCOME BY FUMES, TREATED AND RELEASED.
2025-01-31 10:21 | YES | YES | 19910117 | 1991-08-19 | 6920 | GULF STATES UTILITIES CO | 1665 NORTH 37TH STREET | BATON ROUGE |  | LA | 70802 | 2 | NO | 1000 | 1991-07-17 | 0 | 1 | 5000 | 4013.2582 | 9689.8811 | Null | 0 | 0 | 79857 | 19910717 | 60 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN |  | 0 0 0 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FOLLOWING A SAFETY CHECK ON HOUSEPIPING AND APPLIANCES, OUR SERVICEMAN TURNED THE GAS ON AND CHECK FOR LEAKAGE USING THE GAS METER TEST DIAL. NO LEAKAGEFOUND. SERVICEMAN LIT THE STOVE AND WATER HEATER AND LEFT SITE OK. APPROXIMATELY TWO (2) HOURS LATER THE INCIDENT OCCURRED. OUR INVESTIGATION IMMEDIATELY AFTER THE INCIDENT, FOUND HOUSELINE AND APPLIANCES IN TACT. WE TESTED FOR LEAKS ON HOUSELINE AND FOUND APPROXIMATELY A ONE (1) FOOT PER HOUR LEAK. CONSUMPTION ON THE METER DURING THIS TWO (2) HOURS PERIOD WAS APPROXIMATELY 700 FEET.
2025-01-31 10:21 | YES | YES | 19910118 | 1991-07-25 | 1704 | BRAZOS RIVER GAS CO | 221 LAKE HOLLOW DRIVE | WEATHERFORD | PARKER | TX | 76086 | 3 | NO | 630 | 1991-06-17 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 45 | 75960 | 19910617 | 24 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | PAUL R. JOHNSON | 8173254445 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-06-17 | YES | 3 | YELLOW PAINT | NO
2025-01-31 10:21 | NO | NO | 19910120 | 1991-08-19 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 3RD AVENUE BETWEEN 22ND & 23RD STREETS | NEW YORK | BOROUGH OF MANHATTAN | NY | 10010 | 4 | NO | 944 | 1991-07-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 80276 | 19910721 | 40 | 99 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | RICHARD C. GAULIN - PLANNING ENGINEER | 2124602838 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR UNDER CONTRACT TO CON EDISON DAMAGED 1 1/4 INCH PLASTIC HIHG PRESSURE SERVICE. NEWS MEDIA WAS PRESENT. THIS INCIDENT IS NOT REPORTABLE.
2025-01-31 10:21 | YES | YES | 19910122 | 1991-08-19 | 2169 | CENEX LIQUID PETROLEUM GAS PLANT | UPTOWN MEATS & DELI | PARKERS PRAIRIE | OTTER TAIL | MN | 56361 | 2 | NO | 1215 | 1991-08-05 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 5 | 82415 | 19910805 | 10 | 10 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT HERMANSON - PLANT MANAGER | 2185834122 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION AND SMALL FIRE IN BASEMENT OF UPTOWN MEATS. VICTIM WAS TRAPPED AND CAUGHT UNDER DEBRIS IN BASEMENT. EXPLOSION WAS BELIEVED TO BE CAUSED BY LEAKING PROPANE GAS FROM OUR SERVICE LINE LOCATED OUTSIDE THE BUILDING. THIS WAS DETERMINED BY THE MN STATE FIRE MARSHAL'S OFFICE.
2025-01-31 10:21 | YES | YES | 19910123 | 1991-08-13 | 2200 | CENTRAL ILLINOIS LIGHT CO | 400 BLOCK LAWRENCE STREET | SPRINGFIELD | SANGAMON | IL | 62704 | 4 | NO | 1600 | 1991-07-16 | 0 | 1 | 10000 | 8026.5163 | 19379.7623 | Null | 4 | 30 | 79761 | 19910717 | 40 | 40 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT | MECH | CAST IRON |  | 6 | 0.5 | UNKNOWN | UNKNOWN | 1952 | 1952 | UNDER PAVEMENT |  | ROBERT M. LEHMKUHL - CORROSION & LEAK CONTROL SUPERVISOR | 3096934865 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | MECHANICAL JOINT FAILURE | WHILE REPAIRING A GRADE 2 LEAK, A BURIED MECHANICAL JOINT FAILED, ALLOWING A 6" C.I. MAIN TO BECOM DISCONNECTED FROM THE COMPRESSION FITTING.
2025-01-31 10:21 | YES | NO | 19910124 | 1991-08-05 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | PARK AVENUE AT CARLTON TERR. | HOT SPRINGS | GARLAND | AR | 71901 | 4 | NO | 1130 | 1991-07-24 | 0 | 0 | 100000 | 80265.1631 | 193797.6227 | Null | 3 | 30 | 80809 | 19910724 | 5 | 12 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 | BELL & SPIGO | UNKNOWN | 0 | 1943 | UNDER PAVEMENT |  | JIM BREWER | 5013774771 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | NO |  |  | AN ASPHALT STRIPPING MACHINE REMOVING THREE INCHES OF ASPHALT STRUCK A 4" CAST IRON GAS MAIN, RUPTURING THE MAIN. THE ESCAPING NATURAL GAS IGNITED, DESTROYING THE ASPHALT REMOVING EQUIPMENT.
2025-01-31 10:21 | NO | NO | 19910126 | 1991-08-05 | 15931 | PUBLIC SERVICE CO OF COLORADO | EMERSON AT FLORIDA | DENVER | DENVER | CO |  | 3 | NO | 134 | 1991-07-23 | 0 | 0 | 0 | 0 | 0 | YES | 10 | 25 | 80552 | 19910723 | 0.65 | 3.6 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNKNOWN | CAST IRON |  | 16 | 0.475 | UNKNOWN | UNKNOWN | 0 | 1931 | UNDER PAVEMENT |  | BILL YENKO - GAS ENGINEERING & METRO OPERATIONS SUPV. | 3035713946 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE THE CREW WAS COMPLETING THE FINAL TIE-IN BAG HOLE (3 BAG STOPS REQUIRED), THE GAS IGNITED FROM AN UNKNOWN SOURCE. THE IGNITION TOOK PLACE AS THE FINAL BAG WAS BEING REMOVED. FOUR PEOPLE (1 GAS COMPANY, 3 CONTRACTOR MEMBERS) WERE TREATED AND RELEASED FROM THE HOSPITAL FOR BURNS.
2025-01-31 10:21 | YES | NO | 19910127 | 1991-08-05 | 14210 | OKLAHOMA NATURAL GAS CO | 3805 EAST 98TH | TULSA | TULSA | OK | 74137 | 3 | NO | 2015 | 1991-07-05 | 0 | 0 | 400000 | 321060.6522 | 775190.4907 | Null | 0 | 10 | 78194 | 19910706 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | 733A | FISHER | 1940 | 1986 | WITHIN/UNDER BUILDING |  | GERRY B. LYNN, CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | DIRT PLUGGED REGLTR VENT | NO |  | NO | 0 |  | NO |  |  | THIRD PARTY HAD BEEN PERFORMING LANDSCAPE SERVICE SODDING YARD. NO MATERIALDEFECT WAS APPARENT. HOWEVER, THE REGULATORY HAS NOT BEEN DISASSEMBLED PENDING AND INVESTIGATION BY NTSB. REGULATOR VENT PORT WAS PLUGGED WITH DIRT. RESIDENTIAL FIRE RESULTED WHEN DIRT PLUGGED THE REGULATOR'S VENT AND RELIEF PORT CAUSING AN OVERPRESSURE CONDITION ON THE HOUSE PIPING. GAS APPARENTLY BEGAN TO ESCAPE AT THE FURNACES (2) AND WAS IGNITED BY THE FURNACES' STANDING PILOTS. THE METER AND REGULATOR SETTING WAS IN AN UNDERGROUND METER BOX. THE METER BOX FILLED WITH DIRT POSSIBLY DUE TO LANDSCAPING. AT THE TIME OF THE INCIDENT, THE METER BOX WAS COVERED WITH DIRT FROM A RECENT LANDSCAPING PROJECT. PART B.1 - DIRT FROM THE YARD GOT INTO THE METERBOX AND PLUGGED THEREGULATOR VENT. (POSSIBL) SOILE COULD HAVE BEEN WASHED INTO THE METER BOX BYACTION OF LANDSCAPING OR JUST HEAVY RAIN.
2025-01-31 10:21 | YES | YES | 19910128 | 1991-08-09 | 18536 | SOUTHWEST GAS CORP | 5025 NORTH FIRST AVENUE | TUCSON | PIMA | AZ |  | 3 | NO | 1750 | 1991-07-25 | 1 | 1 | 200000 | 160530.3261 | 387595.2454 | YES | 2 | 35 | 81064 | 19910725 | 59 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0 |  | DUPONT | 1979 | 1980 | UNDER PAVEMENT |  | JOHN HANENBURG - MANAGER, GAS OPERATIONS | 6027946053 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | ON JULY 25, 1991, AT APPROXIMATELY 1750 HOURS, A SOUTHWEST GAS CUSTOMER SERVICE SUPERVISOR HEARD A NEWS REPORT OF AN EXPLOSION AND FIRE IN THE 5000 BLOCKOF NORTH FIRST AVENUE ON HIS F.M. RADIO. THE SUPERVISOR REPORTED THIS TO HIS HAS DISPATCHER AND PROCEEDED TO THE INCIDENT LOCATION. UPON HIS ARRIVAL, HE CONTRACTED THE FIRE CHIEF OF THE NORTHWEST FIRE DISTRICT. PER THE FIRE CHIEF, ALL UTILITIES WERE SECURE AND THE FIRE DEPARTMENT HAD EXTINGUISHED A FIREIN AN ALL ELECTRIC APARTMENT. WE WERE FURTHER ADVISED THAT AN ADULT MALE AND AN ADULT FEMALE HAD BEEN TRANSPORTED BY AMBULANCE TO A HOSPITAL FOR BURNS RECEIVED IN THIS INCIDENT AND THAT TWO FIRE FIGHTERS HAD BEEN TREATED AND RELEASED FOR SMOKE INHALATION. SOUTHWEST GAS RECORDS INDICATED THAT WE HAD A 2" SERVICE LINE TO THIS APARTMENT COMPLEX THAT SUPPLIED GAS TO A CENTRAL WATER HEATING SYSTEM, POOL AND SPA HEATER AND GAS DRYERS IN THE LAUNDRY ROOM. THE CUSTOMER SERVICE SUPERVISOR DIRECTED SOUTHWEST GAS EMPLOYEES TO INSPECT OUR FACILITIES. AT APPROXIMATELY 1855 HOURS, SOUTHWEST GAS EMPLOYEES NOTICED BUBBLES IN THE PAVED DRIVEWAY NEXT TO SEVERAL FIRE TRUCKS. WE IMMEDIATELY NOTIFIED THE FIRE DEPARTMENT AND REQUESTED AN EVACUATION OF THE AREA. AT 1900 HOURS, WE CONFIRMED THAT THERE WAS A NATURAL GAS LEAK ON THE SOUTHWEST GAS SERVICELINE. THE LOCATION OF THE LEAK WAS ESTABLISHED AND NECESSARY REPAIRS MADE.COMPRESSORS AND AERATORS WERE BROUGHT IN AND THE AREA HAD BEEN CONSTANTLY MONITORED FOR GAS RESIDUE. THIS INCIDENT OCCURRED IN A LARGE APARTMENT COMPLEX. AS APARTMENTS WERE CLEARED, OCCUPANTS WERE ALLOWED TO RETURN. ON JULY 29,1991 AT 1915 HOURS, ALL APARTMENTS WERE CLEARED FOR OCCUPANCY EXCEPT THOSE DIRECTLY INVOVLED IN THE FIRE.
2025-01-31 10:21 | NO | NO | 19910130 | 1991-08-23 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 139 HIGH STREET | YONKERS | WESTCHESTER | NY | 10705 | 4 | NO | 527 | 1991-07-07 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 0 | 0 |  | 19910707 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDETERMINED | OTHER | UNDETERMINED | OTHER | UNDETERMINED | 0 | 0 |  |  | 0 | 0 | OTHER | UNDETERMINED | RICHARD C. GAULIN - PLANNING ENGINEER | 2124602838 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | IT WOULD APPEAR THAT AN EXPLOSION CAUSED THE COLLAPSE OF A BUILDING. ALTHOUGH THE INCIDENT IS STILL UNDER INVESTIGATION, GAS DOES NOT APPEAR TO HAVE BEEN INVOLVED.
2025-01-31 10:21 | YES | NO | 19910132 | 1991-09-06 | 11680 | LONE STAR GAS CO | 7618 & 7620 HIGHMONT | DALLAS | DALLAS | TX | 75230 | 3 | NO | 1430 | 1991-07-30 | 0 | 0 | 100000 | 80265.1631 | 193797.6227 | Null | 1 | 45 |  | 19910730 | 22 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | SERVICE LINE RISER | OTHER | UNKNOWN | STEEL |  | 1 | 0.133 | AP15L | UNKNOWN | 1970 | 1970 | ABOVE GROUND |  | PHILIP MURDOCK - MANAGER | 2146702229 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | CREW WAS REPAIRING LEAK ON RISER AND THE GAS WAS IGNITED AND BURNED APARTMENT BUILDING.
2025-01-31 10:21 | YES | YES | 19910134 | 1991-09-09 | 20211 | UNITED CITIES GAS CO | CASA DEL SOL APART. COMPLEX RT. #1 | COFFEYVILLE | MONTGOMERY | KS | 67337 | 2 | NO | 2001 | 1990-11-12 | 1 | 2 | 0 | 0 | 0 | Null | 3 | 0 |  | 19901113 | 77.2 | 100 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.25 | N/A | N/A | 0 | 1932 | WITHIN/UNDER BUILDING |  | KENNY BIGBIE - TOWN MANAGER | 3162514400 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19910135 | 1991-09-03 | 20211 | UNITED CITIES GAS CO | 886 SHERIDAN CR. | OLATHE | JOHNSON | KS | 66061 | 0 | NO | 2000 | 1991-01-15 | 0 | 2 | 80000 | 64212.1304 | 155038.0981 | YES | 1 | 30 |  | 19910115 | 0.25 | 0.4 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | JOINT | WELD | STEEL |  | 3 | 0 | N/A | N/A | 0 | 0 | UNDER PAVEMENT |  | JOHN M. GLERUM - MANAGER | 9137640530 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19910138 | 1991-08-22 | 2488 | CLEARWATER GAS DIV, CITY OF | LOGAN AND BELCHER | CLEARWATER | PINELLAS | FL | 34615 | 0 | NO | 1000 | 1991-08-05 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19910805 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | VALVE |  | POLYETHYLENE PLASTIC |  | 2 | 0.409 | D-2513 | POLYETHYLENE PRODUCTS, INC. | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | J. TERRY NEENAN, GAS SUPERINTENDENT | 8134626630 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-07-31 | YES | 0 |  | YES |  |  | APPROXIMATELY 9:40 AM, AN EMPLOYEE (MIKE RITTER) OF VISK CONSTRUCTION RUPTURED A NATURAL GAS MAIN, WHILE USING A POWER DITCH DIGGER. THE RUPTURED GAS MAIN CAUGHT FIRE AND BURNED THE EMPLOYEE RIDING THE DITCHER. CLEARWATER FIRE DEPARTMENT RESPONDED TO THE CALL. MIKE RITTER WAS TRANSPORTED TO CLEARWATER COMMUNITY HOSPITAL. THE EMPLOYEE RECEIVED FIRST AND SECOND DEGREE BURNES ON HIS LEFT SIDE AND THE DITCHER WAS DESTROYED BY THE FIRE. THE FIRE WAS PUT ON APPROXIMATELY 10:30 AM. THE GAS MAIN WAS REPAIRED AND PUT BACK INTO SERVICE 11:45 AM AND SERVICE WAS RESTORED TO THE ONE CUSTOMER EFFECTED BY 12:30 PM. THE CONTRACTOR CALLED FOR A LINE LOCATION ON 7/31/91. THE CALL NUMBER WAS 000138111. THE END OF THE STEEL GAS MAIN WAS MARKED, BUT THE PLASTIC GAS MAIN WAS NOT MARKED. OUR INSPECTOR, MIKE DEEGAN, LOCATED WHAT HE THOUGHT WAS THE END OF THE MAIN FOR THE CONTRACTOR. DEEGAN ALSO DUG UP THE END OF THE STEEL GAS MAIN. HE DID NOT FIND THE PLASTIC MAIN NOR COULD HE FIND IT WITH A ELECTRICAL LINE LOCATOR. HE DID FIND WHAT HE THOUGHT WAS A 2" PLASTIC GAS SERVICE AND A 1" STEEL SERVICE THAT WENT ACROSS THE STREET. THIS PALSTIC SERVICE TURNOUT TO BE A GAS MAIN. THIS MAIN HEADED ACROSS THE STREET, BUT HAD A 90 DEGREE ELBOW FUSED ON IT (THE 90 DEGREE ELBOW WAS OUTSIDE THE EXCAVATION AND COULD NOT BE SEEN) AND WAS IN FACT THE MAIN THE CONTRACTOR HIT. THE CONTINUITY TRACER WIRE WAS NOT BONDED TO THE STEEL MAIN THEREFORE MR. DEEGAN COULD NOT PICK IT UP WITH THE LINE LOCATOR.
2025-01-31 10:21 | NO | NO | 19910141 | 1991-08-30 | 8290 | IRAAN UTILITY SYSTEMS, CITY OF | NORTH OF COUNTY GOLF COURSE | IRAAN | PECOS | TX | 79744 | 0 | NO | 830 | 1991-08-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  |  | 35 | 100 | BY TEST | 250 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | STEEL |  | 3.5 | 0.135 |  |  | 0 | 0 | ABOVE GROUND |  | HOWARD FLOYD - UTILITY DIRECTOR | 9156392301 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GROUND | NO
2025-01-31 10:21 | NO | NO | 19910143 | 1991-09-13 | 21349 | VIRGINIA NATURAL GAS | HOPE STREET & INTERSTATE 64-WEST | HAMPTON |  | VA | 23667 | 3 | NO | 1400 | 1991-08-22 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 10 |  | 19910922 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | STEEL |  | 2 | 0.154 | API-5L |  | 1983 | 1984 | UNDER GROUND OR UNDER WATER |  | STEVE R. STONE - DISTRICT MANAGER | 8048736262 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-08-19 | YES | 3 | PAINTED MARK | YES |  |  | AUGER STRUCK GAS PIPELINE WHILE INSTALLING SOUND BARRIERS ALONG INTERSTATE.
2025-01-31 10:21 | YES | NO | 19910144 | 1991-09-17 | 10037 | K P L GAS SERVICE | 1004 WEST R.D. MIZE ROAD | BLUE SPRINGS | JACKSON | MO |  | 3 | NO | 1804 | 1991-08-22 | 0 | 0 | 63000 | 50567.0527 | 122092.5023 | Null | 0 | 22 |  |  | 10 | 58 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREAD | STEEL |  | 1.125 | 0.14 | N/A | N/A | 0 | 1962 | ABOVE GROUND |  | HANS E. MERTENS - VICE PRESIDENT OF ENGINEERING | 8163465575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE WENT OUT OF CONTROL - HIT GAS LINE AND HOUSE, IGNITING GAS. DAMAGE TO CAR AND HOUSE. HOUSE SET 45' FROM STREET.
2025-01-31 10:21 | YES | NO | 19910148 | 1991-09-23 | 10037 | K P L GAS SERVICE | 1600 LIBERTY | KANSAS CITY | JACKSON | MO |  | 3 | NO | 2024 | 1991-08-14 | 0 | 0 | 250000 | 200662.9077 | 484494.0567 | Null | 1 | 0 |  | 19910814 | 30 | 5 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 | 10A | AMERICAN | 0 | 1983 | WITHIN/UNDER BUILDING |  | HANS E. MERTENS - VICE PRESIDENT OF ENGINEERING | 8163465575 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A FIRE, OF UNKNOWN ORIGIN, AT THIS RESIDENCE, DAMAGED THE GAS METER ASSEMBLY, RESULTING IN THE IGNITION OF GAS.
2025-01-31 10:21 | YES | NO | 19910150 | 1991-09-30 | 6920 | GULF STATES UTILITIES CO | 2653 PLANK ROAD | BATON ROUGE |  | LA |  | 3 | NO | 125 | 1991-09-24 | 0 | 0 | 100000 | 80265.1631 | 193797.6227 | Null | 0 | 42 |  | 19910924 | 24 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | THOMAS W. ASHLEY - GENERAL SUPERVISOR | 5017671802 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE HIT METER SET BREAKING RISER BELOW VALVE.
2025-01-31 10:21 | NO | NO | 19910151 | 1991-09-30 | 6920 | GULF STATES UTILITIES CO | FLORIDA BLVD & N. FOSTER DRIVE | BATON ROUGE |  | LA | 70806 | 4 | NO | 2016 | 1991-09-19 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 24 |  | 19910920 | 24 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 4 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | THOMAS W. ASHLEY - GENERAL SUPERVISOR | 5047671802 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-09-10 | YES | 3 | PAINT | YES |  |  | CONTRACTOR CUTTING A CONCRETE STREET CUT THE TOP OF A 4" STEEL LINE.
2025-01-31 10:21 | YES | YES | 19910154 | 1991-09-30 | 1344 | BERKSHIRE GAS CO | 129 BEAVER STREET | NORTH ADAMS | BERKSHIRE | MA | 01247 | 3 | NO | 1237 | 1991-08-31 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 0 |  | 19910831 | 0.25 | 0.33 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD L. HAMEL - PRODUCTION SUPERVISOR | 4134421511 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TESTING OF THE SERVICE LINE, METERS AND COMPANY INSTALLED PIPING FROM THE METER TO THE CUSTOMER OWNED PIPING HAS SHOWN THAT THESE WERE NOT FACTORS IN THIS INCIDENT. THE STATE FIRE MARSHALL HAS NOT YET CONCLUDED HIS INVESTIGATION AS TO THE FUEL OR THE IGNITION SOURCE INVOLVED IN THE INCIDENTS.
2025-01-31 10:21 | YES | YES | 19910155 | 1991-08-12 | 4473 | ENERGAS CO | 34TH STREET AND SOUTH MONROE | AMARILLO | RANDALL | TX | 79107 | 3 | NO | 930 | 1991-07-16 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 30 |  | 19910716 | 0.5 | 0.75 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | INTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.25 |  |  | 0 | 1941 | UNDER PAVEMENT |  | CHARLES R. FULKERSON - ENGINEERING SUPERVISOR | 8067984477 | INTERNALLY | GENERAL CORROSION |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CALL WAS RECEIVED AT THE SERVICE CENTER AT APPROXIMATELY 9:40 AM ON TUESDAY, JULY 16TH, REPORTING AND EXPLOSION IN THE VICINITY OF 34TH STREET AND SOUTH MONROE. CHARLES WALLER, SERVICEMAN, WAS DISPATCHED TO THE SCENE. WHEN HE ARRIVED ATH THE SCENE, HE FOUND THAT J. LEE MILLIGAN COMPANY, A PAVING CONTRACTOR, HAD BEEN HEATING THE ASPHALT PAVEMENT. THIS WAS DONE USING A MACHINE WICCURRED AND ONE OF THE MANHOLE COVERS WAS BLOWN SEVERAL FEET INTO THE AIR. A WORKER BY THE NAME OF JOHNNY CARRASCO, AGE 25, WAS STANDING NEXT TO THE MANHOLE NAD WAS HIT BY ASPHALT AND GRAVEL DEBRIS. THERE WAS INJURY TO HIS FACE ANTHER. WHEN GARY ECHOLS AND THE COMPANY C & M CREW ARRIVED, THEY WERE UNCERTAIN WHETHER THE GAS PRESENT WAS NATURAL GAS OR SEWER GAS. SCOTT FUSSELL WAS CALLED TO THE SCENE TO CHECK FOR THE PRESENCE OF EHTANE. HIS EHTANE DETECTORINDICATED THE PRESENCE OF ETHANE, MEANING THAT THE GAS WAS NATURAL GAS. HE ALSO COMPARED THE MANHOLE SAMPLE TO A KNOWN GAS SAMPLE. THE CREW BEGAN DRILLING HOLES AND CHECKING FOR GAS UNDER THE PAVEMENT ALONG THE 6" LP MAIN WHICH IS APPROXIMATELY 15 FEET NORTH OF THE NORTH MANHOLE. THEY CHECKED SEVERAL BLOCKS TO THE EAST WITHOUT FINDING ANY INDICATION OF GAS. AS THEY PROBED ALONGTHE 6" LP MAIN TO THE WEST, GAS WAS FOUND APPROXIMATELY 200 FEET TO THE WESTOF THE MANHOLES. WHEN THE LEAK INDICATION WAS PINPOINTED, THE MAIN WAS EXCAVATED BEGINNING AT THIS LOCATION. SEVERAL LEAKS WERE FOUND AND 4 TEMPORARY LEAK CLAMPS INSTALLED TO STOP THE LEAKAGE. THE COMPANY CONTRACTOR HAS NOW REPLACED 31 FEET OF 6" PIPE, COMPLETING THE WORK ON JULY 18TH. GARY ECHOLAS STATED THAT THE INJURED EMPLOYEE RETURNED TO THE JOB SITE AFTER RECEIVING TREATMENT AT THE HOSPITAL. ONE OF THE VICE-PRESIDENTS FOR J. LEE MILLIGAN COMPANY TOLD GARY THAT IT DID NOT APPEAR THAT THE EMPLOYEE WOULD NEED ANY PLASTIC SURGERY TO HIS FACE BUT THAT THE DOCTOR WAS SENDING HIM TO A PLASTIC SURGEON TO BE CERTAIN. HE ALSO TOLD HIM THAT THE EMPLOYEE WAS RELEASED TO RETURN TO WORK ON JULY 18, 1991. THIS INCIDENT WAS REPORTED TO THE D.O.T. NATIONAL RESPONSE CENTER AND WAS ASSIGNED REPORT NUMBER 79586. IT WAS ALSO REPORTED TO THE TEXAS RAILROAD COMMISSION AT AUSTIN AND GENE MORENO OF THEIR LUBBOCK OFFICE INVESTIGATED ON THE SITE ON THE AFTERNOON OF JULY 16TH.
2025-01-31 10:21 | YES | NO | 19910156 | 1991-09-20 | 15007 | PACIFIC GAS & ELECTRIC CO | 347 REDWOOD DRIVE | FELTON | SANTA CRUZ | CA | 95018 | 3 | NO | 1330 | 1991-09-01 | 0 | 0 | 160350 | 128705.189 | 310754.488 | YES | 0 | 27 |  | 19910901 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | STEEL |  | 0.375 | 0 |  |  | 0 | 1969 | ABOVE GROUND |  | W.R. MAZOTTI - V.P. GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CUSTOMER TAMPERED WITH AND DAMAGED SERVICE VALVE, ALLOWING GAS TO ESCAPE, ENTER THE HOUSE, EXPLODE AND IGNITE FROM UNKNOWN SOURCE OF IGNITION.
2025-01-31 10:21 | NO | NO | 19910157 | 1991-10-08 | 12012 | MADISON GAS DEPT, CITY OF | 406 N. MAIN | MADISON | MONROE | MO | 65263 | 3 | NO | 200 | 1991-08-29 | 0 | 0 | 45000 | 36119.3234 | 87208.9302 | Null | 0 | 15 |  | 19910829 | 26 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | GLUE | OTHER PLASTIC | PVC | 0.75 | 0.09 | SDR-21 AGA | KRALOY/CHEM & ROL | 1964 | 1964 | WITHIN/UNDER BUILDING |  | RANDY HENDREN | 8162915235 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | UNKNOWN | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19910166 | 1991-01-30 | 11680 | LONE STAR GAS CO | 906 TAMANRA | GRAND PRAIRIE | DALLAS | TX | 75051 | 3 | NO | 1620 | 1991-01-21 | 0 | 0 | 6000 | 4815.9098 | 11627.8574 | Null | 4 | 0 |  | 19910121 | 24 | 30 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COLLAR AND FITTING | STEEL |  | 1 | 0.133 | APL 5L CLASS1 | UNKNOWN | 1952 | 1952 | WITHIN/UNDER BUILDING | UNDER GROUND OR UNDER WAT | LOIS ROSS - CLERK | 2146701566 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1990-12-20 | YES | 3 | PAINT | YES
2025-01-31 10:21 | NO | NO | 19910186 | 1991-10-09 | 1640 | BOSTON GAS CO | 16 EAST BROOKLINE STREET | BOSTON | SUFFOLK | MA |  | 4 | NO | 1115 | 1991-09-24 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19910924 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | DOWNSTREAM OF METER | OTHER | NOT SPECIFIED IN REPORT | STEEL |  | 4 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LEO T. CODY, MANAGER DISTRIBUTION ADMINISTRATION | 6173239210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | BOSTON GAS COMPANY RESPONDED TO A REPORT OF SERVICE ON FIRE IN BASEMENT. UPON ARRIVAL, A BOSTON GAS EMPLOYEE NOTICED A FLAME ABOVE THE PIPE AND SHUT OFFA 4" WHEEL VALVE AND EXTINGUISHED THE FLAME. THE CALL WAS MADE BY A WELDER DOING RENOVATION WORK IN THE VACANT BUILDING WHO IGNITED THE GAS LINE AS HE ATTEMPTED TO CUT THE PIPE WITH A TORCH.
2025-01-31 10:21 | NO | NO | 19910187 | 1991-11-05 | 18532 | SOUTHERN UNION GAS CO | 2208 HOLLY ST | AUSTIN | TRAVIS | TX | 78702 | 3 | NO | 1850 | 1991-04-07 | 0 | 0 | 2000 | 1605.3033 | 3875.9525 | YES | 1 | 25 |  | 19910407 | 0.5 | 5 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1.25 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROB FRANSON, REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CAR RUN OVER THE METER.
2025-01-31 10:21 | NO | NO | 19910188 | 1991-11-05 | 6830 | GREY FOREST UTILITIES | 6533 CEDAR LANE | SAN ANTONIO | BEXAR | TX | 78249 | 3 | NO | 900 | 1991-03-12 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19910312 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.125 | API5L | DOMESTIC ORIGIN | 1968 | 1968 | UNDER PAVEMENT |  | KIM A. MANN, OPERATIONS MANAGER | 5126958781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-02-27 | YES | 3 | PAINT-STILL VISIBLE | YES
2025-01-31 10:21 | NO | NO | 19910189 | 1991-11-05 | 6830 | GREY FOREST UTILITIES | 15403 WHITE FAWN | SAN ANTONIO | BEXAR | TX | 78255 | 3 | NO | 1145 | 1991-03-11 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19910311 | 30 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0.125 | API5L | DOMESTIC ORIGIN | 1967 | 1968 | UNDER PAVEMENT |  | KIM A. MANN, OPERATIONS MANAGER | 5126958781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GREY FOREST UTILITIES EMPLOYES VASSAR JONES & KEITH SCHNEIDER HAD DRILLED HOLES THROUGH PAVEMENT AND WERE PROBING TO PINPOINT AN UNDERGROUND LEAK. WHEN THE PROBE BAR CAME IN CONTACT WITH THE STEEL MAIN, THEY PRESUMED THEY WERE IN CONTACT WITH A ROCK. THE TIP OF THE PROBE PENETRATED THE MAIN ALLOWING THE ESCAPE OF GAS. THERE WAS AN ELECTRIC DRILL IN USE ON THE SITE WUICH WAS THE APPARENT CAUSE OF IGNITION. MR. VASSAR JONES RECEIVED MINOR BURNS ON THE FACEAND THE SIDES OF HIS HEAD. HE WAS TREATED AT THE HOSPITAL EMERGENCY ROOM AND RELEASED. MR. KEITH SCHNEIDER DID NOT FEEL HE NEEDED TREATMENT AT THE TIMEAND CONTINUED TO WORK. MR. SCHNEIDER LATER COMPLAINED OF BREATHING PROBLEMSAND WAS TAKEN TO THE HOSPITAL EMERGENCY ROOM. HE WAS TREATED AND RELEASED.APPROXIMATELY 188 HOMES HAD TO BE SHUT-OFF AS A RESULT OF THE ACCIDENT., GREY FOREST UTILITIES CREWS WORKED UNTIL ABOUT 9 P.M. MARCH 11TH, 1991, RELIGHTING ALL HOMES WHERE PEOPLE WERE HOME. THE REMAINING HOMES ARE BEING RELIT ASTHE CUSTOMERS CALL.
2025-01-31 10:21 | NO | NO | 19910190 | 1991-11-05 | 18532 | SOUTHERN UNION GAS CO | 9200 BURNET ROAD | AUSTIN | TRAVIS | TX | 78758 | 3 | NO | 1417 | 1991-03-07 | 0 | 0 | 1000 | 802.6516 | 1937.9762 | Null | 0 | 34 |  | 19910307 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0 | API-5L-B |  | 0 | 0 | OTHER | NOT SPECIFIED | ROB FRANSON REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-02-25 | NO | 0 |  | NO |  |  | THIS LINE WAS DAMAGED BY CONTRACTORS EXCAVATING IN A LOCATION AHEAD OF SCHEDULE. OUR REPRESENTATIVES HAD MET WITH EXCAVATOR ON NUMEROUS OCCASIONS AND "EXPOSED" GAS FACILITIES ACCORDING TO A SCHEDULE AGREED TO BY SUG AND EXCAVATOR.
2025-01-31 10:21 | NO | NO | 19910191 | 1991-10-30 | 11680 | LONE STAR GAS CO | 1200 BLK COCKRELL HILL RD | DUNCANVILLE | DALLAS | TX | 75237 | 2 | NO | 1456 | 1991-03-06 | 0 | 0 | 12000 | 9631.8196 | 23255.7147 | Null | 5 | 9 |  | 19910306 | 335 | 364 |  | 546 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | STEEL |  | 30 | 0.312 | GRADE B |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | LOIS ROSS - CLERK | 2146701566 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-03-06 | YES | 0 | PAINT | YES |  |  | HIGH PRESSURE MAIN WAS HIT BY SUB CONTRACTOR FOR TP L WHILE BORING HOLE. E
2025-01-31 10:21 | NO | NO | 19910192 | 1991-10-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 700 PINEY POINT RD | PINEY POINT VILLAGE | HARRIS | TX | 77024 | 3 | NO | 1149 | 1991-03-06 | 0 | 0 | 1365 | 1095.6195 | 2645.3375 | YES | 2 | 51 |  |  | 28 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | PLUGGING UNIT | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | JOE HURST - HOUSTON DIVISION OPERATIONS MANAGER | 7136545900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION | EQUIPMENT FAILURE; PLUGGING UNIT FAILED | OPERATOR'S CONTRACTOR HAD PLUGGED AN EXTENSION FITTING AND WAS PREPARING TO WELD WHEN PLUG FAILED. ESCAPING GAS IGNITED. STREET WAS BLOCKED. E
2025-01-31 10:21 | NO | NO | 19910193 | 1991-10-30 | 18532 | SOUTHERN UNION GAS CO | 11100 BLOCK OF MONTWOOD | EL PASO | EL PASO | TX | 79936 | 3 | NO | 1413 | 1991-01-20 | 0 | 0 | 7340 | 5891.463 | 14224.7455 | Null | 5 | 15 |  | 19910120 | 20 | 60 |  | 2 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL | ABS | 2 | 0.09 | D2513 |  | 0 | 0 | UNDER PAVEMENT |  | EDWARD H SMITH P E - REGIONAL ENGINEER | 5125446300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AUTOMOBILE STRCUK UTILITY POLE ABOVE GROUND CAUSING DAMAGE BELOW GROUND TO OPERATORS FACILITY.
2025-01-31 10:21 | YES | YES | 19910197 | 1991-10-30 | 1800 | BROOKLYN UNION GAS CO | PERKIOMEN AVE & WAINWRIGHT AVE | STATEN ISLAND | RICHMOND | NY | 10312 | 4 | NO | 1022 | 1991-10-01 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19911001 | 32 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT SPECIFIED | OTHER | NOT SPECIFIED | OTHER | NOT SPECIFIED | 0 | 0 |  |  | 0 | 0 | OTHER | SEWER MANHOLE | J L CROSS - SECTION MANAGER - DCD | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON OCTOBER 1, 1991, A N.Y.C. CONTRACTOR EMPLOYEE WAS INJURED WHILE WORKINGIN A SEWER MANHOLE ON PERKIOMEN AVENUE BETWEEN WAINWRIGHT AVE AND DEAD END.A BROOKLYN UNION CHEMIST CONFIRMED THE PRESENCE OF NATURAL GAS IN THE SEWER MANHOLE. THE SOURCE OF NATURAL GAS HAS NOT BEEN DETERMINED.
2025-01-31 10:21 | YES | YES | 19910198 | 1991-11-01 | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | FILLMORE & FOUGERON ST | BUFFALO | ERIE | NY | 14211 | 0 | NO | 250 | 1991-09-29 | 0 | 2 | 0 | 0 | 0 | Null | 2 | 28 |  |  | 26 | 0 |  | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 20 | 0 |  |  | 0 | 1915 | UNDER PAVEMENT |  | ROBERT A DANIELS | 7168577109 | EXTERNALLY | LOCALIZED PITTING | ALSO GENERAL CORROSION | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEES ATTEMPTING TO BAND CLAMP 7/8" X 1 5/8" CORROSION LEAK.
2025-01-31 10:21 | YES | YES | 19910199 | 1991-10-28 | 2748 | CONSUMERS POWER CO | 4653 BAILY BRIDGE RD | MAPLETON | MIDLAND | MI | 48640 | 3 | NO | 1200 | 1991-07-17 | 1 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19910717 | 360 | 400 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | STEEL |  | 10 | 0.25 | STYLE 40 | DRESSER | 0 | 1933 | UNDER GROUND OR UNDER WATER |  | RICHARD R ZOOK SENIOR ENGINEER | 5177997110 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | INADEQUATE RECORDS | INACCURATE RECORDS. FACILITY RECORDS DID NOT SHOW IN-LINE COMPRESSIONFITTING ADJACENT TO PIPE SEGMENT BEING REPLACED. FITTING PULLED OUT WHEN PIPEWAS SEVERED DOWNSTREAM OF FITTING. SUPPLEMENTAL REPORT 3/10/95 INDICATESCHANGE IN PART 2 TO "C" - FROM OTHER TO CONSTRUCTION/OPERATING ERROR. KENNETHELENBAAS 517-788-0635. INADEQUATE RECORDS IN DLKPC - CLASSIFIED AS "OTHER."
2025-01-31 10:21 | YES | YES | 19910200 | 1991-10-18 | 4497 | ENTEX INC | 463 OAK GROVE AVE | GULFPORT | HARRISON | MS | 39502 | 3 | NO | 215 | 1991-10-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 25 |  | 19911008 | 18 | 60 |  | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.133 | API5LC1.I |  | 0 | 1952 | ABOVE GROUND |  | LANNY W GARGILE PE | 7136545105 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19910201 | 1991-10-23 | 3090 | DALTON WATER LIGHT & SINKING FUND COMMISSION | 2470 DUG GAP RD | DALTON | WHITFIELD | GA | 30720 | 3 | NO | 1519 | 1991-09-25 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 15 |  | 19910925 | 14 | 21 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HEATING UNITS | OTHER | UNKNOWN | OTHER | NOT SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DALE BRIDGES | 4042781313 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SERVICE COMPANY PERSONNEL WERE WORKING ON HEAT UNITS. CAUSE STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19910202 | 1991-10-22 | 22189 | WASHINGTON NATURAL GAS CO | 2ND AVE & UNION ST | SEATTLE | KING | WA | 98101 | 4 | NO | 1255 | 1991-09-30 | 0 | 2 | 0 | 0 | 0 | Null | 11 | 30 |  | 19910930 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.5 |  |  | 0 | 1914 | OTHER | POWER VAULT | DOUGLAS DAMM SAFETY MANAGER | 2062242396 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | TWO CITY UNTILITY WORKERS WERE BURNED WHEN THEIR ACTIVITIES INSIDE A POWER VAULT IGNITED NATURAL GAS THAT HAD ACCUMULATED IN THE VAULT. THERE ARE NO GASFACILITIES IN THE VAULT. THE GAS SOURCE IS POSSIBLY A CRACKED 6" CAST IRON LOW PRESSURE GAS MAIN FOUND A FEW FEET FROM THE VAULT. THE CAUSE OF THE CASTIRON FAILURE IS UNKNOWN, ALTHOUGH SUBSIDENCE OF A DITCH LINE IS SUSPECTED.
2025-01-31 10:21 | YES | NO | 19910204 | 1991-10-18 | 15007 | PACIFIC GAS & ELECTRIC CO | 4012 W WHITESBRIDGE | FRESNO | FRESNO | CA | 93706 | 2 | NO | 430 | 1991-09-12 | 0 | 0 | 75200 | 60359.4026 | 145735.8123 | Null | 0 | 59 |  | 19910912 | 50 | 53 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 1949 | ABOVE GROUND |  | W R MAZOTTI VP-GAS & ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE DAMAGED METER AND REGULATOR
2025-01-31 10:21 | YES | YES | 19910205 | 1991-10-17 | 20211 | UNITED CITIES GAS CO | W 8TH ST & OLD JONESBORO RD | METROPOLIS | MASSAC | IL | 62960 | 3 | NO | 1450 | 1991-09-18 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19910918 | 10 | 500 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER |  | OTHER | NOT SPECIFIED | OTHER | NOT SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | MARY G ELLIOTT - OFFICE SUPERVISOR | 6185248196 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | ACCIDENTALLY CAUSED BY OPERATOR | REMOVING ORFICE PLATE FROM PIPE & BLOWING TRASH OUT OF 4" NATURAL GAS PIPE WITH NATURAL GAS PRESSURE - GAS IGNITED FROM PILOT LIGHT ON THE WATER BATH HEATER.
2025-01-31 10:21 | NO | NO | 19910206 | 1991-11-21 | 15007 | PACIFIC GAS & ELECTRIC CO | BERKELEY, OAKLAND, CONTRA COSTA | BERKELEY |  | CA |  | 3 | NO | 1100 | 1991-10-11 | 0 | 0 | 15000 | 12039.7745 | 29069.6434 | Null | 12 | 0 |  | 19911021 | 60 | 60 |  | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN | ALSO SERVICE LINE&METER S | REGULATOR/METER | ALSO RISER | OTHER | NOT SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | W R MAZOTTI VP GAS & ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | BRUSH FIRE GOT OUT OF CONTROL IN HILLS EAST OF OAKLAND AND BERKELEY. BRUSH FIRE LEAD TO BURNING OF APPROXIMATELY 4,000 DWELLING UNITS, DESTROYING OVER 2000 GAS SERVICES AND OVER 3000 GAS METERS,
2025-01-31 10:21 | NO | NO | 19910207 | 1991-11-15 | 2668 | COMMONWEALTH GAS SERVICES INC | 200 SPRING ST | HERNDON |  | VA | 22070 | 3 | NO | 1615 | 1991-10-22 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19911022 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | NOT SPECIFIED | STEEL | MUELLER FITTING | 6 | 0 |  | MUELLER | 0 | 1991 | UNDER PAVEMENT |  | GARY J LAPE DIRECTOR PLANT OPERATIONS | 8043235413 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | COMPANY PERSONNEL, WHILE IN THE PROCESS OF PLACING APPROXIMATE 700' OF RELOCATED 6" WELDED TREATED MAIN IN-SERVICE, INSTALLED A LINE STOPPER AT THE UNSTREAM TIE-IN BEFORE THE DOWNSTREAM FITTING WAS TAPPED. THE RESULTING EFFECT WAS LOSS OF SERVICE TO APPROXIMATELY 1,740 CUSTOMERS. THERE WAS NO DAMAGE TO FACILITIES OR UNSAFE SITUATION. ACTIONS TO RESTORE SERVICE TO CUSTOMERS WERE INITIATED IMMEDIATELY.
2025-01-31 10:21 | YES | YES | 19910208 | 1991-11-13 | 9070 | JACKSONVILLE WATER WORK, GAS & SEWER BOARD | 711 FRANCIS ST EAST | JACKSONVILLE | CALHOUN | AL | 36265 | 3 | NO | 1243 | 1991-10-09 | 0 | 1 | 50000 | 40132.5815 | 96898.8113 | Null | 1 | 25 |  | 19911009 | 20 | 125 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | OTHER | GALY IRON | 1 | 0.25 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | SALLY JOHNSON OFFICE MANAGER | 2054357657 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ABOUT 5 OR MIN TO NOON, WED 18-9-91, I GOT A CALL ON THE RADIO TO GO TO 711 E FRANCIS ST. SOMEONE WAS CUTTING A TREE AND BROKE THE GAS LINE. I WAS TOLD THIS ON THE RADIO BEFOR I WENT OVER THERE. I GOT OVER THERE AND I SAW THE ONE INCH SERVICE LINE WAS BOWED UP IN THE AIR IN A HOLE, NEXT TO THE TREE THAT WAS BEING CUT. WHEN I GOT THERE SOMEONE WAS PULLING AWAY IN A GREEN CHEVROLET PICK UP TRUCK. HE BACKED UP GOT OUT AND CAME OVER TO THE TREE. WHEN HE GOT OVER TO WHERE I WAS I ASKED HE IF KNEW ANYTHING ABOUT WHAT HAPPENED. HE SAID NO. THE MAN LEFT. I LOOKED AT THE GAS LINE. AT THE SAME TIME I COULD SMELL GAS. I SOAPED THE BOW IN THE PIPE. NP LEAK. THEN I PROBED A HOLE AT THE STAND PIPE. I KNEW THAT IT WAS GOING TO HAVE TO BE CUT OFF. A LADY CAME OUT OF THE HOUSE. I LEFT AND WENT BACK TO THE SHOP TO GET THE BACKHOE AND SOME PARTS. I DROVE THE BACK HOE TO THE HOUSE, AND DUG THE LINE UP BACK TOWARD THESTREET, FROM THE BOW. THE LADY ASKED ME WHAT WE WERE GOING TO DO. I SAID WEWOULD HAVE TO DIG UP THE STANDPIPE AND LINE. THE LADY GOT A SHOVEL AND STARTED DIGGING UP HER FLOWERS. I CALLED "ED" MR. BATES TO COME OVER TO THE HOUSE ON E. FRANCIS. I TOLD THE LADY NOT TO WORRY ABOUT THE FLOWERS. ABOUT TIME"ED" MR. BATES DROVE UP. I WAS GOING BACK TO CAP OR PLUG THE GAS LINE OFF AT THE STUMP WHERE I DUG IT UP. I TURNED AROUND AND THERE WAS AN EXPLOSION.
2025-01-31 10:21 | NO | NO | 19910209 | 1991-11-12 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 226 LINCOLN AVE | HARRISON | WESTCHESTER | NY | 10528 | 4 | NO | 1617 | 1991-10-03 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19911022 | 10 | 15 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RICHARD C CAULIN - PLANNING ENGINEER | 2124602838 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER |  | A CONTRACTOR DAMAGED A ONE-INCH MEDIUM PRESSURE GAS SERVICE. MEDIA WERE PRESENT. THERE WERE NO FATALITIES, INJURIES, OR PROPERTY DAMAGE. THIS INCIDENTSHOULD BE REMOVED FROM THE LIST OF INCIDENTS.
2025-01-31 10:21 | YES | NO | 19910210 | 1991-11-12 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 12929 SYLVIA | ELMWOOD | LEELANAU | MI | 49684 | 3 | NO | 1827 | 1991-10-07 | 0 | 0 | 125000 | 100331.4538 | 242247.0283 | Null | 1 | 51 |  | 19911008 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | COMPRESSION FTG PULL-OUT | OTHER | COPPER | 0.625 | 0 |  |  | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | BRUCE J NIEMAN MANAGER CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR FAILED TO CALL MISS DIG, STRUCK AND PULLED SERVICE LINE OUT OF COMPRESSION FITTING BELOW GRADE.
2025-01-31 10:21 | NO | NO | 19910212 | 1991-11-05 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 141 LANZA AVENUE | GARFIELD | BERGEN | NJ | 07026 | 3 | NO | 1440 | 1991-10-08 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 0 | 14 |  | 19911008 | 120 | 120 | BY TEST | 180 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 12 | 0.219 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | C.W. GREVENITZ - V P GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON TUESDAY 10/8/91 AT APPROXIMATELY 2:40 P.M., WHILE PROCEEDING TO UPRATE A 120 PSI DESIGN GAS MAIN FROM 100 PSI TO 120PSI, MULTIPLE FAILURES OCCURED IN THE AREA OF THE METER SET AT THE GARDEN STATE PAPER CO., #141 LANZA AVE., GARFIELD. THE ESCAPING GAS IGNITED AND EXTENSIVE DAMAGED RESULTED. THERE WERE NO INJURIES.
2025-01-31 10:21 | YES | YES | 19910213 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | 3902 MISTY ROSE CT | SUGARLAND | FORT BEND | TX | 77478 | 3 | NO | 2120 | 1991-05-09 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 53 |  | 19910509 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT SPECIFIED IN REPORT | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | DUPONT | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | FLAGGED | YES |  |  | LINE WAS MARKED FOR PRIME CABLE THE PREVIOUS WEEK. COASTAL CONDUIT DID NOT REQUEST. HAS CUT 2" MAIN - AIR COMPRESSOR 6' FROM CUT - GAS IGNIGHTED.
2025-01-31 10:21 | NO | NO | 19910214 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | 4114 KIRKWALL COURT | SUGARLAND | FORT BEND | TX | 77478 | 3 | NO | 900 | 1991-05-16 | 0 | 0 | 25000 | 20066.2908 | 48449.4057 | YES | 0 | 45 |  | 19910516 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | DUPONT "AA" | 1990 | 1991 | UNDER GROUND OR UNDER WATER |  | JOHN SIMONETTI, ASST DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 2 | FLAGS | YES |  |  | WE RECEIVED CALL FROM BRUCE SMITH OF PERRY HOMES AT 9:07 A.M. REPORTING CUT LINE AND FIRE, WE DISPATCHED TO SERVICEMAN & CONSTRUCTION CREW AT 9:07 A.M.WE ARRIVED ON SCENE AT 9:15 A.M. LINE WAS SQUEEZED AT 9:45 A.M. LINE WAS CUT BY PAUL BATES WITH E&M PLUMBING INC., 2306 CENTURIAN CIRCLE, NEW CANEY, TX77357. E&M PLUMBING WAS INSTALLING LATERAL WATER LINE TO 4114 KIRKWALL CT. FOR PERRY HOMES.
2025-01-31 10:21 | NO | NO | 19910215 | 1991-11-05 | 11680 | LONE STAR GAS CO | 220 BLK. FIVE MILE PARKWAY | DALLAS | DALLAS | TX | 75224 | 3 | NO | 2040 | 1991-05-24 | 0 | 0 | 9000 | 7223.8647 | 17441.786 | YES | 3 | 34 |  | 19910524 | 24 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | FITTING | NOT SPECIFIED IN REPORT | STEEL |  | 4 | 0 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LOIS ROSS-CLERK | 2146701566 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | RUSHING AND RISING WATER IN FIVE MILE CREEK WASHED OUT AND BROKE 4" LP WRAPPED STEEL MAIN.
2025-01-31 10:21 | NO | NO | 19910216 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | 2917 FM 525 | HOUSTON | HARRIS | TX | 77032 | 3 | NO | 1908 | 1991-05-30 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 7 |  |  | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE2306 | DUPONT | 0 | 1991 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMOTTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-29 | YES | 0 |  | YES |  |  | CONTRACTOR BROKE PLASTIC MAIN WHILE INSTALLING DRAINAGE SYSTEM. TRAFFIC WASREROUTED UNTIL AREA WAS MADE SAFE.
2025-01-31 10:21 | NO | NO | 19910218 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | 9988 WINDMILL LAKES "B" | HOUSTON | HARRIS | TX | 77075 | 3 | NO | 1421 | 1991-06-12 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 57 |  |  | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2306 | DUPONT | 0 | 1983 | UNDER GROUND OR UNDER WATER |  | JOHN SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-06-06 | YES | 3 | PAINT ON GROUND | NO |  |  | PIPE WAS INCORRECTLY LOCATED. CONTRACTOR CUT PLASTIC MAON WITH A CORING AUGUR. FIRE DEPARTMENT EVACUATED NEARBY APARTMENT COMPLEX UNTIL AREA WAS MADE SAFE.
2025-01-31 10:21 | NO | NO | 19910219 | 1991-11-05 | 18532 | SOUTHERN UNION GAS CO | HWY. 183 AT GREAT HILLS TR. | AUSTIN | TRAVIS | TX | 78759 | 3 | NO | 920 | 1991-06-15 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 |  | 19910615 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.141 | API5L GRADE A25 | N/A | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | ROB FRANSON, REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-31 | NO | 0 |  | NO |  |  | WHILE EXCAVATING WITH KOMATSU D355A DOZER FOR COMMERCIAL DRIVEWAY APPROACH, CONTRACTOR PULLED 4" WS MAIN APART WITH RIPPER BLADE.
2025-01-31 10:21 | NO | NO | 19910220 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | 4700 BELLAIRE | HOUSTON | HARRIS | TX | 77025 | 3 | NO | 1220 | 1991-06-20 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 20 |  | 19910620 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE2406 | DUPONT | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | ROB W. CARGILE, PE OPERATING ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-31 | YES | 2 |  | NO |  |  | TRAFFIC MAINTENANCE CUT 4", TRAFFIC RE-ROUTED AND POLICE DEPARTMENT EVACUATEDAN OFFICE BUILDING.
2025-01-31 10:21 | NO | NO | 19910221 | 1991-11-05 | 4473 | ENERGAS CO | 3316 ANDREWS HIGHWAY | MIDLAND | MIDLAND | TX | 79703 | 3 | NO | 540 | 1991-06-23 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19910623 | 11 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID V. HAYES, JR. P.E., ENGINEERING SUPERVISOR | 8067984464 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AUTOMOBILE WAS STOLEN BY UNKNOWN PARTY. OUR NOTIFICATION WAS BY THE MIDLANDPOLICE DEPARTMENT. DRIVER OF VEHICLE FLED SCENE AFTER ACCIDENT. DRIVER L;OST CONTROL OF VEHICLE AND RAN INTO METER SETTING. SUBSEQUENT FIRE DESTROYED CAR AND METER SETTING.
2025-01-31 10:21 | NO | NO | 19910222 | 1991-11-05 | 18104 | SAN ANTONIO,CITY PUBLIC SERVICE BOARD OF | 11700 BLOCK WURZBACH | SAN ANTONIO | BEXAR | TX | 78230 | 3 | NO | 500 | 1991-06-28 | 0 | 0 | 30372 | 24378.1353 | 58860.214 | Null | 4 | 0 |  | 19910628 | 168 | 170 | BY TEST | 400 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 24 | 0.25 | API5L-X42 |  | 1962 | 1962 | UNDER PAVEMENT |  | T.L. NARENDORF - PROJECT ENGINEER | 5129783766 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-12-15 | YES | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19910223 | 1991-11-05 | 18532 | SOUTHERN UNION GAS CO | 500 PAMPA DRIVE | AUSTIN | TRAVIS | TX | 78752 | 3 | NO | 838 | 1991-07-03 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 34 |  | 19910703 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | NO ENTRY | BODY OF PIPE |  | OTHER | NO ENTRY | 0.75 | 0.095 | ASTM D2513 | PLEXCO | 0 | 1987 | OTHER | NO ENTRY | ROBERT FRANSON, REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | POLYETHYLENE YARDLINE DID HAVE WARNING TAPE IN DITCH. PLUMBER WORKING ON SPRINKLER SYSTEM DAMAGED SERVICE AND IGNITED GAS.
2025-01-31 10:21 | NO | NO | 19910224 | 1991-11-05 | 18532 | SOUTHERN UNION GAS CO | 6615 NORTH LAMAR | AUSTIN | TRAVIS | TX | 78751 | 3 | NO | 1155 | 1991-07-13 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 55 |  | 19910715 | 15 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.75 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ROBERT FRANSON, REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-07-13 | YES | 2 |  | NO |  |  | BACKHOE POERATOR DAMAGE THE GAS SERVICE LINE.
2025-01-31 10:21 | NO | NO | 19910226 | 1991-11-05 | 11680 | LONE STAR GAS CO | 113 W. MORSE STREET | FREDERICKSBURG | GILLESPIE | TX | 78624 | 3 | NO | 1028 | 1991-07-23 | 0 | 0 | 10000 | 8026.5163 | 19379.7623 | Null | 0 | 15 |  | 19910723 | 10 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NO ENTRY | OTHER | NO ENTRY | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | PHILLIP MURDOCK - MANAGER | 2146702229 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | MRS. COOPER BACKED INTO OUR METER AND REGULATOR PULLING THE REGULATOR FROM THE BASE.
2025-01-31 10:21 | NO | NO | 19910227 | 1991-11-05 | 18532 | SOUTHERN UNION GAS CO | 3400 OWEN AVE | AUSTIN | TRAVIS | TX | 78705 | 3 | NO | 1353 | 1991-07-23 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 32 |  | 19910723 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | API-5L-A25 | N/A | 0 | 1976 | UNDER GROUND OR UNDER WATER |  | ROBERT FRANSON, REGIONAL ENGINEER | 5124751101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-05-21 | YES | 2 |  | NO |  |  | LOCATIONS PROVIDED 5/23/91 AND JOB MONITORED PERIODICALLY. WHILE TRENCHING TO INSTALL TELEPHONE CABLE, CONTRACTOR CUT 1 1/4" GAS SERVICE.
2025-01-31 10:21 | NO | NO | 19910229 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | HARBOR AT ZOLTOWSKI | HOUSTON | HARRIS | TX | 77020 | 3 | NO | 1931 | 1991-07-25 | 0 | 0 | 30794 | 24716.8543 | 59678.0399 | Null | 13 | 0 |  |  | 65 | 160 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | API5L |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PAVING CONTRACTOR CUT STEEL MAIN WHILE EXCAVATING. NO IGNITION
2025-01-31 10:21 | NO | NO | 19910230 | 1991-11-05 | 4499 | ENTEX - DIVISION OF ARKLA INC | 4574 GRIGGS | HOUSTON | HARRIS | TX | 77021 | 3 | NO | 1700 | 1991-08-01 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  |  | 80 | 160 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 16 | 0.25 | API5L |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOHN R. SIMONETTI, ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CITY WATER CO. KNOCKED TAP OFF A 16" MAIN. 4500 GRIGGS BLOCKED BOTH DIRECTIONS.
2025-01-31 10:21 | NO | NO | 19910231 | 1991-10-30 | 1684 | BRACKETTVILLE, CITY OF, HOUSING AUTH OF | WEST SPRING ST | BRACKETTVILLE | KINNEY | TX | 78832 | 0 | NO | 935 | 1991-08-13 | 0 | 0 | 1828 | 1467.2472 | 3542.6205 | Null | 0 | 30 |  | 19910813 | 21 | 60 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0 |  |  | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | DAVID MARTINEZ JR UTILITY SUPERINTENDENT | 5125632412 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE | CENTRAL POWER AND LIGHT | AT APPROXIMATLY 9:35 A.M. MR. JAY HAM, SUPERINTENDENT OF THE RIEMER CALHOUN,JR'S NEW SENOIR CITIZENS PROJECT CAME INTO MY OFFICE AND INFORMED ME THAT C.P.L. HAD DRILLED INTO THE MAIN DISTRIBUTION LINE COMING INTO BRACKETTVILLE FRLOM THE VALERO SUB-STATION. AT 9:40 A.M. WE DISPATCHED SOME MEN TO SHUT OFF THE MAIN LINE AND ALSO WE HAVE AT THIS TIME DISPATCHED A CITY EMPLOYEE, RANDOLPH CASTILLAS, TO INFORM THE PUBLIC VIA P.A. SYSTEM OF THE CUT-OFF OF THE GASUTILITY. AT 9:55 AM, I CALLED MR. JEFF STRACENTER, AREA MANAGER, C.P.L. IN DEL RIO, TEXAS AND INFORMED HIM OF THE INCIDENT. AT 10:02 A.M. MR. BUSTER STRZELZIKI AREA SUPEVISOR, FROM VALERO (PHONE NO. (512) 876 5784, CARRIZA SPRINGS, TX, HAS DISPATCHED 2 OF HIS MEN TO ASSIST US IN THIS CRISIS. HE SAID THAT IF COULD BE OF FURTHER ASSISTANCE TO BE SURE AND CALL HIM UP. 10:50 A.M. MR. TOM FINNEY, TEXAS RAILROAD COMMISSION CALLED AND SAID THAT ANYTIME SOMETHING LIKE THIS HAPPENS TO NOTIFY HIS DEPARTMENT IMMEDIATELY AT (512) 463 7046 -I INFORMED HIM OF THIS INCIDENT FROM THE TIME IT WAS REPORTED TO THE TIME HECALLED IN. I HAD JOSIE GOMEZ, RANDY CASTILLAS, D.VILLAREAL AND GILBERT SANCHEZ GO AROUND THE CITY AND SHUT OFF THE GAS. THEY WILL ALSO BE THE ONES TO GO AROUND AND TURN ON THE GAS AFTER THE LINE IS REPAIRED.
2025-01-31 10:21 | NO | NO | 19910233 | 1991-10-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 4101 CLOVER | HOUSTON | HARRIS | TX | 77051 | 3 | NO | 230 | 1991-08-21 | 0 | 0 | 25000 | 20066.2908 | 48449.4057 | Null | 0 | 35 |  |  | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API5L |  | 0 | 1969 | ABOVE GROUND |  | JOHN R SIMONETTE ASSISTANT DIR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CAR HIT GAS METER - ESCAPING GAS INGNITED - DAMAGE TO METER ABD REGULATOR, CAR AND BUILDING.
2025-01-31 10:21 | NO | NO | 19910234 | 1991-10-30 | 17660 | ROMA GAS DEPT, CITY OF | HWY 83 1 1/2 MILE OF ROMA CITY LIMIT | ROMA | STARR | TX | 78584 | 3 | NO | 945 | 1991-08-22 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19910823 | 28 | 50 |  | 50 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | NON GIVEN | POLYETHYLENE PLASTIC | PVC SCH.40 | 4 | 0.25 | 220 PSIC73 ASTM |  | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | TOMAS CANTU GAS DEPT | 5128491411 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | MOVEMENT OF DIRT BY PREVIOUS CONSTRUCTION IN VICINITY OF GAS MAIN. WATER LINE WAS INSTALLED NEXT TO GAS MAIN, A BORE ACROSS HIGHWAY 83 WAS DONE, AT THIS POINT WAS WHERE THE EARTH SETTLE AND BROKE GAS MAIN.
2025-01-31 10:21 | NO | NO | 19910235 | 1991-10-30 | 1704 | BRAZOS RIVER GAS CO | INTERSECTION COUTS & CHARLES | WEATHERFORD | PARKER | TX | 76086 | 3 | NO | 135 | 1991-08-30 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  |  | 13 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | PAUL R JOHNSON VICE PRESIDENT | 8173254445 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | UNKNOWN AUTOMOBILE RAN THROUGH BARRACADE DESTROYING AN INTERMEDIATE PRESSURETO LOW PRESSURE REGULATOR STATION.
2025-01-31 10:21 | NO | NO | 19910236 | 1991-10-30 | 18532 | SOUTHERN UNION GAS CO | 700 VARGAS RD (AT PONCA) | AUSTIN | TRAVIS | TX | 78741 | 3 | NO | 1543 | 1991-09-16 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 4 |  | 19910916 | 20 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1952 | UNDER PAVEMENT |  | ROBERT FRANSON, REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE | SUBSIDENCE | NO |  | NO | 0 |  | NO |  |  | 4" CAST IRON MAIN CRACKED UNDER ROADWAY.
2025-01-31 10:21 | NO | NO | 19910237 | 1991-10-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 13700 PARADISE VALLEY | HOUSTON | HARRIS | TX | 77069 | 3 | NO | 1325 | 1991-09-23 | 0 | 0 | 1404 | 1126.9229 | 2720.9186 | Null | 0 | 15 |  |  | 25 | 60 |  | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | DUPONT | 0 | 1976 | UNDER GROUND OR UNDER WATER |  | JOHN R SIMONETTI ASST DIR OPER | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-07-30 | YES | 2 |  | NO |  |  | OUTSIDE CONTRACTOR CUT 2" PLASTIC MAIN RESULTING IN THE LOSS OF 72 ACTIVE SERVICES. MARKED LINES ON 8-1-91, CHECKED ON 8-2-91-STILL MARKED. RE-MARKED LINES ON 8-6-91, CHECKED ON 8-8-91 - STILL MARKED.
2025-01-31 10:21 | NO | NO | 19910238 | 1991-10-30 | 4473 | ENERGAS CO | 5000 AVENUE H | LUBBOCK | LUBBOCK | TX | 79404 | 3 | NO | 1409 | 1991-09-24 | 0 | 0 | 15000 | 12039.7745 | 29069.6434 | YES | 2 | 0 |  | 19910924 | 45 | 60 | BY TEST | 60 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.0188 | APT5LGB |  | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | DAVID V HAYES P E ENGINEERING SUPERVISOR | 8067984464 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 | VENT PIPE AT R.O.W. LIMIT | YES
2025-01-31 10:21 | NO | NO | 19910239 | 1991-10-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 1313 LOMBARDY | HOUSTON | HARRIS | TX |  | 3 | NO | 1924 | 1991-10-04 | 0 | 0 | 16150 | 12962.8238 | 31298.3161 | Null | 0 | 31 |  |  | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0 | 0.133 | API 5L |  | 0 | 1975 | ABOVE GROUND |  | JOHN R SIMONETTI ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CAR HIT GAS METER, ESCAPING GAS INITED, DAMAGE TO CAR, GAS METER & REGULATOR.
2025-01-31 10:21 | NO | NO | 19910240 | 1991-10-30 | 6930 | GULFSIDE GAS CO | 10305 MAIN ST | MACDONA | BEXAR | TX | 78054 | 3 | NO | 600 | 1991-05-05 | 0 | 0 | 3745 | 3005.9304 | 7257.721 | YES | 1 | 10 |  | 19910505 | 10 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | METER SETTING SEVERED | OTHER | NON SPECIFIED | 0 | 0 | AL-175 | SINGER | 0 | 1991 | ABOVE GROUND |  | DAVID R LYNN AREA SUPERINTENDENT | 5124293017 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | RECIEVED CALL @ 6:30 AM 5-5-91 FROM BEXAR CO. FIRE ALARM I.E. VEHICLE ON FIRE @ 10305 MAIN ST MACDONA RX. ARRIVED 7:10 AM. AFTER A BRIEF INSPECTION OF SITUATION, IT WAS DETREMINED BEST COURSE OF ACTION WAS TO TURN GAS OFF@ MACDONA REGULATOR STATION. THE AREA WAS DEEMED SAFE @ APPROX. 7:!5 AM. AT THAT TIME, LOCAL FIRE DEPT & WRECKER SERVICE PROCEEDED TO REMOVE BURNT VEHICLE FROM THE AREA. THE DAMAGED METER SET WAS RESTORED. THE GAS WAS TURNED ON @ MACDONA REGULATOR STATION. A HOUSE-TO-HOUSE CHECK OF MACDONA ACCOUNTS WAS CONDUCTED TO INFORM CUSTOMERS OF THE INCIDENT & RELIGHT ALL APPLIANCE PILOTS.
2025-01-31 10:21 | NO | NO | 19910241 | 1991-01-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 2403 HODGES BEND CIRCLE | SUGAR LAND | FORT BEND | TX | 77478 | 3 | NO | 915 | 1991-05-03 | 0 | 0 | 10000 | 8026.5163 | 19379.7623 | YES | 1 | 10 |  | 19910503 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 75 | 0.0095 |  | DUPONT | 0 | 1979 | UNDER GROUND OR UNDER WATER |  | JOHN R SIMONETTI ASSISTANT DIR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-03-27 | NO | 0 |  | YES |  |  | A WORKER FOR C-JO WAS OPERATING A DITCHING MACHINE AND CUT A 3/4" SERVICE LINE. THE GAS IGNITED CAUSING IT TO BURN THE DITCHING MACHINE AND A COUPLE OF HUSHES IN THE YARD.
2025-01-31 10:21 | NO | NO | 19910242 | 1991-10-30 | 18532 | SOUTHERN UNION GAS CO | 505 S KANSAS | EL PASO | EL PASO | TX | 79901 | 0 | NO | 720 | 1991-04-26 | 0 | 0 | 1500 | 1203.9774 | 2906.9643 | Null | 1 | 0 |  | 19910426 | 4 | 8 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | OTHER | MELLEABLE IRON 1/2"X1/4" | 0 | 0 |  |  | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | EDWARD H SMITH P E REGIONAL ENGINEER | 9155214656 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR DEMOLISHING A STRUCTURE AT 505 S. KANSAS CAUSED A WALL TO COLLAPSE. THE WEIGHT OF THE DEBRIS FALLING ON A 1 1/4" GAS RISER RESULTED IN THE FAILURE OF THE ELL ON THE BOTTOM OF THE RISER.
2025-01-31 10:21 | NO | NO | 19910243 | 1991-10-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 6810 LON HOLLOW DR | HOUSTON | HARRIS | TX | 77088 | 3 | NO | 1252 | 1991-04-24 | 0 | 0 | 5350 | 4294.1862 | 10368.1728 | Null | 1 | 3 |  |  | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2306 | DUPONT | 0 | 1978 | UNDER GROUND OR UNDER WATER |  | JOHN R SIMONETTI ASSISTANT DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO | 1991-04-15 | NO | 0 |  | NO |  |  | CONTACTOR TOLD OPERATOR THAT HE WOULD NOT BE WORKING NEAR THIS MAIN AND WOULD NOT NEED IT MARKED UNTIL LATER IN THE WEEK, THEN HE HIT IT.
2025-01-31 10:21 | NO | NO | 19910245 | 1991-10-30 | 4473 | ENERGAS CO | 1101 POLK | AMARILLO | POTTER | TX | 79105 | 3 | NO | 1430 | 1991-04-12 | 0 | 0 | 200 | 160.5303 | 387.5952 | YES | 0 | 30 |  | 19910412 | 0.5 | 1 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | TEMPORARY CLAMP | OTHER | NON SPECIFIED | 6 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAVID V HAYES JR P.E. - ENGINEERING SUPERVISOR | 8067984464 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | A COMPANY CREW WAS REMOVING AN OLD CLAMP-ON SERVICE SADDLE TAP ON A LOW PRESSURE (APPROXIMATLEY 0.5 PSI) MAIN. THE SADDLE HAD BEEN REMOVED AND A TEMPORARY CLAMP HAD BEEN INSTALLED. THE OPERATOR IN THE EXCAVATION WAS CLEANING THEMAIN WITH AN ELECTRIC GRINDER SO A "HALF SOLE" COULD BE INSTALLED. THE TEMPORARY CLAMP WAS KNOCKED OFF THE MAIN RELEASING GAS INTO THE ATMOSPHERE RESULTING IN A FIRE. THE FIRE BURNED THE OPERATOR ON BOTH ARMS FROM THE WRISTS TO THE ELBOWS. THE OPERATOR WAS TREATED AT A HOSPITAL AND RELEASED THAT SAME DAY. THERE WAS NO OTHER INJURIES.
2025-01-31 10:21 | YES | NO | 19910247 | 1991-11-26 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | HUDSON ST -BET SHEFFIELD & HOHMAN AVES | HAMMOND | LAKE | IN | 46320 | 3 | NO | 915 | 1991-10-26 | 0 | 0 | 80000 | 64212.1304 | 155038.0981 | Null | 2 | 50 |  | 19911026 | 40 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | JOINT, SCREWED | OTHER | GALVANIZED STEEL | 8 | 0.219 |  |  | 0 | 1924 | UNDER GROUND OR UNDER WATER |  | D M CAMPOS - MGR GAS CONTROL & STORAGE | 2198535603 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19910248 | 1991-11-26 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | JACKSON STREET | HUMNOKE | LONOKE | AR | 72072 | 3 | NO | 2207 | 1991-10-29 | 0 | 1 | 75000 | 60198.8723 | 145348.217 | Null | 7 | 38 |  | 19911030 | 16 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0 |  |  | 1952 | 1952 | UNDER GROUND OR UNDER WATER |  | JIM BREWER - CODES & PROCEDURES COORDINATOR | 5013774771 | EXTERNALLY | LOCALIZED PITTING |  | OTHER | GRAFFITIZATION | COATED | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A HOLE WAS DISCOVERED IN THE 2" CAST IRON MAIN APPROXIMATELY 93' AWAY FROM THE HOUSE. THE MAIN WAS ON THE STREET FROM THE HOUSE. THE INVESTIGATION IS STILL ON GOING TO DETERMINE IF NATURAL GAS MIGRATED ACROSS THE STREET AND YARDTO TYHE HOUSE.
2025-01-31 10:21 | NO | NO | 19910249 | 1991-11-27 | 15441 | PETROLANE WYOMING GAS SERVICE | 110 NORTH POWER RIVER | MOORCROFT | CROOK | WY | 82721 | 1 | NO | 1430 | 1991-11-21 | 0 | 0 | 16000 | 12842.4261 | 31007.6196 | Null | 0 | 20 |  | 19911121 | 20 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | OTHER | NON SPECIFIED | STEEL |  | 2 | 0.154 |  |  | 1968 | 1968 | ABOVE GROUND |  | DOYLE HEYING - AREA OPERATIONS MANAGER | 3076829325 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES
2025-01-31 10:21 | YES | YES | 19910250 | 1991-11-30 | 12642 | MOBILE GAS SERVICE CORP | 1101 INDUSTRIAL PARKWAY (ALABAMA HWY 158 | SARALAND | MOBILE | AL | 36571 | 2 | NO | 1440 | 1991-11-01 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 1 |  | 19911101 | 30 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 4 | 0.0395 | PE 2406 | PLEXCO | 1990 | 1991 | OTHER | EXCAVATION | JIMMIE L BUTLER ENGINEERING MANAGER | 2054762720 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | WHILE PURGING AIR FROM APPROXIMATLEY 300' OF NEW 4" PLASTIC GAS MAIN WITH GAS, AN IGNITION OCCURRED WHICH LASTED LESS THAN 30 SECOUNDS. AS A RESULT OF THE IGNITION, THREE EMPLOYEES WERE BURNED. THE COMPANY'S OPERATIONS AND MAINTENANCE MANUAL CONTAINS SPECIFIE PROCEDURES FOR PURGING AIR FROM MAINS AND FORTHE CONTROL OF STATIC ELECTRICITY. AN INVESTIGATION OF THE INCIDENT IS IN PROGRESS.
2025-01-31 10:21 | YES | YES | 19910251 | 1991-12-03 | 11680 | LONE STAR GAS CO | 11 CAROLINA | GREENVILLE | HUNT | TX |  | 3 | NO | 1905 | 1991-10-28 | 0 | 2 | 125000 | 100331.4538 | 242247.0283 | Null | 3 | 0 |  | 19911028 | 8 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1959 | WITHIN/UNDER BUILDING |  | PHILLIP MURDOCK - MANAGER | 2146702229 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | FIRE AND APPARENT EXPLOSION OCCURRED AT RESIDENCE. HEAVY RAIN AND LIGHTNINGWAS OCCURRING AT TIME OF INCIDENT. HOME WAS TOTALLY DESTROYED, GARAGE AND AUTOMOBILES WERE DAMAGED. TWO PERSONS WERE INJURED WITH FIRST AND SECOND DEGREE BURNS. INITIAL LEAK TEST ON HOUSE PIPING WAS IMPOSSIBLE. BAR TESTING AT FRONT OF HOUSE REVEALED SOME LEAKAGE. EXTENSIVE BAR TESTING COULD NOT BE DONE DUE TO HEAVY RAINS FALLING AT THE TIME OF INCIDENT. DAMAGE TO SERVICE LINESERVING THE RESIDENCE WAS DISCOVERED.
2025-01-31 10:21 | YES | YES | 19910252 | 1991-12-06 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | RAVENNA GATE STATION | RAVENNA | MUSKEGON | MI | 49451 | 2 | NO | 1020 | 1991-11-09 | 0 | 1 | 300000 | 240795.4892 | 581392.868 | Null | 3 | 25 |  | 19911109 | 165 | 275 | BY TEST | 550 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRUCE J NIEMAN - MANAGER CODES & STANDARDS | 3132566615 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | WHILE MAKING AN INSPECTION OF AN ORIFICE FITTING, EMPLOYES INADVERTENTLY OPENED AN INTERNAL VALVE IN THE ORIFICE FITTING CAUSING A RELEASE OF GAS.
2025-01-31 10:21 | NO | NO | 19910255 | 1991-10-10 | 11800 | LOUISIANA GAS SERVICE CO | INTERSECTION OF LA HWY 443 & FREIDRICH R | HAMMOND | TANGIPAHOA | LA | 70404 | 2 | NO | 1247 | 1991-11-25 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 13 |  |  | 80 | 98 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0.216 | API-5L |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | D L MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A DENT IN THE PIPE WAS SUSTAINED IN THE SUMMER OF 1991 AND CAUSED A CRACK INTHE PIPE ON 11-25-91. DAMAGE WAS DONE BY AN OUTSIDE PARTY DIGGING WITH A BACK HOE.
2025-01-31 10:21 | NO | NO | 19910256 | 1991-12-06 | 12582 | MISSISSIPPI VALLEY GAS | 3RD ST, MEADOWBROOK ST | BROOKSVILLE | NOXUBEE | MS | 39739 | 3 | NO | 430 | 1991-11-20 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 0 | 45 |  | 19911120 | 22 | 25 | BY TEST | 40 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | OTHER | NON SPECIFIED | JOE J POWELL JR - VICE PRESIDENT - TECHNICAL SERVICES | 6019616853 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | NON SPECIFIED | NO |  | NO | 0 |  | NO |  |  | ON NOVEMBER 20, 1991 AT APPROXIMATELY 4:30 A.M. C.S.T., TORNADO STRUCK THE TOWN OF BROOKSVILLE. MISSISSIPI AND DESTROYED OR HEAVILY DAMAGED APPROXIMATELY30 BUILDINGS. MISSISSIPPI VALLEY GAS HAS A RESIDENT MANAGE IN THE AREA AND HE IMMEDIATELY TURNED OFF GAS TO ALL METERS WHERE DAMAGE HAD OCCURRED. THEREWERE NO FIRES, PERSONAL INJURIES OR DEATHS CAUSED BY THE ESCAPED GAS. AT THE TIME THE TELEPHONE REPORT WAS MADE THESE FACTS WERE KNOWN; HOWEVER, THE NUMBER OF LEAKS ON CUSTOMER'S PREMISES AND THE NUMBER OF LEAKS ON COMPANY PROPERTY WERE NOT DETERMINED AND IT WAS APPARENT THAT THE TOTAL DAMAGE IN THE TOWN WOULD BE IN EXCESS OF $50,000. IT IS THE COMPANY'S CONTENTION THAT THIS WAS NEVER AN INCIDENT BECAUSE THE ESCAPING GAS DID NOT CAUSE ANY DAMAGE, INJURIESOR DEATHS; HOWEVER, IN THE PREVIOUS OCCURRENCE WHERE FLOOD WATERS BROKE CAUSED NO PERSONAL INJURIES, DEATHS OR PROPERTY DAMAGE, THE CHIEF OF PIPELINE SAFETY FOR THE STATE OF MISSISSIPPI MAINTAINED THAT AN INCIDENT REPORT SHOULD HAVE BEEN FILED AND THE OFFICE OF PIPELINE SAFETY HAS SUGGESTED THAT THE COMPANY BE FINED FOR NOT DOING SO. AT THIS TIME THE MATTER IS NOT RESOLVED. THIS IS THE REASON THAT A TELEPHONE REPORT WAS MADE. AFTER THE TELEPHONE REPORT WAS MADE IT WAS DETERMINED THAT GAS ESCAPED FROM ONLY TWO LOCATIONS ON COMPANYFACILITIES. BOTH WERE SERVICES AND THE OCCURRED AT THE RISER. THE GAS CAUSED NO INJURIES OR DEATHS. IT IS NOT KNOWN WHETHER ANYONE WAS INJURED BY THE SAME FALLING MATERIAL THAT DAMAGED THE RISERS. ONE RESIDENCE WAS A HOUSE TRAILER AND THE OTHER A SMALL HOUSE AND IT IS BELIEVED THAT DAMAGE DID NOT REACH&50,000 TO THESE FACILITIES.
2025-01-31 10:21 | NO | NO | 19910257 | 1991-12-16 | 18532 | SOUTHERN UNION GAS CO | 2121 PORTLAND | EL PASO | EL PASO | TX | 79930 | 3 | NO | 930 | 1991-11-22 | 0 | 0 | 55000 | 44145.8397 | 106588.6925 | YES | 0 | 15 |  | 19911122 | 0.25 | 0.5 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | BODY OF PIPE |  | STEEL |  | 0.5 | 0.125 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LYNDAL D CHOWNING S & I SUPERVISOR | 9155446300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ALL DUE TO THE WATER LEAKING FROM THE KITCHEN SINK ONTO A 1/2" GASLINE THAT EVIDENTLY CAUSED THE PIPE TO CORRODE TO THE POINT WHERE A GAS LEAK DEVELOPED UNDER THE CRAWL SPACE OF THE BUILDING. THE PILOT LIGHT ON THE WATER HEATER IN THE KITCHEN MOST LIKELY PROVIDED THE SOURCE OF IGNITION RESULTING IN THE DESTRUCTION OF THE HOUSE AT APPROXIMATELY 9:30 AM.
2025-01-31 10:21 | NO | NO | 19910258 | 1991-12-19 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 29-05 21ST AVE | QUEENS |  | NY | 11105 | 4 | NO | 2101 | 1991-10-20 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19911020 | 0 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | OTHER | NON SPECIFIED | RICHARD C GAULIN - PLANNING ENGINEER | 2124602838 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NATURAL GAS WAS NOT INVOLVED.
2025-01-31 10:21 | NO | NO | 19910259 | 1991-12-13 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 101 FANNIN ST | SHREVEPORT | CADDO | LA | 71101 | 3 | NO | 1346 | 1991-11-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 14 |  | 19911114 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | TAP TREE | FITTING |  | POLYETHYLENE PLASTIC |  | 8 | 0.75 | PE2405 TYPE 2 | PLEXCO | 1990 | 1991 | UNDER GROUND OR UNDER WATER | OPEN TRENCH | THOMAS L CUMMINS DISTRICT MANAGER | 3184292523 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | ARKLA'S AGENT WAS IN THE PROCESS OF TAPING OUT AN 8" X 3/4" TAP TEE. THE CONTRACTOR HAD TROUGLE WITH THE CUTTER IN THE 8" X 3/4" TAP TEE BECAUSE IT WOULD NOT PENETRATE THE 8" PLASTIC MAIN. THEY, THEN, ATTEMPTED TO DRILL THE TAP HOLE OUT IN ORDER TO REMOVE THE MELT BEAD. THE DRILL BIT WENT FAUTHER THAN ECPECTED AND PENETRATED THE 8" MAIN. THE GAS ESCAPED THROUGH THE HOLE AND WASIGNITED BY THE DRILL. TWO CONTRACT WORKERS WERE TREATED AND RELEASED THAT DAY ON AN OUT PATIENT BASIS.
2025-01-31 10:21 | YES | YES | 19910260 | 1991-12-16 | 22189 | WASHINGTON NATURAL GAS CO | 802 N PEARL ST | CENTRALIA | LEWIS | WA | 98531 | 3 | NO | 1115 | 1991-12-06 | 0 | 2 | 100000 | 80265.1631 | 193797.6227 | Null | 30 | 0 |  | 19911206 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN | ALSO SERVICE LINE | JOINT | SWING | STEEL |  | 2 | 0 |  |  | 0 | 1910 | WITHIN/UNDER BUILDING |  | DOUGLAS DAMM, SAFETY MANAGER | 2062242396 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-08-29 | YES | 0 |  | YES |  |  | EXPLOSION AND RESULTING FIRE DESTROYED RESIDENTIAL TRIPLEX, INJURED TWO OCCUPANTS OF ONE UNIT. SUSPECTED SOURCE OF NATURAL GAS IS A 3/4" STEEL SERVICE BROKEN AT THE MAIN IN THE ALLEY BEHIND 802 N PEARL ST. THE BREAK APPARENTLY OCCURRED DUE TO POOR COMPACTION BY A SEWER CONTRACTOR OF A SIXTEEN FOOT DEEP TRENCH, CAUSING DOWNWARD PRESSURE ON THE GAS SERVICE CONNECTION TO THE MAIN. TIME THAT BREAK OCCURRED IS UNKNOWN AS IS THE QUESTION OF HOW GAS ENTERED THEHOUSE.
2025-01-31 10:21 | NO | NO | 19910261 | 1991-12-30 | 1640 | BOSTON GAS CO | 601 ALBANY ST | BOSTON | SUFFOLK | MA |  | 4 | NO | 1820 | 1991-12-02 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 3 |  |  | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NON SPECIFIED | CAST IRON |  | 12 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | LEO T CODY - MANAGER DISTRIBUTION ADMINISTRATION | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | G IN BURNS TO ONE EMPLOYEE'S FACE AND BURNS TO A SECOND EMPLOYEE'S FACE AND WRIST. THE TRENCH WAS IN CLOSE PROXIMITY TO AN ELECTRIC COMPANY DUCT LINE, CONTAINING BARE WIRES.
2025-01-31 10:21 | YES | YES | 19910262 | 1991-12-30 | 2568 | COLORADO SPRINGS, CITY OF | 540 ASBURY PLACE | COLORADO SPRINGS | EL PASO | CO | 80906 | 3 | NO | 825 | 1991-11-27 | 0 | 1 | 73000 | 58593.569 | 141472.2646 | Null | 1 | 30 |  | 19911127 | 18 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1952 | UNDER GROUND OR UNDER WATER |  | WAYNE E BROOKER - ENGINEERING/OPERATIONS MANAGER | 7196365722 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-06-25 | YES | 2 |  | YES |  |  | A RESIDENCE AND ITS CONTENTS WERE DESTROYED BY AN EXPLOSION AND FIRE RESULTING IN MINOR INJURIES TO TWO ELDERLY OCCUPANTS. THE APPARENT CAUSE OF THE ACCIDENT WAS GAS LEAKING FROM A METALLURGICAK FRACTURE IN A 1-1/4" STEEL GAS SERVICE. THE SERVICE LINE WAS BENT AND GOUGED BY A PLUMBING CONTRATOR INSTALLING A WATER LINE IN JULY 191. THE CONTRACTOR FAILED TO PROPERLY EXCAVATE AROUND THE SERVICE AND FAILED TO REPORT THE DAMAGE. THE GAS SERVICE IS BELIEVEDTO HAVE FAILED AND THE EVENING BEFORE THE ACCIDENT.
2025-01-31 10:21 | YES | YES | 19910263 | 1991-12-23 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 107 GREENSBORO LANE | PITTSBURGH | ALLEGHENY | PA | 15220 | 3 | NO | 2015 | 1991-11-16 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19911117 | 0.5 | 0 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | OTHER | NON SPECIFIED | STEEL |  | 1.25 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DON WILLIAMS - MGR CONSTRUCTION & MAINTENANCE | 6144606366 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | INITIAL INFORMATION SUGGESTED A RESIDENT AT REFERENCED ADDRESS WAS OVERCOME BY NATURAL GAS. INVESTIGATION REVEALED THAT THERE WAS A SMALL LEAK ON THE CUSTOMER'S HOUSE LINE PIPING AND A SOMEWHAT LARGER LEAK ON CUSTOMER'S SERVICE LINE. RESIDENT, WHO WAS HOSPITALIZED, WAS 79 YEARS OLD AND SUFFERING FROM PNEUMONIA. MEDICAL AUTHORITIES CANNOT CONFIRM THAT THE RESIDENT'S CONDITION WASAFFECTED BY NATURAL GAS LEAK. THERE IS NO INDICATION THAT THERE WAS SUFFICIENT NATURAL GAS IN A SITUATION, E.G., CONFINED SPACE, WHICH WOULD HAVE EXPOSED THE RESIDENT TO SIGNIFICANT QUANTITIES.
2025-01-31 10:21 | NO | NO | 19910264 | 1991-12-23 | 10037 | K P L GAS SERVICE | 3704 E 72ND ST | KANSAS CITY | JACKSON | MO |  | 3 | NO | 835 | 1991-11-25 | 0 | 0 | 35000 | 28092.8071 | 67829.1679 | Null | 1 | 45 |  | 19911125 | 30 | 5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 |  |  | 0 | 1931 | UNDER GROUND OR UNDER WATER |  | HANS E MERTENS - VICE PRESIDENT OF ENGINEERING | 8163465575 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN APPARENT IGNITION OF GAS WHICH OCCURRED AT 3704 E. 72ND STREET MAY HAVE RESULTED FROM A CRACK DISCOVERED ON A 6" CAST IRON MAIN IN THIS VICINITY. THECAUSE OF THE BREAK IS UNDETERMINED AT THIS TIME. GAS POSSIBLY INFILTRATED THROUGH A CLAY TILE SEWER IN THE IMMEDIATE VICINITY OF THE FRACTURE. HOWEVER,THE EXACT IGNITION SOURCE IS UNKNOWN.
2025-01-31 10:21 | YES | NO | 19910267 | 1992-01-03 | 2596 | COLUMBIA GAS OF OHIO INC | 12 BELMONT AVE | MOUNT VERNON | KNOX | OH |  | 4 | NO | 827 | 1991-12-03 | 0 | 0 | 75000 | 60198.8723 | 145348.217 | Null | 0 | 23 |  | 19911203 | 4.5 | 10 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | D E WILLIAMS - MGR CONSTRUCTION & MAINTENANCE | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION & FIRE TOTALLY DESTROYED INSIDE FAMILY RESIDENCE (NO INJURIES ORFATALITIES). AN INSTRUMENT LEAK SURVEY OF THE SURROUNNDING AREA DID NOT REVEAL ANY LEAKAGE ON MAIN OR COMPANY SERVICE LINES. A FOLLOW-UP PRESSURE DROP TEST ON THE CUSTOMER SERVICE LINE WOULD NOT HOLD PRESSURE. A VISUAL EXAMINATION OF THE CUSTOMER SERVICE LINE INDICATED A FRESH BREAK THAT MAY HAVE BEEN CAUSED BY THE EXPLOSION. WE WERE UNABLE TO TEST THE HOUSE PIPING OR APPLIANCESBECAUSE OF THE DAMAGE FROM FIRE AND OR/DEBRIS REMOVAL. THE CAUSE OF THIS INCIDENT HAS NOT BEEN DETERMINED.
2025-01-31 10:21 | YES | YES | 19920001 | 1992-01-06 | 15462 | PHILADELPHIA ELECTRIC CO | 26 FERN AVE | WILLOW GROVE | MONTGOMERY | PA | 19090 | 3 | NO | 1815 | 1991-12-07 | 0 | 1 | 0 | 0 | 0 | Null | 4 | 3 |  |  | 10 | 25 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.41 | ASA A21.7 |  | 0 | 1956 | UNDER PAVEMENT |  | KENNETH L HILL - GAS PROJECT ENGINEER | 2159411778 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19920002 | 1992-01-06 | 2652 | COMMONWEALTH GAS CO | 71 HOLLIS STREET | WORCESTER | WORCESTER | MA | 01610 | 2 | NO | 1110 | 1991-12-27 | 0 | 0 | 70000 | 56185.6141 | 135658.3359 | Null | 0 | 15 |  | 19911227 | 3.5 | 2 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | GAS APPLIANCE DOWNSTREAM | OTHER | GAS HEATER | OTHER | NON SPECIFIED | 0 | 0 | GAS HEATER | GLENWOOD | 0 | 0 | WITHIN/UNDER BUILDING |  | BRAIN J HAWKESWORTH | 5084817900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19920003 | 1992-01-17 | 15007 | PACIFIC GAS & ELECTRIC CO | 735 MILLER RD |  | SUTTER | CA |  | 3 | NO | 846 | 1991-12-08 | 0 | 0 | 50000 | 40132.5815 | 96898.8113 | Null | 0 | 10 |  | 19911208 | 0.25 | 0.25 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | W R MAZOTTI - V P -GAS & ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19920005 | 1992-01-17 | 11680 | LONE STAR GAS CO | 502 E LINDA | GARLAND | DALLAS | TX | 75041 | 3 | NO | 756 | 1991-12-20 | 0 | 0 | 75000 | 60198.8723 | 145348.217 | Null | 5 | 31 |  | 19911220 | 22 | 55 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.304 | PE-3306 | NIPAK | 1970 | 1970 | ABOVE GROUND |  | PHILLIP MURDOCK - MANAGER | 2146702229 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19920007 | 1991-01-21 | 1640 | BOSTON GAS CO | 54-56 BURBANK ST | BOSTON | SUFFOLK | MA | 02108 | 4 | NO | 1611 | 1991-12-01 | 1 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19911202 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN AT THIS TIME | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LEO T CODY - MANAGER DISTRIBUTION ADMINSTRATION | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19920008 | 1992-01-24 | 15007 | PACIFIC GAS & ELECTRIC CO | 631 SPENCER ST | SANTA ROSA | SONOMA | CA | 95402 | 3 | NO | 426 | 1991-12-28 | 2 | 3 | 500000 | 401325.8153 | 968988.1134 | Null | 6 | 23 |  | 19911228 | 50 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0 | 0 | 1" X 1/2" | AMP | 0 | 1972 | UNDER PAVEMENT |  | W R MAZOTTI - VP- GAS ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-04-22 | YES | 3 | TRAFFIC PAINT | YES |  |  | LOCATION WAS FIRST MARKED ON APRIL 22, 1991. MARKS WERE VERIFIED/RENEWED ATTWO WEEK INTERVALS FROM 4/22 TO 10/14/1991. AT APPROXIMATELY 0426 HOURS ONSAT., DECEMBER 28, 1991, A FIRE BROKE OUT IN AN EIGHT UNIT APARTMENT COMPLEXLOCATED AT 631 SPENCER STREET IN SANTA ROSA. BASED ON OUR INVESTIGATION TODATE, WE BELIEVE THAT A SEWER CONTRACTOR STRUCK THE HIGH PRESSURE GAS SERVICELINE TO A NEIGHBORING BUILDING AT 701 SPENCER STREET WITH A BACKHOE EARLIER INTHE YEAR, WHICH ULTIMATELY RESULTED IN THE PIPE SEPARATING FROM THE FITTING.ESCAPING GAS FROM THE PIPE MIGRATED BELOW GROUND AND FOUND ITS WAY UP INTO THEBUILDING AT 631 SPENCER STREET. THE GAS CONCENTRATION IN THE BUILDING REACHEDAN EXPLOSIVE LEVEL, AND IGNITION WAS APPARENTLY TRIGGERED BY AN OCCUPANT OFTHE BUILDING.
2025-01-31 10:21 | NO | NO | 19920009 | 1992-01-21 | 11800 | LOUISIANA GAS SERVICE CO | U S HWY 190 | HAMMOND | TANGIPAHOA | LA | 70401 | 2 | NO | 1300 | 1991-12-20 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  |  | 75 | 98 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API-5L |  | 0 | 1956 | ABOVE GROUND |  | D L MERIWETHER - PIPELINE SAFETY MANAGER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CAR LEFT HIGHWAY HITTING 1 INCH STEEL RISER.
2025-01-31 10:21 | NO | NO | 19920010 | 1992-01-21 | 11800 | LOUISIANA GAS SERVICE CO | LA HWY 16 | AMITE | TANGIPAHOA | LA | 70422 | 2 | NO | 1500 | 1991-12-20 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 45 |  |  | 68 | 80 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE3408 | PLEXCO | 1982 | 1982 | UNDER PAVEMENT |  | D L MERIWETHER - PIPELINE SAFETY MANAGER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | HWY DEPT. WORK CREW DRILLING PAST HOLE CUT 3/4 INCH PLASTIC SERVICE LINE.
2025-01-31 10:21 | YES | YES | 19920011 | 1991-01-22 | 180 | ALABAMA GAS CORP | 1200 GRAYMONT AVE WEST | BIRMINGHAM | JEFFERSON | AL | 35208 | 3 | NO | 1550 | 1992-01-12 | 0 | 1 | 0 | 0 | 0 | Null | 5 | 0 |  | 19920112 | 9 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 16 | 0.7 |  |  | 1923 | 1924 | UNDER PAVEMENT |  | STEVE CHAPMAN - MANAGER - CONSTRUCTION SERVICES | 2053268309 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19920013 | 1992-01-27 | 17570 | ROCHESTER GAS & ELECTRIC CORP | 1530 & 1534 RIDGE RD | ONTARIO CENTER | WAYNE | NY | 14520 | 3 | NO | 28 | 1992-01-02 | 2 | 0 | 1000000 | 783080.5828 | 1890722.5691 | Null | 4 | 57 |  | 19920102 | 56 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | ROBERT A ROSS - ASSOCIATE GAS DISTRIBUTION | 7167248465 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19920014 | 1992-02-09 | 2420 | CITIZENS UTILITY CO | 1212 1/2 W 2ND STREET | WINSLOW |  | AZ | 86047 | 3 | NO | 237 | 1992-01-26 | 0 | 0 | 0 | 0 | 0 | YES | 8 | 0 |  | 19920126 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JIM WARREN - DISTRICT MANAGER | 6027744591 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19920015 | 1992-01-30 | 12684 | MONTANA - DAKOTA UTILITIES CO | 1525 S W 9TH ST | VALLEY CITY | BARNES | ND | 58072 | 3 | NO | 1725 | 1992-01-11 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 |  | 19920122 | 20 | 60 | BY TEST | 102 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | PIPE NIPPLE | STEEL |  | 0.75 | 0.113 | SCHED 40 |  | 0 | 1985 | ABOVE GROUND |  | TONY J FINNEMAN - CORROSION SUPT | 7012227994 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GRND METER SET | YES |  |  | DRIVER LOST CONTROL OF SNOWMOBILE WHEN THROTTLE STRUCK AND HIT THE METER SETALONGSIDE THE MOBILE HOME BREAKING A PIPE NIPPLE IN THE METER SETTING ANDCAUSING A RELEASE OF NATURAL GAS. MONTANA-DAKOTA UTIL. CO GAVE TELEPHONICREPORT UNDER 49CFR, PART 191, SUBSECTION 191.3, PARAGRAPH 3. IT WAS LATERDETERMINED THAT THE DRIVER WAS HOSPITALIZED FOR THREE DAYS AND RELEASED. TELREPORT NO. 104050.
2025-01-31 10:21 | YES | NO | 19920016 | 1992-02-05 | 18537 | SOUTHWEST GAS CORP | 575 FIFTH STREET | ELKO | ELKO | NV | 89801 | 3 | NO | 1019 | 1991-08-10 | 0 | 0 | 250000 | 200662.9077 | 484494.0567 | Null | 1 | 15 |  | 19910810 | 40 | 43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | PVC-2110 | 2 | 0.1 |  | KRALOY | 1965 | 1965 | UNDER PAVEMENT |  | CLARK STONER/ RICHARD TETREAULT | 7028767396 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | EXCAVATION | YES |  |  | SOUTHWEST GAS HAD TEMPORARILY REMOVED A SECTION OF 2" PVC DISTRIBUTIONPIPELINE TO ACCOMMODATE THE INSTALLATION OF A LARGE DIAMETR WAS WATER PIPELINEPROJECT FOR THE CITY OF ELKO. THE GAS FLOW WAS CURTAILED BY THE INSTALLATIONOF TWO 2" SHORTSTOP FITTINGS. THE SOUTHWEST GAS EXCAVATION WAS SUBSEQUENTLYBACKFILLED ON A TEMPORARY BASIS WHILE THE WASTE WATER CONSTRUCTION PROJECTCONTINUED PAST THE SOUTHWEST GAS DISTRIBUTION PIPELINE. APPARENTLY, ANEXTERNAL FORCE OVER THE SOUTHWEST GAS PIPELINE CAUSED A DOWNWARD DEFLECTION OFTHE PIPE STUB WHICH RESULTED IN A SMALL CRACK IN THE PVC PIPE AT THE SHORTSTOPFITTING. THE ESCAPING NATURAL GAS APPARENTLY MIGRATED INTO A BUILDING AT 5755TH STREET AND IGNITION FROM AN UNKNOWN SOURCE OCCURRED. THERE WAS NO ENSUINGFIRE AT THE TIME OF EXPLOSION. SUBSEQUENTLY, AFTER FIRE UNITS ARRIVED, THEESCAPING NATURAL GAS WAS INGNITED FROM A POSSIBLE ELECTRICAL SHORT AND THERESULTING FIRE FURTHER DESTROYED THE STRUCTURE WHICH WAS NOT OCCUPIED AT THETIME OF THE EXPLOSION. THE DAMAGE WAS EXACERBATED BY A LACK OF WATER AT THESCENE TO EXTINGUISH THE FIRE. THERE WAS SOME SLIGHT EXTERIOR DAMAGE TOADJACENT BUILDINGS
2025-01-31 10:21 | NO | NO | 19920017 | 1992-02-11 | 15342 | PEOPLES GAS SYSTEM INC | ST JOHNS RIVER CHANNEL @ ACOSTA BRIDGE | JACKSONVILLE | DUVAL | FL | 32201 | 3 | NO | 725 | 1992-01-06 | 0 | 0 | 0 | 0 | 0 | YES | 12 | 35 |  |  | 120 | 125 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.5 | API-5L |  | 1957 | 1958 | UNDER GROUND OR UNDER WATER |  | GERALD E COX - VICE PRESIDENT, TECHNICAL SERVICES | 8132730074 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | YES |  |  | DAMAGE CAUSED BY UNKNOWN OUTSIDE FORCES. UNDERWATER PIPELINE ON BOTTOM OF 54FT. DEEP CHANNEL AT BRIDGE WAS HIT BY UNKNOWN OUTSIDE FORCE CAUSING LEAK.AFTER UNSUCCESSFUL ATTEMPT TO REPAIR LINE, IT WAS TAKEN OUT OF SERVICE ANDWILL HAVE TO BE REPLACED. WRITTEN REPORT IS BEING FILED FOR INFORMATIONALPURPOSES ONLY.
2025-01-31 10:21 | YES | YES | 19920021 | 1992-02-24 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 245 PATERSON AVE | WALLINGTON | BERGEN | NJ | 07057 | 3 | NO | 1422 | 1992-02-03 | 0 | 3 | 50000 | 39154.0291 | 94536.1285 | Null | 1 | 53 |  | 19920203 | 14.7 | 15 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | STEEL |  | 12 | 0.5 |  |  | 0 | 1955 | UNDER PAVEMENT |  | C W GREVENITZ - V.P. GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON FEBRUARY 3, 1992 AT APPROXIMATELY 2:22 P.M. AN EXPLOSION OCCURRED AT TOMMY'S DINER IN WALLINGTON (245 PATERSON AVE.) CAUSING EXTENSIVE PROPERTY DAMAGEAND INJURY TO 5 FIREFIGHTERS. THE AREA WAS VENTILATED AND INVESTIGATION REVEALED A CIRCUMFERENTIAL CRACK ON A 12" 15PSI DESIGN CAST IRON MAIN APPROXIMATELY 60' FROM THE BUILDING. FURTHER INVESTIGATION DISCLOSED A SECOND CIRCUMFERENTIAL CRACK ON THE 12" MAIN APPROXIMATELY 130' REMOVED FROM THE BUILDING. DUE TO A SIGNIFICANT REDUCTION IN GAS READINGS AFTER THE FIRST BREAK, IT CAN BE CONCLUDED THAT THIS SECOND BREAK OCCURRED AFTER THE INITIAL INCIDENT.
2025-01-31 10:21 | YES | NO | 19920023 | 1992-02-20 | 16667 | ENERGY NORTH NATURAL GAS INC | 144 CONCORD STREET | NASHUA | HILLSBOROUGH | NH | 03061 | 3 | NO | 730 | 1992-01-28 | 0 | 0 | 75000 | 58731.0437 | 141804.1927 | Null | 2 | 25 |  | 19920128 | 10.5 | 11.9 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.5 |  |  | 0 | 1925 | WITHIN/UNDER BUILDING |  | RICHARD MACDONALD | 6036254000 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | 6" CAST ITON MAIN CRACKED AS A RESULT OF FROST CONDITIONS.6" CAST IRON MAIN CRACKED AS A RESULT OF FROST CONDITIONS.
2025-01-31 10:21 | YES | YES | 19920030 | 1992-02-29 | 1640 | BOSTON GAS CO | 155 SHARON ST | MEDFORD | MIDDLESEX | MA |  | 3 | NO | 1824 | 1992-01-23 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 0 |  |  | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LEO T CODY - MANAGER, DISTRIBUTION ADMINSTRATION | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OCCURRED IN A RESIDENCE AT #155 SHARON STREET, MEDFORD, MASSACHUSETTS. A LEAK INVESTIGATION WAS CONDUCTED AND A 4" LOW PRESSURE CAST IRON CIRCUMFERENTIAL BREAK WAS FOUND ON A MAIN LOCATED IN THE STREET WITH APPROXIMATELY 11 1/2' OF FROST. AN ON-GONING INVESTIGATION IS BEING CONDUCTED BY BOSTON GAS, MASS. DEPARTMENT OF PUBLIC UTILITIES AND THE MEDFORD FIRE DEPARTMENT. AS OF THIS DATE THE CAUSED OF THIS INCIDENT REMAIN UNDER INVESTIFATION.
2025-01-31 10:21 | YES | YES | 19920034 | 1992-01-31 | 1640 | BOSTON GAS CO | 11 BILODEAU RD | BOSTON | SUFFOLK | MA |  | 3 | NO | 2010 | 1991-12-30 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 2 |  | 19911231 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NON SPECIFIED | CAST IRON |  | 6 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | LEO T CODY - MANAGER, DISTRIBUTION ADMINSTRATION | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE WORKING IN A TRENCH INSTALLING A SLEEVE, THERE WAS AN IGNITION RESULTING IN BURNS TO AN EMPLOYEE'S FACE AND HANDS. A PORTABLE HALOGEN LIGHT WAS BEING USED TO LIGHT THE JOB SITE AND WAS DETERMINED TO BE THE SOURCE OF IGNITION
2025-01-31 10:21 | YES | NO | 19920035 | 1992-01-31 | 1160 | BATESVILLE GAS UTILITY | 102 NORTH WALNUT ST | BATESVILLE | RIPLEY | IN | 47006 | 1 | NO | 850 | 1992-01-17 | 0 | 0 | 200000 | 156616.1166 | 378144.5138 | Null | 0 | 30 |  | 19920117 | 35 | 40 | BY TEST | 60 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0 | RCW API-5L | REPUBLIC | 1960 | 1961 | UNDER PAVEMENT |  | ELMER M WONDERBEIDE - UTILITY MANAGER | 8129343811 | [6 empty] | Null |  | EARTH MOVEMENT: FROST | FROST | NO |  | NO | 0 |  | NO |  |  | MAIN WAS 6-7 INCHES BELOW CURB SURFACE. STREET HAD BEEN RECURBED SINCE PIPEINSTALLATION.
2025-01-31 10:21 | NO | NO | 19920036 | 1992-02-14 | 12582 | MISSISSIPPI VALLEY GAS | 908 MOORE ST | CLEVELAND | BOLIVAR | MS | 38732 | 0 | NO | 1200 | 1992-01-30 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19920131 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | OTHER |  | JOE J POWELL JR - V P - TECHNICAL SERVICES | 6019616853 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A PRELIMINARY CHECK FOUND NO EVIDENCE OF GAS LEAKAGE FROM MISSISSIPPI VALLEYGAS FACILITIES; BUT THE EXACT CAUSE OF THE EXPLOSION AND FIRE WAS NOT DETERMINED. A TELEPHONE REPORT WAS MADE FOR THE ABOVE REASON. SUBSEQUENT INVESTIGATION PROVED THAT NO GAS LEAKED FROM MISSISSIPPI VALLEY GAS FACILITIES AND THAT THE CAUSE OF THE FIRE AND EXPLOSION WAS ARSON. GASOLINE WAS APPARENTLY USED. FOR THIS REASON THE EVENT REPORTED WAS NOT AN INCIDENT.
2025-01-31 10:21 | YES | YES | 19920038 | 1992-02-27 | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | 541 FLINT ST | JAMES ISLAND | CHARLESTON | SC |  | 3 | NO | 1500 | 1992-01-21 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 20 |  | 19920122 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D-2513 | DUPONT | 1980 | 1981 | OTHER | ROAD RIGHT OF WAY | DANIEL F KASSIS - DIVISION ENGINEER | 8037457296 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | EMPLOYEES FOR JAMES ISLAND PUBLIC SERVICE DISTRICT (JIPSD) WERE PERFORMING ASEWERTAP FOR A NEW HOME AT 1766 MOHOWK STREET WHEN A 2" POLYETHYLENE (PLASTIC) GAS MAIN WAS DAMAGED. A BACKHOE OPERATOR FOR JIPSD DAMAGED THE 2" GAS LINE DUIRING EXCAVATION. JIPSD MADE TEMPORARY RAPAIRS WHICH CONSISTED OF WRAPPING THE DAMAGED 2" GAS MAIN WITH DUCT TAPE. THE DAMAGED WAS REPORTED TO THE JAMES ISLAND BASE STATION, WHO IN TURN, REPORTED IT TO SCE&G COMPANY. IN THE MEANTIME, THE CREW ATTEMPTED TO MAKE THE SEWER TAP INSTALLATION AND STARTED AGASOLINE DRIVEN GENERATOR ADJACENT TO THE EXCAVATION. AFTER RUNNING APPROXIMATELY TEN MINUTES, THE GENERATOR APPARENTLY BEGAN TO RUN ROUGH. TWO OF THE EMPLOYEES CHECKED THE GENERATOR GASOLINE TANK BY REMOVING THE TANK GASOLINE CAP WHILE THE GENERATOR IGNITED THE GASOLINE AND/OR NATURAL GAS FUMES WHICH WHERE LINGERING IN AND AROUND THE EXCAVATED AREA. THE APPROXIMATE TIME OF THE FIRE CALLED INTO SCE& G WAS 3:15 PM. THE 2" GAS MAIN WAS SQUEEZED OFF AT TWOBELL-HOLE LOCATIONS, ONE UPSTREAM AND THE OTHER DOWNSTREAM OF THE CUT IN THE2" GAS MAIN. THE GAS MAIN WAS SQUEEZED OFF AT 4:20 PM AND THE FIRE WAS EXTINGUISHED AT THAT TIME. TWO MEMBERS OF JIPSD WERE TAKEN TO ROPER HOSPITAL IN CHARLESTON, SC, WITH BURNS. ONE VICTIM, OLONSO DELESTON, RECEIVED FIRST AND SECOND BURNS ON HIS FACE AND FIRST DEGREE BURNS ON HIS RIGHT HAND. HE WAS RELEASED FROM THE HOSPITAL HOURS LATER AND PLACED UNDER THE OUTPATIENT CAR OF DR. EARL BRINSTON, MD. HE WAS ALLOWED TO RETURN TO WORK ON FEBRUARY 3. THE OTHER VICTIM, NATHAN JOHNSON, RECEIVED 9-12% FIRST AND SECOND BURNS. A MAJORITY OF THE BURNS WERE FIRST DEGREE BURNS TO HIS RIGHT ARM, WHILE SECOND DEGREEBURNS COVERING 4-6% ON THE RIGHT ARM (UPPER ARM, ELBOW AND FOREARM). HE WASRELEASED FROM THE HOSPITAL ON JANUARY 29, UNDER THE CARE OF DR. ERIC G. LEVEEN, MD, AND AS OF FEBRUARY 5, HE HAD NOT RETURNED TO WORK. RONALD BYCROFT, SUPERINTENDENT FOR JIPSD, CONFIRMED THAT PALMETTO UNDERGROUND PROTECTION SERVICE (PUPS) WAS NOT CALLED TO NOTIFY UTILITIES TO LOCATE UNDERGROUND FACILITIES. A TOTAL OF 397 MCF WAS LOST FROM THE LINE CUT. THIS INCIDENT RECEIVED LOCAL MEDIA ATTENTION.
2025-01-31 10:21 | YES | YES | 19920040 | 1992-02-28 | 22476 | WESTERN KENTUCKY GAS CO | KY HWYS 208 AND 1157 |  | MARION | KY | 40033 | 3 | NO | 1130 | 1992-01-21 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  |  | 255 | 260 | BY TEST | 1200 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | REGULATORY STATION | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | GENE BAKER - DIRECTOR ENGINEERING SERVICES | 5026858025 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER |  | WHILE WORKING ON A REGULATOR CONTROL LINE, GAS ESCAPED AND APPEARED TO BE IGNITED BY A NEARBY HEATER. TWO EMPLOYEES RECEIVED FLASH BURNS. ONE WAS HOSPITALIZED OVERNIGHT FOR OBSERVATION. BOTH EMPLOYEES HAVE SINCE RETURNED TO WORK
2025-01-31 10:21 | NO | NO | 19920041 | 1992-03-19 | 15342 | PEOPLES GAS SYSTEM INC | 2400 BLOCK HENRY AVE. | TAMPA | HILLSBOROUGH | FL | 33604 | 4 | NO |  | 1992-02-21 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19920224 | 40 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | ASTM 2513 |  | 1984 | 0 | UNDER PAVEMENT |  | JEFFERY C RODGER - DISTRICT SAFETY ENGINEER | 8132720230 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SMALL AMOUNT GAS LEAKING THROUGH SANDY SOIL WAS IGNITED BY AN UNKNOWN SOURCE. A "4" P.E. SERVICE LINE WAS LEAKING AS A RESULT OF MATERIAL FAILURE IMMEDIATELY ADJACENT TO A 4" SOCKET FUSION COUPLING. THE CUSTOMER WHO WAS BEING SERVED BY THE LINE REPORTED THE INCIDENT AROUND 1:00P.M. IT WAS MADE SAFE ABOUT 2:00 P.M. THERE WAS NO PERSONAL INJURIES. THE COST OF REPAIR DID NOT EXCEED $50,000. THEREFORE, THIS INCIDENT DOES NOT MEET THE REPORTABLE INCIDENT CRITERIA. HOWEVER, THIS REPORT IS FILED AS A FOLLOW-UP TO THE TELEPHONIC REPO
2025-01-31 10:21 | YES | YES | 19920042 | 1992-03-19 | 13480 | NIAGARA MOHAWK POWER CORP | 1413 EAST PARK RD | UTICA | ONEIDA | NY | 13501 | 2 | NO | 700 | 1992-03-04 | 2 | 0 | 100000 | 78308.0583 | 189072.2569 | Null | 2 | 30 |  | 19920304 | 0.33 | 0.33 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 | 0.437 | '' |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | GEORGE R. TAYLOR - MANAGER | 3157985117 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | GAS MIGRATED FROM 8" CRACKED CAST IRON MAIN (MECHANICAL POINT) INTO HOUSE AT1413 EAST PARK ROAD. AN UNKOWN SOURCE OF IGNITION CAUSED EXPLOSION AND FIRE. BOTH RESIDENTS DIED. ACTION TAKEN: GAS SERVICE TO 1413 EAST PARK RD WAS RETIRED AS HEADER WAS BROKEN AND GAS BURNING. VENT GRATES INSTALLED ON MANHOLES AND VENT HOLES DUG ALONG GAS SERVICE FOR 1400 BUCKLEY ROAD WHERE GAS CONCENTRATIONS WERE FOUND. SEVEN OTHER HOUSES ON EAST PARK ROAD HAS GAS READINGSAND WERE VENTILATED AND PERIODICALLY CHECKED FOR GAS LEVELS. AN 8" CRACKED CAST IRON MAIN WAS DISCOVERED AND REPAIRED AT 10:30.
2025-01-31 10:21 | YES | NO | 19920043 | 1992-03-25 | 15896 | PROVIDENCE GAS CO | 82 SOWANS RS | BARRINGTON | BRISTOL | RI | 02806 | 3 | NO | 1446 | 1992-03-16 | 0 | 0 | 125000 | 97885.0729 | 236340.3211 | Null | 0 | 17 |  | 19920316 | 22 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | OTHER | BRASS | 0.75 | 0.25 |  | MUELLER H-11071 | 1940 | 1940 | WITHIN/UNDER BUILDING |  | LOUIS R. SCHMITT - SUPT OF DISTRIBUTION ENG | 4012725050 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | COMPOSITE NARRATIVE: BACKHOE OPERATOR MICHEAL SILVEIRA WAS EXCAVATING FOR FOOTINGS TO BE INSTALLED UNDER THE FRON PORCH OF 84 SOWANS ROAD, WHICH IS THE REAR HOUS OF 82 SOWANS ROAD (THE REPORTED ADDRESS) AND IS PART OF PROPERTY OWNED BY SILVEIRA'S FATHER, JOSEPH. THIS EXCAVATION WAS BEING DUG WITHOUT A DIG SAFE NOTIFICATION, AND NO UTILITIES WERE MARKED ON THE SITE. DURING THE EXCAVATING PROCESS, THE OPERATOR APPARENTLY DRAGGED THE BACKHOE BUCKET ALONG THE TOP OF THE SERVICE PIPING AND FORCED THE FOUNDATION RESULTED IN THE WITHDRAWAL OF THE SERVICE PIPE AT THE INSIDE WALL OF THE CELLAR. IN TURN, THE CORPORATION COCK ON THE SERVICE WAS DRAWN INTO THE FIELDSTONE FOUNDATION WALL, AND THE RESULTING STRESS ON THE PIPING CAUSED THE BASEMENT TEE TO SEPARATE FROMTHE SERVICE LINE AT THE CORPORATION COCK THREADS, CAUSING THE RELEASE OF HIGH PRESSURE (25 PSIG) GAS DIRECTLY INTO THE CELLAR. A SOURCE OF IGNITION, PRESUMABLY THE OIL BURNER IN THE CELLAR, TRIGGERED THE EXPLOSION AND FIRE. THE EXPLOSION DISTORTED THE FRONT PORCH OF THE BUILDING. THE INTERIOR OF THE BUILDING WAS ENGULFED IN FLAME. MICHEAL SILVEIRA REPORTEDLY WAS KNOCKED FROM THE SEAT OF THE BACKHOE BY THE CONCUSSION, BUT OTHERWISE SUSTAINED NO INJURY. MRS. TRUDI LEMOI OF 81 SOWANS ROAD, ACROSS THE STREET FROM THE SITE, REPORTEDA CRACKED FRONT WINDOW ON HER HOUSE AND A NUMBER OF BROKEN DISHES WHICH HAD FALLEN FROM THEIR DISPLAY IN THE SAME WINDOW. OTHERWISE, NO OTHER OFFSITE DAMAGE OR INJURY WAS REPORTED. THE REPORT WAS INITIALLY RECEIVED AND DISPATCHED BY PROVIDENCE GAS AT 14:46 AND THE RESPONDING PERSONNEL HAD THE FLOW OF GASSECURED BY 15:03, AND THE VOLUME OF FLAME WAS REDUCED. THE BARRINGTON FIRE DEPARTMENT WORKED UNTIL ABOUT 17:00 TO KNOCK DOWN THE FLAMES WITHIN THE BUILDING, AND THEN THE SERVICE WAS CUT OFF AND CAPPED AT THE CURB VALVE. THE DEPUTY STATE FIRE MARSHALL THEN DIRECTED THE REMOVAL OF PIPING AND EQUIPMENT AS EVIDENCE IN THE INVESTIGATION. THESE MATERIALS ARE STORED AT BARRINGTON FIRE STATION 1. THE BACKHOE OPERATOR WAS INTERVIEWED BY THE RHODE ISLAND STATE POLICE TO DETERMINE A VIOLATION OF THE DIG SAFE STATUTES. STATE POLICE WILL REFER THE MATTER TO THE ATTORNEY GENERAL'S OFFICE FOR CHARGES AND PROSECUTION.
2025-01-31 10:21 | YES | YES | 19920046 | 1992-03-23 | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | INTERSECTION DON PATRICIO & WALDRON RDS | CORPUS CHRISTI | NUECES | TX | 78418 | 3 | NO | 1750 | 1992-02-04 | 0 | 1 | 0 | 0 | 0 | Null | 6 | 0 |  | 19920204 | 13 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN | FITTING | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1949 | UNDER GROUND OR UNDER WATER |  | FRANK L SACKY,- P.E., ASSISTANT GAS SUPT. | 5128803140 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-01-30 | NO | 0 |  | NO |  |  | STORMWATER CREW USING A GRADE-ALL TO CLEAN DRAINAGE DITCHES, HIT A 2" GAS MAIN, DAMAGING THE MAIN AND PULLING ONE END OUT OF A VALVE. IN THE PROCESS OF PUMPING WATER OUT OF THE DITCH WHERE DAMAGE OCCURRED, THE ESCAPING GAS WAS IGNITED. ONE EMPLOYEE RECEIVED FIRST DEGREE BURNS ON FACE REQUIRING HOSPITALIZATION FOR 4 DAYS. IGNITION SOURCE WAS PROBABLY A WATER PUMP. THE FLOW OF GAS WAS STOPPED BY CLOSING TWO VALVES AND SQUEEZING ANOTHER 2" MAIN. IN REGIONWHERE DAMAGE OCCURRED, GAS LINES WERE NOT LOCATED OR MARKED SINCE STORMWATERCREW OVED THEIR WORK LOCATION WITHOUT NOTIFYING GAS DIVISION.
2025-01-31 10:21 | NO | NO | 19920048 | 1992-03-23 | 11680 | LONE STAR GAS CO | 1500 BLK W VICKERY | FORT WORTH | TARRANT | TX |  | 3 | NO | 1035 | 1991-12-30 | 0 | 0 | 12000 | 9631.8196 | 23255.7147 | Null | 1 | 25 |  | 19911230 | 27 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | STEEL |  | 8 | 0.219 |  |  | 0 | 1975 | UNDER GROUND OR UNDER WATER |  | PHILLIP MURDOCK - MANAGER | 2146702229 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-12-05 | YES | 1 |  | YES |  |  | HALL CONSTRUCTION COMPANY WAS IN PORCESS OF REMOVING CONCRETE FROM THE WALL OTHE NORTH SIDE OF MARY'S CREEK WHEN THEY HIT AN 8" IP STEEL MAIN. THEY HOOKED A TOOTH IN THE 8" MAIN AT A 45 DEGREE ELL WITH A 235 CAT TRACKHOE. THE GAS HAD TO BE CUT OFF. SERVICE TO 1146 CUSTOMERS WERE EFFECTED.
2025-01-31 10:21 | YES | YES | 19920049 | 1992-02-23 | 18104 | SAN ANTONIO,CITY PUBLIC SERVICE BOARD OF | 1619 BASSE RD | SAN ANTONIO | BEXAR | TX | 78213 | 3 | NO | 452 | 1992-02-07 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19920207 | 6 | 33 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SEPCIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | M. KOTARA, P.E. - SUPERVISOR | 5129782652 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EN EXPLOSION OCCURRED INSIDE A HOUSE LOCATED AT 1619 BASSE ROAD. AT THE TIMEOF THE EXPLOSION THERE WERE THREE OCCUPANTS INSIDE THE HOUSE AND ONE OCCUPANT SUSTAINED INJURIES WHICH REQUIRED IN-PATIENT HOSPITALIZATION TREATMENT
2025-01-31 10:21 | YES | YES | 19920050 | 1992-03-23 | 30511 | GULFSIDE INDUSTRIES LTD | K ST | SOMERSET | BEXAR | TX | 78069 | 3 | NO | 1107 | 1992-02-21 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 23 |  | 19920221 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER | PVC | 2 | 0 |  |  | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | DAVID R LYNN - AREA SUPERINTENDENT | 5124293342 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | NO |  |  | TWO INCH (2") GAS MAIN HIT BY SOMERSET CITY EMPLOYEE WHILE INSTALLING FLAG POLE.
2025-01-31 10:21 | YES | NO | 19920051 | 1992-03-23 | 10037 | K P L GAS SERVICE | 400 RICHWOOD | BLUE SPRINGS | JACKSON | MO |  | 3 | NO | 1920 | 1992-02-21 | 0 | 0 | 80000 | 62646.4466 | 151257.8055 | Null | 0 | 9 |  | 19920221 | 15 | 56 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.133 |  |  | 0 | 0 | ABOVE GROUND |  | HANS E MERTENS - V P ENGINEERING | 8163465575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A VEHICLE LEFT THE ROADWAY AND STRUCK THE METER SETTING ADJACENT TO THE HOUSE LOCATED AT 400 RICHWOOD, DAMAGING THE METER SETTING. GAS WAS SUBSEQUENTLY IGNITED, RESULTING IN DAMAGE TO THE VEHICLE AND THE HOUSE.
2025-01-31 10:21 | NO | NO | 19920052 | 1992-03-23 | 18484 | SOUTHERN CALIFORNIA GAS CO | 308 EAST OJAI AVE | OJAI | VENTURA | CA | 93023 | 2 | NO | 1320 | 1992-02-20 | 0 | 0 | 15000 | 11746.2087 | 28360.8385 | Null | 0 | 0 |  |  | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GARY J LAMBERT - MANAGER OF SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS REPORT IS SUBMITTED UNDER 191.9, INCIDENT REPORTING, PER 191.3(3). NO OPERATOR FACILITY WAS INVOLVED. INVESTIGATION REVEALED CUSTOMER HOUSELINE LEAKED, CAUSING A SUBSEQUENT EXPLOSION AND FIRE THAT ATTRACTED SIGNIFICANT MEDIA ATTENTION. ALL OPERATOR FACILITIES WERE SURVEYED AND FOUND TO BE LEAK FREE.
2025-01-31 10:21 | NO | NO | 19920054 | 1992-03-20 | 17090 | RATON GAS TRANSMISSION CO | 925 OAK ST | RATON | COLFAX | NM | 87740 | 0 | NO | 30 | 1992-02-11 | 0 | 0 | 60000 | 46984.835 | 113443.3541 | Null | 0 | 30 |  | 19920211 | 12 | 20 | BY TEST | 60 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | OTHER PLASTIC | P.V.C. | 1.5 | 0.08 |  |  | 0 | 1964 | UNDER PAVEMENT |  | TONY ENCINIAS SUPT | 5054453613 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | FEBRUARY 11, 1992: AT ABOUT 2:10 P.M., DONNA MUNDEN, ADVISED ME OF A REPORTED DAMAGED GAS LINE AT 925 OAK STREET. I ARRIVED AT THE LOCATION APPROXIMATELY 2:15P.M. AND FOUNS THAT THE 2" P.V.C. GAS MAIN HAD BEEN HIT BY A BACK HOE. LINE WAS CUT IN TWO. INSEATED PLUG (2") AND STOPPED FLOW OF GAS. I ADVISED,R. EMILIO MARTINEZ, OWNER, THAT HE SHOULD HAVE CALLED US TO LOCATE LINE BEFORE HE STARTED DIGGING. HE SAID HE DIDN'T REMEMBER THAT A GAS LINE WAS THERE, SO CLOSE TO HIS SEWER LINE. I CALLED CREW FOREMAN, LARRY MARTINEZ, AND ADVISED AS TO WHAT HAD HAPPEDNED AND HE AND HIS CREW SECURED WHERE THEY WERE WORKING AND WENT TO 925 OAK TO REPAIR DAMAGED GAS LINE. I WAS TOLD LATER THAT LINE HAD BEEN REPAIRED AND THAT ALL UNITS HAD BEEN RELIT (7 TO 8 TRAILERS), ATABOUT 4:45 P.M. AT ABOUT 9:50 P.M. I RECEIVED A CALL FROM THE CITY P.D. THAT AN EXPLOSION HAD OCCURRED AND THAT A FIRE WAS IN PROCESS AT A LOCATION ON OAK STREET. I THOUGHT THEN, THAT THIS MIGHT BE RELATED TO WHAT HAD HAPPENED EALIER. I CALLED LARRY MARTINEZ AND TOLD HIM WHAT I HAD BEEN TOLD BY THE P.D.DISPATCHER AND TOLD HIM TO MEET ME AT THE LOCATION A.S.A.P. WHEN I ARRIVED,APPROXIMATELU TEN (10) MINUTES AFTER HAVING RECEIVED THE CALL, LARRY MET ME. HE THEN LEFT TO GET THE REST OF THE CREW SO THAT WE COULD DIG UP 2" MAIN AND TRY TO FIND WHERE GAS LEAK MIGHT BE. LINE WAS DUG 2' TO 3' BACK TO MAIN AND FOUND WHERE 2" P.V.C. PIPE HAD BEEN TAPPED TO 1 1/2" P.V.C. MAIN AND THAT ITHAD BROKEN LOOSE. WE PLUGGED LINE AND SECURED AREA FOR THE NIGHT. LEFT AT ABOUT 1:00AM 1:15A.M., FEBRUARY 12, 1992, I CALLED ALBINO ZUNIGA WITH THE STATE CORPORATION COMMISSION AND ADVISED OF THE INCIDENT. I TOLD HIM, AT THE TIME, I FELT THE HOUSE IN QUESTION WAS VALUED AT LESS THAN &50,000 AND THERE WERE NOT ANY INJURIES. HE ADVISED ME HE WOULD COME TO RATON AND WOULD BE OKAY IF WE COULD START REPAIR OF LINE AND RESTORE SERVICE TO THE AREA. HE AGREED THAT WE SHOULD; BUT, TO KEEP AS MUCH OF THE DAMAGED PIPE AS POSSIBLE FOR CAUSEOF PROBLEM. FEBRUARY 12, IN THE A.M. LARRY MARTINEZ AND CREW STARTED REPAIRIING LINE. NEW CONNECTIONS WERE MADE TO 1 1/2" LINE AND REATTACHED 2" AND VALVE TO MAIN ON OAK STREET. A PRESSURE TEST WAS APPLIED WITH AN AIR COMPRESSOR. LINE WOULD NOT HOLD PRESSURE. UPON FURTHER CHECKING OF LINE, THEY FOUND THAT THERE WAS ANOTHER BREAK ON 2" LINE ABOUT 30' FROM 1 1/2" MIAN. 2" LINE WAS SEPARATED AT A COUPLING WHICH HAD BROKEN IN HALF AND THERE WAS ABOUT 4 TO 6" SEPARATON BETWEEN THE TWO BROKEN PARTS. PE PIPE WAS INSTALLED AND A PRESSURE TEST WAS AGAIN APPLIED TO 60P.S.I., PRESSURE HELD. UNITS (TRAILERS) WERERELIT AT ABOUT 3:00 P.M. I FEEL SURE THAT WHAT CAUSED THE ESCAPE OF GAS LATER THAT NIGHT, WAS THAT THE LINE WAS BROKEN AGAIN. AFTER THE OWNER FINISHED REPAIRINF SEWER LINE AND BACK-FILLED DITCH. THIS IS WHEN 2ND AND 3RD BREAK OCCURRED.
2025-01-31 10:21 | YES | YES | 19920055 | 1992-03-12 | 15007 | PACIFIC GAS & ELECTRIC CO | 185 PALM AVENUE | SAN RAFAEL | MARIN | CA | 94912 | 3 | NO | 50 | 1992-02-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19920208 | 5 | 0 |  | 0 | CORROSION | CORROSION | EXTERNAL | OTHER | CUSTOMER HOUSELINE | BODY OF PIPE |  | STEEL |  | 200 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | W R MAZOTTI - V.P. GAS & ELEC TECHNICAL SERVICES | 4159736999 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | NO DATA | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19920056 | 1992-02-20 | 11680 | LONE STAR GAS CO | 2020 WALNUT | SAN ANGELO | TOM GREEN | TX | 76901 | 3 | NO | 1810 | 1992-01-18 | 0 | 0 | 20000 | 15661.6117 | 37814.4514 | Null | 0 | 0 |  | 19920118 | 0 | 55 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | GRADE A |  | 0 | 1939 | WITHIN/UNDER BUILDING |  | PHILLIP MURDOCK | 2146702229 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS LEAK IN THE MAIN IN THE ALLEY MIGRATED TO BACK WALL OF HOUSE.
2025-01-31 10:21 | NO | NO | 19920057 | 1992-03-10 | 2416 | CITIZENS UTILITY CO | 1212 1/2 WEST SECOND ST | WINSLOW | NAVAJO | AZ | 86047 | 0 | NO | 0 | 1992-01-26 | 0 | 0 | 60000 | 46984.835 | 113443.3541 | Null | 0 | 0 |  |  | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0.188 | API-5L |  | 0 | 1951 | OTHER | NON SPECIFIED | JIN WARREN - DISTRICT MANAGER | 6027744591 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | NO CAUSE GIVEN | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 02:37 AM. ON 1.26/92 A VACANT RENTAL HOME AT 1212 1/2 WEST SECOND STREET IN WINSLOW, ARIZONA EXPLODED AND COUGHT FIRE. AFTER THE FIRE WAS OUT, EXCAVATION WAS BEGUN TO DISCOVER THE SOURCE OF THE LEAKING GAS. AFTER EXCAVATION, IT WAS DISCOVERED THAT THE 4 INCH PIPE HAD BEEN DAMAGED BY A THIRD PARTY AT SOME TIME IN THE PAST. IT WAS NOT KNOWN WHO DID THE DAMAGE OR WHEN IT WAS DONE. THE CRACK ENCIRCLED THE PIPE FOR APPROXIMATELY 300 DEGREES BUT DID NOT SEVER INTO. THE CRACK AT THE WIDEST POINT WAS APPROXIMATELY .25 IN WIDTH. THIS SECTION OF PIPE WAS REPLACED WITH 34 FEET OF NEW PIPE.
2025-01-31 10:21 | YES | YES | 19920058 | 1992-03-16 | 13783 | NORTHERN STATES POWER CO | 2134 3RD ST | EAU CLAIRE | EAU CLAIRE | WI | 54701 | 3 | NO | 120 | 1992-02-20 | 0 | 4 | 20000 | 15661.6117 | 37814.4514 | Null | 0 | 0 |  | 19920220 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | TRANSITION | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | TR418 | PLEXCO | 1979 | 1979 | WITHIN/UNDER BUILDING |  | RICHARD J HOSCH | 7158392558 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 12:30 -1:00 AM THE UPSTAIRS BUILDING TENANTS CAME HOME AND DROVE CAR INTO DOUBLE METER SET LOCATED ON THE SIDE OT THE DUPLEX. THE METERSET WAS SEPARATED FROM THE PARKING AREA BY APPROXIMATELY 10 FEET OF GRASS COVERED AREA. THE FORCE OF THE IMPACT ON THE METER SET BROKE THE OUTLET PIPINGFROM METER CAUSING GAS TO ESCAPE AROUND HOUSE. IT WAS DETERMINED AFTER EXCAVATION THAT THE PORTION OF THE RISER BELOW THE ELBOW CAUSED GAS TO FLOW INTO THE BASEMENT UNDERGROUND THROUGH THE POROUS STONE FOUNDATION WALL. THE FORCEOF THE IMPACT ALSO DID STRUCTURAL DAMAGE TO THE VEHICLE INVOLVED ACCORDING TO THE POLICE REPORT. THE EXACT SOURCE OF INGNITION CANNOT BE DETERMINED. DUE TO THE PRECARIOUS STATUS OF THE BUILDING AFTER THE EXPLOSION, POLICE OF THEFIRE PERSONNEL DID NOT ALLOW ANYONE TO ENTER THE BUILDING. THE POLICE REPORT STATES THAT THE DRIVER AND PASSENGER OF THE VEHICLE INVOLVED WERE CITED FORDRIVING WHILE UNDER THE INFLUENCE. LATER REPORTS INDICATED A TOTAL OF FOURTEEN CHARGES HAVE BEEN BROUGHT AGAINST THE TWO. A COPY OF THE INITIAL POLICE REPORT AND THE FIRE INVESTIGATION REPORT ARE ATTACHED.
2025-01-31 10:21 | NO | NO | 19920063 | 1992-04-13 | 15425 | PETROLANE GAS SERVICE LP | CONER OF N BARLOW LANE & SIERRA VISTA | BISHOP | INYO | CA | 93514 | 3 | NO | 1030 | 1992-03-25 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  |  | 10 | 20 | BY TEST | 10 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT |  | STEEL |  | 34 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | TOM SIGLER - DISTRICT MANAGER | 6198733559 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | NON SPECIFIED | NO |  | NO | 0 |  | NO |  |  | COUNTY BACK HOE DUG UP 3/4" YARD LINE WHILE EXCAVATING IN ROADWAY.
2025-01-31 10:21 | NO | NO | 19920064 | 1992-04-13 | 21190 | VERMONT GAS SYSTEMS INC | 75 HAYWARD ST | BURLINGTON | CHITTENDEN | VT | 05401 | 3 | NO | 150 | 1992-03-12 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19920312 | 4 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUM | 0 | 0 | 1213-B | AMERICAN METER | 1990 | 1990 | ABOVE GROUND |  | MICHAEL E. SULLIVAN - V.P. OPERATIONS | 8028634511 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | ICE/FREEZING RAIN | NO |  | NO | 0 |  | NO |  |  | RAIN FREEZING ON REGULATOR.
2025-01-31 10:21 | YES | YES | 19920066 | 1992-03-26 | 18440 | SOUTH JERSEY GAS CO | J F KENNEDY BLVD AND PLEASURE AVE | SEA ISLE CITY | CAPE MAY | NJ | 08243 | 4 | NO | 807 | 1992-03-16 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 39 |  | 19920316 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2406 | DUPONT | 1988 | 1988 | UNDER PAVEMENT |  | RICHARD J JACKSON -ASST V.P DIV OPERATIONS | 6095619000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-01-08 | YES | 0 |  | YES |  |  | MARKOUT REQUEST WAS MADE ON THIS DATE BY A SUBCONTRACTOR DOING WORK NEAR THIS LOCATION. THE CITY OF SEA ISLE DID NOT REQUEST A MARKOUT PRIOR TO WORKING ON 3-16-92. SEA ISLE CITY WORKMAN, WHILE PERFORMING WATER MAIN MAINTENANCE, PUNCTURED A 2-INCH PLASTIC GAS MAIN WITH A BACKHOE. NATURAL GAS ESCAPED, IGNITED AND BURNT A SECOND CITY EMPLOYEE WORKING IN THE DITCH NEAR THE DAMAGED GAS MAIN.
2025-01-31 10:21 | NO | NO | 19920071 | 1992-04-29 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 120 RAWSONVILLE RD | BELLEVILLE | WASHTENAW | MI | 48111 | 3 | NO | 1330 | 1992-03-16 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 0 | 15 |  | 19920316 | 570 | 858 | BY TEST | 1600 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | GATE STATION | VALVE | FLANGE | OTHER | GASKET | 24 | 0 | COMPRESSED ASBE |  | 0 | 1991 | ABOVE GROUND |  | EDWARD C SWANSON - CIDES & STANDARDS CONSULTANT | 3132566614 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | UNEXEPECTED EXCESS LIQUIDS ENTERED STATION PUMPING | UNEXPECTED EXCESS LIQUIDS ENTERED STATION PIPING HYDRAULIC HAMMER RESULTING IN SUBSEQUENT GASKET FAILURE.
2025-01-31 10:21 | NO | NO | 19920072 | 1992-04-27 | 18484 | SOUTHERN CALIFORNIA GAS CO | PEMBRIDGE DR 135' S/O DOWING ST | MORENO VALLEY | RIVERSIDE | CA |  | 3 | NO | 940 | 1992-04-08 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 1 | 0 |  | 19920408 | 49 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM 2513 | DRISCO | 0 | 1991 | UNDER GROUND OR UNDER WATER |  | GARY J LAMBERT - MANAGER OF SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A BACKHOE OPERATOR, WORKING FOR LBS PIPELINE CONTRACTORS, WHILE EXCAVATING TO INSTALL A WATER LINE, STRUCK AND DAMAGED A 2" PLASTIC MAIN. THE ESCAPING GAS IGNITED AND THE BACKHOE WAS COMPLETELY DESTROYED.
2025-01-31 10:21 | NO | NO | 19920074 | 1992-04-07 | 20211 | UNITED CITIES GAS CO | 13101 S QUIVIRA RD | OVERLAND PARK | JOHNSON | KS |  | 3 | NO | 1555 | 1992-03-24 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | YES | 0 | 30 |  | 19920324 | 58 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1.5 | 0 | S202 | ROCKWELL | 1964 | 1965 | ABOVE GROUND |  | MIKE WOOLF - MANAGER | 9137640530 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-03-01 | YES | 0 |  | NO |  |  | WATER LINE CONTRACTOR ALLOWED A 42 INCH CONCRETE CONDUIT TO ROLL INTO A METER SETTING. CONDUIT DAMAGED S 202 REGULATOR ALLOWING EXCESS GAS PRESSURE TO ENTER BUILDING. IGNITION OCCURRED DAMAGING INTERIOR OF BUILDING.
2025-01-31 10:21 | NO | NO | 19920076 | 1992-04-23 | 2416 | CITIZENS UTILITY CO | 89 CIVIC CENTER | LAKE HAVASU CITY | MOHAVE | AZ | 86403 | 3 | NO | 1330 | 1992-03-23 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 8 |  | 19920324 | 10 | 52 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 1.5 | 0.066 | 1220.1120 | ASO PIPE | 1968 | 1968 | UNDER GROUND OR UNDER WATER |  | JACK SCHOONMAKER - TOWN MANAGER | 6028552266 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | WHILE REPLACING SERVICE LINE, SHOVEL CUT PLASTIC PIPE CAUSING GAS TO ESCAPE AND IGNITE.
2025-01-31 10:21 | NO | NO | 19920077 | 1992-04-23 | 11800 | LOUISIANA GAS SERVICE CO | 3300 FORSYTHE AVE AT BAYOU DESIARD | MONROE | OUACHITA | LA | 71201 | 3 | NO | 920 | 1992-04-01 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 53 |  |  | 36 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | D L MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | EQUIPMENT OPERATOR FOR LOUISIANA HIGHWAY DEPARTMENT CYT STELL MAIN WHILE REMOVING DIRT FROM A CULVERT CROSSING FORSYTHE AVENUE.
2025-01-31 10:21 | NO | NO | 19920078 | 1992-05-26 | 13790 | NORTHERN GAS OF WYOMING - DIV OF KN ENERGY INC | 818 EAST 5TH STREET #8 | GILLETTE | CAMPBELL | WY | 82716 | 3 | NO | 336 | 1992-05-02 | 0 | 0 | 48000 | 37587.868 | 90754.6833 | YES | 2 | 0 |  | 19920502 | 35 | 38 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 75 | 1.25 |  |  | 0 | 0 | ABOVE GROUND |  | DAN KUEHN - DIRECTOR OF GAS SERVICE | 3072351541 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CAR HIT METER LOOP AND MOBILE HOME. A CAR CAR DRIVEN BY AN 18YR OLD LADY, WHICH WAS LATER CHARGED WITH DWI, LEFT THE STREET, PROCEEDED DOWN AN ALLEY, THEN BETWEEN TWO TRAILERS, RUNNING OVER A FENCE, THE ELECTRICAL BOX, TELEPHONE BOX, AND OVER THE GAS METER LOOP HITTING THE SIDE OF THE MOBILE HOME. THE CAR BROKE OFF THE PIPE NIPPLE ABOVE THE STOP COCK AND THE VEHICLE OR ITS IMPACT IGNITED THE GAS, DESTROYING THE VEHICLE ( A1973 CAMARO) AND THE MOBILE HOME. THERE WAS ALSO HEAT AND SMOKE DAMAGE TO TWO ADJACENT MOBILE HOMES. THE GAS WAS SHUT OFF BY PULLING THE CAR OFF THE SERVICE RISOR AFTER EXTINGUISHING THE FIRE AND TURNING OFF THE GAS STOP, WHICH WAS STILL IN PLACE. THE ENTIRE SERVICE WAS REPLACED AFTER THE FIRE BECAUSE OF POSSIBLE HEAT DAMAGE. THERE WERE NO INJURIES OR FATALITIES. THE FIRE CHIEF'S EESTIMATE OF DAMAGES IS $48,000.00.
2025-01-31 10:21 | YES | YES | 19920080 | 1992-05-18 | 13710 | NORTHERN ILLINOIS GAS CO | 1634 JOHNSON AVE | ROCKFORD | WINNEBAGO | IL | 61109 | 3 | NO | 930 | 1992-04-08 | 0 | 2 | 50000 | 39154.0291 | 94536.1285 | Null | 1 | 33 |  | 19920408 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NON SPECIFIED | STEEL |  | 1.25 | 0.191 |  |  | 0 | 1949 | UNDER GROUND OR UNDER WATER |  | STEVE RIVARD - GENERAL SUPERVISOR SYSTEM OPERATING | 8159655416 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-03-13 | YES | 3 |  | YES |  |  | N1-GAS LOCATOR ATTEMPTED TO LOCATE THE SERVICE BY CONTACTING THE CUSTOMER. THE CUSTOMER TOLD HIM SHE HAD NO GAS SERVICE. THE LOCATOR THEN CONTACTED HISHEADQUARTERS AND DETERMINED THAT THE CUSTOMER WAS A NONUSER OF NATURAL GAS. 3RD PARTY DAMAGED AN UN-MARKED GAS SERVICE CAUSING GAS TO ENTER THE BASMENT& BE IGNITED BY AN UNKNOWN SOURCE.
2025-01-31 10:21 | NO | NO | 19920085 | 1992-05-11 | 4499 | ENTEX - DIVISION OF ARKLA INC | 1019 BROOKS ST | ROSENBERG | FORT BEND | TX | 77471 | 3 | NO | 1019 | 1992-02-16 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 0 | 30 |  | 19920216 | 28 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSELINE | OTHER | N/A | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN R SIMONETTI - ASSISTANT DIRECTOR OF OPERATIONS. | 7136545114 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAK ON CUSTOMER LINE
2025-01-31 10:21 | YES | NO | 19920087 | 1992-05-12 | 2568 | COLORADO SPRINGS, CITY OF | 27 W ST ELMO | COLORADO SPRINGS | EL PASO | CO | 80906 | 3 | NO | 649 | 1992-04-11 | 0 | 0 | 500000 | 391540.2914 | 945361.2846 | Null | 1 | 20 |  | 19920413 | 60 | 70 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | VALVE | SCREWED, FITTING | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1965 | ABOVE GROUND |  | WAYNE E BOOKER - ENGINEERING/ OPERATIONS MANAGER | 7196365722 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | AN EXPLOSION SUSPECTED TO BE CAUSED BY NATURAL GAS BLEW OUT SEVERAL PORTIONSOF WALL ON BOTH STORIES OF THE BUILDING. THE EXPLOSION CAUSED A BRICK WALL TO COLLAPSE ONTO THE GAS METER, BREAKING THE INLET PIPING UPSTREAM OF THE REGULATOR. THE RUPTURED GAS LINE FED THE FIRE LINE UNTIL THE GAS DEPARTMENT EXCAVATED A SERVICE SHUT OFF VALVE AT THE PROPERTY LINE AND THE METER WITH NO LOSS OF PRESSURE. THE COLORADO SPRINGS FIRE DEPARTMENT IS CONINUING TO INVESTIGATE THE ACCIDENT. THE SOURCE OF GAS AND IGNITION IS SUSPECTED TO HAVE BEEN DOWNSTREAM OF THE METER.
2025-01-31 10:21 | YES | YES | 19920090 | 1992-06-29 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 4609 BANGOR ST | DETROIT | WAYNE | MI | 48226 | 3 | NO | 1632 | 1992-05-12 | 0 | 1 | 35000 | 27407.8204 | 66175.2899 | Null | 1 | 50 |  | 19920512 | 2 | 5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | AUTOMATIC METER READING D | OTHER | NON SPECIFIED | 0 | 0 |  | HEXAGRAM | 1986 | 1987 | WITHIN/UNDER BUILDING |  | CANJOR D REED | 3132566196 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | METER ASSEMBLY FAILURE DUE TO EXCESS EXPOSURE TO HIGH LEVEL OF WATER AND SEWAGE. A NATURAL GAS EXPLOSION RESULTED FROM A LEAK ASSOCIATED WITH AN AUTOMATIC METER READING DEVICE (SENSOR). THE SENSOR DISLOGED FROM THE METER DIAL GLASS, THUS ALLOWING THE ESCAPE GAS. THE GAS MIGRATED TO AN UPPER LEVEL APARTMENT WHERE IT IGNITED. THE SENSOR BECAME DISLODGED AFTER BEING SUBMERGED IN SEVERAL FEET OF SEWAGE WATER FOR A PROLONGED PERIOD OF TIME. THE FREEZING OF TTHE WATER OVER THE WINTER CAUSED THE BOND BETWEEN THE SENSOR AND THE METER TO FAIL .
2025-01-31 10:21 | NO | NO | 19920091 | 1992-06-30 | 1640 | BOSTON GAS CO | RICA ROAD | WAYLAND | MIDDLESEX | MA | 01778 | 1 | NO | 30 | 1992-06-14 | 0 | 0 | 0 | 0 | 0 | YES | 6 | 10 |  | 19920614 | 52 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NON SPECIFIED | STEEL |  | 4 | 0.219 | API 5L GRADE B |  | 0 | 1964 | UNDER PAVEMENT |  | ROBERT J CAVICCHI - MANAGER DISTRIBUTION ADM | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SPEEDING CAR HIT A UTILITY POLE THAT HAD A HIGH VOLTAGE ELECTRIC TRANSFORMER ATTACHED TO IT. THE POLE FELL TO THE GROUND AND THE LIVE WIRES ARCED THROUGH THE PAVEMENT AND SOIL. THE STEEL GAS MAIN WAS IN CONTACT WITH A DRAINAGECATCH BASIN. THE ARCING ELECTRICITY BURNT TWO HOLES THROUGH THE GAS MAIN AND THE ESCAPING GAS WAS IGNITED. THE GAS FLOW WAS STOPPED BY SHUTTING OFF THEMAIN LINE GATE VALVES.
2025-01-31 10:21 | YES | YES | 19920092 | 1992-07-01 | 18496 | SOUTHERN CONNECTICUT GAS CO | 385 NEW HAVEN AVE | MILFORD | NEW HAVEN | CT | 06460 | 3 | NO | 350 | 1992-06-06 | 0 | 2 | 15000 | 11746.2087 | 28360.8385 | Null | 2 | 5 |  | 19920606 | 18 | 31 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | NON SPECIFIED | OTHER | NOT SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | PETER D LOOMIS - VP, DISTRIBUTIONS & CUSTOMER SERVICE | 2033828204 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | VENTING GAS FROM REGULATOR VAULT IGNITED DURING STARTUP OF GASOLINE ENGINE PUMP INJURING TWO EMPLOYEES AND DAMAGING TRUCK PARKED NEARBY.
2025-01-31 10:21 | NO | NO | 19920094 | 1992-06-29 | 15007 | PACIFIC GAS & ELECTRIC CO | 4850 KENFIELD ROAD | STOCKTON | SAN JOAQUIN | CA |  | 3 | NO | 2245 | 1992-05-31 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 1 | 45 |  | 19920601 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 1964 | ABOVE GROUND |  | W R MAZOTTI - V P - GAS & ELECTRIC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | CAR VEERED OFF PRIVATE DRIVE & STRUCK GAS 10 METER MANIFOLD. FIRE ENSUED, DAMAGING CAR AND BUILDING.
2025-01-31 10:21 | YES | YES | 19920096 | 1992-06-17 | 2748 | CONSUMERS POWER CO | 440 MAIN ST | ROCHESTER | OAKLAND | MI | 48063 | 4 | NO | 1720 | 1992-05-20 | 1 | 2 | 700000 | 548156.408 | 1323505.7984 | Null | 3 | 25 |  | 19920520 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.113 | COMPRESSION | CHICAGO | 0 | 1958 | UNDER PAVEMENT |  | KENNETH L ELENBAAS - GENERAL SUPVR OF O&M | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | YES |  |  | CONTRACTOR EXCAVATING FOR TREE PLANTING HIT GAS SERVICE LINE AND PULLED COMPRESSION FITTING APART ALLOWING GAS TO MIGRATE INTO BUILDING RESULTING IN EXPLO
2025-01-31 10:21 | NO | NO | 19920097 | 1992-06-24 | 15007 | PACIFIC GAS & ELECTRIC CO | 826 14TH ST | MARYSVILLE |  | CA | 95901 | 3 | NO | 439 | 1992-05-14 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 0 | 59 |  | 19920514 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | VALVE | ALSO REGULATOR METER | STEEL |  | 0 | 0 | STEEL |  | 0 | 1987 | ABOVE GROUND |  | W R MAZOTTI | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | HOUSE WAS VACANT. FIRE STARTED BY AN ARSONIST.
2025-01-31 10:21 | YES | YES | 19920099 | 1992-05-28 | 1088 | BALTIMORE GAS & ELECTRIC CO | 1605 KEY HWY | BALTIMORE |  | MD | 21230 | 3 | NO | 930 | 1992-05-18 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 |  | 19920518 | 90 | 100 | BY TEST | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | METER SET ASSEMBLY |  | OTHER | NO COMPONENT FAILURE | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | RICHARD M LEPSON - SUPT GAS CONSTR | 4102914747 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | TECHNICIANS ON SITE DID NOT PROPERLY DEPRESSURIZE THE GAS FILTER BEFORE SERVICING IT. THE GAS FILTER WAS ISOLATED BETWEEN TWO VALVES BUT WAS STILL PRESSURIZED WIHT 90 PSIG BETWEEN THE REGULATOR AND UPSTREAM VALVES. AS THE TECHNICIAN ATTEMPTED TO REMOVE THE INSPECTION PLATE, ALL THE PRESSURE OF ITS TOTAL VOLUME WAS DISCHARGED AT ONE TIME. THE INSPECTION PLATE STRUCK ONE EMPLOYEE RESULTING IN PERSONNEL SERIOUS INJURY TO ONE TECHNICIAN AND SOME MINOR INJURYTO THE OTHER TECHNICIAN. THE CUSTOMER SYTEM OR BG&E'S SYSTEM WERE NEVER OUTOF SERVICE BECAUSE THE BY-PASS APPARATUS WAS BEING UTILIZED AT THE TIME OF THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 19920100 | 1992-06-03 | 1800 | BROOKLYN UNION GAS CO | 1575 FLATBRUSH AVE | BROOKLYN |  | NY |  | 4 | NO | 342 | 1992-05-25 | 0 | 0 | 400000 | 313232.2331 | 756289.0277 | Null | 2 | 2 |  | 19920527 | 0.25 | 0.43 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J L CROSS - SECTION MANAGER | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON MARCH 25, 1992 AT 03:42 HOURS, BROOKLYN UNION GAS RECEIVED NOTIFICATION FROM THE N.Y.C. FIRE DEPARTMENT THAT A FIRE A WAS IN PROGRESS AT 1575 FLATBUSH AVENUE, BROOKLYN, N.Y. AT 05:45 HOURS THE GAS SERVICE CURB VALVES TO THISADDRESS AND THE TWO ADJACENT BUILDINGS AT 1573 AND 1577 FLATBRUSH AVENUE WERE CLOSED BY BROOKLYN UNION GAS COMPANY CREWS. THE N.Y.C. FIRE DEPARTMENT IS STILL CONDUCTING AN INVESTIGATION AND IT IS NOT KNOWN WHETHER NATURAL GAS WASINVOLVED.
2025-01-31 10:21 | YES | YES | 19920101 | 1992-06-05 | 19205 | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | 1121 DASPIT ST | HOUMA | TERREBONNE | LA | 70361 | 3 | NO | 329 | 1992-04-09 | 0 | 1 | 40000 | 31323.2233 | 75628.9028 | Null | 0 | 45 |  | 19920409 | 20 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | FITTING |  | OTHER | CAST STEEL | 1.66 | 0.14 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | WAYNE RONICHAUX - SUPERINTENDENT | 5048736761 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | WE WERE LOOKING IN THE AREA TO PINPOINT THIS LEAK WHEN THE FIRE OCCURRED. FIRE APPARENTLY STARTED IN THE BACK AREA OF THE RESIDENCE. INITIAL THRUST FROM THE SPREADING FIRE APPARENTLY WAS THE REASON FOR THE GAS LEAK CATCHING IN FIRE. THERE IS NO EVIDENCE OF AN APPARRENT EXPLOSION. THE FIRE AND HEAT DAMAGED THE TIN ROOF BUT NO WINDOWS OR DOORS SHOW ANY SIGNS OF AN EXPLOSION. IF ANYTHING IS PROVEN AT A LATTER DATE, WE WILL FOLLOW-UP WITH A SUPPLEMENT REPORT.
2025-01-31 10:21 | NO | NO | 19920102 | 1992-06-23 | 2668 | COMMONWEALTH GAS SERVICES INC | U S 360 & SOUTHSIDE DR | MIDLOTHIAN |  | VA | 23113 | 1 | NO | 1104 | 1992-05-29 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 1 | 20 |  | 19920529 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 8 | 0.75 | PE 2406 | PLEXCO | 1987 | 1987 | UNDER PAVEMENT |  | R C INNES - GENERAL MANAGER | 8043235300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-04-24 | YES | 3 | PAINT MARKS | YES |  |  | ON MAY 29, 1992 AT APPROXIMATELY 11:04 A.M. A BORING CONTRACTOR WORKING AT THE INTERSECTION OF U.S. ROUTE 360 AND SOUTHSHORE DRIVE, MIDLOTHIAN, VIRGINIA BORED INTO A 8" PLASTIC MEDIUM PRESSURE GAS MAIN LINE. THE RESULTING NATURALGAS LEAK WAS APPARENTLY IGNITED BY THE BORING MACHINE ENGINE. THE RESULTINGFIRE DAMAGED THE BORING MACHINE, A KOMATSU TRACK EXCAVATOR MACHINE, AN ATT SERVICE AND OVERHEAD TV CABLES. NO INJURIES WERE REPORTED. A COMMONWEALTH GAS SERVICES, INC. EMPLOYEE, UPON APPROACHING THE SITE, WITNESSED CONTRACTOR EMPLOYEES FLEEING THE SITE AND INITIAL IGNITION. THE COS EMPLOYEE CONTACTED THE COMPANY DISPATCHER AT 11:07 A.M. AND PERMANENT REPAIRS COMPLETED AT 10:30 P.M. IN ALL, 1179 CUSTOMERS WERE TEMPORARITY WITHOUT SERVICE AND ALL BUT THOSE NOT HOME HAD SERVICE RESTORED BY LATE IN THE AFTERNOON ON MAY 30, 1992.
2025-01-31 10:21 | YES | YES | 19920104 | 1992-06-15 | 3170 | DAYTON POWER & LIGHT CO | 308 S MAIN ST | LEWISBURG | PREBLE | OH | 45338 | 3 | NO | 950 | 1992-05-14 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 |  | 19920514 | 5 | 5 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | IGNITION SOURCE UNKNOWN | STEEL |  | 1 | 0 |  |  | 0 | 0 | OTHER | OPEN EXCAVATION | RICHARD C ROTH - MANAGER, GAS OPERATIONS | 5132272145 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 3-MAN CREW WAS REPLACING A 1" STEEL GAS SERVICE WITH A 1" PLASTIC PIPE. WHILE ONE EMPLOYEE WAS REMOVING THE SCREWED CAP FROM THE COUPLING TO INSERT THE TRANSFITTING TO CONNECT THE SERVICE, THE GAS IGNITED IN THE EXCAVATED TRENCH. BOTH EMPLOYEES JUMPED OUT OF THE TRENCH TO EXTINGUISH THEIR BURNING CLOTHING, WHILE A THIRD EMPLOYEE USED A FIRE EXTINGUISHER TO PUT OUT THE FIRE AND REPLACE THE CAP TO STOP THE ESCAPING GAS. ONE PERSON WAS HOSPITALIZED AND ONEWAS TREATED AND RELEASED. THERE WAS NO PROPERTY DAMAGE.
2025-01-31 10:21 | YES | YES | 19920105 | 1992-06-22 | 4483 | ENSTAR NATURAL GAS CO | 2816 BEAVER LOOP RD | KENAI | KENAI BOROUGH | AK | 99611 | 2 | NO | 30 | 1992-05-24 | 0 | 2 | 80000 | 62646.4466 | 151257.8055 | Null | 2 | 0 |  | 19920526 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER PLASTIC | POLY PLASTIC TUBING ENCAS | 0.875 | 0.09 | DRISCOPIPE | PHILLIPS | 0 | 1981 | OTHER | METER ON SIDE OF TRAILER | DREW SMITH - SENOIR ENGINEER | 9072643744 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | RESIDENTAIL STRUCTURE FIRE MELTED THE GAS METER/REGULATOR ASSEMBLY. THE INITAIL FIRE INVESTIGATION DETERMINED THE FIRE STARTED INSIDE THE STRUCTURE FROMFAULTY HOUSE PIPING AND/OR A GAS APPLIANCE.
2025-01-31 10:21 | NO | NO | 19920107 | 1992-07-10 | 15007 | PACIFIC GAS & ELECTRIC CO | 3411 COTTAGE ST | EUREKA | HUMBOLDT | CA |  | 0 | NO | 1402 | 1992-06-09 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 0 | 8 |  | 19920609 | 40 | 50 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER - OWNED HOUSLINE | OTHER | CUSTOMER OPENED HOUSELINE | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | W R MAZOTTI - V.P. - GAS & ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS ESCAPING FROM AN UNCAPPED GAS CONNECTION IN A LAUNDRY ROOM EXPLODED, SEVERLY DAMAGING A BUILDING. THE CUSTOMER-OWNED BRANCH LINE TO THE CONNECTION CONTAINED A CUSTOMER-OWNED VALVE. IT IS NOT KNOWN IF THE VALVE HAD BEEN OPENED OR WAS LEAKING. SUBSEQUENT INVESTIGATION INDICATED NO LEAKS ON COMPANY-OWNED FACILITIES.
2025-01-31 10:21 | YES | NO | 19920108 | 1992-07-06 | 8280 | IOWA SOUTHERN UTILITIES CO | CORNER OF I-35 & HWY 34 | OSCEOLA | CLARKE | IA | 50213 | 3 | NO | 425 | 1992-06-16 | 0 | 0 | 200000 | 156616.1166 | 378144.5138 | Null | 1 | 0 |  | 19920617 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INTERIOR PIPING | OTHER | UNKNOWN | STEEL |  | 2 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JEFFREY K ROSENCRANTS - ATTORNEY | 5154375281 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 4:00 A.M. ON JUNE 16, BRAIN NELSEN, WHO IS THE OPERATOR OF THE TRUCK STOP, WAS APPARENTLY HOSING OUT A PICKUP TRUCK WHICH WAS LOCATED INTHE PIT AREA OF ONE OF THE SERVICE BAYS. AT THIS TIME THE EXPLOSION OCCURRED. MR. NELSEN HAS BEEN INTEVIEWED BY BOTH THE NATURAL GAS DEPARTMENT AT IOWASOUTHERN UTILITIES COMPANY AND ITS INVESTIGATOR AND REPORTS THAT HE DID NOT SMELL NATURAL GAS PRIOR TO THE TIME OF THE EXPLOSION. AT THE PRESENT TIME THE EXACT CAUSE OF THE EXPLOSION HAS NOT BEEN DETERMINED. THE STATE FIRE MARSHALL'S OFFICE HAD INVESTIGATED, AND HAD PRELIMINARILY INDICATED THAT NATURAL GAS ID THE LIKELY CAUSE. IOWA SOUTHERN UTILITIES COMPANY HAS HIRED AN EXPERTIN EXPLOSION RECONSTRUCTION, DR. JERRY HALL, TO DO OUR OWN INVESTIGATION ANDHE VISITED THE SCENE IN OSCEOLA, IOWA ON JUNE 20, 1992. THERE WERE NO SEROIUS INJURIES NOR FATLITIES ARISING OUT OF THIS EXPLOSION. BRAIN NELSEN, THE OPERATOR OF THE TRUCK STOP, DID HAVE A MINOR BURN ON HIS ARM, BUT WAS NOT HOSPITALIZED. NO OTHER PROPERTY DAMAGE OTHER THAN THE TRUCK STOP/CAFE HAS BEEN REPORTED. IN ADDITION, LEAK SURVEYS WERE PERFORMED ON THE OUTSIDE OF THE TRUCK STOP SUBSEQUENT TO THE EXPLOSION AND INDICATED NO LEAKAGE OF NATURAL GAS. AS FAS AS HISTORY OF NATURAL GAS LEAKS AT THIS LOCATION, OUR RECORDS INDICATETHAT ANNUAL INSIDE BUILDING GAS LEAKS SURVEYS ARE PERFORMED IN OSCEOLA. ON MARCH 19, 1992, THE ANNUAL SURVEY FOR 1992 WAS PREPARED AND A SMALL LEAK ON AN ELBOW FITTING ON THE GAS LINE IN THE BUILDING WAS FOUND. THE TRUCK STOP EMPLOYEE WAS NOTIFIED OF THE RESULTS OF THE SURVEY, AND INDICATED THAT A LOCAL PLUMBING AND HEATING CONTRATOR WOULD FIX THE LEAK. AS A MATTER OF FOLLOW UP,THE AREA OPERATIONS SUPERVISOR FOR OSCEOLA, ED DAVISON, CONTACTED THE OPERATOR OF THE STATION, BRAIN NELSEN, ON APRIL 14, 1992. MR. NELSEN WAS SPECIFICALLY ASKED IF THE GAS LEAK FOUND MARCH 19, 1992 HAD BEEN FIXED AND MR. NELSENINDICATED THAT THE LEAK HAD BEEN FIXED AND NOTED THE SAME ON THE INSIDE LEAKSURVEY SHEET ON THE SAME DAY.
2025-01-31 10:21 | YES | NO | 19920110 | 1992-07-13 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1414 EAST THOUSAND OAKS BLVD | THOUSAND OAKS | VENTURA | CA |  | 3 | NO | 1210 | 1992-06-19 | 0 | 0 | 250000 | 195770.1457 | 472680.6423 | Null | 2 | 5 |  | 19920619 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | OTHER | PIPE FITTING OF VARIOUS S | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | G J LAMBERT - MANAGER , SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | AUTOMOBILE OPERATOR LOST CONTROL OF THE VEHICLE ALLOWING IT TO TRAVEL OVER CONCRETE WHEEL BUMPERS, THROUGH TWO 4" CONCRETE-FILLED STEEL METER GUARDS AND INTO METER SET ASSEMBLY (MSA). ESCAPING GAS FROM THE DAMAGED MSA IGINITED ANDTHE RESULTING FIRE DAMAGED THE CAR, THE BUILDING AND SURROUNDING STRUCTURES.
2025-01-31 10:21 | NO | NO | 19920115 | 1992-08-12 | 15007 | PACIFIC GAS & ELECTRIC CO | SAN FRANCISCO | SAN FRANCISCO |  | CA | 94106 | 3 | NO | 1620 | 1992-07-06 | 0 | 0 | 50000 | 39154.0291 | 94536.1285 | Null | 0 | 45 |  | 19920707 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S FURNACE | OTHER | UNKNOWN AT THIS TIME | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | W R MAZOTTI, V O-GAS & ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER'S GRAVITY FURNACE "BLEW OUT" CAUSING BUILDING FIRE.
2025-01-31 10:21 | YES | NO | 19920116 | 1992-08-10 | 15007 | PACIFIC GAS & ELECTRIC CO | 663 CAMPBELL | SAN FRANCISCO | SAN FRANCISCO | CA |  | 3 | NO | 337 | 1992-07-14 | 0 | 0 | 355000 | 277993.6069 | 671206.512 | Null | 4 | 43 |  | 19920714 | 30 | 35 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | NON SPECIFIED | STEEL |  | 0.75 | 0.133 |  |  | 0 | 1951 | WITHIN/UNDER BUILDING |  | W R MAZOTTI - V.P.- GAS & ELEC TECHNICAL SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OCCURRED IN THE BUILDING AND THE GAS SERVICE RISER WAS FOUND TO HAVE BEEN CUT NEAR THE RISER VALVE. THE ESCAPING GAS IGNITED.
2025-01-31 10:21 | NO | NO | 19920117 | 1992-08-10 | 22763 | WISCONSIN GAS CO | 4300 SOUTH 27TH ST | MILWAUKEE |  | WI | 53202 | 3 | NO | 1711 | 1992-07-09 | 0 | 0 | 51000 | 39937.1097 | 96426.851 | Null | 0 | 27 |  | 19920710 | 33 | 35 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 34 | 0 |  |  | 0 | 1970 | ABOVE GROUND |  | GREGORY B SCHROEDER, P.E. | 4142916700 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE DRIVER OF A CAR PULLING INTO A PARKING SPACE AT THE BUDGET SOUTHGATE MOTEL AT 4300 SOUTH 27TH STREET, MILWAUKEE APPARENTLY DROVE TOO FAR FORWARD. THE CAR EITHER HIT OR PUSHED A WHEEL BARROW INTO THE GAS METER SET. THE SERVICE RISER PIPE BROKE RELEASING NATURAL GAS AT MAIN PRESSURE. A NEARBY AIR CONDITIONING MOTOR APPARENTLY IGNITED THE GAS. A FIRE FIGHTER SHUT OFF THE RISERVALVE TO STOP THE LEAK. FIRE DAMAGE TO THE MOTEL EXCEEDED $50,000.
2025-01-31 10:21 | NO | NO | 19920119 | 1992-08-07 | 21363 | VISION ENERGY JACKSONVILLE BEACH DIV | 1210 BEACH BLVD (REAR OF BUILDING) | JACKSONVILLE BEACH | DUVAL | FL | 32250 | 2 | NO | 1605 | 1992-06-27 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 25 |  |  | 25 | 100 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | MAIN |  | OTHER | NON SPECIFIED | STEEL |  | 2.067 | 0.154 | ASTM A53 |  | 0 | 1968 | UNDER PAVEMENT |  | WAYNE MOORE - DISTRICT MANAGER | 9042467316 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | COATED | YES | 1968 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS MAIN WAS DISCONTINUED FROM SERVICE COMPLETELY (SMALL SECTION) SERVICED ONLY ONE CUSTOMER. COMPLAINTS OF ODOR LED US TO LEAK IN 2" DIST. MAIN (AERATION REQUIRED).
2025-01-31 10:21 | YES | YES | 19920123 | 1992-07-30 | 15359 | PEOPLES NATURAL GAS | 1655 NW 21 AVENUE | ROCHESTER | OLMSTED | MN | 55901 | 3 | NO | 1526 | 1992-07-11 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 15 |  | 19920711 | 14 | 14 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.0062 |  | CENTURY | 1968 | 1968 | UNDER GROUND OR UNDER WATER |  | GREGORY J BENAK | 4022212021 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-06-23 | YES | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19920124 | 1992-08-10 | 14210 | OKLAHOMA NATURAL GAS CO | 5413 EAST 105TH PLACE | TULSA | TULSA | OK | 74137 | 3 | NO | 1130 | 1992-07-30 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 32 |  | 19920730 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.21 | PE-2306 | PHILLIPS | 1990 | 1991 | UNDER GROUND OR UNDER WATER |  | GERRY LYNN - CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-07-27 | YES | 2 |  | YES |  |  | CONTRATOR WORKING ON AN ELECTRICAL SERVICE LINE CUT A 2" PLASTIC LINE WITH AKUBATO DITCHING MACHINE. A SMALL LEAK OCCURRED WHICH THE CONTRACTOR ATTEMPTED TO REPAIR WITH PLASTIC TAPE. THE SAME LEAK WAS IGNITED BY A PROPANE TORCHUSED BY THE CONTRACTOR. THE FIRE INJURED THE CONTRACTOR'S EMPLOYEE AND BURNED A HOLE IN THE PLASTIC PIPE RESULTING IN A MUCH LARGER FIRE.
2025-01-31 10:21 | NO | NO | 19920126 | 1992-08-24 | 4497 | ENTEX INC | 2711 ELEVENTH STREET | HUNTSVILLE | WALKER | TX | 77340 | 1 | NO | 1615 | 1992-07-28 | 0 | 0 | 1600 | 1252.9289 | 3025.1561 | Null | 0 | 18 |  | 19920728 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | ASTM-2513 | DUPONT | 1988 | 1988 | UNDER GROUND OR UNDER WATER | EXPOSED IN CONSTRUCTION D | JOHN R SIMONETTE, ASST. DIRECTOR OF OPERATIONS | 7136545114 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-07-27 | YES | 3 | PAINT | NO |  |  | THIS LINE WAS LOCATED AT 8:00 A.M. JULY 28, 1992, BY PAINT. THE THIRD PARTY HAND DUG AND EXPOSED THE LINE AND TELEPHONE CABLE IN CONSTRUCTION DITCH. AFTER SPLICING, THE TELEPHONE REPAIRMAN USED A TORCH TO PLACE SHRINK HEAT SLEEVES ON SPLICE AND LET THE TORCH GET TO THE PLASTIC LINE AND MELT IT AND CAUSED GAS TO ESCAPE TO THE FIRE ON THE TORCH.
2025-01-31 10:21 | YES | YES | 19920127 | 1992-08-31 | 2392 | CITIZENS GAS & COKE UTILITY | 21ST ST & GIRLS SCHOOL ROAD | INDIANAPOLIS | MARION | IN | 46224 | 3 | NO | 921 | 1992-08-06 | 0 | 3 | 25000 | 19577.0146 | 47268.0642 | Null | 0 | 41 |  | 19920806 | 18 | 40 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | LATERAL CONNECTION | STEEL |  | 8 | 0.25 | API-5L | L B FOSTER | 1985 | 1985 | OTHER | IN EXCAVATION | GREG BIELEFELD - TECHNICAL ADMINSTRATOR | 3179274626 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | THE CAUSE OF THE ACCIDENT HAD BEEN DETERMINED TO BE A MISAPPLICATION OF THE HOT TAPPING PROCEDURE, ALLOW GAS TO ESCAPE INTO THE EXCAVATION WHICH ULTIMATELY WAS IGNITED, BY AN UNKNOWN SOURCE, INFLICTING BURN INJURIES TO FOUR OF THECORBITT AND SONS CONSTRUCTION COMPANY WORKMEN
2025-01-31 10:21 | YES | YES | 19920128 | 1992-08-27 | 18260 | SHELBY GAS ASSOCIATION | INTERSECTION OF 5TH ST & 5TH AVE SO | SHELBY | TOOLE | MT | 59474 | 1 | NO | 1600 | 1992-08-11 | 0 | 2 | 100 | 78.3081 | 189.0723 | Null | 0 | 30 |  | 19920811 | 12 | 18 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NO FAILER | STEEL | POLYETHYLENE PLASTIC | 2 | 0 |  |  | 0 | 0 | OTHER | OPEN DITCH | LARRY L NELSON - GENERAL MANAGER | 4064345575 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SHELBY GAS ASSOCIATION CREW CONSISTING OF A FOREMAN AND TWO SERVICEMEN WERE REPLACING A 600 FT SECTION OF 2" STEEL DISTRIBUTION MAIN WITH 2" ALDYL A PEPIPE. THE DISTRIBUTION SYSTEM WAS BEING OPERATED AT 12 PSIG AND THE TRANSITION FROM STYEEL TO P E PIPE WAS TO BE DONE "HOT" IN ORDER TO MAINTAIN SERVICETO 41 CUSTOMERS. THE DITCH HAD BEEN OPENED AND THE PE PILE LAID IN THE DITCH. THE PE PIPE WAS THEN CUT IN AT THE SOURCE END USING A STANDARD DUPONT ALDYL A TO STEEL TRANSITION FITTING. A DUPONT TRANSITION FITTING HAD PREVIOUSL BEEN INSTALLED AT THE LOAD END AND PLUGGED. A MECHANICAL FITTING WAS TO BE USED TO JOIN THE TRANSITION FITTING TO THE EXISTING STEEL PIPE. THE STEEL PIPE WAS THEN CUT AND WHEN THE SERVICEMAN BROUGHT THE STEEL PART OF THE TRANSITION FITTING IN CONTACT WITH THE EXISTING STEEL PIPE TO SLIDE ON THE MECHANICALFITTING THE ESCAPING GAS IGNITED. A NEAR BY ZONE VALVE WAS THEN CLOSED TO EXTINGUISH THE FLAME. UPON DEBRIEFING THE THREE CREW MEMBERS, IT WAS AGREED THAT A STATIC DISCHARGE FORM THE PE PIPE TO THE STEEL PIPE CAUSED THE IGNITION. THIS PROCEDURE HAD BEEN USED BY THIS CREW OVER THE PAST FIFTEEN YEARS WITHOUT INCIDENT. HOWEVER THEY FELT THAT WEATHER CONDITIONS MAY HAVE CONTRIBUTEDTO THE STATIC BUILD-UP ON THE PE PIPE. THE TEMPERATURE WAS 91 DEGREES, THE HUMIFITY VERY LOW AND THE DITCH DRIER THAN USUAL. THEY ALSO FELT THAT MORE EMPHASIS SHOULD HAVE BEEN GIVEN TO PREVENT STATIC BUILD-UP ON THE PE PIPE BY USING A GROUNDING TAPE OR WET RANGS TO DISSIPSATE THE CHARGE. OPERATING PROCEDURES WILL BE REVIEWED AND MORE EMPHASIS PLACED ON DISSIPATING STATIC ELECTRICITY WHEN WORKING WITH PE PIPE IN THE FUTURE.
2025-01-31 10:21 | YES | YES | 19920129 | 1992-08-26 | 11800 | LOUISIANA GAS SERVICE CO | 28612 KRENTEL RD | LACOMBE | ST TAMMANY | LA | 70445 | 1 | NO | 1050 | 1992-07-27 | 0 | 1 | 5000 | 3915.4029 | 9453.6128 | Null | 0 | 40 |  | 19920727 | 68 | 80 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | TOWN BORDER STATION | REGULATOR/METER |  | CAST IRON |  | 0 | 0 | 500-B | AMERICAN METER | 0 | 0 | ABOVE GROUND |  | D L MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE PRIMARY REGULATOR AT THE LACOMBE TOWN BORDER STATION APPARENTLY MALFUNCTIONED CAUSING AN OVERPRESSURE CONDITION ON THE METER. THE LARGE POSITIVE DISPLACEMENT METER SHATTERED CAUSING INJURY TO ONE EMPLOYEE. THE CAUSE OF THE ACCIDENT IS STILL UNDER INVESTIGATION TO DETERMINE WHAT SEPCIFIC MATERIAL OR EQUIPMENT FALED AND HOW TO PREVENT FUTRUE INCIDENTS.
2025-01-31 10:21 | YES | YES | 19920130 | 1992-08-31 | 11720 | LONG ISLAND LIGHTING COMPANY | 120 ROUND HILL RD | EAST HILLS | NASSAU | NY | 11576 | 4 | NO | 1123 | 1992-07-30 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 28 |  | 19920803 | 59 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1941 | WITHIN/UNDER BUILDING |  | THOMAS E LUPSKI - CODE AND SPECIFICATION ENGINEER | 5169334400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR WAS INSTALLING OIL TANK AT 120 ROUNDHILL ROAD IN EAST HILLS. WHILE EXCAVATING, CONTRACTOR PULLED 3/4" STEEL GAS SERVICE . THE PULLING ACTION CAUSED A FITTING INSIDE THE HOUSE TO BREAK, ALLOWING GAS TO ESCAPE. CONTRACTOR CLOSED THE HEAD OF SERVICE VALVE, STOPPING THE FLOW OF GAS. CONTRACTOR EVACUATED HOUSE. CONTRACTOR AND RESIDENT THEN REENTERED HOUSE TO VENTILATE. UPON RE-ENTRY, THE RESIDENT TURNED ON LIGHT SWITCH. THIS ACTION CAUSED GAS TOEXPLODE. THE EXPLOSION CAUSED INJURY TO CONTRACTOR AND RESIDENT. LILCO GASCUSTOMER SERVICE CLOSED CURB COCK AND MADE SAFE. LILCO GAS CONSTRUCTION NADMAINTENANCE TUBED AND RELOCATED SERVICE. EXPLOSION CAUSED DAMAGE TO WALLS AND WINDOWS OF HOUSE. POLICE AND PUBLIC SERVICE COMMISSION ON LOCATION. NO TRAFFIC DETOURS NOR NEWS MEDIA ON LOCATION. MILDRED ELIE (RESIDENT) AND SCOTT CARTER WERE TAKEN TO HOSPITAL WITH MINOR INJURIES. UPON CONFIRMATION BY THE OPERATOR THAT THE RESIDENT REQUIRED IN-PATIENT HOSPITALIZATION.
2025-01-31 10:21 | YES | YES | 19920131 | 1992-09-01 | 15931 | PUBLIC SERVICE CO OF COLORADO | FOSSIL CREEK & SCENIC DR INTERSECTION | FORT COLLINS | LARIMER | CO | 80526 | 3 | NO | 1030 | 1992-08-03 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  |  | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | ASTM D-2513 |  | 0 | 1974 | UNDER PAVEMENT |  | GARY HUETT | 3032257840 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | WHILE EMPLOYEE WAS INSTALLING A CLAMP ON A LEAKING GAS MAIN IT CAUGHT FIRE INJURING THE EMPLOYEE. THE SOURCE OF THE IGNITION IS PENDING INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19920135 | 1992-09-01 | 15931 | PUBLIC SERVICE CO OF COLORADO | 2724 CHAMPA STREET | DENVER | DENVER | CO | 80202 | 3 | NO | 2039 | 1992-08-18 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 20 |  |  | 1.6 | 3.6 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.2 |  |  | 0 | 0 | UNDER PAVEMENT |  | JIM SHOEMAKER | 3032942051 | [6 empty] | Null |  | OPERATOR ACTION |  | YES | 1992-06-16 | YES | 3 | PAINT | YES |  |  | MATT FITZGERALD, A BACKHOE OPERATOR FOR KEHN CONSTR. CO OF 6322 SO. COLLEGE AVE. - FT. COLLINS, DUG INTO AN 1 1/4" PE GAS MAIN & BROKE THE MAIN AT AN 1 1/4 " STEEL TO PE TRANSITION FITTING. ESCAPING GAS FROM THE BROKEN MAIN BLEW DEBRIS FROM THE EXCAVATION INTO MR. FITZGERALD'S EYES. HE WAS HOSPITALIZED.
2025-01-31 10:21 | YES | NO | 19920138 | 1992-09-17 | 22182 | WASHINGTON GAS LIGHT CO | HOOES RD & WALNUT KNOLL LANE | SPRINGFIELD | FAIRFAX | VA | 22152 | 3 | NO | 822 | 1992-08-18 | 0 | 0 | 75000 | 58731.0437 | 141804.1927 | Null | 1 | 13 |  | 19920818 | 20 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 8 | 0.65 | TYPE II GRADE 4 | DUPONT | 1989 | 1991 | UNDER GROUND OR UNDER WATER |  | WM A. HINDE - SAFETY SUPERVISOR | 7037507687 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-08-11 | YES | 1 | PAINT | YES |  |  | CONTRACTOR WILLIAM HAZEL INC. WAS DRILLING FOR A ROADWAY PROJECT, WHEN THEY DRILLED THROUGH A 12" STEEL CASING AND THE INSERTED 8" PLASTIC MAIN. THE MAIN WAS PROPERLY MARKED WITH PAINT AND WOODEN STAKES.
2025-01-31 10:21 | YES | YES | 19920142 | 1992-09-21 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | MAPLE & MILLER | ANN ARBOR | WASHTENAW | MI | 48111 | 3 | NO | 1935 | 1992-08-12 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 0 |  | 19920812 | 100 | 100 | BY TEST | 150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | TEST TUBE VALVE | STEEL |  | 8 | 0 |  |  | 0 | 1953 | OTHER | VAULT | STANLEY D MACDONALD - CODES AND STANDARDS ANALYST | 3132566596 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WORKER OVERCOME BY GAS WHILE ATTEMPTING TO CHANGE A 3/4" TEST TUBE VALVE IN A VAULT ON A 100 PSIG 8" MAIN VALVE.
2025-01-31 10:21 | NO | NO | 19920143 | 1992-09-21 | 11800 | LOUISIANA GAS SERVICE CO | ALLIANCE AND THIRD STREETS | KENNER | JEFFERSON | LA | 70062 | 3 | NO | 300 | 1992-08-26 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19920826 | 70 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L |  | 1949 | 1949 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | POWER LINES FELL DURING HURRICANE FORCE WINDS AND CONTACTED THE GAS SYSTEM AT AN UNKNOWN LOCATION. A HOLE BLEW THROUGH THE MAIN DUE TO HIGH VOLTAGE, THEGAS INGNITED AND 25 HOMES WERE EVACUATED UNTIL THE GAS LEAK COULD BE CONTROLL
2025-01-31 10:21 | YES | YES | 19920144 | 1992-09-14 | 1640 | BOSTON GAS CO | CROSS ST (NORTH SHORE SHOPPING CENTER | PEABODY | ESSEX | MA | 01960 | 3 | NO | 1000 | 1992-08-21 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 15 |  | 19920821 | 55 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | PROCEDURE | POLYETHYLENE PLASTIC |  | 6 | 0.581 | SDR 11.5 | UPONOR ALDYL CO. | 1992 | 1992 | OTHER | IN INSTALLATION TRENCH | ROBERT J CAVICCHI - MANAGER ,DISTRIBUTION ARMINSTRATION | 6173239210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | NATURAL GAS WAS BEING INTRODUCED INTO A NEWLY INSTALLED PLASTIC MAIN. IGNITION WAS CAUSED BY STATIC ELECTRICITY AT THE PERGING POINT, RESULTING IN BURNSTO ONE COMPANY EMPLOYEE AND TWO CONTRACTOR EMPLOYEES.
2025-01-31 10:21 | YES | YES | 19920145 | 1992-09-04 | 7135 | HASTINGS UTILITIES | K ST. AND LEXINGTON AVE | HASTINGS | ADAMS | NE | 68901 | 3 | NO | 930 | 1992-07-21 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19920721 | 24 | 25 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | HUMAN ERROR | STEEL |  | 2 | 0.237 |  |  | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | KEITH LEONHARDT - DIRECTOR OF ENGINEERING | 4024631371 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | THE ACCIDENT OCCURRED WHEN THE CONSTRUCTION CREW WAS REMOVING AN OLD ABANDONED SERVICE TAP FROM THE MAIN IN ACCORDANCE WITH STANDARD GAS DEPARTMENT PROCEDURES AS GIVEN IN OUR OPERATIONS AND MAINTENANCE MANUAL CHAPTER XIII. IN ACCORDANCE WITH GAS DEPARTMENT POLICY, A TAPERED STEEL SHAFT IS INSERTED THROUGH THE TAP INTO THE MAIN TO PLUG THE HOLE IN THE MAIN AND SHUT OFF THE GAS. ONCE THE GAS FLOW IS STOPPED THE TAP IS REMOVED. AT THIS POINT, A SHORTER TAPERED STEEL SHAFT IS INSERTED INTO THE HOLE AND CLAMPED AND WELDED TO THE MAIN.THE SHAFT IS THEN CUT OFF JUST ABOVE THE WELD AND SMOOTHED OFF AND A PATCH IS WELDED ONTO THE MAIN TO COVER UP THE ORIGINAL WELDED AREA. IF PROBLEMS DEVELOP, THEN A SHUTDOWN OF THE MAIN OR SHORT STOPS ARE USED TO SHUT OFF THE FLOW OF GAS WHILE TAPS ARE REMOVED IN ACCORDANCE WITH CHAPTER III OF OUR OPERATION AND MAINTENANCE MANUAL. ON JULY 21, 1992, GARY JEREMIAS (FOREMAN WELDER),JEFF KEELER, JON PETERSEN, TOM VALENTINE (ALL PIPEFITTER APPRENTICE), AND DEAN NELSON (PIPEFITTER-EQUIPMENT OPERATOR) WERE CUTTING THE OLD TAP FOR 1308 SOUTH LEXINGTON OFF THE MAIN. THEY HAD INSTALLED A NEW SERVICE TO THIS LOCATION ON JULY 20, 1992. GARY JEREMIAS AND JEFF KEELER WERE IN THE HOLE TO CUT THE TAP OFF, GARY AND JEFF HAD TRIED SEVERAL TAPERED STEEL SHAFTS TO SHUTOFF THE FLOW OF GAS. GARY CHOSE ONE OF THE STEEL SHAFTS, BUT IT DIDN'T COMPLETELYSHUT OF THE FLOW OF GAS. GARY PROCEEDED TO GRIND OFF THE OLD TAP INSTEAD OFSHUTTING DOWN THE MAIN AS REQUIRED BY CHAPTER III. GARY HAD THE TAP ABOUT 3/4 OF THE WAY OFF WHEN THE GAS WAS IGNITED BY THE GRINDER OR CUTTING WHEEL. THERE WAS THREE FLASHES AS THE GAS RECEIVED ENOUGH OXYGEN TO BURN. GARY JEREMIAS RECEIVED BURNS OVER 65% OF HIS BODY. HE WAS TRANSPORTED TO MARY LANNINGHOSPITAL AND LATER TRANSFERRED TO SAINT ELIZABETH BURN CENTER IN LINCOLN, NEBRASKA.
2025-01-31 10:21 | YES | YES | 19920146 | 1992-10-08 | 15931 | PUBLIC SERVICE CO OF COLORADO | 16000 W ELLSWORTH AVE | LAKEWOOD | JEFFERSON | CO | 80401 | 3 | NO | 1135 | 1992-09-22 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19920922 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.307 | 2306/2406/0-151 | PLEXCO | 1992 | 1992 | UNDER GROUND OR UNDER WATER |  | MICHEAL CATBAGAN - SUPRV. GAS EMERG. SVCS | 3035713924 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | FENCE COMPNAY RUPTURES A 3" PE NATURAL GAS LINE WHICH IGNITED AFTER ANGERINGINTO THE LINE WITH A TRACTOR MOUNTED POST HOLE DIGGER, OPERATOR WAS BURNED AND TRANSPORTED TO HOSPITAL.
2025-01-31 10:21 | YES | YES | 19920153 | 1992-10-26 | 4060 | EAST OHIO GAS CO | 1423 - 1425 COPLEY ROAD | AKRON | SUMMIT | OH | 44320 | 3 | NO | 1944 | 1992-09-23 | 0 | 1 | 300000 | 234924.1748 | 567216.7707 | Null | 1 | 40 |  | 19920924 | 77 | 100 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 1931 | UNDER GROUND OR UNDER WATER |  | PAUL E ALEKSA - ENVIRONMENTAL & CODES ENGINEER | 2167366858 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1979 | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAK FROM CORROSION PIT MIGRATED INTO BUILDING. EXPLOSION AND FIRE WERE IGNITED WHEN OCCUPANT LIT A CIGARETTE.
2025-01-31 10:21 | YES | YES | 19920154 | 1992-10-20 | 22777 | WISCONSIN NATURAL GAS CO | 9185 SO MEYER LANE | OAK CREEK | MILWAUKEE | WI |  | 2 | NO | 1113 | 1992-09-14 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 7 |  | 19920914 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | ASTM D2513 | PHILLIPS DRISCO PIPE | 1991 | 1992 | UNDER GROUND OR UNDER WATER |  | STUART | 4146377681 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-07-27 | YES | 3 | TEMPORARY FLAGS & PAINT M | YES |  |  | AN ELECTRIC UTILITY EMPLOYEE, WHILE REPORTEDLY SPLICING AN ELECTRIC CABLE WITH A PROPANE TORCH, ACCIDENTALLY DAMAGED A NEARBY GAS SERVICE PIPE. THE LOCATION OF THE SERVICE LINE WAS REASONABLY MARKED BEFORE THE ACCIDENT AND THE SERVICE WAS EXPOSED AND VISIBLE AT THE TIME OF THE ACCIDENT.
2025-01-31 10:21 | NO | NO | 19920155 | 1992-10-13 | 22182 | WASHINGTON GAS LIGHT CO | 3400 MASSCHUSETTS AVE NW | WASHINGTON | DISTRICT OF COLUMBIA | DC | 20008 | 4 | YES | 847 | 1992-09-17 | 0 | 0 | 3000 | 2349.2417 | 5672.1677 | YES | 0 | 33 |  | 19920917 | 20 | 22 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | NON SPECIFIED | 2 | 0.225 | ASTM-D-2513 | DUPONT | 1986 | 1986 | UNDER PAVEMENT |  | WM. A. HINDE - SAFETY SUPERVISOR | 7037504583 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | NON SPECIFIED | BYERS ENGINEERING WORKING AS A CONTRACT LOCATOR FOR WASHINGTON GAS LIGHT COMPANY FAILED TO ADEQUATELY MARK A 2" PLASTIC GAS SERVICE IN THE AREA OF CONSTRUCTION. CONTRACTOR BADGER DRILLING INC. DRILLED THROUGH A 2" PLASTIC GAS SERVICE. IN THE INTEREST OF PUBLIC SAFETY, 180 PEOPLE WERE EVACUATED BY WASHINGTON GAS AND THE DISTRICT OF COLUMBIA FIRE DEPARTMENT FROM FOUR BUILDINGS IN THE COMPLEX. ALL REPAIRS WERE COMPLETED AND PEOPLE WERE ABLE TO RETURN TO THEBUILDINGS WITHIN THE SAME DAY.
2025-01-31 10:21 | YES | YES | 19920158 | 1992-10-08 | 12903 | TWO HARBORS CITY MUNICIPAL GAS DEPT | 1615 - 7TH AVE | TWO HARBORS | LAKE | MN | 55616 | 0 | NO | 1100 | 1992-09-10 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 25 |  | 19920910 | 50 | 56 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0 | P E 2406 | PLEXCO | 0 | 1989 | UNDER GROUND OR UNDER WATER |  | DONALD S NORLEN - SUPT. GAS, WATER & SEWER | 2188345631 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-09-10 | YES | 3 | YELLOW PAINT | YES |  |  | ON THE MORNING OF SEPTEMBER 10, 1992 OUR ELECTRIC DEPARTMENT ASKED US TO MARK GAS SERVIDE FOR THE RELOCATION OF A POLE. WE MARKED THE GAS LINE OUT TO THE MAIN AND LEFT. AT ABOUT 11:00 A.M. THEY HIT THE SERVICE AND IMMEDIATELY CALLED OUR SERVICEMAN ON THE RADIO. UPON ARRIVING ON THE SCENE, BOB CAVALLIN TRIED TO SQUEEZE OFF SERVICE AND WAS OVERCOME BY GAS. THE OTHER GAS SERVICEMAN AND ELECTRICIAN PULLED HIM AWAY FROM THE HOLE AND ADMINISTERED CPR. HE CAME TO IMMEDIATELY AND WAS TAKEN TO THE HOSPITAL WHERE TESTS WERE TAKEN AND WAS RELEASED AT 5:00 P.M., SEPTEMBER 10, 1992. THE SERVICE LINE COMING TOWARDS THE ALLEY AND AREA WHERE THE HOLE WAS TO BE DRILLED TOOK A SHARP LEFT AND THEN INTO THE MAIN. OUR LOCATOR DID NOT DETECT THE TURNING OF PIPE. WE COULD HAVE BEEN PICKING UP SIGNALS FROM TRACER WIRE ON THE MAIN.
2025-01-31 10:21 | YES | YES | 19920160 | 1992-10-19 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1430 OCEAN MEADOWS PLACE | MONTECITO | SANTA BARBARA | CA |  | 3 | NO | 1300 | 1992-09-24 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 15 |  | 19920924 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM 2513 | DUPONT | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | G J LAMBERT - MANAGER OF SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-09-23 | YES | 3 | PAINT | YES |  |  | TWO EMPLOYEES OF TIERRA CONSTRUCTION WERE USING A PROPANE BURNER TORCH WHILEINSTALLING TELEPHONE CONDUIT IN THE SAME EXCAVATION WIHT EXPOSED 2" AND 1/2"PLASTIC GAS LINES. ONE EMPLOYEE WAS LIFTING THE PLASTIC GAS LINE WHILE THE OTHE WAS APPARENTLY APPLYING HEAT TO THE CONDUIT. THE HEAT FROM THE TORCH CAUSED THE PLASTIC LINE TO FAIL AND THE BURNER FLAME IGNITED THE ESCAPING GAS.ONE EMPLOYEE RECEIVED MINOR BURNS AND REMAINED ON THE JOB SITE. THE OTHER WAS TRANSPORTED TO THE HOSPITAL.
2025-01-31 10:21 | NO | NO | 19920167 | 1992-11-06 | 11720 | LONG ISLAND LIGHTING COMPANY | 263 WEST MAIN ST | ISLIP | SUFFOLK | NY | 11751 | 4 | NO | 1733 | 1992-10-03 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 7 |  | 19921003 | 0.22 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | OTHER | CONSUMER HOUSELINE | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1938 | WITHIN/UNDER BUILDING |  | THOMAS E LUPSKI - CODE AND SPECIFICATION ENGINEER | 5169334400 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | BUILDING COLLAPSED | NO |  | NO | 0 |  | NO |  |  | THE STRUCTURE AT 263 WEST MAIN STREET WAS AN APARTMENT BUILDING THAT WAS UNDERGOING RENOVATIONS ON OCTOBER 3, 1992. A FIRE STARTED IN THE REAR OF THE BUILDING AND CAUSED A COLLAPSE OF THE STRUCTURE WHICH BROKE A LOW PRESSURE GAS SERVICE HOUSELINE. THE THREE (3) INCH SERVICE THAT SUPPLIED GAS TO THE BUILDING WAS RETIRED IN ORDER TO SUCCESSFULLY PERFORM "MAKE SAFE" OPERATIONS. THERETIREMENT OF THE SERVICE STOPPED THE FLOW OF GAS ESCAPING FROM THE 3/4 INCHCONSUMER OWNED HOUSELINE AT THE METER SET ASSEMBLY. THE GAS DID NOT INGNITE OR CONTRIBUTE TO THE FIRE. THE OPERATOR NOTIFIED THE DOT BASED UPON PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF THE INCIDENT. SUBSEQUENT INVESTIGATION DETERMINED THAT THE OPERATOR'S GAS FACILITIES WERE NOT INVOLVED IN THE INCIDENT.
2025-01-31 10:21 | NO | NO | 19920169 | 1992-11-02 | 18532 | SOUTHERN UNION GAS CO | 5803 BELMOOR | AUSTIN | TRAVIS | TX | 78723 | 3 | NO | 1211 | 1992-10-26 | 0 | 0 | 35000 | 27407.8204 | 66175.2899 | Null | 2 | 8 |  | 19921026 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | STRAINER | CAST IRON |  | 2 | 0 |  |  | 0 | 1969 | ABOVE GROUND |  | ROBERT FRANSON | 5124651101 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE STRUCK BUILDING AND METER SET. THE IMPACT CRACKED THE STRAINER WHICHPRODUCER HAD ABANDONED PRODUCTION FROM HIGH ISLAND 206 AND MADE NEW CONNECTIO IGNITED.N TO SAME TRANSCO UWTV ASSEMBLY FROM HIGH ISLAND 207. PRODUCER HAD COMPLETED DISASSEMBLING THE HIGH ISLAND 206 PLATFORM AND ON OCTOBER 20, 1992 WAS USING A SHRIMP BOAT TO PERFORM MMS REQUIRED BOTTOM GRID SEARCH FOR DEBRIS. WHILEPERFORMING THE GRID SEARCH,THE SHRIMP BOAT'S NET AND CHAIN SNAGGED THE PRODUCER'S VAVLE AND PIPELINE, PULLING IT OVER AND SEVERING TRANSCO'S UWTV ASSEMBLY AT THE WELD FOR 1 110 DEGREE ELL. DUE TO WEATHER AND SEA CONDITIONS, EQUIPMENT AND DIVERS WERE UNABLE TO ACCESS THE DAMAGE UNTIL EARLY ON OCTOBER 23, 1992.
2025-01-31 10:21 | NO | NO | 19920171 | 1992-11-16 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) |  | HOT SPRINGS | GARLAND | AR | 71901 | 3 | NO | 927 | 1992-11-02 | 0 | 0 | 25000 | 19577.0146 | 47268.0642 | YES | 1 | 53 |  | 19921102 | 23 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 |  |  | 1950 | 1950 | UNDER PAVEMENT |  | JIM BREWER - CODES & PROCEDURES | 5013774771 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | THE ONE INCH SERVICE LINE HAD A STRESS FRACTURE UNDER THE STREET. THE SERVICE LINE APPEARED TO HAVE BEEN BENT UPWARD TO ACCOMODATE THE PASSAGE OF A SEWER LINE BENEATH THE SERVICE. THE SEWER LINE HAD BEEN INSTALLED AS LONG AS FIFTEEN YEARS BEFORE THE INCIDENT. NATURAL GAS APPEARED TO HAVE MIGRATED TO THERESIDENCE FOLLOWING THE SEWER LINE DITCH, RESULTING IN A LOW ORDER EXPLOSIONUNDER THE RESIDENCE.
2025-01-31 10:21 | YES | YES | 19920172 | 1992-10-26 | 180 | ALABAMA GAS CORP | 1928 CLOVER DR | BIRMINGHAM | JEFFERSON | AL | 35117 | 3 | NO | 1525 | 1992-09-29 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19920930 | 10 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406/D2513 | PLEXCO | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | STEVE CHAPMAN MANAGER - CONSTRUCTION SERVICES | 2053268309 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON TUESDAY, SEPTEMBER 29, 1992, LANGFORD PATTON, LABORER - BENTON/MARKS, INCWAS INSTALLING A 3/4" SERVICE LINE TO 1928 CLOVER DRIVE FOR ALABAMA GAS CORPORATION. AFTER HE PRESSURE TESTED THE NEW SERVICE LINE, PATTON TAPPED THE TOW INCH PLASTIC MAIN USING A 2" X 3/4" CONTINENTAL ELIMINATOR SERVIE SADDLE. WHILE SOAL TESTING THE FITTING, PATTON DISCOVERED A SMALL LEAK ON THE LEFT REAR CORNER. HE ATTEMPTED TO TIGHTEN THE BOLTS BUT WAS UNABLE TO STOP THE LEAK. PATTON PLACED ANOTHER 2" X 3/4" SADDLE ON THE MAIN TO REPLACE THELEAKING ONE. HE STATED HE PLACED APPROXIMATELY SIX WET PAPER TOWELS ON THE MAIN TO ELIMINATE STATIC ELECTRICITY. PATTON LOOSENED THE BOLTS ON THE TAPPE SADDLE TO SLIDE THE OTHER IN PLACE. WHEN HE TOUCHED THE MAIN, PATTON STATED HE FELT A SMALL ELECTRICAL CHARGE TO HIS RIGHT SMALL FINGER. PATTON BEGAN TO TURN THE PUNCH DOWN ON THE LEAKING SADDLE TO STOP FLOW OF GAS WHEN THE LEAK IGNITED SCOTCHING HIS NOSE. HE CONTINUED TO TURN THE PUNCH WHEN THE FLAME BECAME TOO HIGH AND HE ROLLED OUT OF THE EXCAVATION. PATTON NOTIFIED HIS OFFICE OF THE FIRE APPROXIMATELY 3:25PM. PAUL MARKS, OWNER - BENTON/ MARKS, INC. THEN O NOTIFIED THE BIRMINGHAM FIRE DEPARTMENT AND ALABAMA GAS. COMPANY CREWS ARRIVED ON THE SCENE AT 3:37 PM. AT 4:19 PM THE PLASTIC MAIN WAS SQUEEZED OFF AT BOTH ENDS AND THE FIRE EXTINGUISHED. PERMANENT REPAIRS WERE COMPLETED AT 6:30 PM. PATTON RECEIVED FIRST DEGREE BURNS TO HIS FACE AND LEFT ARM AND SCOND DEGREE BURNS TO HIS RIGHT ARM. HE WAS ADMITTED TO UNIVERSITY HOSPITAL OVERNIGHT FOR OBSERVATION. HE WAS RELEASED ON SEPTEMBER 30 1992.
2025-01-31 10:21 | YES | YES | 19920178 | 1992-12-03 | 14320 | ONEONTA GAS DEPT | HERITAGE ROAD | ONEONTA | BLOUNT | AL | 35121 | 1 | NO | 1430 | 1992-11-25 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19921125 | 15 | 24 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.395 | PE2306 | PLEXCO | 1989 | 1989 | UNDER PAVEMENT |  | W FRANK LANGNER - GENERAL MANAGER | 2052742159 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | THE ACCIDENT OCCURRED ABOUT 2:30 P.M. AT THE HERITAGE GREEN SUB-DIVISION LOCATED IN ONEONTA, ALABAMA. (BLOUNT COUNTY) WE RECEIVED A CALL FROM THE OFFICE OF THE DEVELOPER STATING THAT ONE OF THEIR MEN HAD CUT OUR GAS LINE AND THAT IT WAS ON FIRE. THE CALL WAS RECEIVED AT 2:35 P.M. AND THE GAS WAS CUT OFF AT 2:45 P.M. THE WORKER WAS USING A TRENCHER TO CUT A DITCH ACROSS THE ROAD TO INSTALL A SEWER LINE. THE TRENCHER CUT THE TOP OF A 4" PLASTIC MAIN WITH 15 PSIG AND THE GAS WAS IGNITED. THE OPERATOR RECEIVED 2ND DEGREE BURNS AROUNDHIS FACE AND ARMS. THE OPERATOR WAS KEPT OVERNIGHT IN THE HOSPITAL FOR OBSERVATION. NO REQUESTS WERE MADE BY THE OPERATOR OR DEVELOPER TO SPOT GAS LINES IN THE AREA OF THE WORK. THREE CUSTOMERS WERE WITHOUT GAS SERVICE FOR ABOUT TWO AND A HALF HOURS.
2025-01-31 10:21 | YES | YES | 19920183 | 1992-12-07 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 1903 NW LINCOLN | LAWTON | COMANCHE | OK | 73507 | 3 | NO | 600 | 1992-11-11 | 0 | 2 | 20000 | 15661.6117 | 37814.4514 | YES | 6 | 0 |  | 19921111 | 11 | 13 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE | YARD LINE & HOUSE APPLIAN | OTHER | UNKNOWN | STEEL |  | 1.25 | 0.156 |  |  | 0 | 1956 | WITHIN/UNDER BUILDING |  | GEORGE R ELLIS - DIVISION STAFF MANAGER | 4054826315 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LEAK FOUND ON FURNACE CONNECTION AND COOK STOVE INSIDE DWELLING AND ON YARD LINE UNDER HOUSE SLAB. WOULD NOT HOLD PRESSURE TEST. CAUSE OF YARD LINE LEAK IS NOT KNOWN.
2025-01-31 10:21 | YES | YES | 19920184 | 1992-12-07 | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | LIBERTY STREET | CATSKILL | GREENE | NY | 12414 | 3 | NO | 1952 | 1992-11-06 | 1 | 1 | 0 | 0 | 0 | Null | 0 | 50 |  | 19921107 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.372 |  |  | 0 | 1930 | UNDER PAVEMENT |  | TIMOTHY D. HAYES - GAS OPERATIONS COORDINATOR | 9144865521 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | YES | 1992-09-28 | YES | 0 | PAINTED MARKS | NO |  |  | ON NOVEMBER 6, 1992 AT 7:52 PM AN EXPLOSION OCCURRED IN A TWO STORY WOOD FRAME RESIDENCE AT 26 LIBERTY STREET IN THE VILLAGE OF CATSKILL, NY. TWO PEOPLEWERE IN THE RESIDENCE AT THE TIME OF THE EXPLOSION. THE OWNER, AN 87 YEAR OLD FEMALE, DIED AND HER DAUGHTER SUSTAINED INJURIES THAT REQUIRED HOSPITALIZATION. BECAUSE NATURAL GAS WAS POTENTIALLY INVOLVED, THE OFFICE OF PIPELINE SAFETY, DEPARTMENT OF TRANSPORTION WAS TELEPHONICALLY NOTIFIED OF THE INCIDENT.SUPPLEMENTAL INFO: THE STAFF OF ENERGY & WATER DIVISION WROTE A MEMO" ...THE SOURCE OF THE GAS THAT CAUSED THE EXPLOSION WAS A CRACKED 4-INCH CASTIRON GAS MAIN LOCATED IN THE STREET APPROXIMATELY 55 FEET FROM THE BUILDING. THE GAS MIGRATED INTO THE BUILDING THROUGH A STRIP OF SANDY SOIL CONTAININGSEVERAL DRAINAGE CONDUCTS AND WAS IGNITED BY AN UNKNOWN SOURCE." CENTRALHUDSON IS IN THE PROCESS OF ANALYZING THE RELEVANT FACTS. ATTHIS TIME, CENTRALHUDSON BELIEVES THAT THE CAUSE OF THE EXPLOSION IS UNDETERMINED. IT ISUNDISPUTED THAT THERE WAS A CRACK IN THE 4-INCH CAST IRON GAS MAIN ON NOVEMBER 6, 1992, AND THAT GAS WAS ESCAPING FROM THE MAIN. IT IS UNDETERMINED WHEN THE CRACK OCCURRED OR HOW MUCH GAS WAS ESCAPING. THE STRIP OF "SANDY" SOIL REFERRED TO BY STAFF IS NOT SUPPORTED BY THE SOILS TESTING PERFORMED BY BLASLAND & BOUCK ENGINEER. ALL OF THE SOILS TESTED TO THE EAST OF THE CRACKEDMAIN IN THE AREA BETWEEN 30 AND 26 LIBERTY ST. HAVE HIGH VOID CONTENTS AND WOULD HAVE ALLOWED UPWARD MIGRATION OF NATURAL GAS AS OPPOSED TO THE UNNATURAL55-FOOT HORIZONTAL MIGRATION, WHICH IS ASSUMED BY THE STAFF. CENTRAL HUDSONIS STUDYING, AMONG OTHER THINGS, WHETHER THERE WAS SUFFICIENT GAS IN THE AREATO HAVE CAUSED THE EXPLOSION. THE MAIN WAS BEING OPERATED AT THE LOW PRESSURE OF APPROX. 1/4 PSI. MOREOVER, THE BAR HOLE READING NEAR 26 LIBERTY STREET APPEAR TO INDICATE QUANTITIES OF GAS THAT, WHEN DILUTED WITH BASEMENT AIR, WOULD HAVE BEEN INSUFFICIENT TO HAVE CAUSED AN EXPLOSION IN THE BASEMENT, PARTICULARLY IN LIGHT OF THE HIGH VOID CONTENT OF THE SOIL AND THE MUCH LARGER VOLUME OF AIR WITHIN THE BASEMENT AS COMPARED TO THE SOIL.
2025-01-31 10:21 | YES | YES | 19920185 | 1992-11-25 | 11680 | LONE STAR GAS CO | 5107 LESTER | ARLINGTON | TARRANT | TX |  | 3 | NO | 635 | 1992-10-24 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 50 |  | 19921024 | 30 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0 | SDR 11.5 | NIPAK | 1970 | 1970 | UNDER GROUND OR UNDER WATER |  | PHILLIP MURDOCK - DIRECTOR | 2146702229 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PERSON DROPPED CIGARETTE ON DYING GRASS. GRASS IGNITED CAUSING LEAKING NATURAL GAS TO IGNITE.
2025-01-31 10:21 | YES | YES | 19920186 | 1992-11-25 | 6930 | GULFSIDE GAS CO | INTERSEC. OF PEARSALL & KEARNEY ROADS |  | BEXAR | TX | 78002 | 3 | NO | 1335 | 1992-10-16 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19921016 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | OTHER PLASTIC | PVC | 2 | 0 |  |  | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | SIMON R PENA JR. | 2104293539 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 | PERMANENT, PIPELIN WAS EX | NO |  |  | SOUTHWESTERN BELL TELEPHONE EMPLOYEE WAS WORKING A "SPLICE PIT" MAKING A "SPLICE CLOSURE" WITH A "MID GAS FLAME TORCH" WHEN NATURAL GAS IGNITED FROM A 2"PVE GAS DISTRIBUTION LINE APPROXIMATELY 3"-12" BELOW THE WORK BEING PERFORMED BY THE SOUTHWESTERN BELL TELEPHONE EMPLOYEE.
2025-01-31 10:21 | NO | NO | 19920187 | 1992-12-08 | 2204 | CENTRAL ILLINOIS PUBLIC SERVICE | 90'S OF LINCOLN TRAIL RD W ROOSEVELT RD | TAYLORVILLE | CHRISTIAN | IL | 62568 | 3 | NO | 1737 | 1992-11-13 | 0 | 0 | 30000 | 23492.4175 | 56721.6771 | Null | 1 | 53 |  |  | 325 | 325 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | VALVE | ALSO FITTING/WELD FILLET | STEEL | CAST IRON | 0 | 0 |  |  | 0 | 1963 | ABOVE GROUND |  | MATTHEW D PATTON - GAS ENGINEER | 2175255326 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GROUND REGULATOR ST | NO |  |  | STATION FAILED AT 4 PLACES: 2 SCREW FITTINGS, A WELD, AND AT A CAST IRON VALVE. CHEVROLET BLAZER STRUCK REGULATOR STATION AFTER MAKING A TURN AND SLIDING ON GRAVEL.
2025-01-31 10:21 | NO | NO | 19920188 | 1992-12-14 | 2309 | CHESAPEAKE UTILITY CORP | 208 EAGLES NEST DR | DOVER | KENT | DE | 19901 | 4 | NO | 1130 | 1992-12-09 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 25 |  | 19921209 | 25 | 42 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTM D-2513 | PLEXCO | 1990 | 1990 | UNDER GROUND OR UNDER WATER |  | EDWARD C DUNLAP - SENOIR DIVISION ENGINEER | 3027346787 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-11-24 | YES | 0 |  | YES |  |  | ON TUESDAY, DECEMBER 9, 1992, AT APPROXIMATELY 11:30 A.M., A GAS IGNITION OCCURRED AT 208 EAGLES NEST DRIVE, DOVER, DELAWARE WHEN A GASOLINE MOTOR-DRIVENFENCE POST HOLE AUGER STRUCK AND BROKE A 3/4" PLASTIC GAS SERVICE. A SERVICEMAN AND STREET CREW WERE IMMEDIATELY DISPATCHED. THE SERVICE ARRIVED AT 11:35 A.M. AND THE STREET CREW ARRIVED SHORTLY THEREAFTER. THE DOVER FIRE DEPARTMENT WERE ALSO ON THE SCENE, AND GAS WAS SHUT OFF AT 11:55 A.M. THERE WERENO EVACUATIONS. REPAIRS BEGAN IMMEDIATELY AND WERE COMPLETED BY 1:00 P.M. THE AUGER WAS OPERATED BY KEN KIENBERGER AND MARK MELVIN OF LIGHTNING FENCE COMPANY. KIENBERGER RECEIVED MINOR FLASH BURNS ON THE FACE. MELVIN WAS EXAMINED AND RELEASED FROM KENT GENERAL HOSPITAL, DOVER, DELAWARE. ON NOVEMBER 24,1992, CHESAPEAKE UTILITIES RECEIVED A NOTICE OF INTENT TO EXCAVATE AT 208 EAGLES NEST DRIVE. THIS SERVICE ENCROACHED UPON 208 EAGLES NEST DRIVE NEAR THEPROPERTY LINE OF 204 EAGLES NEST DRIVE AND WAS THEREFORE, NOT LOCATED. THE DELAWARE PUBLIC SERVICE COMMISSION WAS NOTIFIED AT 1:45 P.M. PETTY OFFICER BESHOAR OF THE DEPARTMENT OF TRANSPORTATION RESPONSE CENTER WAS NOTIFIED AT 1:50 P.M.
2025-01-31 10:21 | YES | NO | 19920189 | 1992-12-08 | 11032 | LACLEDE GAS CO | 1118 SURREY HILLS DR | RICHMOND HEIGHTS | ST LOUIS | MO | 63117 | 3 | NO | 1142 | 1992-11-14 | 0 | 0 | 225000 | 176193.1311 | 425412.5781 | Null | 0 | 33 |  | 19921114 | 38 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0 | 0.4 | .5" I.D. | DONLEY PIPE | 1962 | 1964 | WITHIN/UNDER BUILDING |  | PAUL B HUNKER, JR. - ASSOCIATE GENERAL COUNSEL | 3143429528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THERE WAS A COMPLETE CIRCUMFERENCE BREAK OF A 1/2 INCH COPPER SERVICE THAT HAD BEEN INSERTED INTO 3/4 INCH STEEL. THE BREAK WAS FOUND APPROXIMATELY 8 TO9 INCHES WITHIN THE FOUNDATION WALL.
2025-01-31 10:21 | NO | NO | 19920190 | 1992-12-08 | 8270 | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO | 401 S.E. LINCOLN | BONDURANT | POLK | IA |  | 4 | NO | 1245 | 1992-11-02 | 0 | 0 | 55000 | 43069.4321 | 103989.7413 | Null | 0 | 0 |  | 19921102 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT DETERMINED | OTHER | NON REPORTED | OTHER | NON REPORTED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SANDRA RASMUSSEN - GAS STANDARDS ENGINEER | 7122777928 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ONE RESIDENCE EXPLODED. THE CAUSE OF THE EXPLOSION IS STILL UNDER INVESTIGAT
2025-01-31 10:21 | YES | NO | 19920191 | 1992-12-08 | 17540 | ROANOKE GAS CO | 2926 & 2928 TREE SWALLOW RD., SW |  | ROANOKE | VA | 24018 | 3 | NO | 1121 | 1992-11-12 | 0 | 0 | 250000 | 195770.1457 | 472680.6423 | Null | 0 | 32 |  | 19921112 | 43.3 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CAST ALUMINUM | 0 | 0 | AL-250TC/AL-175 | AMERICAN METER/AMERICAN METER | 1988 | 1989 | ABOVE GROUND |  | RICK PEVARSKI - SUPT OPERATIONS CENTER & APPL. SER | 7039833814 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | APPARENT CAUSE: EXCESSIVE HEAT FROM A FIRE. THE FIRE MARSHALL SUSPECTS ANDIS INVESTIGATING ARSON.11:21AM CENTRAL DISPATCH CENTER RECEIVED CALL FROM ROANOKE COUNTY FIRE DEPARTMENT REPORTING A STRUCTURE FIRE AT 2926 TREE SWALLOW ROAD, SW. 11:23 A.M.: DISPATCHED CALL TO A SERVICE TECHNICIAN. 11:28 A.M.SERVICE TECHNICIAN ARRIVED ON SCENE AND FOUND BACK OF STRUCTURE AT 2926 AND 2928 ON FIRE. THE GAS METERS WERE ALSO BURNING. ENGINEERING ADVISED TECHNICIAN TO TURN VALVE OFF AT THE CORNER OF CHAPARRAL DRIVE AND TREE SWALLOW ROAD. 11:53 A.M. GAS OFF AT MAIN VALVE. MET WITH FIRE MARSHAL, R. FERGUSON AND VIRGINIA STATE CORPORATION INSPECTOR, JIM HOTINGER AT THE FIRE SCENE. ALL AFFECTED GAS PIPELINE FACILITIES WERE PRESSURE TESTED AT 91 PSIG FOR ONE HOUR AND FOUR MINUTES WITHOUT LOSS OF PRESSURE. MR. HOTLINGER AND MR. FERGUSON STATED THEY WERE BOTH SATISFIED THAT THERE WERE NO LEAKS ON THE SERVICE AND THAT THE FIRE WAS NOT GAS RELATED. THE FIRE MARSHALL SUSPECTED ARSON.
2025-01-31 10:21 | YES | NO | 19920193 | 1992-12-15 | 24015 | YANKEE GAS SERVICES CO | 26 DRIGGS ST | WATERBURY | NEW HAVEN | CT | 06714 | 2 | NO | 131 | 1992-11-18 | 0 | 0 | 150000 | 117462.0874 | 283608.3854 | Null | 0 | 45 |  | 19921120 | 0.25 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NON SPECIFIED | STEEL |  | 0.5 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LAURENCE W. MALONE | 2036394152 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INVESTIGATORS FROM THE WATERBURY FIRE MARSHALL'S OFFICE DETERMINED THAT GAS ESCAPING FROM AN OPEN METER COCK WAS IGNITED BY AB UNDETERMINED SOURCE, CAUSING AN EXPLOSION AND FIRE. THE METER HAD BEEN REMOVED IN NOVEMBER 1990. THEY CONCLUDED THAT THE OPEN METER COCK HAD REMOVAL OF THE 1/2" PLUG FROM THE INLET SIDE OF THE METER RESULTED FROM TAMPERING.
2025-01-31 10:21 | YES | YES | 19920194 | 1992-12-15 | 21290 | VILLE PLATTE GAS SYSTEM, TOWN OF | 167 SOUTH & LOLA ST | VILLE PLATTE |  | LA | 70586 | 3 | NO | 957 | 1992-11-18 | 0 | 2 | 3200 | 2505.8579 | 6050.3122 | Null | 10 | 27 |  | 19921118 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 2.38 | 0 | ASTMP2513 | PLEXCO | 1984 | 1984 | OTHER | NON SPECIFIED | CHARLES FONTENOT - GAS SUPT | 3183634505 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WAS WORKING TO RELOCATE A 2" GAS LINE & WHEN THEY SQUEEZE IT OFF & STARTED TO CUT THE 2" LINE, SOMETHING IGNITED THE GAS COMING OUT OF THE 2" PIPE AND MELTED THE 4" LINE A FEW MINUTES LATER WE WENT AND CUT THE 4" VALVE. THE LINE WAS REPAIRED AND TURN BACK ON.
2025-01-31 10:21 | YES | NO | 19920198 | 1992-12-22 | 2200 | CENTRAL ILLINOIS LIGHT CO | 1117 EAST JACKSON STR | SPRINGFIELD | SANGAMON | IL | 62701 | 3 | NO | 1600 | 1992-12-04 | 0 | 0 | 80000 | 62646.4466 | 151257.8055 | YES | 0 | 15 |  | 19921204 | 5 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | REGULATOR STATION | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 1 | 0.099 | D2513 | NI-PACK | 1984 | 1985 | UNDER GROUND OR UNDER WATER |  | E H SIMANEK - SR. CODE COMPLIANCE ADM. | 3096934871 | [6 empty] | Null |  | OPERATOR ACTION |  | YES | 1992-11-30 | YES | 3 | PAINTED YELLOW | YES |  |  | 4" CAST IRON LINE WAS LOCATED, CONTROL LINE APPROXIMATELY 1" ABOVE AND PARELLEL TO 4" CAST IRON MAIN. ----- CONTRACTOR HIT A REGULATOR STATION PLASTIC BURIED CONTROL LINE WHICH THEN CAUSED THE LOW PRESSURE SYSTEM TO BECOME OVERPRESSURED.
2025-01-31 10:21 | YES | YES | 19920200 | 1992-12-23 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 749 MONTGOMERY ST | MEMPHIS | SHELBY | TN | 38107 | 3 | NO | 1400 | 1992-12-04 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19921204 | 90 | 99 | BY TEST | 150 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D-2513 | PHILLIPS DRISCOPIPE | 1984 | 1985 | UNDER PAVEMENT |  | WADE STINSON - MANAGER, HICKORY HILL SERVICE CENTER | 9013673300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE OPERATOR'S CREW ACCIDENTLY STRUCK AND RUPTURED A 2" PE GAS MAIN WHILE EXCAVATING WITH A BACKHOE TO ABANDON THE GAS SERVICE TO 749 MONTGOMERY ST. THE FORCE OF THE ESCAPING NATURAL GAS BURLED SPOIL FROM THE EXCAVATION (DIRT, ROCKS, BROKEN PAVEMENT, ETC.) INTO A PASSING AUTOMOBILE, BREAKING OUT THE FRONT PASSENGER SIDE WINDOW. ONE OF THE PASSENGERS IN THE VEHICLE, WHO HAPPENED TO BE 7 MONTHS PREGNANT, CLAIMED HER SIDE WAS HURTING AS A RESULT OF THE INCIDENT AND WAS HOSPITALIZED.
2025-01-31 10:21 | YES | YES | 19920204 | 1993-01-12 | 11680 | LONE STAR GAS CO | MILLER & MARTIN | FORT WORTH | TARRANT | TX |  | 4 | NO | 513 | 1992-12-09 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19921208 | 42 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 4 | 395 |  |  | 0 | 0 | OTHER |  | PHILLIP MURDOCK - DIRECTOR | 2146702229 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | CREW MEMBER FAILED TO PROPERLY INSTALL COMPLETION PLUG IN 4" SHORT STOP TEE. HE REMOVED COMPLETION TOOL AND OPENED SHORT CUT VALVE COMPLETION BLEW OUT. SHORT CUT VALVE WAS CLOSED STOPPING FLOW OF GAS.
2025-01-31 10:21 | NO | NO | 19920207 | 1993-01-04 | 30516 | WEST VIRGINIA POWER GAS SERVICE | ROUTE 6, NEWARK ROAD | NEWARK | WIRT | WV | 26143 | 3 | NO | 1200 | 1992-12-25 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 50 |  | 19921225 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER | FITTING | STEEL |  | 1 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JERRY L STONE - DIR GOV'T COMPLIANCE | 3046477049 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A VEHICLE TRAVELING ON STATE ROUTE 6, LOST CONTROL DUE TO SNOW AND ICY CONDITIONS, STRIKING NATURAL GAS METER ASSEMBLY. THE FORCE OF THE VEHICLE CAUSED NATURAL GAS LEAKAGE TO IGNITE. THE DRIVER OF THE VEHICLE RECEIVED BURNS ON THE FACE, LEG AND FOOT AREAS. INJURIES DIDN'T REQUIRE HOSPITALIZATION. THE, DRIVER, DOROTHY SPRINGER, WAS THE ONLY OCCUPANT IN THE VEHICLE. METER ASSEMBLY WASLOCATEDON WV DEPARTMENT OF HIGHWAYS RIGHT OF WAY, APPROXIMATELY FIVE FEET FROM EDGE OF PAVEMENT.
2025-01-31 10:21 | YES | NO | 19930001 | 1993-01-21 | 11032 | LACLEDE GAS CO | 7930 HILDESHEIM | ST LOUIS |  | MO | 63123 | 3 | NO | 927 | 1992-12-24 | 0 | 0 | 200000 | 156616.1166 | 378144.5138 | Null | 0 | 38 |  | 19921224 | 40.5 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | VALVE |  | OTHER | BRASS | 0 | 0 | AGA X50664 | MUELLER | 0 | 1957 | WITHIN/UNDER BUILDING |  | PAUL B HUNKER - JR/ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LACLEDE GAS COMPANY SERVICEMAN WAS ATTEMPTING TO TURN OFF SHUT OFF VALVE AT INSIDE BASEMENT WALL TO REPAIR MINOR GAS LEAKS ON COMPANY PIPING WHEN SHUT OFF VAVLE FAILED RESULTING IN INTERMEDIATE PRESSURE GAS BEING RELEASED INSIDE STRUCTURE. SERVICEMAN THEN EVACUATED BUILDING, CALLED THE COMPANY FOR HELP, AND WAS ATTEMPTING TO SHUT GAS OFF AT OUTSIDE CURB VALVE WHEN EXPLOSION AND FIRE OCCURRED. THE THREE-FAMILY TWO STORY RESIDENCE AT 7930 HILDESHEIM WAS TOTALLY DESTROYED AND THE SINGLE-FAMILY ONE STORY RESIDENCE AT 2928 HILSDESHEIM WAS EXTENSIVELY DAMAGED. COMPANY SERVICE RECEIVED MINOR INJURIES.
2025-01-31 10:21 | YES | YES | 19930004 | 1993-01-25 | 2364 | CINCINNATI GAS & ELECTRIC CO | 307 UNION STREET | NEW RICHMOND | CLERMONT | OH | 45157 | 3 | NO | 1010 | 1992-12-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19921223 | 55 | 66 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0 | 0 | ASTM D 2513 | DUPONT | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | WILLIAM HOBLITZELL - GAS ENGINEERING SPECIALIST | 5132873921 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE USE OF AN OPEN FLAME IN AN UNDERGROUND PIT BY THE WATER METER READER. FAILURE OF A PLASTIC SERVICE TEE ALLOWED GAS TO SEEP INTO WATER METER PIT. NOFURTHER ACTION REQUIRED.
2025-01-31 10:21 | YES | YES | 19930005 | 1993-01-25 | 8070 | INDIANA GAS CO INC | 978 BULL RUN DRIVE | GREENWOOD | JOHNSON | IN | 46143 | 3 | NO | 1500 | 1992-12-23 | 0 | 2 | 5000 | 3915.4029 | 9453.6128 | Null | 1 | 5 |  | 19921223 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 2 | 0.216 | D2513 | UPONOR | 1988 | 1989 | UNDER GROUND OR UNDER WATER |  | RONALD J BOES - MANAGER OF GAS SYSTEMS STANDARDS & PROCEDURE | 3173210575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 2 | PAINT, FLAGS | YES |  |  | OPERATORS EMPLOYEES WERE ATTEMPTING TO INSTALL A BY-PASS AROUND DAMAGED MAINWHEN IGNITION OCCURRED.
2025-01-31 10:21 | YES | NO | 19930006 | 1993-01-27 | 22182 | WASHINGTON GAS LIGHT CO | SUDLEY MANOR DR @ WEDGEWOOD DR | MANASSAS | MANASSAS | VA | 22110 | 3 | NO | 1344 | 1993-01-02 | 0 | 0 | 100000 | 76510.7496 | 184732.7135 | Null | 1 | 59 |  | 19930102 | 20 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 4 | 0.39 | SDR 11.5 | DUPONT | 1969 | 1971 | UNDER GROUND OR UNDER WATER |  | WM A HINDE - SAFETY SUPERVISOR | 7037507687 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR S&N COMMUNICATIONS WAS INSTALLING FIBER OPTIC CABLE WITH A TRENCHING MACHINE WHEN THEY STRUCK AND BROKE A 4" PLASTIC NATURAL GAS LINE. THE LINE WAS NOT MARKED DUE TO THE FAILURE OF THE CONTRACTOR TO UTILIZE THE MISS UTILITY SYSTEM. THIS ACTION CREATED AN EMERGENCY RESPONSE FOR WASHINGTON GAS.THE FIRE DEPARTMENT AND WASHINGTON GAS SECURED THE AREA AND THE GAS COMPANY UTILIZED A SECTION SHUTDOWN TO CONTROL PRODUCT FLOW. THIS ACTION RESULTED INA LOSS OF 898 METERS AND CREATED 2500 RELIGHTS. CONTINUOUS ACTIONS BY WASHINGTON GAS RESULTED IN 2050 RELIGHTS BEING COMPLETED BY 2115 HRS ON JANUARY 3,1993. CURRENTLY THE ENTIRE SECTION HAS BEEN FULLY RE-GASSED AND ALL CUSTOMERS ARE ON LINE. THERE WERE NO INJURIES AS A RESULT OF THIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19930009 | 1993-02-04 | 6650 | GREAT FALLS GAS CO | 1207 6 AV S | GREAT FALLS | CASCADE | MT | 59404 | 1 | NO | 2100 | 1993-01-22 | 0 | 1 | 0 | 0 | 0 | Null | 26 | 0 |  | 19930123 | 12 | 54 | BY CFR 192.619(A)(3) | 80 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | OTHER | NON SPECIFIED | 0.5 | 0.4 | ALDYL "A" | DUPONT | 1970 | 1972 | WITHIN/UNDER BUILDING |  | RONALD C SCHLERETH - DISTRIBUTION FOREMAN | 4067917538 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 1/2 IN. CTS PLASTIC BROKE IN TRANSION FITTING.
2025-01-31 10:21 | YES | YES | 19930010 | 1993-02-03 | 3170 | DAYTON POWER & LIGHT CO | INTERSEC MAIN ST & MONUMENT AVE | DAYTON | MONTGOMERY | OH | 45401 | 4 | NO | 615 | 1993-01-05 | 0 | 3 | 6000 | 4590.645 | 11083.9628 | Null | 4 | 15 |  | 19930105 | 0.25 | 1 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.444 |  | PHILLIPS | 1990 | 1990 | UNDER PAVEMENT | ELECTRIC VAULT | JOE A BARTON - GAS ANALYST | 5133314145 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APPARENC CAUSE: THE ESCAPE OF GAS CAUSED BY AN EARLIER ELECTRICAL DUCT FIRETHAT CAUSED AN INSERTED PLASTIC GAS PIPE TO MELT.ON JANUARY 4, 1993, AN ELECTRICAL CABLE, INSIDE A FIBER CONDUIT, SHORTED OUTCAUSING AN ELECTRICAL FIRE IN A VAULT. A 6 INCH PLASTIC PIPE INSERTED INSIDE AN 8 INCH BARE STEEL PIPE WAS LOCATED APPROXIMATELY 6 FEET NORTH OF THE ELECTRICAL VAULT. A CONDUIT CONTAINING THE SHORTED CABLE PASSED OVER THE CASED 6INCH PLASTIC MAIN. THE HEAT FROM THE SHORTED ELECTRICAL CABLE TRANSFERRED TO THE STEEL, AND IN TURN TO THE PLASTIC PIPE. THE PLASTIC PIPE MELTED THROUGHAND GAS ESCAPED INTO THE CASING AND MIGRATED INTO ANOTHER ELECTRICAL CONDUITWHICH ALSO ENTERED THE ELECTRICAL VAULT. AT 6:15 A.M. ON JANUARY 5, 1993, WORKERS INSTALLING A HEAT SHRINK SLEEVE ON AN ELECTRICAL CONNECTION IN THE VAULT WERE INJURED WHEN AN OPEN FLAME WAS PLACED ON THE SHRINK SLEEVE AT THE ENTRANCE TO THE CONDUIT. THE NATURAL GAS "FLASHED" WITH NO ENSUING FIRE.
2025-01-31 10:21 | NO | NO | 19930016 | 1993-01-29 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 924 E CRESTVIEW COURT | CROWN POINT | LAKE | IN | 46307 | 1 | NO | 1300 | 1992-12-30 | 0 | 0 | 60000 | 46984.835 | 113443.3541 | Null | 0 | 16 |  | 19930104 | 48 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.154 |  |  | 0 | 1956 | WITHIN/UNDER BUILDING |  | D.M. CAMPOS - MGR., GAS CONTROL & STORAGE | 2196476027 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | IN 1989, THE HOMEOWNER ENGAGED A CONTRACTOR TO MAKE REPAIRS TO THE FOUNDATION OF THE BUILDING. THE SERVICE LINE WAS HIT AND DAMAGED BY CONTRACTOR'S EQUIPMENT. THIS DAMAGE SUBSEQUENTLY LED TO THE GAS LEAKING AND MIGRATING INTO THE BUILDING WHERE IT SOMEHOW IGNITED RESULTING IN AN EXPLOSION THAT DAMAGED THE BUILDING AND CAUSING INJURIES TO TWO OF THE RESIDENTS WHO WERE TREATED AND RELEASED AT THE LOCAL HOSPITAL.
2025-01-31 10:21 | YES | NO | 19930017 | 1993-01-29 | 4483 | ENSTAR NATURAL GAS CO | 300 LOWER RD (LOT 1 BLK 4 WILDERNESS ACR | WASILLA | MATANUSKA SUSITNA BOROUGH | AK | 99687 | 2 | NO | 1605 | 1993-01-01 | 0 | 0 | 80000 | 61208.5997 | 147786.1708 | Null | 0 | 33 |  | 19930107 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER | S/L RISER | OTHER PLASTIC | HOPE TUBING ENCASING IN S | 0.625 | 0.09 | DRISCOPIPE | PHILLIPS | 0 | 1990 | OTHER | GAS METER ON SIDE OF GARA | DREW SMITH - SENIOR ENGINEER | 9072643744 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | THE OWNER OF LOT 1 BLOCK 4, WILDERNESS ACRES WAS WORKING ON A VEHICLE IN HISGARAGE. WHILE REMOVING THE FUEL PUMP SPILLED GASOLINE ON THE FLOOR. A BATTERY CHARGER WAS HOOKED UP TO CAR AND APPARENTLY IGNITED THE SPILLED GASOLINE. THE RESULTING FIRE BURNED THE GARAGE AND CONTENTS. THE GAS METER WAS LOCATED ON THE OUTSIDE OF THE GARAGE. THE FIRE SCORCHED THE SERVICE LINE RISER ANDMETER ASSEMBLY. THE EXTREME HEAT CAUSED THE COMPRESSION GASKET TO FAIL INSIDE THE STEEL RISER WHERE THE HDPE TUBING TRANSITIONS TO THE STEEL METER/REGULATOR ASSEMBLY. THE GAS ESCAPED TO THE ATMOSPHERE THROUGH THE SERVICE LINE RISER VENT HOLE. ENSTAR EVALUATED THE TOTAL DAMAGE CAUSED BY THE FIRE AND ESTIMATED THE FIRE DAMAGE AT $35,000 - $40,000. SINCE THE PROPERTY LOSS WAS LESSTHAN $50,000 THE RISER LEAK WAS NOT REPORTED AS A DOT INCIDENT. ON JANUARY 7, 1993, THE LOCAL NEWPAPER REPORTED THE PROPERTY DAMAGE AT $80,000 FOR THIS RESIDENTIAL FIRE. ENSTAR CHECKED WITH JACK KRILL, FIRE CHIEF OF THE CENTRAL MAT-SU FIRE DEPARTMENT TO VERIFY THE INCREASE PROPERTY DAMAGE AMOUNT. JACK CONFIRMED THE $80,000 AS THE REVISED ESTIMATE FOR THE PROPERTY LOSS BECAUSE ONE OF THE VEHICLES INVOLVED IN THE FIRE WAS A RACE CAR VALUED $40,000. JACK PROVIDED ENSTAR WITH A LETTER REVISING DAMAGE ESTIMATE AND TELEPHONIC INCIDENTNOTICE WAS IMMEDIATELY FILED WITH THE DOT.
2025-01-31 10:21 | YES | YES | 19930018 | 1993-01-28 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 1238 POPE | MEMPHIS | SHELBY | TN | 38108 | 3 | NO | 1135 | 1992-12-23 | 0 | 2 | 85600 | 67031.6979 | 161845.8519 | Null | 0 | 27 |  | 19921223 | 85 | 99 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NONE | STEEL |  | 4 | 0.237 | API-5L |  | 1970 | 1970 | ABOVE GROUND |  | LEONARD PHILLIPS - MANAGER, GAS OPERATIONS | 9013201401 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON WEDNESDAY, DECEMBER 23, 1992, WORKERS EMPLOYED BY INDUSTRIAL MECHANICAL CONTRACTORS WERE PERFORMING WORK ON NATURAL GAS FUEL LINES OWNED AND OPERATED BY THE HUMKO CHEMICAL DIVISION OF THE WITCO CORPORATION AT 1238 POPE STREET IN MEMPHIS. TO PREVENT SEEPAGE AT THE MLGW METER CENTER, TWO WORKERS HAD INSTALLED A BLANK AT THE DOWNSTREAM FLANGE CONNECTION OF A 4" PLUG VALVE LOCATED IMMEDIATELY DOWNSTREAM OF THE 16M ROTARY GAS METER AND PLANNED TO INSTALL ANOTHER BLANK AT THE 4" BYPASS VALVE, WHICH WAS CLOSED AND LOCKED. AT APPROXIMATELY 11:35 A.M., THE WORKERS WERE IN THE PROCESS OF REMOVING THE BOLTS ON THEUPSTREAM FLANGE WHEN NATURAL GAS AT ABOUT 85 PSIG BEGAN BLOWING FROM THE LOOSENED CONNECTION AND IGNITED. THE MEMPHIS FIRE AND POLICE DEPARTMENTS WERE ALERTED OF THE FIRE AT APPROXIMATELY 11:35 A.M. MLGW RECEIVED NOTICE AT 11:36 A.M. AND BEGAN DISPATCHING SERVICE PERSONNEL AT 11:40 A.M. THE FIRST MLGW EMPLOYEES ARRIVED ON THE SCENE AT 11:45 A.M. AND BEGAN LOCATING VALVES. BY 12:02 P.M. THREE MAIN LINES CONTROL VALVES HAD BEEN CLOSED, AND THE FIRE DIED OUT. THE FIRE INJURED THE TWO CONTRACTOR EMPLOYEES WHO WERE HOSPITALIZED FOR TREATMENT OF BURNS. THE FIRE ALSO DESTROYED TWO PRIVATE VEHICLES AND THEMLGW METER CENTER, AND DAMAGED ONE WALL OF A SHED OWNED BY HUMKO, ELECTRICALFACILITIES BELONGING BOTH TO MLGW AND HUMKO, AND ASPHALT DRIVEWAYS ADJACENT TO THE SITE. AN ELECTRICALLY-POWERED IMPACT WRENCH FOUND AT THE SITE IS SUSPECTED AS THE SOURCE OF IGNITION. ONE OF THE INJURED WAS RELEASED FROM THE HOSPITAL ON DECEMBER 24 AND THE OTHER WAS RELEASED ON JANUARY 5.
2025-01-31 10:21 | YES | NO | 19930030 | 1993-02-16 | 22189 | WASHINGTON NATURAL GAS CO | 125 E MAIN ST | MONROE | SNOHOMISH | WA | 98272 | 3 | NO | 1640 | 1993-01-20 | 0 | 0 | 250000 | 191276.8739 | 461831.7838 | Null | 4 | 30 |  | 19930122 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | STEEL |  | 1 | 0 |  |  | 0 | 1958 | WITHIN/UNDER BUILDING |  | DOUGLAS DAMM - SAFETY MANAGER | 2062242396 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INCIDENT STILL UNDER INVESTIGATION. SUSPECTED CAUSE - DURING SEVERE STORM, POWER OUTAGES AND DOWNED WIRES CAUSED ELECTRICAL CURRENTO TO ENERGIZE STEEL GAS SYSTEM. ARC JUMPED TO ADJACENT WATER LINE AND BURN THROUGH ON GAS SERVICE RESULTED. GAS MIGRATED UNDER HARD SURFACE ALLEY TO BUILDING ABOUT 10 FEET AWAY. IGNITION OF GAS IN BUILDING OCCURRED DUE TO UNKNOWN CAUSES. BUILDING DESTROYED IN RESULTING FIRE. FOUR PERSONS WERE INJURED, ONE HOSPITALIZED.
2025-01-31 10:21 | YES | NO | 19930032 | 1993-01-17 | 15896 | PROVIDENCE GAS CO | 515 FAIR ST | WARWICK | KENT | RI | 02888 | 3 | NO | 1515 | 1993-01-20 | 0 | 0 | 300000 | 229532.2487 | 554198.1406 | Null | 3 | 15 |  | 19930120 | 9 | 12 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 |  |  | 0 | 1929 | UNDER PAVEMENT |  | ROBERT R RINGMAN - MGR. OF DISTR & ENGR | 4012725040 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-01-05 | YES | 0 |  | YES |  |  | D'AMBRA CONSTRUCTION WAS INSTALLING SANITARY SEWERS AT THE INTERSECTION OF CLEARWATER AND FAIR STREETS IN WARWICK, RI. THIS PERPENDICULAR EXCAVATION EXPOIN THE TRENCH OF A 14 FOOT DEEP EXCAVATION. A 10 INCH VITRIFIED CLAY TILE DRAIN RUNNING PARALLEL TO THE GAS MAINS WAS REMOVED DURING CONSTRUCTION AND REPLACED WITH AN 8 FOOT SECTION OF 8 INCH PVC BEFORE BACKFILLING. THE CELLAR OF #515 FAIR STREET WAS EQUIPPED WITH AN INTERNAL PERIMETER DRAIN SYSTEM, INSTALLED DIRECTLY ABOVE THE OPEN END OF A 4 INCH V.C. TILE DRAIN, WHICH LED TO THE STREET AND CONNECTED TO THE 10 INCH V.C. TILE DRAIN, MENTIONED ABOVE. IMPROPER BACKFILLINF AND COMPACTION TECHNIQUES BY THE SEWER CONTRACTOR APPEARED TO HAVE CAUSED BOTH THE CAST IRON MAIN TO BREAK AND THE SECTION OF REPLACEMENT PVC TO DROP BY APPROXIMATELY 11 INCHES. THE CLAY TILES ON EITHER END OF THE10 INCH DRAIN COLLAPSED DUE TO THE DOWNWARD FORCE, AND LEFT AN OPEN END FOR THE GAS LEAKING FROM THE BROKEN MAIN TO MIGRATE INTO #515 FAIR STREET THROUGHTHE CONNECTED 4 INCH V.C., WHERE IT WAS DISTRIBUTEDD BY THE PERIMETER DRAIN SYSTEM AROUND THE CELLAR. IGNITION OF THE ESCAPING GAS MAY BEEN BY THE OIL NURNER IN THE CELLAR.SEDD APPROXIMATELY 7 FEET OF 6 INCH CAST IRON MAIN, OPERATING AAAT 35 PSIG, 0
2025-01-31 10:21 | NO | NO | 19930033 | 1993-02-17 | 6141 | GAS CO OF NEW MEXICO | 2990 PLAZA BLANCA | SANTA FE | SANTA FE | NM | 87501 | 3 | NO | 815 | 1993-01-21 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 10 |  | 19930128 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | NON SPECIFIED | 0.75 | 0 | MODEL 043-92 | ROCKWELL | 0 | 1978 | ABOVE GROUND |  | STEVEN C EMRICK - CHIEF ENGINEER-GAS OPERATIONS | 5058484503 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SERVICE REGULATOR VENT PR | NO |  | NO | 0 |  | NO |  |  | CUSTOMER METER SET, SERVICE REGULATOR VENT PRESUMEDLY BLOCKED BY ICE FORMATION. ALLEDGEDLY CONTRIBUTED TO REGULATOR MALFUNCTION, ALLOWING HIGHER THAN NORMAL .25 PSIG DELIVERY PRESSURE TO ENTER CUSTOMER HOUSEPIPING SYSTEM.. ELEVATED GAS PRESSURE EXTINGUISHED PILOT LIGHT ON CENTRAL HEATING PLANT IN UTILITY ROOM OF RESIDENCE AND GAS ESCAPING FROM CHP CONTROL VALVE ACCUMULATED IN CEILING AREA. SOURCE OF IGNITION ASSUMED TO HAVE BEEN AT NATURAL GAS HOT WATER HEATER OR CLOTHES DRYER.
2025-01-31 10:21 | YES | YES | 19930034 | 1993-02-23 | 12738 | MONTEZUMA MUNICIPAL GAS UTILITIES DEPT | 1113 JEFFERSON STREET | MONTEZUMA | PARKE | IN | 47862 | 3 | NO | 109 | 1993-01-21 | 1 | 3 | 78000 | 59678.3847 | 144091.5166 | Null | 2 | 21 |  |  | 18 | 60 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | JOINT |  | STEEL |  | 1.25 | 0.205 |  |  | 0 | 1942 | UNDER PAVEMENT |  | ROBERT C ALLEN - SUPERINTENDENT | 3172452759 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | NO DATA | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19930035 | 1993-02-11 | 1088 | BALTIMORE GAS & ELECTRIC CO | 213A POPLAR AVE | ANNE ARUNDEL |  | MD |  | 2 | NO | 243 | 1993-01-23 | 0 | 0 | 80000 | 61208.5997 | 147786.1708 | Null | 0 | 47 |  | 19930203 | 95 | 99 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALIMINIUM METER | 0 | 0 |  | AMERICAN MTR | 0 | 0 | WITHIN/UNDER BUILDING | BASEMENT | DENNIS G BLESSING - OPERATIONS ANALYST | 4105612779 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | FIRE | NO |  | NO | 0 |  | NO |  |  | ON JANUARY 23, 1993 AT 0245 HOURS, OPERATIONS RECEIVED A CALL FROM ANNE ARUNDEL FIRE HDGTS, OF A DWELLING FIRE AT 213 POPLAR AVENUE, RES A. AT 0305 HOURS, SERVICEMAN REPORTED A GAS LINE WAS ON FIRE AND WAS FEEDING FIRE. CENTRAL DISTRIBUTION WAS NOTIFIED AT 0308 AND INCIDENT COORDINATOR, WILLIAM O'BYRNE WAS NOTIFIED AT 0310. AT 0330, INSIDE HIGH PRESSURE VALVE WAS TURNED OFF. FIRE INVESTIGATOR SHANKS WOULD NOT ALLOW US ACCESS UNTIL BUILDING WAS SHORED UP. ON 1/23/93 AT 0800, SERVICEMAN DISPATCHED TO REMOVE METERS AND FOUND BUILDING UNSAFE TO ENTER. ON 1/27/93 AT 1630, INVESTIGATION SHANKS CALLED AND SAID BUILDING WAS ACCESSIBLE AND EQUIPMENT COULD BE REMOVED. ON 1/30/93, WE SENT ANOTHER MAN AND HE STATED IT DID NOT SEEM SAFE. ON 2/3/93, MR. BLESSING VISISTED PREMISES AND REMOVED METERS AND EQUIPMENT. ONE METER SEEMED TO HAVE BEEN TAMPERED WITH. A PIECE OF THE GAS METER NEAR THE TOP SEEMED TO BE BROKENOFF AND A HOLE, WHICH RESEMBLED A BULLET HOLE, WAS IN THE SIDE OF THE METER. MR. DANKANICH WAS NOTIFIED AND REQUESTED REPORTS TO BE SUBMITTED TO HIS OFFICE AND DOT. MR. BLESSING EXPLAINED THAT THE REASON FOR THE DELAY WAS DUE TO THE INABILITY TO GAIN ACCESS TO THE METERS. MR. DANKANICH UNDERSTOOD THE DELA
2025-01-31 10:21 | YES | YES | 19930037 | 1993-02-26 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | EAST 5TH ST AND WAYNE ST | ERIE | ERIE | PA | 16507 | 3 | NO | 1600 | 1993-01-27 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 30 |  | 19930127 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | LOW PRESSURE GAS BAG | STEEL |  | 10 | 0.3 | API 5L |  | 0 | 1956 | OTHER | OPEN EXCAVATION | CONRAD L DONELSON/SUPERINTENDENT | 8148718341 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TWO BELL HOLE EXCAVATIONS, APPROXIMATELY 28 FEET APART, HAD BEEN PREPARED PRIOR TO A 10 INCH, LOW PRESSURE MAINLINE REPLACEMENT BY INSERTION. IN BELL HOLE #1, THE GAS FLOW HAD BEEN STOPPED BY USE OF A SINGLE GAS BAG INSERTED IN THE MAINLINE. A 5 FOOT SECTION OF THE 10 INCH PIPE HAD BEEN REMOVED. IN BELLHOLE #2, A WELDER WAS USING A CUTTING TORCH TO BURN OFF AN OLD DRIP LEG PRIOR TO INSERTION. RESIDUAL GAS IN THE OLD 10 INCH MAIN IGNITED AND FLASHED INTO BELL HOLE #1, IGNITED SEEPING GAS AT THE BAG HOLE. A SUPERVISORY EMPLOYEE APPROACHED BELL HOLE #1 AND, NOTICING THE BAG HOLE FIRE, RETRIEVED A NEARBY FIRE EXTINGUISHER. AS HE PREPARED TO USE THE EXTINGUISHER AT THE DITCH EDGE, THE GAS BAG FAILED. THE EMPLOYEE WAS BURNED BY THE ENSUING FIRE FUELED BY ESCAPING.
2025-01-31 10:21 | YES | YES | 19930038 | 1993-02-25 | 18536 | SOUTHWEST GAS CORP | 5102 WEST OSBORN ROAD | PHOENIX | MARICOPA | AZ | 85031 | 3 | NO | 511 | 1993-02-09 | 0 | 1 | 85000 | 65034.1371 | 157022.8065 | Null | 1 | 0 |  | 19930209 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | CAST IRON |  | 2 | 0 |  | ROCKWELL | 1958 | 1958 | UNDER GROUND OR UNDER WATER |  | PHIL S ANDREW / MANAGER - ENGINEERING-CAD | 6024845218 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SOUTHWEST GAS PERSONNEL RESPONDED TO A HOUSE FIRE AT 5102 WEST OSBORN ROAD IN PHOENIX. A TWO-INCH (2") ROCKWELL FIGURE 143 PLUG VALVE SHOWED A CIRCUMFERENTIAL CRACK OF APPROXIMATELY THREE INCHES (3") IN LENGTH NEAR THE FLANGED PORTION OF THE VALVE.
2025-01-31 10:21 | YES | YES | 19930039 | 1993-02-22 | 13783 | NORTHERN STATES POWER CO | W7155 COUNTY RD "F" | PHILLIPS | PRICE | WI | 54555 | 2 | NO | 1417 | 1993-02-02 | 0 | 1 | 50000 | 38255.3748 | 92366.3568 | Null | 2 | 0 |  | 19930202 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.32 |  | EXTRON | 1970 | 1974 | OTHER | UNDER GRAVEL PARKING LOT | SCOTT M OLSON - GAS DISTRIBUTION ENGINEER | 7158392540 | [6 empty] | Null |  | OPERATOR ACTION | 3C | NO |  | NO | 0 |  | NO |  |  | THE MATERIAL FAILURE WHICH LED TO THE INCIDENT MENTIONED ABOVE, OCCURRED ON THE BODY OF THE PIPE, IMMEDIATELY ADJACENT TO A SOCKET FUSION ON A 3"X3"X3" TEE. THE FAILURE IS BELIEVED TO HAVE BEEN CAUSED BY A COMBINATION OF FACTORSTHE PIPE IN QUESTION WAS INSTALLED IN JUNE 1974 IN ROCK-FREE, SANDY SOIL. THERE IS NO RECORD OF LEAKS IN THE AREA WHERE THE FAILURE OCCURRED. IT WAS OBSERVED THAT THE FAILURE WAS LOCATED ON THE PIPE, JUST ALONG SIDE THE SOCKET FUSION. THE CRACK IN THE PIPE APPEARED ALONG THE SURFACE OF THE MAIN, AT HE FACE OF THE TEE. IT WAS ALSO NOTED THAT THE MAIN GOING INTO ONE LEG OF THE TEE. IT WAS ALSO NOTED THAT THE MAIN GOING INTO ONE LEG OF THE TEE, WAS AT A SLIGHT ANGLE. THIS MAY HAVE PLACED UNNECESSARY STRESS ON THE PIPE AND CONTRIBUTED TO THE MATERIAL FAILURE. A SECOND FACTOR THAT MAY HAVE CONTRIBUTED TO THE FAILURE WAS THE FROST. IN THE LOCATION OF THE INCIDENT, FROST USUALLY EXTENS 4-5' BELOW GRADE. IN THIS CASE, HOWEVER, THE FROST EXTENDED TO A GREATERDEPTH BECAUSE THE TEE WAS BENEATH A PARKING LOT. THE INSULATING BENEFIT OF THE SNOW IF REMOVED EACH TIME THE LOT IS CLEARED OF SNOW. THE ADDITIONAL GROUND MOVEMENT CAUSED BY THE FROST/THAW CYCLE MAY HAVE CONTRIBUTED ADDITIONAL STRESS TO THE PIPELINE. FINALLY, RECENT THIRD PARTY EXCAVATION IN THE VICINITY OF THE PIPE, MAY HAVE ALSO CONTRIBUTED TO THE MATERIAL FAILURE. ALTHOUGH THERE WAS NO APPARENT DAMAGE TO THE PIPE, A NEW SEWER LATERAL WAS INSTALLED BENEATH THE EXISTING PIPELINE, IN NOVEMBER 1992. THE EXACT LOCATION OF THE LATERAL CANNOT BE DETERMINED BUT, IT IS IN THE VICINITY OF THE BREAK. IMPROPER BACKFILLING PROCEDURES MAY HAVE CAUSED DELAYED SETTLING IN THE TRENCH AFTER THE WORK WAS COMPLETED, THUS CONTRIBUTING TO ADDITIONAL STRESS AND SUBSEQUENT FAILURE. BASED UPON THE LOCATION OF THE LEAK AND THE SIZE OF THE MAIN, THE PRESENCE OF AN EXCESS FLOW VALVE WOULD HAVE HAD NO EFFECT NO PREVENTING THIS INCIDENT FROM OCCURRING.
2025-01-31 10:21 | YES | YES | 19930040 | 1993-02-23 | 4350 | ELIZABETHTOWN GAS CO | 826 WEST GRAND ST | ELIZABETH | UNION | NJ | 07207 | 4 | NO | 542 | 1993-02-08 | 0 | 3 | 90000 | 68859.6746 | 166259.4422 | Null | 2 | 35 |  | 19930208 | 20 | 35 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.48 | ASA - A21.7 | WARREN FOUNDRY & PIPE PHILLIPSBURG | 0 | 1948 | UNDER PAVEMENT |  | DONALD RING - DIVISION DIRECTOR | 9082895000 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | ESCAPE OF GAS RESULTING FROM CRACK IN MAIN APPARENTLY CAUSED BY WEATHER.
2025-01-31 10:21 | NO | NO | 19930043 | 1993-03-02 | 11800 | LOUISIANA GAS SERVICE CO | INTERS. OF POPE & FRIEDRICH STREETS | MONROE | OUACHITA | LA | 71201 | 3 | NO | 1736 | 1993-02-18 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 46 |  |  | 47 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | COUPLING | STEEL |  | 2 | 0.152 | API-5L |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES |  |  | A BACKHOE OPERATED BY A CONTRACTOR PULLED A 2" GAS MAIN OUT OF A DRESSER COUPLING.
2025-01-31 10:21 | YES | YES | 19930044 | 1993-02-23 | 100 | KIRKWOOD GAS AND ELECTRIC CO | 1370 KIRKWOOD MEADOWS DR | KIRKWOOD | ALPINE | CA | 95646 | 1 | NO | 1424 | 1993-01-20 | 2 | 0 | 0 | 0 | 0 | Null | 0 | 25 |  | 19930121 | 14 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | JOINT |  | STEEL |  | 1.05 | 0.113 |  |  | 0 | 1981 | ABOVE GROUND |  | ANDREW J WUELLNER - GENERAL MANAGER | 2092587216 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SNOW | NO |  | NO | 0 |  | NO |  |  | HEAVY ACCUMULATION OF SNOWFALL.
2025-01-31 10:21 | YES | NO | 19930045 | 1993-03-08 | 15469 | PHILADELPHIA GAS WORKS | 5939 N BEECHWOOD | PHILADELPHIA | PHILADELPHIA | PA |  | 4 | NO | 1845 | 1993-02-25 | 0 | 0 | 86000 | 65799.2446 | 158870.1336 | Null | 1 | 45 |  | 19930225 | 0.26 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 |  |  | 0 | 1902 | UNDER PAVEMENT |  | JOSEPH M CAREY - MANAGER DISTRIBUTION | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | WATER LEAK ON VICINITY | NO |  | NO | 0 |  | NO |  |  | THE MATERIAL DEFECT WAS A "HARDSPOT" ON THE PIPE DUE TO THE MANUFACTURE'S PROCESS. THE "HARDSPOT" WAS PREVIOUSLY INDENTIFIED AND REINFORCED WITH A SLEEVE. THE REINFORCING SLEEVE CONTAINED THE DEFECT.
2025-01-31 10:21 | YES | YES | 19930047 | 1993-03-08 | 2596 | COLUMBIA GAS OF OHIO INC | 108 W WOOSTER AVE | NAVARRE | STARK | OH | 44662 | 3 | NO | 1145 | 1993-02-09 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19930209 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | OTHER | HUMAN ERROR | STEEL |  | 1.25 | 0.179 |  |  | 0 | 0 | OTHER | IN EXCAVATION | DONALD E WILLIAMS - MGR OF CONSTRUCTION & MAINTENANCE | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | HUMAN ERROR | CREW WAS REPLACING A SERVICE LINE. THE OLD SERVICE WAS CUT AND PLUGGED WITHAN EXPANSION PLUG. THE EXPANSION PLUG WAS INSERTED 2-1/2 " INTO THE 6" SERVICE STUB LEFT ON THE MAIN BEFORE THE STUB WAS CAPPED WITH A COMPRESSION END CAP. EMPLOYEE FOUND A PIN HOLE LEAK AT THE SERVICE TAP DURING THE CLEANING OPERATIONS AND WITHOUT THINKING, CUT THE SERVICE STUB OFF UPSTREAM OF THE EXPANSION PLUG. GRINDER INGNITED THE ESCAPING GAS AND BURNED EMPLOYEE'S FACE. EMPLOYEE WAS KEPT OVERNIGHT AT THE HOSPITAL FOR OBSERVATION AND RELEASED.
2025-01-31 10:21 | NO | NO | 19930048 | 1993-03-10 | 8020 | IGNACIO MUNICIPAL GAS | 1/4 MI E OF HWY 172 ON HWY 151 CITY GATE | IGNACIO | LA PLATA | CO | 81137 | 3 | NO | 645 | 1993-02-05 | 0 | 0 | 4950 | 3787.2821 | 9144.2693 | Null | 20 | 15 |  | 19930211 | 50 | 50 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN | SERVICE LINE, METER SET A | REGULATOR/METER |  | STEEL |  | 203 | 0.145 |  |  | 1958 | 1959 | OTHER | WATER IN SYSTEM | JOSE B QUINTANA - MANAGER | 3035639494 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | SUPPLIER (EL PASO NATURAL GAS) ALLOWED SURGE OF WATER TO ENTER CITY GATE. WATER RENDERED MAIN SYSTEM REGULATORS INOPERABLE. WATER SURGE ALSO CAUSED PRESSURE RELIEF VALVE TO NOT RESET WHEN WATER SURGE CAUSED PRESSURE RELIEF VALVETO VENT INTO ATMOSPHERE. DAMAGED ASSESSED INCLUDES MAN HOURS REQUIRED TO RESTORE NORMAL OPERATION. WATER REMAINS IN SYTEM, THEREFORE, FINAL FIGURES ON DAMAGES ARE NOT IN.
2025-01-31 10:21 | NO | NO | 19930049 | 1993-03-16 | 2344 | CHILTON COUNTY GAS DIST | OFF OF STATE HWY #25 | CALERA | SHELBY | AL | 35040 | 2 | NO | 1430 | 1993-01-27 | 0 | 0 | 40000 | 30604.2998 | 73893.0854 | Null | 1 | 0 |  | 19930127 | 150 | 150 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | POLYETHYLENE PLASTIC |  | 3 | 0 | AP15L |  | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | DEBORAH ROBINSON - CLERK | 2056882012 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | ALLIED LIME CO. BULLDOZIER OPERATOR CARRYING OUT SUPERVISOR INSTRUCTIONS, HIT AND TORE LOOSE 53 FEET OF 3 INCH MAIN CAUSING OUTRAGE OF COMPLETE CHILTON COUNTY GAS SYSTEM.
2025-01-31 10:21 | YES | YES | 19930050 | 1993-03-11 | 18153 | SAWYER GAS OF JACKSONVILLE INC | 929 DEPAUL DR. | JACKSONVILLE | DUVAL | FL |  | 0 | NO | 130 | 1992-10-04 | 1 | 0 | 40000 | 31323.2233 | 75628.9028 | Null | 0 | 0 |  | 19921005 | 0.39 | 0.39 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | MARK A DARN | 9042968600 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | SARAH ROBBINS' DEATH WAS REPORTED ON 11-05-92 TO WR BUER (DETECTIVE - ID# 5967) BY THE GAINSVILLE MEDICAL EXAMINERS OFFICE.
2025-01-31 10:21 | YES | NO | 19930056 | 1993-03-08 | 2748 | CONSUMERS POWER CO | 15722 TURNER STREET | DE WITT | CLINTON | MI | 48820 | 3 | NO | 1256 | 1993-01-29 | 0 | 0 | 80000 | 61208.5997 | 147786.1708 | Null | 1 | 54 |  | 19930129 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | VALVE | THREADED | STEEL |  | 2 | 0.154 | THREADED |  | 0 | 1939 | UNDER GROUND OR UNDER WATER |  | KENNETH L ELENBAAS - GENERAL SUPR OF O & M | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | PIPE FAILED AT THREADED JOINT. SEWER CONTRACTOR DAMAGED MAIN NEAR FAILED POINT ON 5/21/91. STRESS FROM DAMAGE CONTRIBUTED TO JOINT FAILURE.
2025-01-31 10:21 | YES | NO | 19930057 | 1993-03-01 | 18536 | SOUTHWEST GAS CORP | 3136 POLARIS | TAHOE CITY | PLACER | CA | 96145 | 3 | NO | 605 | 1993-02-21 | 0 | 0 | 100000 | 76510.7496 | 184732.7135 | Null | 4 | 25 |  | 19930221 | 35 | 43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 0.5 | 0.125 |  |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | CHRIS HERSHBERGER - DISTRICT MANAGER | 7028311575 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOTS AND ROCKS | NO |  | NO | 0 |  | NO |  |  | LACER COUNTY SHERIFF'S DEPARTMENT OF AN APPARENT NATURAL GAS EXPLOSION AT 3135ON FEBRUARY 21, 1993 AT 6:05 A.M., SOUTHWEST GAS RECEIVED A REPORT FROM THE P POLARIS. ON FEBRUARY 21, 1993, PRELIMINARY INVESTIGATION REVEALED THAT THE IGNITION OF NATURAL GAS TOOK PLACE IN THE CRAWL SPACE UNDER THE LIVING ROOMFLOOR OF THE ABOVE MENTIONED RESIDENCE. THE APPARENT SOURCE OF IGNITION WASTHE FORCED AIR FURNACE LOCATED IN A HALL CLOSET. THERE WAS NO SUBSEQUENT FIRE, AND DAMAGE WAS ESTIMATED TO BE APPROXIMATELY $20,000. FURTHER INVESTIGATION INDICATED THAT THE SOUTHWEST GAS SERVICE LINE WAS ISOLATED AT APPROXIMATELY 10:20 A.M. ON FEBRUARY 21, 1993. DUE TO EXTREME WEATHER CONDITIONS INCLUDING LARGE ACCUMULATIONS OF SNOW AND HEAVY SNOW STORM CONDITIONS, THE INVESTIGATION TO LOCATE AND EXAMINE THE SERVICE LINE CONTINUED THROUGH FRIDAY, FEBRUARU 26, 1993. ON FEBRUARY 25, 1993, IT WAS DETERMINED THAT THE 1/2" PVC GAS SERVICE LINE WAS LEAKING AT A POINT APPROXIMATELY 20 FEET OUT TOWARD THE STREET FROM THE FRONT RIGHT CORNER OF THE RESIDENCE. THE CAUSE OF THE LEAKAGE HASBEEN DETERMINED TO BE A TREE ROOT WHICH GREW AGAINST THE 1/2" PVC SERVICE AND EVENTUALLY FORCING THE SERVICE LINE AGAINST ROCKS WHICH CAUSED A 1" CRACK ON THE TOP AND A 5" CRACK ON THE SIDE OF THE PVC. ALSO ON THIS DATE, THE SERVIDE LINE TO THE RESIDENCE WAS REPLACED.
2025-01-31 10:21 | YES | YES | 19930058 | 1993-03-15 | 13610 | NORTH CROSSETT GAS & WATER | RT 4 BOX 208 BINN'S LOOP RD | CROSSETT | ASHLEY | AK | 71635 | 1 | NO | 1530 | 1993-02-10 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 45 |  | 19930210 | 26 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.154 | SCHEDULE 40 |  | 1961 | 1962 | UNDER GROUND OR UNDER WATER |  | DALLAS J ANDERSON - UTILITY MANAGER | 5013642188 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION AT RESIDENCE ACROSS ROAD FROM PIPELINE. THE EXACT CAUSE OF THE HOUSE FIRE AND THE PIPELINE RUPTURE ARE STILL UNDER INVESTIGATION. WHEN DETERMINED, A SUPLEMENTAL REPORT WILL BE ISSUED.
2025-01-31 10:21 | YES | NO | 19930060 | 1993-03-15 | 1640 | BOSTON GAS CO | 54 AUTUMN STREET | MALDEN | MIDDLESEX | MA | 02148 | 1 | NO | 1640 | 1993-02-22 | 0 | 0 | 75000 | 57383.0622 | 138549.5352 | Null | 3 | 0 |  | 19930222 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NON SPECIFIED | STEEL |  | 1.5 | 0 | API5L |  | 0 | 1927 | UNDER GROUND OR UNDER WATER |  | ROBERT J CAVICCHI - MGR - DIST. ADMINISTRATION | 6173239210 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | DAM/EARTH MOVT -POOR FILL | NO |  | NO | 0 |  | NO |  |  | THERE WAS A FIRE INSIDE THE HOUSE AT 54 AUTUMN STREET, MALDEN. AFTER REPORTED EXPLOSIONS, THE HOUSE WAS LEVELED. INVESTIGATION AND EXCAVATION REVEALED A FRESH CRACK IN THE SERVICE PIPE AT THE THREADED CONNECTION TO A COUPLING. SOURCE OF IGNITION FOR THE FIRE AND EXPLOSIONS IS UNKOWN AT THIS TIME.
2025-01-31 10:21 | YES | NO | 19930061 | 1993-03-15 | 24015 | YANKEE GAS SERVICES CO | #844, #850 DERBY AVENUE | SEYMOUR | NEW HAVEN | CT | 06483 | 4 | NO | 37 | 1993-02-08 | 0 | 0 | 1000000 | 765107.4956 | 1847327.1354 | Null | 2 | 8 |  | 19930208 | 46 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NIPPLES | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1979 | ABOVE GROUND |  |  | 0 0 0 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NOMINAL PIPE SIZE (1) 1.25, (2) 0.75. WALL THICKNESS (1) .140, (2) 0.113.YEAR INSTALLED (1) 1979, (2) 1976. REGULATOR/METER MANIFOLDS WERE STRUCK BY FALLING DEBRIS WHICH RESULTED FROM FIRE. 3/4" PIPE NIPLE AT OUTLET OF RISER COCK AND 1 1/4" NIPPLE AT OUTLET OF RISER COCK WERE RUPTURED. ESCAPE OF NATURAL GAS RESULTED, AND THE GAS WAS IGNITED BY THE BUILDING FIRE.
2025-01-31 10:21 | NO | NO | 19930062 | 1993-04-08 | 1088 | BALTIMORE GAS & ELECTRIC CO | 1641 WILIAMS AVE | ESSEX | BALTIMORE | MD | 21221 | 2 | NO | 115 | 1993-03-26 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 1 | 0 |  | 19930326 | 10 | 10 | BY TEST | 10 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | REGULATOR VENT TAMPERED W | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | L WAYNE HARBAUGH - GENERAL SUPERVISOR - TECHNICAL DIVISION | 4105612710 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | UNKNOWN | NO |  | NO | 0 |  | YES |  |  | VENT LINE FROM 3/4 REG. NOT VENTED TO OUTSIDE. REMODELING DONE TO HOUSE, POSSIBLY DISCOUNTED BY CUSTOMER AT THIS TIME. HOUSE AND CONTENTS DESTROYED BY FIRE OF SUSPICIOUS ORIGIN. ELECTRICITY HAD BEEN DENIED FOR NON-PAYMENT ON 2/10/93. FIRE DEPARTMENT INVESTIGATOR STATED THAT TENANT HAD BEEN EVICTED PRIOR WEEK. FIRE DEPARTMENT INVESTIGATOR DETERMINED FIRE STARTED IN AREA OF METER. WITH ELECTRICITY OFF AT METER AND ON ONE LIVING IN HOUSE, IGNITION SOURCE MUST BE SUSPICIOUS. NO EVIDENCE OF EXPLOSION.
2025-01-31 10:21 | YES | NO | 19930063 | 1993-04-02 | 12684 | MONTANA - DAKOTA UTILITIES CO | 512 INDIANA STREET | RAPID CITY | PENNINGTON | SD | 57701 | 3 | NO | 2024 | 1993-03-02 | 0 | 0 | 125000 | 95638.437 | 230915.8919 | Null | 0 | 5 |  | 19930303 | 20 | 29 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NON SPECIFIED | STEEL |  | 2 | 0.188 | UNKNOWN | UNKNOWN | 1950 | 1950 | OTHER | NON SPECIFIED | TONY FINNEMAN - GAS DISTRIBUTION MANAGER | 7012227994 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1991-12-16 | YES | 0 | PAINT | YES |  |  | AT APPROXIMATELY 8:24 P.M., 3/02/93, THE HOUSE AT 512 INDIANA STREET, RAPID CITY, SD, EXPLODED. SUBSEQUENT INVESTIGATION FOUND THE CAUSE TO BE A CRACKEDNATURAL GAS MAIN. THE CRACK WAS IN THE 2 INCH GAS MAIN WHICH PARALLELED A CARPORT 7 FEET AWAY AND NEAR THE MIDDLE OF THE HOUSE AT 512 INDIANA STREET. THE 2 INCH MILL WRAPPED STEEL CATHODICALLY PROTECTED MAIN HAD CRACKED AT THE BOTTOM OF A DENT. THE DENT WAS ON THE TOP HALF OF THE PIPE EXTENDING FROM APPROXIMATELY THE 9 O'CLOCK TO THE 2 O'CLOCK POSITION. THE DENT WAS APPARENTLY CAUSED BY A TOOTH FROM A LARGE EXCAVATING MACHINE SUCH AS A CRAWLER BACKHOE.CITY OF RAPID CITY EXCAVTION AND MDU LINE LOCATION RECORDS INDICATED THE ONLY EXCAVATION IN THE ALLEY ADJACENT TO 512 INDIANA STREET WAS HILLS MATERIALSCO. INSTALLING A SEWER REPLACEMENT PROJECT DURING THE WINTER OF 1991 - 1992.THEY WENT PAST 512 INDIANA STREET DURING THE WEEK OF DECEMBER 16TH, 1991.
2025-01-31 10:21 | NO | NO | 19930064 | 1993-04-02 | 15462 | PHILADELPHIA ELECTRIC CO | 953 MYSTIC LANE | NORRISTOWN | MONTGOMERY | PA | 19403 | 3 | NO | 1530 | 1993-03-04 | 0 | 0 | 55000 | 42080.9123 | 101602.9924 | Null | 22 | 30 |  | 19930304 | 84 | 99 | BY TEST | 99 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | ASA A21.7 | UNKNOWN | 0 | 1960 | UNDER PAVEMENT | UNDER GROUND OR UNDER WAT | K HILL - ENGINEER III | 2159411770 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | TWO LEAKING GAS SERVICES IMMEDIATELY NEXT DOOR AND DOWN HILL FROM THE INCIDENT SCENE CAUSED GAS TO MIGRATE UNDER THE PAVEMENT INTHE SANITARY SEWER MAIN TRENCH AND ALSO IN THE WATER MAIN TRENCH OUTSIDE OF PAVING. THE MIGRATING GASTHEN FOLLOWED THE WATER SERVICE TRENCH TO THE SINGLE FAMILY DWELLING HOUSE WALL AND UNDER THE SLAB FOUNDATION OF THE HOUSE. THE GAS WAS MIGRATING IN A SOFT CLAY SOIL WITH 1 TO 2 INCHES OF FROST ON THE SURFACE. THE GAS BUILT UP IN A CRAWL SPACE UNDER THE KITCHEN STOVE. WHILE THE RESIDENT WAS USING THE OVEN, SHE NOTICED FLAMES EMANATING FROM THE STOVE AND UNDER THE CRAWL SPACE. THE FIRE COMPANY WAS CALLED AND, UPON EXITING THE HOUSE AN EXPLOSION WAS HEARDAND FELT. THE HOUSE EXPERIENCED MINOR FIRE DAMAGE AND MINOR STRUCTURAL DAMAGE AS A RESULT OF THE FIRE AND EXPLOSION. AS A RESULT OF THE LEAKS, TWO OTHERSINGLE STORY DWELLINGS ACROSS THE STREET WERE ALSO FOUND TO HAVE READINGS INCRAWL SPACES AND BOTH OF THE DWELLINGS WERE EVACUATED.
2025-01-31 10:21 | NO | NO | 19930065 | 1993-04-02 | 9050 | JACKSON VANGAS INC | 515 WEST BROADWAY | JACKSON | TETON | WY | 83001 | 3 | NO | 330 | 1993-03-17 | 0 | 0 | 60000 | 45906.4497 | 110839.6281 | Null | 0 | 40 |  | 19930317 | 5 | 15 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | OTHER | UNKNOWN | STEEL |  | 0.75 | 0.15 | SCH 40 |  | 0 | 1988 | ABOVE GROUND |  | MIKE WOHLFARTH - DISTR MGR | 3077333628 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | UNDETERMINED | NO |  | NO | 0 |  | NO |  |  | AS OF 3/24/93, IT IS MY OPINION ALL INVESTIGATIONS ARE INCONCLUSIVE. THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION. IN MY OPINION, THERE IS NO SUBSTANTIAL PROOF OF THE SOURCE OF IGNITION AT THIS TIME. SO FAR THERE IS NO EVIDENCE OF AN EXPLOSION. ON 3/23/93 THE SERVICE LINE, AND THE MAIN, 20 FEET ON BOTH SIDES OF THE SERVICE CONNECTION, WAS BAR HOLED AND SNIFFED WITH THE CGI. TH RESULTS WERE NEGATIVE. AFTER THE BAR HOLE TEST THE SERVICE LINE WAS UNBURIED WHERE IT CONNECTS TO THE MAIN, CUT THE SERVICE LINE AND PRESSURED TO 17PSI (2:00 P.M.). ON 2/24/93, 9:45 A.M. TOWN INSPECTOR VERIFIED PRESSURED TEST 17PSI. NO LEAKS.
2025-01-31 10:21 | YES | NO | 19930066 | 1993-04-01 | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 110 MAIN ST | WELLSBURG | CHEMUNG | NY | 14894 | 3 | NO | 1547 | 1993-02-22 | 0 | 0 | 150000 | 114766.1243 | 277099.0703 | Null | 1 | 3 |  | 19930222 | 39 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5L-A25 | UNAVAILABLE | 1964 | 1964 | UNDER PAVEMENT |  | JAMES J PETRICK - SUPERVISOR CORP. GAS OPERATIONS | 6077624156 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON INDICATES THERE WAS EXCAVATION ACTIVITY IN THE VICINITY OF THE DAMAGED MAIN SEVERAL TIMES SINCE THE MAIN WAS INSTALLED.
2025-01-31 10:21 | YES | NO | 19930067 | 1993-04-08 | 14210 | OKLAHOMA NATURAL GAS CO | 3000 BLOCK ON SOUTH MEMORIAL DR | TULSA | TULSA | OK | 74129 | 3 | NO | 1418 | 1993-03-03 | 0 | 0 | 114000 | 87222.2545 | 210595.2934 | Null | 5 | 22 |  | 19930303 | 220 | 275 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.25 | EW X-42 | YOUNGSTOWN | 0 | 1959 | UNDER PAVEMENT |  | GERRY B LYNN - CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-09-23 | YES | 2 | PAINTED LINES | YES |  |  | A CONTRACTOR, WORKING FOR THE CITY OF TULSA, HIT OUR LINE WHILE MAKING A BORE FOR THE INSTALLATION OF A SEWER LINE. THE FIRST REQUEST TO LOCATED OUR FACILITIES WAS MADE ON SEPTEMBER 23, 1992, AND CONVERED WORK TO BE PERFORMED AT VARIOUS LOCATIONS IN A 20-BLOCK SECTION. THE CONSTRUCTION PLANS THAT WE RECEIVED IN 1989 DID NOT SHOW A CONSTRUCTION CONFLICT. CONSTRUCTION WAS ORIGINALLY SCHEDULED TO OCCUR WITHIN A 12-WEEK PERIOD; HOWEVER, THE BORE WAS NOT ATTEMPTED UNTIL MARCH 3, 1993. ONG WAS NOT MADE AWARE OF THE TIME FOR THE BORE DESPITE THE FACT THAT WE HAD REQUESTED THAT NOTIFICATION BE GIVEN DURING OUR LOCATION MEETINGS ON SEPTEMBER 28, 1992, SEPTEMBER 30, 1992, AND OCTOBER 1, 1992. OUR OPERATING PERSONNEL HAD BEEN MONITORING THE KNOWN CONSTRUCTION ACTIVITIES BUT HAD NOT BEEN NOTIFIED OF THE BORING OPERATION IN THIS PARTICULAR LOCATION. ACTUAL COST OF THE RELOCATION INCLUDING GAS LOSS HAS BEEN ESTIMATEDTO BE $114,000. HOWEVER, ACTUAL REPAIR COST COULD NOT BE DETERMINED SINCE REPAIR WITHOUT RELOCATION WAS IMPOSSIBLE. BECAUSE OF THE NEW SEWER BORE, WE WERE REQUIRED TO RELOCATE OUR LINE, WHICH WAS MORE EXPENSIVE THAN IF WE HAD ONLY BEEN REQUIRED TO REPAIR THE ACTUAL DAMAGE. IF ONLY THE REPAIR DAMAGE WAS CONSIDERED, THE TOTAL COST WOULD HAVE BEEN APPROXIMATELY $79,000.
2025-01-31 10:21 | YES | YES | 19930068 | 1993-03-15 | 9120 | JASONVILLE GAS UTILITY | 507 WEST WALNUT ST | JASONVILLE | GREENE | IN | 47438 | 2 | NO | 330 | 1993-03-04 | 0 | 2 | 10000 | 7651.075 | 18473.2714 | Null | 0 | 30 |  | 19930304 | 18 | 25 | BY TEST | 25 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 0 | 0 |  |  | 1962 | 1962 | UNDER PAVEMENT |  | BRUCE A BORDERS/MAYOR | 8126652266 | EXTERNALLY | OTHER | CRACK IN 2" CAST IRON MAI | OTHER | CRACK IN 2" CAST IRON MAI | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | APPROXIMATELY 5 FEET WEST IF SERVICE TAP, FRACTURE CRACK OCCURRED AROUND ENTURE OUTSIDE DIAMETER OF 2" CAST IRON MAIN. NO CAPTAN ODOR HAD BEEN NOTICED BY TONY 0R DANE HALITON, OR ANYONE ELSE IN THAT NEIGHBOURHOOD. ALSO, A HEAVY SNOW WAS ON THE GROUND JUST PRIOR TO THE EXPLOSION, SO NO SURFACE BUBBLES WERE OBSERVABLE PRIOR TO EXPLOSION. AFTER EXPLOSION, FIRE DEPT NOTICED GAS BUBBLES AT NORTH EDGE OF WALNUT STREET END SOME IN NORTH DITCH RUNNING ALONG STREET. THIS CAUSED UTILITY WORKERS TO DIG UP AROUND SERVICE TAP. NO PROBLEMS.DUG WESTWARD, WHICH LED TO DISCOVERY OF FRACTURE CRACK DESCRIBED ABOVE.
2025-01-31 10:21 | YES | YES | 19930069 | 1993-05-11 | 10037 | K P L GAS SERVICE | 311TH & HEDGE RD | PAOLA | MIAMI | KS | 66071 | 1 | NO | 1705 | 1993-04-07 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 31 |  | 19930407 | 90 | 90 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | BODY OF PIPE |  | STEEL |  | 2 | 0.216 | SDR11IPS |  | 0 | 1992 | ABOVE GROUND |  | HANS E MERTENS - VP - GAS ENGINEERING | 8163465575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | NO |  |  | ERSECTION OF 311TH AND HEDGE ROAD IN PAOLA, KANSAS. UPON IMPACT THE VEHICLEWERE DIVERTED FROM THE ROADWAY AND DAMAGED A BARRICADED DISTRICT REGULATOR STATION. AS A RESULT, THE STATION WAS TOTALLY DESTROYED AND ONE (1) OF THE PARTYS INVOLVED WAS HOSPITALIZED.
2025-01-31 10:21 | YES | NO | 19930070 | 1993-04-30 | 15476 | T W PHILLIPS GAS & OIL CO | SLATE LICK | SOUTH BUFFALO | ARMSTRONG | PA |  | 1 | NO | 1320 | 1993-04-01 | 0 | 0 | 200000 | 153021.4991 | 369465.4271 | Null | 0 | 25 |  | 19930401 | 22 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | REGULATOR STATION | VALVE | INSULATED FLANGE | STEEL |  | 3 | 0.216 |  |  | 0 | 1985 | ABOVE GROUND | REGULATOR BUILDING | KEITH A SWANTON - VP-OPER'S & ENG | 4122872751 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | LIGHTNING STRIKE AT OR NEAR REGULATOR STATION CREATED AN ENORMOUS SURGE OF ELECTRIC CURRENT WHICH ARCED ACROSS AN INSULATED FLANGE ON THE INLET SIDE OF THE MONITOR REGULATOR CAUSING THE GASKET TO BLOW OUT AND IGNITED ESCAPING GAS. THE INTENSE HEAT FROM THE FIRE INSIDE THE 6' X 8' METAL BUILDING DESTROYED THE DIAPHRAGMS IN BOTH THE WORKING AND MONITOR REGULATORS, ALLOWING THE INTERMEDIATE PRESSURE GAS AT 22 LBS. TO FEED DIRECTLY INTOT HE 8 OZ. LOW PRESSURE SYSTEM.
2025-01-31 10:21 | YES | YES | 19930072 | 1993-04-15 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 601 TEXAS AVE | SHREVEPORT | CADDO | LA | 71101 | 4 | NO | 1830 | 1993-04-01 | 0 | 1 | 1000 | 765.1075 | 1847.3271 | Null | 0 | 15 |  | 19930402 | 20 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | FURNACE | OTHER | GAS VALVE AT FURNACE | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RALPH W GREER, MGR LA REGION | 3184292526 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | I RESPONDED TO 601 TEXAS STREET, WHICH IS THE ADDRESS OF THE ROLEX CLUB LOCATED ON THE CORNER OF TEXAS AND MCNEILL. I RESPONDED TO A BUILDING FIRE, WHICH WAS REPORTED TO HAVE HAD A BURN VICTIM INVOLVED. UPON MY ARRIVAL, FIRE FIGHTERS SHOWED ME WHERE THE FIRE APPARENTLY ORIGINATED. THERE WAS A GAS HEATERLOCATED ABOVE THE ENTRANCE WAY OF THE NIGHTCLUB ON A LANDING. APPARENTLY, AFIRE HAD STARTED THERE AND SPREAD DOWN THE WEST SIDE WALL BURNING SOME BLACKTYPE PAPER THAT WAS OVER THE WINDOWS. THE VICTIM HAD BEEN BURNED IN THIS AREA AND FALLEN TO THE FLOOR. AFTER I THEN INVESTIGATED THE AREA WHERE I BELIEVE THE FIRE TO HAVE STARTED, I SAW THAT THERE WAS SOME FLASH-LIKE CHARRING ALL AROUND WHERE THE CUTOFF VALVE WAS LOCATED. THERE WAS SOME BURNT PAPER AND/OR RAGS IN THIS AREA. FIRE FIGHTERS STARTED THAT THE VICTIM IN THIS FIRE WASAPPARENTLY ATTEMPTING TO TURN THE GAS OFF. I THEN LEFT AND WENT TO LSU BURNCENTER TO TALK TO MR. ROBERT HALL, DATE OF BIRTH 9/13/52, WHO LIVES AT 2348 MARION STREET. MR. HALL STATED THAT HE WAS TRYING TO TURN THE GAS OFF, BECAUSE WHEN HE AND HIS COUSIN, ANGELA MAXIE ARRIVED AT THE CLUB, THE WHOLE BUILDING WAS FILLED WITH THE ODOR OF NATURAL GAS. HE STATED THAT THEY OPENED THE DOORS TO ALLEVIATE SOME OF THE GAS ODOR. AT THIS POINT, THEY HEARD A HISSING SSOUND COMING FROM THE AREA OF THE HEATER ABOVE THEE DOOR. HE THEN GOT A LADDER, PUT IT UP, AND WENT UP TO INVESTIGATE. HE SAW WHERE THE LEAK WAS COMING FROM, AND ASKED ANGELA TO THROW UP A WRENCH TO HIM. SHE DID, AND AS HE ATTEMPTED TO TURN THE VALVE OFF, A FLASH ENSUED AND BURNED HIM ABOUT THE FACE AND HANDS. I THEN QUESTIONED MS. ANGELA MAXIE, DATE OF BIRTH 12/28/67, WHO LIVESAT 2360 MARION STREET. SHE STATED BASICALLY THE SAME THING. SHE STATED THAT AS THEY WALKED INTO THE CLUB, THE STRONG ODOR OF NATURAL GAS COULD BE SMELLED. SHE STATED SHE THREW UP A WRENCH TO MR. HALL, AND AS HE WENT TO TURN THEVALVE OFF, A BIG FLASH OF FIRE OCCURRED. SHE STATED THAT HE FELL FROM THE LANDING, WHICH WAS APPROXIMATELY 10 TO 12 FEET HIGH FROM THE FLOOR. SHE THEN DOUSED HIM WITH WATER AND PATTED OUT THE FIRE AND THEN CALLED 911 TO GET HELP. THE NATURE OF THIS FIRE IS ACCIDENTAL, AND THE CAUSE IS A GAS LEAK, WHICH WAS POSSIBLY IGNITED BY THE ELECTRIC STARTED ON THE GAS POWERED HEATER IN THENIGHTCLUB. THIS CASE IS CLOSED. MR. ROBERT HALL WAS TAKEN TO LSU BURN UNIT WHERE HE IS NOW SUFFERING FROM FIRST AND SECOND DEGREE BURNS TO THE FACE AND HANDS. NONE OF THE INJURIES SEEM TO BE LIFE THREATENING AT THIS TIME.
2025-01-31 10:21 | YES | YES | 19930073 | 1993-04-26 | 15342 | PEOPLES GAS SYSTEM INC | INTERSECTION OF GRIFFIN RD/N FLORIDA AVE | LAKELAND | POLK | FL |  | 3 | NO | 1515 | 1993-04-03 | 0 | 1 | 0 | 0 | 0 | Null | 6 | 15 |  | 19930403 | 45 | 133 | BY TEST | 200 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4.5 | 0.125 |  |  | 0 | 1972 | UNDER GROUND OR UNDER WATER |  | DENNIS DIVITTORIO - DISTRICT SAFETY ENGINEER | 4074206619 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-01-07 | YES | 3 | YELLOW PAINT/GAS DISC MAR | YES |  |  | SUB-CONTRACTOR WORKING FOR CITY OF LAKELAND OPERATING A ROAD MIXER STRUCK A4" STEEL GAS MAIN CITY OF LAKELAND HAD REQUESTED A LOCATE IN JANUARY, AND COMPANY PERSONNEL LOCATED THE 4" STEEL MAIN. SUB-CONTRACTOR HAD NOT REQUESTED A LOCATE AT TIME OF INCIDENT.
2025-01-31 10:21 | NO | NO | 19930074 | 1993-04-26 | 2204 | CENTRAL ILLINOIS PUBLIC SERVICE | RT 57 SOUTH OF QUINCY | QUINCY | ADAMS | IL | 62301 | 1 | NO | 1009 | 1993-04-07 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 30 |  | 19930407 | 40 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | DUPONT | 1968 | 1968 | OTHER |  | DALE E VANCIL | 2173232173 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CREW WAS COMPLETING TEMPORARY BYPASS WHEN ESCAPING GAS IGNITED.SUPPLEMENTALREPORT 9/13/94 INDICATES THAT JULIE NOTICE FOR THIS LOCATION WAS CALLED IN11:02 AM ON 4/5/93 LOCATED AND MARKED 4/6/93.
2025-01-31 10:21 | YES | NO | 19930076 | 1993-04-20 | 18536 | SOUTHWEST GAS CORP | 6225 MEADOW VISTA | LAS VEGAS | CLARK | NV | 89103 | 3 | NO | 1047 | 1993-03-29 | 0 | 0 | 400000 | 306042.9983 | 738930.8542 | Null | 0 | 38 |  | 19930329 | 43 | 43 | BY TEST | 91 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | BELL & SPIGOT | OTHER | PVC PLASTIC 2116 | 2 | 0.154 | NATURAL GAS PIP | CELANESE | 0 | 1974 | UNDER PAVEMENT |  | LYNN A MALLOY SUPERVISOR/ENGINEERING | 7023652207 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-03-22 | YES | 3 | PAINT MARKINGS | YES |  |  | OPERATOR LOCATIONS MARKS WERE VERY ACCURATE.
2025-01-31 10:21 | YES | NO | 19930077 | 1993-03-02 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1585 PACIFIC COAST HWY | LAGUNA BEACH | ORANGE | CA |  | 3 | NO | 1118 | 1993-02-05 | 0 | 0 | 100000 | 76510.7496 | 184732.7135 | Null | 0 | 45 |  | 19930205 | 42 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY | REGULATOR | REGULATOR/METER |  | OTHER | NON SPECIFIED | 0.75 | 0 | S202 | FISHER | 1988 | 1988 | OTHER | WITHIN CURB METER BOX | G.J. LAMBETH - MANAGER OF SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A TRUCK DRIVER DROVE HIS VEHICLE UP ONTO A SIDEWALK TO PREVENT A COLLISION WITH ANOTHER VEHICLE. THE TRUCK RAN OVER A CURB METER BOX LOCATED IN THE SIDEWALK. THE WEIGHT OF THE TRUCK CRUSHED THE METER BOX AND DAMAGED THE METER SET ASSEMBLY INSIDE. THE DAMAGED REGULATOR ALLOWED HIGH PRESSURE GAS TO ENTER THE CUSTOMER'S HOUSELINE AND CAUSED NUMEROUS FIRES AT GAS APPLIANCES.
2025-01-31 10:21 | YES | NO | 19930078 | 1993-04-15 | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 31 CARMICHAEL RD | CHENANGO | BROOME | NY | 13901 | 3 | NO | 451 | 1993-03-14 | 0 | 0 | 75000 | 57383.0622 | 138549.5352 | Null | 0 | 54 |  | 19930315 | 18 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | VALVE | SCREW COUPLING | STEEL |  | 2 | 0.154 | API 56-A25 |  | 1937 | 1937 | UNDER PAVEMENT |  | ERIC W RHODES - STAFF ENGINEER | 6077624725 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 | DATA NOT AVAILABLE | YES |  |  | APPARENT OUTSIDE FORCE DAMAGED PIPE, DATE OF CONTACT UNKNOWN, OUR INVESTIGATION INDICATES THERE WAS EXCAVATION ACTIVITY IN THE VICINITY OF THE DAMAGED SCREW COLLAR IN THE FALL OF 1992 WHEN A SEWER LATERAL WAS INSTALLED TO 31 CARMICHAEL RD.
2025-01-31 10:21 | YES | YES | 19930079 | 1993-04-19 | 2700 | CONNECTICUT NATURAL GAS CORP | 1163 OLD CHURCH RD | GREENWICH | FAIRFIELD | CT | 06830 | 1 | NO | 948 | 1993-03-20 | 0 | 1 | 400000 | 306042.9983 | 738930.8542 | Null | 1 | 50 |  | 19930320 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0 |  |  | 0 | 1949 | UNDER GROUND OR UNDER WATER |  | ANTHONY C MIRABELLA VP DISTRIBUTION & ENGINEERING SERVICES | 2037273270 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | BACK FILL | NO |  | NO | 0 |  | NO |  |  | THE PIPE THAT FAILED WAS APPROXIMATELY 7 FEET UNDER THE SURFACE. THE PIPE WAS LOACTED IN THE VICINITY OF A SWIMMING POOL, RETAINING WALL AND A SUBSTANTIAL BACK FILL, MOST OF WHICH APPARENTLY WAS ADDED WITHIN THE LAST 3 YEARS. ITPRESENTLY APPEARS THAT THE PIPE SUFFERED A FRACTURE FAILURE (AS DISTINCT FROM A CORROSION FAILURE).
2025-01-31 10:21 | YES | YES | 19930080 | 1993-04-15 | 22476 | WESTERN KENTUCKY GAS CO | 539 SOUTH THIRD ST | PADUCAH | MCCRACKEN | KY | 42001 | 3 | NO | 2158 | 1993-03-14 | 1 | 1 | 160000 | 122417.1993 | 295572.3417 | Null | 0 | 17 |  | 19930315 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | DAMAGED METER SET | STEEL |  | 1.66 | 0.14 |  |  | 0 | 1954 | ABOVE GROUND |  | KEVIN AKERS - ENGINEER 1 | 5026858026 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ON 3/14/1993, WESTERN KENTUCKY GAS COMPANY (WKG) RECEIVED A CALL FROM THE MCCRACKEN COUNTY SHERIFF'S DEPARTMENT. THE SHERIFF'S DEPARTMENT DISPATCHER STATED THAT A CAR HAD STRUCK SOMETHING AND THERE WAS A GAS LEAK AT THE CORNER OFTHIRD STREET AND JACKSON STREET. WKG DISPATCHED THE ON-CALL SERVICEMAN FOR PADUCAH. HE ARRIVED AT THE SCENE AT 10:15 P.M. THERE WAS A FIRE AND DEBRIS AT THE NW CORNER OF THIRD STREET AND JACKSON STREET. HE WAS TOLD THAT A PICK-UP TRUCK HAD BEEN DRIVEN OFF THE ROAD AND THROUGH THE METER SET AND THE EXTERIOR WALL OF THE BUILDING. THE FIRE DEPARTMENT ADVISED USE THAT THE DRIVER OF THE PICK-UP TRUCK HAD BEEN KILLED AND THAT A FIREMAN HAD BEEN HURT. THE SCENE WAS SAFE. THE FIRE WAS CONSUMING THE GAS ESCAPING FROM THE BROKEN PIPINGOF THE METER SET. THE PADUCAH FIRE AND POLICE DEPARTMENTS WERE ON THE SCENE, AND HAD THE SITUATION UNDER CONTROL. A WKG SUPERVISOR WAS CALLED TO THE SCENE. THE SUPERVISOR CALLED OUT A CONSTRUCTION CREW. LOCAL AGENCIES WERE ATTEMPTING TO REMOVE THE PICK-UP TRUCK FROM THE REMAINS OF THE BUILDING. AFTERTHE PICK-UP WAS REMOVEDD, THE CREW USED A BACKHOE TO CLEAR RUBBLE FROM AROUND THE METER RISER AND THE SHUT-OFF VALVE WAS CLOSED AT 1:25 A.M. THIS INCIDENT WAS REPORTED TELEPHONICALLY TO MR. SCOTT SMITH, OF THE KPSC, AT APPROXIMATELY 12:30 A.M. CST, MARCH 15, 1993.
2025-01-31 10:21 | YES | NO | 19930081 | 1993-04-12 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 13480 KEYSTONE | DETROIT | WAYNE | MI |  | 3 | NO | 1230 | 1992-10-06 | 0 | 0 | 125000 | 97885.0729 | 236340.3211 | Null | 0 | 45 |  | 19921007 | 2 | 2 | BY TEST | 2 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | TEE MAIN | OTHER | COPPER | 1 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | BRUCE NIEMAN - MANAGER, CODES & CORROSION | 3132563290 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-09-30 | YES | 3 | PAINT | YES
2025-01-31 10:21 | YES | NO | 19930083 | 1993-04-05 | 13650 | NORTH PENN GAS CO | RD #1, BOX 494 | WELLSBORO | TIOGA | PA | 16901 | 1 | NO | 957 | 1993-04-14 | 0 | 0 | 80000 | 61208.5997 | 147786.1708 | Null | 0 | 0 |  | 19930414 | 25 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | SERVICE REGULATOR & METER | 0 | 0 |  | ROCKWELL | 1967 | 1971 | ABOVE GROUND |  | JAMES N SEWELL - ENGINEER | 8146422511 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INCIDENT INVOVLED A STRUCTURE FIRE OF UNKNOWN ORIGIN AT THE JOHN WASHINSKI RESIDENCE, LOCATED IN A RURAL AREA NEAR WHITNEYVILLE IN THE WELLSBORO DISTRICT, CHARLESTON TOWNSHIP, TIOGA COUNTY. NO ONE WAS HOME AT THE TIME AND THERE WERE NO FATALITIES OR REPORTED INJURIES, BUT PROPERTY DAMAGES EXCEEDED $50,000. NORTH PENN RESPONDENTS WITNESSED A FULLY INVOLVED STRUCTURE, WHICH APPEAREDD TO HAVE CONSUMED AND MELTED THE METER AND SERVICE REGULATOR. THE MELTED METER AND SERVICE REGULATOR CAUSED A RELEASE OF GAS, WHICH IN TURN WAS STOPPED BY SHUTTING THE WINGSTOP VALVE JUST AHEAD OF THE SERVICE REGULATOR. BASED ON THESE ONSERVATIONSS AND THE ABSENCE OF ANY DETECTABLE LEAKGE ON OTHER ADJACCENT FACILITIES, RESPONDENTS CONCLUDED THAT NORTH PENN FACILITIES NEITHER CASSED NOR CONTRIBUTED TO THIS INCIDENT. THE INCIDENT WAS REPORTATBLE BECAUSE THERE WAS A RELEASE OF GAS AND PROPERTY DAMAGE EXCEEDED $50,000.
2025-01-31 10:21 | YES | NO | 19930084 | 1993-05-25 | 1088 | BALTIMORE GAS & ELECTRIC CO | 9623 BASKET RING RD | COLUMBIA | HOWARD | MD | 21045 | 2 | NO | 935 | 1993-05-13 | 0 | 0 | 500000 | 382553.7478 | 923663.5677 | Null | 1 | 45 |  | 19930513 | 94 | 99 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE | 3 | OTHER | SERVICE RISER CUT WITH A | STEEL |  | 0.75 | 0.154 | AP15L |  | 1970 | 1971 | ABOVE GROUND |  | DENNIS C BLESSING - OPERATIONS ANALYST | 4105612700 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | AT APPOXIMATELY 0935, THURSDAY, MAY 13, 1993, DURING PLANNED WORK BY BG&E PELEAK ON CUSTOMER OWNED FUEL LINE INSIDE HOUSE.RSONNEL, A RELEASE OF GSS FROM A HIGH PRESSURE SERVICE RISER INTO THE UTILITYROOM AT THE REAR OF 9623 BASKET RING RD IN COLUMBIA, MARYLAND IGNITED AND AMINOR EXPLOSION OCCURRED WHICH CAUSED HEAVY FIRE DAMAGE TO THE STRUCTURE. CONSTRUCTION PROCEDURES WERE NOT FOLLOWED.
2025-01-31 10:21 | NO | NO | 19930085 | 1993-05-10 | 11800 | LOUISIANA GAS SERVICE CO | INTERSECTION OF HWY 90 & PEA RIDGE RD | ALBANY | LIVINGSTON | LA | 70711 | 2 | NO | 1602 | 1993-04-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 28 |  | 19930429 | 85 | 98 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | VALVE |  | STEEL |  | 2 | 0.154 | API-5L |  | 0 | 1955 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER - PIPELINE SAFETY ENGINEERR | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-04-20 | YES | 3 | PAINT | YES |  |  | CONTRACTOR INSTALLING SEWER LINE BROKE 2" GAS MAIN VALVE WITH BACKHOE.
2025-01-31 10:21 | YES | NO | 19930087 | 1993-05-20 | 18484 | SOUTHERN CALIFORNIA GAS CO | 4343 E LA PALMA AVENUE | ANAHEIM | ORANGE | CA | 92806 | 3 | NO | 1008 | 1993-04-23 | 0 | 0 | 70000 | 53557.5247 | 129312.8995 | Null | 1 | 7 |  | 19930423 | 44 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0 | ASTM-D1248 | DUPONT | 1983 | 1983 | UNDER PAVEMENT | 2 | G.J. LAMBERT - MGR OF SAFETY MANAGEMENT | 2132443480 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-02-17 | NO | 0 |  | YES |  |  | A BACKHOE OPERATOR WAS EXCAVATING A TRENCH TO INSTALL ELECTRICAL CONDUIT. THE BACKHOE BUCKET HIT AND RUPTURED THE PLASTIC MAIN, CAUSING GAS TO ESCAPE. APPROXIMATELY TWO MINUTES LATER, STATIC ELECTRICITY FROM OVERHEAD ELECTRICAL LINES, IGNITED THE ESCAPING GAS. THE RESULTING FIRE CAUSED DAMAGE TO THE PIPELINE, BACKHOE, AND OVERHEAD TELEPHONE, CABLE T.V. AND ELECTRICAL LINES.
2025-01-31 10:21 | YES | YES | 19930088 | 1993-05-20 | 22476 | WESTERN KENTUCKY GAS CO | 5TH STREET & CARTER RD | OWENSBORO | DAVIESS | KY | 42301 | 3 | NO | 118 | 1993-04-18 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 11 |  | 19930418 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | OTHER | NIPPLE | STEEL |  | 2 | 0.154 | SCHD. 40 |  | 0 | 1964 | ABOVE GROUND | 33 | DAVID H DOGGETTE | 5026858037 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | THE INCIDENT APPEARS TO HAVE OCCURRED WHEN A CAR, THAT WAS BEING PURSUED BY POLICE, LEFT THE ROAD AND STRUCK A 6-INCH STEEL PIPE BARRICADE FILLED WITH CONCRETE AND SET IN CONCRETE THAT WAS PROTECTING A DISTRICT REGULATOR STATION. AFTER STRIKING THE BARRICADE, THE CAR BECAME AIRBORNE AND DURING DESCENT STRUCK A NIPPLE ON THE STATION PIPING, THUS, CAUSING GAS TO BE RELEASED AND A SUBSEQUEBT IGNITION.
2025-01-31 10:21 | NO | NO | 19930091 | 1993-05-14 | 11800 | LOUISIANA GAS SERVICE CO | INTERS MEADOWBROOK BLVD. &MEADOWBROOK DR | MANDEVILLE | ST TAMMANY | LA | 70448 | 3 | NO | 957 | 1993-04-20 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 |  | 19930420 | 75 | 80 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTM D-2513 | PLEXCO PE 3408 | 1990 | 1992 | UNDER GROUND OR UNDER WATER |  | D L MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-04-16 | YES | 2 |  | YES |  |  | CONTRACTOR DAMAGED PLASTIC GAS MAIN WHILE REMOVING STUMPS WITH TRACKHOE.THE LOCATE WAS INCORRECT DUE TO A TELEPHONE CABLE CROSSING THE GAS MAIN.
2025-01-31 10:21 | NO | NO | 19930092 | 1993-05-14 | 11800 | LOUISIANA GAS SERVICE CO | INTERS. OF CLEVELAND & THIRD STR | SLIDELL | ST TAMMANY | LA | 70458 | 3 | NO | 1110 | 1993-04-20 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 50 |  | 19930420 | 70 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | WELD | GIRTH | STEEL |  | 2 | 0.154 | API-5L |  | 0 | 1949 | UNDER GROUND OR UNDER WATER |  | D.L. MERIWETHER - PIPELINE SAFETY ENGINEER | 5043677000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | WHILE LAYING DRAIN LINES, CONTRACTOR PULLED GAS MAIN AND BROKE IT IN A WELD.
2025-01-31 10:21 | YES | YES | 19930095 | 1993-06-21 | 15259 | PENNSYLVANIA GAS & WATER CO | #17 LESLIE DRIVE | SCRANTON | LACKAWANNA | PA | 18508 | 3 | NO | 1400 | 1993-06-10 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 5 |  | 19930614 | 25 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN | SERVICE LINE | VALVE | FITTING | STEEL |  | 4 | 0.237 | ASP-B36-10 |  | 0 | 1962 | UNDER PAVEMENT |  | JAMES M GREGER, MGR - SPECIAL PROGRAMS | 7178298866 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | B" LEAK ON EXISTING FOUR-INCH (4") STEEL GAS MAIN. TWO (2) APPARENT LEAKS WERE VISIBLE AFTER EXCAVATION; 90 DEGREES ELBOW GOING FROM THE SERVICE TEE, AND THE OTHER, A PINHOLE AT 4:00 ON THE BOTTOM OF THE PIPE. CONTRACTOR WAS CLEANING WITH POWER CLEANER AROUND THE PIPE TO ALLOW PROPER FITTING OF A MECHANICAL FITTING. APPARENT SPARK CAUSED IGNITION AND FLASH.
2025-01-31 10:21 | YES | NO | 19930097 | 1993-06-15 | 4483 | ENSTAR NATURAL GAS CO | 22626 NORTH SHORE DR | CHUGIAK |  | AL | 99567 | 3 | NO | 1220 | 1993-05-27 | 0 | 0 | 250000 | 191276.8739 | 461831.7838 | Null | 1 | 5 |  | 19930527 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M 8000 | PHILLIPS DRISCOPIPE | 1979 | 1979 | ABOVE GROUND |  | DAVID W. BREDIN - MGR DISTRIBUTION OPERATIONS | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A STRUCTURE FIRE OF UNKNOWN ORIGIN SEVERLY DAMAGED THE HOUSE, GARAGE AND A VEHICLE PARK INSIDE THE GARAGE AT 22626 NORTH SHORE DRIVE, CHUGIAK, ALASKA. THE HOUSE WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICELINE OPERATING AT APPROXIMATELY 55 PSIG. WHERE THE SERVICE LINE CAME ABOVE FGROUND, IT DID SO THROUGH A RIGID STEEL RISER. HEAT FROM THE FIRE MELTED THE 5/8" PLASTIC TUBING INSIDE THE STEEL RISER, CAUSING A RELEASE OF GAS. THE GAS WAS SHUT OFF BY DIGGING UP THE SERVICE LINE A SAFE DISTANCE FROM THE FIREAND INSTALLING A PINCHER ON THE SERVICE LINE.
2025-01-31 10:21 | NO | NO | 19930098 | 1993-06-15 | 4483 | ENSTAR NATURAL GAS CO | 520 W THIRD AVE | ANCHORAGE |  | AK | 99501 | 3 | NO | 12 | 1993-05-21 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 1 | 13 |  | 19930521 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER | RISER | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | M 8000 | PHILLIPS DRISCOPIPE | 1984 | 1984 | ABOVE GROUND |  | DAVID W BREDIN - MGR DISTRIBUTION OPERATIONS | 9072642645 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A FIRE, CLASSIFIED AS ARSON BY THE ANCHORAGE FIRE DEPARTMENT, WAS STARTED INA DUMPSTER DIRECTLY ADJACENT TO ENSTAR'S METER SET ASSEMBLY (MSA). THE MSA WAS FED BY 55 PSIG GAS THROUGH A 7/8" NPS, POLYETHYLENE SERVICE LINE. WHERE THE SERVICE LINE CAME ABOVE GROUND, IT DID SO THROUGH A RIGID STEEL RISER. HEAT FROM THE FIRE CAUSED THE 7/8" PLASTIC TUBING INSIDE THE RISER TO MELT, RELEASING NATURAL GAS TO THE ATMOSPHERE. THE GAS IGNITED AND ENGULFED THE MSA. THE GAS WAS SHUT OFF BY INSTALLING A PINCHER ON THE RISER AT GROUND LEVEL. THE SERVICE LINE WAS ABANDONED AT THE TEE WHERE IT TIED INTO THE MAIN.
2025-01-31 10:21 | NO | NO | 19930100 | 1993-06-08 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | FORD MOTOR COMPANY - ROUGE PLANT | DEARBORN | WAYNE | MI | 48120 | 0 | NO | 1215 | 1993-05-03 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19930503 | 145 | 300 | BY TEST | 450 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | GATE STATION | OTHER | HUMAN ERROR | OTHER | NON SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | MICHEAL F SUCHARSKI | 3132566596 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | SUPPLY TO LARGE INDUSTRIAL CUSTOMER WAS INTERRUPTED DURING A SUPPLY CHANGE-OVER PROCEDURE. HUMAN ERRORS IN DEVELOPING AND EXECUTING THE CHANGE-OVER CAUSED THE SUPPLY INTERRUPTION.
2025-01-31 10:21 | YES | NO | 19930108 | 1993-07-16 | 22777 | WISCONSIN NATURAL GAS CO | 1108 CARROLL AVE | SOUTH MILWAUKEE | MILWAUKEE | WI | 53172 | 3 | NO | 40 | 1993-06-12 | 0 | 0 | 1000000 | 765107.4956 | 1847327.1354 | Null | 1 | 20 |  | 19930612 | 3030 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING | PIPE NIPPLE | STEEL |  | 1.25 | 0.189 | API5L |  | 0 | 1972 | ABOVE GROUND |  | SHELDON B. SEPSTEAD | 4146377681 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | METER SET ASSEMBLY WAS STRUCK BY MOTOR VEHICLE. LEAK OCCURRED AT OR NEAR DAMAGED PIPE NIPPLE. FIRE STARTED IMMEDIATELY AND INVOLVED ENTIRE BUILDING WITHIN SEVERAL MINUTES.
2025-01-31 10:21 | YES | NO | 19930111 | 1993-07-16 | 22182 | WASHINGTON GAS LIGHT CO | 19211 WATKINS MILL RD | GAITHERSBURG | MONTGOMERY | MD | 20879 | 3 | NO | 2332 | 1993-06-15 | 0 | 0 | 1000000 | 765107.4956 | 1847327.1354 | Null | 0 | 56 |  | 19930616 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | NON SPECIFIED | BODY OF PIPE |  | OTHER | NON SPECIFIED | 2 | 0.216 | PE 2406 | DUPONT | 1989 | 1989 | ABOVE GROUND |  | JOHN C SHEA | 7037504583 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | UNKNOWN ARSONIST STARTED A FIRE UNDER THE 2" NONCORRODIBLE RISER TO 19211 WATKINS MILL ROAD. THE FIRE CREATED SUFFICIENT HEAT TO MELT THE FACTORY INSERTED PLASTIC PIPE CREATING A HIGH PRESSURE LEAK UNDERGROUND. UNDER THE SURFACETHERE WAS AN OPEN PIPE CHASE THAT RAN FROM THE GIANT FOOD STORE INTO THE GRAPE & GRAIN LIQUOR STORE 19211 & 19223 WATKINS MILL ROAD. THE HIGH PRESSURE GAS TRAVELED THROUGH THIS OPEN PIPE CHASE, EVENTUALLY REACHING AN EXPLOSIVE MIXTURE IN 19219 WATKINS MILL ROAD SETTING OFF A DOMINO OF EXPLOSIONS BACK TO THE SOURCE AT 19211 WATKINS MILL ROAD. THE INCIDENT INJURED SEVEN FIREFIGHTERS AND THREE WASHINGTON GAS EMPLOYEES, ALL INJURED PARTIES WERE TREATED AND RELEASED.
2025-01-31 10:21 | YES | NO | 19930113 | 1993-07-07 | 14210 | OKLAHOMA NATURAL GAS CO | 4323 EAST 101 ST | TULSA | TULSA | OK | 74137 | 3 | NO | 2245 | 1993-06-09 | 0 | 0 | 150000 | 114766.1243 | 277099.0703 | Null | 0 | 20 |  | 19930610 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | METER RISER AND CUSTOMER | DRIP/RISER |  | STEEL |  | 1 | 0.133 |  | CENTRAL | 1973 | 1973 | UNDER GROUND OR UNDER WATER |  | GERRY B LYNN | 9185887600 | [6 empty] | Null |  | LIGHTNING OR FIRE | 7200-VOLT FALLEN POWER LI | NO |  | NO | 0 |  | NO |  |  | STRAY ELECTRICAL CURRENT CAUSED ADJOINING HOLES IN THE MEDIUM-PRESSURE METERRISER AND THE CUSTOMER'S LOW-PRESSURE SERVICE LINE AT THE CUSTOMER'S PROPERTY LINE. GAS LINES ARE USUALLY SEPARATED BY A DISTANCE OF AT LEAST ONE FOOT; HOWEVER, IN THIS INCIDENT THEY WERE IN CONTACT WITH EACH OTHER UNDERGROUND. THE CUSTOMER PIPING COULD HAVE BEEN MOVED TO ALLOW ROOM FOR CONSTRUCTION OF APRIVACY FENCE. NO DEFINITE REASON FOR THE PIPE ROUTING COULD BE DETERMINED.MEDIUM-PRESSURE GAS FROM THE SERVICE RISER ENTERED THE LOW-PRESSURE CUSTOMERSERVICE LINE AND OVERPRESSURED THE LOW-PRESSURE SYSTEM. CUSTOMER'S FURNACE CONTROL VALVE RUPTURED AND THE ESCAPING GAS IGNITED RESULTING IN A FIRE. THESTRAY CURRENT WAS EITHER FROM FALLEN POWER LINES BLOWN DOWN DURING A STORM OF FROM LIGHTNING FROM THE STORM.
2025-01-31 10:21 | NO | NO | 19930115 | 1993-06-29 | 4483 | ENSTAR NATURAL GAS CO | 901 W 53 AVE | ANCHORAGE |  | AK | 99502 | 3 | NO | 155 | 1993-06-17 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 50 |  | 19930617 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M3000 | PHILLIPS DRISCOPIPE | 1977 | 1977 | ABOVE GROUND |  | DVAID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A STRUCTURE FIRE, CLASSIFIED AS ARSON BY THE ANCHORAGE FIRE DEPARTMENT, SEVERLY DAMAGED THE HOUSE LOCATED AT 901 W. 53RD AVE, ANCHORAGE, ALASKA. THE HOUSE WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICE LINE OPERATING AT APPROXIMATELY 55 PSIG. WHERE THE SERVICE LINE CAME ABOVE GROUND, IT DID SO THROUGH A RIGID STEEL RISER. THE HOUSE WAS EXTENSIVELY DESTROYEDAND HEAT FROM THE FIRE MELTED THE 5/8" PLASTIC TUBING INSIDE THE STEEL RISER, CAUSING A SMALL RELEASE OF GAS. THE GAS DID NOT IGNITE AND WAS SHUT OFF BYDIGGING UP THE THE SERVICE LINE A SAFE DISTANCE FROM THE FIRE AND INSTALLINGA PINCHER ON THE SERVICE LINE. NATURAL GAS DID NOT CONTRIBUTE TO THE CAUSE OF THIS FIRE AND HAD LITTLE IMPACT ON THE FIRE. IT IS QUESTIONABLE AS TO WHETHER THIS SHOULD BE SUBMITTED AS AN "INCIDENT".
2025-01-31 10:21 | NO | NO | 19930116 | 1993-06-29 | 4060 | EAST OHIO GAS CO | 96 CUYAHOGA STREET | AKRON | SUMMIT | OH | 44304 | 3 | NO | 728 | 1993-05-22 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 39 |  | 19930522 | 6.5 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | PAUL E OLEKSA | 2167366858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AN UNDERAGED JUVENILE USED ANOTHER PERSON'S AUTOMOBILE AND LEFT THE PREMISESAT 96 CUYAHOGA STREET IN AKRON, OHIO. UPON ENTERING CUYAHOGA STREET, THIS PERSON MADE A LEFT HAND TUNR BUT NEVER PULLED OUT OF THE TURN. THIS MOVEMENT BROUGHT HIM BACK TO A CONCRETE BLOCK BUILDING THAT HOUSED A BAR AND LOUNGE THAT HE HAD JUST LEFT. THE AUTOMOBILE WAS DRIVEN THROUGH THE BUSHES, JUST MISSING THE SIGN FOR C.J.'C BAR NAD LOUNGE, BUT HITTING THE EAST OHIO GAS COMPANYMETER AND THE BUILDING WALL. A FIRE STARTED AND WAS FED BY THE BLOWING LOW PRESSURE NATURAL GAS SERVICE LINE RISER. WHEN THE FIRE DEPARTMENT ARRIVE, THEY SHUT THE GAS OFF AT THE CURB BOX AND EXTINGUISHED THE FIRE. LATER THAT DAYTHE COSNTRUCTION AND MAINTENANCE DEPARTMENT FROM THE EAST OHIO GAS COMPANY DISCONNECTED THE 1-1/2" STEEL SERVICE LINE FROM THE 4" STEEL MAIN LINE AND TESTED THE SERVICE. THE 1 - 1/2" STEEL SERVICE LINE TESTED GOOD.
2025-01-31 10:21 | YES | YES | 19930118 | 1993-07-01 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 1359 PYLE ST | SOUTH BEND | ST JOSEPH | IN | 46615 | 3 | NO | 1400 | 1993-06-17 | 1 | 2 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 43 |  | 19930617 | 35 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1954 | UNDER GROUND OR UNDER WATER |  | KENNETH FOLEY | 2188535603 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-06-07 | YES | 2 | PAINT | YES |  |  | AN EXCAVATOR STRUCK A MARKED RESIDENTIAL SERVICE LINE, PULLING APART A COMPRESSION FITTING, WHICH ALLOWED THE UNDERGROUND RELEASE OF NATURAL GAS. THIS GAS MIGRATED INTO THE RESIDENCE, WHCIH WAS ULTIMATELY DAMAGE.
2025-01-31 10:21 | YES | YES | 19930119 | 1993-07-13 | 15259 | PENNSYLVANIA GAS & WATER CO | 18 SOUTH MARKET ST | NANTICOKE | LUZERNE | PA | 18634 | 4 | NO | 1020 | 1993-06-28 | 0 | 3 | 500000 | 382553.7478 | 923663.5677 | Null | 1 | 7 |  | 19930628 | 51 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 1 | 0.133 | SCHED. 40 |  | 0 | 1970 | UNDER PAVEMENT |  | JAMES M GREGER | 7178298866 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | IN RESPONSE TO A CUSTOMER'S REQUEST TO RAISE A WATER VALVE BOX LOCATED IN PARKING LOT THAT WAS SCHEDULED FOR REPAVING, PENNSYLVANIA GAS AND WATER COMPANYDISPATCHED A CREW TO 18 MARKET STREET, NANTICOKE, ON MONDAY, JUNE 28, 1993.THE CREW LOCATED THE WATER BOX AND BEGAN WORKING ON WHAT CLEARLY APPEARED TOBE A WATER APPURTENANCE AT 8:30 A.M. UPON ATTEMPTING TO REMOVE A PLUG FROMWHAT APPEARED TO BE A WATER CURB BOX STANDPIPE LOCATED INSIDE THE STREET BOXWHICH WAS CLEARLY MARKED "WATER" FOR THE PURPOSE OF EXTENDING THE PIPE TO REACH THE INTENDED NEW GRADE, THE EMPLOYEE DISCOVERED THAT THE WHOLE PIPE TURNED AND IMMEDIATELY HEARD AND SMELLED ESCAPING GAS. IMMEDIATE EFFORT BEGAN TO EXCAVATE THE CONCEALED GAS FACILITY WHILE ADDITIONAL HELP WAS SUMMONED AND MEASUREMENTS FOR THE CURB VALVE HAD BEEN BURIED UNDER A CONCRETE DRIVEWAY. AMID EFFORTS TO UNCOVER THE LEAK, EVACUATE THE PREMISES, AND DETERMINE THE MIGRATION OF THE GAS, THE BUILDING EXPLODED AT 10:20 A.M.
2025-01-31 10:21 | YES | NO | 19930122 | 1993-07-19 | 5330 | FLORIDA PUBLIC UTILITIES CO | 1330 NORTH LAKE WAY | PALM BEACH | PALM BEACH | FL | 33480 | 3 | NO | 2036 | 1993-06-27 | 0 | 0 | 1500000 | 1147661.2435 | 2770990.7031 | Null | 3 | 20 |  | 19930628 | 18 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1950 | UNDER GROUND OR UNDER WATER |  | GEORGE SIMS - DIVISION OPERATIONS MANAGER | 4078381802 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | INVESTIGATION TO DATE REVEALS THAT A THREE INCH, THREE PHASE ELECTRICAL CONDUIT SERVING THIS RESIDENCE WAS INSTALLED DIAGONALLY ACROSS AND IN DIRECT CONTACT WITH THE TOP OF AN EXISTING ONE INCH GAS SERVICE LINE. A HIGH VOLTAGE ELECTRICAL SURGE, EITHER FROM LIGHTNING OR AN UNKNOWN SOURCE, CAUSED AN ELECTRICAL CURRENT TO ARC FROM THE CONDUIT TO THE GAS SERVICE LINE, WHICH FUSED THE TWO LINES TOGHETHER AND CREATED A HOLE, APPROXIMATELY THREE FOURTH OF AN INCH IN DIAMETER, IN BOTH PIPES. GAS ENTERED THE HOUSE VIA THE ELECTRICAL CONDUIT FILLING THE HOUSE WITH GAS UNTIL IT WAS IGNITED FROM AN UNKNOWN SOURCE. THEREWAS NO EVIDENCE OF UNDERGROUND GAS LEAKAGE PRIOR TO THE ELECTRICAL CONDUIT AND GAS SERVICE LINE BEING FORCEDLY SEPARATED.
2025-01-31 10:21 | YES | YES | 19930125 | 1993-08-06 | 8270 | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO | 0158 EAST HIGH STREET, UNIT 9 | ROCKWELL CITY | CALHOUN | IA | 50579 | 0 | NO | 915 | 1993-06-28 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19930628 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT DETERMINED | OTHER | NOT DETERMINED | OTHER | NOT DETERMINED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SANDRA RASMUSSEN - GAS STANDARDS ENGINEER | 7122777928 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19930126 | 1993-08-06 | 18536 | SOUTHWEST GAS CORP | CENTRAL AND ADAMS | PHOENIX | MARICOPA | AZ | 85004 | 4 | NO | 900 | 1993-07-15 | 0 | 0 | 50600 | 38714.4393 | 93474.7531 | Null | 1 | 25 |  | 19930716 | 55 | 55 |  | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 |  |  | 1934 | 1934 | UNDER PAVEMENT |  | PHILLIP S. ANDREW - MANAGER/ENGINEERING | 6024845218 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1990 | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EIGHT INCH (8") X .250" W.T. STEEL MAIN WAS BEING UPRATED TO SUPPLY ADDITIONAL SYSTEM CAPACITY. ON THE FINAL STEP OF THE URATING (55 PSIG), A CORROSION PIT FAILED, CAUSING TWO BUILDINGS TO BE EVACUTATED. THE MAIN WAS REPLACED BY INSERTION OF A FOUR INCH (4") HIGH DENSITY POLYETHYLENE INTO THE EXISTING EIGHT INCH (8") STEEL MAIN. THE PERMANENT REPAIR COSTS WERE NOT DETERMINED ON JULY 15, 1993. THESE COST WERE ESTIMATED EARLY JULY 16, 1993, AND WHEN THE $50,000 THRESHOLD WAS EXCEEDED, TELEPHONIC NOTIFICATION TO DOT WAS MADE.
2025-01-31 10:21 | YES | YES | 19930127 | 1993-08-02 | 13782 | NORTHERN STATES POWER CO | 679-681 E. THIRD STREET | ST. PAUL | RAMSEY | MN | 55106 | 3 | NO | 843 | 1993-07-22 | 3 | 11 | 1000000 | 765107.4956 | 1847327.1354 | Null | 1 | 39 |  | 19930722 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC | 3 | 1.25 | 0.166 | ASTM D2513 | DUPONT | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | DANIEL J. WOEHRLE - SENIOR GAS ENGINEER | 6122292211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-07-16 | YES | 3 | PAINT | YES |  |  | ON THURSDAY, JULY 22, 1993, AN EXPLOSION AND FIRE OCCURRED AT THE SUBJECT ADDRESS. NSP REPORTED THIS INCIDENT TO YOUR OFFICE ( MR. BRUYERE) THIS SAME DAY.THE EXPLOSION AND ENSUING FIRE INVOLVED NATURAL GAS AND RESULTED IN FATALITIES, IN-PATIENT HOSPITALIZATION, AND DAMAGES IN EXCESS OF $50,000 AND MEETS US-DOT REPORTING CRITERIA FOR INCIDENTS. ATTACHED IS A COPY OF THE INCIDENT REPORT - GAS DISTRIBUTION SYSTEM ( FORM RSPA F7100.1) THIS REPORT IS BASED UPON INITIAL INFORMATION AVAILABLE DURING THE INVESTIGATION SHOULD ADDITIONAL INFORMATION BECOME AVAILABLE, A SUPPLEMENTARY REPORT WILL BE SUBMITTED.
2025-01-31 10:21 | NO | NO | 19930128 | 1993-07-23 | 15469 | PHILADELPHIA GAS WORKS | 418 W. BERKS STREET | PHILADELPHIA | PHILADELPHIA | PA | 19122 | 0 | NO | 1910 | 1993-07-15 | 0 | 0 | 14405 | 11021.3735 | 26610.7474 | Null | 1 | 5 |  | 19930716 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1968 | UNDER PAVEMENT |  | JOSEPH M. CAREY - MANAGER DISTRIBUTION DEPT. | 2156846372 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | NO | 19930129 | 1993-08-24 | 11680 | LONE STAR GAS CO | 104 E. PARSONAGE | WINTERS | RUNNELS | TX |  | 3 | NO | 1455 | 1993-07-28 | 0 | 0 | 100000 | 76510.7496 | 184732.7135 | Null | 1 | 45 |  | 19930728 | 14 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | 3306 | NIPAK | 0 | 1971 | UNDER PAVEMENT |  | PHILLIP MURDOCK - DIRECTOR | 2146702229 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19930131 | 1993-08-23 | 2392 | CITIZENS GAS & COKE UTILITY | 5243 NORWALDO AVENUE | INDIANAPOLIS | MARION | IN | 46220 | 3 | NO | 745 | 1993-08-08 | 0 | 0 | 100000 | 76510.7496 | 184732.7135 | YES | 1 | 37 |  | 19930808 | 0.25 | 0.33 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER HOUSE LINE | OTHER | UNION DISCONNECTED | STEEL |  | 1 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | EARLE D. STEVENSON - DIRECTOR OF DISTRIBUTION | 3179274626 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON AUGHUST 8, 1993 WE RECEIVED A CALL FROM INDIANAPOLIS FIRE DEPARTMENT AT 7:53 AM REPORTING A WORKING FIRE AND EXPLOSION AT 5218 NORWALDO AVENUE. WHEN WE ARRIVED ON THE SCENE THE HOUSE AT 5243 NORWALDO AVENUE HAS BEEN DESTROYED. MS. LESLEY WILLIAMS, AGE 32, HAD BEEN INJURED AND TAKEN TO METHODIST HOSPITAL. THE GAS SERVICE LINE TO THIS ADDRESS WAH SHUT OFF. ADJACENT HOUSES WERE CHECKED FOR INDICATION OF GAS, NO READINGS WERE DETECTED. THE SERVICE LINE TO THE ADDRESS WAS PRESSURE TESTED, NO LEAKS FOUND. THE MAIN IN FRONT OF THE HOUSEWAS BAR TESTED AT 10 FOOT INTERNALS AND 100 FEET EITHER SIDE OF THE ADDRESS,NO LEAKS FOUND. ARSON INVESTIGATORS FOUND, ON THE GAS LINE GOING TO THE WATER HEATER, A UNION WAS DISCONNECTED.
2025-01-31 10:21 | YES | YES | 19930134 | 1993-07-19 | 18532 | SOUTHERN UNION GAS CO | 1149 WALNUT STREET | EL PASO | EL PASO | TX | 79976 | 4 | NO | 2140 | 1993-07-02 | 0 | 4 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 15 |  | 19930702 | 25 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S SYSTEM | OTHER | NOT SPECIFIED | OTHER | NOT SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN M. WILLIS - REGIONAL OPERATIONS MANAGER | 9155214654 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | SOUTHERN UNION GAS COMPANY'S INVOLVEMENT WAS STRICTLY T ASSIST THE FIRE MARSHALL WITH THE INVESTIGATION. NO DETERMINATION HAS BEEN MADE AS TO THE LOCATION OF THE GAS ACCUMULATION OR THE SOURCE OR IGNITION.
2025-01-31 10:21 | YES | YES | 19930135 | 1993-07-28 | 22182 | WASHINGTON GAS LIGHT CO | PENNSYLVANIA AVE & 30 STREET , SE | WASHINGTON |  | DC | 20020 | 3 | NO | 1649 | 1993-06-28 | 1 | 2 | 0 | 0 | 0 | Null | 1 | 19 |  | 19930629 | 20 | 25 |  | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.48 | CLASS 150 | UNKNOWN | 1941 | 1941 | UNDER GROUND OR UNDER WATER |  | WM. A. HINDE - SAFETY SUPERVISOR | 7037507687 | EXTERNALLY | OTHER | LOCALIZED GRAPHITIZATION | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JUNE 28,1993, AT APPROXIMATELY 1649 HOURS, A 12" CAST IRON MAIN FAILED DUE TO GRAPHITIZATION AT THE INTERSECTION OF PENNSYLVANIA AVENUE AT 30TH STREET, SE, WASHINGTON. THE ESCAPING GAS FOUND AN IGNITION SOURCE AND ENGULFED THEINTERSECTION IN FIRE, INJURING FIVE CIVILIANS. ONE OF THE CIVILIANS SUCCUMBEDTO THEIR INJURIES. WASHINGTON GAS RECEIVED NOTICE OF THE INCIDENT FROM THE DISTRICT OF COLUMBIA FIRE DEPARTMENT. WASHINGTON GAS UTILIZED ITS SECTION SHUTDOWN AND MADE SAFE IN ONE HOUR AND NINETEEN MINUTES. THE NATIONAL TRANSPORTATION SAFETY BOARD AND WASHINGTON GAS ARE CONTINUING THE IVESTIGATION INTO THIS
2025-01-31 10:21 | YES | NO | 19930136 | 1993-08-23 | 6920 | GULF STATES UTILITIES CO | S.E. CORNER GOODWOOD BLVD & BRAEBURN | BATON ROUGE | EAST BATON ROUGE | LA |  | 2 | NO | 830 | 1993-07-20 | 0 | 0 | 250000 | 191276.8739 | 461831.7838 | Null | 1 | 40 |  | 19930723 | 25 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT SPECIFIED | STEEL |  | 4 | 0 |  |  | 0 | 1964 | UNDER PAVEMENT |  | ROBERT A. BORNE - ENGR. SECTION HEAD | 5043795208 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-05-27 | YES | 3 | PAINT | YES |  |  | THE CITY OF BATON ROUGE INITIATED A MAJOR STREET RE-BUILDING PROGRAM IN 1990.TO DATE, THERE HAS BEEN MAJOR RE-WORK OF 409 MILES OF CITY STREETS. THE WORKIS BEING PERFORMED BY MULTIPLE CONTRACTORS AND PROJECTS ARE SCATTERED THROUGHOUT THE CITY. AT 8:30 A.M. ON JULY 20, 1993, GSU RECEIVED A CALL FROM THE LOCAL EMERGENCY OPERATIONS STATING THERE WAS A NATURAL GAS FIRE AT THE INTERSECTION OF GOODWOOD BOULEVARD AND BRAEBURN STREET INVOLVING A BROKEN GAS LINE. GSU DISPATCHED SEVERAL CREWS AND SUPERVISORS TO THE SITE AND FOUND THAT THE STREET WORK CONTRACTOR HAD DUG INTO GSU'S FOUR-INCH GAS MAIN WITH A CATERPILLAR250 ROAD RECLAIMER. THE MACHINE'S ENGINE HAD IGNITED THE ESCAPING GAS AND MACHINE TO BURN. THERE WERE NO INJURIES AND THE FIRE WAS CONTAINED BY THE FIRE DEPARTMENT. GSU PERSONNEL BEGAN TO CUT OFF THE GAS SUPPLY TO THE SITE AND BY 9:45 A.M. THE MAIN AND ALL BACKFEEDS HAD BEEN CLOSED. BY 10:00 A.M. THE FIRE HAD BEEN EXTINGUISHED. GSU GEGAN REPAIRS TO THE GAS MAIN AND CUSTOMER SERVICES' WERE RESTORED BY 10:00 P.M. ON JULY 20,1993. THE GAS MAIN HAD BEEN SURFACELOCATED BY GSU FOR THE CONTRACTOR ON MAY 29,1993. THE CONTRACTOR DID NOT DIGPILOT HOLES TO DETERMINE PIPE DEPTH AFTER REMOVAL OF THE ASPALT AND THE CONTRACTOR DID NOT NOTIFY GSU THAT HE WAS DIGGING AT THIS LOCATION. GSU'S PREVIOUS LOCATE INDICATED THE GAS MAIN HAD SUFFICIENT DEPTH BELOW THE BOTTOM OF TH CURB. DEPTH CONTROL OF THE RECLAIMER CUT IS CRITICAL IN PROTECTION OF THE EXISTING UNDERGROUND FACILITIES OF ALL UTILITIES IN THE CONSTRUCTION AREA. THIS WAS NOT ACHIEVED BY THE CONTRACTOR IN THIS PARTICULAR INCIDENT.
2025-01-31 10:21 | YES | YES | 19930137 | 1993-08-20 | 18536 | SOUTHWEST GAS CORP | 2067 N. LAS VEGAS BLVD SPACE 60 & 61 | LAS VEGAS | CLARK | NV |  | 3 | NO | 416 | 1993-07-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 49 |  | 19930723 | 43 | 43 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 2 | 0.111 | SCHEDULE A | LINK | 0 | 1964 | UNDER GROUND OR UNDER WATER |  | LYNN A. MALLOY - SUPERVISOR/ENGINEERING | 7023652207 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JULY 23, 1993, AT APPROXIMATELY 0416 HOURS, SOUTHWEST GAS CORPORATION (SOUTHWEST) WAS NOTIFIED BY THE NORTH LAS VEGAS FIRE DEPARTMENT OF A FIRE AT A MOBILE HOME COMMUNITY AT 2067 NORTH LAS VEGAS BOULEVARD. SOUTHWEST IMMEDIATELYDISPATCHED EMERGENCY CREWS TO THE SCENE WHERE THEY OBSERVED TWO (2) MOBILE HOMES LOCATED AT SPACE #62 DAMAGED BEYOND REPAIR, AND ONE VEHICLED DESTROYED. TWO (2) INDIVIDUALS WERE SENT TO THE HOSPITAL AND TREATED, ONE FOR FIRST AND SECOND DEGREE BURNS AND KEPT OVERNIGHT, THE OTHER FOR ANXIETY AND RELEASED. FIRE, POLICE, AND MEDIA PERSONNEL WERE ALSO ON SITE. THE GAS FLOW WAS CONTROLLED BY CLOSING A VALVE AT THE ENTRANCE TO THE MOBILE HOME COMMUNITY AT APPROXIMATELY 0505 HOURS. AFTER THE AREA WAS MADE SAFE, IT WAS DETERMINED THAT A 2-INCH POLYVINYL CHLORIDE (PVC MAIN HAD FAILED NEAR THE POINT OF CONNECTION TO ADRESSER COUPLING. A REVIEW OF THE TOTAL PROPERTY DAMAGES WAS MADE AND IS ESTIMATED TO BE $40,000. APPROXIMATELY FIVE (5) FEET OF PIPE INCLUDING THE DRESSER COUPLING WAS REPLACED WITH 2-INCH POLYETHYLENE (PE) PIPE. A PRESSURE TEST WAS PERFORMED PRIOR TO RESTORING SERVICE TO THE MOBILE HOME COMMUNITY AT 1915
2025-01-31 10:21 | YES | YES | 19930139 | 1993-08-30 | 18536 | SOUTHWEST GAS CORP | 2962 WEST THOMAS ROAD | PHOENIX | MARICOPA | AZ | 85017 | 3 | NO | 816 | 1993-08-05 | 1 | 3 | 800000 | 612085.9965 | 1477861.7083 | Null | 0 | 5 |  | 19930805 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.125 | 3306PE |  | 1973 | 1973 | UNDER PAVEMENT |  | PHILLIP S. ANDREW - MANAGER ENGINEERING - CAD | 6024845222 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A LONGITUDINAL CRACK OF APPROXIMATELY 1-1/2" IN LENGTH PROPOGATED FROM THE VICINITY OF A COMPRESSION COUPLING.A LONGITUDIHAL CACK IN THE 3/4" 3306 PE SERVICE ALLOWED NATURAL GAS TO ENTER A BUILDING. THE SUBSEQUENT EXPLOSION INJURED FOUR PERSONS WHO REQUIRED HOSPITALIZATION. ONE FATALITY HAS OCCURRED SINCE THE TELEPHONIC REPORT. THIS AREA WAS LEAK SURVEYED ON JUNE 22, 1993 (DURING ABUSINESSS DISTRICT SURVEY) WITH NO LEAKS FOUND. THE FIRST NOTIFICATION TO SOUTHWEST GS WAS 8:16 A.M. NATURAL GAS INVOLVEMENT WAS NOT DTERMINED UNTIL APPROXIMATELY 11:30 A.M. ON AUGUST 5,1993.
2025-01-31 10:21 | YES | YES | 19930140 | 1993-08-24 | 1088 | BALTIMORE GAS & ELECTRIC CO | 38 COATS BRIDGE COURT | BALTIMORE | BALTIMORE | MD | 21236 | 3 | NO | 1600 | 1993-03-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 |  | 19930811 | 96 | 99 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | OTHER | COPPER RISER | 0.25 | 0.062 | ASTM 88B TYPE L | UNKNOWN | 1972 | 1972 | ABOVE GROUND |  | DONALD L. SHRADER - SUPERVISOR | 4105612728 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | THE EMPLOYEE WAS TIGHTENING AL LOOSE FITTING ON AN OUTSIDE METER REGULATOR INSTALLATION. THE SERVICE WAS 3/8" PLASTIC, WITH THE ABOVE GROND PORTION BEING3/8" COPPER. A COMPRESSION NUT ON THE COPPER PORTION WAS BEING TIGHTENED WHEN IT CRACKED. THE EMPLOYEE WAS IN THE PROCESS OF INSTALLING A PINCH-OFF TOOL WHEN THE TUBING CAME OUT OF THE FITTING - IGNITION OCCURRED AND THE EMPLOYEE WAS BURNED. SOURCE OF IGNITION IS UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19930141 | 1993-09-15 | 10037 | WESTERN RESOURCES INC | 804 & 806 SOUTH 15TH STREET | BLUE SPRINGS | JACKSON | MO |  | 2 | NO | 1623 | 1993-08-24 | 0 | 0 | 500000 | 382553.7478 | 923663.5677 | Null | 0 | 22 |  | 19930824 | 10 | 10 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | UNKNOWN | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | HANS E. MERTENS - VICE PRESIDENT | 8163465575 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE CAUSE OF THE DAMAGE TO THE APARTMENT COMPLEX WS APPAENTLY DUE TO VEHICULAR DAMAGE TO THE APARTMENT METER SET. THE SERVICE RISER BROKE AT A LOCATION BELOW THE SERVICE REGULATOR AND WAS BENT SO AS TO ALLOW GAS TO ENTER A WINDOW WHICH WAS ALSO DAMAGED DURING THE COLLISION. APPARENTLY, THE GAS WHICH ENTEREDTHE APARTMENT THROUGH THE WINDOW IGNITE, RESULTING IN DAMAGES TO THE APARTMENT BUILDING.
2025-01-31 10:21 | NO | NO | 19930147 | 1993-08-25 | 2392 | CITIZENS GAS & COKE UTILITY | 6300 SOUTH MERIDIAN STREET | INDIANAPOLIS | MARION | IN | 46217 | 1 | NO | 1545 | 1993-08-18 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 45 |  | 19930818 | 25 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | 2406 | PLEXCO | 1992 | 1992 | UNDER GROUND OR UNDER WATER |  | KERRY T. LOWDERMILK - SUPERINTENDENT | 3179274681 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | WE RECEIVED A CALL FROM PERRY TOWNSHIP FIRE DEPARTMENT THAT OUR MAIN HAD BEEN HIT. WHEN WE ARRIVED OUR MAIN WAS ON FIRE. A VAN DRIVEN BY EDWARD ESKEW HADLEFT THE ROADWAY AND STRUCK A UTILITY POLE ON THE NORTHWEST CORNER OF MERIDIAN STREET AND DAHLIA LANE. THE VAN CONTINUED ON THROUGH THE INTERSECTION COMING TO REST IN THE YARD ON THE SOUTHWEST CORNER OF THE STREET. THE POWER POLE WAS BROKEN OFF BY THE IMPACT AND PUSHED OVER AWAY FROM THE GAS LINE. THE LOWER PORTION OF THE POLE CAME UP UNDER THE GAS LINE CAUSING IT TO RUPTURE AND CATCH ON FIRE. THE 8-INCH STEEL WRAPPED MAIN WAS ISOLATED WHICH ALSO STOPPED THE FLOW OF GAS TO THE 2-INCH MAIN IN DAHLIA LANE. REPAIRS WERE MADE TO OUR MAIN AND GAS SERVICE WAS RESTORED TO THE AFFECTED AREA.
2025-01-31 10:21 | YES | YES | 19930149 | 1993-09-13 | 7650 | HUMBOLDT UTILITIES - GAS DEPT | 241 WOODLAND | HUMBOLDT | GIBSON | TN | 38343 | 3 | NO | 1045 | 1993-09-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19930902 | 50 | 47.5 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | EXPANSION PLUG | STEEL |  | 2 | 0.154 | API 5L GRADE B | UNKNOWN | 1956 | 1956 | UNDER GROUND OR UNDER WATER |  | GREG HALL - MANAGER | 9017849212 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MARK WAS IN A HOLE EXCAVATED TO EXPOSE A NATURAL GAS PIPE WHICH WAS LEAKING.DURING THE EXCAVATING PROCESS A SERVICE TAPPING TEE WAS HIT AND TORE LOOSE FROM THE MAIN GAS PIPELINE. A RUBBER EXPANSION PLUG WAS PUT IN THE HOLE LEFT AFTER THE TAPPING TEE WAS REMOVED. MARK WAS IN THE PROCESS OF WELDING A NIPPLEOVER THE PLUG AND GAS BEGAN LEAKING AROUND THE PLUG. THE WELDER IGNITED THE ESCAPING GAS. THE ESCAPING GAS WHICH WAS IGNITED, BLEW TOWARD MARK AND BURNEDBOTH HIS FOREARMS (2ND DEGREE BURNS) AND A COUPLE OF SMALL AREARS ON HIS FACE (1ST DEGREE BURNS). MARK WAS TRANSPORTED TO THE HOSPITAL BY HUMOLDT UTILITYCREWS. HE WAS KEPT IN THE HOSPITAL OVERNIGHT FOR OBSERVATION.
2025-01-31 10:21 | YES | NO | 19930150 | 1993-10-14 | 13480 | NIAGARA MOHAWK POWER CORP | SYRACUSE | SYRACUSE | ONONDAGA | NY | 13202 | 3 | NO | 1410 | 1993-09-07 | 0 | 0 | 150000 | 114766.1243 | 277099.0703 | Null | 0 | 45 |  | 19930907 | 22 | 24 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 6 | 0.602 | G-1039 | PLEXCO | 1993 | 1993 | OTHER | IN OPEN EXCAVATION | THOMAS J. GILBERT | 3154285078 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | WHILE COMPLETING A 6" PLASTIC TIE-IN ON SEPTEMBER 7, 1993 AT APPROXIMATELY2:00 PM, A FAILURE OCCURRED RESULTING IN GAS ESCAPING AT 22 PSI. THE GASIGNIGHTED FROM AN APPARENT STATIC BUILD UP CAUSING VARIOUS LEVELS OF DAMAGE TOCOMPANY-OWNED EQUIPMENT AND PRIVATE PROPERTY IN THE SURROUNDING AREA. NIGARAMOHAWK GAS TECHNICAL SUPPORT INVESTIGATED THE INCIDENT IN THE FOLLOWINGMANNER: 1. COLLECTION OF EVIDENCE AT THE SCENE - THIS INCLUDED THE COLLECTIONAND PRESERVATION OF PHYSICAL EVIDENCE ALONG WITH PHOTOS, VIDEOS AND OTHERDOCUMENTATION DEEMED NECESSARY FOR INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19930151 | 1993-10-27 | 12878 | MOUNTAINEER GAS CO | 1505 BEACON STREET | KEYSER | MINERAL | WV | 26526 | 4 | NO | 1244 | 1993-09-27 | 0 | 1 | 150000 | 114766.1243 | 277099.0703 | Null | 0 | 18 |  | 19930927 | 36 | 40 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 2 | 0.216 | ALYDL A | DUPONT | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | DAVID ESTEP - AREA MANAGER | 3043290165 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | 1 | YES | 1993-07-26 | YES | 3 | PAINT | NO
2025-01-31 10:21 | NO | NO | 19930152 | 1993-10-25 | 12684 | MONTANA - DAKOTA UTILITIES CO | 620 SIXTH AVE. N. | WOLF POINT | ROOSEVELT | MT | 59201 | 3 | YES | 1114 | 1993-08-29 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 1 | 1 |  | 19930830 | 15 | 21 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | MILL WRAPPED |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RONALD E. BLUM - STAFF ENGINEER | 7012227924 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19930153 | 1993-09-28 | 2860 | COVINGTON MUNICIPAL GAS SYSTEM, CITY OF | SR 81 | WALNUT GROVE | WALTON | GA | 30209 | 2 | NO | 915 | 1993-09-01 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19930901 | 450 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | FILTER | OTHER | BAND CLAMP | STEEL |  | 0 | 0 | FD 300-4 | AMERICAN/SINGER | 0 | 0 | ABOVE GROUND |  | STEVE COADY - GAS SUPERINTENDENT | 4047868049 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE | BAND CLAMP FOR LOWER FILTER PLATE | PART 3 NARRATIVE - SMALL INTERNAL CORROSION PIN HOLE LEAK, AT 5:00 POITION ON PIPE, WAS REPAIRED WITH PLIDCO CLAMP.
2025-01-31 10:21 | NO | NO | 19930154 | 1993-09-28 | 6141 | GAS CO OF NEW MEXICO | 1399 ROOSEVELT | GRANTS | CIBOLA | NM | 87020 | 3 | NO | 1430 | 1993-09-17 | 0 | 0 | 5000 | 3825.5375 | 9236.6357 | Null | 0 | 30 |  | 19930917 | 45 | 50 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 |  | UNKNOWN | 0 | 1958 | UNDER PAVEMENT |  | JON W. JONES - MANAGER - ENGR SUPPORT | 5058484571 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-09-18 | NO | 2 | MAIN WAS NOT LOCATED,ONLY | YES |  |  | PART 3 NARRATIVE - SPECULATE THAT FISHING NET SNAG BROKE 1" PLEECO BLEEDER VALVE ON BLIND FANGE ON SUB-SEA VALVE SETTING.
2025-01-31 10:21 | YES | YES | 19930155 | 1993-11-03 | 12582 | MISSISSIPPI VALLEY GAS | 316 FOREST STREET | ABERDEEN | MONROE | MS | 39730 | 3 | NO | 912 | 1993-10-22 | 0 | 2 | 1500 | 1147.6612 | 2770.9907 | Null | 0 | 38 |  | 19931022 | 16 | 25 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 1952 | WITHIN/UNDER BUILDING |  | PAUL D. NOEL - DIRECTOR OF OPERATING SERVICES | 6019616860 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1973 | NO DATA |  | Null |  | Null |  |  | Null |  |  | PART A - CORROSION - THE LEAKAGE OCCURED AT TWO (2) SMALL CORROSION PIT HOLES LOCATED IN A 1" LONG DENT IN THE PIPE WALL. VISUAL INSPECTION DID NOT INDICATE RECENT CORROSIVE ACTIVITY AND THE PIPE -TO-SOIL POTENTIAL READING WAS -1.0VOLT AT THE TIME OF THE INCIDENT. PART D - IT APPEARED THAT LEAKING GAS UNDER A SMALL ASPHALT PARKING AREA MIGRATED THROUGH THE SOIL (AND POSSIBLY AN ABANDONED DRAIN LINE) TO THE INTERIOR OF A SMALL STORAGE AND COOLER BUILDING. THE APPARENT GAS/AIR MIXTURE WAS IGNITED BY SOME SOURCE WHEN TWO (2) PEOPLE ENTERED THE BUILDING AND THEY WERE BURNED BY THE RESULTING FLASH FLAME.
2025-01-31 10:21 | YES | YES | 19930156 | 1993-09-21 | 13650 | NORTH PENN GAS CO | 303 EXTENSION STREET | MANSFIELD | TIOGA | PA | 16933 | 2 | NO | 910 | 1993-08-26 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19930827 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D 2513 | PLEXCO | 1983 | 1983 | UNDER GROUND OR UNDER WATER |  | JAMES N. SEWELL - MANAGER OF OPERATIONS | 8006520550 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | PART B #3. OPERATOR GAVE NOTICE T0 A ONE CALL SYSTEM ON AUGUST 19,1993. PART1 GENERAL REPORT INFORMATION - THIS INCIDENT BECAME REPORTABLE UNDER PART 191.3 ONE DAY AFTER THE ACTUAL ACCIDENT WHEN THE INJURED EMPLOYEE SOUGHT A SECOND APPRAISAL OF HIS CONDITION AND WAS ADMITTED FOR OBSERVATION. PART 3 THE OPERATOR ASSIGNED A TWO MAN CREW TO INSTALL A SERVICE LINE TO A NEW RESIDENTIALDWELLOING. ONCE ON LOCATION, THE CREW FOUND A LINE MARKER AND SEVERAL TEMPORARY MARKERS (FLAGS). ALTHOUGH EQUIPPED TO DO SO, THE CREW MADE NO EFFORT TO IDENTIFY THE MAIN WITH ELECTRONIC LOCATING EQUIPMENT, BUT ASSUMED THE MARKERS FOUND IDENTIFIED THE LOCATION OF THE MAIN. THE CREW PROCEEDED TO TRENCH FROM THE DWELLING TO THE ASSUMED MAIN LOCATION, HITTING THE MAIN WITH A TRENCHER. THER WAS FLASH FIRE, WHICH WAS QUICKLY EXTINGUISHED, BUT NOT BEFORE IT BURNED THE TRENCHER OPERATOR RESULTING IN FIRST AND SECOND DEGREE BURNS TO THE FACE, NECK , ARMS AND HANDS. THE EMPLOYEE WAS TAKEN TO A HOSPITAL, TREATED AND RELEASED. THE FOLLOWING DAY, THE OPERATOR TOOK THE EMPLOYEE TO A DIFFERENT HOSPITAL, WHERE HE WAS ADMITTED. UPON ADMISSION THE THE HOSPITAL, THE OPERATOR GAVE NOTICE TO THE DEPARTMENT OF TRANSPORTATION AND THE PENNSYLVANIA PUBLIC UTILITY COMMISSION PURSUANT OT PART 191 OF TITLE 49 OF THE CODE OF FEDERAL REGULATIONS. THE APPARENT CAUSE OF THE INCIDENT WAS THE CREW'S DECISION TO RELYON THE MARKERS FOUND AND NOT TO USE AN ELECTRONIC LINE LOCATOR TO VERIFY THESAME. ALTHOUGH THE MARKERS ON SITE WERE ACCURATE, THEY DID NOT ALL MARK THE MAIN THAT THE CREW NEEDED TO FIND. THE PERMANENT MARKER WAS, IN FACT, ON A SECONDARY MAIN (MAIN #2) THAT BRANCHED OFF THE PRIMARY MAIN )MAIN#1). THE PERMANENT MARKER WAS OFFSET FROM THE JUNCTURE OF THE TWO MAINS APPROXIMATELY 6 FEET TO BLEND INTO EXISTING SHRUBBERY. UNAWARE THAT THE PERMANENT MARKER WAS OFFSET, AND IN FACT ON MAIN #2 AND NOT ON MAIN #2, THE CREW DUG INTO MAIN #1.
2025-01-31 10:21 | YES | YES | 19930157 | 1993-09-22 | 22182 | WASHINGTON GAS LIGHT CO | 12010 ROGART ROAD | SILVER SPRING | MONTGOMERY | MD | 20901 | 3 | NO | 2300 | 1993-08-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19930908 | 20 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | SCHEDULE 40 | BETHEHEM STEEL | 1939 | 1940 | UNDER PAVEMENT |  | WM. A. HINDE - SAFETY SUPERVISOR | 7037507687 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | AN ELECTRIC ARC FROM AN EXTENSION CORD THAT SEPARATED WHILE NATURAL GAS WAS BEING RELEASED.WHILE WORKING TO REMOVE A 3/4" STEEL RISER FROM A 2" STEEL MAIN, A 3/4" STREET ELL FAILED. WHILE THE CREW LEADER WAS ATTEMPTING TO PLACE A WOODEN PLUG INTHE BROKEN FITTING, AN EMPLOYEE STANDING A STREET LEVEL LEANED A FLOODLIGHT OVER THE EXCAVATION, IN DOING SO, HE SEPARATED THE LIGHT FROM THE EXTENSION CORD. THE ENSUING FIRE TRAPPED THE CREW LEADER IN THE EXCAVATION. THE FIRE WASRAPIDLY EXTINGUISHED, BUT THE CREW LEADER RECEIVED SERIOUS BURNS TO HIS ARMS,FACE, AND HANDS THAT REQUIRED IN-HOSPITAL TREATMENT.
2025-01-31 10:21 | NO | NO | 19930160 | 1993-10-05 | 4483 | ENSTAR NATURAL GAS CO | NE CORNOR OLD GLENN HWY & HANSON ST | EAGLE RIVER |  | AK | 99577 | 3 | NO | 2145 | 1993-09-23 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 1 | 0 |  | 19930923 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M8000 | PHILLIPS DRISCOPIPE | 1992 | 1992 | ABOVE GROUND |  | DAVID W. BREDIN - MANAGER DISTRIBUTION OPERATIONS | 9072543745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A STRUCTURE FIRE, CLASSIFIED AS SUSPICIOUS ORIGIN BY THE ANCHORAGE FIRE DEPARTMENT, SEVERELY DAMAGED THE COMMERICAL BUILDING AT THE CORNER OF THE OLD GLENN HWY AND HANSON STREET IN EAGLE RIVER, ALASKA. THE INTENSE HEAT FROM THE FIRE MELTED THE 5/8" PLASTIC TUBING INSIDE THE STEEL SERVICE LINE RISER ON AN ADJACENT COMMERCIAL GREENHOUSE LOCATED APPROXIMATELY 15' FROM THE BUILDING. THEGREENHOUSE WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICE LINE OPERATING AT APPROXIMATELY 55 PSIG. WHERE THE SERVICE LINE CAME ABOVEGROUND IT DID SO THROUGH A RIGID STEEL RISER. WHEN THE PLASTIC SERVICE LINE MELTED, THERE WAS A RELEASE OF NATURAL GAS. THE GAS WAS SHUT OFF BY DIGGING UP THE SERVICE LINE A SAFE DISTANCE FROM THE FIRE AND INSTALLING A PINCHER ON THE SERVICE LINE. NATURAL GAS DID NOT CONTRIBUTE TO THE CAUSE OF THE FIRE.
2025-01-31 10:21 | YES | YES | 19930161 | 1993-10-05 | 11720 | LONG ISLAND LIGHTING COMPANY | 1285 OLD WALT WHITMAN ROAD | MELVILLE | SUFFOLK | NY | 11747 | 4 | NO | 1519 | 1993-08-31 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 34 |  | 19930902 | 46 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.66 | 0.14 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | THOMAS E. LUPSKI - CODE & SPECIFICATIONS ENGINEER | 5169334400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON AUGUST 31, 1993, A.J. ANTONINO WHILE EXCAVATING TO INSTALL A SEWER LINE, STRUCK AND PULLED A 1 1/4 INCH STEEL GAS SERVICE FROM A COMPRESSION COUPLING RESULTING IN A LEAK AND SUBSEQUENT EVACUATION OF 100 PEOPLE FROM A BUILDING.THE EVACUATION WAS PERFORMED BY THE MELVILLE N.Y. FIRE DEPARTMENT PRIOR TO LILCO'S ARRIVAL AT THE SCENE OF THE INCIDENT. ON SEPTEMBER 2, 1993 AFTER LILCOLEARNED OF THE POSSIBLE TRANSPORTING OF VICTIMS TO A HOSPITAL BY THE FIRE DEPARTMENT ON THE DATE OF THE INCIDENT, A TELEPHONIC NOTIFICATION WAS MADE TO THE DEPARTMENT OF TRANSPORTATION. LILCO LATER RECEIVED CONFIRMATION OF INPATIENT HOSPITALIZATION INVOLVING (1) INDIVIDUAL WHO WAS ADMITTED TO THE HOSPITAL ON AUGUST 31, 1993 AND RELEASED THE FOLLOWING DAY.
2025-01-31 10:21 | YES | YES | 19930166 | 1993-10-14 | 8270 | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO | 285 E. COURT | ROCKWELL | CALHOUN | IA | 50469 | 4 | NO | 615 | 1993-09-09 | 2 | 0 | 100000 | 76510.7496 | 184732.7135 | Null | 0 | 15 |  | 19930909 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | STILL UNDER INVESTIGATION | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SANDRA RASMUSSEN - GAS STANDARDS ENGINEER | 7122777928 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19930167 | 1993-10-13 | 7240 | HERMANN CITY NATURAL GAS SYSTEM | HERMANN MISSOURI RIVER BRIDGE | HERMANN | GASCONADE | MO | 65041 | 1 | NO | 1930 | 1993-09-30 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19931005 | 0 | 250 | BY TEST | 375 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | OTHER | PIPE LINE | OTHER | RUPTURED 6"LINE CAUSED BY | STEEL |  | 6 | 0.145 |  |  | 0 | 1964 | ABOVE GROUND |  | ROY J. MILLER - DISTRICT MANAGER | 3144862914 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | PART 2 - FLASH FIRE FROM GAS POCKET IN DAMAGED 6" STEEL GAS LINE FORCED OUT DUE TO FLOOD WATER FLOW AT OPEN END.
2025-01-31 10:21 | YES | NO | 19930170 | 1993-11-03 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 50 BRETT STREET | PISCATAWAY | MIDDLESEX | NJ | 08854 | 4 | NO | 1724 | 1993-10-18 | 0 | 0 | 115000 | 87987.362 | 212442.6206 | Null | 0 | 9 |  | 19931018 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER ERROR | OTHER | CUSTOMER ERROR | OTHER | CUSTOMER ERROR | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | D.W. GREVENTIZ - VICE PRESIDENT | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN INVESTIGATION REVEALED THIS HOUSE WAS IN THE PROCESS OF BEING SOLD AND NOONE WAS LIVING IN THE HOUSE AT THE PRESENT TIME. THE OWNER'S BROTHER, SHU-HONG SHIEL, WAS CHECKING THE HOUSE PERIODICALLY. ON 10/18/1993 AT APPROXIMATELY12:00 NOON, MR SHIEL TURNED ON THE GAS VALVE IN THE BOILER ROOM TO LIGHT A PILOT ON THE RANGE. THIS INDAVERTENTLY CAUSED GAS TO ESCAPE THROUGH AN OPEN PIPE WHICH LED TO A PROVIOUSLY DISCONNECTED DRYER. MR. SHIEL LEFT THE THE HOUSE, AND WHEN HE RETURNED AT 5:00 P.M. HE OPENED THE FRONT DOOR AND SMELLED GAS.HE WALKED AWAY FROM THE HOUSE AND SEVERAL MINUTES LATER IT EXPLODED
2025-01-31 10:21 | YES | YES | 19930172 | 1993-11-03 | 18532 | SOUTHERN UNION GAS CO | NEAR 49TH ST & AVE. S | GALVESTON | GALVESTON | TX | 77553 | 3 | NO | 1030 | 1993-09-20 | 0 | 3 | 117000 | 89517.577 | 216137.2748 | Null | 13 | 58 |  | 19930920 | 33 | 60 | BY TEST | 2 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | UNKNOWN | STEEL |  | 6 | 0.28 |  |  | 0 | 1936 | UNDER PAVEMENT |  | OTIS LARRY - ASSISTANT VICE PRESIDENT | 4097633312 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE REPLACING MAIN LINE WAS MISLOCATED AND HIT WITH ROCK SAW OPERATED BY COMPANY EMPLOYEES.MISLOCATE OF COMPANY FACILITIES AND 6" MAIN HIT WITH ROCKSAW.
2025-01-31 10:21 | NO | NO | 19930177 | 1993-10-27 | 11680 | LONE STAR GAS CO | 303 MAIN STREET | LAKE DALLAS | DENTON | TX | 75065 | 2 | NO | 615 | 1993-08-22 | 0 | 0 | 200 | 153.0215 | 369.4654 | Null | 0 | 30 |  | 19930822 | 15 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER | PREBENT RISER | POLYETHYLENE PLASTIC | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | PHILLIP MURDOCK - DIRECTOR | 2146702229 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | THE BUILDING HOUSING THE LAKE DALLAS CAFE, TIMBERLINE TAXIDERMY AND A VACANTHARDWARE STORE AND LUMBERYARD CAUGHT FIRE. THE HEAT FROM THE FIRE MELTED THEGAS METER AND THE REGULATOR.
2025-01-31 10:21 | YES | YES | 19930179 | 1993-10-19 | 11264 | LAURENS COMMISSION OF PUBLIC WORKS | GARLINGTON STREET TRAILER PARK #15 | LAURENS | LAURENS | SC | 29360 | 2 | NO | 1437 | 1993-09-15 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 45 |  | 19930915 | 30 | 42 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 0.5 | 0.19 | ASTM D2513 | DRISCOPIPE | 0 | 1992 | OTHER | DITCH LINE | RAYMOND R. CRAFT - SUPT. NATURAL GAS DEPT | 8039840841 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON SEPTEMBER 15,1993, THE LAURENS COMMISSION OF PUBLIC WORKS (CPW) WAS CALLEDBY THE FIRE DEPARTMENT FOR ASSISTANCE IN REFERENCE TO A NATURAL GAS FIRE AT THE GARLINGTON STREET TRAILER PARK. WHEN CPW PERSONNEL ARRIVED AT THE SCENE, THE FIRE DEPARTMENT HAD PUT THE FIRE OUT AND FIRE FIGHTERS WERE HOSING DOWN THE SIDE OF THE TRAILER INVOLVED. THERE WERE TWO,1/2 INCH POLYETHYLENE PLASTICGAS LINES EXPOSED IN A DITCH LINE THAT WAS UNCOVERED. NATURAL GAS WAS BLOWINGFROM ON OF THE LINES. WITH THE FIRE DEPARTMENT STILL SPRAYING WATER ON THE LINES, OUR SERVICE WORKERS PROCEEDED TO PINCH-OFF BOTH LINES. AFTER BOTH LINES WERE PINCHED-OFF, OUR CONSTRUCTION CREW ARRIVED ON THE SCENE AND WERE TOLD TO KILL THE GAS SERVICE LINES BY RAY CRAFT. SINCE THIS INCIDENT FALLS UNDER PART 191.5 OF THE PIPELINE SAFETY REGULATIONS, TELEPHONIC NOTICE WAS GIVEN AT THE EARLIEST PRACTICABEL MOMENT TO THE PUBLIC SERVICE COMMISSION OF SOUTH CAROLINA AND TO THE U.S. DEPARTMENT OF TRANSPORTATION, WASHINGTON, DC. ALSO, A WRITTEN REPORT FORM RSPA F1700.1 WILL BE SUBMITTED WHEN ADDITIONAL INFORMATIONIS OBTAINED. ON SEPTEMBER 16, 1993, I INSTRUCTED THE CONSTRUCTION CREW TO REROUTE THE GAS LINES THAT WERE KILLED BECAUSE:(1) THEY WERE SERVING TWO OTHER CUSTOMERS AND (2) MR. WILLIAMS (THE OWNER OF THE TRAILER PARK) HAD MOVED A TRAILER OVER THE GAS LINES. I ALSO TOLD THE CONSTRUCITON CREW TO CUT-OUT THE LINE THAT WAS EXPOSED IN THE DITCH LINE. ON SEPTEMBER 17, 1993, MR. CARL MORSE OF THE PUBLIC SERVICE COMMISSION VISITED THE CPW TO ASSIST ME IN INSPECTING THE INCIDENT. WE SITE OF THE INCIDENT. MR. MORSE ADVISED US TO PRESSURE TEST THE SEGMENTS OF PIPES THAT WERE STILL IN THE GROUND, TO GET A COPY OF THE FIREDEPARTMENT REPORT, AND TO CHECK ANY LEAK REPORTS AND ANY LEAK SURVEYS THAT WERE CONDUCTED. WHILE WE WERE AT THE SCENE, MR. WILLIAMS ARRIVED. HE GAVE US HIS SON'S DETAILS OF THE INCIDENTS. ACCORDING TO MR. WILLIAMS, HIS SON WAS SETTING UP THE TRAILER. HE HAD SMELLED NATURAL GAS FOR A COUPLE OF DAYS, BUT HE DID NOT CALL US. HE SAID THE GAS FUMES HAD EVEN MADE HIM SICK AT TIMES. HE SAID THAT HE EVEN WENT INTO THE STORE AND GOT SOME SOAP BUBBLES AND SOAPED THE EXPOSED LINES. HE ALSO ADDED THAT HIS SON SAW THE DIRT BLOWING. THE HE PROCEEDED TO GO BACK TO WORK, AND WHILE DRIVING A WEDGE TO SET UP THE TRAILER, HE CAUSED A SPARKS WHICH IGNITED THE GAS AND CAUSING THE FIRE. I TOLD MR. WILLIAMS THAT WE WERE CONDUCTING AN INVESTIGATION, THAT WE WERE GOING TO DIG UP THE LINESAND PRESSURE TEST THEM, AND THAT I WOULD LET HIM KNOW WHEN WE WERE GOINGTO DO THIS. ON SEPTEMBER 21, 1993, WITH MR. WILLIAMS AND HIS SON PRESENT, WETESTED THE LINES. MR. WILLIAMS SON SAID HE SAW DIRT BLOWING FROM UNDERNEATH THE SIDE OF THE TRAILER. WE TESTED THREE, 1/2 INCH LINES UNDER THE TRAILER'S SIDE AND FOUND NO LEAKS. ON THE BACK SIDE OF THE TRAILER, WE DUG UP THE LINESAND ONLY FOUND ONE 1/2 INCH LINE, TESTED IT, AND FOUND NO LEAK. WE ALSO FOUNDAN OLD CAP THAT MAY HAVE BEEN USED TO CAP-OFF THE OTHER LINE. WHILE DIGGING WE DID FIND VERY HARD DRY DIRT WITH AN ODOR TO IT THAD SMELLED OF GAS. THIS GENERALLY THE KIND OF CONDITIONS WE FIND AT LEAKS.
2025-01-31 10:21 | YES | YES | 19930183 | 1993-11-17 | 12684 | MONTANA - DAKOTA UTILITIES CO | 414 W. GRAND CROSSING | MOBRIDGE | WALWORTH | SD | 57601 | 3 | NO | 1045 | 1993-10-22 | 0 | 1 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 35 |  | 19931022 | 40 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406ASTMD2513 | PHILLIPS DRISCO | 1993 | 1993 | OTHER | IN EXCAVATION | RONALD E. BLUM - STAFF ENGINEER | 7012227924 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | PART 3 NARRATIVE - SADDLE FUSION AREA ON THE PIPE WAS OVERHEATED AND BLEW OUT - IGNITION SOURCE UNKOWN.
2025-01-31 10:21 | YES | YES | 19930184 | 1993-11-15 | 18112 | SAN DIEGO GAS & ELECTRIC CO | SCRIPPS RANCH BL D & CARROLL CYN RD | SAN DIEGO | SAN DIEGO | CA | 92131 | 3 | NO | 1025 | 1993-10-12 | 0 | 1 | 0 | 0 | 0 | Null | 15 | 35 |  | 19931013 | 60 | 60 | BY TEST | 105 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 3 | 0.304 | ASTM D2513 | DUPONT | 1981 | 1981 | UNDER PAVEMENT |  | E.L. MORRISON - MANAGER | 6196995011 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 3" OOLYETHYLENE TEE FAILED. BENDING STRESS ON THE TEE AND PIPE ASSEMBLY INITIATED A SLOW GROWTH CRACK IN THE RUN PORTION OF THE TEE. OVER THE LAST FEW YEARS SEVERAL EXCAVATIONS HAVE OCCURRED IN CLOSE PROXIMITY TO THE INCIDENT LOCATION. WE BELIEVE ONE OF THESE ACTIVITIES DISTURBED THE GAS MAIN AND INDUCEDTHE BENDING STRESS WHICH CAUSED THE TEE CRACK. A CRACK IN THE GAS TEE ALLOWEDGAS TO MIGRATE INTO THE ELECTRIC CONDUIT AND VAULT SYSTEM. THE GAS IGNITED FROM AN UNKNOWN IGNITION SOURCE CAUSING AN EXPLOSION, BLOWING OFF THREE VAULT COVERS, AND STARTING A SMALL GRASS FIRE. TWO SAMARITANS EXTINGUISHED THE FIREAND A THIRD RAN UP TO HELP AND FELL INTO THE OPEN VAULT. HE INJURED HIS ANKLE AND BACK.
2025-01-31 10:21 | YES | YES | 19930188 | 1993-11-16 | 22798 | WISCONSIN SOUTHERN GAS CO INC | 135 & 137 PRAIRIE STREET | VILLAGE OF SHARON | WALWORTH | WI | 53585 | 3 | NO | 805 | 1993-10-27 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19931027 | 50 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | PLEXCO | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | SAM FREDRICKSON - DIRECTOR OF OPERATIOS | 4142488861 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19930189 | 1993-11-16 | 11720 | LONG ISLAND LIGHTING COMPANY | UNION BOULEVARD | WEST ISLIP | SUFFOLK | NY | 11795 | 4 | NO | 2317 | 1993-10-13 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 51 |  | 19931014 | 86 | 99 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.62 |  |  | 0 | 1944 | UNDER PAVEMENT |  | THOMAS E. LUPSKI - CODE & SPECIFICATIONS ENGINEER | 5169334400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE LONG ISLAND LIGHTING COMPANY PLACED A TELEPHONIC NOTIFICATION TO THE DEPARTMENT OF TRANSPORTATION BASED UPON THE PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF THE INCIDENT. THIS INFORMATION INDICATED THAT A FIRE FIGHTER WAS TRANSPORTED TO THE HOSPITAL. SUBSEQUENT INVESTIGATION REVEALEDTHAT THE INJURED FIRE FIGHTER DID NOT REQUIRE INPATIENT HOSPITALIZATION.CHRONOLOGICAL SEQUENCE OF EVENTS10/13/1993 23:17 LILCO RECEIVED A TELEPHONE CALL FROM SUFFOLK COUNTY FIREAND RESCUE.10/13/1993 23:18 LILCO GAS CUSTOMER SERVICE CREW DISPATCHED TO JOB SITE10/13/1993 23:32 LILCO GAS CUSTOMER SERVICE CREW ARRIVED AT THE JOB SITE.10/13/1993 23:34 LILCO PERFORMED SHUTDOWN OPERATIONS.10/13/1993 00:08 JOB "MADE SAFE" AT 00:0810/14/1993 00:09 PERIMETER HOUSES WERE CHECKED FOR THE PRESENCE OF NATURAL 01:00 GAS.10/14/1993 01:00- REPAIRS MADE TO GAS MAIN. 08:0010/14/1993 08:40 GAS MAIN WAS BACK TO NORMAL OPERATIONS.
2025-01-31 10:21 | NO | NO | 19930191 | 1993-11-12 | 15359 | PEOPLES NATURAL GAS | 19455 KENWOOD TRAIL | LAKEVILLE | DAKOTA | MN | 55044 | 3 | NO | 1026 | 1993-10-20 | 0 | 0 | 5000 | 3825.5375 | 9236.6357 | YES | 0 | 30 |  | 19931020 | 25 | 75 | BY TEST | 75 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.409 |  | ALDYLA | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | GREGORY J. BENAK - ATTORNEY | 4022212021 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-09-17 | YES | 2 |  | YES |  |  | LINE WAS STRUCK BY CONTRACTOR. LINE WAS MARKED BUT MAY NOT HAVE BEEN MARKED WHERE HIT. 148 JUNIOR HIGH STUDENTS EXAMINED BY MEDICAL PERSONNEL AT AREA CLINICS.
2025-01-31 10:21 | NO | NO | 19930194 | 1993-11-08 | 22210 | WASHINGTON WATER POWER CO | S. 1231 MAIN | BONNERS FERRY | BOUNDARY | ID | 83805 | 3 | NO | 510 | 1993-10-15 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19931015 | 30 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER EQUIPMENT | OTHER | PILOT SAFETY VALVE | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DEBORAH MARTIN - MANAGER GAS ENGINEERING | 5094828493 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PART 3 CUSTOMER EQUIPMENT FAILURE AND LACK OF PROPER VENTILATION ALLOWED ACCUMULATIONOF GAS RESULTING IN EXPLOSION AND SMALL FIRE. SEE COVER LETTER FOR MORE DETAIL. DURING A PLANNED CONSTRUCTION PROJECT TO REPLACE THE BONNERS FERRY DISTRICT REGULATOR STATION, THE DOWNSTREAM VALVE WAS INADVERTENTLY INSTALLED WITH THE OPEN/CLOSED INDICATOR IN THE REVERSED DIRECTION. THIS CAUSED THE VALVE TO BE LEFT IN THE CLOSED POSITION, THERE BY ELIMINATING THE GAS SUPPLY INTO THE DISTRIBUTION SYSTEM. APPROXIMATELY 600 CUSTOMERS LOST GAS SERVICE. RELIGHTING OF CUSTOMERS BEGAN AT 8:00 P.M. ON OCTOBER 14 AND WAS COMPLETED ATNOON ON OCTOBER 16. PRIOR TO PERSONNEL RELIGHTING THE BOILER AT THE MAIN STREET CAR WASH 1231 MAIN, AN EXPLOSION AND FIRE OCCURRED ON THE PREMISES AT 5:10 A.M ON OCTOBER 15. AN INVESTIGATION OF THIS INCIDENT WAS CONDUCTED BY WWP PERSONNEL AND THE BONNERS FERRY FIRE CHIEF. IT IS THEIR CONCLUSION THAT GAS ACCUMULATED IN THE BOILER ROOM (700,00 BTU/HR) AND NO VENTILATION OR COMBUSTION SUPPPLY AIR WAS AVAILABLE AS REQUIRED BY CODE (NFPA 54). IT IS ALSO LIKELY THAT THE PILOT SAFETY CONTROL VALVE FAILED, WHICH ALLOWED GAS TO ENTER THE ROOM. WWP SERVICE PERSONNEL WERE LIGHTING NEAR THE AREA AND RESPONDED IMMEDIATELY TO SAFELY SECURE THE AREA AND EXTINGUISH A SMALL FIRE. CUSTOMER FACILITY DAMAGE IS ESTIMATED TO BE LESS THAN $3000.
2025-01-31 10:21 | NO | NO | 19930199 | 1993-12-01 | 12690 | MONTANA POWER CO | 1028 E. IDAHO STREET | KALISPELL | FLATHEAD | MT | 59901 | 2 | NO | 1148 | 1993-10-20 | 0 | 0 | 56000 | 42846.0198 | 103450.3196 | Null | 0 | 30 |  | 19931020 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | GRADE B |  | 1970 | 1970 | UNDER GROUND OR UNDER WATER |  | FRANK CABBAGE | 4067528340 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-10-18 | NO | 0 |  | YES |  |  | A CONTRACTOR INSTALLING A NEW SEWER LINE STRUCK AND DAMAGED AN INACTIVE NATURAL GAS SERVICE LINE. SINCE THE LINE WAS NOT MARKED, AND LOCATIONS HAD BEEN REQUESTED, THE PERSON OPERATING THE EXCAVATOR DID NOT NOTIFY ANYONE THAT A LINE, HE CONSIDERED TO BE ABANDONED, WAS DAMAGED. NATURAL GAS MIGRATED UNDERGROUND, COMING UP UNDER A MOBIL HOME SALES OFFICE, SEE ATTACHED SKETCH. MONTANA POWER COMPANY RECEIVED NOTICE OF A GAS ODOR INSIDE A MOBIL HOME SALES OFFICE AT THE ABOVEADDRESS. THE SERVICEMAN ANSWERING THE CALL DETECTED THE PRESENCE OF GAS UNDER THE STRUCTURE AND ADVISED THE OCCUPANTS TO EVACUATE. WHILE HE WASOUTSIDE SEARCHING FOR THE SOURCE OF THE GAS, ONE OF THE OCCUPANTS, ACTING AGAINST INSTRUCTIONS, WENT BACK IN THE STRUCTURE AN TURNED OFF THE BREAKERS FORTHE ELECTRICAL SUPPLY. AS SOON AS HE DID THIS, THE GAS MIXTURE UNDER THE OFFICE IGNITED. THE SKIRTING AROUND THE STRUCTURE WAS BLOWN AWAY AND THE STRUCTURE WAS LIFTED VIOLENTLY AND THEN CAUGHT FIRE.THE ONLY INJURY WAS TO OUR SERVICEMAN WHO WAS KNOCKED DOWN. HE SUSTAINED A CRACKED RIB AS A RESULT OF BEING KNOCKED DOWN. AT SOME TIME, THE RISER PORTION OF THE DAMAGED INACTIVE GAS SERVICE LINE WAS BENT OVER AND BURIED BY PERSONS UNKNOWN. HAD THE RISER AND METERCOCK BEEN IN ITS ORIGINAL POSITION IT WOULD HAVE BEEN SEEN BY THE LOCATOR AND THE LINE WOULD HAVE BEEN MARKED. THE LOCATOR DID "SWEEP" THE AREA WITH HIS LOCATOR BUT, WITHOUT A DIRECT CONNECTION, WAS UNABLE TO DETECT THE PRESENCE OF AN UNDERGROUND LINE. THE EXCAVATOR FAILED TO NOTIFY THE OPERATOR THAT AN UNMARKED LINE HAD BEEN DAMAGED. THIS IS IN VIOLATION OF A STATE LAW THAT REQUIRES IMMEDIATE NOTIFICATION OF THE GAS COMPANY WHEN AN UNMARKED LINE IS DISCOVERED. THE BUILDING OCCUPANT RE-ENTERED THE STRUCTURE DESPITE OUR INSTRUCTIONS AND OPERATED AN ELECTRICAL CIRCUIT BREAKER WHICH WE BELIEVE WAS THE SOURCE OFIGNITION.
2025-01-31 10:21 | NO | NO | 19930201 | 1993-11-22 | 4483 | ENSTAR NATURAL GAS CO | LOT 2, BLK 1 | SAMPSON ESTATES | PETERS CREEK | AK | 99567 | 3 | NO | 1255 | 1993-11-11 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 1 | 10 |  | 19931111 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M8000 | PHILLIPS DRISCOPIPE | 1993 | 1993 | ABOVE GROUND |  | DAVID W. BREDIN - MANAGER DISTRIBUTION OPERATIONS | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A STRUCTURE FIRE, CLASSIFIED AS "ORIGIN UNKNOWN" BY THE PETERS CREEK FIRE DEPARTMENT, SEVERELY DAMAGED A SINGLE FAMILY HOME THAT WAS UNDER CONSTRUCTION. THE BUILDING WAS LOCATED AT LOT 2, BLK 1 SAMPSON ESTATES, PETERS CREEK, ALASKA. THE BUILDING WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICE LINE OPERATING AT APPROXIMATELY 50 PSIG. THE INTENSE HEAT FROM THE FIRE MELTED THE 5/8" PLASTIC TUBING INSIDE THE STEEL SERVICE LINE RISER ON THE BUILDING. WHEN THE PLASTIC SERVICE LINE MELTED, THERE WAS A RELEASE OF NATURAL GAS. THE GAS WAS SHUT OFF BY DIGGING UP THE SERVICE LINE A SAFE DISTANCE FROM THE FIRE AND INSTALLING A PINCHER ON THE SERVICE LINE. NATURAL GAS DID NOTCONTRIBUTE TO THE CAUSE OF THE FIRE.
2025-01-31 10:21 | YES | NO | 19930204 | 1993-11-23 | 15259 | PENNSYLVANIA GAS & WATER CO | INTERSECTION BROOKSIDE & LOCK STS. | WILKES-BARRE | LUZERNE | PA | 18705 | 3 | NO | 550 | 1993-10-31 | 0 | 0 | 115000 | 87987.362 | 212442.6206 | Null | 2 | 14 |  | 19931031 | 56 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING | AMP. | OTHER | UNKNOWN | 0 | 0 | trans | AMP. SPECIAL INDUSTRIES. | 1978 | 1979 | UNDER PAVEMENT |  | JAMES M. GREGER - MANAGER OF SPECIAL PROGRAMS | 7178298866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A DEFECTIVE AMP. FITTING DISTURBED DURING BACKFILLING AND /OR COMPACTION LEDTO THE SEPARATION OF THE TWO-INCH PLASTIC GAS MAIN FROM THE FITTING WHICH RESULTED IN THE ESCAPE OF GAS.PART 2 APPARENT CAUSE- OTHER - DEFECTIVE FITTING.
2025-01-31 10:21 | YES | YES | 19930205 | 1993-11-16 | 2392 | CITIZENS GAS & COKE UTILITY | 2425 EAST 30TH STREET | INDIANAPOLIS | MARION | IN | 46218 | 0 | YES | 1020 | 1993-10-30 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19931030 | 21 | 40 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | METER SET ASSEMBLY |  | OTHER | RELIEF | STEEL |  | 1 | 0 |  | FISHER | 0 | 1989 | ABOVE GROUND |  | EARLE D. STEVENSON - DIRECTOR OF DISTRIBUTION | 3179274626 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 1" RELIEF VALVE BLEW BECAUSE OF A PROCEDURAL ERROR WHILE ATTEMPTING TO ISOLATE 23M-125 METER FOR REMOVAL. GAS IGNITED FROM UNKNOWN SOURCE AS EMPLOYEES WERE ATTEMPTING TO TURN OFF AT 2" 1/4 TURN PLUG VALVE. PART 4 - ORIGIN OF THEINCIDENT - GAS ESCAPED FROM 1" FISTHER 289H RELIEF VALVE.
2025-01-31 10:21 | YES | NO | 19930207 | 1993-11-15 | 15931 | PUBLIC SERVICE CO OF COLORADO | CENTENNIAL BLVD - PLAZA DR. |  | DOUGLAS | CO |  | 3 | NO | 1655 | 1993-11-02 | 0 | 0 | 75000 | 57383.0622 | 138549.5352 | YES | 1 | 25 |  | 19931102 | 48 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | 2306/2406 SDR11 | DRISCO/PLEXCO | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | JOHN STEVENSON - EXECUTIVE FOREMAN | 3175713887 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 2 |  | YES |  |  | TCS CABLE, INC. DID HAVE LOCATES AND LOCATES WERE CORRECT. BACKHOE OPERATOR HIT 2" MAIN, WHEN LOOKING FOR PIPE LINE. CAUSE OF IGNITION OF GAS FIRE IS UNKNOWN.
2025-01-31 10:21 | NO | NO | 19930210 | 1993-12-03 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 13-15 WILLIAM STREET | BLOOMINGDALE | PASSAIC | NJ | 07403 | 3 | NO | 1005 | 1993-11-15 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 0 | 5 |  | 19931115 | 53 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.154 |  |  | 0 | 1960 | WITHIN/UNDER BUILDING |  | C.W. GREVENITA - VICE PRESIDENT GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON 11/15/93, AT APPROXIMATELY 10:05 AM, AN EXPLOSION AND FIRE OCCURRED AT 13-15 WILLIAMS STREET, BLOOMINGDALE, CAUSING EXPTENSIVE PROPERY DAMAGE AND MINOR FACIAL INJYURY TO ONE RESIDENT INVESTIGATION DISCLOSEC A BACKHOE OPERATED BY N. FARRO CONSTRUCTION COMPANY HAD BEEN WORKING IN THE VICINITY OF THE GAS SERVICE PRIOR TO THE INCIDENT. NO MARKOUT HAD BEEN REQUESTED AT THIS ADDRESS. THE 3/4" PSI DESIGN STEEL SERVICE HAD BEEN STRUCK APPROXIMATELY HAF WAY FROM THE CURB TO THE HOUSE CAUSING SEPARATION AT THE OUTLET SIDE OF THE INSIDE SHUT OFF. THE IMMEDIATE CAUSE OF IGNITION IS UNKNOWN. THE GAS WAS SHUT OFF TO THE BUILDING AT 10:15AM.
2025-01-31 10:21 | YES | NO | 19930212 | 1993-12-08 | 11032 | LACLEDE GAS CO | 124,126,128 E.STEINS&7700,7702,7704 S.B | ST LOUIS |  | MO |  | 3 | NO | 530 | 1993-11-04 | 0 | 0 | 500000 | 382553.7478 | 923663.5677 | Null | 1 | 30 |  | 19931104 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | WELD | GIRTH | STEEL |  | 8 | 0 |  |  | 0 | 1927 | UNDER PAVEMENT |  | PAUL B. HUNKER JR - ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | THE INVESTIGATION IS CONTINUING AS TO THE CAUSE OF THE WELD FAILURE ON THE 8- INCH S.I.P. MAIN. THE FAILURE WAS APPROXIMATELY 280 DEGREES AND THE SEPARATION APPROXIMATELY 1/2 TO 5/8 INCHES. THERE WARE APPARENTLY TWO SEPARATE EXPLOSIONS IN THE INCIDENT. AT APPROXIMATELY 0530 HOURS AT 124,126,128 E. STEINS AND APPROXIMATELY 0608 HOURS AT 7700-7702-7704 S. BROADWAY.
2025-01-31 10:21 | NO | NO | 19930213 | 1993-12-08 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 8 SOUTH, 566 WEST HILL STREET | VALPARAISO | PORTER | IN | 46383 | 3 | NO | 1330 | 1993-11-05 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 1 | 30 |  | 19931105 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | KENNETH FOLEY - MANAGER GAS CONTROL & STORAGE | 2198535603 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-10-26 | YES | 3 | PAINT | YES |  |  | AN EXCAVATOR STRUCK A MARKED RESIDENTIAL SERVICE LINE, PULLING IT AND CAUSING AN ELBOW AT THE RISER TO BREAK, WHICH ALLOWED THE UNDERGROUND RELEASE OF NATURAL GAS. THIS GAS MIGRATED INTO THE RESIDENCE, WHERE IT BECAME IGNITED, CAUSING PROPERTY DAMAGE.
2025-01-31 10:21 | YES | YES | 19930214 | 1993-12-08 | 4499 | ENTEX - DIVISION OF ARKLA INC | 15693 FM 2493 | TYLER | SMITH | TX | 75703 | 3 | NO | 1600 | 1993-10-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19931011 | 300 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  | ROCKWELL | 0 | 1987 | ABOVE GROUND |  | LANNY W. CARGILE PE - SENIOR ENGINEER | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GRND-NO EXCAVATION | NO |  |  | PART B- ADDITIONAL INFORMATION - CUSTOMER OPENED REGULATOR BYPASS, ALLOWING UPSTREAM HIGH PRESSURE TO ENTER METER, OVERPRESSURING AND BURSTING METER CASE. FLYING DEBRIS CAUSED INJURY.
2025-01-31 10:21 | YES | NO | 19930216 | 1993-12-16 | 13299 | NEW JERSEY NATURAL GAS CO | INTERSECTION OF HECK & DRUMMOND AVE. | NEPTUNE | MONMOUTH | NJ | 07753 | 3 | NO | 1458 | 1993-11-04 | 0 | 0 | 400000 | 306042.9983 | 738930.8542 | Null | 3 | 2 |  | 19931108 | 47 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING | STEEL TEES | STEEL |  | 4 | 0.237 |  |  | 0 | 1965 | UNDER PAVEMENT |  | MONIQUE HERZOG - ENGINEER COMPANY QUALITY CONTROL | 9089381193 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-09-28 | YES | 3 | PAINT | YES |  |  | ON THURSDAY, NOVEMBER 4, 1993, A REPORT OF A "CAR FIRE-POSSIBLE BROKEN LINE"AT 201 DRUMMOND AVENUE WAS RECEIVED BY NEW JERSEY NATURAL GAS COMPANY (NJNG)AT 2:58 P.M. BOTH A DISTRIBUTION CREW AND AN APPLIANCE SERVICEPERSON WERE DISPATCHED TO THE SITE. THEY ARRIVED SIMULTANEOUSLY AT 3:08 P.M. AND REQUESTED SUPERVISION. ROY HULSE, DISTRIBUTION SUPERVISOR ARRIVED AT APPROXIMATELY 3:30P.M.. AT 3:38 P.M., ROY CALL A "CODE 1000" (ORDER TO ALL PERSONNEL TO SUSPEND ALL RADIO TAFFIC AND STANDY TO RESPND TO AN EMERGENCY). HE ALSO REQUESTED ADDITIONAL MANPOWER TO SHUT DOWN THE LINE. SCOT MACOMBER, GENERAL MANAGER - FIELD SERVICES, NOTIFIED THE BRC BY TELEPHONE AT 4:37 P.M. WHEN IT WAS ESTIMATED THAT NEARLY 1,000 CUSTOMER WOULD BY WITHOUT GAS WHEN THE LINE WAS SHUT DOWN.A MILLING MACHINE FROM CARDELL, INC. OF 1000 INDUSTRIAL RAD, KEASBY, NJ 08832, HAD DAMAGED TOWN 2" STEEL TEES WELDED TO 4" STEEL, HIGH PRESSURE MAIN IN THE INTERSECTION OF HECK AVENUE AND DRUMMOND AVENUE IN NEPTUNE. THE SYSTEM, WITH AN MAOP OF 60 PSIG, WAS OPERATING AT APPROXIMATELY 50 SIG AS INDICATED BY THE CHARTS FROM THE NEAREST REFULATOR STATION, ASBURY CIRCLE STATION. THE THREE MEN OPERATING THE MACHINE MOVED TO SAFETY WHEN THEY REALIZED THE GAS LINE HAD RUPTURED. THE ESCAPING GAS SUBSEQUENTLY IGNITED, DESTROYING THE MILLING MACHINE AND CAUSING MINOR DAMAGED TO THE SIDING OF 148 DRUMMOND AVENUE AND TO OVERHEAD TELEPHONE LINES. THERE WERE NO INJURIES REPORTED. THE FIRE DEPARTMENT KEPT THE FIRE UNDER CONTROL BUT DID NOT EXTINGUISH IT UNTIL THE GAS LEAK WASSHUT OFF AT THE REQUEST OF NJNG. ALL AVAILABEL FIELD PERSONNEL WERE MOBILIZED TO SHUT OFF THE CUSTOMERS IN THE AFFECTED AREA WHILE A CREW STOOD BY, PREPARED TO SQUEEZE-OFF THE 4" STEEL MAIN ON HECK AVENUE EAST OF ROUTE 35. AT 6:00P.M. ALL METERS WERE OFF THE MAIN WAS SQUEEZED OFF, CONTROLLING THE FIRE. TO EFFECT A COMPLETE SHUT-DOWN, A STOPPER WAS SUBSEQUENTLY INSTALLED AT 8:22P.M.WHICH ISOLATED THE SYSTEM AND EXTINGUISHED THE FIRE COMPLETELY. THE MAIN WASTHEN RETIRED ON THE EITHER SIDE OF THE INTERSECTION. THERE WERE 185 SERVICESINVOLVED. THE SERVED APPROXIMATELY 500 CUSTOMERS, INCLUDING THE NEPTUNE AND ASBURY PARK HOUSING AUTHORITY COMPLEXESS. CONTRUCTION CREWS WORKED OVERNIGHT TO SUPPLY THE AFFECTED SYSTEM BY CONNECTING TO THE 2" MAIN ON BORDEN AVENUE. THIS WAS COMPLETED AT 8:15 A.M. ON NOVEMBER 5, 1993. RELIGHTS BEGAN AT 8:30 A.M. AND SERVICE WAS RESTORED TO ALL BUT 38 SERVICES. A NEW 4" PLASTIC MAIN WAS INSTALLED TO TIE THE SYSTEM BACK TOGETHER ACROSS THE INTERSECTION OF HECK AND DRUMMOND. RELIGHTS FOR THE REMAINING 38 SERVICES BEGAN AT 12:15A.M. ON SATURDAY MORNING AND WERE COMPLETED BY 2:00 A.M. AT 4:30 P.M. ON MONDAY, NOVEMBER 8, 1993, A PRELIMINARY ESTIMATE OF THE COST OF THE MILLING MACHINE WAS MADEAT $100,000 TO $200,000 AND TELEPHONE REPORT WAS MADE TO THE D.O.T. AS REQUIRED BY CFR 49, PARY 191.5. THE REPLACEMENT COAST OF THE MILLING MACHINE IS NOW ESTIMATED AT #379,000. TOTAL DAMAGES ARE ESTIMATED AT $400,000. EVENTS LEADING TO THE INCIDENT- THE MILLING WAS BEING DONE AS THE FINAL PHASE OF A NEPTUNE TOWNSHIP DRAINAGE IMPROVEMENT PROJECT. NEW JERSEY NATURAL GAS COMPANY'S OPERATIONS TECHNICIAN, STEVE, MCGRATH, COORDINATED NUMEROUS GAS MAIN CONFLICTS WITH BIRDSALL ENGINEERING WHO WAS HANDLING THE PROJECT FOR THE TOWNSHIP. THE GAS MARK-OUT WAS LAST CHECKED ON SEPTEMBER 30, 1993. NINE MARK-OUT REQUEST WERE RECEIVED AND COPLETED OVVER THE DURATIONOF THE PROJECT THE MOST RECENT REQUEST WAS RECEIVED ON SEPTEMBER 28, 1993 WHEN CARDELL DAMAGED A GAS SERVICE TO207 DRUMMOND AVENUE. IN JULY AND AUGUST OF THIS YERA, NJNG LOWERED A 2" STEEL MAIN IN CONFLICT WITH THE SAME PROJECT. AT THAT TIME, IT WAS NOTED THAT THE
2025-01-31 10:21 | NO | NO | 19930217 | 1993-12-16 | 13299 | NEW JERSEY NATURAL GAS CO | DOVER ROAD AT CORNELL ROAD | SOUTH TOMS RIVER | OCEAN | NJ | 07719 | 2 | NO | 922 | 1993-11-15 | 0 | 0 | 20000 | 15302.1499 | 36946.5427 | Null | 1 | 43 |  | 19931115 | 30 | 60 | BY TEST | 94 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 |  |  | 0 | 1960 | UNDER PAVEMENT |  | MONIQUE HERZOG - ENGINEER COMPANY QUALITY CONTROL | 9089381193 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DAMAGE CAUSED BY ARC FROM DOWNED OVERHEAD ELECTRIC LINE. PART 3 NARRATIVE- AT APPROXIMATELY 9:00 A.M. ON NOVEMBER 15, 1993, RESIDENTS OF DOVER ROAD, S. TOMS RIVER, NEW JERSEY REPORTED AN OVERHEAD ELECTRIC LINE WAS CRACKLING AND ARCING. AT 9:22 A.M. , NEW JERSEY NATURAL GAS COMPANY RECEIVED A TELEPHONIC REPORT OF A FIRE IN A CATCH BASIN AT DOVER ROAD AND CORNELL ROAD. A 19, 500 KVA ELECTRIC LINE HAD SHORTED OUT AT A TRANSORMER AND DROPPED TO THE GROUND STRIKING A METAL CATCH BASIN. THE STORM DRAIN LEAKING AWAY FROM THE CATCH BASIN WAS MAKDE OF CORRUGATED ALUMINUM AND ACARRIED THE CURRENT ROUGHLY 600 FEET TO ANOTHER CATCH BASIN WHERE FURTHER ARCING OCCURRED. THE DRAIN LEAVING THE SECOND BASIN CROSSED THE ROAD APPROXIMATELY 3: ABOVE A 4: STEEL GAS MAIN. AN ELECTRIC AND 3/4" DIAMETER HOLE THROUGH THE WALL OF THE STEEL PIPE. THE HIGH PRESSURE MAIN WAS OPERATING AT APPROXIMATELY 30 PSIG AND THE ESCAPING GAS ENTERED THE DRAIN AND FLOWED BACK TO THE SECOND CATCH BASIN WHER IT WAS IGNITED BY THE ELECTRIC SPARKS. SIX HOMES WERE EVACUATED AS A PRECAUSTION BUT THE ONLY DAMAGE WAS TO OVERHEAD UTIITIES AND WOODS ON ADJACENT PARK LAND. THE D.O.T. WAS NOTIFIED BY TELEPHONE WHEN IT WAS DISCOVERED THAT ONE OF THE DAMAGED LINES WAS A FIBER OPTICS CABLE AND THE LOSS WAS EXPECTED TO EXCEED %50,000. HOWEVER THE LINE WAS NOT OPERATIONAL AND THE ESTIMATE HAS BEEN REVISED TO $20000,, INCLUDING THE COST OF THE 40,635 CUBIC FEET OF LOST GAS. THE MADE SAFE TIME WAS11:05 A.M. WHEN THE FIRE WAS EXTINGUISHED. THE DAMAGED GAS LINE WAS REPLACEDAND ALL RELIGHTS WERE COMPLETED BY 11:00 P.M.
2025-01-31 10:21 | NO | NO | 19940001 | 1994-01-04 | 11720 | LONG ISLAND LIGHTING COMPANY | WAVERLY AVENUE | HOLTSVILLE | SUFFOLK | NY | 11742 | 4 | NO | 1120 | 1993-12-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19931216 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | UNKNOWN | FITTING |  | OTHER | 8" DRESSER COUPLING | 0 | 0 |  | DRESSER | 0 | 0 | UNDER GROUND OR UNDER WATER |  | THOMAS E. LUPSKI - CODE AND SPECIFICATIONS ENGINEER | 5169334400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON DECEMBER 15, 1993, AN INSULATED DRESSER COUPLING WAS INSTALLED ON A TEN (10) FOOT SECTION OF EIGHT (8) INCH GAS MAIN BETWEEN TWO VALVES. THE VALVES WERE CLOSED, HOWEVER, ONE OF THE GAS VALVES WAS NOT TIGHTLY SEALED. THE DRESSERCOUPLING WAS TORQUED, TESTED FOR LEAKAGE AND LEFT IN PLACE THROUGH THE NIGHT.ON DECEMBER 16, 1993, THE DRESSER COUPLING WAS LEAK TESTED (BY SOAPY WATER) PRIOR TO COMMENCING ANY WELDING OPERATIONS. THE WELDER RETURNED TO THE LOCATION TO WELD ON THE DRESSER COUPLING REINFORCING LUG SUPPORTS. AS A RESULT OF THE BUILD-UP OF PRESSURIZED NATURAL GAS IN THE 10 FOOT SECTION OF MAIN BETWEENTHE TWO VALVES, THE PIPE PULLED APART AT THE DRESSER COUPLING AND RELEASED NATURAL GAS INOT THE AREA OF THE WELDER'S ARC CAUSING SUBSEQUENT IGNITION. THELONG ISLAND LIGHTING COMPANY PLACED A TELEPHONIC NOTIFICATION TO THE DEPARTMTENT OF TRANSPORTATION BASED UPON THE PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF THE INCIDENT. THIS INFORMATION INDICATED THE TWO (2) LILCO EMPLOYEES SUSTAINED BURNS AND WERE BEING TRANSPORTED TO THE HOSPITAL. SUBSEQUENT INVESTIGATION REVEALED THAT THE TWO (2) INJURED LILCO EMPLOYEES DIDNOT REQUIER IN-PATIENT HOSPITALIZATION. PART D - OTHER -BRIEF DESCRIPTION CHRONOLOGICAL SEQUENCE OF EVENTS. 12/16/93 11:20 TWO (2) LILCO EMPLOYEES WERE BURNED WHILE INSTALLING A DRESSER COUPLING. 12/16/93 11:30-16:30 THE TWO (2) INJURED LILCO EMPLOYEES WERE TRANSPORTED TO AN AREA HOSPITAL AND WERE SUBSEQUENTLY TREATED AND RELEASED.
2025-01-31 10:21 | NO | NO | 19940002 | 1994-01-04 | 15359 | PEOPLES NATURAL GAS | 208 5TH STREET | WATERLOO | DOUGLAS | NE | 68102 | 3 | NO | 230 | 1994-01-14 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 2 | 0 |  | 19940114 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | UNKNOWN | OTHER | UNKNOWN | 10 | 1.33 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | GREGORY J. BENAK - SR. ATTORNEY | 4022212021 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | POWER SURGE CAUSED OVERHEAD ELECTRICAL DISTRIBUTION WIRE TO FALL ON METER SETALLOWING ELECTRICAL CURRENT ON GAS SERVICE LINE TO ARC ACROSS AN INSULATOR, THEREBY MELTING A HOLE IN THE SERVICE LINE AND ALLOWING GAS TO ESCAPE INTO HOUSE AND IGNITE. PART 3 - BROKEN POWER LINE COMING IN CONTACT WITH METER SET.
2025-01-31 10:21 | YES | YES | 19940003 | 1994-01-04 | 18484 | SOUTHERN CALIFORNIA GAS CO | VANOWEN BLVD. & DESOTO STREET | CANOGA PARK | LOS ANGELES | CA | 91304 | 3 | NO | 1325 | 1993-12-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19931214 | 40 | 45 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | UNKNOWN | POLYETHYLENE PLASTIC |  | 3 | 0.312 | ASTM 2513 | PLEXCO | 1993 | 1993 | UNDER GROUND OR UNDER WATER |  | GARY J. LAMBETH - MANAGER OF SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SOUTHERN CALIFORNIA GAS COMPANY CREW WAS MAKING PREPARATIONS TO TIE IN ANEWLY INSTALLED 3" POLYETHYLENE PLASTIC MAIN TO AN EXISTING 3" POLYETHYLENEPLASTIC MAIN. TO ACCOMMODATE THE TIE-IN, THE EXISTING MAIN WAS PINCHEDAPPROXIMATELY 3 FEET FROM ITS END. THIS 8 FEET OF PIPE WAS BEING PURGED OFNATURAL GAS THROUGH A 3"X1/2" PUNCH TEE. DURING THIS PROCESS, THE ESCAPINGGAS IGNITED, CAUSING BURNS TO THE EMPLOYEE PERFORMING THE PURGE OPERATION. THEFLOW OF GAS WAS IMMEDIATELY BROUGHT UNDER CONTROL BY ANOTHER EMPLOYEE WHOSHUT THE GAS OFF AT THE PUNCH TEE. IT WAS DETERMINED THAT THE PINCH MADE ONTHE EXISTING 3" MAIN WAS NOT SUFFICIENTLY TIGHT ENOUGH TO STOP THE FLOW OFGAS, WHICH CAUSED A MUCH LARGER AMOUNT OF GAS TO BE PRESENT THAN ANTICIPATED.IT HAS BEEN FURTHER DETERMINED THAT THE PROBABLE SOURCE OF IGNITION WAS ALIGHTED BUTANE BURNER LOCATED NEAR THE EXCAVATION BEING USED TO HEAT A FUSINGIRON IN PREPARATION FOR THE TIE-IN. ATTACHED IS A REPORT OF AN INCIDENT WHICHOCCURRED AT THE INTERSECTION OF VANOWEN BLVD. AND DESOTO STREET IN THE CITY OFCANOGA PARK, LOS ANGELES COUNTY. ON DECEMBER 13, 1993, AT APPROXIMATELY 1:25P.M., A SOUTHERN CALIFORNIA GAS COMPANY CREW WAS MAKING PREPARATIONS TO TIEIN A NEWLY INSTALLED 3" POLYETHYLENE PLASTIC MAIN TO AN EXISTING 3"POLYETHYLENE PLASTIC MAIN. TO ACCOMMODATE THE TIE-IN, THE EXISTING MAIN WASPINCHED APPROXIMATELY 8 FEET FROM ITS END. THIS 8 FEET OF PIPE WAS BEINGPURGED OF NATURAL GAS THROUGH A 3" X 1/2" PUNCH TEE. DURING THIS PROCESS, THEESCAPING GAS IGNITED, CAUSING BURNS OT THE EMPLOYEE PERFORMING THE PURGEOPERATION. THE FLOW OF GAS WAS IMMEDIATELY BROUGHT UNDER CONTROL BY ANOTHEREMPLOYEE WHO SHUT THE GAS OFF AT THE PUNCH TEE. IN REVIEWING THE INCIDENT, ITWAS DETERMINED THAT THE PINCH MADE ON THE EXISTING 3" MAIN WAS NOTSUFFICIENTLY TIGHT ENOUGH TO STOP THE FLOW OF GAS, WHICH CAUSED A MUCH LARGERAMOUNT OF GAS TO BE PRESENT THAN ANTICIPATED. IT HAS BEEN FURTHER DETERMINEDTHAT THE PROBABLE SOURCE OF IGNITION WAS A LIGHTED BUTANE BURNER LOCATED NEARTHE EXCAVATION BEING USED TO HEAS A FUSING IRON IN PREPARATION FOR THE TIE-IN.THE INCIDENT CAUSED ONE INJURY THAT RESULTED IN EMERGENCY TREATMENT ANDCONFINEMENT BEYOND THE TREATMENT FOR OBSERVATION. THERE WERE NO EVACUATIONSOR STREET CLOSURES. NO DOLLAR DAMAGE TO COMPANY FACILITIES OR TO THE PROPERTYOF OTHERS WAS INCURRED. DOT NOTIFICATION ON DECEMBER 14, 1993;REFERENCEREPORT #212504. FURTHER REVIEW 1/12/95 INDICATES A RECLASSIFICATION IN PART 5- ENVIRONMENT FROM "OTHER - UNKNOWN" TO "UNDERGROUND/UNDER WATER." CHANGESNOTED IN SYSTEM 1/18/95. ALSO, LOCATION OF SERVICE LINE IS DESCRIBED IN PART D.
2025-01-31 10:21 | NO | NO | 19940005 | 1993-12-24 | 15007 | PACIFIC GAS & ELECTRIC CO | #1 LAKE HERRMANN ROAD | VALLEJO | SOLANO | CA | 94590 | 1 | NO | 1335 | 1993-12-01 | 0 | 0 | 50000 | 38255.3748 | 92366.3568 | Null | 3 | 58 |  | 19931201 | 600 | 675 | BY TEST | 1350 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 24 | 0.312 | API 5LX GRX52 | UNKNOWN | 1966 | 1966 | UNDER GROUND OR UNDER WATER |  | JAMES H. POPE - VICE PRESIDENT TECH & CONSTRUCTION SERV. | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | PART 3 - A SYAR INDUSTRIES EMPLOYEE STRUCK AND DMAGED A 24-INCH STEEL TRANSMISSION LINE 210 WHILE GRADING A ROAD WITH A BULLDOZER.
2025-01-31 10:21 | NO | NO | 19940006 | 1993-12-24 | 15007 | PACIFIC GAS & ELECTRIC CO | 1608 DWIGHT LANE | MODESTO | STANISLAUS | CA | 95351 | 3 | NO | 800 | 1993-11-25 | 0 | 0 | 60000 | 45906.4497 | 110839.6281 | YES | 1 | 20 |  | 19931125 | 0.25 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S FLEX LINE | BODY OF PIPE |  | OTHER | FLEX CONNECTOR | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES H. POPE - VICE PRESIDENT TECH & CONSTRUCTION SERVICES | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PART 3- BROKEN FLEX LINE AT RANGE, ESCAPING GAS IGNITED AT FURNACE. STRUCTURE FIRE RESULTED. PART D - FLEX CONNECTOR AT RANGE WAS PARTIALLY SEVERED. THE CAUSE IS UNKNOWN. ESCAPING GAS IGNITED AT A FORCED AIR FURNACE RESULTING IN AFIRE WHICH DESTROYED THE HOUSE. THE HOUSE WAS UNOCCUPIED AT THE TIME OF THE INCIDENT.
2025-01-31 10:21 | YES | YES | 19940007 | 1994-01-14 | 2596 | COLUMBIA GAS OF OHIO INC | 5260 BROAD BOULEVARD | NORTH RIDGEVILLE | LORAIN | OH | 44039 | 3 | NO | 900 | 1993-12-16 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19931220 | 40 | 45 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.109 | PE 2406 | DRISCO #6500 | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS - MANAGER CONSTRUCTION & MAINTENANCE | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON THURSDAY, DECEMBER 16, 1993, AT APPROXIMATELY 9:00 A.M., COLUMBIA GAS OF OHIO, INC. (COLUMBIA) DISPATCHED AN EMPLOYEE TO A NORTH RIDGEVILLE CITY STORMSEWER CONSTRUCTION SITE TO LOCATE AND MONITOR SEWER CONSTRUCTION. WHILE THERE HE RELOCATED A 1-INCH DIAMETER PLASTIC SERVICE LINE FOR THE CITY CREW. THECOLUMBIA EMPLOYEE ATTEMPTED TO SQUEEZE OFF THE SERVICE WITH A SCREW JACK BUTCOULD NOT SEAT THE JACK AND ELECTED TO CUT THE LINE, ASSUMING IT WAS LOW PRESSURE. AFTER THE CUT WAS MADE, HE REALIZED HE WAS ON A HIGHER PRESSURE LINE (40 PSIG) AND NEEDED AND EXPANSION PLUG. WHILE INSERTING THE PLUG, THE GAS IGNITED AND BURNED THE COLUMBIA EMPLOYEE AND A NORTH RIDGEVILLE CITY EMPLOYEE. THE COLUMBIA EMPLOYEE EXITED THE HOLE, CALLED FOR ASSISTANCE ON HIS RADIO AND EXTINGUISHED THE FIRE. BOTH EMPLOYEES WERE TREATED AND RELEASED FROM ST. JOHN'S WEST SHORE HOSPITAL IN WESTLAKE. A NEARBY COLUMBIA CREW HEARD THE RADIO CALL AND WENT TO THE SCENE AT 9:15 A.M. AND MADE CONDITIONS SAFE. ON FRIDAY, DECEMBER 17, 1993 THE COLUMBIA EMPLOYEE EXPERIENCED DISCOMFORT AND WAS ADMITTEDTO THE CLEVELAND METRO BURN CENTER AND WAS RELEASED ON DECEMBER 27, 1993. (THIS HOSPITALIZATION MADE THE INCIDENT, REPORTABLE WHEN THE COMPANY FIRST BECAME AWARE OF THE EMPLOYEE'S READMISSION ON DECEMBER 20,1993.)
2025-01-31 10:21 | YES | NO | 19940008 | 1994-02-03 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 890 VAN HOUTEN AVE | CLIFTON | PASSAIC | NJ | 07011 | 3 | NO | 947 | 1994-01-09 | 0 | 0 | 500000 | 374395.7919 | 903966.4487 | Null | 1 | 48 |  | 19940109 | 10.75 | 15 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.5 |  |  | 0 | 1956 | UNDER PAVEMENT |  | C.W. GREVENITZ - VICE PRESIDENT GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JANUARY 9, 1994, AT APPROXIMATELY 11:05 P.M. AND EXPLOSION OCCURRED AT VANHOUTEN AUTO PARTS #890 VAN HOUTEN AVENUE CLIFTON,CAUSING EXTENSIVE PROERTY DMAGE TO #890 VAN HOUTEN AVENUE AND ADDITIONAL DMAGE TO FOUR SURROUNDING BUILDINGS AND PARKED VEHICLES. NO INJURIES WERE REPORTED. THE AREA WS VENTILATED AND INVESTIGATION REVEALED A CIRCUMFERENTIAL CRACK ON 12" 15 PSI CAST IRON MAIN. APPROXIMATELY 50 FEET FROM #890 HOUTEN AVENUE.
2025-01-31 10:21 | YES | YES | 19940010 | 1993-12-24 | 30516 | WEST VIRGINIA POWER GAS SERVICE | INTERSECTION OF OAK ST & S. RITTER DR. | BEAVER | RALEIGH | WV |  | 3 | NO | 811 | 1993-11-22 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19931122 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JERRY L. STONE - DIR GOVERNMENTAL COMPL. | 3046477049 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A RALIEGH COUNTY PUBLIC SERVICE DISTRICT EMPLOYEE ENTERED A 4' X 8' UNDERGROUND VAULT TO RECORD WATER METER READINGS. INFORMATION GATHERED LEAD US TO BELIEVE THE EMPLOYEE LIT A CIGERETTE LIGHTER TO PROVIDE LIGHT TO READ THE LARGE CAPACITY TRANSFER POINT SALES METERS AND FIRE OCCURRED CAUSING BURNS TO THE EMPLOYEE.
2025-01-31 10:21 | YES | NO | 19940011 | 1994-02-03 | 1640 | BOSTON GAS CO | 787 FELLSWAY WEST | MEDFORD | MIDDLESEX | MA | 02155 | 1 | NO | 2236 | 1994-01-14 | 0 | 0 | 75000 | 56159.3688 | 135594.9673 | Null | 1 | 45 |  | 19940115 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 |  |  | 0 | 1927 | UNDER GROUND OR UNDER WATER |  | ROBERT J. CAVICCHI - MANAGER | 6177235512 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 2,100 HOURS THE OWNER/OCCUPANT OF 787 FELLSWAY WEST WENT TOHIS BASEMENT TO INVESTIGATE A GAS ODOR. HE THEN RETURNED TO HIS LIVING QUARTERS. AT APPROXIMATELY 2236 HOURS HE HEARD A "THUD". HE THEN OBSERVED FLAMES ON THE LEFT SIDE OF HIS HOUSE AND THE FRONT WALL WAS BLOWN OUT. THE OCCUPANTS (TWO ) LEFT THE PREMISES UNINJURED. A LEAK INVESTIGATION WAS CONDUCTED AND ONE-HALF CIRCUMFERENTIAL BREAK WAS FOUND ON A 6" LOW PRESSURE CAST IRON MAIN.
2025-01-31 10:21 | YES | NO | 19940012 | 1994-02-01 | 18112 | SAN DIEGO GAS & ELECTRIC CO | 3085 UNIVERSITY AVENUE | SAN DIEGO | SAN DIEGO | CA | 92104 | 3 | NO | 1330 | 1994-01-03 | 0 | 0 | 800000 | 599033.267 | 1446346.3179 | Null | 0 | 35 |  | 19940103 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | VALVE |  | CAST IRON |  | 0.75 | 0 |  |  | 1949 | 1949 | ABOVE GROUND |  | E.L. MORRISON - MANAGER-CLAIMS ADMIN | 6196995011 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A 3/4 INCH GS RISER WAS BROKEN OFF BELOW THE STOP COCK BY A HIT AND RUN VEHICLE CONTACT. THE GAS WAS BLOWING INTO THE REAR DOORWAY OF THE BUILDING. THE RISER WAS APPROXIMATELY THREE FEET FROM THE DOORWAY. THE GAS WAS IGNITED BY ANUNKNOWN IGNITION SOURCE WHICH RESULTED IN A FIRE THAT COMPLETELY DESTROYED THE BUILDING.
2025-01-31 10:21 | YES | NO | 19940013 | 1994-02-04 | 15469 | PHILADELPHIA GAS WORKS | 3149 ARAMINGO AVENUE | PHILADELPHIA | PHILADELPHIA | PA | 19134 | 3 | NO | 1522 | 1994-01-10 | 0 | 0 | 120000 | 89854.99 | 216951.9477 | Null | 0 | 45 |  | 19940110 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6.9 | 0.043 |  |  | 0 | 1910 | WITHIN/UNDER BUILDING |  | JOSEPH M. CAREY - MANAGER DISTRIBUTION DEPT. | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | THE FOLLOWING IS A DESCRIPTION OF THE FACTORS BELIEVED TO HAVE CONTRIBUTED TO THIS INCIDENT BASED UPON INITIAL ON-SITE FINDINGS.THE INITIAL REPORT TO PGWFROM THE PHILADELPHIA FIRE DEPARTMENT WAS A BUILDING COLLAPSED AT 1522 ON JANUARY 10, 1994. UPON ARRIVAL AT 1539, THE FIRE MARSHALL REPORTED AND EXPLOSION AND FIR AT THE 3149 ARAMINGO AVENUE WITH NO PERSONAL INJURIES. THE ODOR OF NATURAL GAS WAS DETECTED AT THE FRONT FOUNDATION WALL TO 3149. THE GAS METERSTO 3145, 3149, 3151, 3153 AND 3157 WERE SHUT OFF. INVESTIGATION OF THE GAS LEAK DISCOVERED A 6" CAST IRON MAIN AHD SUSTAINED A CIRCUMFERENTIAL BREAK IN FRONT OF 3149 ARAMINGO AVENUE IN THE ROADWAY, 3'6" WEST OF THE EAST CURB OF ARAMINGO AVENUE AND 406'6" SOUTH OF THE SUTH CURB OF ALLEGHENY AVENUE. THE BREAK WAS 21"6" FROM THE FRONT FONDATION WALL OF 3149, APPROXIMATELY 4" FROM THE PARTY LINE OF 3147 ARAMINGO AVENUE. THE BREAK IS BELIEVED TO HAVE BEEN CAUSEDBY STRAIN INDUCED FROM SEWER REPAIR OPERATIONS TO A SEWER LATERAL THAT WAS RECENTLY INSTALLED UNDER THE GAS MAIN, EVIDENCED BY NEW PAVING (CONCRETE) WHEREBELGIUM BLOCK UNDER ASPHALT HAD PREVIOUSLY EXISTED. OBSERVATION OF 6" OF FROST BELOW THE OPENING WAS ALSO OBSERVED AT THE TIME OF EXCAVATION WHICH IS BELIEVED TO BE A CONTRIBUTING FACTOR TO THE BREAK. IT IS THOUGHT THAT THE GS FROMTHE LOWER PRESSURE 6" GAS MAIN THEN MIGRATED ALONG THE SOFT TRENCH OF THE SEWER LATERAL, ENTERED THE BASEMENT OF 3149 THROUGH THE FRONT FOUNDATION WALL. THERE CONCENTRATION OF GAS BUILT UP UNDETECTED IN THE BASEMENT WHERE A SOURCEOF IGNITION (UNKNOWN) CAUSED THESUBSEQUENT FIRE AND EXPLOSION. THE BREAK WASREPAIRED TEMPORARILY ON JANUARY 10, 1994. ON JANUARY 11,1994, A SECTION OF THE 6" CAST IRON CONTAINING THE BREAK AREA WAS REMOVED AND IS IN THE CUSTODY OF PGW. PART 3- THIS INCIDENT IS CURRENTLY UNDER INVESTIGATION BY THE PHILA. FIRE DEPT.
2025-01-31 10:21 | YES | YES | 19940014 | 1994-02-04 | 180 | ALABAMA GAS CORP | 2324 WEST FAIRVIEW AVENUE | MONTGOMERY | MONTGOMERY | AL | 36108 | 3 | NO | 820 | 1994-01-12 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 5 |  | 19940112 | 20 | 25 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | ASTM D2513 | PHILLIPS DRISCOPIPE | 1992 | 1993 | UNDER PAVEMENT |  | KENNETH A. SMITH - DIRECTOR - ENGINEERING SVCS. | 2053268474 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A VACANT BUILDING WASUNDER RENOVATION WHEN GAS APPARENTLY ENTERED THE BUILDING AND WAS IGNITED. TWO PERSON WERE INJURED IN THE INCIDENT AND WERE HOSPITALIZED WITH BURN INJURIES. THE SERVICE LINE TO THE BUILDING WAS TESTED FOR LEAKAGE BUT NONE WAS FOUND. A LEAK SURVEY OF THE AREA (PRIMARILY ALL NEW PARKING LOT) WAS PERFORMED AND A PLASTIC SERVICE LINE TO ANOTHER BUILDING ADJOINING THE PARKING LOT WAS FOUND SEVERED.
2025-01-31 10:21 | YES | YES | 19940015 | 1994-01-18 | 13299 | NEW JERSEY NATURAL GAS CO | 55 NEPTUNE BOULEVARD | NEPTUNE TOWNSHIP | MONMOUTH | NJ | 07753 | 1 | NO | 820 | 1993-12-16 | 0 | 1 | 0 | 0 | 0 | Null | 6 | 25 |  | 19931216 | 54 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.375 |  |  | 0 | 1930 | UNDER PAVEMENT |  | MONIQUE HERZOG - QUALITY CONTROL ENGINEER | 9089381193 | EXTERNALLY | LOCALIZED PITTING |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 8:17 A.M. ON THURSDAY DECEMBER 16, 1993, NEW JERSEY NATURALGAS COMPANY'S (NJNG) DISPATCH CENTER RECEIVED A TELEPHONE REPORT OF A "MANHOLE EXPLOSION WITH A BURN VICTIM" FROM THE NEPTUNE POLICE. THE NJNG CONSTRUCTION AND REPAIR CRREW ARRIVED AT 8:35 A.M. AND IMMEDIATELY BEGAN TO CHECK FOR THE PRESENCE OF GAS IN THE MANHOLE WITH A COMBUSTIBLE GAS INDICATOR. THE NJNGFOREMAN, DAVE BOSS, NOTED THAT ALTHOUGH POLICE AND FIRE PERSONNEL WERE ON THE SCENE THERE WAS NO FIRE WHEN HE ARRIVED. DISTRIBUTION SUPERVISOR, ROY C. HULSE, ARRIVED AT APPROXIMATELY 9:00 A.M. AND ASSESSED THE SITUATION. THE NEPTUNE EMERGENCY COORDINATOR WAS ON THE SCENE AND SUPPLIED ROY WITH THE FOLLOWINGDETAILS: TWO EMPLOYEES OF HENKELS AND MCCOY, INC., BURLINGTON, NJ (A LOCAL UTILITY CONTRACTOR) WERE WORKING IN A MANHOLE BELONGING TO NEW JERSEY AMERICANWATER COMPANY. ONE MAN ENTERED THE STRUCTURE AND THE SECOND MAN REMAINED ON TOP. THE MAN IN THE MANHOLE LIT A CIGARETTE LIGHTER. HERE WAS A FLASH, BUT NOSUSTAINED IGNITION. BOTH MEN WERE INJURED AND WERE TAKEN TO JERSEY SHORE MEDICAL CENTER, 1945 ROUTE 33, NEPTUNE NJ. NJNG LATER LEARNED THAT ONE MAN WAS TREATED AND RELEASED AND THE OTHER WAS TRANSFERRED TO ST. BARNABAS MEDICAL CENTER BURN UNIT IN LIVINGSTON, NJ. NO INDICATION OF GAS WAS FOUND IN THE MANHOLE. THE CREW SURVEYED THE STREET FOR LEAKS WITH A COMBUSTIBLE GS INDICATOR. THEY FOUND AN INDICATION OF A LEAK ON THE 12" BARE STEEL GS MAIN IN THE PAVED AREA OF NEPTUNE BOULEVARD APPROXIMATELY 46 FEET FROM THE MANHOLE. THE MAIN WASEXCAVATED AND A PINHOLE SIZED LEAK WAS DISCOVERED IN A 3" LONG 0.15" DEEP "SCRATCH" ON THE BOTTOM OF THE MAIN. A LEAK CLAMP WAS INSTALLED AND THE SITUATION PRONOUNCED SAFE AT 2:45 P.M. THE REPAIR WAS RECHECKED ON DECEMBER 28, 1993IN ACCORDANCE WITH OUR PROCEDURES. DURING THE RECHECK, ANOTHER LEAK INDICATION WAS FOUND APPROXIMATELY 100' FURTHER AWAY. A SECOND REPAIR CLAMP WAS INSTALLED OVER A 1/8" PIT IN THE STEEL PIPE. A CHECK OF THE SYSTEM ODORANT WAS PERFORMED AS PART OF THE INVESTIGATION AND WAS FOUND TO BE ADEQUATE ACCORDING TOCFR 49, PART 192.625. A COPY OF THE REPORT IS ATTACHED. PRIOR TO THIS INCIDENT, THE MAIN WAS SURVEYED FOR LEAKS AS PART OF THE 1993 BARE STEEL SURVEY ANDWAS CLASSIFIED AS AN AREA OF ACTIVE CORROSION ACCORDING TO CFR 49, PART 192.465 (E). BUSINESS DISTRICT AND CURB VALVE LEAK SURVEYS WERE ALSO PERFORMED HERE IN 1993. LEAKS WERE FOUND ON THE METER SETS AT #55 AND #60 NEPTUNE BOULEVARD BUT THERE WERE NO INDICATIONS OF LEAKS ON THE MAIN. DRAWINGS ILLUSTRATING THE SITE ARE ATTACHED ALONG WITH STATEMENTS FROM ROY HULSE AND DAVE BOSS. NJNG PROCEDURES CONCERNING LEAK SURVEYS AND THE REFERENCED LEAK ORDERS ARE ALSO ATTACHED.
2025-01-31 10:21 | NO | NO | 19940017 | 1994-02-02 | 4483 | ENSTAR NATURAL GAS CO | LOT 4, BLK 1 MIDWAY ESTATES | MATANUSKA | SUSITNA BOROUGH | AK | 99654 | 3 | NO | 1315 | 1994-01-25 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 1 | 0 |  | 19940125 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M8000 | PHILLIPS DRISCOPIPE | 1985 | 1985 | ABOVE GROUND |  | DAVID W. BREDIN - MANAGER DISTRIBUTION OPERATIONS | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | A STRUCTURE FIRE WHICH STARTED IN THE KITCHEN, SEVERELY DAMAGED A SINGLE FAMILY HOME LOCATED AT LOT 4, BLK1 MIDWAY ESTATES , WASILLA, ALASKA. THE BUILDING WAS SERVED WITH NATURAL GAS THROUGH A 5/8" NPS, POLYETHYLENE SERVICE LINE OPERATING AT APPROXIMATELY 50 PSIG. THE INTENSE HEAT FROM THE FIRE MELTED THE 5/8" PLASTIC TUBING INSIDE THE STEEL SERVICE LINE RISER ON THE BUILDING. WHENTHE PLASTIC SERVICE LINE MELTED, THERE WAS A RELEASE OF NATURAL GAS. THE GASWAS SHUT OFF BY DIGGING UP THE SERVICE LINE A SAFE DISTANCE FROM THE FIRE AND INSTALLING A PINCHER ON THE SERVICE LINE. NATURAL GAS DID NOT CONTRIBUTE THE CAUSE OF THE FIRE.
2025-01-31 10:21 | YES | YES | 19940022 | 1994-03-08 | 15469 | PHILADELPHIA GAS WORKS | 2452 S. PHILLIP STREET | PHILADELPHIA | PHILADELPHIA | PA |  | 3 | NO | 321 | 1994-01-25 | 1 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 0 | 0 |  | 19940127 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 |  |  | 0 | 1914 | UNDER PAVEMENT |  | JOSEPH M. CAREY - MANAGER DISTRIBUTION DEPT | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19940031 | 1994-03-01 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 63 ROUTE 46 (WINANT AVENUE) | RIDGEFIELD PARK | BERGEN | NJ | 07660 | 3 | NO | 629 | 1994-02-07 | 0 | 2 | 250000 | 187197.8959 | 451983.2243 | Null | 3 | 31 |  | 19940209 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.34 |  |  | 0 | 1933 | UNDER PAVEMENT |  | G.W. GREVENITZ - V.P. GAS OPERATIONS | 2014307797 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON FEBRUARY 7, 1994, AT APPROXIMATELY 6:29 AM A FIRE WAS REPORTED AT #63 ROUTE 46 (WINANT AVE), RIDGEFIELD PARK, N.J. ONCE THE GAS SERVICE WAS CUT-OFF, AN ADDITIONAL INVESTIGATION REVEALED A CIRCUMFERENTIAL CRACK ON A 4" CAST IRONUTILIZATION PRESSURE MAIN LOCATED NINE (9) FEET BEHIND THE CURB. THE CRACK WAS LOCATED APPROXIMATELY 13 FEET FROM THE EASTERN WALL OF THE BUILDING. THE FIRE CAUSED EXTENSIVE DAMAGE TO THE PROPERTY. FOUR (4) PEOPLE WERE HOSPITALIZED; TWO (2) WERE TREATED AND RELEASED, AND TWO (2) WERE ADMITTED.
2025-01-31 10:21 | YES | YES | 19940032 | 1994-02-22 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 4018 W. HANCOCK | DETROIT | WAYNE | MI | 48226 | 3 | NO | 220 | 1994-01-23 | 0 | 1 | 0 | 0 | 0 | Null | 10 | 7 |  | 19940124 | 2 | 2 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NOT GIVEN | CAST IRON |  | 4 | 0 |  |  | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | THADDEUS S. SLIWINSKI - CLAIMS INVESTIGATOR | 3135777024 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEE, USING AIR HAMMER DUE TO FROST, HIT PUBLIC LIGHTING CABLE, WHICH WAS NOT STAKED PROPERLY, EVEN AFTER SECOND CALL WAS PLACED FOR STAKING. EMPLOYEE WAS FLASHED WHEN SPARK FROM CABLE IGNITED LEAKING GAS FROM MAIN.
2025-01-31 10:21 | YES | YES | 19940034 | 1994-03-11 | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 14 FRANKLIN ST & 33 MARKET STREET | WAPPINGERS FALLS | DUTCHESS | NY | 12590 | 3 | NO | 719 | 1994-02-12 | 0 | 1 | 800000 | 599033.267 | 1446346.3179 | Null | 3 | 56 |  | 19940212 | 52 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | UNDER INVESTIGATION | STEEL |  | 8 | 0.277 |  |  | 1929 | 0 | UNDER PAVEMENT |  | DAVID W. MERTE - DIRECTOR GAS OPERATIONS | 9144865521 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON FEBRUARY 12, 1994, AT 7:19 A.M. A FIRE AND EXPLOSION OCCURRED IN A TWOSTORY WOOD FRAME RESIDENCE AT 14 FRANKLIN STREET IN THE VILLAGE OF WAPPINGERSFALLS, N.Y. ONE PERSON, A 50 YEAR OLD MALE, WAS IN THE RESIDENCE AT THE TIMEOF THE EXPLOSION AND HE SUSTAINED INJURIES THAT REQUIRED HOSPITALIZATION. AT7:27 A.M., A SECOND EXPLOSION AND FIRE OCCURRED AT AN AUTO BODY SHOP ON 33MARKET STREET, WHICH IS LOCATED ACROSS THE STREET FROM THE RESIDENCE.ALTHOUGH PROPERTY DAMAGE WAS SUSTAINED, NO INJURIES RESULTED IN THIS SECONDEXPLOSION. THE OFFICE OF PIPELINE SAFETY, DEPARTMENT OF TRANSPORTATION WASTELEPHONICALLY NOTIFIED OF THIS INCIDENT AT 8:20 A.M. ON 02/12/1994. CENTRALHUDSON AND THE NEW YORK STATE PUBLIC SERVICE COMMISSION ARE CONDUCTINGINDEPENDENT INVESTIGATIONS TO DETERMINE THE CAUSE OF THIS INCIDENT. THERESIDENCE AND AUTO BODY SHOP INVOLVED IN THIS INCIDENT DID NOT HAVE NATURALGAS SERVICE. THE RESIDENCE AND THE AUTO BODY SHOP REVEALED THE EXISTENCE OFA CIRCUMFERENTIAL CRACK IN THE HEAT AFFECTED AREA ADJACENT TO A WELD. DURINGTHE INVESTIGATION, IT WAS NOTED THAT THE PIPE WAS BURIED 4 FEET DEEP AND,FURTHER, THAT FROST HAD PENETRATED TO THIS DEPTH. IT WAS ALSO OBSERVED THATTHERE WAS A SLIGHT INDENTATION ON THE TOP OF THE MAIN NEAR THE CRACK. THISINDENTATION EXISTED PRIOR TO THE INCIDENT. INTERVIEWS AND OBSERVATIONS AT THESITE ALSO UNCOVERED THE FACT THAT SEWER EXCAVATION WORK HAD BEEN PERFORMED INTHE VICINITY OF THE CRACK LOCATION NINE MONTHS PRIOR TO THE INCIDENT. THEREMOVED PORTION OF THE STEEL MAIN AND AIR SAMPLES TAKEN IN THE VICINITY OF THEINCIDENT ARE BEING ANALYZED BY INDEPENDENT LABORATORIES TO AID IN DETERMININGTHE CAUSE OF THE INCIDENT. CENTRAL HUDSON IS FULLY COOPERATING WITH THEINVESTIGATION OF THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE. SUPPLEMENTALREPORT 12/22/94 INDICATED THE FOLLOWING: CENTRAL HUDSON GAS & ELECTRICCORPORATION ("CENTRAL HUDSON" OR "THE COMPANY") AND THE ENERGY AND WATERDIVISION ("PSC STAFF") SAFETY AND RELIABILITY OF THE NEW YORK STATE PUBLICSERVICE COMMISSION ("PSC"), CONDUCTED INDEPENDENT INVESTIGATIONS OF THISINCIDENT, WHICH OCCURRED IN THE VILLAGE OF WAPPINGERS FALLS, NEW YORK, ONFEBRUARY 12, 1994 IN THE COMPANY'S SERVICE TERRITORY. THE INCIDENT INVOLVED ANEXPLOSION AND FIRE AT A RESIDENCE AND, A SHORT TIME LATER, AN EXPLOSION ANDFIRE AT A NEARBY COMMERCIAL BUILDING. FOLLOWING THIS INCIDENT, THE COMPANY,IN AGREEMENT WITH THE PSC STAFF, DEVELOPED A PLAN TO ASSESS THE INTEGRITY OFTHE PN LINE TO DETERMINE IF ADDITIONAL MEASURES WERE NECESSARY TO ENHANCE THESAFETY AND RELIABILITY OF THE LINE. SUCH PLAN COMMITS THE COMPANY TO: (1)REPLACE A CERTAIN SECTION OF THE PN LINE, (2) SURVEY THE PN LINE IN THEVILLAGE OF WAPPINGERS FALLS MONTHLY THROUGHOUT THE 1994-95 HEATING SEASON, (3)DEVELOP AN ENHANCED GAS EMERGENCY RESPONSE PLAN AND (4) DEVELOP A GAS SYSTEMEMERGENCY VALVING PLAN AND SCHEDULE. BY REPORT DATED OCTOBER 25, 1994, THE PSCSTAFF ACCEPTED THE COMPANY'S PLAN. THE REPORT WAS ACCEPTED BY THE PSC ONNOVEMBER 9, 1994 AND RECEIVED BY THE COMPANY ON NOVEMBER 10, 1994. THE REPORTCONCLUDES THAT THE PROBABLE CAUSE OF THE INCIDENT WAS AN IGNITION OF GAS THATACCUMULATED IN EACH OF THE STRUCTURES AFTER MIGRATING THROUGH THE GROUND FROMA LEAK IN CENTRAL HUDSON'S HAS MAIN IN THE IMMEDIATE AREA OF THE TWO DESTROYEDBUILDINGS. THE COMPANY CONTINUES TO INVESTIGATE THIS INCIDENT, BUT DISAGREESTHAT THE FACTS KNOWN TO DATE SUPPORT THE CONCLUSIONS IN THE REPORT AS TO THEPROBABLE CAUSE OF THE INCIDENT. THE COMPANY'S INVESTIGATION HAS NOT YETDETERMINED WHAT CAUSED THE FIRST EXPLOSION, WHICH DESTROYED THE RESIDENCE, BUT
2025-01-31 10:21 | YES | NO | 19940036 | 1994-02-04 | 13710 | NORTHERN ILLINOIS GAS CO | 110 S. MONROE | STREATOR | LIVINGSTON | IL | 61364 | 3 | NO | 710 | 1994-01-31 | 0 | 0 | 150000 | 112318.7376 | 271189.9346 | Null | 2 | 20 |  | 19940131 | 55 | 60 | BY TEST | 98 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1981 | UNDER PAVEMENT |  | RICH WOODARD - CONSTR./MAINT. MANAGER | 8154333850 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | YES | NO | 19940037 | 1994-02-10 | 13710 | NORTHERN ILLINOIS GAS CO | 559 PALMER AVE | AURORA | KANE | IL |  | 3 | NO | 1003 | 1994-02-10 | 0 | 0 | 80000 | 59903.3267 | 144634.6318 | Null | 9 | 0 |  | 19940210 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 1953 | UNDER PAVEMENT |  | RONALD KATT - GENERAL SUPERVISOR | 7086292500 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19940038 | 1994-03-08 | 2748 | CONSUMERS POWER CO | 28606 KARAM | MADISON HEIGHTS | OAKLAND | MI | 48071 | 3 | NO | 321 | 1994-02-11 | 0 | 2 | 90000 | 67391.2425 | 162713.9608 | Null | 1 | 24 |  | 19940211 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L,GRB | US STEEL | 0 | 1955 | UNDER GROUND OR UNDER WATER |  | KENNETH L. ELENBAAS - GENERAL SUPERVISOR OF O & M | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | PART 3 - PIPE FAILED AT THIRD-PARTY DAMAGE. GAS MIGRATED INTO HOUSE CAUSING AN EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | YES | 19940039 | 1994-03-16 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 3841 - 14TH STREET | ECORSE | WAYNE | MI | 48229 | 3 | NO | 2256 | 1994-02-13 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 28 |  | 19940214 | 5 | 5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1930 | UNDER PAVEMENT |  | ROGER J. GREGORY - CLAIMS SENIOR INVESTIGATOR | 3135777045 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | GROUND FROST OF APPROXIMATELY 38" TO 40" INCHES RESULTED IN A CIRCUMFERENTIAL FRACTURE OF THE 4" C.I. MAIN.
2025-01-31 10:21 | YES | NO | 19940041 | 1994-02-01 | 22182 | WASHINGTON GAS LIGHT CO | 110 BECKWITH STREET | GAITHERSBURG | MONTGOMERY | MD | 20878 | 3 | NO | 107 | 1994-01-21 | 0 | 0 | 400000 | 299516.6335 | 723173.1589 | Null | 1 | 7 |  | 19940121 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD2513 | DUPOUNT | 1990 | 1990 | WITHIN/UNDER BUILDING | UNDER PAVEMENT | WM. A. HINDE - SUPERVISOR | 7037507687 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | UNKNOWN CONTRACTOR DROVE A 1.5" x 1.5" WOODEN SQUARE STAKE THROUGH A 2" PLASTIC GAS LINE. DURING THE RECENT COLD WEATHER, THE GROUND FROZE CAUSING IT TO HEAVE, PULLING THE STAKE UP AND OUT OF THE HOLE IN THE MAIN. THE LEAKAGE TRAPPED BY THE FROZEN CAP OF SOIL CAUSED THE ESCAPING NATURAL GAS TO FOLLOW UTILITY TRENCH AND CONDUIT INTO THE BASEMENT OF THE STRUCTURE UNTIL IT REACHED A FLAMMABLE MIXTURE AND AN UNKNOWN SOURCE OF THE IGNITED THE NATURAL GAS CAUSINGAND EXPLOSION AND FIRE THAT RESULTED IN TOTAL DESTRUCTION OF THE DWELLING.
2025-01-31 10:21 | YES | YES | 19940042 | 1994-02-13 | 22182 | WASHINGTON GAS LIGHT CO | 4414 BENNING ROAD, NE | WASHINGTON |  | DC |  | 3 | NO | 1518 | 1994-02-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 26 |  | 19940213 | 27 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | VALVE |  | STEEL |  | 12 | 0 | ASTM126 CLASS B | STOCKHAM | 1974 | 1976 | UNDER GROUND OR UNDER WATER |  | JOHN C. SHEA JR. - SAFETY SUPERVISOR | 7037505631 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | THE FACTORS CONTRIBUTING TO THE INCIDENT WERE THE UNUSUALLY COLD WEATHER IN THIS AREA, WHICH CAUSE THE FROST LINE IN THE GROUND TO GO DEEPER THAN NORMAL WHICH CAUSED EXTREME PRESSURE TO BE EXERTED ON THE BOY OF THE 12" VALVE. THISPRESSURE CAUSED THE BODY OF THIS CAST IRON VALVE TO CRACK AT THE CAST FLANGECAUSING GAS TO ESCAPE AND MIGRATE THROUGH THE AIR AND ALSO INTO AN ELECTRIC CONDUIT INTO THE BUILDING AT 4414 BENNING ROAD, N.E. THIS GAS REACHED THE FLAMMABILITY RANGE AND WHEN THE OWNER TURNED OFF AND ELECTRIC SWITH WHILE EXITING THE BUILDING, THIS CAUSED A FLASH WHICH BURNT THE OWNER ON THE HANDS, NECK,FACE AND HAIR.
2025-01-31 10:21 | YES | NO | 19940043 | 1994-02-23 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 1617 PARK AVE | SOUTH PLAINFIELD | MIDDLESEX | NJ | 07080 | 3 | NO | 155 | 1994-01-28 | 0 | 0 | 3000000 | 2246374.7512 | 5423798.6921 | Null | 1 | 30 |  | 19940128 | 28 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1954 | WITHIN/UNDER BUILDING |  | B.S. WAGAMAN - LEAD ENFGINEER | 9086683840 | EXTERNALLY | GENERAL CORROSION |  | OTHER | GENERAL | COATED | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE AND EXPLOSION WAS REPORTED AT A STRIP MALL ON PARK AVE, SOUTH PLAINFIELD. SERVICEMEN AND STREET CREWS RESPONDED TO SHUT OFF THE TWO GAS SERVICES TO THE MALL. A LEAK SURVEY OF THE SURROUNDING AREA WAS PERFORMED WITH NO SIGNIFICANT LEAKAGE FOUND. THE GAS SERVICE TO 1617 PARK AVE, THE PARK AVENUE LUNCHEONETTE, WAS FOUND WITH CORROSION HOLES AT A POINT WHERE THE SERVICE LINE TRAVELS THROUGH THE CINDER BLOCK WALL ENTERING THE CELLAR.
2025-01-31 10:21 | YES | YES | 19940044 | 1994-02-24 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 38-02 22ND STREET | QUEENS |  | NY |  | 4 | NO | 835 | 1994-01-26 | 0 | 2 | 50000 | 37439.5792 | 90396.6449 | Null | 0 | 10 |  | 19940126 | 7 | 12 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.66 |  |  | 0 | 1931 | WITHIN/UNDER BUILDING |  | DANIEL S. POLIN - ENGINEERING TECHNICIAN | 2124603872 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | CREWS RESPONDED TO A REPORT OF AN EXPLOSION AND FOUND HIGH GAS READINGS ALONG 38TH AVENUE BETWEEN 21ST AND 22ND STREETS. AFTER CUTTING AND CAPPING A 12 INCH LOW PRESSURE CAST IRON GAS MAIN, GAS READINGS DISSIPATED. EXCAVATION OF THE GAS MAIN REVEALED A SINGLE CIRCUMFERENTIAL CRACK. THE SECTION OF THE MAINCOANTAINING THE BREAK WAS REMOVED FOR ANALYSIS.
2025-01-31 10:21 | YES | YES | 19940045 | 1994-02-18 | 11720 | LONG ISLAND LIGHTING COMPANY | 42 BAYSIDE PLACE | AMITYVILLE | SUFFOLK | NY | 11701 | 4 | NO | 621 | 1994-01-20 | 0 | 1 | 500000 | 374395.7919 | 903966.4487 | Null | 0 | 59 |  | 19940120 | 44 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1930 | UNDER PAVEMENT |  | THOMAS E. LUPSKI - CODE AND SPECIFICATIONS ENGINEER | 5169334400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE PIPE APPEARS TO HAVE BEEN PHYSICALLY DAMAGED BY AN UNKNOWN PARTY, POSSIBLY DURING A PREVIOUSLY COMPLETED SEWER CONNECTION. THE COMBINATION OF THE DAMAGED PIPE AND SEVERE WEATHER CONDITIONS APPARENTLY CONTRIBUTED TO THE INCIDENTPART B - DAMAGE BY OUTSIDE FORCES - VISUAL INVESTIGATION INDICATES A CRACK AND PHYSICAL DEFORMITY OF THE GAS MAIN DUE TO APPARENT EXTERNAL FORCE EXERTED ON THE PIPE. SEVERE COLD WEATHER AND A TWO (2) FOOT FROST LEVEL ALSO APPEAR TO BE CONTRIBUTING FACTORS, WHICH ALLOWED THE GAS TO MIGRATE INTO THE HOME.
2025-01-31 10:21 | YES | YES | 19940046 | 1994-02-22 | 20010 | U G I CORP | 925 WYOMING STREET | ALLENTOWN | LEHIGH | PA | 18103 | 3 | NO | 900 | 1994-01-28 | 1 | 1 | 300000 | 224637.4751 | 542379.8692 | Null | 1 | 20 |  | 19940128 | 0.25 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1923 | UNDER PAVEMENT |  | C.W. BECKER - VICE PRESIDENT - OPERATIONS SERVICES | 6107963502 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | IT APPEARS NATURAL GAS ESCAPING FROM A CRACK IN A FOUR INCH CAST IRON MAIN LOCATED ALONG THE 900 BLOCK OF WYOMING STREET IN ALLENTOWN, PENNSYLVANIA MIGRATED INTO HOUSE 925 WYOMING STREET. THE GAS WAS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE CAUSING AND EXPLOSION AND FIRE DESTROYING THE HOUSE. THERE WAS ONE FATALITY AND ONE INJURY TO THE RESIDENTS OF THE HOUSE. ADJACENT HOMES AT 927, 923 AND 921 ALSO SUSTAINED DAMAGE. IN EXCAVATING THE MAIN, IT WAS FOUND TOBE CRACKED IN FRONT OF HOUSE 927. ALSO THE FROST DEPTH WAS APPROXIMATELY 36 INCHES (MAIN DEPTH).
2025-01-31 10:21 | NO | NO | 19940047 | 1994-02-28 | 5200 | FITCHBURG GAS & ELECTRIC LIGHT CO | 15 PARSON CIRCLE | FITCHBURG | WORCESTER | MA | 01420 | 3 | NO | 810 | 1994-02-05 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 |  | 19940205 | 1 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.145 | SCH.40 |  | 1926 | 1926 | UNDER PAVEMENT |  | DALE C. NUDD - ASS'T VICE PRESIDENT OPERATIONS | 5083436931 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-02-05 | YES | 3 | TEMPORARY FLAGS | YES
2025-01-31 10:21 | YES | YES | 19940048 | 1994-02-15 | 15329 | PEOPLES GAS LIGHT & COKE CO | 8049 TO 59 SOUTH ST. LAWRENCE AVENUE | CHICAGO | COOK | IL | 60619 | 3 | NO | 733 | 1994-01-18 | 1 | 0 | 600000 | 449274.9502 | 1084759.7384 | Null | 1 | 55 |  | 19940118 | 21 | 24 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.322 |  |  | 0 | 1974 | UNDER PAVEMENT |  | RODNEY LOONEY - FIELD SUPERINTENDENT | 3129624841 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1989-06-28 | YES | 3 | PAINT | NO |  |  | PART 3- A CRACK IN AN 8" STEEL CATHODICALLY PROTECTED MEDIUM PRESSURE PIPE LEAKED, CAUSING GAS TO MIGRATE UNDERGROUND. OUR INVESTIGATION CONTINUES AS TO THE CAUSE OF THIS INCIDENT. PART B.3- THE PIPE WAS PREVIOUSLY DENTED AT THE POINT WHERE THE CRACK OCCURRED. THE DENT MAY HAVE HAPPENED IN 1989 WHEN SEWER WORK WAS PERFORMED AT 81ST STREET AND CHAMPLAIN. THE COMPANY WAS NOT NOTIFIED, AT THAT TIME, OF ANY DAMAGE (DENT) TO THE PIPE CAUSED BY THE CONTRACTOR. OUR INVESTIGATION CONTINUES AS TO THE REASON FOR THE LEAK ON OR ABOUT JANUARY 18, 1994.
2025-01-31 10:21 | YES | NO | 19940049 | 1994-02-23 | 15469 | PHILADELPHIA GAS WORKS | 3724 "M" STREET | PHILADELPHIA | PHILADELPHIA | PA | 19124 | 3 | NO | 1748 | 1994-01-23 | 0 | 0 | 110000 | 82367.0742 | 198872.6187 | Null | 1 | 6 |  | 19940123 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | OTHER | NOT GIVEN | 6 | 0.485 |  |  | 0 | 1916 | UNDER PAVEMENT |  | JOSEPH M. CAREY - MANAGER DISTRIBUTION DEPT | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | CIRCUMFERENTIAL BREAK ON A LOW PRESSURE 6" CAST IRON GAS MAIN IN FRONT OF 3724 "M" STREET, 63" NORTH OF THE NORTH CURB LINE OF AIRDRIE STREET, 3'6" EAST OF THE WEST CURB OF "M" STREET.
2025-01-31 10:21 | YES | NO | 19940050 | 1994-02-17 | 22476 | WESTERN KENTUCKY GAS CO | 232,234,239, & 245 . 15TH STREET | BOWLING GREEN | WARREN | KY | 42101 | 3 | NO | 1538 | 1994-01-19 | 0 | 0 | 250000 | 187197.8959 | 451983.2243 | Null | 4 | 22 |  | 19940119 | 54 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 1946 | 1946 | UNDER PAVEMENT |  | DOUGLAS E. STEARNS P.E. - SENIOR ENGINEER | 5026858020 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | FROST | NO |  | NO | 0 |  | NO |  |  | ON THE ABOVE DATE AND TIME, WKG RECEIVED NOTIFICATION FROM THE BOWLING GREENFIRE DEPARTMENT THAT A HOUSE AT 239 W. 15TH STREET IN BOWLING GREEN WAS ON FIRE. WKG PERSONNEL WERE DISPATCHED IMMEDIATELY TO THE SCENE AND SOON AFTER ARRIVING, THE THREE HOUSES AT 245,232 AND 234 W. 15TH STREET ALSO BEGAN TO BURNIN RAPID SEQUENCE. LEAKING GAS THEN BEGAN TO BURN ACROSS THE WIDTH OF THE STREET AS IT ESCAPED THROUGH CRACKS IN THE PAVEMENT. AIR TEMPERATURE AT THE TIME OF THE INCIDENT WAS APPROXIMATELY 0 DEGREES F. THE GROUND WAS COVERED BY APPROXIMATELY ONE INCH OF ICE AND FOUR INCHES OF SNOW WHICH FELL THE NIGHT OF JANUARY 17. THE GAS WAS SHUT OFF TO 19 HOUSES IN THE IMMEDIATE VICINITY WHERE GAS WAS DETECTED. AN ADDITIONAL 258 HOUSES WERE EVACUATED. THE LEAKING 2" STEEL MAIN WAS A TWO-WAY FEED. THE GAS WAS STOPPED OFF ON THE SOUTH SIDE OF THE LEAK AT 6:00 P.M. APPROXIMATELY 50 FEET TO THE NORTH OF THE LEAK, THE 2" MAINTIED INTO A 6" DISTRIBUTION MAIN (PRIMARY FEED). GAS WAS LEAKING THROUGH THEGROUND INTO THE HOLE DUG AT THE 6" MAIN TO INSTALL A FITTING. WKG WORKED THROUGH THE NIGHT DIGGING OTHER HOLES TO VENT THE LEAKING, BURNING GAS AND MAKE THE SECOND SHUTDOWN HOLE ACCESSIBLE. ALL EVACUATED HOUSED WERE TURNED OFF BY THE FIRE DEPARTMENT ON ORDERS OF THE ASSISTANT FIRE CHIEF. THE BLOWING GAS WAS STOPPED AT 7:45 AM CST BY PLUGGING THE SECOND STOPPER FITTING NEAR THE 6" MAIN. RESTORATION OF SERVICE TO THE 277 CUSTOMERS TURNED OFF, BEGAN AT 2:00 PMCST AND WAS COMPLETED BY 11:30 PM CST ON JANUARY 20, EXCEPT FOR THE FIRST 12CUSTOMERS SHUT DOWN. ON MONDAY JANUARY 24, THE MAIN WAS EXCAVATED TO DETERMINE THE SOURCE AND CAUSE OF THE LEAK. IT WAS DISCOVERED THAT THE 2" STEEL GAS MAIN HAD APPARENTLY BEEN DAMAGED BY A THIRD PARTY. THERE WERE ALSO INDICATIONS THAT THE TRENCH HAD SETTLED AND THE STREET HAD BEEN REPAIRED AT SOME LATER DATE. THE EXCAVATION REVEALED A CAVITY UNDER THE CONCRETE SUB-BASE, LEAVING THE PIPE UNSUPPORTED BY BACKFILL. LABORATORY TESTS REVEALED THAT THE MAIN SUFFERED BRITTLE FRACTURE DUE TO STRESS CONCENTRATION CAUSED BY DAMAGE BY EXTERENAL FORCES, AND THE REDUCED DUCTILITY OF THE PIPE DUE TO THE LOW TEMPERATURES AT THE TIME OF FAILURE. NEW MAIN AND SERVICES WERE RUN IN W. 15TH STREET AND THE REMAINING SEVEN HOMES WERE TURNED BACK ON JANUARY 27, 1994.
2025-01-31 10:21 | YES | NO | 19940051 | 1994-02-14 | 24015 | YANKEE GAS SERVICES CO | 187 WINDSORVILLE ROAD | ELLINGTON | TOLLAND | CT | 06029 | 3 | NO | 2004 | 1994-02-04 | 0 | 0 | 350000 | 262077.0543 | 632776.5141 | Null | 6 | 16 |  | 19940204 | 35 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | VALVE |  | OTHER | CAST STEEL | 0 | 0 |  | MERCO | 0 | 1959 | UNDER PAVEMENT |  | E.W. FLANAGAN - AREA SUPERINTENDENT | 2032922257 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | FIRE FIGHTERS WERE CALLED TO RESPOND TO AN ODOR OF GAS AND FIRE AT THE SITE OF A BRICK AND WOOD FRAME TENANT HOUSE. YANKEE GAS RESPONDED WHEN CALLED FOR AND LOCATED AND CLOSED THE SERVICE CURB VALVE. YANKEE GAS CREWS CONTINUED INVESTIGATING FOR THE LEAK AND DETERMINED THE SOURCE TO BE A 6" MAIN LINE, FLANGED VALVE LOCATED IN CLOSE PROXIMITY TO THE STRUCTURE. HEAVY FROST HAMPERED DIGGING OPERATIONS TO EXPOSE AND CLOSE THE VALVE. CLOSING THE LEAKING VALVE DISRUPTED SERVICE TO TWENTY-THREE CUSTOMERS. THE VALVE WAS REPLACED AND SERVICE RESTORED. PART B - THE 6" FLANGED VALVE WAS FOUND CRACKED AND IS BEING ANALYZED TO DETERMINE THE CAUSE OF THE DAMAGE.
2025-01-31 10:21 | NO | NO | 19940052 | 1994-02-15 | 13299 | NEW JERSEY NATURAL GAS CO | 3 FAIRWAY W | COLTS NECK | MONMOUTH | NJ |  | 2 | NO | 233 | 1994-01-09 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19940109 | 0 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE THE HOUSE | OTHER | NONE | OTHER | NONE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MONIQUE HERZOG - ENGINEER - COMPANY QUALITY CONTROL | 9089381193 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 2:33 A.M. ON SUNDAY, JANUARY 9, 1994, NEW JERSEY NATURAL GAS COMPANY (NJNG) RECEIVED A REPORT OF A HOUSE FIRE AT 3 FAIRWAY W., COLTS NECK. THE NJNG APPLIANCE SERVICEMAN ARRIVED AT 2:57 A.M. AND FOUND THAT THE UNOCCUPIED HOUSE WAS ON FIRE. FIRE PERSONNEL WERE ON THE SCENE AND GAS HAD ALREADY BEEN TURNED OFF AT THE OUTSIDE METER SET. AT APPROXIMATELY 4:00 A.M., THE MAIN AND SERVICE WERE SURVEYED FOR LEAKS. NO INDICATION OF LEAKING NATURAL GAS WAS FOUND. THE GAS METER AND REGULATOR WERE REMOVED BY NJNG PERSONNEL AND DELIVERED TO PETER VALLAS ASSOCIATES, INC. OF 125 STAT STREET, HACKENSACK, NJ 07601 FOR TESTING. SEVERE WEATHER CONDITIONS HAD RESULTED IN A NUMBER OF "NO HEAT" COMPLAINTS IN OUR SERVICE TERRITORY CAUSED BY ICE COVERING THE OUTSIDE METERS. NJNG WANTED TO ASSURE THAT THE SUSPECTED ICING CONDITION OF THIS METER DID NOT IN ANY WAY CAUSE THE INCIDENT. THE OCCUPANT OF THIS HOUSE, MR. WILLIAM HAHN, HAD CALLED IN A COMPLAINT OF "NO GAS" AT 6:18 P.M. THE PREVIOUS EVENING. HE REPORTED THAT HIS ELECTRICITY HAD ALSO BEEN OFF BUT WAS NOW BACK ON.THE FAMILY THEN LEFT TO SPEND THE NIGHT AT A NEARBY HOTEL. THE FOLLOWING DAY, THE SERVICE WAS EXCAVATED AT THE MAIN CONNECTION AND PRESSURE TESTED. THE SERVICE HEALD SYSTEM PRESSUE: 39.5 PSIG AND WAS THEN TESTED WITH AIR AT 100 PSIG FOR 10 MINUTES. AGAIN, THE PRESSURE HELD. THE .5" DIAMETER X-TRUBE SERVICEWAS EXAMINED IN THE EXCAVATION AND FOUND TO BE IN GOOD CONDITION. THE MAINTENANCE ORDER IS ATTACHED. ARTHUR L. JACKSON, CHIEF INVESTIGATOR FOR PETER VALLAS ASSOCIATES, INC., HAS REPORTED VERBALLY THAT WHILE THE METER AND REGULATORWERE DAMAGED BY THE FIRE, THEY COULD FIND NO EVIDENCE THAT ANY FAILURE OF OUR FACILITIES OCCURRED WHICH COULD HAVE CAUSED THIS ACCIDENT. IT IS THEREFORE NJNJ'S CONCLUSION THAT THIS FIRE IS NOT A PIPELINE INCIDENT AND THUS NON-REPORTABLE. NO FURTHER REPORTS WILL BE SUBMITTED UNLESS OTHERWISE REQUESTED BY THE DEPARTMENT OF TRANSPORTATION.
2025-01-31 10:21 | YES | YES | 19940053 | 1994-02-14 | 1640 | BOSTON GAS CO | 15 EGREMONT ROAD, APT. A | BRIGHTON | SUFFOLK | MA | 02146 | 3 | NO | 830 | 1994-01-25 | 0 | 1 | 25000 | 18719.7896 | 45198.3224 | Null | 1 | 30 |  | 19940125 | 0 | 0 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 |  |  | 0 | 1915 | UNDER PAVEMENT |  | ROBERT J. CAVICCHI - MANAGER DISTRIBUTION ADMIISTRATION | 6177235512 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THE OCCUPANT ARRIVED HOME FROM WORK AT 6:OO A.M. AND NOTICED AN ODOR OF GAS IN HIS BASEMENT APARTMENT. HE INVESTIGATED THE ODOR IN EACH ROOM OF THE APARTMENT AND THE UTILITY AREA. SHORTLY BEFORE 8:30 A.M. HE SAT DOWN AND LIT A CIGARETTE. THERE WAS AN IMMEDIATE FLASH FIRE WITHIN HIS LIVING ROOM. A LEAK INVESTIGATION WAS CONDUCTED AND A CIRCUMFERENTIAL BREAK WAS FOUND ON A 6" LOW PRESSURE CAST IRON MAIN. THE BREAK WAS FOUND IN A WATER TRENCH THAT WAS EXCAVATED AND BACKFILLED APPROXIMATELY FIVE MONTHS EARLIER.
2025-01-31 10:21 | NO | NO | 19940054 | 1994-02-14 | 11720 | LONG ISLAND LIGHTING COMPANY | COMMERCIAL STREET | GARDEN CITY | NASSAU | NY | 11530 | 4 | NO | 911 | 1994-01-05 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 44 |  | 19940105 | 60 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 |  |  | 0 | 0 | UNDER PAVEMENT |  | THOMAS E. LUPSKI - CODE & SPECIFICATION ENGINEER | 5169334400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | YES |  |  | A THIRD PARTY CONTRACTOR DRILLED THROUGH AN 8" GAS MAIN WHILE PERFORMING TEST BORING OPERATIONS. THE LONG ISLAND LIGHTING COMPANY PLACED A TELEPHONIC NOTIFICATION OT THE DEPARTMENT OF TRANSPORTATION BASED UPON THE PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF THE INCIDENT. SUBSEQUENT INVESTIGATION DETERMINED THAT THE TELEPHONE NOTIFICATION WAS NOT REQUIRED UNDER THE 49CFR PART 191.5 GUIDELINES.
2025-01-31 10:21 | YES | YES | 19940055 | 1994-02-14 | 20010 | U G I CORP | 156 BUTTONWOOD STREET | READING | BERKS | PA | 19601 | 3 | NO | 2310 | 1994-01-19 | 0 | 1 | 0 | 0 | 0 | Null | 4 | 20 |  | 19940120 | 0.25 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1899 | UNDER PAVEMENT |  | C.W. BECKER - VICE PRESIDENT OPERATIONS SERVICES | 6107963502 | [6 empty] | Null |  | EARTH MOVEMENT: FROST | EARTHQUAKE | NO |  | NO | 0 |  | NO |  |  | DUE TO OUTSIDE FORCES, CAUSED EITHER BY AN EARTHQUAKE FIVE DAYS PREVIOUSLY OR BY FROST RESULTING FROM ESTREMELY COLD WEATHER, A NOMINAL FOUR INCH CAST IRON GAS MAIN WAS BROKEN. THE MAIN WAS LOCATED UNDER THE STREET PAVEMENT ALONG THE 300 BLOCK OF NORTH SECOND STREET WHICH RUNS PERPENDICULAR TO THE 100 BLOCK OF BUTTONWOOD STREET IN READING, PENNSYLVANIA. GAS ESCAPING FROM THE BROKENMAIN MIGRATED INTO THE BASEMENT OF 156 BUTTONWOOD STREET., LOCATED AT THE NORTHWEST CORNER OF SECOND & BUTTONWOOD STREETS, AND FURTHER MOVED INTO THE REAR APARTMENT ON THE FIRST FLOOR OF 156 BUTTONWOOD. WHILE ATTEMPTING TO EVACUATE THE BUILDING, GAS CONFINED TO THE APARTMENT WAS IGNITED BY AN UNKNOWN SOURCE CAUSING A LOW GRADE EXPLOSION AND FLASH FIRE. THE FLASH FIRE BURNED ONE OF THE APARTMENT'S TENANTS. THE TENANT SUFFERED SECOND AND THIRD DEGREE BURNS OFHANDS AND FACE AND WAS HOSPITALIZED.
2025-01-31 10:21 | YES | YES | 19940059 | 1993-12-21 | 4473 | ENERGAS CO | 717 N. WELLS | PAMPA | GRAY | TX | 79065 | 3 | NO | 225 | 1993-12-11 | 0 | 2 | 17000 | 13006.8274 | 31404.5613 | Null | 0 | 20 |  | 19931211 | 0.5 | 2 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | CHARLES R. FULKERSON - MANAGER ENGINEERING SERVICES | 8067984477 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION DUE TO GAS ACCUMLATION FROM OPEN OUTLET WHERE A GAS DRYER PREVIOULSLY HAD BEEN CONNECTED
2025-01-31 10:21 | YES | YES | 19940063 | 1994-02-18 | 18440 | SOUTH JERSEY GAS CO | 604 FAIRMOUNT DRIVE | GLASSBORO | GLOUCESTER | NJ | 08028 | 3 | NO | 1425 | 1994-01-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 40 |  | 19940124 | 50 | 60 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1958 | WITHIN/UNDER BUILDING |  | EDWARD TONIELLI - VICE PRESIDENT DISTRIBUTION OPERATIONS | 6095619000 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION AND FIRE OCCURRED AT A RESIDENTIAL HOME INJURING THE HOMEOWNER ANDREQUIRING HOSPITALIZATION. UPON ARRIVAL, NATURAL GAS WAS DETECTED AT THE FOUNDATION. TWO CORROSION LEAKS WERE DISCOVERED ON THE MAIN IN FRONT OF THE PROPERTY AND REPAIRED. CURRENT INVESTIGATION IS ONGOING TO DETERMINE THE EXACT CAUSE OF THE EXPLOSION.
2025-01-31 10:21 | NO | NO | 19940064 | 1994-02-14 | 11680 | LONE STAR GAS CO | WILD FLOWER WAY & GOLDEN | FORT WORTH | TARRANT | TX | 76123 | 3 | NO | 1150 | 1994-01-19 | 0 | 0 | 20000 | 14975.8317 | 36158.6579 | Null | 2 | 35 |  | 19940119 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | SDR - 11 |  | 0 | 0 | ABOVE GROUND |  | PHILLIP MURDOCK - DIRECTOR | 2146702229 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-01-13 | YES | 2 |  | NO |  |  | 4" POLY MAIN BROKEN AND ON FIRE AFTER BEING STRUCK BY BACKHOE WHILE DIGGING DITCH FOR NEW ELECTRIC CABLE.
2025-01-31 10:21 | NO | NO | 19940065 | 1994-03-02 | 7110 | HARTSELLE UTILITIES BOARD | RAILROAD ST & SPARKMAN STREET | HARTSELLE | MORGAN | AL | 35640 | 1 | NO | 1300 | 1994-01-07 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 19940107 | 18 | 0 | BY TEST | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JIM HOLLINGSWORTH - GAS MANAGER | 2057732533 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OUR WASTE WATER CONSTRUCTION CREW, WAS BLASTING IN AREA CAUSING PIPE TO BREAK.NO DAMAGE OTHER THAN LOSS OF GAS.
2025-01-31 10:21 | YES | YES | 19940067 | 1994-02-17 | 2588 | COLUMBIA GAS OF MARYLAND INC | 71 STATE RD., RT. 36 | LONACONING | ALLEGANY | MD | 21539 | 2 | NO | 900 | 1994-01-19 | 1 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 1 | 30 |  | 19940119 | 25 | 90 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | THREADED COLLAR | STEEL |  | 2 | 0.25 |  |  | 0 | 1939 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS - MANAGER CONSTRUCTION & MAINTENANCE | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DAMAGE WAS INITIATED BY ACTIONS OF A SEWER CONTRACTOR APPROXIMATELY 10 YEARSAGO. COLUMBIA GAS OF MARYLAND, INC. IS THE OWNER AND OPERATOR OF A 2-INCH STEEL GAS MAIN (90 PSIG MAOP) ALONG STATE ROUTE 36 IN THE VILLAGE OF LONACONING, MARYLAND. THE NATURAL GAS FACILITY WAS INSTALLED IN 1939. THE PIPE SECTIONS, WHICH ARE EACH APPROXIMATELY 22 FEET LONG, WERE JOINED BY THREADED COLLARS.ON JANUARY 19, 1994 , AT ABOUT 9:00 A.M., AN EXPLOSION AND FIRE DESTROYED A TWO-STORY SINGLE-FAMILY RESIDENCE. THERE WAS ONE TO THE EMERGENCY AND MADE THE AREA SAFE BY SHUTTING OFF THE SUPPLY OF GAS. PART OF COLUMBIA'S INVESTIGATION INCLUDED EXPOSING THE 2-INCH MAIN TO EXAMINE ITS CONDITION. A CIRCUMFERENTIAL BREAK WAS DISCOVERED AT A THREADED COLLAR JOINT. THE PIPE WAS COMPLETELY SEPARATED AT THIS JOINT. APPARENT CAUSE - APPROXIMATELY 10 YEARS AGO, A SEWERCONTRACTOR INSTALLED A NEW SEWER LINE IN THE VICINITY OF COLUMBIA'S 2-INCH MAIN. THE SEWER LINE WAS INSTALLED PARALLEL TO AND DEEPER THAN THE 2-INCH MAIN. THERE WAS PHYSICAL EVIDENCE FOUND UPON EXCAVATING THE PIPE AFTER THE INCIDENT INDICATING THAT THE SEWER CONTRACTOR PUT STRESS ON THE 2-INCH MAIN BY PULLING AND TYING IT TO THE SIDE OF THE EXCAVATION TO ACCOMMODATE THE INSTALLATION OF THE SEWER LINE. THE PHYSICAL EVIDENCE ALSO REVEALED THAT THE BACKFILL OVER THE 2-INCH MAIN WAS NOT PLACED BACK IN ITS ORIGINAL POSITION. THIS EVIDENCE INDICATED THE MAIN REMAINED IN A STRESSED POSITION FROM THE DAY IT WAS DISTURBED. IT APPEARS THAT A COMBINATION OF DEEP FROST FROM THE SEVERE WEATHER CONDITIONS AND THE STRESS ON THE MAIN CAUSED IT TO FAIL AT THE JOINT.
2025-01-31 10:21 | YES | NO | 19940068 | 1994-02-17 | 2596 | COLUMBIA GAS OF OHIO INC | 1375\1377 ORCHARD PARK DRIVE | COLUMBUS | FRANKLIN | OH | 43232 | 3 | NO | 57 | 1994-01-20 | 0 | 0 | 200000 | 149758.3167 | 361586.5795 | Null | 5 | 43 |  | 19940120 | 45 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 |  |  | 0 | 1981 | ABOVE GROUND |  | D.E. WILLIAMS - MANAGER CONSTRUCTION & MAINTENANCE | 6144606407 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | GROUND FREEZING AND CONTRACTION OF PIPE PUT PULL-OUT STRESS ON COMPRESSION FITTING AT TOP OF METER RISER. PULL-OUT STRESS WAS INDUCED DUE TO EXTREME COLDTEMPERATURES (-22). THE ONE-INCH PLASTIC SERVICE LINE SEPARATED AT THE COMPRESSION NUT AND AT THE OPPOSITE END OF THE RISER UNDERGROUND. THERE WAS NO EVIDENCE OF A STIFFENER BEING INSTALLED IN THE RISER COMPRESSION FITTING. COMPANY HAD DIFFICULTY IN TURNING OFF SERVICE DUE, IN PART, TO SEVERE WEATHER CONDITIONS. COMPANY DEEMED IT INAPPROPRIATE TO TURN OFF CRITICAL VALVES BECAUSE ITWOULD HAVE INTERRUPTED SERVICE TO HUNDREDS OF CUSTOMERS DURING A TIME OF SEVERE WEATHER.
2025-01-31 10:21 | YES | NO | 19940072 | 1994-03-08 | 4350 | ELIZABETHTOWN GAS CO | 288 PLAINFIELD ROAD | EDISON | MIDDLESEX | NJ | 08820 | 4 | NO | 2351 | 1994-02-14 | 0 | 0 | 300000 | 224637.4751 | 542379.8692 | Null | 3 | 26 |  | 19940215 | 22 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 | 0.6 |  |  | 0 | 1950 | UNDER PAVEMENT |  | JOSEPH RADA - DIVISION DIRECTOR | 9082895000 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | LEAKING GAS FROM CRACKED MAIN, APPARENTLY CAUSED BY THE WEATHER.
2025-01-31 10:21 | YES | YES | 19940074 | 1994-06-09 | 6720 | GREELEY GAS CO | 442 LINCOLN AVENUE | STEAMBOAT SPRINGS | ROUTT | CO | 80477 | 3 | NO | 1215 | 1994-02-03 | 0 | 7 | 1500000 | 1123187.3756 | 2711899.346 | Null | 0 | 50 |  | 19940203 | 58 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1966 | UNDER PAVEMENT |  | RICHARD W. REMLEY | 3038618080 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A LEAK CALL FROM 704 LINCOLN AVENUE WAS RECEIVED AT 12:10 P.M. A SERVICE MANWAS DISPATCHED AND GAS WAS DETECTED AT THE LEAK CALL SITE. WHILE THE BUILDING WAS BEING EVACUATED, THE FIRE WAS REPORTED AT 442 LINCOLN AVENUE UPON FURTHER INVESTIGATION NATURAL GAS WAS FOUND IN THE STORM SEWER AND TELEPHONE CONDUIT IN THE LINCOLN/OAK ALLEY. THE SYSTEM WAS SHUT DOWN. THE 1 1/4" MAIN IN THELINCOLN/OAK ALLEY WAS ISOLATED FROM THE SYSTEM AND THE REMAINING PORTION WASRELIT. THE ISOLATED PIPE IN THE ALLEY WAS SEPARATED AND TESTED UNTIL A 180 FOOT LONG SECTION WAS FOUND NOT TO HOLD PRESSURE. THE FROST LEVEL IS BELOW THEPIPE DEPTH AND IT WAS DECIDED TO CAP THIS PIPE AND NOT INVESTIGATE UNTIL THEGROUND THAWS. WE WILL SUBMIT AND SUPPLEMENTAL REPORT WHEN THIS INVESTIGATIONIS COMPLETE. PART 2 - OTHER - UNABLE TO DETERMINE CAUSE DUE TO FROST. WILL DIG AND EXAMINE IN SPRING.
2025-01-31 10:21 | YES | YES | 19940075 | 1994-03-08 | 15469 | PHILADELPHIA GAS WORKS | 1014 SLOCUM STREET | PHILADELPHIA | PHILADELPHIA | PA | 19150 | 3 | NO | 914 | 1994-01-28 | 0 | 1 | 4000 | 2995.1663 | 7231.7316 | Null | 1 | 0 |  | 19940128 | 0.3 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 |  |  | 0 | 1951 | UNDER PAVEMENT |  | JOSEPH M. CAREY - MANAGER DISTRIUTION DEPT | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | TED BY THE PHILADELPHIA FIRE DEPARTMENT AND ARE ATTRIBUTED TO A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON GAS MAIN AT 148'6" EAST CURB LINE OF MANSFIELD STREET AND 7'6" SOUTH OF THE SOUTH CURB LINE OF SLOCUM STREET. THIS ALLOWED NATURAL GAS TO MIGRATE INTO THE BASEMENT BATHROOM OF 1014 SLOCUM STREET AND WAS IGNITED WHEN THE OCCCUPANT ATTEMPTED TO LIGHT HIS PIPE WITH A MATCH.
2025-01-31 10:21 | YES | YES | 19940076 | 1994-03-08 | 15469 | PHILADELPHIA GAS WORKS | 4205 N. 9TH STREET | PHILADELPHIA | PHILADELPHIA | PA | 19140 | 3 | NO | 2355 | 1994-01-23 | 0 | 1 | 240000 | 179709.9801 | 433903.8954 | Null | 0 | 55 |  | 19940124 | 0.3 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 |  |  | 0 | 1913 | UNDER PAVEMENT |  | JOSEPH M. CAREY - MANAGER DISTRIBUTION DEPT. | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | THE FACTORS CONTRIBUTING TO THIS INCIDENT WERE UNDER INVESTIGATION BY THE PHILADELPHIA FIRE DEPARTMENT. THE INVESTIGATION CONCLUDED THAT THERE WAS A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON GAS MAIN IN FRONT OF 4203 N. 9TH STREET (41'8" NNC HUNTING PARKS AVENUE, 3'6" WEC 9TH STREET). THE NATURAL GAS MIGRATED INTO ONE OF THE HOMES AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING THE SUBSEQUENT FIRE AND EXPLOSION.
2025-01-31 10:21 | NO | NO | 19940077 | 1994-03-01 | 12582 | MISSISSIPPI VALLEY GAS | U.S. HIGHWAY 61 | MOUND BAYOU | BOLIVAR | MS | 38762 | 2 | NO | 1145 | 1994-02-22 | 0 | 0 | 20000 | 14975.8317 | 36158.6579 | YES | 1 | 10 |  | 19940222 | 175 | 175 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | PAUL D. NOEL - DIRECTOR OF OPERATING SERVICES | 6019616860 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-02-21 | YES | 3 | FLAGS | YES |  |  | DAMAGE TO MAIN SUPPLYING GAS TO MOUND BAYOU CAUSED LOSS OF PRESSURE ON THE DISTRIBUTION SYSTEM. THE MAJOR PORTION OF THE DAMAGE COST WAS TURNING OFF CUSTOMER'S SERVICE AND RELIGHTING AFTER THE MAIN WAS REPAIRED. PART 3 - ELECTRIC UTILITY COMPANY, DRILLING HOLE TO SET UTILITY POLE, DAMAGED GAS MAIN.
2025-01-31 10:21 | NO | NO | 19940078 | 1994-02-16 | 15931 | PUBLIC SERVICE CO OF COLORADO | 1016 EAST 13TH STREET | PUEBLO | PUEBLO | CO | 81001 | 3 | NO | 1700 | 1994-02-02 | 0 | 0 | 25000 | 18719.7896 | 45198.3224 | Null | 5 | 0 |  | 19940203 | 7 | 7 |  | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.29 |  | NORMAC | 0 | 1973 | UNDER GROUND OR UNDER WATER |  | MICHAEL L. PETERSON - OPERATION MANAGER | 7195493638 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | PART 3- A COMPRESSION COUPLING CONNECTING PVI TO STEEL SLIPPED OFF THE PVC.
2025-01-31 10:21 | YES | YES | 19940079 | 1994-03-17 | 14210 | OKLAHOMA NATURAL GAS CO | SECOND AND OKFUSKEE STREETS | WEWOKA | SEMINOLE | OK | 74884 | 3 | NO | 1450 | 1994-02-17 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19940217 | 30 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 4 | 0.395 | TYPE 2 GR 3 |  | 0 | 0 | OTHER | OPEN TRENCH | GERRY LYNN - CHIEF ENGINEER | 9185887600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | PLASTIC PIPE WAS NOT GROUNDED AND STATIC ELECTRICAL DISCHARGE COULD HAVE BEEN THE IGNITION SOURCE.
2025-01-31 10:21 | NO | NO | 19940080 | 1994-03-22 | 18472 | SOUTHEASTERN MICHIGAN GAS CO | 57 HOWARD STREET | CROSWELL | SANILAC | MI | 48422 | 1 | NO | 1107 | 1994-02-09 | 0 | 0 | 30000 | 22463.7475 | 54237.9869 | Null | 1 | 13 |  | 19940211 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT |  | STEEL | DRESSER FITTING | 0 | 0 | 2" 90 | DRESSER | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | THOMAS M. REILLY - MANAGER OF INVESTIGATION AND CLAIMS | 8109877900 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR HIT AND BROKE 2" RISER PIPE AT METER SET.
2025-01-31 10:21 | NO | NO | 19940081 | 1994-03-22 | 18472 | SOUTHEASTERN MICHIGAN GAS CO | 69 MACK AVENUE | MARYSVILLE | ST CLAIR | MI | 48040 | 1 | NO | 42 | 1994-02-10 | 0 | 0 | 20000 | 14975.8317 | 36158.6579 | Null | 2 | 20 |  | 19940217 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | JOINT | DRESSER | STEEL | DRESSER FITTING | 0 | 0 | 3/4" COUPLING | DRESSER | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | THOMAS M. REILLY - MANAGER OF INVESTIGATION AND CLAIMS | 8109877900 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | NATURAL GAS EXPLOSION WAS CAUSED BY FROST HEAVING ON SERVICE LINE.
2025-01-31 10:21 | NO | NO | 19940083 | 1994-03-18 | 13480 | NIAGARA MOHAWK POWER CORP | QUAKER ROAD | QUEENSBURY | WARREN | NY | 12804 | 3 | NO | 1255 | 1994-02-19 | 0 | 0 | 52000 | 38937.1624 | 94012.5107 | Null | 1 | 45 |  | 19940222 | 28 | 30 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 6 | 0.602 | ASTM 2513 | DRISCO | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | GREGG C. VANDERMARK - MGR GAS C&M, NORTHEAST REGION | 5185835750 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | SUPPLEMENTAL REPORT 4/8/1994 INDICATES AT APPROX. 12:30PM. A GAS FIRE ERUPTEDDURING A SQUEEZE OFF OPERATION ON A 6INCH PLASTIC MAIN; THE MAIN WAS LEAKINGDUE TO BREAKAGE OF A PLASTIC FUSION JOINT. THE ENSUING FIRE CAUSEDSECOND-DEGREE BURNS TO TWO EMPLOYEES AND SOME PROPERTY DAMAGE. THE TWO INJUREDEMPLOYEES RECEIVED MEDICAL TREATMENT AT THE HOSPITAL EMERGENCY ROOM AND WERERELEASED. ONE EMPLOYEE'S BURNS WERE TO THE BACK OF HIS HANDS, RESULTING IN TWOWEEKS OF RECUPERATION. THE OTHER INJURED EMPLOYEES HAD NO LOST TIME. THEINTERIOR OF THE BACKHOE, WHICH WAS ON THE JOB SITE, BURNED; THE TELEPHONE ANDELECTRIC WIRES WERE BURNED DOWN. THIS, ALONG WITH THE LOSS OF GAS AND CLAIMSRECEIVED DUE TO A LOSS OF BUSINESS RESULTING FROM BEING SHUT OFF DURING THEREPAIRS, WAS THE EXTENT OF THE DAMAGE. NIAGARA MOHAWK INVESTIGATED THEINCIDENT IN THE FOLLOWING MANNER: COLLECTION OF EVIDENCE AT THE SCENE - THISINCLUDED THE COLLECTION AND PRESERVATION OF PHYSICAL EVIDENCE ALONG WITHPHOTOS, VIDEOS, AND OTHER DOCUMENTATION DEEMED NECESSARY FOR INVESTIGATION.INITIAL AND FOLLOW-UP INTERVIEWS- THE INITIAL INTERVIEWS WITH THE CREW WEREHELD ON A ONE-ON-ONE BASIS, ALONG WITH INTERVIEWS WITH THE SERVICEREPRESENTATIVES THAT INVESTIGATED AND ASSISTED IN THE GAS LEAK AND ENSUINGFIRE. FAILURE MODE INVESTIGATION - THIS WAS DONE TO IDENTIFY THE PHYSICALATTRIBUTES THAT LED TO COMPONENT FAILURE. THIS INCLUDED EXAMINING OUR EXISTINGSTANDARD PROCEDURES, ALONG WITH THE PLASTIC PIPE MANUFACTURER'S REPRESENTATIVEEXAMINING THE FAILED FUSION JOINT. OTHER GROUPS INVOLVED IN INVESTIGATION -REPRESENTATIVES FROM SYSTEM GAS OPERATIONS, SYSTEM GAS ENGINEERING, SYSTEMTRAINING, SAFETY, AND CENTRAL REGION OPERATIONS ASSISTED IN AN OUTSIDEEVALUATION OF THE INCIDENT. BURNETT POWELL JR, TECHNICAL SERVICES REPR., OFPHILLIPS DRISCOPIPE INC. EVALUATED THE FUSION JOINT THAT FAILED. CAUSE OF THEINCIDENT - THE MOST PROBABLE CAUSE OF THE INCIDENT, AS RECONSTRUCTED FROM THEINVESTIGATION PERFORMED, WAS THAT THE STATIC ELECTRICITY BUILT UP DURING THESQUEEZE OFF OPERATION AND IGNITED THE GAS LEAKING FROM THE PLASTIC FUSED JOINTTHAT FAILED. ROOT CAUSE - POOR JUDGMENT WAS USED IN PLACEMENT OF THESQUEEZE-OFF TOOL; IT WAS TOO CLOSE TO A GAS LEAK. NO PROVISIONS WERE MADE TODISSIPATE THE STATIC CHARGE. THE SAFETY ASPECTS OF WHAT COULD HAPPEND WERE NOTCONSIDERED PRIOR TO THIS OPERATION. ACTIONS TO PREVENT REOCCURENCES: ALLSQUEEZE-OFF TOOLS ARE NOW EQUIPPED AND PERSONNEL HAVE BEEN TRAINED TO INSTALLGROUNDING KITS ON ALL SQUEEZE-OFF EQUIPMENT. PLASTIC PIPE TO BE SQUEEZED OFF,ALONG WITH TIE-IN OF PLASTIC PIPE, WILL BE SPRAYED WITH A SOAPY WATER SOLUTIONTO ASSIST IN DISSIPATING THE STATIC CHARGE ON THE PIPE. THE TIE-IN FUSE THATFAILED WAS MADE WITH THE OVERBEND METHOD; THIS METHOD WILL ONLY BE USED IFCONDITIONS ARE IDEAL. ALL 6" FUSES MADE BY THIS METHOD IN THIS DISTRICT WILLBE EXCAVATED AND EVALUATED FOR PROPER MELT. A 6" COUPLING WILL BE PLACED OVERTHESE FUSES TO PREVENT REOCCURENCES OF THIS TYPE OF GAS LEAK. A VIDEO ONSTATIC ELECTRICITY WILL BE SHOWN TO ALL MEMBERS OF THE CREWS PLUS SUPERVISIONTO HIGHLIGHT THE IMPORTANCE OF THIS SUBJECT. THE CREW CHIEF AND THE SUPERVISORON THE JOB SITE WERE REPRIMANDED FOR THE USE OF POOR JUDGMENT. THIS CREW ANDTHE SUPERVISOR ARE NOW HOLDING SAFETY MEETINGS WITH ALL GAS PERSONNEL IN THEREGION TO EXPLAIN THE INCIDENT AND HOW THEY FELT IT COULD HAVE BEEN PREVENTED.
2025-01-31 10:21 | YES | NO | 19940084 | 1994-03-23 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 7919 TROUT STREET | NEW ORLEANS | ORLEANS | LA |  | 3 | NO | 1326 | 1994-03-14 | 0 | 0 | 75000 | 56159.3688 | 135594.9673 | Null | 0 | 14 |  | 19940314 | 75 | 95 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER OWNED FUEL LINE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GREG J. GRILLO - MANAGER - GAS ENGINEERING | 5045953541 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19940085 | 1994-03-23 | 13710 | NORTHERN ILLINOIS GAS CO | 345 E. WASHINGTON | SOMONAUK | DE KALB | IL | 60552 | 1 | NO | 1307 | 1994-02-17 | 0 | 0 | 90000 | 67391.2425 | 162713.9608 | Null | 2 | 22 |  | 19940217 | 56 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 1960 | UNDER PAVEMENT |  | RICH WOODARD - CONSTR/MAINT. MANAGER | 8154333850 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | NOT GIVEN | NO |  | NO | 0 |  | NO |  |  | MAIN DAMAGED BY OUTSIDE FORCE CAUSING PIPE STRESSES THAT LEAD TO PIPE FAILURE
2025-01-31 10:21 | YES | YES | 19940086 | 1994-03-25 | 18532 | SOUTHERN UNION GAS CO | 1004 EAST 49TH STREET | AUSTIN | TRAVIS | TX | 78751 | 3 | NO | 200 | 1994-02-02 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 35 |  | 19940202 | 42 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0 |  |  | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | ROBERT FRANSON - REGIONAL ENGINEER | 5124651101 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19940087 | 1994-03-30 | 15931 | PUBLIC SERVICE CO OF COLORADO | 14935 EAST STANFORD DRIVE | AURORA | ARAPAHOE | CO | 80015 | 3 | NO | 329 | 1994-02-28 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 0 | 30 |  | 19940228 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | VALVE |  | OTHER | GAS METER | 75 | 0 |  | SPRAGUE MTR,ECONOMY REG,DRESSER,CAP. UN. | 0 | 1973 | ABOVE GROUND |  | TOMY L. WILSON - EXECUTIVE FOREMAN | 3035713858 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | FIRE ON STRUCTURE DAMAGED PUBLIC SERVICE COMPANY FACILITIES AT STRUCTURE.
2025-01-31 10:21 | YES | NO | 19940088 | 1994-03-29 | 8070 | INDIANA GAS CO INC | 117 BLUE RIVER ROAD | EDINBURG | JOHNSON | IN | 46124 | 3 | NO | 1315 | 1994-03-04 | 0 | 0 | 78000 | 58405.7435 | 141018.766 | Null | 0 | 20 |  | 19940304 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 1 | 0.099 | D2513 | UPONOR | 1989 | 1990 | UNDER GROUND OR UNDER WATER |  | RICHARD L. SLAGLE - PROJECT ENGINEER | 3173210518 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-03-01 | YES | 3 | PAINT | YES |  |  | A 1" PLASTIC SERVICE TO 117 BLUE RIVER ROAD, IN EDINBURG, JOHNSON COUNTY, INDIANA, WAS MISLOCATED. LOCATOR LOCATED RETIRED 3/4" STEEL SERVICE THAT RAN PARALLEL AND 3" NORTH OF LIVE PLASTIC SERVICE. THE ESTIMATED DAMAGE OF $78,000 CONSISTED OF; DAMAGE TO THE STRUCTURE AT 117 BLUE RIVER ROAD OF $50,000, DAMAGE TO THE STRUCTURE AT 115 BLUE RIVER ROAD OF $20,000, AND DAMAGE TO A WALK BEHIND TRENCHER OF $8,000.
2025-01-31 10:21 | NO | NO | 19940092 | 1994-04-06 | 12390 | METROPOLITAN UTILITIES DISTRICT | 6TH & EMMET STREET | OMAHA | DOUGLAS | NE | 68104 | 3 | NO | 1620 | 1994-03-22 | 0 | 0 | 3000 | 2246.3748 | 5423.7987 | YES | 0 | 45 |  |  | 122 | 125 | BY TEST | 210 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | JOINT | CPLG | STEEL |  | 12 | 0.25 | API 5L X42 | LTB STEEL TUBULAR PROD. CO | 1990 | 1994 | UNDER GROUND OR UNDER WATER | OPEN DITCH | DONALD D. BLOCKER | 4024498210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | EXIST. 12" 125# MAIN REQUIRED RELOCATION FOR SEWER CONST. NEW SEGMENT INSTALLED & PRESSURE TESTED-OK. NEW SEGMENT CONNECTED TO EXIST MAIN W/OFFSET OF 2-90 BENOS & COMPRESION CPLG'S. OFFSETS BLOCKED, MAIN PURGED OF AIR & BROUGHT UPTO 15 PSIG. WELDER STARTED INSTALLATION OF HARNESS ASSBLY ON CPL'S JOINTS. BEFORE JOB COMPLETED END OF WORK DAY & JOB SHUT DOWN. CONST & GAS DIST FELT TEMPORORY BACKING ON OFFSETS WAS ADEQUATE TO HOLD 125#. MAIN PRESSURE RAISED TO125#. JOINTS CHECKED. ALL SEEMED SECURE. CREW LEFT. SHORT TIME LATER: SHORING JACK FAILED & PRIDE PUSHED OUT OF CLG. MAIN SHUT DOWN & REPAIRS COMPLETED -NO IGNITION/EXPLOSION- MINDEBRIS DAMAGE SEGMENT OF EXIST. MAIN RELOCATED NEWSECTION PRESSURE TESTED-OK. NEW SECTION TIED IN THE EXIST. SECTION W/OFFSETS. OFFSET BRACED & PRESSURIZED TO 15LB. HARNESSES BEING INSTALLED ON CPL'S. PRESSURE INCREASED TO 125LB BEFORE HARNESSES COMPLETE. SHORING JACK FAILED & PIPE PUSHED OUT OF CPLG.
2025-01-31 10:21 | NO | NO | 19940093 | 1994-02-28 | 13299 | NEW JERSEY NATURAL GAS CO | 2041 PENNSYLVANIA AVENUE | SHIP BOTTOM | OCEAN | NJ | 08008 | 3 | NO | 239 | 1994-02-10 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 19 |  | 19940210 | 54 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE THE BUILDING | OTHER | SEE REMARKS | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MONIQUE L. HERZOG - COMPANY QUALITY CONTROL ENGINEER | 9089381193 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19940094 | 1994-04-07 | 1376 | BERWICK, TOWN OF | GULF INTRACOASTAL WATERWAY | BERWICK | ST MARY | LA | 70342 | 1 | NO | 412 | 1994-03-03 | 0 | 0 | 32000 | 23961.3307 | 57853.8527 | YES | 0 | 8 |  | 19940303 | 350 | 350 | BY TEST | 525 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | STEEL |  | 40 | 0.337 | SCH 80 |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ALLEN J. BENOIT - TOWN SUPERINTENDANT | 5043848858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES
2025-01-31 10:21 | NO | NO | 19940095 | 1994-01-15 | 1134 | BARROW UTILITIES & ELECTRIC CORP | 5201 KARLUK STREET | BARROW |  | AK | 99723 | 3 | NO | 1345 | 1994-01-13 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 4 |  | 19940114 | 20 | 65 | BY TEST | 110 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.315 | 0.12 | SDR 11 | DRISCO PIPE | 1992 | 1993 | UNDER GROUND OR UNDER WATER | EXPOSED TRENCH | ALLEN NESTEBY - OPERATIONS SUPERINTENDENT | 9078526166 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 2:39 A.M. ON FEBRUARY 10, 1994, NEW JERSEY NATURAL GASCOMPANY (NJNG) RECEIVED A TELEPHONE REPORT OF AN EXPLOSION FROM THE SHIPBOTTOMPLOICE DEPARTMENT. AN NJNG SERVICEMAN ARRIVED ON THE SCENE AT 3:30 A.M.AND FOUND THE BUILDING DESTROYED AND A SMALL, CONTROLLED FIRE BURNING IN THEKITCHEN AREA. FIRE AND POLICE PERSONNEL WERE AT THE SCENE BUT HAD NOT SHUT OFFTHE GAS. THE OUTSIDE METER SET WAS BLOCKED BY DEBRIS AND THE CURB VALVE BOXWAS COVERED BY ICE AND SNOW. ADDITIONAL NJNG PERSONNEL WERE DISPATCHED TO THESITE AND THE OTHER BUILDINGS IN THE AREA WERE CHECKED FOR THE PRESENCE OF GASWITH A COMBUSTIBLE GAS INDICATOR. ALL MAINS AND SERVICES UNIT. AT 6: A.M., ASINGLE LEAK WAS LOCATED. THIS LEAK WAS ON THE SERVICE RISER AT #2005PENNSYLVANIA AVENUE AND COULD NOT HAVE CONTRIBUTIED TO THE EXPLOSION. NO OTHERLEAKS WERE FOUND AND NO INDICATION OF GAS WAS FOUND IN ANY NEARBY BUILDINGS.THE 3/4" STEEL SERVICE LINE OT #2041 PENNSYLVANIA AVENUE WAS RETIRED ATAPPROXIMATELY 7:20 A.M. AND PRESSURE TESTED WITH AIR AT THE CURRENT OPERATINGPRESSURE, 54 PSIG, FOR 20 MINUTES. THE LINE HELD THE PRESSURE. THIS SERVICELINE AND 2" STEEL GAS MAIN IN PENNSYLVANIA AVENUE WERE EXAMINED AND FOUND TOBE IN GOOD CONDITION. COPIES OF THE MAINTANANCE ORDERS FOR THE PRESSURE TESTAND MAIN CONDITION REPORT ARE ATTACHED. THE METER BUILD-UP AND SERVICEREGULATOR WERE EXAMINED AND FOUND TO BE INTACT. THEY WERE REMOVED BY NJNG ANDHELD IN STORAGE PENDING RECEIPT OF THE FIRE MARSHAL'S REPORT WHICH IS ALSOATTACHED. THE FIRE MARSHAL'S REPORT CONCLUDES THAT THE EXPLOSION OCCURRED INTHE KITCHEN AREA WHERE THE STOVE AND WATER HEATER WERE LOCATED. THIS ISCONSISTENT WITH NJNJG'S CONCLUSION THAT OUR FACILITIES WERE NOT INVOLVED INTHE INCIDENT.AT APPROXIMATELY 1:45 PM ON THURSDAY, 01/13/94, A FIRE ERUPTED IN TRENCH S/CH 1 CONTINUATION OT HOUSES 19 AND 20. THE FIRE WAS QUICKLY EXTINGUISHED AND THERE WAS NO INJURY OR SIGNIFICANT DAMAGE. THE FIRE WAS CAUSED BY ONE OF THE LABORERS USING A PROPANE TORCH TO APPLY THE HEAT SHRINK TO THE SEWER TIE-IN. THIS REQUIRES SOME EXPLANATION. ALL OF THE UTILITIES IN THE 21 - UNIT HOUSING(SEWER, WATER AND GAS) RUN IN THE SAME TRENCH (SEE 12/21 HOUSING SERVICE CONNECTIONS, SHEET C6, DETAIL 7). OFTEN IN THE COURSE OF CONSTRUCTION, A GIVEN TRENCH MAY NOT BE COMPLETED IN ONE CONTINUOUS TIME SPAN. OFTEN THE UTILITIES ARE COMPLETED IN SEGMENTS. WHEN THIS OCCURS, THE UTILITIES ARE STUBBED-OUT (IE: CAPPED OFF) AND BURIED. WHEN THE REMAINING WORK IS TO BE DONE, THE STUBS ARE EXPOSED AND THE REST OF THE UTILITY LINES ARE THEN TIED INTO THE EXISTING LINES. THE WORK THAT WAS IN PROGRESS AT THE TIME OF IGNITION WAS THE PLACING OF THE HEAT SHRINK AT THE SEWERLINE TIE-IN. AS SHOWN IN THE ABOVE REFERENCED DRAWING, THE GAS LINE IS IN VERY CLOSE PROXIMITY TO THE OTHER LINES IN THE TRENCH. THE LABORER WHO WAS PERFORMING THE HEAT SHRINK WORK (FOREST AHKIVIANA) HAD NOT PLACED ANY HEAT SHIELDING OVER THE GAS LINE. SINCE THE GAS LINE IN THIS AREA IS MADE OF HDPE (HIGH DENSITY POLYETHYLENE) THE FLAME FROM THE TORCH SOFTENED THE HDPE LINE. THE GAS DISTRIBUTION PRESSURE OF TWENTY POUNDS CAUSED THE SOFTENED PIPE TO RUPTURE AND THE GAS WAS THEN IGNITED BY THE TORCH. ONE OF THE WORKERS (BILLY ITTA) RAN TO A NEARBY VEHICLE (APPROXIMATELY 30 FEET AWAY) FOR A FIRE EXTINGUISHER AND QUICKLY EXTINGUISHED THE FIRE. I ESTIMATE THATTHE FIRE LASTED APPROXIMATELY 30 SECONDS. MEANWHILE, ANOTHER WORKER (MARK TYREE) HAD GOTTEN A CLAMP AND BEGUN TO SQUEEZE THE LINE CLOSED. BEFORE HE COULDACCOMPLISH THE TASK, A WORKER FROM BUECI (BARROW UTILITIES AND ELECTRIC COOPE
2025-01-31 10:21 | YES | YES | 19940096 | 1994-01-18 | 13660 | NORTH SHORE GAS CO | 219 GREENWOOD AVENUE | WAUKEGAN | LAKE | IL | 60085 | 3 | NO | 300 | 1994-01-15 | 1 | 0 | 0 | 0 | 0 | Null | 3 | 0 |  | 19940115 | 40 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 |  |  | 0 | 1961 | UNDER PAVEMENT |  | M.P. CWIK - MANAGER OF OPERATIONS | 7083367400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CIRCUMFERENTIAL CRACK IN 4-INCH CATHODICALLY PROTECTED STEEL PIPE LEAKED CAUSING GAS TO MIGRATE UNDERGROUND TO THE BUILDING. GAS IGNITED BY UNKNOWN CAUSE. CAUSE OF CRACK UNKNOWN AT THIS TIME.
2025-01-31 10:21 | NO | NO | 19940097 | 1994-02-09 | 1209 | BAY STATE GAS CO | ENTERPRISE DRIVE | MARSHFIELD | PLYMOUTH | MA | 02401 | 2 | NO | 1700 | 1994-01-15 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 10 |  | 19940116 | 70 | 99 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | MIXING CHAMBER | DRIP/RISER |  | STEEL |  | 16 | 0.375 |  |  | 1972 | 1972 | UNDER GROUND OR UNDER WATER |  | ROBERT E. CHRISTINE - MANAGER GAS OPERATOR | 5085867390 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE FRACTURE WAS A 16" MIXING CHAMBER AS IT ENTERS OUR 12" DISTRIBUTION SYSTEM. IT OCCURRED SHORTLY AFTER STARTING UP THE PORTABLE LNG VAPORIZER. THERE IS SOME EVIDENCE OF COLD GAS CARRY OVER. WE DO NOT KNOW IF IT OCCURRED BEFOREOR AFTER THE FRACTURE. THE FRACTURED MIXING CHAMBER HAS BEEN SENT TO A METALLURGIST FOR ANALYSIS TO DETERMINE TYPE AND CAUSE OF FRACTURE.
2025-01-31 10:21 | YES | YES | 19940098 | 1994-02-09 | 8040 | ILLINOIS POWER CO | 127 COOPER AVENUE | EAST ALTON | MADISON | IL | 62095 | 3 | NO | 832 | 1994-01-21 | 2 | 2 | 150000 | 112318.7376 | 271189.9346 | Null | 3 | 35 |  | 19940121 | 30 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | JOINT | COMP | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | GLEN E. CARTER - SUPERVISOR GAS QUALITY PROGRAMS | 2174246853 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 8:32 A.M. ON JANUARY 21, 1994, ILLINOIS POWER WAS NOTIFIED OF A FIRE AND WXPLOSION AT 127 COOPER AVENUE, EAST ALTON, ILLINOIS. UPON ARRIVAL AT THE SCENE, IT WAS NOTED THAT AN EXPLOSION HAD OCCURRED AND THE RISER WAS BROKEN "FUELING THE FIRE". AN INVESTIGATION OF THE SURROUNDING AREA SHOWED NO HOMES OR SURROUNDING MAINS AND SERVICES HAD ANY DETECTABLE GAS. THE SERVICE LINE WAS DISCONNECTED AT 12:05 P.M., STOPPING THE FIRE AT WHICH TIME IT WAS DETERMINED THE AREA WAS SAFE. THE SERVICE LINE WAS DISCONNECTED AT 12:05 P.M., STOPPING THE FIRE AT WHICH TIME IT WAS DETERMINED THE AREA SAFE. THE SERVICE WAS SUBSEQUENTLY PRESSURE TESTED AND FAILED THE PRESSURE TEST. A COMPRESSION COUPLING ATTACHING THE SERVICE RISER WAS THE APPARENT REASON FOR THE FAILED PRESSURE TEST. PER THE EAST ALTON FIRE DEPARTMENT, THE FUEL SOURCE OF THE EXPLOSION WAS NATURAL GAS AND THE IGNITION SOURCE WAS THE RESIDENT'S CIGARETTE. THE CIRCUMSTANCES CONTRIBUTING TO THE SOURCE OF NATURAL GAS ARE YET TO BE DETERMINED.
2025-01-31 10:21 | YES | YES | 19940099 | 1994-02-18 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | RED ROCK HILL | DUKE CENTER | MCKEAN | PA | 16729 | 3 | NO | 2345 | 1994-01-26 | 0 | 1 | 35000 | 26207.7054 | 63277.6514 | Null | 0 | 40 |  | 19940127 | 0 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | OTHER | RELIEF VALVE | CAST IRON |  | 0 | 0 | ASTM A126-71 | ROCKWELL | 0 | 1993 | ABOVE GROUND |  | CONRAD L. DONELSON - SUPERINTENDENT | 8148718341 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A PRESSURE REDUCING REGULATOR IN A GAS SUPPLY REGULATOR STATION FAILED IN THEOPEN POSITION ACTIVATING THE PRESSURE RELIEF VALVE AT THE STATION. THE SUBSEQUENT CLOSED FAILURE OF THIS PRESSURE RELIEF VALVE OVER-PRESSURED THE DOWNSTREAM GAS DISTRIBUTION SYSTEM ACTIVATING THE INTERNAL PRESSURE RELIEF MECHANISMON MANY SERVICE REGULATORS. ESCAPING GAS FROM ONE OF THESE SERVICE REGULATORS WAS IGNITED BY AN UNKNOWN SOURCE. ONE (1) TRAILER WAS DESTROYED BY FIRE ANDONE (1) OCCUPANT WAS INJURED.
2025-01-31 10:21 | YES | NO | 19940100 | 1994-02-14 | 15462 | PHILADELPHIA ELECTRIC CO | 2289 MULBERRY LANE | WHITEMARSH | MONTGOMERY | PA | 19444 | 2 | NO | 1100 | 1994-01-23 | 0 | 0 | 200000 | 149758.3167 | 361586.5795 | Null | 1 | 40 |  | 19940123 | 15 | 25 | BY TEST | 50 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.41 | ASA A21.7 |  | 0 | 1957 | UNDER PAVEMENT |  | SANDRA J. MAY - PROJECT ENGINEER | 6109471779 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | CORRODED SERVICE AT 2289 WAS A PROBABLE CONTRIBUTOR TO THE FIRE. A CRACKED MAIN AND LEAKING GAS SERVICE CAUSED GAS TO MIGRATE UNDER THE PAVEMENT AND INTOTHE HOME AT 2289 MULBERRY. THE GAS BUILT UP BEHIND AN ELECTRIC DRYER LOCATEDIN THE BASEMENT. WHILE THE RESIDENT WAS SHOWERING, SHE HEARD A PLATE FALL FROM THE WALL, APPARENTLY CAUSED WHEN THE GAS IGNITED. SHE VACATED THE HOUSE ALONG WITH HER 2 DAUGHTERS AND CALLED THE FIRE COMPANY. THE HOUSE EXPERIENCED MAJOR FIRE DAMAGE. AS A RESULT OF THE LEAKS, 4 OTHER HOMES WERE EVACUATED.SHORTLY BEFORE 11:OO AM, SUNDAY, JANUARY 23, 1994, THE RESIDENT A 2289 MULBERRY LANE WAS SHOWERING WHEN SHE HEARD A PLATE FALL FROM THE WALL SHE HAD JUST LEFTTHE BASEMENT AFTER PUTTING IN A LOAD OF CLOTHES INTO THE ELECTRIC DRYER. AT APPROXIMATELY 10:00 AM, WHILE IN THE BASEMENT, SHE SMELLED GAS JUST AS SHE HAD 3 TO 4 DAYS PRIOR. SHE RUSHED DOWNSTAIRS AND OPENED THE BASEMENT DOOR AND SAW THE FIRE. SHE EVACUATED THE HOUSE IMMEDIATELY WITH HER 2 TEENAGE DAUGHTERSAND CALLED 911 FROM A NEIGHBOR'S HOME. AT 11:OO AM PLYMOUTH DISPATCH WAS NOTIFIED OF A FIRE AT 2289 MULBERRY LANE IN WHITEMARSH TOWNSHIP. UTILIZATION MECHANIC, STEVE TODOR, WAS DISPATCHED TO THIS LOCATION. WHEN TODOR ARRIVED AT 11:30 AM, AN OFFICER OF THE FIRE DEPARTMENT INFORMED HIM THAT THE GAS METER IN THE BASEMENT OF 2289 HAD BEEN SHUT OFF. THE OFFICER THEN REQUESTED TODOR TO SHUT OFF THE VALVE AT THE CURB BOX. DUE TO ICE AND SNOW THE CURB BOX COULD NOTBE LOCATED. AT 11:40 AM, DUE TO THE URGENCY OF THE SITUATION, HE RADIOED DISPATCH AND REQUESTED ASSISTANCE. ANOTHER UTILIZATION MECHANIC, JOE WOLOS, ARRIVED AT 11:53 SHORTLY AFTER JOHN NORMAN, THE ON-CALL UTILIZATION SUPERVISOR. IMMEDIATELY, WOLOS AND NORMAN ENTERED 2289 WHERE WOLOS INSTRUCTED A FIREMAN INSHUTTING OFF THE SAVAGE COCK. THIS SHUT OFF IMMEDIATELY EXTINGUISHED THE FLAMES AT THE OUTSIDE VENT AND AROUND THE INDOOR METER LOCATION. HOWEVER, THE FLAMES AT THE WINDOW WELL CONTINUED TO BURN. TODOR THEN CHECKED THE PERIMETERS ON NEARBY MANHOLES WHICH THE UTILIZATION MECHANICS BEGAN TO OPEN AT 11:55 AM.AT 11:58 AM, NORMAN INSTRUCTED WOLOS TO CALL DISPATCH FOR A DISTRIBUTION CREW. THE ON-CALL ENGINEER, SANDRA MAY, WAS MONITORING THE RADIO AND REPORTED TOTHE SITE BY 12:00 PM. IT WAS LATER DETERMINED THAT THE FIRE WAS A RESULT OF A LEAKING MEDIUM PRESSURE CAST IRON MAIN. ANOTHER POSSIBLE CONTRIBUTOR WAS A LEAK FOUND ON THE SERVICE AT 2289. THIS SERVICE WAS RENEWED ALONG WITH 4 OTHERS ON MULBERRY LANE.
2025-01-31 10:21 | YES | NO | 19940101 | 1994-02-16 | 18484 | SOUTHERN CALIFORNIA GAS CO |  | LOS ANGELES | VENTURA | CA |  | 3 | NO | 431 | 1994-01-17 | 0 | 0 | 30000000 | 22463747.5121 | 54237986.9207 | YES | 0 | 0 |  | 19940117 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | G.J. LAMBETH - MANAGER OF SAFETY MANAGEMENT | 2132443280 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JANUARY 17, 1994, AT 0431 HOURS, AN EARTHQUAKE WITH A RICHTER SCALE MAGNITUDE OF 6.7 HIT THE SOUTHERN CALIFORNIA AREA. THE AREAS MOST SEVERELY IMPACTED IN SOUTHERN CALIFORNIA GAS COMPANY SERVICE TERRITORY WERE THE AREAS OF NORTHRIDGE, VALENCIA, SIMI VALLEY, FILLMORE, SANTA MONICA AND ADJACENT AREAS IN LOS ANGELES AND VENTURA COUNTIES.
2025-01-31 10:21 | YES | YES | 19940105 | 1994-01-18 | 2392 | CITIZENS GAS & COKE UTILITY | 1100 WEST 21 STREET | INDIANAPOLIS | MARION | IN | 46202 | 3 | NO | 1002 | 1994-01-12 | 0 | 1 | 30000 | 22463.7475 | 54237.9869 | YES | 1 | 30 |  | 19940112 | 25 | 40 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 16 | 0.5 |  |  | 0 | 1925 | WITHIN/UNDER BUILDING |  | EARLE D. STEVENSON - DIRECTOR OF DISTRIBUTION OPERATIONS | 3179274626 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | 16" CAST IRON MAIN BROKE ALLOWING GAS TO MIGRATE INTO THE BUILDING. THE GAS WAS IGNITED BY AN UNKNOWN SOURCE CAUSING THE BUILDING TO EXPLODE, BLOWING OUTSEVERAL WINDOWS AND CAUSING EXTENSIVE FIRE DAMAGE. ONE EMPLOYEE OF THE WAREHOUSE WAS SEVERELY BURNED. RECEIVED NOTIFIECATION FROM INDIANAPOLIS FIRE DEPARTMENT OF REPORTED EXPLOSION. UPON ARRIVAL FOUND WINDOWS BROKEN AND EVIDENCE OFFIRE. INJURED IN THE EXPLOSION WAS JIMMY HAMMITT, 04/20/1937. SECOND AND THIRD DEGREE BURNS ON HANDS, FOREARMS, FACE AND LEGS. CAUSE OF IGNITION IS UNKNOWN. WE FOUND A 16" CAST IRON MAIN BROKEN. GAS ENTERED THE BUILDING AND IGNITED CAUSING THE EXPLOSION.
2025-01-31 10:21 | NO | NO | 19940107 | 1994-04-06 | 15007 | PACIFIC GAS & ELECTRIC CO | 27685 MANON AVENUE | HAYWARD | ALAMEDA | CA | 94541 | 3 | NO | 2307 | 1994-03-26 | 0 | 0 | 30000 | 22463.7475 | 54237.9869 | Null | 2 | 35 |  |  | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 1.75 | 0.113 | SCHEDULE 40 |  | 1982 | 1983 | ABOVE GROUND |  | JAMES H. POPE - VICE PRESIDENT TECHNICAL & CONSTRUCTION SVC | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | U.S.A. INFORMATION DOES NOT APPLY DUE TO NATURE OF INCIDENT. SEE PART 3 DESCRIPTION. AUTOMOBILE STRUCK METER SET AND IGNITED. FIRE SPREAD TO RESIDENCE.
2025-01-31 10:21 | NO | NO | 19940110 | 1994-04-18 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | DECATUR ST. AT ST. PETER | NEW ORLEANS | ORLEANS | LA |  | 4 | NO | 616 | 1994-03-20 | 0 | 0 | 0 | 0 | 0 | YES | 12 | 5 |  |  | 70 | 110 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0 |  |  | 0 | 1928 | UNDER PAVEMENT |  | GREG J. GRILLO - ENGINEERING MANAGER | 5045953541 | EXTERNALLY | GENERAL CORROSION |  | OTHER | FIELD WRAP | COATED | YES | 1930 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19940117 | 1994-04-21 | 15084 | PALO ALTO, CITY OF | 3303 THOMAS DRIVE | PALO ALTO | SANTA CLARA | CA | 94306 | 3 | NO | 0 | 1994-03-22 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19940322 | 12 | 25 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | ABS PIPE | 0.75 | 0.09 |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | RODGER JENSEN | 4154966932 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION
2025-01-31 10:21 | YES | YES | 19940119 | 1994-05-02 | 21349 | VIRGINIA NATURAL GAS | 876 C AVENUE | NORFOLK |  | VA | 23504 | 3 | NO | 1500 | 1994-04-05 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 2 |  | 19940405 | 0.25 | 2 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | NOT GIVEN | STEEL |  | 1.14 | 0.14 | APL 5L |  | 1993 | 1994 | OTHER | NOT GIVEN | DONAL L. WHITE - MANAGER | 8044665422 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19940122 | 1994-05-06 | 20061 | UNION GAS CO | 338 FREMONT STREET | WEST PITTSTON | LUZERNE | PA | 18643 | 3 | NO | 700 | 1994-04-02 | 0 | 2 | 200000 | 149758.3167 | 361586.5795 | Null | 2 | 26 |  |  | 58 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDETERMINED | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | WILLIAM SHUGDINIS | 7176543353 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | UNDETERMINED AND UNDER INVESTIGATION. SUPPLEMENTAL REPORT 1/19/95 INDICATESTHE FOLLOWING: UNION GAS CO, PITTSTON DISTRICT ON APRIL 2, 1994, CONDUCTED AHOUSE TO HOUSE INVESTIGATION INSIDE THE BASEMENTS, FIRST FLOORS, AND SECONDFLOORS OF THE HOMES IN THE 300 BLOCK OF FREMONT ST. AND ALSO THE HOMES ON THESURROUNDING STREETS. ANOTHER SURVEY WAS CONDUCTED ALONG THE MAINS IN THE TWOBLOCKS SURROUNDING THE SITE. ALL INVESTIGATIONS SHOWED NO INDICATIONS OF ANYGAS LEAKAGE. AN INACTIVE SERVICE TO THE 338 FREMONT ST. WAS RETIRED AT 9:26AMON APRIL 2, 1994 DUE TO A FIRE IN THE AREA OF AN INACTIVE RISER AT THISLOCATION. ON APRIL 4, 1994, IN THE PRESENCE OF THE P.U.C. AND THE PA. STATEFIRE MARSHALL, THE PLASTIC PORTION OF THIS SERVICE WAS AIR TESTED AT 61POUNDS FOR A PERIOD OF THREE HOURS AND THREE MINUTES. THE TEST INDICATED NOLEAKAGES. A TEST OF THE PLASTIC TAPPING TEE ATTACHED TO THE MAIN WAS ALSOCONDUCTED WITH NO LEAKAGE FOUND. A 1" PLASTIC COUPLING WAS REMOVED AND ALSOTHE SERVICE RISER WAS REMANDED TO THE CUSTODY OF THE P.U.C. A SURVEY OF THESTORM DRAINS AND MANHOLES WAS CONDUCTED IN THE TWO BLOCK AREA AND AGAIN, NOTRACES A GAS WERE FOUND. ADDITIONAL LEAK TESTS DONE AROUND THE FOUNDATIONAREA OF 338 FREMONT ST. ON APRIL 7, 1994 AND APRIL 11, 1994 AGAIN ALSORESULTED IN NEGATIVE RESULTS. THE REMOVED 1" CTS COUPLING AND RISER WERETESTED BY UBA FIRE AND EXPLOSION INVESTIGATORS IN THE PRESENCE OF THE P.U.C.THE COUPLING WAS AIR TESTED AND SHOWED NO LEAKAGE. THE RISER AND VALVE WEREDISASSEMBLED AND IT WAS FOUND THAT AN O RING SEAL IN THE TOP OF THE RISER HADMELTED. AS OF THIS DATE, UNION GAS CO AND THE PA. STATE FIRE MARSHALL HAVELISTED THE CAUSE AS UNDETERMINED.
2025-01-31 10:21 | YES | NO | 19940124 | 1994-05-06 | 11032 | LACLEDE GAS CO | 2452 COUNTRY RUN COURT | MARYLAND HEIGHT | ST LOUIS | MO | 63043 | 3 | NO | 1240 | 1994-04-11 | 0 | 0 | 100000 | 74879.1584 | 180793.2897 | Null | 1 | 25 |  | 19940411 | 14.2 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 |  | CONTINENTAL INDUSTRIAL | 1975 | 1975 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER | 3143420528 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 3 | NOT GIVEN | NO |  |  | THE AREA SURROUNDING THE SERVICE TEE HAD BEEN EXCAVATED ON AUGUST 2,1993, BYSOUTHWSTERN BELL TELEPHONE COMPANY OR THEIR SUBCONTRACTOR TO EXPOSE HE TELEPHONE CABLES THAT HAD BEEN INSTALLED IN THE SAME TRENCH WITH THE GAS MAIN AND SERVICE LINE. THE GAS MAIN, SERVICE TEE, OR GAS SERVICE LINE WERE DISTURBED WHEN EXPOSED. RECENT HEAVY RAINS MAY HAVE CONTRIBUTED TO SUBSIDENCE OF THE SOIL AROUND THE GAS MAIN AND SERVICE LINE. SUCH SUBSIDENCE MAY HAVE CONTRIBUTED TO THE PULL-OUT OF THE SERVICE LINE FROM THE SERVICE TEE. SATURATED SOIL MAY HAVE PREVENTED THE VENTING OF THE GAS TO THE ATMSPHERE CAUSING IT TO MIGRATE INTO THE RESIDENCE, RESULTING IN THE EXPLOSION AND FIRE.
2025-01-31 10:21 | NO | NO | 19940127 | 1994-05-10 | 15359 | PEOPLES NATURAL GAS | 2430 BUFFALO BLVD | WINTHROP | BUCHANAN | IA | 50682 | 1 | NO | 400 | 1994-04-09 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | YES | 0 | 30 |  | 19940409 | 10 | 10 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER | NOT GIVEN | OTHER PLASTIC | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GREGORY J. BENAK | 4022212021 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE IN GARAGE BELIEVED TO HAVEE BEEN CAUSED BY GASOLINE LEAK FROM AUTOMOBILE(PER FIRE MARSHALL).
2025-01-31 10:21 | YES | YES | 19940128 | 1994-05-03 | 12810 | MORTON MUNICIPAL GAS UTILITY, CITY OF | NORTH OF 128 W. QUEENWOOD ROAD | MORTON | TAZEWELL | IL | 61550 | 3 | NO | 815 | 1994-04-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19940423 | 25 | 40 | BY TEST | 60 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D 2513 | PLEXCO PE 2406 | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | LON K. BARKDOLL | 3092665361 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 2" PE GAS MAIN STRUCK BY UTILITY OWNED BACKHOE AND EMPLOYEES. AT APPROXIMATELY 08:15 AM ON PRIL 23, 1994, MORTON UTILITY GAS & WATER DISTRIBUTION CREWS, STRUCK A 2 IN. PE 2406 GAS MAIN WHILE ATTEMPTING TO REPAIR A WATER LEAK THAT WAS LOCATED BELOW THE GAS MAIN THE RESULTING DAMAGE WAS A 9 TO 10" RIP IN THE2" PE MAIN THAT WAS OPERATED AT 25 PSIG. THE CREW ATTEMPTED TO CONTROL THE ESCAPING GAS BY USE OF A SINGLE VALVVE AND A SQUEEZE-OFF OF THE 2" PE IN THE AREA OF THE DAMAGE. WHILE ATTEMPTING THE SQUEEZE-OFF IN THE EXCAVATION. GAS EMPLOYEE - TOM J. SKAGGS SUFFERED ASPHYXIATION FROM THE ESCAPING NATURAL GAS. EMPLOYEES AT THE SCENE REMOVED TOM FROM THE ENVIRONMENT AND IMMEDIATLEY PERFORMED CPR REVIVING HIM. PARAMEDICS ARRIVED ON THE SCENE WITHIN 4 TO 5 MINUTES AND CONTINUED LIFE SUPPORT WHILE TRANSPORTING TO EMERGENCY AT ST. FRANCIS MEDICAL ,PEOIA, ILLINOIS. GAS WAS SHUT-OFF BY USE OF ONE ADDITIONAL VALVE AT APPROXIMATELY 08:30 AM AFFECTING 4 CUSTOMERS, INCLUDING A RESTAURANT AND MOTEL. REPAIRS WERE COMPLETED AND SERVICE RESTORED BY 09:30 AM.
2025-01-31 10:21 | YES | NO | 19940130 | 1994-04-19 | 15359 | PEOPLES NATURAL GAS | 603 WEST WATER STREET | FAYETTE | FAYETTE | IA | 52142 | 3 | NO | 1330 | 1994-02-25 | 0 | 0 | 110000 | 82367.0742 | 198872.6187 | Null | 14 | 0 |  | 19940414 | 9 | 9 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GREGORY J. BENAK - SENIOR ATTORNEY | 4022212021 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19940132 | 1994-06-13 | 22182 | WASHINGTON GAS | 654 NORTHAMPTON DRIVE | SILVER SPRING | MONTGOMERY | MD | 20903 | 3 | NO | 1700 | 1994-05-18 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 5 |  | 19940518 | 43 | 55 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | OTHER | NO FAILURE | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | WILLIAM A. HINDE | 7037507687 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | GAS DISTRIBUTION CONTRACTOR TAPED A LOW PRESSURE CUSTOMER-OWNED UNDERGROUND HOUSELINE AND INTRODUCED HIGH PRESSURE. THE GAS WAS CONTROLLED IMMEDIATELY. THERE WERE NO INJURIES. DAMAGE WAS LIMITED TO 34 GAS RANGES AND MINOR PAINT DAMAGE IN A FEW APARTMENTS.
2025-01-31 10:21 | YES | NO | 19940133 | 1994-06-15 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 7TH & VICTORY | LITTLE ROCK | PULASKI | AR | 72203 | 3 | NO | 1100 | 1994-05-18 | 0 | 0 | 75000 | 56159.3688 | 135594.9673 | Null | 4 | 30 |  | 19940518 | 22 | 60 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 16 | 0.6 |  |  | 1940 | 1940 | UNDER PAVEMENT |  | TOM CONNELL | 5013774732 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AGENT FOR OPERATOR ACCIDENTLY CUT & IGNITED 2" PLASTIC WHILE REMOVING ABANDONED LINE. 16" CI BROKE DUE TO EXPOSURE TO HEAT .
2025-01-31 10:21 | YES | YES | 19940134 | 1994-06-13 | 14210 | OKLAHOMA NATURAL GAS CO | PIONEER AND MONUMENT ROAD | PONCA CITY | KAY | OK | 74601 | 3 | NO | 900 | 1994-05-18 | 0 | 1 | 150000 | 112318.7376 | 271189.9346 | Null | 1 | 5 |  | 19940518 | 35 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4.5 | 0.156 |  |  | 0 | 1970 | UNDER PAVEMENT |  | G.B. LYNN | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-04-26 | YES | 3 | FLAGS AND PAINT | YES |  |  | DEPTH OF GAS LINE RELATIVE TO DEPTH OF STREET REPAIR WAS NOT DETERMINED BUT LINE WAS LOCATED IN A PLAN VIEW. STREET REPAIR MACHINE CUT DEEPER THAN EXPECTED AND STRUCK THE PIPE DURING PREPARATION FOR RESURFACING. OPERATOR KILLED THE ENGINE AND LEFT THE MACHINE IN PLACE. A FIRE IGNITED WHEN ANOTHER OF THE CONTRACTOR'S EMPLOYEES RETURNED TO THE MACHINE. SOURCE OF IGNITION IS NOT CERTAIN. PART 3- ELEVATION OF PIPE AND ELEVATION OF STREET CUT WERE TOO CLOSE.
2025-01-31 10:21 | YES | YES | 19940136 | 1994-06-07 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 7301 RIVER ROAD | NORTH BERGEN | BERGEN | NJ | 07047 | 3 | NO | 811 | 1994-05-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 29 |  | 19940512 | 13 | 15 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR11-3408 | DRISCOPIPE | 0 | 1990 | UNDER PAVEMENT |  | C.W. GREVENITZ | 2014307797 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-04-11 | YES | 3 | SEE REMARKS | YES |  |  | ON 04/11/1994 AT APPROXIMATELY 8:11 A.M. A 2" PLASTIC 15 PSI DESIGN GAS SERVICE TO #7301 RIVER ROAD, NORTH BERGEN WAS DAMAGED BY JAF EQUIPMENT INC. OF 88FOREST WAY, ESSEX FELLS, N.J. 07021, WHILE EXCAVATING WITH A VERMEER WHEEL TO INSTALL A SEWER LINE. ESCAPING GAS IGNITED CAUSING PERSONAL INJURIES TO MR.JOSE CARVEHLO THE EQUIPMENT OPERATOR. MR. CARVEHLO WAS ADMITTED TO THE HOSPITAL WITH BURNS TO HIS FACE AND ARMS. THE GAS WAS SHUT OFF AND PERMANENT REPAIRS TO THE SERVICE WERE COMPLETED THAT SAME DAY. PART B - DAMAGE BY OUTSIDE FORCE- TRAFFIC YELLOW PAINT ON PAVEMENT.
2025-01-31 10:21 | YES | YES | 19940137 | 1994-06-06 | 2204 | CENTRAL ILLINOIS PUBLIC SERVICE | CARGILL INC 1ST STREET | FLORENCE | PIKE | IL | 62363 | 3 | NO | 720 | 1994-04-12 | 0 | 1 | 20000 | 14975.8317 | 36158.6579 | Null | 10 | 25 |  | 19940412 | 400 | 400 | BY TEST | 600 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | WELD |  | STEEL |  | 2 | 0.154 | API-5L 68.8 |  | 0 | 1985 | WITHIN/UNDER BUILDING |  | JEROME S. THEMIG | 2175231792 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION | SEE REMARKS | A LEAKING WELD WAS FOUND APPROXIMATELY 70 FEET FROM THE BUILDING WHERE THE EXPLOSION OCCURED. AN ONGOING INVESTIGATION IS BEING CONDUCTED TO DETERMINE IFTHIS WAS A CONTRIBUTING FACTOR. PRELIMINARY FINDINGS INDIATE ABNORMALLY HIGHCONCENTRATION OF NATURALLY OCCURING METHANE OR "SWAMP GAS" IN THE AREA. AN INDEPENDANT CONSULTANT HAS TAKEN SAMPLES OF THE GAS FOUND UNDERGROUND AND OF PIPELINE GAS FOR ANALYSIS. THE RESULTS OF TEH ANALYSIS IS NOT YET KNOWN. AT APPROXIMATELY 07:20 ON TUESDAY APRIL 12, 1994 AN EMPLOYEE OF CARGILL INC. ENTERED THE BATHROOM OF A CONCRETE BLOCK BUILDING ON CARGILL INC. PROPERTY IN FLORENCE, IL AND WHILE IN THE PROCESS OF LIGHTING CIGARETTE CAUSED AND EXPLOSIONIN THE BUILDING. AN INVESTIGATION INTO THE CAUSE OF THE EXPLOSION WAS CONDUCTED BY CENTRAL ILLINOIS PUBLIC SERVICE COMPANY EMPLOYEES WHICH FOUND THE FOLLOWING: 1). THE BUILDING IN WHICH THE EXPLOSION OCCURRED CONTAINED NO NATURAL GAS OR L.P. GAS PIPING OR APPLIANCES. 2). A PINHOLE LEAK WAS FOUND AT A WELD ON A 2 IN. STEEL INTERCITY GAS MAIN APPROXIMATELY 70 FT. FROM THE BUILDING. 3). HIGH LEVELS OF A COMBUSTIBLE CONCENTRATION OF GAS WERE FOUND UNDERGROUND IN THE VICINITY OF BUILDING. 4). AN OPENING IN THE SLAB FLOOR OF THE BUILDING IS BELIEVED TO BE THE ENTRY POINT OF THE COMBUSTIBLE MIXTURE. PRELIMINARY FINDINGS INDICATE THAT ALL OR PART OF THE UNDERGROUND GAS MAY BE NATURALLY OCCURRING METHANE OR "SWAMP GAS". AN ONGOING INVESTIGATION IS BEING CONDUCTED TO DETERMINED THE CONTRIBUTING FACTORS AND THE CAUSE OF THE EXPLOSION. AN OUTSIDECONSULTANT IS ANALYZING THE WELD FOUND TO BE LEAKING TO DETERMINE THE CAUSE OF THE LEAK, THE RATE OF FLOW OF GAS ESCAPING FROM THE PINHOLE, AND IF THE LEAK COULD BE A CONTRIUTING FACTOR TO THE EXPLOSION. AN OUTSIDE CONSULTANT IS ALSO ANALYZING SAMPLES OF THE UNDERGROUND GAS FOUND IN THE VICINITY TO DETERMINE ITS COMPOSITION, SOURCE, AND TO DETERMINE IF IT COULD BE A CONTRIBUTING FACTOR, OR THE SOLE CAUSE OF THE EXPLOSION. AT THIS TIME THE INVESTIGATION IS NOT COMPLETE AND THE RESULTS OF THESE TESTS ARE NOT KNOWN.
2025-01-31 10:21 | YES | NO | 19940138 | 1994-06-06 | 4499 | ENTEX - DIVISION OF ARKLA INC | 3154 BAYBERRY | TAYLOR LAKE VILLAGE | HARRIS | TX |  | 0 | NO | 1532 | 1994-02-06 | 0 | 0 | 81786 | 61240.6685 | 147863.5999 | Null | 2 | 5 |  | 19940206 | 28 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | CONTACTOR CUT 2"PLASTIC | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR 11 | DUPONT | 0 | 1993 | UNDER GROUND OR UNDER WATER |  | LARRY L. HAMILTON | 7134228308 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | SEE REMARKS | NO |  |  | ELECTRICAL CONTRACTOR WAS TRENCHING AND HIT 2" PLASTIC MAIN LINE IN UTILITY EASEMENT, GAS IGNITED RESULTING IN LOSS OF ADJACENT HOME UNDER CONSTRUCTION. (APPROX. 60% COMPLETE) NO REQUEST WAS MADE FOR A LINE LOCATION. PART B - STAKED WITH FLAGS WHEN INSTALLED.
2025-01-31 10:21 | YES | NO | 19940139 | 1994-06-06 | 15007 | PACIFIC GAS & ELECTRIC CO | WEBSTER AND EAGLE | ALAMEDA | ALAMEDA | CA | 94501 | 3 | NO | 2304 | 1994-04-13 | 0 | 0 | 3600000 | 2695649.7015 | 6508558.4305 | YES | 3 | 52 |  | 19940414 | 3 | 36 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR/SECURITY VALVE | VALVE | REGULATOR/METER | STEEL |  | 0 | 0 | AFV | SINGER/ROCKWELL | 1967 | 1967 | UNDER PAVEMENT |  | JAMES H. POPE | 4159732063 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | LOW PRESSURE REGULATOR AND SECURITY VALVE FAILED, THUS OVERPRESSURIZING THEALAMEDA LOW PRESSURE SYSTEM. LOW PRESSURE REGULATOR AND SECURITY VALVE FAILED AND OVERPRESSUED THE SYSTEM.
2025-01-31 10:21 | YES | YES | 19940141 | 1994-06-03 | 4499 | ENTEX - DIVISION OF ARKLA INC | HWY.69 | LINDALE | SMITH | TX | 75773 | 3 | NO | 1554 | 1994-04-08 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19940408 | 30 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR 11.0 | UPONOR | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | KENNETH ROACH | 9035695402 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PIPE RUPTURED AND THE GAS IGNITED. THE TWO INCH PIPE RUPTURED AT THE SQUEEZER AND IGNITED, BURNING ONE EMPLOYEE ON HIS HANDS AND FACE. THIS EMPLOYEE WAS ABLE TO REPORT TO WORK THE NEXT WORK DAY.
2025-01-31 10:21 | YES | YES | 19940143 | 1994-05-17 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 4676 EASTERN AVENUE | KENTWOOD | KENT CITY | MI | 49508 | 2 | NO | 1005 | 1994-04-14 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 60 |  | 19940414 | 100 | 150 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | WELD | SERVICE TEE | STEEL |  | 8 | 0 |  |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | THADDEUS S. SLIWINSKI | 3135777024 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | OPERATOR FAILED TO PROPERLY LOCATE PIPELINE BEFORE FINAL SERVICE LINE TIE-ININSTALLATION AND MISTAKENLY TAPPED A HIGH PRESSURE DISTRIBUTION MAIN INSTEADOF THE LOW PRESSURE MAIN. OPERATOR FAILED TO FOLLOW COMPANY STANDARDS WHILE ABADONING THE SERVICE UNTIL INSTALLATION CAUSING A FIRE AND PERSONAL INJURY TO ONE (1) EMPLOYEE. PART 3. OPERATOR ERROR- FAILURE TO PROPERLY IDENTIFY FACILITY TO BE TAPPED.
2025-01-31 10:21 | NO | NO | 19940144 | 1994-06-21 | 792 | ATLANTA GAS LIGHT CO | HIGHWAY 29 & PATTERSON ROAD | LAWRENCEVILLE | GWINNETT | GA | 30136 | 3 | NO | 1003 | 1994-05-18 | 0 | 0 | 41976 | 31431.2755 | 75889.7913 | Null | 0 | 30 |  |  | 60 | 60 | BY TEST | 118 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API-5L | MAVERICK STEEL | 0 | 1988 | UNDER GROUND OR UNDER WATER |  | R.J. RIDLEY | 4044182215 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-05-13 | YES | 2 |  | YES |  |  | REYNOLDS CONSTRUCTION, INC. CUT 6" MHP GAS MAIN WITH A TRACK HOE, WHILE INSTALLING FORCED SEWER MAIN FOR GWINNETT COUNTY.
2025-01-31 10:21 | NO | NO | 19940148 | 1994-06-21 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 2915 ATWOOD | PITTSBURGH | ALLEGHENY | PA | 15216 | 3 | NO | 1810 | 1994-05-22 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 0 | 30 |  | 19940522 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 1 | 0.133 |  |  | 0 | 0 | ABOVE GROUND |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | VEHICLE STRUCK METER RISER. TRUCK DRIVER LOST CONTROL OF RENTAL TRUCK AND THE VEHICLE DRIFTED BACK INTO THE GAS AND ELECTRIC METERS. THE GAS METER WAS SHEARED OFF AT THE METER RISER AND ESCAPING GAS WAS APPARENTLY IGNITED FROM THEARCING DAMAGED ELECTRIC METER. THE FIRE DEPARTMENT ESTIMATED $50,000 DAMAGE TO THE DUPLEX APARTMENTS.
2025-01-31 10:21 | NO | NO | 19940149 | 1994-06-16 | 15359 | PEOPLES NATURAL GAS | 231 W 6TH STREET | WAHOO | SAUNDERS | NE | 68066 | 3 | NO | 8 | 1994-05-27 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 1 | 0 |  | 19940527 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GREGORY J. BENAK | 4022212021 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FAULTY TAR HEATER. FIRE IS NOT NATURAL GAS RELATED. PART 2 FAILURE OF TAR HEATER.
2025-01-31 10:21 | YES | NO | 19940150 | 1994-06-16 | 18536 | SOUTHWEST GAS CORP | 910 W. COUNTRY CLUB | BIG BEAR CITY | SAN BERNARDINO | CA | 92314 | 3 | NO | 1410 | 1994-06-03 | 0 | 0 | 90000 | 67391.2425 | 162713.9608 | Null | 0 | 29 |  | 19940603 | 35 | 43 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC SCHED 40 | 0.5 | 0.109 | 2110 | STAUFFER | 1965 | 1965 | WITHIN/UNDER BUILDING |  | ROBERT STEPHENSON | 6199514023 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOTS | NO |  | NO | 0 |  | NO |  |  | PIPE WAS DAMAGED BY TREE ROOT GROWTH WHICH BOWED THE PIPE UP FROM ON ROOT AND DOWN FROM ANOTHER. THIS CAUSED A CRACK IN THE PIPE. ESCAPING GAS MIGRATED TO 910 WEST COUNTRY CLUB WHERE THE EXPLOSION AND FIRE OCCURRED. BIG BEAR CITY FIRE DEPARTMENT EXTINGUISHED THE FIRE AND CALLED SOUTHWEST GAS TO RESPOND. SOUTHWEST GAS DUG UP AND SECURED THE SERVICE AT THE PROPERTY LINE. THERE WERE NO PERSONAL INJURIES REQUIRING IN-PATIENT HOSPITALIZATION. PART 3 - PIPE DAMAGED BY TREE ROOTS.
2025-01-31 10:21 | YES | YES | 19940152 | 1994-05-23 | 4060 | EAST OHIO GAS CO | 14811 LAKESHORE BLVD | CLEVELAND | CUYAHOGA | OH | 44111 | 3 | NO | 1215 | 1994-04-20 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19940420 | 6 | 16 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | NOT GIVEN | STEEL |  | 6 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | ROBERT J. BRADACH | 2167366272 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DURING A ROUTINE LEAKAGE SURVEY ON THURSDAY, MARCH 31, 1994, A LEAK WAS FOUND AT THE NORTH SIDE OF LAKESHORE BLVD., AND THE EAST SIDE OVERLOOK PARK DRIVE, IN CLEVELAND, OHIO. THIS LEAK WAS DETERMINED TO BE A CLASS 11 LEAK, MEANINGTHAT REPAIR OR RECLASSIFICATION NEEDED TO BE COMPLETED WITHIN 180 DAYS. ON WEDNESDAY, APRIL 20, 1994, AN EAST OHIO GAS CONSTRUCTION AND MAINTENANCE CREW ARRIVED AT THE LOCATION OF THE LEAK AT 8:15 A.M. EXCAVATION OF THE SITE WAS COMPLETED AT APPROXIMATELY 11:00 A.M., AND THE CREW BEGAN TO MAKE REPAIRS TO A6 INCH NOMINAL DIAMETER, PLAIN END, LOW PRESSURE STEEL MAIN. THREE SHRINK SLEEVES PATCHES WERE APPLIED TO THE PIPE, AND REPAIRS WERE COMPLETED BY 12:15 P.M. THE CREW THEN PROCEEDED TO TAKE A 1/2 HOUR LUNCH BREAK. AT 12:45 P.M., MR. LUDWIG UDOVIC, EAST OHIO GAS FITTER "A", RE-ENTERED THE DITCH IN ORDER TO REPLACE A 1-1/2 INCH DRIP LINE WHICH IS LOCATED ON A 4 INCH NOMINAL DIAMETER SECTION OF PLAIN END STEEL MAIN ATTACHED TO THE EAST END OF THE 6 INCH DIAMETER SECTION OF THE PIPELINE ON WHICH THE REPAIRS WERE MADE. THIS DRIP WAS VISUALLY EXAMINED BY THE CREW AND DETERMINATION WAS MADE TO REPLACE THIS DRIP WHILE THE PIPING WAS EXPOSED. AFTER REMOVING THE DRIP PIPING, MR. UDOVIC WAS ATTEMPTING TO INSERT A 1 INCH STEEL PLUG INTO THE THREADED OPENING ON THE BOTTOM OF THIS SECTION OF PIPING WHEN A FIRE OCCURRED. HE SUSTAINED FIRST AND SECONDDEGREE BURNS TO HIS NOSE, HANDS, AND ARMS. THE SECOND CREWW MEMBER MR. WILLIAM MAUSER, EAST OHIO GAS TECHNICIAN, ASSISTED MR. UDOVIC OUT OF THE DITCH, ATTENDED IS IS BURNS, AND THEN EXTINGUISHED THE FIRE WITH A DRY CHEMICAL EXTINGUISHER. MR. MAUSER THEN PLUGGED THE OPENING, STOPPING THE FLOW OF GAS. AS A RESULT OF HIS INJURIES, MR. UDOVIC WAS ADMITTED TO EUCLID MERIDIA HOSPITAL FORADDITIONAL TREATMENT AND OBSERVATION. HE WAS RELEASED THE FOLLOWING DAY. UPON COMPLETION OF A THROUGH EXAMINATION OF THE WORK SITE AND AFTER INTERVIEWINGTHE TWO WORKERS, AN EXACT CAUSE OF THE FIRE COULD NOT BE DETERMINED. BASED ON THE EVIDENCE AT THE SCENE, IT IS SUSPECTED THAT THE IGNITION SOURCE OF THE FIRE WAS A SPARK CAUSED BY METAL TO METAL CONTACT IN THE COURSE OF THE DRIP REPLACEMENT. THERE WERE NO RUNNING VEHICLES NEAR THE WORK SITE DURING THE TIMETHE WORK WAS BEING COMPLETED, AND THE TORCH USED TO APPLY THE SHRINK SLEEVESHAD BEEN PLACED BACK ON THE TRUCK PRIOR TO THE LUNCH BREAK. AN ANODE WAS TO BE ATTACHED TO THE PIPE AFTER THIS JOB WAS COMPLETED, BUT NONE OF THE CADWELDEQUIPMENT AND MATERIALS WERE PRESENT NEAR THE DITCH AT THE TIME OF THE INCIDENT. NEITHER OF THE WORKERS ON THIS CREW ARE SMOKERS. AFTER MR. UDOVIC WAS TAKEN TO THE HOSPITAL, A SECOND WORK CREW ARRIVED TO ASSIST MR. MAUSER IN COMPLETING THE JOB. DUE TO DAMAGE SUSTAINED IN THE FIRE, THE SHRINK SLEEVES WERE REPLACE, AND REPLACEMENT OF THE DRIP WAS COMPLETED WITHOUT INCIDENT. IN ORDERTO MINIMIZE THE CHANCES OF A RECURRENCE, ALL PERSONNEL INVOLVED IN THIS TYPEOF WORK WILL BE MADE AWARE OF THE DETAILS OF THIS INCIDENTS.
2025-01-31 10:21 | YES | NO | 19940156 | 1994-05-24 | 13710 | NORTHERN ILLINOIS GAS CO | 212-18 THORNAPPLE CT. | BUFFALO GROVE | LAKE | IL | 60089 | 3 | NO | 1825 | 1994-04-23 | 0 | 0 | 100000 | 74879.1584 | 180793.2897 | Null | 0 | 50 |  | 19940426 | 55 | 60 | BY TEST | 95 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | OTHER | PLASTIC/ALUM COMPOSITE | 0.625 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | NEIL SANTEE | 7089838888 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE CAUSING DAMAGE TO A FOUR UNIT CONDOMINIUM STARTED ON THE OUTSIDE OF THE STRUCTURE NEAR OUR SERVICE RISER. INVESTIGATION OF THE SERVICE MATERIAL AFTER THE INCIDENT REVEALED THE PLASTIC AND ALUMINUM HAD MELTED. SOURCE OF FIREAND IGNITION IS UNKNOWN.
2025-01-31 10:21 | NO | NO | 19940157 | 1994-07-18 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 2116 PHILLIPS LANE | TEXARKANA | BOWIE | TX | 75501 | 2 | NO | 956 | 1994-06-20 | 0 | 0 | 10000 | 7487.9158 | 18079.329 | YES | 1 | 0 |  | 19940620 | 6 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | APPLIANCE INSIDE STRUCTUR | FITTING |  | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING | APPLIANCE | JIM WILLIAMS | 5017796308 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | COPPER TUBING LINE SERVING RANGE TOP WAS DISCONNECTED AND UNCAPPED.
2025-01-31 10:21 | NO | NO | 19940159 | 1994-07-21 | 11720 | LONG ISLAND LIGHTING COMPANY | 317 JACKSON AVENUE | SYOSSET | NASSAU | NY | 11791 | 4 | NO | 1115 | 1994-06-17 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19940617 | 3.5 | 0 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | CUSTOMER OWNED UNIT HEATE | OTHER | CUSTOMER UNIT HEATER | OTHER | CUSTOMER UNIT HEATER | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS E. LUPSKI | 5165454400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE DEPARTMENT OF TRANSPORTATION BASED UPON PRELIMINARY INFORMATION RECEIVEDFROM THE FIELD AT THE TIME OF THE INCIDENT. THIS INFORMATION INDICATED THAT TWO (2) LILCO EMPLOYEES (WHO WERE IN THE PROCESS OF REPAIRING A CUSTOMER OWNED UNIT HEATER) HAD RECEIVED "FLASH BURNS" CAUSED BY A DELAYED IGNITION AND WERE BEING TRANSPORTED TO THE HOSPITAL. HOWEVER, SUBSEQUENT INFORMATION REVEALED THAT THE TWO (2) LILCO EMPLOYEES WERE TREATED AND RELEASED FROM THE HOSPITAL AND DID NOT REQUIRE INPATIENT HOSPITALIZATION.
2025-01-31 10:21 | YES | YES | 19940160 | 1994-07-12 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 210-20 POPLAR | MAPLE RAPIDS | ESSEX | MI | 48853 | 3 | NO | 1515 | 1993-06-16 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 45 |  | 19940621 | 60 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | SWEAT COUPLING | OTHER | COPPER | 12 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | THADDEUS S. SLIWINSKI | 3135777024 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19940161 | 1994-06-20 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | M-22 & SHORE DRIVE | SUTTONS BAY | LEELANAU | MI |  | 2 | NO | 1750 | 1994-05-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 20 |  | 19940502 | 150 | 60 | BY TEST | 225 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | VAULT | OTHER | NOT GIVEN | STEEL |  | 0 | 0 | 298 TK | FISHER | 0 | 1967 | UNDER GROUND OR UNDER WATER |  | GEORGE A. VALRANCE | 3135777029 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIELD EMPLOYEES WERE PERFORMING MAINTENANCE ON A REGULATOR IN A VAULT SUPPLYING GAS TO APPROXIMATELY 800 CUSTOMERS. TWO EMPLOYEES WERE IN THE VAULT WHEN A SUDDEN RELEASE OF GAS FILLED THE VAULT. THE TWO EMPLOYEES VACATED THE VAULTWITH THE ASSISTANCE FROM THE TOP MAN. THE TOP MAN THEN PUT ON RESPIRATORY EQUIPMENT AND ENTERED THE VAULT. SHORTLY AFTER, THE EMPLOYEE FELL TO THE FLOOR.THE OTHER TWO EMPLOYEES RESCUED THE DOWNED EMPLOYEE USING A WINCH AND SAFETYHARNESS ATTACHED TO HIM. HE WAS HOPITALIZED OVERNIGHT FOR OBSERVATION.
2025-01-31 10:21 | YES | YES | 19940162 | 1994-07-21 | 12876 | MOUNTAIN FUEL SUPPLY CO | 3249 SOUTH WEST TEMPLE STREET | SALT LAKE CITY | SALT LAKE | UT | 84115 | 3 | NO | 1436 | 1994-06-24 | 1 | 0 | 80000 | 59903.3267 | 144634.6318 | YES | 1 | 5 |  | 19940624 | 60 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION FITTING | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | EDWARD B. KELSEY | 8015345650 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-06-20 | YES | 3 | MARKINGS AND MAPS PROVIDE | YES |  |  | ON JUNE 24, 1994, A PRIVATE CONTRACTOR INSTALLING A WATER LINE IN THE MIDDLEOF WEST TEMPLE STREET, SALT LAKE CITY, UTAH, HIT A 3/4" STEEL SERVICE LINE DURING EXCAVATION. THIS CAUSED THE SERVICE LINE TO BE PULLED OUT OF A COMPRESSION COUPLING WHERE THE SERVICE LINE CONNECTED TO THE RISER. WHEN THE SERVICE LINE WAS UNCOVERED, AFTER THE INCIDENT, THERE WAS A SPACE OF 12" BETWEEN THE COMPRESSION COUPLING AND THE STEEL SERVICE LINE. AS A RESULT, AN EXPLOSION AND FIRE OCCURRED, WHICH CAUSED THE DEATH OF 75-YEAR-OLD WOMAN IN THE RESIDENCEAFFECTED. ALSO, ANOTHER WOMAN DRIVING IN FRONT OF THE RESIDENCE REQUIRED FIRST-AID TREATMENT AT A LOCAL HOSPITAL AND WAS RELEASED. THE SERVICE LINE WAS ORIGINALLY INSTALLED FEBRUARY 5, 1953. A NEW SERVICE LINE RISER AND COMPRESSOR
2025-01-31 10:21 | YES | YES | 19940163 | 1994-06-23 | 12684 | MONTANA - DAKOTA UTILITIES CO | 1900 BLK. MEMORIAL HWY | MANDAN | MORTON | ND | 58554 | 3 | NO | 2240 | 1994-05-23 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 40 |  | 19940523 | 50 | 55 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR STATION | JOINT | SCREW | STEEL |  | 1 | 0.133 | SCHED 40 |  | 0 | 1977 | ABOVE GROUND |  | RONALD E. BLUM | 7012227924 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 | WARNING SIGN ABOVE GROUND | NO |  |  | AN AUTOMOBILE WENT OUT OF CONTROL, LEFT THE HIGHWAY STRIKING A REGULATOR STATION BARRIER.
2025-01-31 10:21 | YES | YES | 19940164 | 1994-07-18 | 15007 | PACIFIC GAS & ELECTRIC CO | 11058 COLFAX HIGHWAY | GRASS VALLEY | NEVADA | CA | 95945 | 2 | NO | 619 | 1994-06-15 | 0 | 2 | 48000 | 35941.996 | 86780.7791 | Null | 3 | 41 |  | 19940615 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ALDYL A | DUPONT | 0 | 1970 | UNDER PAVEMENT |  | JAMES H. POPE | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | NOT GIVEN | NO |  | NO | 0 |  | NO |  |  | AT 6:19 A.M. ON WEDNESDAY, JUNE 15, 1994, PG&E WAS NOTIFIED BY THE CALIFORNIA DIVISION OF FORESTRY (CDF) OF A HOUSE EXPLOSION AND FIRE AT "10635 SILVER WAY" (NOTE: THE ACTUAL ADDRESS TURNED OUT TO BE 11058 COLFAX HIGHWAY)., GRASS VALLEY, NEVADA COUNTY. A GAS SERVICE MAN WAS DISPATCHED AT 6:25 A.M. AND ARRIVED AT 6:45 A.M. FOLLOWED BY A GAS CREW'S ARRIVAL AT 7:45 A.M. CDF CLOSED THERISER SERVICE VALVE TO THE STRUCTURE AT 6:41 A.M. AND THE GAS CREW SQUEEZED THE SERVICE OFF UPSTREAM OF THE RISER AT 10:00 A.M. SUBSWQUENT INVESTIGATION REVEALED THAT PACIFIC BELL (IN 1976) AND NEVADA IRRIGATION DISTRICT (IN 1990)HAD TRENCHED ACROSS PG & E'S GAS SERVICE TO INSTALL THEIR FACILITIES.
2025-01-31 10:21 | YES | YES | 19940165 | 1994-07-14 | 15896 | PROVIDENCE GAS CO | 41 BEACH STREET | WESTERLY | WASHINGTON | RI | 02891 | 3 | NO | 720 | 1994-06-23 | 0 | 1 | 100000 | 74879.1584 | 180793.2897 | Null | 1 | 40 |  | 19940623 | 7 | 12 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT R. RINGMAN | 4012725040 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CORROSION HOLE WAS DISCOVERED ON THE UNDERSIDE OF THE SERVICE LINE, INSIDETHE BASEMENT, APPROXIMATELY ONE-HALF INCH FROM THE WALL. POSSIBLE SOURCE OF IGNITION MAY HAVE BEEN THE OIL BURNER IN THE CELLAR. THERE WAS NO RECORD OF THIS SERVICE LINE OR ANY CUSTOMER ACCOUNTS RELATING TO THIS LOCATION.
2025-01-31 10:21 | YES | NO | 19940169 | 1994-07-14 | 20010 | U G I CORP | 2349 READING ROAD | ALLENTOWN | LEHIGH | PA | 18103 | 3 | NO | 1713 | 1994-03-22 | 0 | 0 | 100000 | 74879.1584 | 180793.2897 | Null | 1 | 33 |  | 19940707 | 0.25 | 1 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1927 | UNDER PAVEMENT |  | JAMES R. HEINTZ | 6107963528 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | TED IN THE 00 BLOCK OF S. 24TH ST. IN ALLENTOWN LEHIGH COUNTY, PA MIGRATED INTO THE CORNER PROPERTY AT 2349 READING ROAD. THE GAS WAS SUBSQUENTLY IGNITEDBY AN UNKNOWN SOURCE CAUSING A LOW LEVEL EXPLOSION AND BRIEF FLASH FIRE. THERE WERE NO FATALITIES OR INJURIES AND NO OTHER STRUCTURES SUSTAINED DAMAGE.
2025-01-31 10:21 | YES | YES | 19940170 | 1994-07-12 | 20010 | U G I CORP | 1339 ALLEN STREET | ALLENTOWN | LEHIGH | PA | 18103 | 4 | NO | 1900 | 1994-06-09 | 1 | 17 | 2000000 | 1497583.1675 | 3615865.7947 | Null | 0 | 20 |  | 19940609 | 55 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMP. | STEEL |  | 2 | 0.154 |  |  | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | JAMES R. HEINTZ | 6107963528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-05-19 | YES | 3 | PAINT | YES
2025-01-31 10:21 | NO | NO | 19940171 | 1994-07-18 | 22182 | WASHINGTON GAS LIGHT CO | S. OF HANGER #8 THOMAS AVENUE | WASHINGTON |  | DC | 20001 | 3 | YES | 1049 | 1994-06-24 | 0 | 0 | 1560 | 1168.1149 | 2820.3753 | YES | 1 | 24 |  | 19940624 | 20 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | ASTM D2513 | UPONOR | 1994 | 1994 | UNDER GROUND OR UNDER WATER |  | JOHN C. SHEA | 7037505631 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-06-16 | YES | 3 | FLAGS & PAINT MARKS | YES |  |  | WHILE GRADING A PARKING LOT DRIVEWAY, D&J EXCAVATING, WHO WAS WORKING FOR GOLDIN STAFFORD, ACCIDENTALLY HIT AND TORE OFF A 3" X 4" PIECE OF THE TOP OF THE 4" PLASTIC MAIN AND PUNCTURED THE SIDE WITH A SLIT 2" X1". THIS RELEASED GAS TO THE ATMOSPHERE. AS A PRECAUTIONARY MEASURE, THE FIRE DEPARTMENT HAD METRO CLOSE DOWN THE ORANGE AND BLUE LINES TO NATIONAL AIRPORT. THEY ALSO HAD THEROADWAYS CLOSED WHICH CAUSED A MAJOR TRAFFIC JAM IN THE AREA FOR APPROXIMATELY 1.5 HOURS. THE 4" PLASTIC MAIN WAS CAPPED OFF. THERE WAS NO INTERRUPTION OF SERVICE, NO INJURIES OR DAMAGE TO PUBLIC PROPERTY.
2025-01-31 10:21 | YES | YES | 19940172 | 1994-06-28 | 13299 | NEW JERSEY NATURAL GAS CO | 634 CLIFFWOOD AVENUE | CLIFFWOOD | MONMOUTH | NJ |  | 4 | NO | 1135 | 1993-06-09 | 3 | 3 | 160000 | 122417.1993 | 295572.3417 | Null | 0 | 7 |  | 19930609 | 52 | 60 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | INACTIVE SERVICE LINE | JOINT |  | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | MONIQUE HERZOG | 9089381193 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1993-06-09 | NO | 0 |  | YES
2025-01-31 10:21 | YES | YES | 19940173 | 1993-05-04 | 18520 | SOUTHERN PUBLIC SERVICE CO | WV RT. 44 | SWITZER | LOGAN | WV |  | 3 | NO | 1600 | 1993-03-03 | 0 | 2 | 30000 | 22953.2249 | 55419.8141 | Null | 1 | 0 |  | 19930304 | 15 | 45 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | CLAMP | STEEL |  | 4 | 0 | SCD.40 |  | 0 | 1957 | WITHIN/UNDER BUILDING |  | DALLAS M. NCNAH | 3047433501 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19940174 | 1994-07-31 | 22182 | WASHINGTON GAS LIGHT CO | 2130 CHILLUM ROAD | CHILLUM |  | MD |  | 3 | NO | 1930 | 1994-07-06 | 0 | 0 | 64000 | 47922.6614 | 115707.7054 | YES | 3 | 23 |  | 19940706 | 117 | 135 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER | gas plant | REGULATOR/METER |  | OTHER PLASTIC | NOT GIVEN | 8 | 0 |  |  | 1974 | 1974 | ABOVE GROUND |  | JAMES O. BIELASKI | 7037505566 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | DAMAGED BELLOWS ASSEMBLY
2025-01-31 10:21 | YES | NO | 19940175 | 1994-08-02 | 21190 | VERMONT GAS SYSTEMS INC | MAPLE STREET (95) | BURLINGTON | CHITTENDEN | VT | 05401 | 3 | NO | 1346 | 1994-07-05 | 0 | 0 | 90000 | 67391.2425 | 162713.9608 | Null | 0 | 7 |  | 19940706 | 0 | 0 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID A. ATTIG | 8028634511 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19940177 | 1994-08-12 | 4499 | ENTEX - DIVISION OF ARKLA INC | 10000 FAIRBANKS NORTH HOUSTON | HOUSTON | HARRIS | TX | 77064 | 3 | NO | 1741 | 1994-04-25 | 0 | 0 | 60000 | 44927.495 | 108475.9738 | Null | 1 | 49 |  |  | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE2406 | DUPONT | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LANNY W. CARGILE | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-04-19 | NO | 0 |  | NO
2025-01-31 10:21 | YES | YES | 19940178 | 1994-08-15 | 1209 | BAY STATE GAS CO | 1085 BROADWAY | HANOVER | PLYMOUTH | MA |  | 2 | NO | 1540 | 1994-08-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19940805 | 50 | 99 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NOT GIVEN | STEEL |  | 3 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | WILLIAM ST. CYR | 5085800100 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19940179 | 1994-08-09 | 18484 | SOUTHERN CALIFORNIA GAS CO | BETTINA COURT & LANTANA | CAMARILLO | VENTURA | CA | 93010 | 3 | NO | 1511 | 1994-07-13 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 45 |  | 19940713 | 45 | 59 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | 40-00 | UPINOR | 1994 | 1994 | OTHER | EXPOSED PIPE IN EXCAVATIO | D.J. RENDLER | 2132443280 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19940181 | 1994-09-14 | 18112 | SAN DIEGO GAS & ELECTRIC CO | MIRAMAR ROAD & CARROLL ROAD | SAN DIEGO | SAN DIEGO | CA |  | 3 | NO | 1030 | 1994-08-12 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19940812 | 0 | 60 | BY TEST | 105 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 3 | 0.304 | ASTM D2513 | PLEXCO | 1994 | 1994 | OTHER | IN OPEN TRENCH | JAMES J. BOLAND | 6196962183 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON FRIDAY, AUGUST 12, 1994 AT APPROXIMATELY 10:30 A.M. DURING PURGING OPERATIONS NATURAL GAS FROM A POLYETHYLENE (PE) PIPE IGNITIED ON A CONSTRUCTION SITE ON MIRAMAR ROAD. THE RELIEF FOREMAN, BILL DIMMOCK, WAS BURNED ON HIS ARMS, FACE AND NECK AND TAKEN TO THE EMERGENCY ROOM AT SHARPS HOSPITAL. HE WAS ADMITTED TO THE HOSPITAL FOR TREATMENT AND RELEASED ON TUESDAY, AUGUST 16, 1994. THE INCIDENT CAUSE WAS INVESTIGATED BY A COMPANY ACCIDENT INVESTIGATION TEAM.THE FINDINGS BY THIS TEAM INDICATE THE FOLLOWING AS FACTORS CONTRIBUTING TO THE INCIDENTS: THE GAS IGNITION WAS CAUSED BY STATIC ELECTRICITY DURING THE PIPELINE PURGING OPERATION. PERSONNEL PERFORMING THE PURGING OPERATION DID NOTFOLLOW COMPANY STANDARD PRACTICES WHICH INCLUDED GROUNDING THE PIPE AND VENTING THE GAS FROM THE TRENCH DURING THE PUGING PROCEDURE. THE INJURED EMPLOYEEHAD ENTERED THE TRENCH WITH GAS BLOWING WITHOUT CHECKING THE ATMOSPHERE FOR COMBUSTIBLE GAS WHICH IS NOT IN ACCORDANCE WITH COMPANY SAFETY PRACTICES. DISCIPLINARY ACTION IS BEING REVIEWED.
2025-01-31 10:21 | NO | NO | 19940187 | 1994-09-01 | 18440 | SOUTH JERSEY GAS CO | 215 CATES ROAD | MCKEEE CITY | ATLANTIC | NJ | 08232 | 4 | NO | 1010 | 1994-08-24 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 20 |  | 19940824 | 0 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | LNG TANKER TRAILER | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | CHARLES BISCIEGLIA | 6095674000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | LNG TANK TRUCK OPERATOR FAILED TO PROPERLY SECURE CONNECTOR HOSE TO THE TANKER EXIT PORT WHILE OFFLOADING LNG. LNG SPILLED AND VAPORIZED FROM/AT THE LOOSECONNECTION.
2025-01-31 10:21 | NO | NO | 19940188 | 1994-08-31 | 15931 | PUBLIC SERVICE CO OF COLORADO | 2981 KRAMERIA STREET | DENVER | DENVER | CO | 80207 | 3 | NO | 2310 | 1994-08-01 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  |  | 6 | 6 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 | AL 175 | AMERICAN | 1965 | 1965 | WITHIN/UNDER BUILDING |  | DOUGLAS MATZICK | 3036282620 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURAL FIRE IN THE GARAGE MELTED GAS METER IN GARAGE. ORIGINAL CAUSE OF FIRE UNKNOWN. INSIDE STRUCTURE FIRE MELTED THE GAS METER.
2025-01-31 10:21 | NO | NO | 19940190 | 1994-08-29 | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | MEDAUGH ROAD (PLEASANT VALLEY GATE SUB) | PLEASANT VALLEY | DUTCHESS | NY | 12569 | 0 | NO | 1020 | 1994-07-28 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19940810 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID W. MERTE | 9144865521 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JULY 28, 1994, A GAS MECHANIC, ALONG WITH TWO PROFESSIONAL ENGINEERS, TWOCONTRACT WELDERS, A GAS FORMAN AND A SECOND GAS MECHANIC, WAS WORKING ON A3000 GALLON ABOVE GROUND BULK ODORANT TANK CONTAINING TERTIARY BUTYLMERCAPTAN. THIS WORK WAS PERFORMED AT OUR PLEASANT VALLEY GATE STATION OFFMEDAUGH ROAD IN PLEASANT VALLEY. DUE TO A SEALANT LEAK NEAR THE TOP OF THETANK, NITROGEN WAS BEING ADDED TO THE TANK AS PART OF A PURGING OPERATION TOCREATE A BLANKET OF INERT GAS ON THE TOP OF THE TANK IN ORDER TO PERMANENTLYWELD THE LEAKING SEAL. AFTER OBSERVING PRESSURE GAUGE READINGS AND OPERATINGTHE JAMESBURY VALVE CONTROLING THE NITROGEN INPUT FOR APPROXIMATELY 20MINUTES, THE GAS MECHANIC BECAME ILL. THIS GAS MECHANIC RECEIVED AMBULATORYCARE AND WAS TRANSPORTED TO THE HOSPITAL. THIS WAS CONSIDERED AN EMPLOYEEILLNESS THAT DID NOT REQUIRE NOTIFICATION. ON AUGUST 10, 1994, CENTRAL HUDSONWAS INFORMED BY THE FAMILY THAT THE STILL HOSPITALIZED GAS MECHANIC HAD BEENOPERATED ON THE REMOVE A BLOOD CLOT IN HIS BRAIN. DUE TO THE FACT THAT MEDICALDETERMINATIONS WITH REFERENCE TO CAUSATIVE FACTORS WERE PENDING AND THIS WASSIGNIFICANT IN OUR JUDGEMENT, TELEPHONIC NOTIFICATION WAS MADE TO THENATIONAL RESPONSE CENTER AT THAT TIME. ON AUGUST 11, 1994, AT APPROXIMATELY2:20PM, SUBSEQUENT TO THE OPERATION TO REMOVE THE BLOOD CLOT, THE GASMECHANIC'S DEATH WAS MADE TO THE NATIONAL RESPONSE CENTER AT 3:48PM.PRELIMINARY MEDICAL REPORTS RECEIVED FROM TH E UTILITIES MUTUAL INSURANCECOMPANY SUBSEQUENT TO THE GAS MECHANIC'S DEATH, HAVE INDICATED THAT GASMECHANIC DIED OF NATURAL CAUSES DUE TO A BLOOD CLOT IN THE BRAIN THAT WAS NOTRELATED TO THE WORK PERFORMED BY THE GAS MECHANIC. CENTRAL HUDSON ISCONDUCTING AN INVESTIGATION OF THE WORK PROCEDURES LEADING UP TO THISINCIDENT. THE OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION (OSHA) WASNOTIFIED AND IS CURRENTLY CONDUCTING AN INDEPENDENT INVESTIGATION OF THISINCIDENT. CENTRAL HUDSON IS FULLY COOPERATING IN THIS INVESTIGATION.SUPPLEMENTAL REPORT 12/15/94: THE RECENTLY RELEASED CORONER'S REPORT CITEDNATURAL CAUSES AS THE CAUSE OF THE GAS MECHANIC'S DEATH WHICH OCCURRED ONAUGUST 11, 1994. MEDICAL REPORTS RECEIVED FROM THE UTILITIES MUTUAL INSURANCECOMPANY HAVE CONCURRED WITH THIS OPINION. CENTRAL HUDSON HAS COMPLETED ITSINVESTIGATION OF THE WORK PROCEDURES LEADING UP TO THIS INCIDENT. THECOMPANY'S INVESTIGATION CONCLUDED THAT WORK PROCEDURES DID NOT CONTRIBUTE TOTHIS INCIDENT. THE OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION (OSHA) HASCONDUCTED AN INDEPENDENT INVESTIGATION OF THIS INCIDENT. CENTRAL HUDSON HASFULLY COOPERATED IN THIS INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19940191 | 1994-08-29 | 12606 | MISSOURI PUBLIC SERVICE CO | HIGHWAY 13 MISSOURI RIVER BRIDGE | LEXINGTON | LAFAYETTE | MO | 64067 | 2 | NO | 1845 | 1994-07-13 | 0 | 0 | 200000 | 149758.3167 | 361586.5795 | Null | 0 | 40 |  | 19940714 | 190 | 200 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.5 | GRADE B |  | 1946 | 1947 | ABOVE GROUND |  | ALAN STEELE | 8167377617 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 1 |  | YES |  |  | ON JULY 13, 1994 AT APPROXIMATELY 6:45 PM, A BARGE OPERATED BY CANTON TOWINGSTRUCK A NATURAL GAS PIPELINE OWNED BY MISSOURI PUBLIC SERVICE COMPANY. THE BARGE WAS TRAVELING EAST BOUND ON THE MISSOURI RIVER TOWARDS THE HIGHWAY 13 BRIDGE AT LEXINGTON, MO. THE BARGE OPERATOR DID NOT HAVE ENOUGH CLEARANCE TO PASS UNDER THE BRIDGE AS AN ANCHOR SPUD WAS EXTENDED TOO HIGH ABOVE THE DECK OF THE BARGE. THE SPUD INITIALLY IMPACTED THE 6" STEEL GAS PIPELINE WHICH WAS ATTACHED ALONG THE LOWER WEST SIDE OF THE STEEL TRUSS BRIDGE. THE IMPACT COMPLETELY SEVERED THE PIPELINE AND PULLED A 300 FOOT SECTION OF PIPE OFF OF ITS HANGERS. THERE WERE NO APPARENT EXTENUATING CIRCUMSTANCES WHICH WOULD HAVE CONTRIBUTED TO THE INCIDENT.
2025-01-31 10:21 | YES | YES | 19940195 | 1994-08-22 | 2596 | COLUMBIA GAS OF OHIO INC | 4746 MACKENSEY CIRCLE | MEDINA | MEDINA | OH | 44256 | 3 | NO | 1325 | 1994-07-19 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 25 |  | 19940719 | 27 | 32 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | UPONOR ALDYL A | 1992 | 1993 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OPERATOR ACTION |  | YES | 1994-07-19 | YES | 2 | LOCATED ON SITE | YES |  |  | OUPS LOCATED REQUEST TO OTHER UTILITIES PLACED ON 07/12/1994 AT 1502 HOURS BY MAINTENANCE UNLIMITED. A COLUMBIA GAS OF OHIO CONTRACTOR, MAINTENANCE UNLIMITED, INC., WAS INSTALLING A NEW SERVICE TAP ON A 2-INCH DIAMETER PLASTIC MEDIUM PRESSURE (32 PSIG) MAIN ON MACKENSEY CIRCLE IN MEDINA, OHIO WHEN THEY STRUCK THE MAIN WITH THE BACKHOE BUCKET. GAS WAS BLOWING IN THE HOLE WHEN A CONTRACT EMPLOYEE ENTERED IT WITH A SHOVEL TO ASSESS THE DAMAGE. THE GAS IGNITED FROM AN UNKNOWN SOURCE CAUSING INJURIES TO THREE (3) CONTRACT EMPLOYEES. A COMPANY INSPECTOR ON SITE UTILIZED AN EXTINGUISHER AND ALMOST IMMEDIATELY PUT ON THE FIRE. THE 3 CONTRACT EMPLOYEES SUFFERED 1ST AND 2ND DEGREE BURNS AND WERE EVENTUALLY RELEASED FROM THE HOSPITAL.
2025-01-31 10:21 | YES | YES | 19940196 | 1994-08-29 | 19205 | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | 412 ASHLAWN | HOUMA | TERREBONNE | LA | 70363 | 3 | NO | 1600 | 1994-08-10 | 0 | 1 | 65000 | 48671.4529 | 117515.6383 | Null | 0 | 15 |  | 19940810 | 28 | 35 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR | REGULATOR/METER |  | OTHER | REGULATOR | 0 | 0 | 043 | ROCKWELL | 1972 | 1972 | WITHIN/UNDER BUILDING |  | WAYNE ROBICHAUX | 5048736761 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | X-RAY OF REGULATOR SHOWS LINKAGE DISCONNECTED FROM DIAPHRAGM CONTROL ARM. X-RAY INDICATES REGULTOR ARM TO BE DISCONNECTED FROM DIAPHRAGM CONTROL LINKAGE.CAUSE IS UNKNOWN AT THIS TIME, AND WE ARE CURRENTLY INVESTIGATING THE CAUSE OF THE REGULATOR FAILURE. AFTER COMPLETION OF INVESTIGATION OR DISCOVERY OF OTHER FINDINGS, SUPPLEMENTAL REPORT BE SUBMITTED. NOTES: 1. GAS CLOSED OFF TO RESIDENCE AT 4:05 P.M. 2. COMPLETED F.I. SURVEY AT 5:30 P.M. SUPPLEMENTAL:=ON SEPTEMBER 7, 1994, THE SERVICE REGULATOR WAS DISMANTLED IN THE PRESENCE OFTWO MANUFACTURER'S REPRESENTATIVES. A CIGARETTE FILTER AND A HYPERDERMICNEEDLE WERE FOUND INSIDE THE REGULATOR CASING, ON THE ATMOSPHERIC SIDE OF THEDIAPHRAGM. NUMEROUS SCRATCHES WERE APPARENT ON THE METAL GROMMET AT THECENTER OF THE DIAPHRAGM. ADDITIONALLY, THE DIAPHRAGM ROD WAS FOUND TO BEDISCONNECTED FROM THE SEAT CONTROL ARM.
2025-01-31 10:21 | YES | NO | 19940197 | 1994-10-17 | 18496 | SOUTHERN CONNECTICUT GAS CO | 84 FIRST STREET | HAMDEN | NEW HAVEN | CT | 06514 | 3 | NO | 1530 | 1993-03-25 | 0 | 0 | 250000 | 191276.8739 | 461831.7838 | Null | 2 | 0 |  | 19930325 | 0.25 | 0.65 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 |  |  | 0 | 1915 | UNDER PAVEMENT |  | JOHN L. MATHIEU | 2033828204 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | A CIRCUMFERENCIAL CRACK WAS FOUND ON THE EAST SIDE OF A 4" BY 1 1/4" TAPPINGSLEEVE INSTALLED ON NOVEMBER 21, 1931, WHEN THE 1 1/4" SERVICE TO 84 FIRST STREET, HAMDEN, CT, WAS INSTALLED.
2025-01-31 10:21 | YES | NO | 19940198 | 1994-10-17 | 18496 | SOUTHERN CONNECTICUT GAS CO | 112 MERWIN AVENUE | MILFORD | NEW HAVEN | CT | 06460 | 3 | NO | 423 | 1993-06-10 | 0 | 0 | 100000 | 76510.7496 | 184732.7135 | Null | 0 | 27 |  | 19930610 | 0.25 | 0.65 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | STEEL |  | 1.5 | 0 |  |  | 0 | 1927 | ABOVE GROUND |  | JOHN L. MATHIEU | 2033822874 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | EXPOSED PIPING | YES |  |  | AS PART OF A DWELLING REHABILITATION, A THIRD PARTY REMOVED A SECTION OF A LIVE SERVICE AND LEFT IT UNCAPPED. ESCAPING GAS WAS APPARENTLY IGNITED BY A GAS HOT WATER HEATER AND AN EXPLOSION RESULTED.
2025-01-31 10:21 | YES | YES | 19940204 | 1994-11-04 | 13650 | NORTH PENN GAS CO | WEST ST. TO RT 6# | COUDERSPORT | POTTER | PA |  | 0 | NO | 1410 | 1994-10-18 | 0 | 4 | 0 | 0 | 0 | Null | 0 | 6 |  | 19941018 | 25 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | PINCHING TOOL FAILURE | POLYETHYLENE PLASTIC |  | 4 | 0.395 | 4" ITS | PLEXCO | 1994 | 1994 | ABOVE GROUND |  | BOYD MCCARTNEY | 8153553051 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | OTHER | PINCHING TOOL FAILURE | SQUEEZE TOOL FAILURE CAUSING RELEASE OF NATURAL GAS, DURING TIE IN OPERATION,IGNITION OF PRODUCT CAUSING FLASH FIRE, INJURING EMPLOYEES AT WORK SITE.SUBSEQUENT INVESTIGATION RECLASSIFIED APPARENT CAUSE - PART 2 - AS "C"CONSTRUCTION/OPERATING ERROR. ALSO RECLASSIFICATION OF ENVIRONMENT FROMUNDERGROUND TO ABOVE GROUND - PINCHING TOOL FAILURE.
2025-01-31 10:21 | YES | NO | 19940206 | 1994-10-18 | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 3742 RT 11 | POLKVILLE | CORTLAND | NY | 13045 | 3 | NO | 1315 | 1994-09-28 | 0 | 0 | 100000 | 74879.1584 | 180793.2897 | Null | 0 | 15 |  | 19940928 | 90 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1 | 0.133 | API 5LB | UNAVAILABLE | 1969 | 1969 | UNDER PAVEMENT |  | ANDREW G. SOLOMON | 6077624711 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | PAINT | YES |  |  | APPARENT CONTRACTOR NEGILIGENCE.
2025-01-31 10:21 | YES | NO | 19940208 | 1994-10-19 | 15931 | PUBLIC SERVICE CO OF COLORADO | 11117 ALCOTT STREET | WESTMINSTER | ADAMS | CO | 80030 | 3 | NO | 1722 | 1994-09-26 | 0 | 0 | 125000 | 93598.948 | 225991.6122 | Null | 3 | 7 |  | 19940926 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0.75 | 0 | D2513-81/82 | PLEXCO | 0 | 1984 | UNDER GROUND OR UNDER WATER |  | JOHN C. SCHMIDT | 3035713761 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A. 75" PED SVC TEE CAP CRACKED COMPLETELY ALONG THE TOP EDGE OF CAP, ALLOWINGGAS TO ESCAPE AND ENTER THE WATER SERVICE DITCH. THIS WAS A 0.75" PEDSERVICE ON A 1.25" PED MAIN.
2025-01-31 10:21 | NO | NO | 19940211 | 1994-11-16 | 887 | ONALASKA, CITY OF | 2.5 MILES N FM 356 | ONALASKA | POLK | TX | 77360 | 2 | NO | 215 | 1994-10-17 | 0 | 0 | 21894 | 16394.0429 | 39582.8829 | Null | 0 | 0 |  | 19941017 | 42 | 58 | BY TEST | 42 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0.216 | 1BPE300 |  | 1991 | 1992 | ABOVE GROUND |  | WM STUTTS | 4096465376 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | NO |  |  | TOTAL WASHOUT OF APPROXIMATELY 220' ABOVEGROUND STEEL PIPE ACROSS BRUSHY CREEK IN POLK COUNTY, TEXAS.AREA RECEIVED APPROX. 15 INCHES OF RAIN CAUSING CREEK FLOODING, WASHING OUT.
2025-01-31 10:21 | NO | NO | 19940212 | 1994-11-16 | 8250 | IOWA - ILLINOIS GAS & ELECTRIC CO | 1267 ELMHURST DR. NE | CEDAR RAPIDS | LINN | IA | 52402 | 3 | NO | 45 | 1994-10-12 | 0 | 0 | 60000 | 44927.495 | 108475.9738 | Null | 1 | 5 |  | 19941012 | 30 | 30 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | THREAD | STEEL |  | 0.75 | 0.113 | API 5L GRA25 |  | 0 | 1971 | ABOVE GROUND |  | C.E. NAYLOR | 3097933687 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 12:45 AM, OCTOBER 12, 1994, THE RRESIDENT OF 1267 ELMHURST DRIVE NE HIT THE GAS METER INSTALLATION AT HIS HOME WHEN THE BRAKES ON HIS CAR FAILED. THE IMPACT BROKE THE SERVICE RISER ON THE UPSTREAM SIDE OF THE SERVICE TERMINATION VALVE RELEASING 30 PSIG GAS TO THE ATMOSPHERE. THE SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | YES | YES | 19940213 | 1994-11-14 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | R.D.3 TOWNHSIP RD 363 (MOSER ROAD) | MEYERSDALE | SOMERSET | PA | 15552 | 1 | NO | 1820 | 1994-10-15 | 1 | 1 | 3000 | 2246.3748 | 5423.7987 | Null | 2 | 18 |  | 19941015 | 90 | 100 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NOT GIVEN | OTHER | ALUMINUM SVC REGULATOR | 1.25 | 0 | RW143 | ROCKWELL | 0 | 1992 | ABOVE GROUND |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ON OCTOBER 15, 1994 AT 6:20 P.M., MR. ERNEST MILLER, AGE 84 BACKED HIS VEHICLE INTO A RESIDENTIAL METER/REGULATOR SET WHICH RESULTED IN THE RELEASE AND IGNITION OF NATURAL GAS. THE VEHICLE CAUGHT FIRE. MR. MILLER WAS ABLE TO EXIT THE VEHICLE; HOWEVER, HE RECEIVED SEVERE BURNS OVER 70% OF HIS BODY IN DOING SO. MR. MILLER WAS LIFE-FLIGHTED FROM THE SCENE TO THE BURN UNIT OF WEST PENNHOSPITAL, PITTSBURGH, PENNSYLVANIA. HE DIED ON OCTOBER 19, 1994. MR. MILLER'S DAUGHTER, JANET YUTSEY, AGE 50, ASSISTED HER FATHER IN PUTTING OUT THE FLAMES ON HIS BODY. SHE RECEIVED BURNS TO THE HANDS AND FOREARMS AND WAS HOSPITALIZED FOR ONE DAY AT THE MEYERSDALE HOSPITAL. TO EXTINGUISH THE RESULTING FIRE IT WAS NECESSARY TO SHUT DOWN A TWO-MILE SECTION OF DISTRIBUTION MAIN BY USING EXISTING ISOLATING VALVES IN THE SYSTEM. APPROXIMATELY TEN (10) CUSTOMERSWERE OUT OF SERVICE FOR FIVE (5) HOURS UNTIL THE MAIN COULD BE PLACED BACK IN
2025-01-31 10:21 | NO | NO | 19940214 | 1994-11-14 | 2596 | COLUMBIA GAS OF OHIO INC | 2950 MALLARDD MEADOWS | COLUMBUS | FRANKLIN | OH | 43017 | 3 | NO | 900 | 1994-10-14 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 0 | 37 |  | 19941018 | 45 | 45 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 1 | 0.09 | ASTM D2513 | APPALACHIAN GAS TUBING | 1983 | 1985 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 10/14/1994 A FIRE OCCURRED IN THE ATTACHED GARAGE OF AN APARTMENT AT 2950MALLARD MEADOWS, COLUMBUS, OHIO. DAMAGES TO THE GARAGE THE APARTMENT AND THREE MOTOR CYCLES ARE ESTIMATED AT APPROXIMATELY $50,000. A VERY SMALL LEAK WASFOUND ON THE CUSTOMER OWNED PORTION OF THE SERVICE LINE. A LEAK SURVEY OF THE AREA WAS PERFORMED AND NO OTHER INDICATION OF GAS WAS PRESENT. COH PERSONNEL AT THE SCENE FELT LEAK WAS INSUFFICIENT TO BE THE CAUSE AND INITIAL INDICATIONS FROM THE FIRE DEPARTMENT DID NOT INDICATE GAS AS THE CAUSE. FOUR DAYS LATER COH LEARNED FROM THE FIRE DEPARTMENT THAT THERE WERE REPORTS OF A GAS ODOR AND AN EXPLOSION PRIOR TO THE FIRE. WITH THIS NEW INFORMATION, COH NOTIFIEDTHE NRC OF THE POTENTIAL GAS INVOLVEMENT. THE APARTMENT MANAGEMENT CONTACTEDA PLUMBER TO REPLACE THE CUSTOMER OWNED PORTION OF THE SERVICE LINE. DURING THE REPLACEMENT THE ORGINIAL SERVICE LINE WAS TORN FROM THE GROUND AND DAMAGED BEYOND THE POINT OF EVER DETERMINING IT'S ORIGINAL INTERGRITY. CONSEQUENTLY, THE EXACT POINT OF LEAKAGE AND THE CAUSE MAY NEVER BE KNOWN.
2025-01-31 10:21 | NO | NO | 19940215 | 1994-11-21 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | ESMT W OF MAIN S OF KCS RR | GRAMBLING | LINCOLN | LA | 71245 | 3 | NO | 1749 | 1994-10-25 | 0 | 0 | 4800 | 3594.1996 | 8678.0779 | YES | 2 | 21 |  | 19941025 | 53 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 156 |  |  | 0 | 1978 | UNDER GROUND OR UNDER WATER |  | BENNY CARSWELL | 3182559931 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THIRD PARTY CONTRACTOR WAS CLEANING R-O-W AND HIT LINE. CONTRACTOR LOCATION REQUEST WAS NOT FOR THIS LOCATION.THIRD PARTY DAMAGE.
2025-01-31 10:21 | YES | YES | 19940217 | 1994-11-02 | 15359 | PEOPLES NATURAL GAS | 402 SOUTH MAIN STREET | MADISON | MADISON | NE | 68748 | 3 | NO | 1045 | 1994-10-07 | 0 | 3 | 100000 | 74879.1584 | 180793.2897 | Null | 0 | 55 |  | 19941007 | 8 | 10 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | STEEL |  | 1.25 | 0.14 | API5L | UNKNOWN | 1952 | 1952 | UNDER PAVEMENT |  | GREGORY J. BENAK | 4022212021 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | BACKHOE INSTALLING STORM SEWER HIT 1 1/4INCH SERVICE LINE. NO LOCATE REQUESTED. SERVICE LINE WAS PULLED AWAY FROM METER.
2025-01-31 10:21 | NO | NO | 19940220 | 1994-10-24 | 12410 | MICHIGAN GAS CO | 3472 HARROW COURT | ZEELAND TWP | OTTAWA | MI | 49464 | 3 | NO | 1758 | 1994-09-15 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 1 | 0 |  | 19940916 | 50 | 100 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | UNDER INVESTIGATION | STEEL | POLYETHYLENE PLASTIC | 0.824 | 0.113 |  |  | 0 | 1993 | ABOVE GROUND |  | THOMAS M. REILLY | 8109877900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INVESTIGATING OF FIRE AND EXPLOSION AT ABOVE ADDRESS IS STILL UNDER INVESTIGATION. COMPLETE REPORT WILL FOLLOW.
2025-01-31 10:21 | YES | NO | 19940221 | 1994-11-22 | 10310 | KNOXVILLE UTILITIES BOARD | 871 WEISGARBER ROAD | KNOXVILLE | KNOX | TN |  | 4 | NO | 55 | 1994-11-07 | 0 | 0 | 100000 | 74879.1584 | 180793.2897 | Null | 8 | 5 |  | 19941107 | 38 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | WW-P-421 | CLAN & SONS | 1962 | 1962 | UNDER PAVEMENT |  | PAUL D. RANDOLPH | 6155947546 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | UPON THE COMPLETION OF THE REPAIR THE EFFECTED SECTION OF 6-INCH CIMJ PIPE WAS EXAMINED. NO EVIDENCE OF PITTING OR GRAPHITIZATION WAS FOUND.FULL CIRCLE BREAK APPARENTLY DUE TO EARTH MOVEMENT, MIGRATED TO STRUCTURE VIA SEWER DRAIN FIELD CAPPED BY ASPHALT DRIVE AND PARKING, STRUCTURE WAS COVERTED HOUSE USED FOR OFFICE.
2025-01-31 10:21 | YES | YES | 19940222 | 1994-11-22 | 8270 | MIDWEST GAS - DIV OF IOWA PUBLIC SERVICE CO | 856 RAINBOW DRIVE | WATERLOO | BLACK HAWK | IA | 50703 | 3 | NO | 1004 | 1994-10-17 | 6 | 1 | 250000 | 187197.8959 | 451983.2243 | Null | 1 | 36 |  | 19941017 | 25 | 25 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT DETERMINED | OTHER | NOT GIVEN | OTHER | NOT DETERMINED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SANDRA RASMUSSEN | 7122777928 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BY N.T.S.B WE HAVE BEEN ASKED BY N.T.S.B NOT TO SPECULATE AS TO CAUSE. WE WILL FILE A SUPPLEMENTAL REPORT AS SOON AS N.T.S.B. ISSUES THEIR OPINION. MWG HAS DISCOVERED A BREAK IN A PLASTIC SERVICE LINE AT THE TEE TO A STEEL MAIN. THE SERVICE LINE SERVED THE ADJOINING PROPERTY. WE DO NOT KNOW WHETHER THIS LINE WAS BROKEN BEFORE OR AFTER THE EXPLOSION. CAUSE OF INCIDENT STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19940223 | 1994-11-21 | 7348 | HOPE GAS INC | WATER ST. AT INTERSECTION W/MAIN ST. | CLARKSBURG | HARRISON | WV | 26301 | 3 | NO | 1445 | 1994-11-07 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 0 |  | 19941107 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | TIE-IN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER | TIE-IN DITCH | MICHELENE SHEPPARD | 3046238657 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CONTRACTOR WAS IN THE PROCESS OF TIEING IN REPLACEMENT PIPE. GAS WHICH WAS LEAKING THROUGH A GATE VALVE WAS IGNITED BY AN UNKNOWN SOURCE. TWO MEN WORKINGIN THE DITCH WERE BURNED AND HOSPITALIZED.
2025-01-31 10:21 | NO | NO | 19940224 | 1994-11-21 | 11720 | LONG ISLAND LIGHTING COMPANY | 2760 MIDDLE COUNTRY ROAD | LAKE GROVE | SUFFOLK | NY | 11755 | 4 | NO | 2300 | 1994-10-20 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 52 |  | 19941021 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | THOMAS E. LUPSKI | 5165454400 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE LONG ISLAND LIGHTING COMPANY (LILCO) PLACED A TELEPHONIC NOTIFICATION TOTHE DOT BASED UPON PRELIMINARY INFORMATION RECEIVED FROM THE FIELD AT THE TIME OF INCIDENT. THIS INFORMATION INDICATED THAT ONE (1) FATALITY OCCURRED, AND TWO (2) INJURED PERSONS REQUIRED HOSPITALIZATION. HOWEVER, SUBSEQUENT INVESTIGATION REVEALED THAT THE FATALITY AND INJURIES RESULTED FROM A STOLEN AUTOMOBILE CRASHING INTO THE SERVICE METER HEADER. THEY WERE NOT RELATED TO A GASINCIDENT.
2025-01-31 10:21 | YES | YES | 19940228 | 1994-11-16 | 21349 | VIRGINIA NATURAL GAS | 2609 ELON DRIVE | VIRGINIA BEACH |  | VA |  | 3 | NO | 1610 | 1994-11-07 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19941107 | 37 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PREMISE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER |  | DONALD L. WHITE | 8044665422 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OUR DISPATCHER RECEIVED A CALL FROM THE VIRGINIA BEACH FIRE DEPARTMENT REPORTING THAT THERE HAD BEEN AN EXPLOSION AND FIRE AT THIS LOCATION AND A FIFTEENYEAR OLD BOY HAD BEEN KILLED. THE INVESTIGATION INDICATES THAT THE BOY WAS WORKING WITH GASOLINE IN THE GARAGE WHICH MAY HAVE IGNITED WHEN THE BOY LIT ACIGARETTE. THERE WAS A SECOND EXPLOSION SHORTLY AFTER THE FIRST WHICH PROBABLY HAPPENED WHEN A NEARLY EMPTY, 40 GALLON PROPANE TANK WHICH WAS ALSO IN THEGARAGE EXPLODED. INITIAL REPORTS FROM THE VIRGINIA BEACH FIRE INVESTIGATORS AND OUR INVESTIGATION INDICATES THAT THIS INCIDENT WAS NOT CAUSED BY NATURALGAS.
2025-01-31 10:21 | YES | YES | 19950003 | 1994-12-27 | 2596 | COLUMBIA GAS OF OHIO INC | 800 MARTINSBURG ROAD | MOUNT VERNON | KNOX | OH | 43050 | 3 | NO | 1120 | 1994-11-18 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 5 |  | 19941128 | 37 | 52 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT | BUTT FUSION | POLYETHYLENE PLASTIC |  | 2 | 0.26 | PE2406 | UPONOR ALDYL | 1993 | 1994 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A 2" BUTT FUSION JOINT FAILED, ALLOWING ESCAPING GAS TO ENTER A COLLEGE DORMITORY. GAS WAS IGNITED BY A STUDENT LIGHTING AN INCENSE CANDLE. THE STUDENT SUFFERED SECOND AND/OR THIRD DEGREE BURNS TO UPPER BODY AND UPPER EXTREMITIES.
2025-01-31 10:21 | YES | YES | 19950005 | 1994-12-19 | 10037 | WESTERN RESOURCES, INC | 2260 SOUTH OLD MANOR | WICHITA | SEDGWICK | KS | 67218 | 3 | NO | 2247 | 1994-11-19 | 1 | 0 | 90000 | 67391.2425 | 162713.9608 | Null | 2 | 45 |  | 19941119 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 0.75 | 0.025 |  |  | 0 | 1965 | WITHIN/UNDER BUILDING |  | JAMES M. FALLON | 9132341441 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SETTLING | NO |  | NO | 0 |  | NO |  |  | A PVC SERVICE LINE IN THE VICINITY OF THIS RESIDENCE EXPERIENCED A BREAK,POSSIBLY DUE TO SOIL SETTLEMENT, RESULTING IN A LEAK WHICH APPARENTLY MIGRATEDTO THIS STRUCTURE AND WAS IGNITED BY AN UNKNOWN SOURCE. THE IGNITION OF GASRESULTED IN AN EXPLOSION AND FIRE WHICH LED TO THE PROPERTY DAMAGE ANDFATALITY.
2025-01-31 10:21 | YES | YES | 19950006 | 1994-12-21 | 12582 | MISSISSIPPI VALLEY GAS | 407 HICKORY STREET | GREENWOOD | LEFLORE | MS | 38930 | 3 | NO | 23 | 1994-12-12 | 0 | 2 | 98000 | 73381.5752 | 177177.4239 | Null | 4 | 42 |  | 19941212 | 18 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0 |  |  | 0 | 1930 | OTHER | UNDER DRIVEWAY | PAUL D. NOEL | 6019616860 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | NOT GIVEN | NO |  | NO | 0 |  | NO |  |  | A 2" CAST IRON MAIN, CROSSING UNDERNEATH A DRIVEWAY, DEVELOPED A HAIRLINE CRACK ALLOWING NATURAL GAS TO ESCAPE AND APPARENTLY MIGRATE UNDER THE ADJOINING FOUNDATION OF THE RESIDENCE. GAS THEN ENTERED THE BUILDING THROUGH CRACKS IN THE CONCRETE SLAP TYPE FOUNDATION RESULTING IN AN EXPLOSION AND FIRE. TWO (2) OCCUPANTS OF THE BUILDING RECEIVED BURNS AND THE HOUSE, ITS CONTENTS AND TWO (2) VEHICLES WERE BURNED.
2025-01-31 10:21 | YES | NO | 19950007 | 1994-12-14 | 15007 | PACIFIC GAS & ELECTRIC CO | 4171 STANLEY BOULEVARD | PLEASANTON | ALAMEDA | CA | 94566 | 3 | NO | 920 | 1994-11-12 | 0 | 0 | 250000 | 187197.8959 | 451983.2243 | Null | 1 | 48 |  | 19941112 | 50 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | VALVE |  | OTHER | NOT GIVEN | 0.075 | 0 |  | MUELLER | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES H. POPE | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS INCIDENT OCCURRED AS EMPLOYEES OF A FUMIGATING COMPANY WERE ATTEMPTINGTO SHUT OFF THE GAS SERVICE PRIOR TO FUMIGATING THE RESIDENCE. THE FUMIGATINGCOMPANY EMPLOYEE ATTEMPTED TO CLOSE THE RISER VALVE BY TURNING THE NUT THATHOLDS THE CORE IN PLACE INSTEAD OF THE VALVE STOP.IN DOING SO, HE BROKE THESHANK AND THE CORE DROPPED OUT OF THE VALVE, ALLOWING 50 PSIG GAS TO ESCAPEINTO THE BUILDING. THE RISER VALVE, REGULATOR AND METER WERE LOCATEDUNDERNEATH THE BUILDING. THE GAS IGNITED AND INITIATED A STRUCTURE FIRE THATULTIMATELY DESTROYED THE BUILDING. THE SOURCE OF THE IGNITION HAS NOT YET BEENDETERMINED, BUT IT IS SUSPECTED TO BE A FLOOR FURNACE PILOT THAT THEFUMIGATORS HAD NOT SHUT OFF.
2025-01-31 10:21 | YES | NO | 19950010 | 1994-12-14 | 15007 | PACIFIC GAS & ELECTRIC CO | 8102 KELLEY DRIVE | STOCKTON | SAN JOAQUIN | CA | 95209 | 3 | NO | 1858 | 1994-10-28 | 0 | 0 | 1500000 | 1123187.3756 | 2711899.346 | Null | 0 | 12 |  | 19941028 | 40 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER HOUSELINE | BODY OF PIPE |  | STEEL |  | 4 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES H. POPE | 4159736998 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CONTRACTOR INSTALLING NEW GAS DRYERS IN THE LAUNDROMAT BROKE THE HOUSE GASLINE WHICH SUBSEQUENTLY IGNITED AND STARTED A STRUCTURE FIRE. THE GASBUILDING WAS TURNED OFF AT THE METER SET BY THE FIRE DEPARTMENT AND CHECKEDBY THE SERVICEMAN UPON HIS ARRIVAL AT THE SCENE.
2025-01-31 10:21 | YES | NO | 19950012 | 1995-01-10 | 18308 | SIERRA PACIFIC POWER CO | 1735 RILEY AVENUE | RENO | WASHOE | NV | 89502 | 4 | NO | 1750 | 1994-12-10 | 0 | 0 | 120000 | 89854.99 | 216951.9477 | Null | 3 | 0 |  | 19941212 | 38 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.113 | API5L |  | 0 | 1964 | WITHIN/UNDER BUILDING |  | ANNE M. TAVERNIA | 7026893265 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-12-10 | NO | 0 |  | YES |  |  | ON SATURDAY, DECEMBER 10, 1993, A BACKHOE OPERATOR DIGGING A TRENCH FOR AREPLACEMENT SEWER LINE MADE CONTACT WITH THE 3/4" STEEL SERVICE LINE OWNEDBY SIERRA PACIFIC POWER COMPANY. THE LINE SERVED A SINGLE FAMILY DWELLING.THE LINE WAS PULLED FROM ITS LOCATION BUT WAS NOT PUNCTURED AT THE POINT OFCONTACT WITH THE BACKHOE. THE HOMEOWNER, WHO WAS OVERSEEING THE BACKHOEWORK, DID NOT IMMEDIATELY NOTIFY SIERRA PACIFIC OF THE DAMAGE, AND THEBACKHOE OPERATOR CONTINUED TO DIG AFTER MAKING LINE CONTACT. NOTIFICATION TOSIERRA PACIFIC OCCURRED AT APPROXIMATELY 1730 HOURS. THE CONTACT WITH THE LINECAUSED A SEPARATION OF THE SERVICE LINE FROM A 90 DEGREE COMPRESSION COUPLING(DRESSER) AT A POINT ON THE SERVICE LINE APPROXIMATELY 45 FEET FROM THE POINTOF CONTACT. THE PORTION THAT SEPARATED WAS BURIED IN THE YARD AT APPROXIMATELY10 FEET FROM THE HOUSE FOUNDATION. GAS MIGRATED UNDER THE HOUSE POSSIBLY VIAAN ADJACENT WATER LINE, FOR AN UNSPECIFIED AMOUNT OF TIME, AND ROSE INTO THEDWELLING. AT 1752 HOURS, AN EXPLOSION AND FIRE OCCURRED IN THE DWELLING.SEVERAL SUBSEQUENT EXPLOSIONS OCCURRED, AND THE HOUSE AND CONTENTS WEREDESTROYED. THE IGNITION SOURCE WAS POSSIBLY AN OIL BURING FURNACE. THERE WERENO INJURIES AND NO FATALITIES IN THIS INCIDENT. LOCATIONS HAD NOT BEENREQUESTED THROUGH THE STATE - MANDATED ONE-CALL SYSTEM. THE SON OF THEHOMEOWNER CALLED SIERRA PACIFIC DISPATCH ON THAT SATURDAY MORNING REQUESTINGLOCATION OF GAS FACILITIES. HE WAS TOLD THAT LOCATION REQUESTS REQUIRED ATLEAST 48 HOURS NOTICE (UNLESS AN EMERGENCY), AND THAT LOCATIONS WERE DONEMONDAY THRU FRIDAY.
2025-01-31 10:21 | NO | NO | 19950014 | 1995-01-04 | 8250 | IOWA - ILLINOIS GAS & ELECTRIC CO | 965 40TH STREET | MOLINE | ROCK ISLAND | IL | 61265 | 3 | NO | 2005 | 1994-11-07 | 0 | 0 | 55000 | 41183.5371 | 99436.3094 | Null | 2 | 5 |  | 19941107 | 7 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | APPLIANCE CONNECTOR | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | C.E. NAYLOR | 3097933687 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APPLIANCE CONNECTOR WAS DISCONNECTED ALLOWING GAS TO FLOW INTO STRUCTURE.NATURAL GAS CONNECTION TO STOVE WAS DISCONNECTED ALLOWING GAS TO FILL STRUCTURE.SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | NO | NO | 19950015 | 1995-01-04 | 1088 | BALTIMORE GAS & ELECTRIC CO | PARKWAY DR. AND DORSEY ROAD (RT. 176) | HARMANS | DORSEY | MD | 21076 | 3 | NO | 1408 | 1994-12-02 | 0 | 0 | 55000 | 41183.5371 | 99436.3094 | Null | 3 | 4 |  | 19941202 | 110 | 269 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NOT GIVEN | STEEL |  | 16 | 0.25 | AP15L CLASS B |  | 1990 | 1991 | UNDER GROUND OR UNDER WATER |  | DONALD L. SHRADER | 4105612728 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WILLIAM'S CONSTRUCTION COMPANY HAD MADE A MISS UTILITY CALL ON 11/15/1994 THE LOCATION OF THE PIPELINE WAS AGREED UPON. ON A FOLLOW-UP VISIT THE LOCATIONWAS STILL IN AGREEMENT. AT THIS TIME THE GRADING COMPANY WAS INFORMED THE BLOW OFF STAND PIPE WAS ABANDONED, WHEN IN FACT IT WAS NOT. ON 12/02/94, WILLIAMS CONSTRUCTION COMPANY OF 8660 PULASKI HWY. WAS CONDUCTING GRADING ACTIVITIES IN THE AREA OF PARKWAY DR. AND DORSEY RD. AT 14:08 BGE WAS NOTIFIED OF A STRUCK GAS MAIN ON DORSEY RD, THE CALL WAS DISPATCHED TO FIRST SITE RESPONDER AT 14:12 AND MR. AL CROSS ARRIVED AT 114:31 CONFIRMING A STRUCK 16" GAS MAIN WAS BLOWING GAS MR. CROSS CALLED FOR MORE HELP. GAS SURVEY AND REPAIR, SERVICE TECHNICIANS, AND SUPERVISION ALREADY WAS ON THE WAY. THE LOCATION OF THE STRUCK 16" GAS MAIN WAS 590' NORTHWEST OF THE NORTHWEST CORNER OF PARKWAY DR. SOUTH,ON THE SOUTHEAST SIDE OF DORSEY RD AT A 4" BLOW-OFF STAND PIPE. THE BLOW-OFF STAND PIPE WAS 4" AND PULLED OUT OF THE 16" GAS MAIN, LEAVING HOLE 6 /8"IN DIAMETER OR 29SQ.INCHES. ESTIMATED GAS LOSS OF $31,373 OCCURRED WHEN STAND PIPE WAS STRUCK BY A GRADING MACHINE, FILLING IN A SEDIMENT POND. THROTTLING OF THE GAS LINE STARTED AND THEN FOUND NECESSARY TO TAKE THE 16" OHP LINE OUT OF SERVICE BY TURNING MAIN VALVES AT RIDGE ROAD. AND SANDELWOOD ROAD. ON DORSEY RD OFF. THE GAS WAS OFF AT 17:20. A COMMAND CENTER WAS ESTABLISHED AT DORSEY ROAD AND PARKWAY DR. TO CONTROL THE TURN OFF OF 182 GAS SERVICES. THE REPAIR WAS MADE, TESTED AND PURGED. THE RELIGHT OF OUTAGE CUSTOMERS BEGAN AT 21:28. 115 CUSTOMERS WERE TURNED BACK ON THE REMAINING 67 CUSTOMERS WERE TURNED ON SATURDAY, 12/03/1994 AND MONDAY 12/05/1994.
2025-01-31 10:21 | YES | YES | 19950016 | 1995-01-12 | 13480 | NIAGARA MOHAWK POWER CORP | 95 TROY-SCHENECTADY ROAD (RTE.2) | LATHAM | ALBANY | NY | 12110 | 3 | NO | 245 | 1994-12-10 | 1 | 0 | 0 | 0 | 0 | Null | 10 | 36 |  | 19941210 | 20 | 22 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | NO ENTRY | OTHER | NO ENTRY | OTHER | NO ENTRY | 12 | 0.375 | G-1008 | U.S. STEEL | 1960 | 1960 | UNDER GROUND OR UNDER WATER |  | DANIEL P. THURN | 5184333535 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | FATALITY WAS THE RESULT OF PLANE CRASH. DAMAGED PIPE WAS THE RESULT OF PLANECRASH, WHICH WAS ACCIDENTAL.
2025-01-31 10:21 | YES | YES | 19950017 | 1995-01-18 | 15259 | PENNSYLVANIA GAS & WATER CO | OAKFORD & STURBRIDGE STS. | CLARKS SUMMIT | LACKAWANNA | PA | 18411 | 3 | NO | 1507 | 1994-08-31 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19940901 | 30 | 100 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | NO ENTRY | POLYETHYLENE PLASTIC |  | 4 | 0.391 | ALDYL-A | UPONOR | 1993 | 1994 | UNDER GROUND OR UNDER WATER |  | JAMES M. GREGER | 7178298866 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | PURGING AIR OUT OF NEWLY INSTALLED GAS MAIN. GAS IGNITED AS A RESULT OFSTATIC DISCHARGE. COMPANY EMPLOYEE RECEIVED 1ST AND SECOND DEGREE BURNS WHICHREQUIRED IN-PATIENT HOSPITALIZATION. MISPLACED FILES CAUSED THE DELAY OFWRITTEN REPORT.
2025-01-31 10:21 | YES | YES | 19950018 | 1995-01-18 | 2585 | COLUMBIA GAS OF KENTUCKY INC | KENTUCKY STATE ROUTE 89 | IRVINE | ESTILL | KY | 49336 | 3 | NO | 1330 | 1994-12-21 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19941221 | 5 | 7 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | REGULATOR STATION | OTHER | NO ENTRY | STEEL |  | 2 | 0.188 | GR B |  | 0 | 1969 | OTHER | REGULATOR STATION | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | CREW WAS REBUILDING A DISTRICT REGULATOR STATION. AN EMPLOYEE REMOVED A 2"THREADED RELIEF VALVE WITHOUT CLOSING THE 2"GATE VALVE AT ITS INLET. THERESULTING 5 PSIG OF GAS IGNITED CAUSING FIRST AND SECOND DEGREE BURNS TO THEEMPLOYEE'S FACE AND THIRD DEGREE BURNS TO HIS SCALP.
2025-01-31 10:21 | YES | YES | 19950023 | 1994-01-20 | 13299 | NEW JERSEY NATURAL GAS CO | 6 CHERRY COURT | SPRING LAKE HEIGHTS | MONMOUTH | NJ | 07762 | 0 | NO | 1320 | 1994-12-22 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19941222 | 6.5 | 0 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | CUSTOMERS FUEL LINE | OTHER | NO ENTRY | OTHER | NO ENTRY | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MONIQUE HERZOG | 9089381193 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO
2025-01-31 10:21 | NO | NO | 19950027 | 1995-01-30 | 11096 | LAKE APOPKA NATURAL GAS DISTRICT | SR 50 & HANCOCK ROAD |  | LAKE | FL |  | 1 | NO | 0 | 1994-12-28 | 0 | 0 | 50000 | 37439.5792 | 90396.6449 | Null | 0 | 40 |  | 19941228 | 180 | 300 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | 5LX42 |  | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | LARRY E. ASMUS | 4076562734 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-12-22 | YES | 2 | FLAGGED | YES |  |  | DAMAGED FUEL LINE. AT APPROXIMATELY 1:20 P.M. ON THURSDAY, DECEMBER 22,1994,NEW JERSEY NATURAL GAS COMPANY (NJNG) RECEIVED A REPORT FROM THE SPRINGLAKE HEIGHTS POLICE IN MONMOUTH COUNTY, NEW JERSEY THAT AN EXPLOSION AND FIREHAD OCCURRED IN A TOWNHOUSE AT 8 CHERRY COURT. THE FIRE WAS APPARENTLY CAUSEDBY NATURAL GAS LEAKING FROM A FUEL LINE TO THE HEATING UNIT LOCATED IN THEATTACHED GARAGE. ONE OF THE RESIDENTS HAD DRIVEN HIS CAR INTO THE UNITEARLIER THAT DAY, APPARENTLY DAMAGING THE LINE. THE RESIDENT, MR. NEARY, WASHOSPITALIZED IN CRITICAL CONDITION AND MRS. NEARY WAS TREATED FOR MINORINJURIES AND RELEASED. MR. NEARY LATER DIED. THE GARAGE AND TOWNHOUSE WEREBADLY DAMAGED BUT THE FIRE DID NOT SPREAD TO THE OTHER UNITS. A SKETCH OF THESITE IS ATTACHED. THE FIRST NJNG DISTRIBUTION CREW ARRIIVED ON THE SCENE AT1:32 P.M. AND VERIFIED THAT THE FIRE AND EMERGENCY PERSONNEL ON THE SCENE HADSHUT OFF THE GAS AT THE OUTSIDE METER SET. THE CREW WAS SHORTLY JOINED BYOTHER NJNG PERSONNEL WHO VERIFIED THAT THE SITUATION HAD BEEN MADE SAFE ANDTHAT GAS COMPANY FACILITIES WERE NOT INVOLVED IN THE ACCIDENT. AFTER THEEMERGENCY CALL WAS RECEIVED BY NJNG, A CUSTOMER ASSISTANT RECALLED RECEIVINGA CALL FROM MR. NEARY EARLIER IN THE DAY. THE TELEPHONE RECORDINGS WEREREVIEWED AND THE CALL WAS LOCATED. MR. NEARY HAD CALLED NJNG AT 12:04 P.M. ANDREPORTED THAT HE HAD STRUCK THE FOUNDATION OF HIS FURNANCE WITH HIS CAR. HEALSO STATED THAT HE EXPECTED A HEATING CONTRACTOR WITHIN THE NEXT COUPLE OFHOURS. SINCE HE INDICATED THAT HE DID NOT NOTICE ANY ODOR, NJNG DID NOT MAKEA SERVICE CALL. THE CUSTOMER ASSISTANT ADVISED HIM TO CALL BACK IMMEDIATELY IFHE DID DETECT AN ODOR. REFER TO REPORT FOR DETAILED CHRONOLOGICAL LISTING OFREPORTS.PIPELINE OPERATOR EXPOSED GAS PIPELINE, EXCAVATION OPERATOR ERROR - STRUCK EXPOSED PIPELINE W/EQUIPMENT CAUSING PIPELINE RUPTURE, GAS IGNITED, EXCAVATIONEQUIPMENT DESTROYED BY FIRE. FLAGGED, DUG UP AT 50FT INTERVALS TO VERIFY, PLACED PIPELINE MARKERS AT SPOT HOLE LOCATIONS. PIPELINE OPERATOR HAD SMALL CREW FOREMAN ON SITE ASSISTING 3RD PARTY EXCAVATOR BY DIGGING UP AND UNCOVERING PIPELINE FACILITY, EXCAVATION EQUIPMENT OPERATOR ERROR- STRUCK PIPELINE W/EQUIPMENT RUPTURING PIPELINE.
2025-01-31 10:21 | NO | NO | 19950028 | 1995-01-30 | 11683 | LONE STAR GAS CO OF TEXAS, INC | 209 B TOWN NORTH | TERRELL | KAUFMAN | TX | 75160 | 3 | NO | 1150 | 1995-01-11 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 19950111 | 16 | 45 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | 2306 |  | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | M.L. IMBODEN | 2146702779 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | PLUMBER HIT SERVICE LINE WITH DITCHING MACHINE WHILE INSTALLING POOL HEATER AND IGNITED GAS.
2025-01-31 10:21 | YES | NO | 19950029 | 1995-01-31 | 20010 | U G I CORP | 831 E. FEDERAL STREET | SALISBURY TWP | LEHIGH | PA | 18103 | 3 | NO | 800 | 1994-12-29 | 0 | 0 | 122000 | 91352.5732 | 220567.8135 | Null | 0 | 35 |  | 19941229 | 58 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | API51FBW CLASSB |  | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | JAMES R. HEINTZ | 6107963528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-10-31 | NO | 0 |  | YES |  |  | A CONTRACTOR WAS EXCAVATING TO INSTALL STORM DRAINS ON HALSTEAD STREET IN SALISBURY TOWNSHIP, LEHIGH COUNTY. THE CONTRACTOR HIT AND PULLED AN UNMARKED SERVICE LATERAL TO 831 EAST FEDERAL STREET. WHILE THE HOUSE'S ADDRESS WAS 831 EAST FEDERAL, BEING A CORNER PROPERTY, ITS SERVICE LATERAL WAS TAKEN FROM THE GAS MAIN ON HALSTEAD STREET. THE HIT CAUSED A CIRCUMFERENTIAL CRACK IN THE 3/4 INCH STEEL SERVICE PIPE WHERE THIS PIPE ENTERED A THREADED 90 DEGREE ELL. THE CRACK WAS LOCATED APPROXIMATELY TWO FEET FROM THE HOUSE. THE ESCAPING GAS MIGRATED INTO A CRAWL SPACE UNDER THE HOUSE AND WAS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE CAUSING A FIRE.
2025-01-31 10:21 | YES | NO | 19950030 | 1995-02-02 | 15007 | PACIFIC GAS & ELECTRIC CO | 198 ABLERTS AVENUE | BAY POINT | CONTRA COSTA | CA |  | 3 | NO | 1510 | 1995-01-11 | 0 | 0 | 150000 | 109988.8626 | 265564.5274 | Null | 0 | 50 |  | 19950111 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | JAMES H. POPE | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER SET VISIBLE | NO |  |  | GAS METER AND HOUSE STRUCK BY THIRD-PARTY VEHICLE. METER AND HOUSE WERE LOCATED BEHIND CURB AND FRONT YARD. AUTOMOBILE ACCELERATOR PEDAL STUCK. CAR DROVEACROSS SIDEWALK, LAWN AND FLOWERBED BEFORE STRIKING THE GAS METER SET.THEREFORE, NO ADDITIONAL METER PROTECTION REQUIRED.
2025-01-31 10:21 | YES | YES | 19950031 | 1995-02-01 | 12876 | MOUNTAIN FUEL SUPPLY CO | 800 SOUTH 300 EAST | SALT LAKE | SALT LAKE | UT | 84105 | 3 | NO | 945 | 1995-01-09 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19950109 | 50 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | FITTING |  | STEEL |  | 12 | 0.25 |  |  | 0 | 1971 | OTHER | VALVE PIT | EDWARD B. KELSEY | 8015345650 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DURING ROUTINE INSPECTION OF VALVES CONTAINED IN A SMALL VALVE PIT, LOCATEDAT 800 EAST 300 SOUTH, SALT LAKE CITY, UTAH, ATMOSPHERIC CORROSION WASDETECTED ON A NEEDLE VALVE NIPPLE. AS A COURSE OF CORRECTIVE ACTION, TOELIMINATE THIS ATMOSPHERIC CORROSION, IT WAS DECIDED TO REMOVE FROM SERVICETHE NEEDLE VALVE AND THE ASSOCIATED NIPPLE FITTING. DURING THE REMOVAL OFTHIS NEEDLE VALVE AND NIPPLE, A SLIGHT AMOUNT OF GAS ESCAPED AND ACCUMULATEDAT THE TOP OF THE PIT. WHEN THE WELDING OPERATION COMMENCED A FLASH OCCURREDCAUSING BURNS TO THE WELDER'S FACE AND HAIR. THE WELDER WAS TAKEN TO THEUNIVERSITY OF UTAH BU RN CENTER FOR TREATMENT, KEPT OVERNIGHT FOR OBSERVATION,AND RELEASED THE FOL LOWING DAY. THE OVERNIGHT OBSERVATION WAS A PRECAUTIONARYMEASURE. THERE WILL NOT BE ANY LASTING EFFECTS FROM THE BURNS. AN INITIALCHECK FOR ACCUMULATION OF GAS WAS VERIFIED BUT ADDITIONAL CHECKS, DURING THECOURSE OF WORK, WERE N OT VERIFIED. SUBSEQUENTIALLY, EMPHASIS, BY MOUNTAINFUEL MANAGEMENT IN COORDI NATION WITH THE COMPANY'S TRAINING DEPARTMENT, HASBEEN PLACED ON THE HAZARDS OF NOT FOLLOWING COMPANY PROCEDURES. COMPANY POLICYIS TO CONTINUALLY VERIFY THE EXISTENCE OF GAS THROUGHOUT THE COURSE OF THEWORK.
2025-01-31 10:21 | YES | YES | 19950032 | 1995-02-22 | 6243 | BHP GAS CO. | 6133 KALANIANAOLE HIGHWAY | HONOLULU |  | HI | 96821 | 4 | NO | 1315 | 1995-01-20 | 0 | 2 | 0 | 0 | 0 | Null | 3 | 0 |  | 19950120 | 8 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | ASTM D2513 | PLEXCO | 1994 | 1994 | UNDER GROUND OR UNDER WATER |  | DEAN M. UYEHARA | 8085945556 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-01-20 | NO | 0 |  | YES |  |  | GAS WARNING TAPE INSTALLED. THE INCIDENT OCCURRED WHEN A CONTRACTOR PUNCTURED OUR 4-INCH MAIN WHILE EXCAVATING FOR AN ELECTRICAL CONDUIT. THE ESCAPING GAS IGNITED, AND TWO OF THE CONTRACTOR'S EMPLOYEES WERE BURNED WHILE THEY EXITED THE TRENCH. IGNITION SOURCE UNKNOWN. THE LEAK WAS SECURED IN APPROXIMATELY THREE (3) HOURS.
2025-01-31 10:21 | YES | YES | 19950033 | 1995-02-24 | 18532 | SOUTHERN UNION GAS CO | 10TH AND MABLE | MONAHANS | WARD | TX | 79756 | 3 | NO | 815 | 1994-12-27 | 0 | 2 | 49150 | 36803.1063 | 88859.9019 | Null | 0 | 40 |  | 19941227 | 90 | 175 | BY TEST | 265 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | METER & REG STATION | OTHER | NOT GIVEN | STEEL |  | 4.38 | 0.144 | 5LX42 | LONE STAR | 0 | 1986 | ABOVE GROUND |  | GREG POLLARD | 9159432791 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO |  |  | SMALL AIRCRAFT CRASHED INTO METER AND REGULATOR STATION.
2025-01-31 10:21 | YES | YES | 19950034 | 1995-02-08 | 22182 | WASHINGTON GAS LIGHT CO | 4100 BLK PLAZA LANE | CHANTILLY | FAIRFAX | VA | 22020 | 3 | NO | 1330 | 1995-01-04 | 0 | 2 | 0 | 0 | 0 | Null | 2 | 0 |  | 19950104 | 55 | 55 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | GAUGE LINE | OTHER | NO FAILURE | POLYETHYLENE PLASTIC |  | 0.75 | 0.113 | PE2306 | UPENDOUT | 1994 | 1995 | UNDER GROUND OR UNDER WATER |  | J.O. BIELASKI | 7037505566 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | TWO WASHINGTON GAS COMPANY EMPLOYEES, WHILE REPLACING STEEL 3/4" GAUGE LINESFAILED TO GUARD AGAINST STATIC DISCHARGE WHILE HANDLING PLASTIC PIPE IN A GASEOUS ATMOSPHERE CAUSING SUBSEQUENT IGNITION.
2025-01-31 10:21 | YES | NO | 19950035 | 1995-02-14 | 4499 | ENTEX - DIVISION OF ARKLA INC | 101 ELM | CROSBY | HARRIS | TX | 77532 | 0 | NO | 2310 | 1994-10-07 | 0 | 0 | 85000 | 63647.2846 | 153674.2963 | Null | 1 | 15 |  | 19941008 | 27 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NOT GIVEN | STEEL |  | 1 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | LANNY W. CARGILE P.E. | 7136545105 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | DRIVER LOST CONTROL OF AUTOMOBILE. DRIVER LEFT SCENE.
2025-01-31 10:21 | YES | YES | 19950036 | 1995-02-15 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 105-107 CHATSWORTH STREET | CARY |  | NC |  | 1 | NO | 1435 | 1995-02-06 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19950206 | 60 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 |  |  | 0 | 1995 | UNDER GROUND OR UNDER WATER |  | SANDRA JOHNSON | 9198362421 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-02-03 | YES | 3 | MARKING PAINT | YES |  |  | 107 CHATSWORTH WAS MARKED. SERVICE LINE TO 105 SPLIT FROM 107 AND WAS NOTMARKED. 105 CHATSWORTH HAD BEEN MARKED ON PREVIOUS LOCATE CALL. MARKS HAD BEENBY RAIN. J & L SERVICES CALLED PUBLIC SERVICE DISPATCHER AND REPORTEDA DAMAGED SERVICE AT 114 CHANCELLORS RIDGE CT WHEN PUBLIC SERVICE PERSONNELARRIVED AT THIS ADDRESS THERE WAS NO DAMAGED LINE. THE FIRE DEPT RESPONDEDALSO. THE DISPATCHER PAGED THE CONTRACTOR AND GOT THE CORRECT ADDRESS. THECORRECT ADDRESS WAS 105 CHATSWORTH ST. UPON ARRIVAL, THE PUBLIC SERVICE TEAMFOUND THE SERVICE HAD BEEN DOUBLED BACK AND TAPED BY THE CONTRACTOR. J & LSERVICES WAS INSTALLING TELEPHONE DROP WIRE AT 107 CHATSWORTH ST AND CUT THESERVICE TO 105 CHATSWORTH ST SERVICE TO 105 CHATSWORTH ST. THE SERVICE AT 107CHATSWORTH ST WAS MARKED WITH YELLOW PAINT. THE SERVICE AT 105 CHATSWORTH STWAS NOT MARKED. PUBLIC SERVICE PERSONNEL SQUEEZED THE SERVICE OFF WITH THEAPPROPRIATE TOOL. THEN THE FIRE DEPT ON THE SCENE INFORMED OUR PERSONNEL THATTHERE WAS ANOTHER LINE BREAK, THIS TIME WITH A FIRE. THIS WAS ACROSS W.CHATHAM ST AT 208 RED FIELD STREET. PUBLIC SERVICE RESPONDED TO THE LINE BREAKON RED FIELD ST. MADE IT SAFE, THEN RETURNED TO CHATSWORTH ST. AND REPAIREDTHE LINE THERE. THE FOLLOWING DAY LEWIS MCLAMB WITH J & L SERVICES CALLED TOLET US KNOW THAT DOUG GAINEY HAD BEEN TAKEN TO THE WESTERN WAKE HOSPITAL.
2025-01-31 10:21 | NO | NO | 19950037 | 1995-02-16 | 11320 | LAWRENCEVILLE, CITY OF | 390 TWIN BROOKS WAY | LAWRENCEVILLE | GWINNETT | GA | 30245 | 3 | NO | 1500 | 1995-02-02 | 0 | 0 | 65000 | 47661.8405 | 115077.9619 | Null | 2 | 0 |  | 19950202 | 60 | 0 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 4 | 0 | 3408 | DRISCOPIPE | 1981 | 1982 | OTHER | NO ENTRY | ALLEN R. POWERS | 4049633332 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | YES | 3 | GROUND AND STREET PAINTED | YES |  |  | GEORGIA STAT LAW REQUIRES CALL TO THE UPC PRIOR TO DIGGING. ON THURSDAY FEB 2, 1995 AT 3:00 P.M. LAWRENCEVILLE GAS WAS NOTIFIED OF A CUT GAS MAIN AND HOUSEFIRE AT A NEW CONSTRUCTION SITE NEXT DOOR TO 390 TWIN BROOKS WAY IN TWINBROOKS SUBDIVISION. THE 4" PE GAS MAIN (60 PSIG MAOP) WAS CUT BY A TRACKLOADER DIGGING INTO A BANK ON THE SIDE OF THE HILL. THE AREA IS ALONG SIDECOLONIAL PIPELINE RIGHT OF WAY. THE BUILDER'S REPRESENTATIVE HAD BEEN TOLDOF THE PRESENCE OF GAS MAINS NEAR HIS BUILDING. THE REPRESENTATIVE FOR THEBUILDER AT THAT TIME WAS DAVID JOHNSTON WITH BOCK HOMES WAS TOLD BY NEILJOHNSON AND AUBRE Y GILMORE OF LAWRENCEVILLE GAS DEPT. THE HOUSE UNDERCONSTRUCTION WAS APPROXIMATELY 75% COMPLETE AND WAS BURNED COMPLETELY TO THEGROUND. AT 5:00 P.M., THE GAS MAIN WAS SHUT OFF AND SECURED AND THE FIREEXTINGUISHED.
2025-01-31 10:21 | NO | NO | 19950038 | 1995-02-23 | 14210 | OKLAHOMA NATURAL GAS CO | 575 FT N. OF 7ST ST. AND SOUTH HARVARD | TULSA | TULSA | OK | 74136 | 3 | NO | 820 | 1995-01-27 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 2 | 15 |  | 19950127 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | STEEL |  | 4.5 | 0.156 | X-42 | TEX TUBE | 1992 | 1993 | UNDER PAVEMENT |  | G.B. LYNN | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-01-12 | YES | 2 | PAINT ON STREET SURFACE | YES |  |  | STORM SEWER CONTRACTOR EXCAVATED TO A DEPTH BELOW THE ELEVATION OF THE GAS LINE AND THE LINE WAS HIT BY A TRACKHOE. THE GAS LINE HAD BEEN RELOCATED BELOWGRADE TO ACCOMMODATE THE STREET IMPROVEMENT PROJECT. THE LINE HAD BEEN MARKED PRIOR TO THE INCIDENT.
2025-01-31 10:21 | YES | NO | 19950039 | 1995-02-23 | 1088 | BALTIMORE GAS & ELECTRIC CO | 90 W. SUNSHINE WAY | WESTMINSTER | CARROLL | MD | 21158 | 3 | NO | 1030 | 1995-01-19 | 0 | 0 | 1500000 | 1099888.6259 | 2655645.2736 | Null | 1 | 31 |  | 19950119 | 94 | 99 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | 50R11 | DRISCO 8000 | 0 | 1994 | UNDER GROUND OR UNDER WATER |  | DENNIS C. BLESSING | 4105612526 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-01-12 | YES | 3 | GROUND & STREET PAINTED | YES |  |  | A FOUR INCH PLASTIC HIGH PRESSURE MAIN RUNNING ALONG THE WEST SIDE OF WESTSUNSHINE WAY, BETWEEN THE CURB AND SIDEWALK, WAS STRUCK AND PENETRATED BY ABORING MACHINE OPERATED BY APOLLO TRENCHING COMPANY AT 10:26, ON 01/19/95.THE STRIKE OCCURRED BETWEEN #88 AND #90 W. SUNSHINE WAY, APPROXIMATELY FORTYTWO FEET FROM THE NE CORNER OF #90. THE STRIKE WAS ON THE RIGHT-OF-WAY NEARTHE PR OPERTY LINE, SLIGHTLY CLOSER TO #90. THE BORING MACHINE CREATED ANIRREGULAR SHAPED HOLE ABOUT ONE INCH IN DIAMETER. BECAUSE THE BORING MACHINEREMAINED IN THE HOLE WHILE THE GAS WAS BLOWING, IT WAS ESTIMATED THAT THEAREA OF THE HOLE WAS REDUCED BY ABOUT 25%. BGE WAS NOTIFIED OF THE STRIKE AT10:30HRS. BY A PERSON FROM PRESTIEGE CABLE CO. OUR FIRST SITE RESPONDERARRIVED AT 11:25HRS., AND CHECKED HOUSES THAT WERE OCCUPIED, HE DETERMINEDTHAT NO GAS WAS PRESENT IN ANY OF THE BUILDINGS CHECKED. FOUR OF THE BUILDINGSWE COULD NOT GAIN ENTRY INTO BECAUSE NO ONE WAS HOME. OUR SURVEY & REPAIR CREWARRIVED @ 11:50HRS SHUT MAIN GAS VALVE OFF AT SULLIVAN ROAD AND W. SUNSHINEWAY. AT 12:01HRS. THE GAS WAS SHUT DOWN AND WORK WAS STARTED TO EXCAVATE THEAREA OF THE STRIKE. THE TOTAL TIME THAT THE GAS ESCAPED WAS 1HR. AND 31MINS.AT 13:18HRS #90 W. SUNSHINE WAY EXPLODED. WE COULD NOT GET INTO THIS BUILDINGON OUR INITIAL CANVASS OF THE AREA, BECAUSE IT WAS VACANT AND FOR SALE. AFTERTHE EXPLOSION ALL BUILDINGS WITHIN A ONE BLOCK AREA WERE CHECKED ANDMONITORED FOR THE PRESENCE OF NATURAL GAS UNTIL THE AREA WAS DETERMINED TO BESAFE. THIS MONITORING WAS CONDUCTED UNTIL MONDAY 01/23/95. THE AREA WASRECHECKED SEVEN DAYS LATER BY FLAME PACK AND COMBUSTIBLE GAS INDICATOR METERAND RESULTED IN NO READINGS.SUPPLEMENTAL REPORT SUBMITTED 7/17/1995 INDICATESPROPERTY DAMAGE CHANGE TO 1.5 MILLION DOLLARS, AS WELL AS A MODIFICATION INTHE MANUFACTURER. REPORT SUBMITTED BY D. BLESSING/D.L. SHRADER.
2025-01-31 10:21 | YES | NO | 19950040 | 1995-02-27 | 12350 | MINNEGASCO INC | 11833 MAGNOLIA STREET NW | COON RAPIDS | ANOKA | MN | 55448 | 3 | NO | 1600 | 1994-12-14 | 0 | 0 | 150000 | 112318.7376 | 271189.9346 | Null | 2 | 30 |  | 19941214 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | REGULATOR | 1 | 0 |  | FISHER | 1960 | 1960 | ABOVE GROUND |  | GENE SCHULTZ | 6123214756 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FISHER S252-4 SERVICE REGULATOR FAILED IN THE OPEN POSITION WHILE IT WAS BEING PREPARED FOR REPLACEMENT.
2025-01-31 10:21 | YES | YES | 19950041 | 1995-02-28 | 18536 | SOUTHWEST GAS CORP | 3308 WEST FIREFALL PLACE | TUCSON | PIMA | AZ |  | 3 | NO | 1614 | 1995-02-04 | 1 | 0 | 200000 | 146651.8168 | 354086.0365 | Null | 1 | 16 |  | 19950204 | 58 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ALDYL HD | DUPONT | 1979 | 1980 | UNDER GROUND OR UNDER WATER |  | JOHN HANENBURG | 5207946053 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | UNKNOWN | YES
2025-01-31 10:21 | YES | YES | 19950046 | 1995-03-07 | 15469 | PHILADELPHIA GAS WORKS | 4633 MILNOR STREET | PHILADELPHIA | PHILADELPHIA | PA | 19137 | 4 | NO | 1940 | 1995-02-15 | 1 | 1 | 120000 | 87991.0901 | 212451.6219 | YES | 1 | 35 |  | 19950216 | 0.24 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1906 | WITHIN/UNDER BUILDING |  | JOSEPH M. CAREY | 2156846372 | EXTERNALLY | GENERAL CORROSION |  | OTHER | SOIL | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | NATURAL GAS FROM A DAMAGED MAIN MIGRATED INTO A RESIDENCE AND IGNITED.NATURAL GAS FROM A 3RD PARTY, DAMAGED MAIN, MIGRATED INTO A RESIDENCE. THEHOMEOWNER LIT A CIGARETTE WITH A LIGHTER AND IGNITED THE NATURAL GAS CAUSINGTWO SEPARATE EXPLOSIONS WITHIN THE RESIDENCE. THE INCIDENT OCCURRED AT 3308WEST FIREFALL PLACE, TUCSON, ARIZONA. THE RESIDENT OF THIS TOWNHOUSE WASATTEMPTING TO LIGHT A CIGARETTE WITH A LIGHTER WHEN A FLAM FLASHED INTO THEKITCHEN AREA FOLLOWED BY AN EXPLOSION. THE OCCUPANT EXITED THE RESIDENCE INTOTHE GARAGE AREA WHERE NEIGHBORS ASSISTED HER. AS SHE WAS BEING HELPED OUT OFTHE GARAGE, A SECOND EXPLOSION OCCURRED IN THE REAR NORTH END OF THERESIDENCE. THE RESIDENT WAS TRANSPORTED TO ST. MARY'S HOSPITAL WITH FIRST ANDSECOND DEGREE BURNS. SOUTHWEST GAS CUSTOMER SERVICE TECHNICIAN AND A LEAKSURVEY TECHNICIAN WERE DISPATCHED TO THIS INCIDENT. A LEAK SURVEY IN THEALLEY BEHIND 3308 WEST FIREFALL DETECTED HIGH CONCENTRATIONS OF NATURAL GAS INTHE AREA. RURAL METRO FIRE AND THE PIMA COUNTY SHERIFF'S OFFICE WERE NOTIFIEDOF THESE FINDINGS AND BEGAN EVACUATING THE AREA. SOUTHWEST GAS CORPORATIONCONSTRUCTION CREWS WERE DISPATCHED TO THE INCIDENT. THE PRELIMINARYINVESTIGATION CONCLUDED THAT A SOUTHWEST GAS MAIN IN THE ALLEY BEHIND 3308WEST FIREFALL PLACE HAD BEEN DAMAGED. THE INVESTIGATION AS TO WHO DAMAGED THELINE IS ONGOING. NECESSARY REPAIRS WERE MADE ON THE DAMAGED FACILITY ANDEXTENSIVE LEAK SURVEYING CONTINUED FOR SEVERAL DAYS. THE AREA HAS RETURNED TONORMAL ACTIVITIES. IT IS UNKNOWN WHO DAMAGED THE GAS MAIN AT THISTIME.SUPPLEMENTAL REPORT 3/28/1995 INDICATED THAT THE PIMA COUNTY SHERIFF'SDEPARTMENT CONTACTED SOUTHWEST GAS AND REPORTED THAT ON MARCH 17, 1995, THEHOMEOWNER DIED WHILE STILL BEING TREATED AT ST.MARY'S HOSPITAL.1906 1-1/4" SERVICE PIPE WAS COVERED WITH CORROSIVE SCALE AND AT THE TIME OFEXCAVATION APPEARED INTACT. WHEN THE PIPE WAS CLEANED FOR TESTING THE SCALEWAS INADVERTENTLY REMOVED, AS WELL AS BEING DISTRURBED BY A SERVICE STOPPERINSERTED FROM WITHIN THE EXCAVATION THEREBY CREATING A HOLE IN THE SERVICE.OBSERVATION OF THIS HOLE IS THE PRIME FACTOR IN THE PHILADELPHIA FIREDEPARTMENT'S FINDING THAT THIS INCIDENT WAS CAUSED BY GAS MIGRATION FROM THEHOLE IN THE SERVICE TO A SOURCE OF IGNITION INSIDE 4633 MILNOR STREET.THEPHILADELPHIA FIRE DEPARTMENT AND REPRESENTATIVES OF THE BUREAU OF ALCOHOL,TOBACCO AND FIREARMS INVESTIGATED THE INCIDENT. THE PHILADELPHIA FIREDEPARTMENT CONCLUDES THAT A HOLE IN THE 1-1/4" LOW PRESSURE STEEL SERVICE PIPETO 4633 MILNOR STREET WAS THE SOURCE OF UNCONTROLLED NATURAL GAS THATMIGRATED THROUGH A CAVITY BEHIND A LEAKING FIRE HYDRANT IN FRONT OF 4633MILNOR STREET, THEN INTO THE BASEMENT OF THAT PROPERTY WHERE IT FOUND A SOURCEOF IGNITION. ATTHIS TIME, THE PHILADELPHIA GAS WORKS IS CONDUCTING A SEPARATEINVESTIGATION BASED ON FINDINGS THAT THE PROBLEMS DISCOVERED DURING THEEXCAVATION OF THE DISTRIBUTION SYSTEM OCCURRED AFTER THE INCIDENT.THE PHILADELPHIA GAS WORKS SUSPECTS THAT IF NATURAL GAS WAS THE SOURCE OF FUELIN THIS INCIDENT THAT SOURCE MAY HAVE BEEN FROM AN INTERNAL FUEL LINE FAILUREOR OTHER DELIBERATE MEANS. SUPPLEMENTAL REPORT RECEIVED 11/8/1995 INDICATESATTACHED [LENGTHY] METALLURGICAL REPORT CONCERNING THE 6" CAST IRON MAIN AND 11/4" STEEL SERVICE FROM THE INITIAL INCIDENT. THE SERVICE PIPE HAD A PATCH OFCORROSION WHICH AFFECTED THE ENTIRE THICKNESS OF THE PIPE IN AN EXTREMELYLOCALIZED AREA, BUT ITS WROUGHT IRON MICROSTRUCTURE KEPT THE CORROSIONPRODUCTS IN PLACE THERE. REFER TO THE LENGTHY REPORT FILED WITH THESUPPLEMENTAL SUBMISSION 11/8/1995 FOR MORE DETAILS ON THE CHANGE IN CAUSE FROMCORROSION TO OTHER.
2025-01-31 10:21 | YES | YES | 19950047 | 1995-03-10 | 15007 | PACIFIC GAS & ELECTRIC CO | 123 -129B DORE STREET | SAN FRANCISCO | SAN FRANCISCO | CA | 94103 | 4 | NO | 330 | 1995-02-22 | 1 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 1 | 30 |  | 19950222 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER APPLIANCE | OTHER | NOT GIVEN | OTHER | CUSTOMER APPLIANCE | 0 | 0 |  |  | 0 | 0 | OTHER | WITHIN BUILDING | JAMES H. POPE | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE GAS USED TO FILL APARTMENT DID IGNITE, CREATING AN EXPLOSION, THE CAUSEOF DEATH IS UNDER INVESTIGATION. THE VICTIM MAY HAVE BEEN DEAD PRIOR TO THEEXPLOSION AND FIRE. IGNITION OF GAS USE TO FILL APARTMENT IN ATTEMPTED SUICIDE.
2025-01-31 10:21 | YES | NO | 19950050 | 1995-03-21 | 13710 | NORTHERN ILLINOIS GAS CO | 1822 PLAINFIELD ROAD | CREST HILL | WILL | IL | 60435 | 3 | NO | 520 | 1995-02-28 | 0 | 0 | 250000 | 183314.771 | 442607.5456 | Null | 0 | 38 |  | 19950228 | 58 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | CLINT WHYBARK | 8157404100 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE AT 1822 PLAINFIELD ROAD (MICHAEL'S RIBS) IN CREST HILL. ARSON INVESTIGATION CURRENTLY UNDERWAY BY STATE FIRE MARSHALL. SERVICE LINE TESTED AT OPERATING PRESSURE WITH NO LEAKS FOUND. MAIN AND SERVICES F.I. ADJACENT TO ADDESS WITH NO GAS FOUND.
2025-01-31 10:21 | YES | NO | 19950051 | 1995-03-21 | 20010 | U G I CORP | 191 TILGHMAN STREET | ALLENTOWN | LEHIGH | PA | 18102 | 3 | NO | 830 | 1995-02-21 | 0 | 0 | 170000 | 124654.0443 | 300973.131 | Null | 2 | 0 |  | 19950221 | 9 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 | CAST IRON | UNKNOWN | 0 | 1913 | UNDER PAVEMENT |  | DAVID R. HANNUM | 6107963507 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | IT APPEARS THAT NATURAL GAS ESCAPING FROM A CRACK IN A 4" CAST IRON MAIN LOCATED IN THE 700 BLOCK OF NORTH 2ND STREET IN ALLENTOWN, LEHIGH COUNTY, MIGRATED INTO THE CORNER PROPERTY AT 191 TILGHMAN ST. THE GAS WAS SUBSEQUENTLY IGNITED BY AN UNKNOWN SOURCE CAUSING A LOW LEVEL EXPLOSION AND A BRIEF FLASH FIRE. THERE WERE NO FATALITIES OR INJURIES AND NO OTHER STRUCTURES SUSTAINED DAMAG
2025-01-31 10:21 | YES | YES | 19950052 | 1995-03-21 | 12582 | MISSISSIPPI VALLEY GAS | WESTER STREET | JACKSON | HINDS | MS | 39201 | 4 | NO | 1300 | 1995-03-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19950313 | 20 | 37 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.35 |  | MCWANE | 0 | 0 | UNDER PAVEMENT |  | PAUL D. NOEL | 6019616860 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SHIFTING SOIL IN THE AREA | NO |  | NO | 0 |  | NO |  |  | THE INDIVIDUAL WAS EXPOSED TO NATURAL GAS FOR APPROXIMATELY TWO MINUTES WHILE ATTEMPTING TO INSTALL A CLAMP ON A 4" CAST IRON MAIN. THE INDIVIDUAL WAS TREATED FOR ASPHYXIATION AND REMAINED IN THE HOSPITAL ONE NIGHT FOR OBSERVATION.
2025-01-31 10:21 | NO | NO | 19950055 | 1995-04-13 | 4499 | ENTEX - DIVISION OF ARKLA INC | S FRY ROAD AT PERDIDO BAY | HOUSTON | HARRIS | TX | 77084 | 3 | NO | 1459 | 1995-02-02 | 0 | 0 | 27127 | 19891.1192 | 48026.4596 | Null | 1 | 31 |  |  | 30 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.576 | PE2406 | DUPONT | 0 | 1995 | UNDER GROUND OR UNDER WATER |  | JOE HURST | 7136545900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | BUTT FUSION JOINT FAILED DURING BACK FILLING OPERATION. GAS COMPANY CONTRACTOR MADE A BAD BUTT FUSION (6"PLASTIC MAIN) WHILE BACK FILLING THE HOLE THE LEAKING GAS WAS IGNITED BY A BACKHOE - THE BACKHOE WAS DESTROYED.
2025-01-31 10:21 | YES | NO | 19950056 | 1995-04-13 | 3600 | DUMAS, CITY OF | 315 EAST SECOND | DUMAS | MOORE | TX | 79029 | 1 | NO | 2130 | 1994-10-30 | 0 | 0 | 400000 | 299516.6335 | 723173.1589 | Null | 2 | 0 |  | 19941030 | 18 | 60 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDECIDED | OTHER | UNDECIDED | OTHER | UNDECIDED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LARRY SMITH | 8069354101 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | UNDECIDED CAUSE. DAMAGED BY OUTSIDE FORCES - OTHER - UNKNOWN.
2025-01-31 10:21 | YES | NO | 19950057 | 1995-04-07 | 12876 | MOUNTAIN FUEL SUPPLY CO | 7720 ROYAL STREET | PARK CITY | SUMMIT | UT | 84060 | 3 | NO | 2035 | 1995-03-14 | 0 | 0 | 250000 | 183314.771 | 442607.5456 | Null | 0 | 55 |  | 19950314 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | OTHER | CUSTOMER OWNED FUEL LINE | OTHER | CUSTOMER OWNED FUEL LINE | STEEL |  | 0.75 | 0.09 | ASTM2513 | PHILLIPS | 1991 | 1992 | WITHIN/UNDER BUILDING |  | EDWARD B. KELSEY | 8015345650 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | ICE AND SNOW | NO |  | NO | 0 |  | NO |  |  | ON MARCH 14, 1995, ICE AND SNOW SLUFFED OFF OF THE ROOF OF THE DEER VALLEYCLUB LOCATED AT 7720 ROYAL STREET PARK CITY, SUMMIT COUNTY,UTAH. THIS ICE ANDSNOW LANDED ON A VERY STEEP SLOPE AND SLID IN A DOWNWARD DIRECTION INTO THESERVICE LINE RISER AND METER SET. THE METER SET WAS SLIGHTLY TWISTED. THESERVICE LINE RISER AND METER SET WERE NOT SEVERELY DAMAGED AND DID NOT LEAKDURING THIS INCIDENT. HOWEVER, THE FORCE ON THE METER SET CAUSED THECUSTOMER-OWNED FUEL LINE, EXTENDING THROUGH THE WALL OF THE BUILDING, TO BEDAMAGED0 CAUSING AN EXPLOSION AND SUBSEQUENT FIRE. FORTUNATELY, THE BUILDINGWAS NOT OCCUPIED I N THE AREA OF THE EXPLOSION/FIRE AND NO ONE WAS INJURED.THE DAMAGE TO THE C USTOMER-OWNED FUEL LINE CAUSED A THREADED JOINT AT ONELOCATION TO CRACK AND THE CUSTOMER-OWNED PIPING WAS SEVERED AT A SECONDLOCATION ALLOWING GAS TO RELEASE INSIDE THE BUILDING. THE EXPLOSION/FIRECAUSED APPROXIMATELY $250,000 WO RTH OF DAMAGE TO THE BUILDING. MR. RUSSCOPELAND, UTAH DIVISION OF PUBLIC UTI LITIES, PIPELINE SAFETY SECTION, FOR THESTATE OF UTAH, WAS PROMPTLY NOTIFIED AND HAS INVESTIGATED THIS INCIDENT. MR.COPELAND AND MANAGEMENT PERSONNEL FROM MOUNTAIN FUEL ARE SCHEDULING MEETINGSWITH THE SUMMIT COUNTY BUILDING OFFICIALS TO EXPLORE THE POSSIBILITIES OFADDITIONAL BUILDING CODES TO PREVENT THIS PREVENT THIS TYPE OF REOCCURRENCE.
2025-01-31 10:21 | YES | YES | 19950058 | 1995-04-04 | 2596 | COLUMBIA GAS OF OHIO INC | 1782 CHANNINGWAY COURT WEST | COLUMBUS | FRANKLIN | OH | 43232 | 3 | NO | 1051 | 1994-05-05 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 16 |  | 19940505 | 50 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.09 |  |  | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-05-04 | NO | 0 |  | YES |  |  | FOR A LOCATION 25' FROM WHERE THEY EXCAVATED COLUMBIA REPRESENTATIVE SHOWEDUP TO MAKE THE LOCATE BUT WAS INFORMED BY THE REQUESTING PARTY THAT NO EXCAVATION WOULD BE MADE IN THE VICINITY OF OUR FACILITIES. COLUMBUS SOUTHERN POWER(CSP) WAS REPAIRING BURIED ELECTRIC CABLE IN THE REAR OF 1782 CHANNINGWAY COURT WEST. THE REPAIRS CONSISTED OF INSTALLING SHRINK SLEEVE OVER DAMAGED AREAS OF ELECTRIC CABLE BY HEATING THE SLEEVE WITH AN OPEN FLAME TORCH TO SEAL AND SECURE IT TO THE CABLE. AT THE LOCATION OF THE INCIDENT, SHRINK SLEEVE WASSERVICE LINE. DURING THE CABLE REPAIR, IT APPEARS THAT THE OPEN FLAME TORCH CAME TOO CLOSE TO THE PLASTIC SERVICE LINE CAUSING THE SERVICE LINE TO RUPTUREFROM EXCESSIVE HEAT. ESCAPING GAS WAS APPARENTLY IGNITED BY THE TORCH, RESULTING IN THE INJURY TO THE CSP EMPLOYEE MAKING THE REPAIRS. THE EMPLOYEE WAS ADMITTED TO THE OHIO STATE UNIVERSITY BURN UNIT AND WAS RELEASED 05/20/94. A SECOND EMPLOYEE STANDING ABOVE THE WORK AREA RECEIVED MINOR INJURIES BUT DID NOT REQUIRE HOSPITALIZATION. A BACKHOE OR DITCHING MACHINE WAS ALSO MODERATELYDAMAGED BY THE FIRE. ON THURSDAY, MAY 5, 1995 A COLUMBUS AND SOUTHERN POWER COMPANY (CSP) EMPLOYEE WAS REPAIRING AND UNDERGROUND ELECTRIC CABLE. THE REPAIR INVOLVED THE INSTALLATION OF A HEAT SHRINK SLEEVE WITH AN OPEN FLAME TORCHEXPOSED IN THE SAME EXCAVATION WAS A 1" PLASTIC CUSTOMER OWNED GAS SERVICE LINE. THE TORCH APPARENTLY CAME TOO CLOSE TO THE 1" GAS SERVICE LINE CAUSING ITTO RUPTURE FROM THE EXCESSIVE HEAT. THE ESCAPING GAS WAS IGNITED BY THE TORCH AND RESULTED IN BURNS TO TWO CSP EMPLOYEES, A BACKHOE AND A SECTION OF FENCE. ONE OF THE EMPLOYEES WAS ADMITTED TO THE OSU BURN CENTER. THE 1" PLASTIC SERVICE LINE FAILED FROM EXPOSURE TO EXCESSIVE HEAT GENERATED BY THE OPEN FLAME TORCH USED TO HEAT THE SHRINK SLEEVE. THE SHRINK SLEEVE WAS BEING INSTALLEDAPPROXIMATELY 8 TO 10" FROM THE EXPOSED PLASTIC GAS SERVICE LINE. A FACILITYLOCATED REQUEST WAS MADE BY CSP THROUGH THE OHIO UTILITY PROTECTION SERVICE(OUPS) ON MAY 4, 1994. ON THE MORNING OF MAY 5, 1994 A COLUMBIA GAS OF OHIO,INC. (OUPS) ON MAY 4,1994. ON THE MORNING OF MAY 5, 1994 A COLUMBIA GAS OF OHIO, INC (COH) REPRESENTATIVE SHOWED UP AT THE JOB SITE TO MEET WITH CSP PERSONNEL AND LOCATED THE GAS FACILITIES. THERE WERE NO GAS FACILITIES IN THE AREAWHERE OUR REPRESENTATIVE WAS ADVISED THAT CSP WOULD BE EXCAVATING. THE LOCATION OF THE INCIDENT WAS 25' FROM WHERE CSP INDICATED THEY WOULD BE EXCAVATING. AT 10:51 A.M. ON THURSDAY, MAY 5, 1994, COH'S DISPATCHING OPERATION AT 920GOODALE BLVD., COLUMBUS, OHIO RECEIVED A CALL FROM THE COLUMBUS FIRE DEPARTMENT FOR ASSISTANCE AT 1782 CHANNINGWAY COURT. THEY REPORTED AN EXPLOSION ANDIGNITION OF NATURAL GAS. COH DISPATCHED PERSONNEL AT 10:53 A.M. AND FOUND GASBURNING AT AN EXCAVATION OVER A CUSTOMER SERVICE LINE. THE COH EMPLOYEE TURNED OFF THE MASTER CURB VALVE AT 11:07 AM. WHICH EXTINGUISHED THE FLAMES. COH'SOPERATION MANAGER, AL STEINMETZ, HAS DISCUSSED THE SITUATION WITH CSP'S SAFETY AND HEALTH SECTON POINTING OUT THE POSSIBLE HAZARDS OF USING AN OPEN FLAME WHEN WORKING IN CLOSE PROXIMITY TO A PLASTIC GAS LINE. WE ARE INFORMED THATCSP'S ACCIDENT INVESTIGATION COMMITTEE WILL BE REVIEWING THEIR FACTS FROM THEINCIDENT AND WILL MAKE RECOMMENDATION FROM THEIR FINDINGS TO PREVENT A RECURRENCE.
2025-01-31 10:21 | NO | NO | 19950062 | 1995-04-25 | 6141 | GAS CO OF NEW MEXICO | 11 PEACH STREET | CLAYTON | UNION | NM | 88415 | 3 | NO | 1012 | 1995-04-05 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 0 | 30 |  | 19950405 | 35 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  | NATIONAL METER | 1981 | 0 | WITHIN/UNDER BUILDING |  | JON W. JONES | 5052414571 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | ABOVE GROUND METER ASSEMB | YES |  |  | METER ASSEMBLY WAS HIT BY A VEHICLE. APRIL 5, 1995, 10:00AM, PNM CUSTOMERSERVICE REPRESENTATIVE JANET MOSIER RECEIVED A TELEPHONE CALL FROM AURORAPADILLA. MS. PADILLA INFORMED MS. MOSIER THAT THER WAS GAS IN THE HOUSELOCATED AT 11 PEACH. MS. MOSIER ASKED IF ANYONE WAS IN THE HOUSe AND WASADVISED THERE WAS NO ONE THERE. MS. MOSIER TOLD MS. PADILLA TO NOT ENTER THEHOUSE. MS. MOSIER THEN DISPATCHED NARCISSO CARDENAS, GCNM OPERATIONSREPRESENTATIVE III, TO THE LOCATION WITH AN INSIDE GAS LEAK ORDER. MR.CARDENAS PROCEEDED TO 11 PEACH . ABOUT ONE BLOCK AWAY FROM THE ADDRESS, MR.CARDENAS HEARD AN EXPLOSION. HE CONTINUED TO THE ADDRESS, FOUND THE HOUSEBURNING, ENTERED THE ALLEY AND TURNED OFF THE METER AT 10:05 AM. HE FOUNDTHERE WERE VISIBLE SIGNS THAT THE METER SET HAD BEEN DAMAGED AND THEREGULATOR HAD BEEN PUSHED OFF CENTER OF ITS NORMAL POSITION. AFTER TURNINGOFF THE METER, MR. CARDENAS INFORMED GCNM EMPLOYEES WES GANT AND DARRELLCHANCEY OF THE EXPLOSION. HE ALSO ADVISED PNM EMPLOYEES GERALD BUCKNER AND TYBRADLEY WHO RESPONED TO THE SCENE TO DISCONNECT THE ELECTRIC SERVICE. MR.CARDENAS, MR.GANT AND MR. CHANCEY BEGAN THE INVESTIGATION OF THE INCIDENT ATAPPROXIMATELY 10:15 AM. MR. GANT, SENIOR CORROSION TECHNICIAN, INFORMED GCNMAREA MANAGER, DIANA MORRIS, OF THE INCIDENT AT 10:15AM. SHE ASSIGNED HIM THERESPONSIBILITY OF SUPERVISOR ON SITE AND IN CHARGE OF THE INVESTIGATION. AT10:17AM, MS. MORRIS NOTIFIED TERRY D. RISTER, GCNM VICE -PRESIDENT OF GASOPERATIONS. SHE THEN INFORMED JAMES K. BARFIELD III, GCNM OPERATIONSSUPERVISOR III AND DANNY DECARD, GCNM OPERATIONS SUPERVISOR II (BOTHLOCATED IN CLOVIS, NM) OF THE INCIDENT AT APPROXIMATELY 10:20 AM. AT 10:37 AMMR. JON JONES, GCNM ENGINEERING WAS NOTIFIED. ON SITE INVESTIGATIONCONFIRMED THAT THE METER ASSEMBLY HAD BEEN DAMAGED AND THE REGULATOR HAD BEENKNOCKED OUT OF ITS ORIGINAL POSITION ALLOWING INCREASED PRESSURE TO ENTER THEBUILDING. LOCAL POLICE APPREHENDED THE SUPSPECTS WHO ADMITTED THEIR VEHICLEHAD STRUCK THE METER ASSEMBLY. GCNM EMPLOYEES BAR TESTED CUSTOMER YARDLINESIN THE AREA AND GCNM FACILITIES IN THE AREA. NO LEAKS WERE FOUND. THE DAMAGEDMETER AND REGULATOR WERE REMOVED FROM THE LOOP AND SECURED FOR FURTHERINVESTIGATION. A NEW METER AND REGULATOR WERE INSTALLED AND A CLOCK TEST WASPERFORMED . FIRST CLOCK TEST SHOWED 1/2 FOOT LEAKAGE IN 28 SECONDS. ALLAPPLIANCES IN THE HOUSE WERE THEN SHUT OFF AT THE STOPS. SECOND CLOCK TESTREVEALED NO LEAKAGE IN A 3 MINUTE TEST. SOIL AND AIR SAMPLES WERE TAKEN ATTHE SITE, SEALED AND LABELED. ODORANT TESTS WERE TAKEN AT 11 PEACH, 20 PEACHAND AT POPLAR AND NORTH FIRST. ALL TESTS REVEALED ODORANT LEVELS TO BE WITHINTHE REQUIRED PARAMETERS. THE NEW METER AND REGULATOR WERE REMOVED FROM THEMETER ASSEMBLY AND WERE SECURED. THESE ITEMS AS WELL AS THE ORGINIAL METERAND REGULATOR WERE OBSERVED ON APRIL 6, 1995 BY KEN HUTCHINSON GCNMCOMPLIANCE SPECIALIST, J.K. BARFIELD, GCNM OPERATIONS SUPERVISOR III AND BYRAY ELLIOT, NEW MEXICO OFFICE OF PIPELINE SAFETY. ALL EQUIPMENT WAS BOXED,SECURED AND HAND DELIVERED TO GCNM MANZANO METER SHOP ON APRIL 6, 1995 BY MR.HUTCHINSON. DURING THE INVESTIGATION, BOTH VIDEO AND 35MM PHOTOS WERE TAKENOF THE INCIDENT SCENE. THESE ITEMS AS WELL AS OTHER DOCUMENTAITON AND EVIDENCEARE IN THE CUSTODY OF MS. DIANA MORRIS, CLOVIS, NM.
2025-01-31 10:21 | NO | NO | 19950063 | 1995-04-24 | 2332 | CHEYENNE LIGHT FUEL & POWER | 2700 E 5TH STREET | CHEYENNE | LARAMIE | WY | 82001 | 3 | NO | 530 | 1995-02-21 | 0 | 0 | 0 | 0 | 0 | YES | 22 | 30 |  | 19950221 | 130 | 150 | BY TEST | 150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | WELD | GIRTH | STEEL |  | 12 | 0.25 |  |  | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | DAVID MCLINTOCK | 3077782168 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ALTHOUGH THERE WAS A CRACKED WELD, IT HAS NOT BEEN DETERMINED WHETHER IT WASA RESULT OF THE WELD FAILING OR CAUSED BY OUTSIDE FORCES, OTHER SUBSIDENCE OROVERBEARING SOIL CONDITIONS.AT APPROXIMATELY 5:05 A.M., 02/21/1995, A CALLWAS RECEIVED FROM FRONTIER REFINERY REPORTING THE ODOR OF NATURAL GAS. THISWAS INDICATED AS TO BE COMING FROM THE GROUND IN THE VICINITY OF GATE #15. ASERVICEMAN WAS DISPATCHED TO THE SCENE FROM HIS HOME. HE ARRIVED AT 5:25 A.M.HE OBSERVED THE ODOR OF NATURAL GAS AND SAW BUBBLES IN A PUDDLE OF WATER ATTHIS LOCATION. HE REQUESTED ADDITIONAL BE SENT TO ASSIST HIM. HE PERFORMED ALEAK SURVEY IN THE AREA ABOVE A 12" GAS LINE WHICH PARALLELS CAMPSTOOL ROADIN A BORROW DITCH ON THE SOUTH SIDE OF THE STREET. HE DETERMINED THAT THE AREAOF GAS LEAKAGE WAS APPROXIMATELY 8' BY 10', WITH READINGS DIMINISHED ON EACHEND OF THIS AREA. ADDITIONAL CREW MEMEBERS ARRIVED AND EXCAVATION BEGAN. ASUPERVISOR ARRIVED AT THE SCENE AND AFTER CONFERRING WITH THE CREW DETERMINEDTHAT THE LINE SHOULD BE SHUT DOWN BEFORE PROCEEDING WITH EXCAVATIONACTIVITIES. THE REFINERY AND TWO COMMERICAL CUSTOMERS WIERE ADVISED OF THE GASLINE SHUT DOWN. THE SHUT DOWN WAS COMPLETED AFTER APPROXIMATELY 45 MINUTES.EXCAVATION ACTIVITIES WAER SLOWED BY FROZEN SOIL CONIDITIONS. THE PIPE WASEXPOSED AT A PPROXIMATELY 12:15 P.M. ADDITIONAL EXCAVATING WAS REQUIRED TOEXPOSE THE AREA OF LEAK. THIS ACTIVITY BEGAN AT APPROXIMATELY 12:40 P.M. ANEXPLOSION OCCURRED AT ABOUT 1:00 P.M. AS CHEYENNE LIGHT FUEL AND POWEREMPLOYEES WERE WORKING IN THE EXCAVATION AND THE AREA. A STRUCTURE WHICHCONTAINED ELECTRICAL CONTROL EQUIPMENT WAS THE APPARENT SITE OF THE EXPLOSION.THIS BUILDING WAS APPROXIMATELY 10' BY 15' AND CONSTRUCTED OF CONCRETE BLOCK.IT HAD TWO ENTRANCES ON EITHER END OF THE BUILDING AND NO WINDOWS. IT WASLOCATED ABOUT 150' TO THE SOUTHWEST FROM THE AREA OF THE LEAK ON THE GASLINE. THREE CLF&P EMPLOYEES WERE INJURED BY DEBRIS. THEY WERE TAKEN TO ALOCAL HOSPITAL, TREATED FOR MINOR INJURIES AND RELEASED. AN EMPLOYEE OFFRONTIER REFINERY WAS SLIGHTLY INJURED, TREATED AND RELEASED THE SAMEAFTERNOON. DUE TO A REQUEST BY REPRESENTATIVES OF THE WYOMING OCCUPATIONALHEALTH AND SAFETY AGENCY, (WOHSA) , EXCAVATION OF THE GAS LINE WAS DELAYED.AFTER THE REPRESENTATIVES OF WOHSA HAD EXAMINED T HE SCENE THEY ALLOWED WORKTO RESUME. EXCAVATION RESUMED AT 4:00 P.M. AND WAS COMPLETED AT ABOUT 9:00P.M. THE GAS LEAK WAS FOUND TO BE ORIGINATING FROM A CRACKED CIRCUMFERENTIALWELD. A BONNET WAS WELDED AROUND THE LEAK AND SERVICE WAS RESTORED AT 4:00A.M. ON 2-22-95. ADDITIONAL INVESTIGATION TO DETERMINE THE CAUSE WAS DELAYEDBY FRONTIER REFINERY. OFFICIALS OF THE REFINERY DENIED ACCESS TO THEIRPROPERTY FOR THE PURPOSE OF CONDUCTING ADDITIONAL LEAK SURVEY TEST. CLF&P HADMADE REPEATED REQUESTS TO PERFORM THESE TESTS TO ESTABLISH IF NATURAL GAS WASEVEN PRESENT ON THEIR PROPERTY AND ESPECIALLY THE EXPLOSION AREA. LEAK SURVEYTESTS WERE CONDUCTED OUTSIDE THE PERIMETER OF THE REFINERY'S FENCE FORRESIDUAL NATURAL GAS. THOSE TESTS REVEALED VERY LOW LEVELS IN THE IMMEDIATEVICINITY OF THE EXCAVATION. FRONTIER REFINERY REMOVED THE BUILDING FOUNDATIONAND SURROUNDING EXPLOSION DEBRIS BEFORE ALLOWING ACCESS TO TH E REFINERYPROPERTY. AS A RESULT, THE INITIAL TELEPHONE REPORT TO THE DOT WAS MADE AT ATIME WHEN DETAILS WERE UNCERTAIN. IT WAS IN THE NATURE OF A FYI CALL. IT WASTHOUGHT THAT AFTER ADDITIONAL DETAILS COULD BE DEVELOPED THAT IT MAY BERESCINDED. AT THE PRESENT THE INVESTIGATION IS ON-GOING TO DETERMINE WHETHERNATURAL GAS OR THE REFINERY'S SOLVENTS OR BY-PRODUCTS WAS THE CAUSE OF THE
2025-01-31 10:21 | YES | YES | 19950064 | 1995-04-25 | 2392 | CITIZENS GAS & COKE UTILITY | 8733 LOG DUN DRIVE NORTH | INDIANAPOLIS | MARION | IN | 46202 | 1 | NO | 1352 | 1995-04-17 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 45 |  | 19950417 | 25 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | P.E. 2306 | DUPONT | 1979 | 1980 | OTHER | NON SPECIFIED | KERRY T. LOWDERMILK | 3179274681 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DESCRIPTION OF INCIDENT: WE RECEIVED A CALL FROM PIKE TOWNSHIP FIRE DEPARTMENT REPORTING THAT WE HAD A GAS LINE ON FIRE AT 8733 LOG RUN NORTH DRIVE. A CONTRACTOR, HAMMER AND NAILS CONSTRUCTION, HAD BEEN USING A GASOLINE POWERED POST HOLE DIGGER WHEN THEY STRUCK OUR SERVICE LINE. THE ESCAPING GAS IGNITED BURNING THE TWO MEN WHO WERE OPERATING THE MACHINE. STEVEN LEWIS, AGE 37, WAS ADMITTED TO WISHARD HOSPITAL WITH FACIAL BURNS AND POSSIBLE LUNG DAMAGE. ERIC LEWIS, AGE 30 WAS TREATED AND RELEASED. THE FLOW OF GAS WAS STOPPED AND THE FIRE EXTINGUISHED AT 2:39 P.M. THERE WAS NO PROPERTY DAMAGE AS A RESULT OF THE FIRE. THE CONTRACTOR DID NOT CALL FOR A LINE LOCATE PRIOR TO DIGGING.
2025-01-31 10:21 | YES | NO | 19950065 | 1995-04-20 | 15931 | PUBLIC SERVICE CO OF COLORADO | 3489 WEST 112TH CIRCLE | WESTMINSTER | ADAMS | CO | 80030 | 3 | NO | 1100 | 1995-03-13 | 0 | 0 | 1500000 | 1099888.6259 | 2655645.2736 | Null | 2 | 30 |  | 19950313 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | PE2306/2406 | PHILLIPS DRISCO | 1993 | 1993 | UNDER GROUND OR UNDER WATER |  | RIC UTESCH | 3035713922 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-03-10 | YES | 3 | FLAGS & PAINT & SKETCHES | YES |  |  | TV CABLE CONTRACTOR WAS MAKING APPROXIMATELY 400' DIRECTIONAL BORE. AFTER COMPLETING PILOT BORE AND CROSSING PUBLIC SERVICE COMPANY'S 1 1/4" GAS MAIN, THIS CONTRACTOR BEGAN TO BACK BORE WITH A CUTTING AUGER AND PULL 2" PLASTIC CONDUIT FOR CABLE. WHEN THE BACK CUTTING AUGER REACHED THE INTERSECTION WITH PSCO'S 1 1/4" GAS MAIN, THE GAS MAIN WAS BROKEN AND A 11" SECTION OF THE GAS MAIN WAS PULLED AWAY FROM THE MAIN LINE. THE CABLE CONDUIT AND AUGER CONTINUED TO BE PULLED DOWN THE PILOT BORE FOR APPROXIMATLEY 75-100 FEET. THE 11" SECTION OF GAS PIPE WAS RECOVERED LATER, STILL STUCK IN THE AUGER. THIS REMOVAL OF A SHORT SECTION OF PSCO'S 1 1/4" GAS PIPE LEFT AN OPEN END 1 1/4" GAS PIPE WITH 59.5 PSIG BLOWING WIDE OPEN RESULTING IN TWO RESIDENCES BEING DESTROYED BYEXPLOSION AND SEVEN OTHER HOMES BEING DAMAGED BY FIRE AND FLYING DEBRIS.
2025-01-31 10:21 | NO | NO | 19950066 | 1995-04-20 | 14430 | OXFORD NATURAL GAS CO | 4975 COLLEGE CORNER PIKE | OXFORD | BUTLER | OH | 45056 | 3 | NO | 848 | 1995-03-24 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 17 |  | 19950324 | 38 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.238 | 4" |  | 1962 | 1962 | UNDER GROUND OR UNDER WATER |  | MATTHEW M. CLARK | 5135232555 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-01-22 | NO | 2 | FLAGS ON MAIN PAINT ON SL | YES
2025-01-31 10:21 | YES | YES | 19950070 | 1995-05-16 | 22259 | WAVELAND WATER & GAS DEPT, CITY OF | HWY 603 AND LAGAN STREET |  | HANCOCK | MS |  | 1 | NO | 130 | 1995-04-30 | 0 | 1 | 8002 | 5867.5392 | 14166.9823 | Null | 4 | 45 |  | 19950501 | 180 | 180 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | STEPHEN W. LANDRY | 6014679248 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | SIGN MARKER | YES |  |  | THE DRIVER OF A 1975 CAMARO RAN-OFF THE ROAD AND HIT OUR REGULATOR LOCATED AT HWY 603 AND LAGAN STREET.
2025-01-31 10:21 | YES | YES | 19950075 | 1995-05-24 | 13710 | NORTHERN ILLINOIS GAS CO | NE CORNER STATE AND OHIO ST. | JOLIET | WILL | IL | 60435 | 3 | NO | 915 | 1995-05-05 | 0 | 1 | 0 | 0 | 0 | Null | 4 | 18 |  | 19950505 | 56 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | 3RD PARTY DAMAGE | STEEL |  | 2 | 0.154 |  |  | 0 | 1969 | UNDER PAVEMENT |  | MICHAEL MCLAMORE | 7089838888 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 2" MAIN DAMAGED BY THIRD PARTY. DURING EXCAVATION TO REPAIR, GAS WAS IGNITED. OPERATOR'S EMPLOYEE SUFFERED FIRST AND SECOND DEGREE BURNS TO FACE AND HANDS
2025-01-31 10:21 | YES | NO | 19950076 | 1995-05-25 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 102 E. STATE | MANCELONA | ANTRIM | MI | 49659 | 2 | NO | 1255 | 1995-04-23 | 0 | 0 | 1000000 | 733259.0839 | 1770430.1824 | Null | 0 | 0 |  | 19950423 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | 3/4" .90 DEGREE | STEEL |  | 0.75 | 0 |  |  | 0 | 1964 | UNDER PAVEMENT |  | THOMAS P. FUNTSCH | 3135777026 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-04-06 | YES | 3 | PAINT | YES |  |  | CONTRACTOR USING EXCAVATOR PULLED UP SERVICE LINE CAUSING IT TO BREAK AT 90 DEGREE ELL FITTING.
2025-01-31 10:21 | NO | NO | 19950077 | 1995-05-23 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 6306-6308 BACCICH STREET | NEW ORLEANS | ORLEANS | LA | 70112 | 3 | NO | 1124 | 1995-04-26 | 0 | 0 | 60000 | 43995.545 | 106225.8109 | Null | 0 | 6 |  | 19950426 | 75 | 95 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOSEPH A. LALUMIA | 5045953567 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS ESCAPED THROUGH A .5" FUEL LINE VALVE IN THE LAUNDRY ROOM. NO APPLIANCE W AS ATTACHED.
2025-01-31 10:21 | YES | NO | 19950078 | 1995-05-23 | 4350 | ELIZABETHTOWN GAS CO | 28 HOLLYWOOD DRIVE | WOODBRIDGE | MIDDLESEX | NJ | 07095 | 4 | NO | 1545 | 1995-05-13 | 0 | 0 | 160000 | 117321.4534 | 283268.8292 | Null | 3 | 0 |  | 19950513 | 18 | 35 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | DOUGLAS STAEBLER | 9082895000 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | EARTH LANDING ON PIPE | NO |  | NO | 0 |  | NO |  |  | MAIN CRACK IN SERVICE CONNECTION/ TAP. ESCAPE OF GAS RESULTING FROM CRACKIN 4" CAST IRON MAIN.
2025-01-31 10:21 | YES | YES | 19950079 | 1995-05-24 | 2060 | CANTON MUNICIPAL UTILITY | 512 SUGAR HILL | CANTON | MADISON | MS | 39046 | 1 | NO | 150 | 1995-04-23 | 1 | 0 | 25000 | 18331.4771 | 44260.7546 | Null | 0 | 30 |  | 19950503 | 12 | 50 |  | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | DRIP/RISER |  | OTHER | 5/8 TUBING | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DON CHILDERS | 6018592474 | EXTERNALLY | GENERAL CORROSION |  | NO DATA | NO ENTRY | COATED | Null | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | UPON ARRIVAL AT 1:45 AM DEPUTY SPENCER OBSERVED THREE UNITS OF THE CANTON FIREDEPARTMENT ON THE SCENE WITH FIREMEN FIGHTING THE FIRE FROM THE WEST, SOUTH,AND EAST SIDES OF THE BUILDING. DEPUTY SPENCER DISCONNECTED THE ELECTRICALMETER AND OBSERVED THAT THE GAS HAD ALREADY BEEN SHUT OFF BY FIREMEN. THEOCCUPANT, LATER IDENTIFIED AS NOLA DIAMOND, WAS LYING BESIDE THE BED IN THECENTER REAR ROOM. SHE WAS TRANSPORTED TO MADISON GENERAL HOSPITAL WHERE SHEWAS VIEWED BY THE CORONER AND RELEASED TO THE FUNERAL HOME. AFTER REMOVAL OFTHE BODY, FIREMEN RESUMED FIRE FIGHTING EFFORTS AND EXTINGUISHED THE FIRE. THEEXTERIOR OF THE BUILDING INDICATED THE FIRE HAD VENTED THRU THE FRONT AND SIDELIVING ROOM WINDOWNS AND THRU THE ROOF NEAR AT WHAT APPARENTLY WAS A "WHIRLYBIRD" TYPE VENT. ON 5/10/95 THE CASE WAS CLOSED AND RULED ACCIDENTAL. CHARLENEHILL STILL HAS NOT BEEN CONTACTED, HOWEVER HER ACCOUNT IS BELIEVED ONLY TOEFFECT THE CIVIL LITIGATION AND HAVE NO EFFECT ON THE ACCIDENTAL RULING. THISIS SUMMARY OF THE 4 PAGE NARRATIVE SENT TO OPS BY OPERATOR SEE ORIGINAL.
2025-01-31 10:21 | YES | NO | 19950082 | 1995-06-08 | 10037 | WESTERN RESOURCES, INC | 600 CLARK | EMPORIA | LYON | KS | 66860 | 3 | NO | 1345 | 1995-05-07 | 0 | 0 | 150000 | 109988.8626 | 265564.5274 | Null | 0 | 35 |  | 19950507 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 | S201-603 | FISHER | 0 | 1963 | ABOVE GROUND |  | JAMES M. FALLON | 9132341441 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A METER SETTING AT 600 CLARK IN EMPORIA, KANSAS, WAS STUCK BY AN AUTOMOBILERESULTING IN DAMAGE TO A PRESSURE REGULATOR WHICH LED TO HIGHER THAN NORMALDELIVERY PRESSURE TO A CUSTOMER-OWNED DISTRIBUTION SYSTEM.
2025-01-31 10:21 | NO | NO | 19950083 | 1995-06-15 | 13041 | NASHVILLE GAS CO | 1205 BRADLEY DRIVE | FRANKLIN | WILLIAMSON | TN | 37064 | 2 | NO | 1445 | 1995-05-16 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 0 | 22 |  | 19950516 | 40 | 60 | BY TEST | 300 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | HOLE BURNED INLET SWIVEL | STEEL |  | 0 | 0 | METER SET | ROCKWELL | 0 | 1993 | ABOVE GROUND |  | JOHN L. CLARK | 6157341709 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | SECONDARY CAUSATION FROM DAMAGE TO GAS METER AND SUBSEQUENT IGNITION RESULTING FORM LIGHTNING STRIKE TO HOUSE DURING ELECTRICAL STORM.
2025-01-31 10:21 | YES | YES | 19950086 | 1995-06-23 | 14210 | OKLAHOMA NATURAL GAS CO | 204 EAST THIRD | BROKEN BOW | MCCURTAIN | OK | 74728 | 3 | NO | 1708 | 1995-05-20 | 1 | 0 | 0 | 0 | 0 | Null | 2 | 47 |  | 19950520 | 30 | 45 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | NOT GIVEN | 0 | 0 |  | UNIVERSAL | 1960 | 1961 | ABOVE GROUND |  | GERRY LYNN | 9185887600 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THE INCIDENT WAS ON VISIBLE ABOVE GROUND METER SETTING.HOMEOWNER HIT METER AND REGULATOR SETTING WITH CAR RESULTING IN DAMAGE TO REGULATOR CAUSING OVERPRESSURE ON HOUSE PIPING RESULTING IN A FIRE. HOMEOWNER ENTERED HER RESIDENCE THREE TIMES BUT DID NOT COME OUT AFTER THE THIRD ENTRY.
2025-01-31 10:21 | YES | YES | 19950087 | 1995-06-23 | 3110 | DANVILLE GAS DEPT | 400 MEMORIAL DRIVE | DANVILLE |  | VA | 24541 | 3 | NO | 1300 | 1995-05-22 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19950615 | 1 | 25 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | NO DATA |  | VALVE |  | STEEL |  | 6 | 0.602 | SDR/PE3408 | DRISOPIPE 8000 | 1994 | 1995 | OTHER | OPEN TRENCH | BILL KEENER | 8047995280 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | A SIX INCH SERVICE CONNECTION INTO A TWELVE INCH MAIN HAD BEEN MADE. THE LINE WAS BEING PURGED. A SPARK APPARENTLY IGNITED THE PURGING GAS. A FLASH BURNED AN EMPLOYEE WHO WAS LOCATED APPROXIMATELY 25-30 FEET FROM THE PURGING LOCATION.
2025-01-31 10:21 | YES | NO | 19950088 | 1995-07-05 | 18112 | SAN DIEGO GAS & ELECTRIC CO | 3202 VISTA WAY | OCEANSIDE | SAN DIEGO | CA | 92056 | 0 | NO | 1508 | 1995-06-03 | 0 | 0 | 75000 | 54994.4313 | 132782.2637 | Null | 1 | 2 |  | 19950603 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | VALVE |  | STEEL |  | 0.75 | 0 |  |  | 1980 | 1980 | ABOVE GROUND |  | THOMAS SAUNDERS | 6196964962 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A 3/4-INCH GAS RISER WAS BROKEN OFF BELOW THE STOP COCK BY VEHICLE CONTACT. THE ESCAPING GAS WAS IGNITED BY AN UNKNOWN IGNITION SOURCE. THE RESULTING FIRE DESTROYED THREE VEHICLES AND A PALM TREE. A FOURTH VEHICLE AND A RETAINING WALL SUFFERED SMOKE DAMAGE AS WELL.
2025-01-31 10:21 | YES | NO | 19950089 | 1995-06-20 | 2748 | CONSUMERS POWER CO | 750 HAZEN STREET | PAW PAW | VAN BUREN | MI | 49079 | 0 | NO | 1813 | 1995-05-22 | 0 | 0 | 80000 | 58660.7267 | 141634.4146 | Null | 0 | 48 |  | 19950522 | 55 | 60 | BY TEST | 106 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.062 | ASTM 2513 | PHILLIPS | 1979 | 1980 | UNDER GROUND OR UNDER WATER |  | KENNETH L. ELENBAAS | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | MAINTENANCE WORKER DROVE METAL STAKE INTO GROUND IN FLOWER BED AND PUNCTURED5/8" PLASTIC GAS SERVICE. GAS ENTERED BUILDING THROUGH AN OPEN WINDOW IN THEUTILITY ROOM. POSSIBLE SOURCE OF IGNITION WAS A WATER PUMP.
2025-01-31 10:21 | NO | NO | 19950090 | 1995-06-27 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 4603 CANE RUN ROAD | LOUISVILLE | JEFFERSON | KY | 40211 | 3 | NO | 1500 | 1995-05-22 | 0 | 0 | 60000 | 43995.545 | 106225.8109 | Null | 0 | 0 |  | 19950523 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.219 | API5L-GRB | INTERLAKE STEEL | 1979 | 1979 | UNDER PAVEMENT |  | D.A. VOGEL | 5026273722 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ON 05/22/95 AT APPROXIMATELY 3:00 PM, OUR TROUBLE COMPLAINT DESK BEGAN RECEIVING COMPLAINTS OF GAS OUTAGES IN THE CANE RUN ROAD AND CRUMS LANE AREA. APPROXIMATE TIMES: 3:15 PM - A CREW AND THE AREAL SUPERVISOR WERE DISPATCHED TO THE SCENE. IT SOON BECAME APPARENT WATER WAS IN OUR GAS MAINS AND SERVICES SPREAD OVER A LARGE AREA. A WATER LEAK WAS DISCOVERD INFRONT OF THE LAKE DREAMLAND FIRE DEPARTMENT ON CANE RUN ROAD AND LOUISVILLE WATER COMPANY PERSONNEL WERE ON THE SCENE LOCATING VALVES TO TURN OFF A WATER MAIN THAT SERVED A FIRE HYDRANT. 6:00 PM - AFTER THE HOLE WAS EXCAVATED AT THE WATER MAIN LEAK, OUR CREWS FOUND TWO HOLES IN THE WATER MAIN AND A HOLE IN THE GAS MAIN. IT APPEARSTHAT THE WATER PRESSURE (70 PSI) WORE A HOLE IN OUR MEDIUM PRESSURE (30 PSI)GAS MAIN. THE WATER MAIN PASSED PERPENDICULAR UNDER THE GAS MAIN WITH APPROXIMATELY FOUR INCHES OF CLEARANCE AND A STEADY STREAM OF WATER HAD BEEN SHOOTING IN OUR 6 INCH GAS MAIN. THE WATER SOURCE WAS TURNED OFF AND REPAIRS BEGAN ON OUR MAIN. 6:00-9:00 PM - THE DAMAGED SECTION OF GAS MAIN WAS ISOLATED BY TURNING OFF VALVES. THE REPAIRS WERE COMPLETED BY COUPLING IN A SMALL SECTION OF PIPE. THE PURGING PROCESS BEGAN TO CLEAR WATER FROM THE GAS MAIN. SIDE STREETS WERE ALSO ISOLATED BY CLOSING VALVES. BLOWOFFS WERE LOCATED AT THE ENDS OF GAS MAINS AND THE PURGING PROCESS BEGAN ON EACH OF THESE. 9:00PM0 6:00 AM 5/23/95 THE PURGING OPERATION CONTINUED THROUGH THE NIGHT. THE MAINS WOULD CLEAR FOR A PERIOD OF TIME AND THEN START COMING ON WATER AGAIN. 6:00 AM- THE FIRST STREET WAS CLEARED AND CUSTOMERS WERE PUT BACK IN SERVICE. 6:00 AM-9:00PMMAINS AND SERVICE WERE CONTINUALLY PURGED UNTIL THEY CLEARED OF WATER AND ONE BY ONE CUSTOMERS WERE PUT BACK IN SERVICE. A TOTAL OF APPROXIMATELY 259 SERVICES AND APPROXIMATELY 350 CUSTOMERS WERE AFFECTED BY THE OUTAGE. ALL METERSAND REGULATORS WERE CHARGED OUT. 11:00 PM - OUR CREWS CONTINUED TO GET CUSTOMERS BACK IN SERVICE WHO WERE NOT HOME WHEN THEIR STREET WAS RESTORED. CARDSWERE LEFT FOR THE FEW REMAINING CUSTOMERS TO CALL WHEN THEY RETURNED HOME. AJOINT COMMITTEE OF THE LOUISVILLE WATER COMPANY AND LG & E ARE STILL INVESTIGATING TO DETERMINE THE EXACT CAUSE OF THE FAILURE.
2025-01-31 10:21 | YES | YES | 19950091 | 1995-07-06 | 18308 | SIERRA PACIFIC POWER CO | N.VIRGINIA ST & W. 5TH STREET | RENO | WASHOE | NV | 89520 | 4 | NO | 820 | 1995-06-09 | 0 | 5 | 0 | 0 | 0 | Null | 1 | 0 |  | 19950609 | 36 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | API5L GRADE B | UNKNOWN | 0 | 1970 | UNDER GROUND OR UNDER WATER |  | ANNE TAVERNIA | 7026893265 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-04-26 | YES | 2 | YELLOW PAINT | YES |  |  | ON JUNE 9, 1995 AT 8:20 A.M. (PST) TW CONSTRUCTION COMPANY, A LOCAL CONTRACTOR, STRUCK AND RUPTURED A 4" STEEL MAIN WHILE EXCAVATING FOR THE INSTALLATIONOF A SEWER LINE AT THE INTERSECTION OF NORTH VIRGINIA STREET AND WEST 5TH STREET IN RENO, NEVADA. AS A RESULT OF ESCAPING GAS AND ITS PROXIMITY TO OCCUPIED BUILDINGS, LOCAL FIRE OFFICIALS EVACUATED APPROXIMATELY 2,000 PEOPLE FROM NEARBY BUILDINGS AND CONSTRUCTION SITES. SIXTY-ONE PEOPLE WERE TREATED IN AREA HOSPITALS FOR RESPIRATORY PROBLEMS ALLEGEDLY ASSOCIATED WITH NATURAL GAS, AND FIVE OF THOSE PEOPLE WERE ADMITTED TO HOSPITALS FOR ONE TO TWO DAYS. THIRTY-THREE CUSTOMERS WERE CURTAILED OF GAS WHEN THE AFFECTED PORTION OF PIPING WAS ISOLATED AND SHUT DOWN AT APPROXIMATELY 9:30 A.M. (PST). REPAIRS WERE MADETO THE DAMAGED PIPING, AND THE LINE WAS RESTORED AT APPROXIMATELY 2:00 P.M. (PST). CUSTOMER RELIGHTING BEGAN SHORTLY AFTER RESTORATION. THE SAME DAY, AT 2:35 P.M. (PST), ANOTHER BACKHOE OPERATOR FROM TW CONSTRUCTION COMPANY STRUCKA 2" CAPPED SERVICE LINE ON THE SAME MAIN AT A LOCATION APPROXIMATELY 40 FEET FROM THE FIRST DIG-IN LOCATION. THE SAME LINE WAS AGAIN ISOLATED AND SHUTDOWN, AFFECTING THE SAME CUSTOMERS. NO EVACUATIONS OR MEDICAL CONDITIONS RESULTED FROM THE SECOND DIG-IN. THE LINE WAS RESTORED AT APPROXIMATELY 4:00 P.M. (PST) AND CUSTOMER RELIGHTING WAS COMPLETED AT APPROXIMATELY 5:00 P.M. (PST).
2025-01-31 10:21 | YES | YES | 19950095 | 1995-07-13 | 19205 | TERREBONNE PARISH CONSOLIDATED GOVERNMENT | 2247 BRADY ROAD | BAYOU DULARGE | TERREBONNE | LA | 70397 | 3 | NO | 1957 | 1995-06-21 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19950621 | 45 | 80 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | RISER | BODY OF PIPE |  | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | WAYNE ROBICHAUX | 5048736761 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | GRASS WAS BEING CUT WITH A RIDING LAWNMOWER ON VACANT LOT. LAWNMOWER HIT STEEL RISER AND BROKE OFF AT GROUND LEVEL. LAWNMOWER CAUGHT FIRE AND OPERATOR WAS BURNED. HE WAS TRANSFERRED TO THE HOSPITAL FOR TREATMENT.
2025-01-31 10:21 | NO | NO | 19950097 | 1995-07-25 | 22189 | WASHINGTON NATURAL GAS CO | 18404 SE 264 PL | KENT | KING | WA | 98042 | 3 | NO | 1035 | 1995-06-23 | 0 | 0 | 60000 | 43995.545 | 106225.8109 | Null | 1 | 23 |  | 19950623 | 60 | 60 | BY TEST | 98 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | ASTM A53 | RW LYALL | 1991 | 1992 | ABOVE GROUND |  | DAVID AMUNDSON | 2062242042 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | METER SET ASSEMBLY | YES |  |  | MR. M. PETERMAN, NEIGHBOR, WAS USING A BACKHOE TO CLEAR AND GRADE THE BACK YARD AT 18404 SE 264 PL WHEN HE CAUSED THE MOVEMENT OF 2" X 4" TIMBERS WHICH STRUCK AND DAMAGED OUR METER SET ASSEMBLY. THE SERVICE RISER WAS DAMAGED BELOWTHE SHUT OFF VALVE AND MR. PETERMAN COULD NOT CONTROL THE NATURAL GAS FLOW. M. PETERMAN THEN CALLED 911 FROM HIS RESIDENCE AND NOTED UPON HIS RETURN THATTHE NATURAL GAS WAS IGNITED. THE GAS WAS IGNITED BY AN UNDETERMINED IGNITITON SOURCE AND HAD INVOLVED THE MANUFACTURED HOME STRUCTURE. LOCAL FIRE EMERGENCY RESPONSE PERSONNEL RESPONDED AND CONTROLLED THE STRUCTURE FIRE WHILE WNG CREWS STOPPED THE FLOW OF GAS. THE MSA WAS REMOVED AND THE SERVICE WAS TERMINATED AND CAPPED. FIRE DEPARTMENT PERSONNEL ESTIMATED THE MANUFACTURED HOME DAMAGES AT $60,000.
2025-01-31 10:21 | YES | YES | 19950098 | 1995-07-25 | 1800 | BROOKLYN UNION GAS CO | 435 LAKE STREET | BROOKLYN | KINGS | NY | 11223 | 4 | NO | 1909 | 1995-06-24 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 30 |  | 19950625 | 0.25 | 0.4 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 |  |  | 0 | 1929 | OTHER | SEWER MANHOLE | FRANK J. MARCAZZO | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SEWER MANHOLE IGNITIED AS CHILDREN WERE PLAYING WITH FIREWORKS AROUND THE MANHOLE. ONE CHILD WAS HOSPITALIZED WITH BURNS. NATURAL GAS, AS WELL AS HEAVYHYDROCARBONS, WERE CONFIRMED TO EXIST WITHIN SAID MANHOLE. A CRACKED 4 INCH CAST IRON MAIN WAS DISCOVERED AND REPAIRED 95 FEET FROM THE INCIDENT MANHOLE,THE CAUSE OF THE CRACK UNKNOWN.
2025-01-31 10:21 | NO | NO | 19950100 | 1995-08-02 | 3240 | DELMARVA POWER & LIGHT CO | INTERSECTION FOULK & SILVERSIDE ROADS | WILMINGTON | NEW CASTLE | DE | 19803 | 3 | NO | 1235 | 1995-07-20 | 0 | 0 | 60000 | 43995.545 | 106225.8109 | YES | 0 | 30 |  | 19950801 | 35 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0 |  |  | 0 | 1931 | UNDER PAVEMENT |  | PHILIP L. PHILLIPS, JR | 3024293846 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-07-17 | YES | 0 | YELLOW PAINT | YES |  |  | Received information 8-1-95 that estimated property loss could exceed $50,000. Based on that new information, telephonic notice was made immediately. Contractor representative advised of line location on site. THE BURIED 12"DIAMETER STEEL NATURAL GAS DISTRIBUTION MAIN WAS STRUCK AND PENETRATED BY ADIRECTIONAL BORING DEVICE. THE EQUIPMENT WAS BEING OPERATED BY A CONTRACTORWORKING ON A STATE OF DELAWARE HIGHWAY PROJECT. IN RESPONSE TO AN EARLIERREQUEST BY THIS CONTRACTOR, THE MAIN LOCATION HAS BEEN MARKED AND THE LOCATIONHAD BEEN REVIEWED WITH A CONTRACTOR REPRESENTATIVE ON SITE. THE MARKS WERESTILL VISIBLE AT THE TIME OF THE INCIDENT. A TEST HOLE HAS BEEN PREVIOUSLYVACUUM EXCAVATED WITHIN SIX (6) FEET OF THE LOCATION WHERE THE MAIN WAS HIT.
2025-01-31 10:21 | YES | YES | 19950101 | 1995-07-20 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 2104 W. BREEN | KINGSFORD | DICKINSON | MI | 49801 | 3 | NO | 1320 | 1995-07-12 | 0 | 1 | 50000 | 36662.9542 | 88521.5091 | YES | 0 | 0 |  | 19950713 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NONE | POLYETHYLENE PLASTIC |  | 0.625 | 0.062 | ASTM D2513 | PHILLIPS DRISCOPIPE M8000 HDPE | 0 | 1994 | WITHIN/UNDER BUILDING |  | ROGER J. GREGORY | 3135777045 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | INVESTIGATION AND EXTENSIVE LABRATORY TESTING CONFIRMED THE EXISTENCE OFFERMENTATION GAS CONTRIBUTING TO THE INCIDENT. NUMEROUS GROUND/AIR ATMOSPHERICSAMPLES CONFIRMED THE EXISTENCE OF FERMENTATION GAS. THE LABRATORY TESTRESULTS WERE CONVEYED VERBALLY 7/17/1995 AND IN WRITING 7/17/1995 TO THEPUBLIC SAFETY DIRECTOR - KINGSFORD PUBLIC SAFETY DEPARTMENT FOR CONTINUINGINVESTIGATION. SAFETY MEASURES HAVE BEEN INSTITUTED WHILE THE INVESTIGATIONCONTINUES BY PUBLIC OFFICIALS.
2025-01-31 10:21 | NO | NO | 19950103 | 1995-07-27 | 15084 | PALO ALTO, CITY OF | 1001 FOREST AVE. | PALO ALTO | SANTA CLARA | CA | 94303 | 3 | NO | 1515 | 1995-07-19 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 35 |  | 19950720 | 12 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | ABS-1PS | 0.75 | 0.125 |  |  | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | RODGER JENSEN | 4154966932 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-07-10 | YES | 0 | PAINT | YES |  |  | ON JULY 19, 1995 AT 3:15 PM, THE CITY OF PALO ALTO GAS CREW SUPERVISOR (MIKEROGERS) RECEIVED A RADIO CALL FROM A PUBLIC WORKS DEPARTMENT INSPECTOR (DONPETERS) THAT A PLASTIC GAS SERVICE, AT 1001 FOREST AVE., HAD BEEN SEVERED ANDHAD IGNITED. THE PALO ALTO FIRE DEPARTMENT AND GAS CREWS WERE DISPATCHED TOTHE SCENE. THE MAINLINE VALVES WERE TURNED OFF AND THE FIRE WAS EXTINGUISHEDAT 3:50PM. GAS SERVICE WAS DISRUPTED TO 16 HOMES. BY 5:30 PM, A NEW PE SERVICEHAS BEEN INSTALLED TO 1001 FOREST AVE. AND SERVICE WAS RESTORED TO THE AREA.SUBSEQUENT INVESTIGATION BY THE GAS CREW SUPERVISOR REVEALED THAT ACONTRACTOR, SANCHEZ CONSTRUCTION, WAS INSTALLING A NEW SIDEWALK FOR THE CITYOF PALO ALTO, UNDER A PUBLIC WORKS DEPARTMENT CONTRACT. THE CONTRACT SPECIFIEDTHAT THE CONTRACTOR HAD TO SAW-CUT THE TREE ROOTS AND INSTALL ROOT BARRIERSWHERE REQUIRED. THE AREA HAD BEEN MARKED AND THE CONTRACTOR HAD MADE AN EFFORTTO "POTHOLE" THE GAS SERVICE TO NO AVAIL. HE ASSUMED THE GAS SERVICE WASDEEPER THAN HE WAS REQUIRED TO ROOT SAW, HOWEVER, IN ACTUALITY, THE GASSERVICE TOOK A SLIGHT HORIZONTAL TURN IN THE SIDEWALK AREA. WHEN THE ROOT SAWSEVERED THE PLASTIC GAS SERVICE, THE ESCAPING GAS WAS IGNITED, APPARENTLY BYTHE ROOT SAW. THE SAW OPERATOR IMMEDIATELY LEFT THE SAW AND RECEIVED NOINJURIES. HOWEVER, THE ROOT SAW SUSTAINED DAMAGE. THERE WAS NO OTHER PROPERTYDAMAGE OR PERSONAL INJURIES.
2025-01-31 10:21 | YES | YES | 19950109 | 1995-08-14 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | HWY 79 | BETHANY | PANOLA | TX | 71007 | 2 | NO | 1152 | 1995-07-16 | 1 | 0 | 0 | 0 | 0 | YES | 0 | 46 |  | 19950717 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | BROKE AT THREADS | STEEL |  | 0.824 | 0.113 | API-5L A25 | US STEEL CORP | 1986 | 1986 | ABOVE GROUND |  | BUDDY SIMS | 3184294160 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | ABOVE GROUND RISER | NO |  |  | MR. HORACE SONNY LACY WAS MOWING ADJACENT PROPERTY AND HIGHWAY RIGHT-OF-WAY IN THE PROCESS OF MOWING, MR. LACY STRUCK AN ABOVE-GROUND METER SET ASSEMBLY.AT A TIME APPROXIMATING THE TIME OF THE INCIDENT, MR. LACY SUCCUMBED TO A HEART ATTACK. IT IS OUR UNDERSTANDING THAT MR. LACY HAD A HISTORY OF HEART DISEASE. THE CAUSE OF DEATH WAS LISTED AS A HEART ATTACK, BUT THE CAUSE AND EXACTTIME OF THE HEART ATTACK WAS NOT ASCERTAINED.
2025-01-31 10:21 | YES | YES | 19950110 | 1995-08-14 | 18536 | SOUTHWEST GAS CORP | 875 LAKESHORE DRIVE | INCLINE VILLAGE | WASHOE | NV | 89451 | 3 | NO | 1048 | 1995-08-01 | 0 | 1 | 400 | 293.3036 | 708.1721 | Null | 0 | 18 |  | 19950801 | 43 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.151 | ASTM D2513 | DRISCO | 1995 | 1995 | ABOVE GROUND | AREA OF NEW VAULT | MURRAY JOHNSON | 7028311066 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | PROPANE TORCH | NO |  | YES | 3 | PAINT/EXPOSED | YES |  |  | THIS INCIDENT OCCURRED WHEN A PLUMBER ACCIDENTLY BURNED A SOUTHWEST GAS PLASTIC SERVICE LINE WITH HIS TORCH, WHICH RESULTED IN AN UNCONTROLLED ESCAPE OF NATURAL GAS. FURTHER, THE TORCH CAUSED IGNITION OF THE NATURAL GAS, RESULTINGIN MINOR BURNS TO THE ARMS AND FACE OF THE PLUMBER.
2025-01-31 10:21 | NO | NO | 19950111 | 1995-08-15 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 5001 PERLITA DR | NEW ORLEANS | ORLEANS | LA | 70122 | 3 | NO | 205 | 1995-07-24 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 3 |  | 19950724 | 80 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE | FITTING | POLYETHYLENE PLASTIC |  | 1 | 0.119 | ASTM D2513 | UPONOR | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | JOSEPH A. LALUMIA | 5045953567 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AFTER COMPLETING THE WRAPPING OF A SERVICE TEE AND TRANSITION FITTING ON ANEWLY INSTALLED POLYETHYLENE SERVICE, OUR CONTRACT EMPLOYEE HEARD GAS ESCAPING BEHIND HIM WHILE HE WAS CLIMBING OUT OF THE EXCAVATION. BEFORE THE CONTRACT EMPLOYEE COULD COMPLETELY GET OUT OF THE EXCAVATION, THE ESCAPING GAS IGNITIED.THE ESCAPING GAS WAS STOPPED USING OUR EXISTING VALVE SYSTEM AND PINCH OFF EQUIPMENT.
2025-01-31 10:21 | YES | YES | 19950116 | 1995-08-21 | 8070 | INDIANA GAS CO INC | 2202 SOUTH NEBRASKA STREET | MARION | GRANT | IN | 46952 | 3 | NO | 1240 | 1995-07-24 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19950724 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 8.62 | 0.288 |  |  | 0 | 1911 | UNDER PAVEMENT |  | RICHARD L. SLAGLE - MANAGER GAS SYSTEM STANDARDS | 3173210518 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | INDIANA GAS CO. WAS REPAIRING A LEAK ("LEAK #1") ON AN 8" BARE STEEL MAIN AT2202 S. NEBRASKA ST. IN MARION, IN. THE REPAIR WAS BEING MADE BY WELDING A REINFORCING SLEEVE (PUMPKIN) AROUND THE AREA OF LEAKAGE.AS THE WELDER WAS COMPLETING THE FINAL PASS ON THE REINFORCING SLEEVE, A "POP" WAS HEARD BY THE WELDER DOWNSTREAM OF THE REPAIR AND A FIRE ENSUED. THE FIRE IS THOUGHT TO HAVE BEEN IGNITED BY THE WELDING PROCESS. WHEN THE WELDER FELT THE HEAT FROM THE FLAMES, HE EVACUATED THE BELL HOLE. AS HE WAS LEAVINGTHE EXCAVATION, HE WAS SPRAYED WITH A FIRE EXTINGUISHER OPERATED BY A LABORER STANDING ABOVE THE "HOLE". FLAMES THEN ENGULFED THE LABORER. THE WELDER WAS THE ONLY INDIVIDUAL IN THE EXCAVATION AT THE TIME THE FIRE STARTED.THE WELDER EXPERIENCED 2ND DEGREE BURNS TO THE FACE AND ARMS. HE WAS TREATEDAT THE HOSPITAL AND RELEASED. THE LABORER HAD 3RD DEGREE BURNS TO THE ARMS AND LEGS. HE WAS ADMITTED TO A HOSPITAL FOR TREATMENT OF THESE BURNS.THE BANKS OF THE EXCAVATION HAD BEEN CHECKED MINUTES PRIOR TO THE FIRE STARTING. A READING OF FIVE (5) PERCENT LEL WAS OBTAINED UPSTREAM OF THE EXCAVATION. IT IS BELIEVED THAT THIS READING WAS RESIDUAL GAS FROM LEAK #1. NO GAS WAS DETECTED IN THE BANK (DOWNSTREAM) AT ANY TIME DURING THE REPAIR OF LEAK #1.AFTER FURTHER INVESTIGATION, IT APPEARS THAT A "SCAB" FROM THE BOTTOM OF THE8" PIPE AT A POINT 18 FEET DOWNSTREAM OF LEAK #1 (LEAK #2) CAME OFF AT SOME TIME DURING THE REPAIR OF LEAK #1. IGC BELIEVES THAT VIBRATION OF THE PIPE IN PREPARATION FOR THE INSTALLATION OF THE REINFORCING SLEEVE, AS WELL AS THE HEATING AND COOLING OF THE PIPE DURING THE WELDING PROCESS, MAY HAVE CONTRIBUTED TO THE SCAB SEPARATING FROM THE PIPE. IT IS IGC'S CONCLUSION THAT THE GASMIGRATED TO THE BELL HOLE FROM THE LOCATION OF LEAK #2, AND WAS IGNITED BY THE WELDING PROCESS.
2025-01-31 10:21 | NO | NO | 19950117 | 1995-08-24 | 18712 | SUMMERVILLE GAS SYSTEM, CITY OF | HIGHWAY 114 | SUMMERVILLE | CHATTOOGA | GA | 30747 | 1 | NO | 1420 | 1995-08-09 | 0 | 0 | 61294 | 44944.3823 | 108516.7476 | YES | 14 | 50 |  | 19950809 | 80 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.58 | SCHEDULE 40 |  | 0 | 1976 | UNDER GROUND OR UNDER WATER |  | MAX W. REED, MAPS AND RECORDS | 7068570907 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-07-27 | YES | 1 | TEMPORARY STAKES | YES
2025-01-31 10:21 | NO | NO | 19950118 | 1995-08-28 | 15462 | PHILADELPHIA ELECTRIC CO | 765 CHURCHVILLE ROAD | UPPER SOUTHAMPTON | BUCKS | PA | 18966 | 1 | NO | 225 | 1995-07-31 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 43 |  | 19950731 | 65 | 99 | BY TEST | 120 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | SERVICE RISER | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 |  | PLEXCO | 1986 | 1986 | UNDER GROUND OR UNDER WATER | SERVICE RISER | JOSEPH E. HOFFMAN - PROJECT ENGINEER | 6109411529 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIS REPORT IS FOLLOW UP TO THE CALL TO MR. BLANCHARD & CLAIM #302096 (SEE ATTACHED)CORROSION SECTION NOT APPLICABLE DUE TO PLASTIC PIPING.STRUCTURE FIRE AT LOCATION CAUSED DAMAGE TO GAS FACILITIES AS DESCRIBED IN ATTACHMENT.NO CONSTRUCTION DEFECTS - SERVICE PRESSURE TESTED TO 120 PSIG FOR 20 MINUTES.PRESSURE TEST WITNESSED BY FIRE CHIEF MARK SHOWMAKER OF UPPER SOUTHAMPTON FIRE CO.FIRE IS CURRENTLY UNDER INVESTIGATION DUE TO SUSPICIOUS CIRCUMSTANCES. DEPTOF ALCOHOL, TOBACCO AND FIREARMS WAS AT SCENE TO INVESTIGATE. ARSON IS SUSPECTED AND CAUSES ARE UNDER INVESTIGATION. PETE STANLEY, PA PUC SAFETY COORDINATOR EXAMINED METER SET AND RISER ASSEMBLY AND VERIFIED CONCLUSION THAT THE MELT IN THE RISER WAS DUE TO THE HEAT OF THE STRUCTURE FIRE. LATER IN THE DAY THE FIRE MARSHALL CONCLUDED THAT THE FIRE WAS SUSPICIOUS IN NATURE AND THATNATURAL GAS WAS NOT THE CAUSE.ON THE MORNING OF 7/31/95, PECO ENERGY GAS DISPATCH RECEIVED A CALL REGARDING A STRUCTURE FIRE AND POSSIBLE EXPLOSION AT 765 CHURCHVILLE RD., UPPER SOUTHAMPTON, PA. AN ENERGY TECHNICIAN WAS DISPATCHED TO THE LOCATION. UPON ARRIVING AT THE LOCATION, THE STRUCTURE WAS FULLY INVOLVED AND IT WAS DETERMINED THAT THE GAS WAS ESCAPING FROM THE SERVICE RISER PORTION OF THE METER SET. THROUGH THE HELP OF THE LOCAL FIRE COMPANY, HE WAS ABLE TO SQUEEZE OFF THE 1/2"PLASTIC SERVICE TO THE RESIDENCE. ONCE THE FIRE WAS EXTINGUISHED, THE METERSET WAS REMOVED AND THE SERVICE WAS PRESSURE TESTED. THE PRESSURE TEST OF 120 PSIG HELD FOR A PERIOD OF 20 MINUTES AND WAS WITNESSED BY MARK SHOWMAKER, FIRE CHIEF OF UPPER SOUTHAMPTON FIRE COMPANY. THE SERVICE WAS THEN TERMINATEDAT THE PROPERTY LINE BY A DISTRIBUTION CREW. THE METER SET WAS EXAMINED BY PETE STANLEY OF THE PA PUC SAFETY DIVISION WHO VERIFIED THE CONCLUSION THAT THE GAS LEAK WAS DUE TO THE MELT OF THE 1/2" PLASTIC PIPE INSIDE THE 3/4" STEELRISER PIPE. THIS MELT WAS CAUSED BY THE EXTREME HEAT OF THE FIRE WHICH SURROUNDED THE METER SET.FURTHER INVESTIGATION BY THE FIRE DEPARTMENT OFFICIALS REVEALED SUSPICIOUS CIRCUMSTANCES SURROUNDING THE FIRE AND THE FIRE CHIEF CONTACTED THE DEPARTMENTOF ALCOHOL, TOBACCO AND FIREARMS FOR ASSISTANCE. THE FIRE CHIEF CONCLUDED THAT THE FIRE WAS SUSPICIOUS IN NATURE AND NATURAL GAS WAS NOT THE CAUSE.SERVICE PIPE TO 765 CHURCHVILLE RD. WAS LAST LEAK SURVEYED IN JUNE, 1991 ANDTHE MAIN WAS SURVEYED ON 7/15/93. THE METER SET WAS SHUT OFF AND BARREL LOCKED ON 4/28/94 AND WAS FOUND IN THE SAME CONDITION. ELECTRIC WAS ALSO SHUTOFF ON THE SAME DATE AND FOUND IN THE SAME CONDITION.
2025-01-31 10:21 | YES | YES | 19950119 | 1995-09-01 | 15007 | PACIFIC GAS & ELECTRIC CO | 1806 DALLAS | MODESTO | STANISLAUS | CA | 95351 | 3 | NO | 1807 | 1995-08-16 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 3 |  | 19950816 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NOT GIVEN | STEEL |  | 0 | 0 |  | NORDSTROM | 0 | 1950 | ABOVE GROUND |  | JAMES H. POPE | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | A DISGRUNTLED CUSTOMER WHO WAS TURNED OFF FOR NON-PAYMENT ATTEMPTED TO OPEN THE VALVE ON THE RISER TO RE-ESTABLISH SERVICE. THE THIRD PARTY LOOSENED THE NUT ON THE BACK OF THE VALVE CORE, RESULTING IN THE ESCAPE OF GAS. ANOTHER PERSON, DEBBIE RICH, APPROACHED THE AREA AND WAS OVERCOME. SHE WAS TRANSPORTED BY AMBULANCE TO DOCTOR'S HOSPITAL IN MODESTO. THE FLOW OF GAS WAS SUBSEQUENTLY STOPPED, AND THE AREA WAS MADE SAFE.
2025-01-31 10:21 | YES | YES | 19950120 | 1995-09-01 | 22420 | WEST OHIO GAS CO | COLLETT STREET | LIMA | ALLEN | OH | 45805 | 3 | NO | 1120 | 1995-07-28 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 1 |  | 19950728 | 50 | 60 | BY TEST | 150 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | STEEL | POLYETHYLENE PLASTIC | 4 | 0.409 | 8000 | DRISCOPIPE | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | TY V. LOTZ | 4192264827 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR EMPLOYEES, WORKING ON BEHALF OF WEST OHIO GAS (WOG), WERE REPLACING A SECTION OF 6" STEEL MAINLINE WITH 6" PLASTIC. INSTALLATION OF THE NEW SECTION OF MAINLINE HAD BEEN COMPLETED. CONTRACTOR AND WOG EMPLOYEES WERE PURGING AIR FROM THE LINE IN ORDER TO PLACE INTO SERVICE. TWO CONTRACTOR EMPLOYEESWERE IN OR NEAR THE TRENCH DURING THE PURGING PROCESS WHILE THREE WOG EMPLOYEES OPERATED A VALVE AND PROVIDED COMMUNICATION. SHORTLY AFTER THE PURGING HAD BEGUN, A FLASH FIRE OCCURRED INJURING BOTH CONTRACTOR EMPLOYEES. BOTH INJURED EMPLOYEES REQUIRED HOSPITALIZATION. WOG EMPLOYEES WERE NOT INJURED. SOURCEOF IGNITION WAS NOT DETERMINED.
2025-01-31 10:21 | YES | YES | 19950121 | 1995-09-08 | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 611 GENESEE STREET | MEDINA | ORLEANS | NY | 14103 | 3 | NO | 1055 | 1995-08-29 | 0 | 2 | 80000 | 58660.7267 | 141634.4146 | Null | 0 | 6 |  | 19950829 | 0 | 0 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | APPLIANCE CONNECTION | OTHER | NOT GIVEN | OTHER | INSIDE PIPNG | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ANDREW G. SOLOMON | 6077624711 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 2 CUSTOMERS REMODELING HOME NOTICED GAS ODOR IN DWELLING. TRACED ODOR TO KITCHEN AREA WHERE A PIPE FOR A GAS APPLIANCE WAS NOTICED WITHOUT A PLUG AND THE VALVE PARTIALLY OPENED. GAS/AIR MIXTURE IGNITED RESULTING IN AN EXPLOSION,INJURING BOTH PERSONS. NEAR BY NYSEG GAS FITLER RESPONDED TO LOCATION IN 5 MIN. TO MAKE THE DWELLING & SURROUNDING DWELLINGS SAFE. SERVICE INTERPUTED TO 3 DWELLINGS.
2025-01-31 10:21 | YES | NO | 19950123 | 1995-09-15 | 6141 | PUBLIC SERVICE CO OF NEW MEXICO GAS SERVICES | 1026 JEWEL PLACE NE | ALBUQUERQUE | BERNALILLO | NM | 87123 | 3 | NO | 936 | 1995-09-05 | 0 | 0 | 225000 | 164983.2939 | 398346.791 | Null | 1 | 4 |  | 19950905 | 59 | 60 | BY TEST | 105 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.113 | A-25 |  | 0 | 1978 | UNDER PAVEMENT |  | JON W. JONES | 5052414571 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-08-30 | YES | 2 | PAINT | YES |  |  | ON TUESDAY SEPTEMBER 5, 1995, CONDOR CONSTRUCTION OF ALBUQUERQUE, NEW MEXICOWAS INSTALLING NEW WATER LINES ON JEWEL PLACE WHEN A TRACKHOE OPERATOR DUG INTO THE GAS SERVICE LINE FOR 1027 JEWEL PLACE NE. THE SERVICE LINE WAS BENT AND THE TEE AT THE MAIN TIE-IN WAS BENT AND PULLED OFF, CAUSING THE RELEASE OFGAS AT THE MAIN TIE-IN. AT 0905, PNM GAS SERVICES (PNMGS) WAS NOTIFIED BY THEALBUQUERUE FIRE DEPARTMENT THAT THERE WAS A BLOWING GAS LINE AT 1027 JEWEL PLACE NE. AN EMERGENCY TRUCK AND A LINESPOTTER ARRIVED AT THE SCENE AT 0926. AT 0936, SOMETHING IN THE GARAGE AT 1026 JEWEL PLACE IGNITED AND BLEW THE GARAGE DOOR OUT. THE FIRE FROM THE GARAGE IGNITED THE GAS IN THE STREET OVER THEMAIN. THE FIRE ALSO SPREAD TO THE HOUSE. ESTIMATED DAMAGE TO THE HOUSE AND LANDSCAPING WAS REPORTED TO BE $225,000. ESTIMATED COST TO REPAIR THE DAMAGED GAS MAINS SERVICES AND THE COST OF GAS LOST IS $7800. CONSTRUCTION CREWS WEREDISPATCHED AT 0935 AND THE LINE WAS SQUEEZED OFF AT 1040. FOURTEEN HOUSES WERE EVACUATED BY THE AFD. EIGHT HOUSES WERE WITHOUT SERVICE. MAIN REPAIRS AND SERVICE REPLACEMENTS WERE COMPLETED BY 4:30 AM ON SEPTEMBER 6, 1995. RELIGHTSWERE COMPLETED BY ABOUT NOON THAT DAY. ON AUGUST 22, 1995, PNMGS RECEIVED A REQUEST FOR LINE LOCATIONS FOR JEWEL PLACE NE. ON AUGUST 23, 1995, OUR LINESPOTTER SPOTTED ALL SERVICE LINES AND THE MAIN ON THIS STREET. WHEN HE ARRIVED,CONDOR WAS ALREADY SCRAPING ASPHALT. ON AUGUST 31, 1995, WE RE-SPOTTED ALLSERVICES NO LONGER VISIBLE. THE SPOTS FOR THE MAIN WERE STILL VISIBLE. ATTHIS TIME, THE LINESPOT FOR 1027 JEWEL PLACE NE WAS PLAINLY VISIBLE. AT THETIME OF THE INCIDENT, THE LINESPOT AT 1027 JEWEL PLACE NE WAS COVERED WITHDIRT. DAVE KASPAREK OF RISK MANAGEMENT AND BOB CONKLIN OF KELEHER & MCLEODARE CONDUCTING AN INVESTIGATION INTO THE INCIDENT. ALBINO ZUNIGA OF THE STATECORPORATION COMMISSION INTERVIEWED SEVERAL METRO STAFF MEMBERS AND VISITEDTHE SITE ON WEDNESDAY SEPTEMBER 6.
2025-01-31 10:21 | YES | YES | 19950124 | 1995-09-19 | 12878 | MOUNTAINEER GAS CO | 10 STREET, CHARLES AVENUE, ROYAL OAK EST | WHEELING | OHIO | WV | 26003 | 4 | NO | 915 | 1995-09-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 40 |  | 19950905 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | DRISCOPIPE 6500 | PHILLIPS DRISCOPIPE | 1991 | 1992 | UNDER GROUND OR UNDER WATER |  | CARL B. ACKERMAN | 3042340331 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-06-28 | YES | 2 |  | NO |  |  | AT APPROXIMATELY 9:15 AM ON SEPTEMBER 2, 1995, A BACKHOE OPERATOR EMPLOYED BY HOSKINS CONSTRUCTION COMPANY A 2" PLASTIC GAS MAIN BELONGING TO MGC. A MGC CREW CONSISTING OF GARY WOOFTER AND RON TROWBRIDGE AND SUPERVISED BY JORDAN WEBER ARRIVED AT APPROXIMATELY 9:30 A.M. AT THE SCENE OF THE ACCIDENT. IN AN ATTEMPT TO EXCAVATE ENOUGH AREA AROUND THE DAMAGED PIPE SO THE MGC CREW COULD MAKE REPAIRS, THE BACKHOE OPERATOR FOR HOSKINS CONSTRUCTION HIT A BURIED ELECTRIC SERVICE WHICH IGNITED THE ESCAPING GAS. GARY WOOFER WAS APPROXIMATELY 5'AWAY IN THE 3'X6'X30" EXCAVATION WHEN THE FIRE OCCURRED. GARY RECEIVED FIRSTAND SECOND DEGREE BURNS ON BOTH ARMS, BACK AND NECK REQUIRING IMPATIENT HOSPITALIZATION. RON TROWBRIDGE RECEIVED FIRST DEGREE BURNS ON HIS NECK WHICH REQUIRED OUTPATIENT HOSPITALIZATION. FIRE WAS IMMEDIATELY PUT OUT BY FIRE EXTINGUISHER.
2025-01-31 10:21 | NO | NO | 19950125 | 1995-09-18 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 441 CREEK HOLLOW STREET | SHREVEPORT | CADDO | LA | 71115 | 3 | NO | 1015 | 1995-08-19 | 0 | 0 | 1350 | 989.8998 | 2390.0807 | YES | 1 | 35 |  | 19950819 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.103 | ASTM D2513 | UPONOR ALDYL | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | BUDDY SIMS | 3184294160 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | GENE KENT OF G & L IRRIGATION WAS TRENCHING & STRUCK 3/4 PLASTIC SERVICE LINE.GENE KENT OF G & L IRRIGATION WAS TRENCHING IN FRONT YARD OF 441 CREEK HOLLOW ST. TRENCHER STUCK A 3/4 PLASTIC SERVICE LINE TO THIS ADDRESS. GAS ESCAPEDTO THE ATMOSPHERE AND IGNITED FROM TRENCHER OPERATION. NO INJURIES OCURRED. PROPERTY DAMAGES AMOUNTED TO APPROXIMATELY $250.00 TO TRENCHER ONLY. TOTAL DAMAGES WERE $1350.00. ADDRESS WAS ORIGINALLY CALLED IN AS 9314 CORTANA.
2025-01-31 10:21 | YES | NO | 19950126 | 1995-09-19 | 17570 | ROCHESTER GAS & ELECTRIC CORP | 5647 RUNNING BROOK ROAD | FARMINGTON | ONTARIO | NY |  | 0 | NO | 1315 | 1995-08-17 | 0 | 0 | 1000000 | 733259.0839 | 1770430.1824 | Null | 1 | 57 |  | 19950817 | 60 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D2513 | PHILLIPS PETROLEUM CO | 1987 | 1987 | UNDER GROUND OR UNDER WATER |  | GREGORY A. GEORGE | 7167248481 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | ON AUGUST 17, 1995, AT APPROXIMATELY 1400 HOURS A NATURAL GAS EXPLOSION AND SUBSEQUENT FIRE CAUSED EXTENSIVE DAMAGE TO THE TOWNHOUSE COMPLEX AT THE SUBJECT ADDRESS. THE GAS AND ELECTRIC SERVICES TO THE TOWNHOUSE COMPLEX HAD BEEN INSTALLED IN A COMMON TRENCH IN EARLY 1987. OPERATING PRESSURE IN THE GAS SERVICE LINE WAS 60 PSI. AMBIENT TEMPERATURE IN AFTERNOON OF AUGUST 17 WAS APPROXIMATELY 85 DEGREE F. AT THE TIME OF THE INCIDENT, AN RG&E EMPLOYEE WAS WORKING AT THE SITE TO REPAIR AN UNDERGROUND ELECTRIC CABLE (URD) FAULT. BOTH THE CABLE FAULT AND A BREAK IN THE GAS SERVICE TRACER WIRE HAD BEEN PREVIOUSLY LOCATED DURING A STAKE-OUT AND FOUND TO BE IN THE IMMEDIATE VICINITY OF A FENCE POST. THE FENCE CONSISTED OF TWO SECTIONS (EACH APPROXIMATELY EIGHT FEET LONG) AND THREE POSTS WHICH HAD BEEN INSTALLED SOME TIME AFTER THE GAS AND ELECTRIC SERVICE WERE INSTALLED. AFTER THE FAULT WAS LOCATED, A TRENCH APPROXIMATELY 3 1/2' LONG X 1 1/2' DEEP WAS EXCAVATED ON THE EAST SIDE OF THE FENCE. THE ELECTRIC CABLES WERE FOUND BEHIND THE FENCE POST, ON THE WEST SIDE. THE FAULTED AREAS WERE CUT OUT IN PREPARTION FOR SPLICING IN NEW CABLE. DURING THE INSTALLATION OF HEAT SHRINK TUBING MATERIAL OVER THE FIRST COMPLETED CABLE SPLICE USING A PROPANE TORCH FLAME AS A SOURCE OF HEAT, THE EMPLOYEE WAS THROWN DIAGONALLY OUT OF THE TRENCH BY A SUDDEN BLAST AND LANDED ON HIS BACK. WHEN THEEMPLOYEE CLIMBED TO HIS FEET, HE NOTED THAT THE WOODEN FENCE WAS BEGINNING TO BURN AND HEARD A "ROAR". AFTER CALLING FOR HELP FROM HIS TRUCK, HE RETURNEDTO THE SCENE OF THE EXPLOSION, PICKED UP THE PROPANE TORCH (WHICH HE HAD CARRIED WITH HIM AS HE WAS THROWN OUT OF THE TRENCH AND WHICH,AT THIS POINT, WASBURNING) AND THREW IT AWAY FROM THE FIRE ONTO THE LAWN IN THE BACKYARD. HE RECALLED THAT THE FIRE HAD INCREASED IN INTENSITY AT THIS POINT. THE EMPLOYEE STATED REPEATEDLY DURING INTERVIEWS THAT HE NEITHER HEARD NOR SMELLED ESCAPING NATURAL GAS PRIOR TO THE EXPLOSION, NOR DID HE EVER SEE THE GAS SERVICE LINE. AFTER THE FIRE WAS EXTINGUISHED, EXTENSIVE PHOTOGRAPHS WERE TAKEN OF THE ENTIRE SCENE. PIECES OF GAS SERVICE TUBING, ELECTRIC CABLE, SOIL, REMAINS OF TWO FENCE POSTS AND ASSOCIATED CONCRETE, REMNANTS OF HEAT SHRINK TUBING AND ALUMINUM SPLICE CONNECTOR WERE COLLECTED AT THE SCENE OF THE INCIDENT AND BROUGHT TO THE METALLURGICAL LABORATORY FOR QUARANTINE AND EXAMINATION.
2025-01-31 10:21 | YES | NO | 19950127 | 1995-09-22 | 2585 | COLUMBIA GAS OF KENTUCKY INC | NORTH HAMILTON ST. & CHESTNUT | GEORGETOWN | SCOTT | KY |  | 4 | NO | 1145 | 1995-08-15 | 0 | 0 | 70000 | 51328.1359 | 123930.1128 | Null | 0 | 25 |  | 19950815 | 34 | 44 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0 |  |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-07-27 | YES | 3 | PAINT ON GROUND | YES |  |  | A WATER LINE CONTRACTOR STRUCK A 4" STEEL GAS MAIN WITH A ROCK TRENCHER. THEESCAPING GAS IGNITED AND CAUSED APPROXIMATELY $70,000 DAMAGE TO THE TRENCHER. A LINE LOCATE REQUEST HAD BEEN MADE, BUT THE LOCATING CONTRACTOR EMPLOYED BY COLUMBIA GAS OF KENTUCKY, INC. INCORRECTLY MARKED THE GAS LINE.
2025-01-31 10:21 | YES | NO | 19950131 | 1995-10-06 | 12479 | MIDWEST ENERGY INC | 1117 DRUM | HAYS | ELLIS | KS | 67601 | 3 | NO | 2113 | 1995-09-29 | 0 | 0 | 85000 | 62327.0221 | 150486.5655 | Null | 0 | 0 |  | 19950929 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE HOUSE PIPING | OTHER | NOT GIVEN | OTHER PLASTIC | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD J. FRIENDLY | 9136251436 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INSIDE PIPING IN HOUSE - NON JURISDICTIONAL
2025-01-31 10:21 | YES | NO | 19950132 | 1995-10-11 | 4510 | EQUITABLE GAS CO | CARPENTER LN & WATSON DR | NORTH HUNTINGTON | WESTMORELAND | PA | 15642 | 2 | NO | 1025 | 1995-09-05 | 0 | 0 | 120000 | 87991.0901 | 212451.6219 | Null | 1 | 30 |  | 19950905 | 14 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.307 | ASTM-D2513 | DU PONT | 0 | 1976 | UNDER PAVEMENT |  | JOHN S. HORENSKY | 4125535398 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-09-01 | NO | 0 |  | YES |  |  | A NOTICE WAS PLACED ON THE PA ONE-CALL SYSTEM BY THE OUTSIDE PARTY AT 2:20 PM, FRIDAY, SEPTEMBER 1, 1995 (9/4/95 LABOR DAY). HOWEVER, THE INCIDENT OCCURRED BEFORE THE UTILITY HAD SUFFICIENT TIME TO MARK OUT ITS FACILITIES.
2025-01-31 10:21 | YES | NO | 19950137 | 1995-10-24 | 14210 | OKLAHOMA NATURAL GAS CO | 235 SOUTH 49TH WEST AVENUE | TULSA | TULSA | OK | 74127 | 0 | NO | 1255 | 1995-09-25 | 0 | 0 | 180000 | 131986.6351 | 318677.4328 | Null | 2 | 0 |  | 19950925 | 40 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 2 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GERRY LYNN | 9185887600 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DAMAGE RESULTED WHEN A VEHICLE LEFT THE ROADWAY, JUMPED A CURB, CROSSED A SIDEWALK, TRAVELED APPROXIMATELY 15 FEET AND STRUCK THE GAS METER PUSHING IT INTO THE WALL OF THE BUILDING. A FIRE RESULTED WHICH VIRTUALLY DESTROYED THE BUILDING.
2025-01-31 10:21 | YES | YES | 19950138 | 1995-10-27 | 7348 | HOPE GAS INC | BOX 109 DOOLINS RUN | NEW MARTINSVILLE | WETZEL | WV | 26155 | 2 | NO | 1606 | 1995-10-18 | 0 | 1 | 3000 | 2199.7773 | 5311.2905 | Null | 0 | 54 |  | 19951018 | 32 | 60 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD2513 | PLEXCO | 0 | 1984 | UNDER GROUND OR UNDER WATER |  | THOMAS C. YOKUM | 3046238909 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR (J & L DITCHWITCH) WAS IN THE PROCESS OF EXCAVATING A DITCH FOR AWATER LINE USING A DITCH-WITCH TYPE TRENCHER. THE TRENCHER CUT INTO THE GAS PIPELINE CAUSING A RELEASE OF GAS AND IGNITION. THE TRENCHER OPERATOR WAS BURNED AND HOSPITALIZED. WARNING TAPE (6" WIDE) INSTALLED ABOVE PIPELINE AT ALEVEL APPROXIMATELY 12" BELOW GROUND SURFACE.
2025-01-31 10:21 | NO | NO | 19950139 | 1995-10-30 | 15462 | PHILADELPHIA ELECTRIC CO | BROAD & GARFIELD STS | UPPER GWYNEDD TWP | MONTGOMERY | PA |  | 3 | NO | 900 | 1995-09-20 | 0 | 0 | 0 | 0 | 0 | YES | 7 | 20 |  | 19950921 | 650 | 710 | BY TEST | 1200 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NO FAILURE | OTHER | NOT GIVEN | 0.6 | 0.432 |  | U.S. STEEL GROUP | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | JOSEPH E. HOFFMAN | 6109411529 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-09-12 | YES | 1 | PA ONE CALL NOTIFICATION | YES |  |  | CONTRACTOR WORKING TO INSTALL OVERHEAD TRAFFIC SIGNALS AUGERED INTO HIGHPRESSURE GAS LINE THAT SUPPLIES MERCK, SHARP & DOHME. THE LINE WAS MARKEDINCORRECTLY AND REPAIRS TO THE FACILITIES HAVE BEEN MADE IN THE FORM OFREPLACEMENT OF THE DAMAGED SECTION OF PIPE. THERE WERE NO INJURIES ORFATALITIES. THIS REPORT IS FOR INFORMATIONAL PURPOSES ONLY. PA ONE CALL WASPLACED BY CONTRACTOR EXCAVATING IN THE AREA AND UTILITIES WERE MARKED PRIOR TOEXCAVATION. LOCATION WAS INACCURATE.
2025-01-31 10:21 | NO | NO | 19950140 | 1995-10-30 | 12390 | METROPOLITAN UTILITIES DISTRICT | 4522 SO. 48TH STREET | OMAHA | DOUGLAS | NE | 68102 | 2 | NO | 1604 | 1995-10-16 | 0 | 0 | 35000 | 25664.0679 | 61965.0564 | YES | 0 | 35 |  | 19951016 | 7 | 7 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | FUEL LINE | JOINT | THREADED | OTHER | BLACK IRON | 1.25 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DONALD D. BLOCKER | 4024498211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | PROPERTY OWNER HIRED CONTRACTOR TO DO MASON WORK ON PROPERTY INCLUDING REMOVAL OF CONCRETE PARKING AREA ADJACENT TO INVOLVED STRUCTURE. AS CONTRACTOR REMOVED CONCRETE PARKING AREA WITH FRONT LOADER, CONCRETE DEBRIS WAS PUSHED UP AGAINST SOUTH SIDE OF INVOLVED STRUCTURE. TWO NATURAL GAS FUEL LINES EXITED THE SOUTH SIDE OF THE STRUCTURE ABOUT 8" ABOVE GROUND AND THEN WENT UNDER GROUND. CONCRETE DEBRIS WAS PUSHED UP AGAINST THOSE FUEL LINES SEVERING ONE OF THELINES IN THE BASEMENT. THE PROPERTY OWNER NOTIFIED THE GAS COMPANY OF A SERIOUS GAS LEAK AT 1557 HRS. AT 1604 HRS. AN EXPLOSION WAS REPORTED. THE GAS SERVICE ENTERED THE INVOLVED STRUCTURE FROM THE EAST AND SUPPLIED TWO GAS METERSIN THE BASEMENT. THE INVOLVED FUEL LINE EXTENDED FROM THE METERS OUT THE SOUTH SIDE OF THE STRUCTURE. THE PROPERTY OWNER NOR THE CONTRACTOR HAD REQUESTEDUTILITY LOCATIONS. THE SUBJECT FUEL LINES HAD BEEN DISCUSSED BY THE OWNER AND CONTRACTOR. THE CONTRACTOR UNDERSTOOD THE FUEL LINES WERE DEAD. THE OWNER STATES HE HAD ADVISED THE CONTRACTOR THEY WERE LIVE BUT WERE TO BE CUT OFF. A " MISUNDERSTANDING."
2025-01-31 10:21 | NO | NO | 19950142 | 1995-11-06 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 7201 MIDLOTHIAN TURNPIKE | RICHMOND | CHESTERFIELD | VA |  | 3 | NO | 515 | 1995-10-12 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 0 | 30 |  | 19951012 | 20 | 30 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | WILLIAM J. GALLI | 8042308301 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 05:15, THURSDAY, OCTOBER 10, 1995 THE CHESTERFIELD COUNTY FIRE DEPARTMENT NOTIFIED THE CITY OF RICHMOND DEPARTMENT OF UTILITIES NIGHT DISPATCHER OF A GAS FED FIRE AT CLOVERLEAF MALL SHOPPING CENTER AT 2201 MIDLOTHIAN TURNPIKE. OUR DISPATCHER IMMEDIATELY NOTIFIED OUR NIGHT SUPERVISOR, WHO RESPONDED WITHIN 30 MINUTES TO THE SITE. WITHIN ANOTHER 15 MINUTES THE GAS CONTROL VALVES WERE CLOSED AND THE FIRE WENT OUT (APPROXIMATELY 0600 HRS). WHILEINVESTIGATION CONTINUES, OUR INTITIAL COLLECTION OF FACTS HAS INDICATED THAT:A MALL CUSTODIAN PUSHED A NUMBER (4 OR 5) LARGE PLASTIC TRASH RECEPTACLES OUT OF THE BUILDING AND POSITIONED THEM IMMEDIATELY NEXT TO OR AGAINST A BANK OF SEVEN GAS METERS. THIS HAPPENED APPROXIMATELY 0220 HOURS. SOMETHING CAUSEDTHIS TRASH TO IGNITE. WHEN THE TRASH IGNITED AND INTENSIFIED IT WAS IMMEDIATELY BELOW THE BANK OF METERS. THIS CAUSED THE METER OR METERS TO MELT AND RELEASE GAS WHICH ALSO IGNITED. THE INTENSITY OF FLAMES FURTHER CAUSED THE 1 1/2" PRESSURE REGULATOR TO MELT, RELEASING THE MAIN FLOW OF BURNING GAS (AT APPROXIMATELY 20 PSI). THE CHESTERFIELD FIRE AND POLICE ARSON INVESTIGATION UNITHAS ARRESTED AN INDIVIDUAL AND CHARGED HIM WITH ARSON FOR DELIBERATELY STARTING THIS FIRE. OUR INVESTIGATION REVEALED NO MECHANICAL MALFUNCTION OF OUR EQUIPMENT. IT WAS WITHIN A SECURED AREA NOT OPEN TO THE PUBLIC. WE ARE SATISFIEDTHAT THE INCIDENT WAS CAUSED BY A DELIBERATE ACT.
2025-01-31 10:21 | YES | YES | 19950143 | 1995-11-06 | 18532 | SOUTHERN UNION GAS CO | 9600 BLOCK OF KENWORTHY | EL PASO | EL PASO | TX | 79924 | 3 | NO | 1250 | 1995-10-16 | 0 | 1 | 10000 | 7332.5908 | 17704.3018 | Null | 0 | 20 |  | 19951016 | 28 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.409 | SDR11-3408 | PLEXCO | 1990 | 1990 | OTHER | EXCAVATION SITE | JOHN SEDILLO | 9155446300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A THREE-MAN CREW WAS WORKING ON OFFSETTING A 4" PE GAS MAIN IN THE 9600 BLOCKOF KENWORTHY, BEHIND COHEN STADIUM. THE GAS MAIN WAS ACCIDENTALLY PUNCTUREDWITH THE BACKHOE. WITHIN 30 SECONDS THE GAS IGNITED CAUSING FIRST, SECOND ANDTHIRD DEGREE BURNS TO THE FACE, ARMS, AND HANDS OF THE BACKHOE OPERATOR. A 4"POLYETHYLENE MAIN WAS ACCIDENTALLY HIT AND PUNCTURED WHILE TRENCHING WITH ABACKHOE. GAS IGNITED.
2025-01-31 10:21 | NO | NO | 19950144 | 1995-11-06 | 30740 | AMERIGAS PROPANE, L.P. | 724 WEST LINE STREET | BISHOP | INYO | CA | 93514 | 1 | NO | 2230 | 1995-10-30 | 0 | 0 | 60000 | 43995.545 | 106225.8109 | Null | 2 | 30 |  | 19951031 | 10 | 15 | BY TEST | 15 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | STEEL |  | 0.75 | 0.113 |  |  | 1990 | 1990 | ABOVE GROUND |  | MIKE WALTERS | 3155982806 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | MOTOR VEHICLE ACCIDENT- VEHICLE FAILED TO NEGOTIATE TURN - VEHICLE STRUCK BUILDING "DAYS INN" HIT AND RUN - IMPACT AT POINT OF SECOND STAGE REGULATOR - BROKEN PIPELINE AND UPSTREAM OF SECOND STAGE REGULATOR - WITNESS SMELLED GAS CONTACTED FIRE DEPARTMENT. AMERIGAS EMPLOYEE, MEMBER OF FD HEARD CALL AND RESPONDED - TURNED OFF TANK - MOMENT OR SO LATER FUEL IGINITED IN LAUNDRY ROOM - SOURCE WATER HEATER - EXTENSIVE STRUCTURAL DAMAGE IN AREA OF LAUNDRY ROOM BUILDING EVACUATED. TELEPHONE REPORT TO MR. HUDSPATH #312616 10-31-95 14:26.
2025-01-31 10:21 | YES | YES | 19950147 | 1995-11-16 | 15007 | PACIFIC GAS & ELECTRIC CO | 5311 N. DIANA | FRESNO | FRESNO | CA |  | 3 | NO | 1330 | 1995-10-11 | 0 | 1 | 1000 | 733.2591 | 1770.4302 | Null | 0 | 54 |  | 19951011 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC | DIG IN | 1.25 | 0.166 | PE 2406 | UPONOR | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | WILLIAM R. BLASTIC | 4159734903 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ELECTRIC LIGHTING CONTRACTOR DUG INTO MAIN, WHICH WAS AT A DEPTH OF 48 INCHES. EMPLOYEE LAID ON GROUND AND REACHED DOWN INTO HOLE TO PREPARE PIPE TO INSTALL PLASTIC SQUEEZERS. FELLOW EMPLOYEE NOTICED THE OTHER SLUMPED IN THE HOLE AND PULLED HIM OUT. EMPLOYEE EXPERIENCED ASPHYXIA FROM THE BLOWING GAS. EMPLOYEE WAS GIVEN CPR AND REVIVED. HE WAS THEN TRANSPORTED TO THE HOSPITAL VIA AMBULANCE, WHERE HE REMAINED OVERNIGHT FOR OBSERVATION. EMPLOYEE REQUIRED INPATIENT HOSPITALIZATION AFTER BEING OVERCOME BY GAS.
2025-01-31 10:21 | YES | YES | 19950148 | 1995-11-16 | 10310 | KNOXVILLE UTILITIES BOARD | 9000 BLK OF GEORGE WILLIAMS RD | KNOXVILLE | KNOX | TN | 37922 | 3 | NO | 1014 | 1995-10-18 | 0 | 1 | 150000 | 109988.8626 | 265564.5274 | Null | 0 | 54 |  | 19951018 | 33 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.39 | PE 2406 | PHILLIPS-DRISCO PIPE | 1994 | 1994 | UNDER GROUND OR UNDER WATER |  | MICHAEL BEST | 4235948162 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | GAS FACILITIES HAD BEEN PREVIOUSLY MARKED IN AREA AT THE REQUEST OF ANOTHER EXCAVATOR - NO REQUEST AT THIS SITE BY THIRD PARTY CAUSING DAMAGE. A 4-INCH POLYETHYLENE GAS MAIN WAS DAMAGED BY ACTION OF THIRD PARTY WHILE INSTALLING AN18-INCH STORM DRAIN. WHILE A KUB LEAK REPAIR CREW WAS MAKING THE REPAIR, ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE. A 4 INCH POLYETHYLNE GAS MAIN WASDAMAGED BY ACTION OF A 3RD PARTY WHILE INSTALLING AN EIGHTEEN INCH STORM DRAIN. WHILE THE KUB LEAK REPAIR CREW WAS MAKING THE REPAIR, ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE. THE KUB LEAK REPAIR CREW WAS DISPATCHED THE REPORT OF A GAS MAIN BLOWING AT 10:12 A.M. KUB'S AREA CONSTRUCTION SUPERVISOR ALSOHEARD THE INITIAL DISPATCH. THE AREA CONSTRUCTION SUPERVISOR RADIOED FOR A NEARBY KUB GAS CONSTRUCTION CREW AND ENGINEERING FIELD SERVICES REPRESENTATIVETO RESPOND. ALL KUB PERSONNEL AND EQUIPMENT RESPONDED TO THE SITE ALMOST SIMULTANEOUSLY AT APPROXIMATELY 10:27 A.M. AFTER ASSESSING THE SITUATION, KUB PERSONNEL CLOSED A VALVE ELIMINATING THE ONE OF THE TWO GAS FEEDS AND ENTERED THE TRENCH AT APPROXIMATELY 10:35 A.M. TO INSTALL A TEMPORARY LEAK REPAIR CLAMP. AT APPROXIMATELY 10:45 A.M. IGNITION OF THE GAS OCCURRED. PERSONNEL EXITED THE TRENCH WHILE EXTINGUISHERS WERE DISCHARED. SIMULTANEOUSLY INJURED PERSONNEL WERE CARED FOR, REPORT OF THE INCIDENT WAS MADE TO KUB DISPATCH; AND VALVE LOCATION INFORMATION NEEDED TO SHUT OFF THE GAS SUPPLY WAS DISPATCHED. APPROPRIATE VALVES WERE CLOSED TO EXTINGUISH THE NATURAL GAS FIRE AT 11:05 A.M.
2025-01-31 10:21 | YES | YES | 19950149 | 1995-11-27 | 18536 | SOUTHWEST GAS CORP | 286 B HARMON AVENUE | LAS VEGAS | CLARK | NV | 89109 | 3 | NO | 30 | 1995-11-05 | 0 | 2 | 500000 | 366629.542 | 885215.0912 | Null | 1 | 15 |  | 19951105 | 30 | 33 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 0.84 | 0.0652 | STD.PVC | KRALOY | 1965 | 1965 | UNDER GROUND OR UNDER WATER |  | JOHN B. CLAYTON | 7023652102 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE | LANDSLIDE/WASHOUT | NO |  | NO | 0 |  | NO |  |  | AN EXPLOSION AND FIRE OCCURRED IN AN EIGHT-UNIT, TWO-STORY APARTMENT STRUCTURE AT THE GRAND PLAZA APARTMENTS LOCATED AT 286 E. HARMON AVENUE. ACTUAL CAUSE OF THE INCIDENT IS UNKNOWN. PROBABLE CAUSE WAS AN ACCUMULATION OF GAS, EITHER METHANE SEWER GAS, NATURAL GAS OR A COMBINATION THEREOF IN THE UPPER REAR APARTMENT. A FAILURE OCCURRED IN THE BUILDING SEWER SYSTEM UNDER THE STRUCTURE PERMITTING SEWER GAS TO ENTER AN UPPER REAR APARTMENT. A NATURAL GAS LEAK WAS FOUND OUTSIDE IN A SOUTHWEST GAS ONE-HALF INCH PLASTIC POLYVINYL CHLORIDE (PVC) SERVICE PIPE LOCATED IN THE REAR OF THE STRUCTURE. THE NATURAL GAS LEAKWAS CAUSED BY EXTERNAL DAMAGE DUE TO SETTLEMENT OF THE EARTH IN THE VICINITYOF THE METER SET ASSEMBLY. EARTH SETTLEMENT FROM WASHOUT DUE TO POSSIBLE WATERLINE BREAK.
2025-01-31 10:21 | YES | NO | 19950156 | 1995-12-01 | 12684 | MONTANA - DAKOTA UTILITIES CO | 614 S. 31ST STREET | BILLINGS | YELLOWSTONE | MT | 59101 | 3 | NO | 452 | 1995-11-01 | 0 | 0 | 212000 | 155450.9258 | 375331.1987 | Null | 0 | 2 |  | 19951101 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | JOINT | THREAD | STEEL |  | 0.75 | 0 | SCHED 40 |  | 0 | 0 | ABOVE GROUND |  | RONALD E. BLUM | 7012227924 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | INVESTIGATION SHOWED THAT INITIAL EXPLOSION WAS NOT CAUSED BY LEAKAGE FROM JURISDICTIONAL PIPING. EXPLOSION OF UNKNOWN ORIGIN INSIDE BUILDING COLLAPSED WALL ON METER SET CAUSING LEAKAGE.
2025-01-31 10:21 | YES | NO | 19950157 | 1995-12-05 | 6920 | GULF STATES UTILITIES CO | 13310 PALOMINO STREET | BATON ROUGE | EAST BATON ROUGE | LA | 70739 | 2 | NO | 808 | 1995-11-28 | 0 | 0 | 100000 | 73325.9084 | 177043.0182 | Null | 0 | 55 |  | 19951128 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | ASTM D 2513 | PLEXCO | 1976 | 1976 | UNDER PAVEMENT |  | ALBERT A. GABRIEL | 5043543111 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-11-13 | YES | 3 | MARKING PAINT | YES |  |  | ON NOVEMBER 28, 1995, A BARBER BROTHERS CONSTRUCTION ROAD REPAIR CREW, RUPTURED AN UNDERGROUND NATURAL GAS SERVICE LINE OWNED AND OPERATED BY GULF STATESUTILITIES. THIS WAS A 1-INCH PLASTIC LINE SERVING A SINGLE RESIDENCE AT 13310 PALOMINO STREET IN BATON ROUGE, LOUISIANA. THE LINE WAS PROPERLY MARKED BY GULF STATES UTILITIES PERSONNEL PRIOR TO ROAD REPAIR WORK. WHEN THE LINE RUPTURED, AN UNKNOWN SOURCE IGNITED THE ESCAPING GAS WHICH CAUSED SEVERE DAMAGE TO THE CMI RECLAIMER 333, OPERATED BY BARBER BROTHERS CONSTRUCTION. THERE WERENO REPORTED INJURIED OR DAMAGE TO PUBLIC PROPERTY. THE ESTIMATED DAMAGE TO THE CMI RECLAIMER IS $100,000. DAMAGE TO GULF STATES UTILITIES FACILITIES WAS MINIMAL.
2025-01-31 10:21 | NO | NO | 19950158 | 1995-12-06 | 18484 | SOUTHERN CALIFORNIA GAS CO | INTERSTATE 5 RIDGEROUTE | EL TORO | ORANGE | CA | 92630 | 3 | NO | 1347 | 1995-11-08 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 8 | 55 |  | 19951127 | 43 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | STEEL |  | 6.625 | 0.188 | 41-06 |  | 0 | 1979 | UNDER GROUND OR UNDER WATER |  | DONALD K. MYERS | 2132443218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1992-02-12 | YES | 2 | PAINT | YES |  |  | AT 1:57 PM, ON WEDNESDAY, NOVEMBER 11, 1995, ORTIZ ENTERPRISES INC. WAS EXCAVATING IN INSTALL A NOISE ABATEMENT WALL ADJACENT TO THE NORTHBOUND LANES OF THE SANTA ANA FREEWAY (1-5), WHEN THEY STRUCK AND DAMAGED A SIX INCH GAS MAIN. THEY WERE WORKING FOR CALTRANS AND WERE EXCAVATING WITH A D-6 TRACK DOZER. THEY HAD NOTIFIED USA TO REQUEST SUBSTRUCTURE LOCATION AS REQUIRED; THE GAS COMPANY RESPONDED AND CORRECTLY LOCATED THE LINE. THE LINE LOCATION WAS MARKEDWITH PAINT AND STAKES. THE COMPANY ALSO "POTHOLED" THE MAIN TO VISUALLY VERIFY THE LOCATION AND DEPTH. THIS INFORMATION WAS PROVIDED TO CALTRANS AND TO THE CONTRACTOR. DUE TO THE BLOWING GAS, SOME NORTHBOUND LANES OF THE SANTA ANAFREEWAY WERE CLOSED. EIGHTY PERSON WERE EVACUATED FROM NEAR-BY STRUCTURES. VARIOUS NEWS MEDIA AND THE RED CROSS WERE ON SCENE. BILL DOUGLAS, PROJECT SUPERINTENDENT FOR ORTIZ CONSTRUCTION STATED THAT CALTRANS CHANGED THE LOCATION OF THE SOUND WALL EIGHT FEET TO THE EAST, BUT THEY DID NOT NOTIFY THE GAS COMPANY OF THIS CHANGE. HE FUTHER STATED THAT "WE SCREWED UP" (MEANING HIS COMPANY). TO CONTROL THE BLOWING GAS, THREE PINCHES WERE REQUIRED. 2-6 INCH STEEL AND 1-3 INCH PLASTIC. THE DAMAGE WAS THE RESULT OF CALTRANS CHANGING THE LOCATION OF THE SOUND WALL WITHOUT NOTIFYING THE GAS COMPANY OF THIS CHANGE SO THAT THE LINE COULD BE RE-LOCATED AND / OR RE-POTHOLED AS NECESSARY. STATEMENTS BY THE CONTRACTOR SUPERINTENDENT SUPPORT THIS CONCLUSION AND INDICATE AN ACCEPTANCE OF RESPONSIBILITY.
2025-01-31 10:21 | YES | YES | 19950159 | 1995-12-06 | 2412 | CITIZENS GAS UTIL DIST | HIGHWAY 52 AREA | ELGIN | SCOTT | TN |  | 2 | NO | 805 | 1995-11-05 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 1 |  | 19951106 | 150 | 400 | BY TEST | 675 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NO FAILURE | STEEL | POLYETHYLENE PLASTIC | 2 | 0.154 |  |  | 0 | 1995 | ABOVE GROUND |  | MARK J. BOATNER | 4235694457 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON SUNDAY, NOVEMBER 5, 1995, AT APPROXIMATELY 8:00 A.M., DARRYL CROSS AND DENNIS GOAD WENT TO THE METER STATION NEAR ELGIN TOINVESTIGATE AND CORRECT A LOW PRESSURE PROBLEM ON THE DISTRIBUTION SYSTEM IN THE ELGIN/HIGHWAY 52 AREA. THE METERING STATION NEAR ELGIN IS DESIGNED TO ALLOW NATURAL GAS TO FLOW FROM THE HIGH PRESSURE 6 INCH MAIN OF CITIZENS GAS INTO THE LOW PRESSURE DISTRIBUTION SYSTEM OF CITIZENS GAS IN THE ELGIN/HIGHWAY 52 AREA. FOR A DIAGRAM OF THEMETERING STATION, SEE EXHIBIT "A" ATTACHED. THE NATURAL GAS TRAVELS FROM THE6 INCH MAIN THROUGH A 4 INCH FLANGED VALVE, WHICH IS LOCATED ON TOP OF THE GROUND. THE NATURAL GAS THEN FLOWS VERTICALLY THROUGH A STEEL TRANSITION INTO 2 INCH DIAMETER STEEL PIPE. THE NATURAL GAS THEN FLOWS THROUGH A 90 DEGREE ELBOW AND THEN TRAVELS HORIZONTALLY THROUGH A 2 INCH NIPPLE WITH A GAUGE PORT, THROUGH A PRESSURE REGULATOR, THROUGH A 2 INCH NIPPLE WITH A GAUGE PORT, THROUGH A METER STOP VALVE, AND THROUGH A DIAPHRAGM METER. THE NATURAL GAS, UPON LEAVING THE METER, THEN FLOWS THROUGH A METER STOP VALVE, A CHECK VALVE, AND SAFETY RELIEF VALVE, THEN THROUGH A 90 DEGREE ELBOW DOWN VERTICALLY INTO PIPEBURIED UNDER THE GROUND. UPON ARRIVING AT THE SCENE, DARRYL CROSS AND DENNISGOAD APPARENTLY SHUT OFF THE 4 INCH FLANGED VALVE, PREVENTING GAS FLOW INTO THE METERING STATION. THE MEN THEN REMOVED THE REGULATOR AND INSPECTED IT FORICE FORMATION AND BLOCKAGE ON THE REGULATOR OFFICE. ONE OF THE MEN PLACED THE REGULATOR INSIDE ONE OF THE TRUCKS IN ORDER TO THAW THE ICE FORMED ON THE ORIFICE. ONE OF THE MEN THEN CONNECTED 2 INCH DIAMETER PIPE MEASURING APPROXIMATELY 30 INCHES IN LENGTH ONTO THE METER RUN WHERE THE REGULATOR WAS PREVIOUSLY INSTALLED. ON THE END OF THE 2 INCH DIAMETER PIPE, A 90 DEGREE ELBOW WAS ATTACHED, AND THEN A SHORT SECTION OF PLASTIC PIPE. THIS 2 INCH PIPE ASSEMBLY WAS ATTACHED SO THAT THE "L" ASSEMBLY WAS PARALLEL TO THE GROUND. THE PIPE ASSEMBLY WAS ATTACHED IN ORDER TO DIVERT THE FLOW OF NATURAL GAS AWAY FROM A NEARBY HOUSE AND AWAY FROM THE OPERATOR OF THE 4 INCH FLANGED VALVE. DARRYL CROSS THEN POSITIONED HIMSELF OVER THE 4 INCH FLANGED VALVE AND PLACED A PIPE WRENCH ON THE VALVE STEM IN ORDER TO OPERATE THE VALVE. THE PROCEDURE INITIATEDBY MR. CROSS WAS USED TO ALLOW NATURAL GAS TO FLOW THROUGH THE 4 INCH FLANGED VALVE AND OUT THE 2 INCH PIPE ASSEMBLY IN ORDER TO CLEAR THAT SECTION OF PIPE OF ANY OBSTRUCTIONS SUCH AS AN ICE FORMATION IN THE PIPE. UPON SO DOING AND UNFORESEEABLE SURGE OF NATURAL GAS FLOWED THROUGH THE 4 INCH FLANGED VALVE AND OUT THE 2 INCH PIPE ASSEMBLY, CAUSING THE 2 INCH PIPE ASSEMBLY TO SPIN OUT OF CONTROL. WHEREUPON, THE 2 INCH PIPE ASSEMBLY HIT MR. CROSS IN THE HEAD, RENDERING HIM UNCONSCIOUS. THE 2 INCH PIPE ASSEMBLY THEN HIT DENNIS GOAD IN THE PELVIC AREA, KNOCKING HIM TO THE GROUND. TIM LOGGINS IMMEDIATELY SHUT OFF THE GAS FLOWING THROUGH THE 4 INCH FLANGED VALVE AND RENDERED FIRST AID TO THE INJURED EMPLOYEES. A NEIGHBOR SUMMONED THE AMBULANCE SERVICE AND THE SCOTT C OUNTY SHERIFF'S DEPARTMENT. DARRYL CROSS LATER DIED AT THE UNIVERSITY OF TENNESSEE MEDICAL CENTER, NEVER HAVING REGAINED CONSCIOUSNESS. DENNIS GOAD WAS TREATED AT THE SCOTT COUNTY HOSPITAL AND RELEASED. DARRYL CROSS HAS BEEN EMPLOYED BY CITIZENS GAS FOR NEARLY 27 YEARS. DENNIS GOAD HAS BEEN EMPLOYED BY CITIZENS GAS FOR APPROXIMATELY 10 YEARS. THIS INCIDENT STATEMENT HAS BEEN PREPARED BASED UPON INTERVIEWS WITH THE WITNESSES, AN INSPECTION OF THE ACCIDENT SCENE, AND A REVIEW OF THE BUSINESS RECORDS OF CITIZENS GAS UTILITY DISTRICT OF SCOTT AND MORGAN COUNTIES.
2025-01-31 10:21 | YES | YES | 19950160 | 1995-12-07 | 12582 | MISSISSIPPI VALLEY GAS | 1703 OLD MARION ROAD | MERIDIAN | LAUDERDALE | MS | 39301 | 3 | NO | 747 | 1995-11-22 | 0 | 1 | 6000 | 4399.5545 | 10622.5811 | Null | 1 | 13 |  | 19951122 | 25 | 34 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0 |  |  | 0 | 1940 | WITHIN/UNDER BUILDING |  | PAUL D. NOEL | 6019616860 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | YES | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE OCCUPANT WAS ATTEMPTING TO LIGHT A BATHROOM HEATER WHEN THE FLASH FIRE OCCURRED AND WAS BURNED ON THE FACE AND ARMS. FIRE DAMAGE TO THE BUILDING WAS ESTIMATED TO BE $6,000.00. LEAKAGE ON THE SERVICE LINE WAS LOCATED AT THE EDGE OF A FOUNDATION FOOTING WHICH SUPPORTED A BRICK PILLAR.
2025-01-31 10:21 | YES | NO | 19950161 | 1995-12-13 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 1040 WOODSIDE AVENUE | ELLWOOD CITY | LAWRENCE | PA | 16117 | 2 | NO | 850 | 1995-11-11 | 0 | 0 | 75000 | 54994.4313 | 132782.2637 | Null | 0 | 56 |  | 19951111 | 19 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION | STEEL |  | 1.25 | 0.14 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | METER WAS EXPOSED | YES |  |  | AN 1.25" STEEL METER RISER SEPARATED FROM AN 1.25" COMPRESSION ELBOW ALLOWING ESCAPING GAS TO ENTER THROUGH THE FOUNDATION WALL OF THE RESIDENCE. GAS WASIGNITIED FROM AN UNDETERMINED SOURCE RESULTING IN AN EXPLOSION AND FIRE. THECAUSE OF THE SERVICE LINE SEPARATION WAS FOUND TO BE THE INSTALLATION OF A 4" PLASTIC DRAIN LINE PRESSING AGAINST THE SERVICE LINE TO THE POINT OF BOWINGTHE SERVICE LINE APPROXIMATELY 12" AND DEFORMING THE DRAIN. THERE WAS ALSO INDICATIONS THAT THE STEEL SERVICE LINE HAD BEEN STRUCK WITH EXCAVATING EQUIPMENT. THE LDC HAD NO KNOWLEDGE OF THIS CONSTRUCTION AND NO LOCATE INFORMATION HAD BEEN REQUESTED.
2025-01-31 10:21 | NO | NO | 19950163 | 1995-12-18 | 24015 | YANKEE GAS SERVICES CO | MURDOCK AVENUE | MERIDEN | NEW HAVEN | CT | 06450 | 3 | NO | 2156 | 1995-11-14 | 0 | 0 | 20000 | 14665.1817 | 35408.6036 | Null | 2 | 49 |  | 19951115 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.219 | API5L |  | 1967 | 1967 | OTHER | UNDER BRIDGE | JOSEPH R. ANCONA | 2035963034 | [6 empty] | Null |  | NO DATA | NO ENTRY | NO |  | NO | 0 |  | NO |  |  | SEVERE WINDS CAUSED A HIGH VOLTAGE ELECTRIC DISTRIBUTION CONDUCTOR (APPROXIMATELY 13,200 VOLTS AC, PHASE TO GROUND) TO PART AND FALL FROM ITS OVERHEAD POSITION. THE CONDUCTOR LANDED ON THE BRIDGE DECKING IN DIRECT CONTACT WITH A STEEL EXPANSION JOINT IN THE BRIDGE DECKING. AN ELECTRICAL ARC OCCURRED BETWEEN THE BRIDGE STEEL AND THE GAS PIPELINE WHICH WAS SUPPORTED UNDER THE BRIDGE.THE ARC CAUSED A BURN THROUGH THE STEEL GAS PIPE AND NATURAL GAS IGNITED. DAMAGE TO THE OPERATOR IS APPROXIMATELY $20,000. DAMAGE TO THE BRIDGE, IF ANY, IS UNDER EVALUATION BY THE STATE OF CONNECTICUT DEPARTMENT OF TRANSPORTATION AND HAS NOT YET BEEN QUANTIFIED.
2025-01-31 10:21 | YES | YES | 19950164 | 1995-12-19 | 18484 | SOUTHERN CALIFORNIA GAS CO | 5780 E. LA PALMA AVENUE | ANAHEIM | ORANGE | CA | 92807 | 3 | NO | 2110 | 1995-12-04 | 0 | 1 | 0 | 0 | 0 | Null | 13 | 0 |  | 19951205 | 42 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | 40-00 | DUPONT | 1971 | 1971 | UNDER PAVEMENT |  | DONALD K. MYERS | 2132443218 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | AN EMPLOYEE OF NURSERYLAND CARE CENTER WAS ATTEMPTING TO TURN THE WATER OFF AT THE WATER METER WHILE USING A CIGARETTE LIGHTER TO SEE IN THE DARK. AS HE LIT THE LIGHTER, GAS THAT HAD ACCUMULATED IN THE WATER METER VAULT IGNITED, FLASHED, AND BURNED HIM. THE EMPLOYEE WAS TAKEN TO SANTA ANA WESTERN MEDICAL CENTER WHERE HE WAS ADMITTED AND TREATED FOR 1ST AND 2ND DEGREE BURNS TO HIS FACE AND ARMS. THE NURSERY MANAGER CALLED THE GAS COMPANY THE FOLLOWING MORNING TO REPORT A GAS LEAK. THE LATER ADVISED A COMPANY SUPERVISOR, WHO WAS AT THE SITE, THAT ONE OF HIS EMPLOYEES HAD BEEN INJURED THE NIGHT BEFORE AND HAD BEEN TAKEN TO THE HOSPITAL. A GAS COMPANY CREW LOCATED THE SOURCE OF THE GAS AT A 4-INCH COUPLING ON THE PLASTIC MAIN, FIFTEEN FEET AWAY, WHERE THEY FOUND A CIRCUMFERENTIAL CRACK WHERE THE MAIN ENTERED THE COUPLING. THE TWO MOST RECENT LEAKAGE SURVEYS OF THIS BUSINESS DISTRICT FOUND NO LEAKAGE. THE MAIN WHICH WAS INSTALLED IN OCTOBER, 1971 WAS PINCHED ON BOTH SIDES OF THE LEAK AND THE DAMAGED SECTION REPLACED USING A SECITON OF 4" PLASTIC PIPE AND TWO ELECTRO-FUSION COUPLINGS.
2025-01-31 10:21 | YES | YES | 19950165 | 1995-12-19 | 15007 | PACIFIC GAS & ELECTRIC CO | 1916 FALLON | MODESTO | STANISLAUS | CA |  | 0 | NO | 10 | 1995-11-30 | 2 | 0 | 40000 | 29330.3634 | 70817.2073 | Null | 0 | 20 |  | 19951130 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | CUSTOMER WATER HEATER | FITTING |  | OTHER | ALUM FLEX CONNECTOR | 0.5 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | WILLIAM R. BLASTIC | 4159734903 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | STRUCTURE FIRE CAUSED BY DEBRIS AROUND WATER HEATER.
2025-01-31 10:21 | NO | NO | 19950167 | 1995-12-27 | 4483 | ENSTAR NATURAL GAS CO | 14751 GROVER LANE | PALMER | MATANUSKA-SUSITNA | AK |  | 2 | NO | 250 | 1995-12-15 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 0 | 27 |  | 19951215 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY | SERVICE LINE | REGULATOR/METER |  | POLYETHYLENE PLASTIC | METER | 0.625 | 0.09 | M8000 | PHILLIP DRISCOPIPE | 1991 | 1991 | WITHIN/UNDER BUILDING |  | DAVID W. BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | THE BUILDING OWNER WAS RELOADING AMMUNITION AND SMOKING AT THE TIME. A CIGARETTE IGNITED GUNPOWDER AND THE BUILDING CAUGHT FIRE. THE FIRE CAUSED THE GAS METER AND PLASITC SERVCIE LINE TO MELT INSIDE THE STEEL RISER, RESULTING IN ARELEASE OF NATURAL GAS. THE SERVICE LINE RISER WAS CUT AND THE PLASTIC LINE PINCHED OFF AND CAPPED. NATURAL GAS DID NOT CONTRIBUTE TO THE CAUSE OF THE FIR
2025-01-31 10:21 | YES | YES | 19950168 | 1995-12-27 | 2764 | COOKEVILLE GAS DEPT, CITY OF | WEST WALL ST & WEST MAIN STREET | ALGOOD | PUTNAM | TN |  | 0 | NO | 847 | 1995-08-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 18 |  | 19950811 | 42 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 1 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | JAMES A. DANIEL | 6155267900 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | WAS IN THE PROCESS OF LOWERING A 6' SECTION OF 1" STEEL SERVICE LINE BY INSTALLING A PIECE OF 1" PLASTIC. HAD THE UPSTREAM CONNECTION MADE USING DRESSER COUPLING AND WAS GETTING READY TO CONNECT OTHER END OF PIPE TO EXISTING LINE WHEN FIRE ERUPTED. THREE MEN WERE BURNED (NOT SEVERLY) ALONG WITH A TRACKHOE.TWO OF THE MEN WERE TREATED AND RELEASED AT HOSPITAL SAME DAY, ONE OF THE EMPLOYEES KEPT IN HOSPITAL 2.5 DAYS. ALL THREED RETURNED TO WORK IN 12 DAYS.
2025-01-31 10:21 | NO | NO | 19950169 | 1995-12-26 | 20211 | UNITED CITIES GAS CO | OLD NASHVILL HWY | MURFREESBORO | RUTHERFORD | TN |  | 3 | NO | 950 | 1995-12-13 | 0 | 0 | 25000 | 18331.4771 | 44260.7546 | YES | 1 | 30 |  | 19951213 | 425 | 550 | BY TEST | 825 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.145 |  |  | 0 | 1952 | UNDER GROUND OR UNDER WATER |  | CONRAD A. BARGER | 6153735310 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-11-10 | YES | 2 |  | YES |  |  | SECTION OF PIPE DAMAGED WAS NOT MARKED. SECTION THAT WAS DAMAGE WAS STUB OUTLEFT FROM LAST RELOCATION TO SERVE FARM TAP. WAS NOT MARKED BY LOCATER. HE WAS NOT AWARE OF THIS SECTION. TRACK HOE HIT 4 STEEL LINE CAUSING LINE CUT.
2025-01-31 10:21 | YES | YES | 19950170 | 1995-12-26 | 792 | ATLANTA GAS LIGHT CO | 114 ARCADO ROAD | LILBURN | GWINNETT | GA | 30247 | 3 | NO | 1000 | 1995-11-25 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19951125 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.66 | 0.166 | ASTM D2513 | PLEXCO | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | MICKEY WATTS | 7704182261 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-11-22 | YES | 3 | PARTIALLY | YES |  |  | CONTRACTOR REQUESTED THAT LOCATOR NOT LOCATE SERVICE LINE COMPLETELY AT THE JOB SITE. THE UNLOCATED PORTION OF THE SERVICE LINE IS WHERE DAMAGE OCCURRED.
2025-01-31 10:21 | YES | NO | 19950171 | 1995-12-27 | 4350 | ELIZABETHTOWN GAS CO | 51 AMELIA DRIVE | CLARK | UNION | NJ | 07095 | 4 | NO | 239 | 1995-12-17 | 0 | 0 | 200000 | 146651.8168 | 354086.0365 | Null | 2 | 10 |  | 19951217 | 18 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | DOUGLAS STAEBLER | 9082895000 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | EARTH LOADING | NO |  | NO | 0 |  | NO |  |  | POSSIBLE ESCAPE OF GAS RESULTING FROM CRACK IN 4" CAST IRON MAIN.7
2025-01-31 10:21 | NO | NO | 19960003 | 1996-01-17 | 1640 | BOSTON GAS CO | 69 OLIVE AVENUE | MALDEN | MIDDLESEX | MA | 02148 | 3 | NO | 1839 | 1995-12-22 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 3 | 6 |  | 19951223 | 0.33 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.5 |  |  | 0 | 1912 | UNDER PAVEMENT |  | ROBERT J. CAVICCHI | 6177235512 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | NO | 0 |  | NO |  |  | COMPANY PERSONNEL WERE REQUESTED TO RESPOND TO A FIRE THAT OCCURRED AT 69 OLIVE AVENUE, MALDEN, MASSACHUSETTS. A LEAK INVESTIGATION WAS CONDUCTED AND A SIX INCH (6") LOW PRESSURE CAST IRON CIRCUMFERENTIAL BREAK (270) WAS FOUND ON THE MAIN LOCATED IN THE STREET.
2025-01-31 10:21 | YES | NO | 19960004 | 1996-01-17 | 792 | ATLANTA GAS LIGHT CO | 939 CAMILLA STREET SW | ATLANTA | FULTON | GA | 30314 | 3 | NO | 1524 | 1995-12-04 | 0 | 0 | 100000 | 73325.9084 | 177043.0182 | Null | 4 | 1 |  | 19951204 | 15 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | SERVICE STUB | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | A25 |  | 1951 | 1951 | UNDER GROUND OR UNDER WATER |  | JACK R. SAPP | 4045844054 | [6 empty] | Null |  | OPERATOR ACTION |  | NO |  | NO | 0 |  | NO |  |  | OPERATOR'S CONTRACTOR HIT AN OLD SERVICE STUB WHILE BORING TO INSTALL NEW MAIN. GAS MIGRATED BACK UP BORING DITCH TO SANITARY SEWER LATERAL WHICH HAD BEEN BORED THROUGH. GAS THEN MIGRATED INTO SANITARY SEWER MAIN LINE AND FROM THERE UP SEWER LATERAL INTO HOUSE AT 939 CAMILLA STREET. UNKNOWN SOURCE OF IGNITION CAUSED EXPLOSION.
2025-01-31 10:21 | YES | YES | 19960005 | 1996-01-16 | 15329 | PEOPLES GAS LIGHT & COKE CO | 2232 NORTH CLEVELAND | CHICAGO | COOK | IL | 60614 | 4 | NO | 1305 | 1995-12-08 | 1 | 1 | 0 | 0 | 0 | Null | 0 | 30 |  | 19951208 | 8.25 | 12 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | STAINLESS STEEL BANDCLAMP | OTHER | STAINLESS STEEL BANDCLAMP | 6 | 0.38 | CAST IRON | US PIPE | 1939 | 1939 | UNDER PAVEMENT |  | PHILIP J. EGIZIO | 3127946840 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FOUR PERSON CREW WAS REPLACING A LEAKING 6" STAINLESS STEEL BAND CLAMP WHICH WAS COVERING A CRACK ON A 6" LOW PRESSURE CAST IRON MAIN. THE CREW DID NOTFOLLOW COMPANY PROCEDURES. DURING THE JOB, THREE OF THE CREW MEMBERS WERE OVERCOME BY GAS. ONE SUBSEQUENTLY DIED. DISCUSSION 1/26/1996 WITH MATTHEW GREEN,ATTORNEY FOR PEOPLE'S GAS. ADDITIONAL INFORMATION WAS OBTAINED FROM HIM,CLARIFYING DATA IN PART B.
2025-01-31 10:21 | YES | NO | 19960006 | 1996-01-16 | 20211 | UNITED CITIES GAS CO | #5 PARKVIEW DRIVE | HANNIBAL | MARION | MO | 63401 | 2 | NO | 330 | 1995-12-14 | 0 | 0 | 80000 | 58660.7267 | 141634.4146 | Null | 1 | 0 |  | 19951214 | 45 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2.25 | 0.2656 |  |  | 1964 | 1965 | UNDER PAVEMENT |  | BEN NOBLES | 3142216773 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | GROUND SETTLEMENT | NO |  | NO | 0 |  | NO |  |  | THE 2 1/4" C.I. MAIN BROKE AND LET GAS TRAVEL BY PIPE TO WATER LINE DITCH AND THIS LET GAS INTO HOUSE WHERE WATER PIPE ENTERED. THE 2 1/4" PIPE WAS FOUNDTO BE ON A ROCK AND SETTLEMENT CAUSED THE PIPE TO BREAK. THIS CAST IRON PIPEWAS INSTALLED IN 1965 IN CLAY SOIL. PIPE WAS LAYING ON ROCK WHEN WE DUG IT UP. GROUND SETTLEMENT OVER THE YEARS IS THOUGHT TO BE THE CAUSE OF BREAKAGE, AS PIPE WAS IN GOOD CONDITION OTHERWISE.
2025-01-31 10:21 | YES | YES | 19960007 | 1996-01-05 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 1832 RIDGECREST | SHREVEPORT | CADDO | LA | 71118 | 3 | NO | 2313 | 1995-12-11 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 9 |  | 19951212 | 30 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 1956 | OTHER | NOT GIVEN | BUDDY SIMS | 3184294160 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INCIDENT WAS TELEPHONICALLY REPORTED 12 12 95 AT 12:28 AM AND WAS REPORTED AS POSSIBLE GAS RELATED. AFTER INVESTIGATION BY FIRE DEPARTMENT, CAUSE OF FIREDETERMINED TO BE NOT GAS RELATED.
2025-01-31 10:21 | YES | YES | 19960010 | 1996-01-23 | 15462 | PHILADELPHIA ELECTRIC CO | 831 TREMONT STREET | NORRISTOWN | MONTGOMERY | PA | 19401 | 1 | NO | 142 | 1995-12-19 | 2 | 1 | 100000 | 73325.9084 | 177043.0182 | YES | 4 | 45 |  | 19951219 | 17 | 25 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.44 |  |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | JOSEPH E. HOFFMAN | 6109411529 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CAST IRON MAIN BREAK IN STREET IN FRONT OF #840 TREMONT AVE., NORRISTOWN, PARESULTED IN THE MIGRATION OF NATURAL GAS THROUGH THE SOIL AND INTO THE AMBIENT ATMOSPHERE INSIDE OF THE STRUCTURE LOCATED AT #831 TREMONT AVE, NORRISTOWN.DURING THE MIGRATION OF THE GAS, AN EXPLOSION OCCURRED AT #831 TREMONT ST, NORRISTOWN. THIS EXPLOSION RESULTED IN TWO (2) DEATHS AND ONE (1) INJURY THAT REQUIRED HOSPITALIZATION. THE PROPERTIES AT #829 AND #831 TREMONT AVENUE WERECOMPLETELY DESTROYED BY THE ENSUING FIRE. FURTHER INVESTIGATION IS BEING CONDUCTED BY THE PA PUC FOR THE DOT.
2025-01-31 10:21 | YES | NO | 19960011 | 1996-01-23 | 15469 | PHILADELPHIA GAS WORKS | 4744 OXFORD AVENUE | PHILADELPHIA | PHILADELPHIA | PA | 19124 | 4 | NO | 325 | 1995-12-29 | 0 | 0 | 250000 | 183314.771 | 442607.5456 | Null | 4 | 20 |  | 19951229 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRIAN C. SCHENK | 2156846372 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | THE PHILADELPHIA FIRE DEPARTMENT, FIRE MARSHALL'S OFFICE, PHILADELPHIA POLICE DEPARTMENT AND THE BUREAU OF ALCOHOL, TOBACCO AND FIREARMS ARE CURRENTLY CONDUCTING A CRIMINAL INVESTIGATION INTO THE SUBJECT INCIDENT. THEY HAVE DETERMINED THAT THE INCIDENT WAS INCENDIARY IN NATURE AND THAT NATURAL GAS WAS INTENTIONALLY ALLOWED TO ESCAPE WITHIN THE BUILDING AND CAME IN CONTACT WITH AN UNKNOWN IGNITION SOURCE. THE INCIDENT WAS REPORTED TO THE EMERGENCY RESPONSE CENTER AT 0710 ON DECEMBER 29, 1995, REPORT NUMBER 318462.
2025-01-31 10:21 | NO | NO | 19960012 | 1996-01-22 | 13782 | NORTHERN STATES POWER CO | 5220 PARK AVENUE | WHITE BEAR TOWNSHIP |  | MN | 55110 | 2 | NO | 1319 | 1995-12-01 | 0 | 0 | 40000 | 29330.3634 | 70817.2073 | Null | 0 | 32 |  | 19951201 | 58 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | BARBARA K. BELEW | 6122292261 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SNOW MELT | NO |  | NO | 0 |  | NO |  |  | SNOW MELT OFF ROOF CAUSED ICE BUILD-UP ON SERVICE REGULATOR, CAUSING OVER PRESSURIZED CUSTOMER HOUSE PIPING.
2025-01-31 10:21 | YES | YES | 19960014 | 1996-01-26 | 2596 | COLUMBIA GAS OF OHIO INC | 38557 OTTEN ROAD | NORTH RIDGEVILLE | LORAIN | OH | 44039 | 3 | NO | 47 | 1995-12-26 | 1 | 1 | 150000 | 109988.8626 | 265564.5274 | Null | 1 | 11 |  | 19951226 | 38 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COMPRESSION | STEEL |  | 1.25 | 0.14 | GR-B |  | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | D.E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | INVESTIGATION HAS REVEALED THAT THE MOST LIKELY CAUSE OF ESCAPING GAS WAS THAT AN 1 1/4" STEEL RISER TO A METER SET PULLED OUT OF THE TOP OF AN 1 1/4" COMPRESSION ELL IN THE CUSTOMER SERVICE LINE. THE ESCAPING GAS MIGRATED TO THE HOUSE AND WAS IGNITIED FROM AN UNDETERMINED SOURCE. THE EXPLOSION KILLED ONE OCCUPANT AND INJURED A SECOND. AT THIS TIME REPORTS ARE THAT THE FOUNDATION WALL NEAR THE RISER PIPE HAD BEEN RECENTLY EXCAVATED WHICH MAY HAVE CAUSED SETTLEMENT OF THE GROUND
2025-01-31 10:21 | YES | NO | 19960015 | 1996-01-25 | 18536 | SOUTHWEST GAS CORP | 441.5 W. 6 TH STREET | WINNEMUCCA | HUMBOLDT | NV | 89445 | 3 | NO | 1214 | 1996-01-02 | 0 | 0 | 250000 | 179933.0418 | 434442.4706 | Null | 0 | 41 |  | 19960102 | 36 | 43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | PVC | 2 | 0.105 | STD.PVC | KRALOY | 0 | 1964 | UNDER PAVEMENT |  | DAVID PARENTEAU | 7026233642 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOT | Null |  | Null | 0 |  | Null |  |  | AN INVESTIGATION AFTER THE INCIDENT REVEALED THAT A LARGE TREE ROOT HAD GROWN ALONG SIDE OF, AND A SMALLER ROOT HAD GROWN FROM THE LARGER ROOT AND WRAPPED AROUND THE 2" PVC MAIN SERVING THE RESIDENCE INVOLVED IN THE INCIDENT. THE 2" PVC MAIN WAS FOUND TO HAVE A CIRCUMFERENTIAL CRACK JUST OUTSIDE A 2" PVC COUPLING ADJACENT TO WHERE THE TREE ROOTS CAME IN CONTACT WITH THE MAIN.THE SURROUNDING DIRT WAS 3/8" MINUS OR SMALLER, AND NO EVIDENCE OF PRIOR LEAKAGE WAS FOUND.
2025-01-31 10:21 | YES | NO | 19960016 | 1996-01-26 | 1640 | BOSTON GAS CO | 396 MARLBOROUGH STREET | BOSTON | SUFFOLK | MA |  | 3 | NO | 1657 | 1995-12-28 | 0 | 0 | 500000 | 366629.542 | 885215.0912 | Null | 1 | 3 |  | 19951228 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 |  |  | 0 | 1914 | UNDER PAVEMENT |  | FRANCIS J. COLEMAN | 6177235512 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | ON DECEMBER 28, 1995 AN EXPLOSION OCCURRED IN THE BASEMENT OF A FIVE-STORY BUILDING LOCATED AT 396 MARLBOROUGH STREET, BOSTON. A LEAK INVESTIGATION WAS CONDUCTED AND A SIX (6) INCH CAST IRON CIRCUMFERENTIAL BREAK WAS FOUND ON MAINLOCATED IN THE STREET UNDER APPROXIMATELY SIXTEEN (16) INCHES OF FROST. AN ONGOING INVESTIGATION IS BEING CONDUCTED BY BOSTON GAS COMPANY, MASSACHUSETTS DEPARTMENT OF PUBLIC UTILITIES.
2025-01-31 10:21 | NO | NO | 19960017 | 1996-01-26 | 15350 | PEOPLES NATURAL GAS CO | 1700 GREENSBURG AVENUE | NORTH VERSAILLES | ALLEGHENY | PA | 15137 | 2 | NO | 1432 | 1995-12-25 | 0 | 0 | 50000 | 36662.9542 | 88521.5091 | Null | 4 | 50 |  | 19951225 | 15 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1963 | ABOVE GROUND |  | JOYCE C. DAILEY | 4124975668 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | MR. RICHARD CASKEY SLID OFF THE HIGHWAY, STRUCK A RAILROAD TIE RETAINING WALL, A GAS METER, AND A TELEPHONE POLE. ESCAPING NATURAL GAS IGNITED AND DESTROYED THE VEHICLE. THERE WAS ALSO CONSIDERABLE DAMAGE TO TELEPHONE, ELECTRIC, AND CABLE T.V. LINES.0
2025-01-31 10:21 | YES | YES | 19960022 | 1996-01-30 | 12410 | MICHIGAN GAS CO | 2702 N. FIFTH STREET | NILES | BERRIEN | MI | 49120 | 2 | NO | 2130 | 1995-12-23 | 0 | 1 | 500 | 366.6295 | 885.2151 | Null | 4 | 0 |  | 19951224 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.32 | 0.119 |  | CENTURY | 0 | 1972 | UNDER PAVEMENT |  | THOMAS M. REILLY | 8109877900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MINOR FLASH FIRE AND SMALL EXPLOSION CAUSED BY A CRACK IN A 1" CENTURY PIPE SERVICE LINE. THIS A FOLLOW UP REPORT OF THE INCIDENT THAT HAPPENED IN NILES TOWNSHIP ON DECEMBER 23, 1995 AT 2702 N. FIFTH STREET. AS WE HAVE DISCUSSED, THIS WAS A MINOR FLASH FIRE AND A SMALL EXPLOSION IN A BODY SHOP. WE DETERMINED THAT THE CAUSE OF THE INCIDENT WAS FROM A LEAKING SERVICE APPROXIMATELY 120FOOT ANGLING TO AN ADDRESS OF 2628 N. FIFTH STREET. THE SERVICE LEAK WAS A CRACK IN A 1" CENTURY PIPE SERVICE THAT FED GAS SUPPLY TO 2628 N. FIFTH STREET. THIS GAS LEAK MIGRATED UNDERNEATH A BLACKTOP PARKING LOT WITH APPROXIMATELY24" OF FROST TO THE BODY SHOP WHERE THE INCIDENT HAD OCCURRED. WITHIN THIS PARKING LOT THERE WAS TELEPHONE AND ELECTRIC FLOOD LIGHT TRENCHES. THE TRENCHES HAD BEEN COVERED OVER WITH BLACKTOP BUT COULD BE SEEN WHERE IT WAS PATCHEDAND THE TRENCHES RAN DIRECTLY TO THE CORNER OF THE BODY SHOP AREA. I HAVE ENCLOSED A DRAWING SHOWING THE LOCATIONS OF THE BODY SHOP AND ALSO THE STRUCTURE NEXT DOOR WHERE THE LEAK OCCURRED AS WELL AS THE TELEPHONE INCIDENT REPORTS. BOTH SERVICES TO THESE BUILDINGS WERE COMPLETELY REPLACED EVEN THOUGH THE BODY SHOP SERVICE WAS A STEEL SERVICE AND WAS NOT LEAKING WE REPLACED IT ALSO.AFTER BOTH OF THESE SERVICES WERE REPLACED THE MAINS IN BOTH DIRECTIONS FORAPPROXIMATELY A HALF MILE WERE LEAK SURVEYED AND SERVICES AT OTHER RESIDENTSAND BUSINESSES WERE ALSO CHECKED AS WELL AS SEWERS AND MANHOLES IN THEAREA WERE CHECKED FOR MIGRATION GAS WHICH WE HAD ZERO. THE ONLY GAS MIGRATIONWE HAD SHOWING READINGS WAS ON THE PROPERTY AND WAS UNDERNEATH THE BLACKTOP.AS WE HAVE SPOKEN WE ARE IN THE PROCESS OF USING A VACUUM TRUCK TO PULL THEMETH ANE THAT IS LYING UNDERNEATH THE BLACKTOP IN POCKETS BACK OUT INTO THEATMOSP HERE. THE CONTRACTOR THAT IS DOING THIS IS WORKING WITH OUR FIELDPEOPLE IN T HE NILES DIVISION. WE HAVE ALSO HIRED A LABORATORY IN KALKASKA TORUN GAS TES T PERIODICALLY THROUGH THIS VENTING PROCEDURE TO MAKE SURE WE AREGETTING EV ERYTHING OUT OF THE GROUND AND END UP WITH A COMPLETELY CLEAR AREA.
2025-01-31 10:21 | NO | NO | 19960023 | 1996-02-05 | 18532 | SOUTHERN UNION GAS CO | 1300 BLOCK S. CONGRESS AVE | AUSTIN | TRAVIS | TX | 78704 | 3 | NO | 553 | 1995-12-24 | 0 | 0 | 0 | 0 | 0 | Null | 19 | 7 |  | 19951224 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | PENDING INVESTIGATION | STEEL |  | 10 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | ROB WESCH | 5124651101 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE CAUSE OF THIS GAS LEAK IS BEING INVESTIGATED. THE AFFECTED SECTION OF THE MAIN HAS REMAINED OUT OF SERVICE. DUE TO THE HIGH TRAFFIC VOLUME ON SOUTH CONGRESS AVE, THE INVESTIGATION HAS BEEN DELAYED UNTIL PERMANENT REPAIRS ARE MADE. THE OLD MAIN WILL BE EXPOSED, AND A CAUSE SOUGHT, AS THE NEW MAIN IS INSTALLED.
2025-01-31 10:21 | YES | YES | 19960024 | 1996-02-06 | 15259 | PENNSYLVANIA GAS & WATER CO | 910 JEFFERSON AVE, 703 MYRTLE ST. | SCRANTON | LACKAWANNA | PA | 18510 | 3 | NO | 619 | 1996-01-13 | 0 | 4 | 275000 | 197926.346 | 477886.7177 | Null | 2 | 57 |  | 19960113 | 11 | 12 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.45 | AGA SPEC |  | 1908 | 1908 | UNDER PAVEMENT |  | JAMES M. GREGER | 7178298866 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | NO |  | Null | 0 |  | Null |  |  | EXCAVATION ON JEFFERSON ST. REVEALED A FOUR INCH (4) CAST IRON GAS MAIN BREAK WHICH LEAKED THROUGH NATURAL OPENINGS IN THE SOIL, ENTERING BOTH BUILDINGS.INSPECTION SUBSEQUENT TO EXCAVATION REVEALED A DEEP FROST LINE CREATING PRESSURE ON THE GAS MAIN, CAUSING THE MAIN TO CRACK.
2025-01-31 10:21 | YES | NO | 19960025 | 1996-02-06 | 10037 | WESTERN RESOURCES, INC | 7001 RUSSELL | OVERLAND PARK | JOHNSON | KS | 66204 | 3 | NO | 1420 | 1996-01-08 | 0 | 0 | 90000 | 64775.8951 | 156399.2894 | Null | 1 | 40 |  | 19960108 | 45 | 58 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 1955 | OTHER | UNDER DRIVEWAY | JAMES M. FALLON | 9132713910 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-07-24 | YES | 3 | PAINT | YES |  |  | JOHNSON COUNTY WATER DISTRICT #1 EMERGENCY LOCATE REQUESTED AT 7001 RUSSELL ON 07/24/95. LOCATED ON 07/24/95. A TWO-INCH STEEL MAIN, WHICH APPARENTLY HADBEEN DAMAGED SOMETIME PRIOR TO THIS INCIDENT FAILED AT THE POINT OF THE PREVIOUS THIRD-PARTY DAMAGE, AND A RELEASE OF NATURAL GAS OCCURRED. THE GAS APPARENTLY MIGRATED UNDER THE DRIVEWAY AT THIS RESIDENCE. ENTERED THE STRUCTURE AND APPARENTLY IGNITED DUE TO AN UNKNOWN SOURCE OF IGNITION.
2025-01-31 10:21 | NO | NO | 19960026 | 1996-02-13 | 8070 | INDIANA GAS CO INC | 2500 S. WEST STREET | YORKTOWN | DELAWARE | IN | 47369 | 3 | NO | 1350 | 1996-01-17 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 28 |  | 19960117 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | THREADS | STEEL |  | 1 | 0 |  |  | 0 | 1948 | OTHER | NEAR BUILDING WALL | RICHARD L. SLAGLE | 3173210518 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | NO | 19960027 | 1996-02-20 | 11032 | LACLEDE GAS CO | 11565 & 11575 WICKSHIRE COURT | BRIDGETON | ST LOUIS | MO | 63044 | 3 | NO | 1615 | 1996-01-24 | 0 | 0 | 315000 | 226715.6327 | 547397.513 | Null | 2 | 5 |  | 19960124 | 21 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2.375 | 0.154 | API 5L |  | 0 | 1962 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INVESTIGATION IS CONTINUING AS TO THE CAUSE OF THE FAILURE AT THE LAST THREAD OF THE COUPLING OF THE 2-INCH SCREWED, STEEL MAIN. THE FAILURE WAS A FULL CIRCUMFERENCE BREAK WITH A SEPARATION OF APPROXIMATELY 1/2 INCH. THERE WERE TWO SEPARATE EXPLOSIONS IN THIS INCIDENT; AT APPROXIMATELY 1615 HOURS AT 11565 AND APPROXIMATELY 1645 HOURS AT 11575 WICKSHIRE COURT.INDIANA GAS CO. RESPONDED TO 2500 S. WEST ST. IN YORKTOWN,IN , TO TEND TO THE NATURAL GAS FACILITIES AT THE PROPERTY, DUE TO A FIRE AND EXPLOSION. GAS WAS SHUTOFF TO THE STRUCTURE AT THE CURB VALVE AT 2:18 P.M.. NO INJURIES OCCURRED AS A RESULT OF THE INCIDENT. INITIAL INVESTIGATION BY INDIANA GAS CO. PERSONNEL INDICATED THAT THERE WAS NO LEAKAGE ON THE ADJACENT MAINS. ODORANT TESTS IN THE AREA INDICATED THAT ODORANT WAS SUFFICIENT IN THE GAS STREAM. THE 1"BARE STEEL SERVICE LINE THAT SERVED THE STRUCTURE AT 2500 S. WEST ST. (INSTALLED IN 1948) WHICH OPERATED AT A NORMAL OPERATING PRESSURE OF 20 PSIG, WAS TESTED WITH AIR AT A PRESSURE OF 50 PSIG. THE TEST INDICATED THAT THE SERVICE WOULD NOT HOLD PRESSURE. FUTHER INVESTIGATION FOUND THAT A CRACK HAD DEVELOPED ON THE THREADS OF THE PIPE AT THE OUTLET OF A 1" ELBOW ON THE SERVICE LINE NEAR THE BUILDING WALL. THIS PIECE WAS LATER CUT OUT FOR TESTING. INITIAL TESTS CONCERNING CORROSION OF PIPE HAVE INDICATED THAT CORROSION WAS NOT PRESENT. FURTHER TEST OF THIS PIECE OF PIPE WILL OCCUR IN THE NEAR FUTURE, WHEN PERMISSION IS GRANTED FROM THE INSURANCE COMPANY OF THE HOMEOWNER, TO DESTRUCTIVELY TEST THIS PIECE OF PIPE. THESE TESTS WILL DETERMINE IF THE CRACK WAS CAUSED BY STRESS OR FATIGUE. THE REMAINDER OF THE SERVICE LINE WAS TESTED IN TWO (2) DIFFERENT SECTIONS. THE FIRST SECTION TESTED WAS A 34' PIECE OF 1" STEEL THAT ORIGINATED AT THE OUTLET OF THE CURB VALVE AND ENDED AT THE POINT WHERE THE ELBOW MENTIONED ABOVE WAS CUT OUT, THE SECOND SECTION WAS A 21" PIECE OF 1" STEEL RISER TO THE METER SET. TESTS INDICATED THAT BOTH PIECES OF THE PIPEWERE PRESSURE TIGHT AT APPROXIMATELY 20 PSIG FOR 15 MINUTES. AS INDICATED ABOVE, FINDINGS AS TO THE CAUSE OF THIS INCIDENT HAVE NOT YET BEEN DETERMINED. A SUPPLEMENTAL WEPORT WILL BE FILED AS CAUSE BECOMES KNOWN.
2025-01-31 10:21 | YES | YES | 19960028 | 1996-02-20 | 12684 | MONTANA - DAKOTA UTILITIES CO | 407 WEST 18TH STREET | WILLISTON | WILLIAMS | ND | 58801 | 3 | NO | 1425 | 1996-01-29 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19960129 | 18 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5L GA |  | 0 | 0 | UNDER PAVEMENT |  | RONALD E. BLUM | 7012227924 | [6 empty] | Null |  | EARTH MOVEMENT: FROST | FROST CAUSED LINE BURST | Null |  | Null | 0 |  | Null |  |  | AT 2:25 PM CST, GAS MIGRATING FROM A LEAK ON A 2" ST MAIN COLLECTED IN A HOUSE AND WAS IGNITED. THE RESULTING FIRE DESTROYED THE HOME. ONE RESIDENT RECEIVED MINOR BURNS AND WAS TRANSPORTED TO THE HOSPITAL. OTHER CIRCUMSTANCES: A MONTANA-DAKOTA SERVICEMAN RESPONDED TO A "STRONG ODOR IN THE ALLEY" CALL AT 9:00 AM CST. THE INVESTIGATION FOUND 90% GAS IN THE GROUND NEXT TO THE SMALL HOUSE. THE HOUSE WAS LOCKED AND NO-ONE WAS HOME. THE GAS WAS SHUT OFF, THE LANDLORD WAS CALLED AND HE LET US IN THE HOUSE. 82 % & 90% LEL WAS FOUND IN THE HOUSE. THE ELECTRICITY WAS SHUT OFF AND THE EARTH NEXT TO THE HOUSE WAS DUG UPTO VENTILATE THE GAS. WITH MAKE SAFE ACTIONS COMPLETED THE CREW BEGAN TO PINPOINT THE LEAK AND EXCAVATE TO MAKE REPAIRS. THE RENTER EVIDENTLY SHOWED UP AND ENTERED THE HOUSE UNDETECTED. HE TRIED TO LIGHT A CIGARETTE AT WHICH POINTTHE HOUSE EXPLODED. HE EXITED THE HOUSE AND WAS DISCOVERED BY THE GAS CREW. THEY CALLED THE FIRE DEPARTMENT AND AN AMBULANCE AND SHUT DOWN THE GAS MAIN THAT FED THE HOUSE AND SEVERAL APARTMENT HOUSES.
2025-01-31 10:21 | YES | NO | 19960029 | 1996-02-12 | 1088 | BALTIMORE GAS & ELECTRIC CO | 822 BONAPARTE AVENUE | BALTIMORE |  | MD | 21218 | 3 | Null | 45 | 1996-01-19 | 0 | 0 | 75000 | 53979.9125 | 130332.7412 | Null | 3 | 42 |  | 19960119 | 8.6 | 10 | BY TEST | 10 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | JOINT | COUPLING, FITTING | STEEL |  | 2 | 0.154 | NONE 1936 |  | 0 | 1936 | UNDER PAVEMENT |  | DONALD L SHRADER | 4102915130 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | ON 01/19/96, THERE WAS AN APPARENT EXPLOSION AND FIRE AT 822 BONAPARTE AVE.OBSERVATIONS OF THE TWO STORY BRICK BUILDING SHOWED THE STRUCTURE COLLAPSED INTO THE BASEMENT. NO INJURIED WERE REPORTED WITH A PROPERTY DAMAGE OF APPROXIMATELY $75,000.00. TELEPHONIC NOTICE WAS GIVEN TO THE DEPARTMENT OF TRANSPORTATION AND MARYLAND PUBLIC SERVICE COMMISSION. FROM GAS LEAK INVESTIGATION WEFOUND TWO GAS LEAKS ON A BARE STEEL GAS MAIN IN THE 2300 BLOCK OF CECIL AVE.,45' NORTH OF THE NORTH CURB LINE OF BONAPARTE AVEN., AND 40' SOUTH OF THE SOUTH CURB LINE OF THE ALLEY IN THE REAR OF 822 BONAPARTE AVE. A THREADED 2" PIPE HAD PULLED OUT OF A 2" COUPLING AND A SMALL RUST THROUGH WAS LOCATED 5' NORTH OF THE SEPARATED GAS MAIN. FROM OBSERVATIONS IT APPEARS THE SEPARATION WAS CAUSED BY EARTH MOVEMENT ATTRIBUTED TO COLD AND FROST. THE TWO GAS LEAKS WERE REPAIRED AND A REQUEST FOR A GAS MAIN REPLACEMENT WAS ISSUED.
2025-01-31 10:21 | NO | NO | 19960030 | 1996-02-23 | 4060 | EAST OHIO GAS CO | BOX 257, S. R. 7 | NEW MATAMORAS | WASHINGTON | OH |  | 2 | NO | 840 | 1996-01-22 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 3 | 0 |  | 19960122 | 0.44 | 46 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 | B-31-R | SPRAGUE | 0 | 1971 | ABOVE GROUND |  | ROBERT J. BRADACH | 2167366872 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FIRE OF UNDETERMINED ORIGIN CAUSED EXTENSIVE DAMAGE TO A SINGLE FAMILY HOME. WHILE IT HAS NEVER BEEN DETERMINED WHAT THE EXACT CAUSE OF THE FIRE WAS, IT IS SUSPECTED THAT AN OVER-PRESSURIZATION OF THE NATURAL GAS HOUSELINE MAY HAVE CAUSED THE FLAME ON EITHER THE GAS WATER HEATER OR GAS FURNACE TO INCREASE, IGNITING ONE OF SEVERAL COMBUSTIBLE SOURCES STORED IN CLOSE PROXIMITY TO THESE APPLIANCES (NEWSPAPER, PAINT, MISCELLANEOUS SOLVENTS). THIS HOUSE WAS SUPPLIED NATURAL GAS FROM TWO SOURCES: A LOCAL WELL PROVIDING GAS AT 6 POUNDS, AND EAST OHIO GAS SERVICE AT 7 OUNCES. A POSSIBLE CONTRIBUTING FACTOR TO THISINCIDENT WAS EXTENSIVE FLOODING OF THE OHIO RIVER IN THE AREA OF THE EAST OHIO GAS METER SET. TEMPORARY VENT STACKS HAD BEEN INSTALLED ON THE TWO SERVICEREGULATORS ON THIS METER SET TO A HEIGHT OF 7 FEET IN ANTICIPATION OF THE RISING FLOOD WATERS. HOWEVER, THE FLOOD WATERS ROSE TO THE APPROXIMATE HEIGHT OF THE STACK OPENINGS, INTRODUCING WATER TO THE INTERIOR OF THE REGULATORS. THIS WATER MAY HAVE IMPEDED THE PERFORMANCE OF THE REGULATORS WHICH WERE DESIGNED TO REGULATE GAS PRESSURE FROM 46 POUNDS DOWN TO 7 OUNCES. AN OVER-PRESSURESITUATION MAY HAVE RESULTED.
2025-01-31 10:21 | YES | YES | 19960039 | 1996-02-27 | 12684 | MONTANA - DAKOTA UTILITIES CO | 794 N. ADAMS | BUFFALO | JOHNSON | WY | 82834 | 3 | NO | 917 | 1996-02-02 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 15 |  | 19960202 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5L GA |  | 0 | 0 | UNDER PAVEMENT |  | RONALD E. BLUM | 7012227924 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | FROST CAUSED THE LINE TO BURST AT A LOCATION THAT HAD PREVIOUSLY BEEN DAMAGED BY A CONTRACTOR OR UNKNOWN PARTY. AT ABOUT 11:25 AM MST, 02/02/96, GAS MIGRATING FROM A LEAK ON A 2" STEEL MAIN COLLECTED IN AN ADJACENT HOUSE IGNITED. THE EXPLOSION SEVERLY DAMAGED THE HOME. TWO RESIDENTS RECEIVED BURNS AND WERETRANSPORTED TO THE HOSPITAL. OTHER CIRCUMSTANCES: TWO MONTANA-DAKOTA SERVICEMEN WERE NEARBY WHEN THE EXPLOSION OCCURRED INVESTIGATING ODOR CALLS REPORTED BY NEIGHBORS. NO GAS WAS FOUND IN THE GROUND AROUND ANY OF THE REPORTED LOCATIONS. COMBUSTIBLE GAS WAS DISCOVERED IN A NEARBY SANITARY SEWER MANHOLE. THE GAS PROBABLY ENTERED THE BUILDING THROUGH THE SANITARY SEWER.
2025-01-31 10:21 | YES | YES | 19960040 | 1996-02-28 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 409 N. ASH STREET | MARLOW | STEPHENS | OK | 73055 | 3 | NO | 1215 | 1995-11-04 | 2 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19951104 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE RESIDENCE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | OTHER | INSIDE RESIDENCE | GERALD R. KOLB | 4055366254 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DOOR TO BLOWER SECTION OF FURNACE (CENTRAL HEATER) HAD BEEN REMOVED. FLUEVENT WAS NOT PROPERLY FITTED TO CENTRAL HEATER, APPROXIMATELY 1" ABOVE HEATEXCHANGER. FLUE VENT ON WATER HEATER WAS NOT PROPERLY INSTALLED ON APPLIANCE.CARBON MONOXIDE EMISSION DOOR TO BLOWER SECTION OF CENTRAL FURNACE OFF - FLUEVENTS IMPROPER.
2025-01-31 10:21 | NO | NO | 19960041 | 1996-03-01 | 792 | ATLANTA GAS LIGHT CO | 1606 HOMESTEAD TRAIL | ALPHARETTA | FULTON | GA | 30201 | 3 | NO | 1430 | 1996-02-04 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 30 |  | 19960204 | 58 | 60 | BY TEST | 93 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CLEAR ALUMINUM | 0 | 0 | 1313 REG | AMERICAN METER | 1988 | 1988 | ABOVE GROUND |  | DENNIS MCCRARY | 7707725510 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WATER RAN OFF THE ROOF TOP ONTO THE NATURAL GAS METER SET ASSEMBLY DURING SUB-FREEZING TEMPERATURE. THE WATER HAD TRAVELED AROUND THE 1313 REGULATOR FORMING ICE OVER THE RELIEF VENT WHICH WAS IN THE DOWNWARD POSITION. WHEN THE REGULATOR FAILED IN THE OPEN POSITION, THE INTERNAL RELIEF COULD NOT OPERATE PROPERLY THUS CAUSING OVERPRESSURE INSIDE THE CONDOMINIUM. THE EXCESS GAS IGNITED FROM AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 19960042 | 1996-03-01 | 6490 | GRANBY GAS, CITY OF | 132 WEST NEOSHO STREET | GRANBY | NEWTON | MO | 64844 | 3 | NO | 106 | 1996-02-07 | 1 | 0 | 35000 | 25190.6259 | 60821.9459 | YES | 4 | 54 |  | 19960207 | 32 | 32 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JIM CHANNEL | 4174723542 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | ON ADVICE OF COUNSEL, NO STATEMENT IS BEING MADE AT THIS TIME SINCE THE CITYIS ON NOTICE OF POSSIBLE LITIGATION CONCERNING THIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19960043 | 1996-03-04 | 2748 | CONSUMERS POWER CO | 113 AUSTIN ROAD | NAPOLEON | JACKSON | MI | 49261 | 3 | NO | 2240 | 1996-02-03 | 2 | 0 | 0 | 0 | 0 | Null | 1 | 5 |  | 19960204 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L,GDB | US STEEL | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | KENNETH L. ELENBAAS | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-05-25 | YES | 2 |  | YES |  |  | PIPE FAILED AT THIRD-PARTY DAMAGE. GAS MIGRATED INTO HOUSE CAUSING AN EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | YES | 19960044 | 1996-03-05 | 705 | ASHFORD GAS CO | ASHFORD HILL | ASHFORD |  | WV | 25009 | 2 | NO | 2015 | 1996-02-23 | 0 | 1 | 267 | 192.1685 | 463.9846 | Null | 0 | 40 |  | 19960226 | 12 | 30 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.151 | SDR 11 | PLEXCO | 1992 | 1992 | ABOVE GROUND |  | BOYD A. REED | 3043440474 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE 1.250 INCH SERVICE LINE WAS ON TOP OF THE GROUND WHEN ALLEGEDLY TWO CHILDREN STARTED A FIRE ON TOP OF THE GAS LINE. MR. SEAN BOWLES NOTICED THE FIRE AND TRIED TO PUT THE FIRE OUT WITH HIS FEET WHEN THE GAS IGNITED.
2025-01-31 10:21 | YES | NO | 19960046 | 1996-03-05 | 22777 | WISCONSIN NATURAL GAS CO | N. 9142 S. ONEIDA ROAD | HARRISON | CALUMET | WI | 54915 | 2 | NO | 1136 | 1996-01-23 | 0 | 0 | 150000 | 107959.8251 | 260665.4824 | Null | 0 | 19 |  | 19960123 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PLEXCO | 1988 | 1989 | UNDER GROUND OR UNDER WATER |  | RUSSELL C. ACKERMAN | 4146352154 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1995-11-06 | YES | 3 | TEMPORARY PAINT MARKS | YES |  |  | AREA OF INCIDENT WAS RELOCATED THE SAME DAY OF INCIDENT.THE EXPLOSION OCCURRED AFTER HOLTGER BROTHER ACCIDENTALLY STRUCK AND DAMAGED OUR 2" PE (PLASTIC) GAS MAIN WHILE DIRECTIONALLY BORING TELEPHONE CABLE. THE GAS MAIN HAD BEEN MARKED CORRECTLY. GAS FROM THE DAMAGED MAIN TRAVELED UNDER 30" FROST APPROXIMATELY 100 FEET INTO THE BASEMENT OF THE HOME AND IGNITED FROM AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | NO | 19960047 | 1996-02-26 | 12420 | MICHIGAN GAS UTILITIES CO | 336 HILLSDALE STREET | HILLSDALE | HILLSDALE | MI | 49242 | 3 | NO | 120 | 1996-02-07 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 2 | 10 |  | 19960207 | 48 | 55 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | JOHN W. ROYSTON | 3132424983 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | DAMAGE TO PIPE APPEARS TO BE MONTHS OR YEARS OLD. N. RECENT CONSTRUCTION IN AREA. PIPE BROKE AT LOCATION OF PREVIOUS DAMAGE. 2" PIPE HAD BEEN STRUCK.
2025-01-31 10:21 | NO | NO | 19960048 | 1996-03-07 | 180 | ALABAMA GAS CORP | 1637 CHOCCOLOCCO ROAD | ANNISTON | CALHOUN | AL | 36207 | 3 | NO | 1255 | 1996-02-03 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 15 |  | 19960203 | 44 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | UNKNOWN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JOSEPH G. WHEELER | 2053268472 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DURING A WINTER STROM THE DISPATCHER RECEIVED A REPORT OF A HOUSE FIRE FROM THE FIRE DEPARTMENT AT THE ABOVE MENTIONED ADDRESS. THE FIRE DEPARTMENT REQUESTED ASSISTANCE IN TURNING OFF THE GAS. THE GAS WAS TURNED OFF BY A CREWMAN APPROXIMATELY FIFTEEN (15) MINUTES AFTER THE DISPATCHER RECEIVED THE CAL FROM THE FIRE DEPARTMENT.
2025-01-31 10:21 | YES | NO | 19960056 | 1996-03-19 | 30560 | WP NATURAL GAS CO | 2404 RIDDLE ROAD | LA GRANDE |  | OR | 97850 | 3 | NO | 1000 | 1996-02-18 | 0 | 0 | 170000 | 122354.4684 | 295420.88 | Null | 1 | 10 |  | 19960218 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LINDA BURGER | 5094824423 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON SUNDAY, FEBRUARY 18, 1996, A LITTLE BEFORE 10:00 AM.,AN EXPLOSION OCCURRED THAT DESTROYED A HOUSE AT 2404 RIDDLE ROAD IN LA GRANDE, OREGON.OUR SEVICE MAN RECEIVED A CALL FROM 911 AT 10:04 AM. HE CONTACTED THE AREA MANAGER WHO MEET HIM AT THE SITE OF THE INCIDENT. WHEN THEY ARRIVED, THE HOUSE WAS IN FLAMES AND THE FIRE DEPARTMENT ASKED OUR PEOPLE TO STAY OUT OF THE AREA UNTIL 11:10 AM. AT THAT TIME WE TURNED OFF THE SERVICE RISER AND REMOVED THE METER.
2025-01-31 10:21 | NO | NO | 19960058 | 1996-03-19 | 4483 | ENSTAR NATURAL GAS CO | 1718 CARA LOOP | ANCHORAGE |  | AK | 99515 | 2 | NO | 1648 | 1996-03-08 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 15 |  | 19960308 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | PHILLIPS DRISCOPIPE | 1974 | 1974 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON FRIDAY, MARCH 8, 1996, AT APPROXIMATELY 4:48 PM AST, ENSTAR NATURAL GAS COMPANY PERSONNEL RESPONDED TO A HOUSE FIRE AT 1718 CARA LOOP, ANCHORAGE, ALASKA (LOT 22, BLOCK 1 COLONIAL MANOR SUBDIVISION). ACCORDING TO ANCHORAGE FIRE DEPARTMENT OFFICIALS, THE FIRE ORIGINATED AT THE CLOTHES DRYER. THE RESULTINGFIRE ENGULFED THE STRUCTURE. THE INTENSE HEAT FROM THE FIRE CAUSED THE 5/8" HDPE SERVICE LINE TO MELT INSIDE THE STEEL RISER, CAUSING A RELEASE OF NATURAL GAS. THE PLASTIC SERVICE LINE WAS PINCHED OFF BY FIRE DEPARTMENT PERSONNEL AND CAPPED BY ENSTAR PERSONNEL. ESTIMATED DAMAGE TO THE STRUCTURE WAS IN EXCESS OF $50,000. NATURAL GAS DID NOT CONTRIBUTE TO THE CAUSE OF THE FIRE.
2025-01-31 10:21 | NO | NO | 19960059 | 1996-03-19 | 15469 | PHILADELPHIA GAS WORKS | 7700 MICHENER | PHILADELPHIA | PHILADELPHIA | PA | 19150 | 4 | NO | 1231 | 1996-02-23 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | YES | 2 | 19 |  | 19960223 | 0.25 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRIAN C. SCHENK | 2156846372 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | THE PHILADELPHIA FIRE DEPARTMENT AND PHILADELPHIA GAS WORKS HAVE CONCLUDED THAT THIS FIRE WAS CAUSED BY AN UNKNOWN PERSON TAMPERING WITH THE GAS METER. THE GAS METER SWIVELS WERE FOUND LOSSENED AND LEAKING WITH ADDITIONAL INDICATIONS THAT THE FIRE HAD STARTED AT THIS SAME METER. THE PHILADELPHIA FIRE DEPARTMENT'S ARSON INVESTIGATION UNIT IS CONTINUING TO INVESTIGATE THE INCIDENT. THIS INCIDENT WAS REPORTED TO THE EMERGENCY RESPONSE CENTER AT 1740 ON FEBRUARY 23, 1996, REPORT NUMBER 327781.
2025-01-31 10:21 | YES | YES | 19960060 | 1996-03-21 | 4499 | ENTEX - DIVISION OF ARKLA INC | 721 EMPIRE ST | EL CAMPO | WHARTON | TX | 77437 | 3 | NO | 321 | 1996-03-16 | 1 | 0 | 45000 | 32387.9475 | 78199.6447 | Null | 0 | 19 |  | 19960316 | 36 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | CUSTOMERS FACILITY | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD HORN | 2106257781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT FIRST REPORT A GAS LEAK EXPLOSION WAS SUSPECTED; HOWEVER, INVESTIGATION HAS REVEALED THAT NO GAS LEAKS OR MALFUNCTIONS OF EQUIPMENT & SIGNS OF HOMICIDE. INVESTIGATION REVEALED THAT GAS METER, REGULATOR & CUSTOMER HOUSELINE WERENOT DEFECTIVE. A BAR TEST AND COMBUSTION GAS INDICATOR TEST REVEALED THAT THERE WERE NO LEAKS ON THE GAS MAIN AND SERVICE LINE. POLICE ARE INVESTIGATING THE POSSIBILITY OF A HOMICIDE.
2025-01-31 10:21 | YES | NO | 19960064 | 1996-03-25 | 15359 | PEOPLES NATURAL GAS | 516-2ND ST WILD SIDE SPORTS BAR | WEBSTER | HAMILTON | IA | 50595 | 3 | NO | 945 | 1996-03-17 | 0 | 0 | 500000 | 359866.0836 | 868884.9412 | Null | 4 | 0 |  | 19960319 | 6 | 7 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.033 | 0.117 |  |  | 0 | 0 | ABOVE GROUND | FITTING METAL BUILD.WALL | EDWIN M. HATTER | 4022212546 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ELECTRICAL ARC ON STEEL SERVICE CAUSED RELEASE OF GAS. FIRE DESTROYED 2 BUILDINGS, SMOKE AND WATER DAMAGE TO OTHERS.
2025-01-31 10:21 | YES | NO | 19960065 | 1996-03-25 | 792 | ATLANTA GAS LIGHT CO | 2370 STEWART AVENUE., SW | ATLANTA | FULTON | GA | 30315 | 3 | NO | 1627 | 1996-03-11 | 0 | 0 | 90000 | 64775.8951 | 156399.2894 | Null | 0 | 58 |  | 19960311 | 60 | 60 | BY TEST | 128 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.125 | TR418 | DUPONT | 1995 | 1996 | UNDER GROUND OR UNDER WATER |  | FREDDIE R. WALKER | 7704733347 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | AN 1 1/4" PLASTIC NATURAL GAS SERVICE WAS RUPTURED BY A PLUMBING CONTRACTOR WHILE REPAIRING A COPPER WATER LINE. WHILE REPAIRING THE DAMAGED PIPE, THE CONTRACTOR ACCIDENTALLY BURNED A HOLE IN THE PLASTIC GAS SERVICE USING A SOLDERING TORCH. THE ESCAPING GAS IGNITED CAUSING EXTENSIVE DAMAGE TO TWO (2) APARTMENT BUILDINGS.
2025-01-31 10:21 | YES | NO | 19960066 | 1996-03-26 | 22189 | WASHINGTON NATURAL GAS CO | 24613-231 AVE SE | MAPLE VALLEY | KING | WA | 98038 | 3 | NO | 1528 | 1996-03-05 | 0 | 0 | 350000 | 251906.2585 | 608219.4589 | Null | 0 | 56 |  | 19960305 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.151 | ASTMD-2513 | PLEXCO | 1990 | 1991 | UNDER PAVEMENT |  | DAVID B. LAGERQUIST | 2062242268 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-03-04 | YES | 3 | PAINT MARKINGS | YES |  |  | A CABLE TV CONTRACTOR RUPTURED AN 1 1/4" PE GAS DISTRIBUTION MAIN WHILE USING A BORING TOOL TO REPLACE A CABLE TV WIRE LOCATED UNDER THE CONCRETE DRIVEWAY OF THE ABOVE ADDRESS. THE CONTRACTOR NOTIFIED WASHINGTON NATURAL GAS COMPANY(WNG) OF THE DAMAGED LINE AND, UPON ARRIVING ON SITE, WNG PERSONNEL FOUND THAT THE HOUSE WAS ON FIRE AND ESCAPING GAS HAD IGNITED. LOCAL FIRE DEPARTMENT PERSONNEL RESPONDED AND CONTAINED THE STRUCTURE FIRE WHILE WNG CREWS CHECKED NEIGHBORING BUILDINGS AND SHUT OFF GAS TO THE BROKEN MAIN. THE FIRE BEGAN IN THE GARAGE WHERE ESCAPING NATURAL GAS HAD ACCUMULATED AND IGNITION OCCURRED.ACCORDING TO FIRE DEPARTMENT INVESTIGATORS, THE FURNACE WAS THE MOST LIKELY IGNITION SOURCE. THE HOME IS CONSIDERED TO BE A TOTAL LOSS. FOUR VEHICLES WERE ALSO DAMAGED BEYOND REPAIR AS A RESULT OF THE FIRE. THE DAMAGED SECTION OF MAIN WAS REMOVED AND REPLACED WITH NEW PIPE. GAS SERVICE WAS RESTORED TO THREE AFFECTED HOMES IN THE AREA LATER THAT SAME NIGHT. FIRE DEPARTMENT INVESTIGATORS ESTIMATED PROPERTY DAMAGE TO BE $350,000. GAS LOSS COST IS ESTIMATED TO BE AN ADDITIONAL $169.23.
2025-01-31 10:21 | YES | NO | 19960067 | 1996-03-26 | 8170 | INTERSTATE POWER CO | 514 ELM STREET | KENSETT | WORTH | IA | 50448 | 3 | NO | 843 | 1996-03-05 | 0 | 0 | 161490 | 116229.5477 | 280632.4583 | Null | 1 | 37 |  | 19960305 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | VALVE |  | CAST IRON |  | 0.75 | 0 |  | WALWORTH | 0 | 1940 | UNDER GROUND OR UNDER WATER |  | JIM HOUSE | 5154232060 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | FROST HEAVE CRACKED THE CAST IRON BODY OF THE UNDERGROUND 3/4" WALWORTH SERVICE VALVE. THE GAS MIGRATD INTO THE UNOCCUPIED BUILDING AND WAS PROBABLY IGNITED BY A CEILING MOUNTED GAS HEATER.
2025-01-31 10:21 | YES | NO | 19960068 | 1996-03-26 | 13660 | NORTH SHORE GAS CO | 682 CHESTNUT | GLENCOE | COOK | IL |  | 3 | NO | 1655 | 1996-02-26 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 1 | 0 |  | 19960226 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1954 | UNDER GROUND OR UNDER WATER |  | M.P. CWIK | 8472634605 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | THE SERVICE PIPE WAS HIT AND DAMAGED BY SOME UNKNOWN THIRD PARTY. OVER TIME THE DAMAGED SECTION OF PIPE LEAKED, GAS MIGRATED INTO THE SINGLE FAMILY RESIDENCE AND IGNITED.THIRD PARTY HIT & DAMAGED SERVICE PIPE (DATE & THIRD PARTY UNKNOWN). A GAS LEAK RESULTED AT THE POINT WHERE THE PIPE WAS HIT.
2025-01-31 10:21 | YES | NO | 19960069 | 1996-03-27 | 24015 | YANKEE GAS SERVICES CO | 263 GREENWOOD AVENUE | BETHEL | FAIRFIELD | CT | 06801 | 3 | NO | 100 | 1996-02-28 | 0 | 0 | 200000 | 143946.4335 | 347553.9765 | Null | 0 | 0 |  | 19960228 | 34 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY | CUSTOMER PIPING | OTHER | NOT GIVEN | OTHER | ALUMINUM METERS | 0 | 0 |  |  | 0 | 0 | OTHER | NOT GIVEN | GARY B. LEWIS | 2037963227 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | STRUCTURE FIRE INVOLVED 3 GAS METERS ON OUTSIDE REAR OF BUILDING. NO LEAK ONSERVICE PIPING. A STRUCTURE FIRE AT #263 GREENWOOD AVENUE ORIGINATED IN THE AREA OF THREE (3) ABOVE GROUND METERS LOCATED AT THE OUTSIDE REAR OF THE BUILDING. THE METERS AND REGULATOR WERE DAMAGED BY THE FIRE CAUSING GAS TO ESCAPEAND FURTHER FUEL THE FIRE. THE INCIDENT IS CURRENTLY CLASSIFIED AS SUSPICIOUS BY THE LOCAL FIRE MARSHALL SINCE NO SOURCE OF IGNITION WAS IDENTIFIED AT THE LOCATION. STILL UNDER INVESTIGATION WILL FILE SUPPLEMENT IF CAUSE IS DEEMEDDOF.
2025-01-31 10:21 | YES | NO | 19960070 | 1996-03-28 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 1819 GERMAN STREET | ERIE | ERIE | PA | 16503 | 3 | NO | 2312 | 1996-03-03 | 0 | 0 | 180000 | 129551.7901 | 312798.5788 | Null | 1 | 30 |  | 19960305 | 25 | 48 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | THREADED | STEEL |  | 1 | 0.133 |  |  | 0 | 1962 | ABOVE GROUND |  | CONRAD L. DONELSON | 8148718341 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | Null | 3 | METER SETTING ABOVE GROUN | NO |  |  | 1" SERVICE REGULATOR WAS STRUCK BY SNOW PLOW. PRIVATE CONTRACTOR SNOW PLOW OPERATOR STRUCK 1" SERVICE REGULATOR AND PIPING. IMPACT CAUSED 1" PIPING TO BREAK AT THREAD AT REGULATOR INLET. IN ADDITION, THE METER (LOCATED INSIDE THE BUILDING) INLET BROKE OFF. THE ESCAPING GAS IMMEDIATELY IGNITED AT A NEARBY HEATER HUNG FROM THE CEILING. THERE WAS NO EXPLOSION.
2025-01-31 10:21 | YES | YES | 19960071 | 1996-04-01 | 22434 | WEST TENNESSEE PUBLIC UTIL DIST | S.R.22 | CLARKSBURG | CARROLL | TN | 38324 | 3 | NO | 930 | 1996-03-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19960311 | 30 | 55 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | NOT GIVEN | STEEL |  | 0.75 | 0.113 |  |  | 1970 | 1970 | OTHER | BELL HOLE | JAMES I. WEBB | 9019868289 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INCIDENT OCCURRED WHEN A EMPLOYEE OF HUGHEY CONSTRUCTION COMPANY OF WAVERLY, TENNESSEE, UNDER CONTRACT WITH WEST TENNESSEE PUBLIC UTILITY DISTRICT TORELOCATE NATURAL GAS LINES DUE TO THE ROAD CONSTRUCTION ON HIGHWAY 22 IN CARROLL COUNTY, TENNESSEE. THE EMPLOYEE USED IMPROPER PROCEDURES WHEN CUTTING A 3/4" STEEL SERVICE LINE INTO WITH A GRINDER. THIS ACTION CREATED SPARKS WHICHIGNITED THE GAS RESULTING IN MINOR BURNS TO THE FACE. THE EMPLOYEE REQUIRED OVERNIGHT HOSPITAL CONFINEMENT FOR OBSERVATION.
2025-01-31 10:21 | NO | NO | 19960072 | 1996-04-16 | 15007 | PACIFIC GAS & ELECTRIC CO | 2300 WALSH AVENUE | SANTA CLARA | SANTA CLARA | CA |  | 3 | NO | 1100 | 1996-03-14 | 0 | 0 | 60000 | 43183.93 | 104266.1929 | Null | 5 | 49 |  | 19960315 | 50 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | TR418 |  | 0 | 1973 | UNDER GROUND OR UNDER WATER |  | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-03-08 | YES | 3 | TEMPORARY FLAGS | YES |  |  | LINE WAS MARKED INACCURATELY. CITY OF SANTA CLARA WATER DEPARTMENT STRUCK 4-INCH PLASTIC MAIN WHILE EXCAVATING FOR A FIRE HYDRANT.
2025-01-31 10:21 | YES | NO | 19960073 | 1996-04-12 | 22763 | WISCONSIN GAS CO | 2610 THIRD STREET SOUTH | WISCONSIN RAPIDS | WOOD | WI | 54494 | 3 | NO | 900 | 1996-04-01 | 0 | 0 | 70000 | 50381.2517 | 121643.8918 | Null | 1 | 0 |  | 19960402 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER | NOT GIVEN | 0.75 | 0.113 | GRADE B |  | 0 | 1962 | ABOVE GROUND |  | GREGORY B. SCHROEDER | 4142916729 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null |  |  | ON APRIL 1, 1996, AN EXPLOSION OCCURRED IN A HOME AT 2610 THIRD STREET SOUTHIN WISCONSIN RAPIDS. TWO OCCUPANTS WERE ON THE PREMISES AT THE TIME OF THE EXPLOSION BUT ESCAPED WITHOUT INJURY. APPROXIMATELY $70,000 OF DAMAGE OCCURRED TO THE HOME. NATURAL GAS HAD LEAKED INTO THE HOME FROM A BREAK IN THE SERVICE RISER PIPE JUST BELOW THE METER SHUT OFF VALVE. THE SOURCE OF IGNITION OF THE NATURAL GAS WAS NOT DETERMINED. A BUILDING ADDITION WAS UNDER CONSTRUCTION AT THE RESIDENCE. ON DECEMBER 12, 1995, THE METER SET HAD BEEN RELOCATED BYWISCONSIN GAS TO A WALL OF THE NEW ADDITION. THE SERVICE PIPE NEST TO THE BUILDING AND THE RISER WERE EXPOSED BY THE CONSTRUCTION AND UNSUPPORTED AT THE TIME OF THE INCIDENT. THAWING AND SUBSIDENCE OF THE SOIL BELOW THE SERVICE LINE PLACED A DOWNWARD FORCE ON THE EXPOSED RISER WHICH MAY HAVE STRESSED THE PIPE AND CAUSED IT TO CRACK.
2025-01-31 10:21 | YES | YES | 19960074 | 1996-04-10 | 2568 | COLORADO SPRINGS, CITY OF | 7241 RISING MOON DRIVE | COLORADO SPRINGS | EL PASO | CO | 80919 | 3 | NO | 1243 | 1996-03-13 | 0 | 1 | 200000 | 143946.4335 | 347553.9765 | Null | 1 | 37 |  | 19960313 | 32 | 34 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE2306 |  | 0 | 1982 | UNDER GROUND OR UNDER WATER |  | WAYNE E. BOOKER | 7196365722 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | IN THE PROCESS OF ADDING A BASEMENT WINDOW TO THE RESIDENCE, A CONTRACTOR HAND EXCAVATED TO INSTALL A WINDOW WELL AND EXPOSED THE GAS SERVICE LINE WHICH WAS LOCATED APPROXIMATELY 4 INCHES LATERALLY FROM THE EXTERIOR BASEMENT WALL.CONTRACTOR PROCEEDED TO SAW A HOLE FOR THE NEW WINDOW IN THE CONCRETE BASEMENT WALL FROM INSIDE THE BUILDING USING A 32 INCH DIAMETER CONCRETE SAW. THE SAW CUT/NICKED THE SERVICE LINE AND GAS BEGAN ENTERING THE BUILDING THROUGH THE SAW CUT. WHEN THE CONTRACTOR SMELLED GAS HE WENT OUTSIDE TO INVESTIGATE. WHILE INVESTIGATING, GAS IGNITED FROM THE BLOWING SERVICE LINE AND THE BUILDINGEXPLODED. THE SOURCE OF IGNITION IS BELIEVED TO BE THE PILOT LIGHT ON THE FURNACE. REF - PART1 ITEM 4) THE TELEPHONIC REPORT FOR THIS INCIDENT INDICATED 1 INJURY REQUIRING INPATIENT HOSPITALIZATION. THE INJURED PARTY WS ACTUALLY TREATED AND RELEASED FROM THE EMERGENCY ROOM AND NOT HOPITALIZED.
2025-01-31 10:21 | YES | NO | 19960075 | 1996-04-04 | 15350 | PEOPLES NATURAL GAS CO | 3218 GORSUCH LANE | HOPEWELL TOWNSHIP | BEAVER | PA |  | 3 | NO | 2300 | 1996-03-06 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 0 | 15 |  | 19960307 | 38 | 40 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 | MODEL 173 | ROCKWELL | 0 | 1953 | ABOVE GROUND |  | JOYCE C. DAILEY | 4124975668 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE SERVICE REGULATORY ON THE METER SET SUPPLYING GAS TO THE RESIDENCE FAILED TO OPERATE PROPERLY AND ALLOWED 6 PSIG GAS PRESSURE TO ENTER THE HOUSE AND ITS GAS APPLIANCES. FLAMES FROM A GAS WAER HEATER MAY HAVE INITIATED THE FIRETO THE RESIDENCE WHICH SUSTAINED CONSIDERABLE DAMAGE. WEATHER AT THE TIME OFTHE INCIDENT WAS COLD WITH FREEZING RAIN IN THE AIR. FURTHER INVESTIGATION AND ANALYSIS OF THE SERVICE REGULATOR IS PLANNED
2025-01-31 10:21 | YES | YES | 19960076 | 1996-04-22 | 22182 | WASHINGTON GAS LIGHT CO | 11405 TRILLUM STREET | BOWIE | PRINCE GEORGES | MD | 20721 | 3 | NO | 1051 | 1996-03-23 | 0 | 1 | 13871 | 9983.4049 | 24104.606 | Null | 1 | 16 |  | 19960323 | 35 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD 2513 | UPONOR | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | JOHN C. SHEA | 7037505631 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-03-15 | YES | 3 | PAINT | YES |  |  | THIS INCIDENT IS A RESULT OF A CABLE SUBCONTRACTOR BORING UNDER THE ROAD. THE SUBCONTRACTOR BORED THROUGH A BURIED 2" PLASTIC MAIN, CAUSING NATURAL GAS TO ESCAPE. THE ESCAPING GAS WAS VENTING OUT OF THE GROUND AND TRAVELLING AIRBORNE THROUGH THE SUBDIVISION. A WASHINGTON GAS COMPANY CREW LEADER OPERATING ASMALL BACKHOE WAS EXCAVATING TO EXPOSE THE MAIN WHEN THE DIGIT CUTOFF. WHILETRYING TO RESTART THE DIGIT, THE MACHINE BACKFIRED AND IGNITED THE ECAPING GAS. THE DIGIT CAUGHT ON FIRE AND WAS EXTINGUISHED BY THE FIRE DEPARTMENT. THECREW LEADER WHO WAS BURNED ON HIS FACE WAS TRANSPORTED TO A LOCAL HOSPITAL, TREATED AND ULTIMATELY ADMITTED.
2025-01-31 10:21 | YES | YES | 19960078 | 1996-04-30 | 4483 | ENSTAR NATURAL GAS CO | 137 W. 13TH AVENUE | ANCHORAGE |  | AK | 99501 | 3 | NO | 226 | 1996-04-24 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 58 |  | 19960424 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | PHILLIPS DRISCOPIPE | 1982 | 1982 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | AT APPROXIMATELY 2:30 AM AST, WEDNESDAY MORNING, APRIL 24, 1996, A FIRE OF UNKNOWN ORIGIN DEVELOPED INSIDE THE STRUCTURE AT 137 W. 13TH AVE., ANCHORAGE, ALASKA. THE FIRE CAUSED ONE FATALITY AND DESTROYED THE STRUCTURE. THE FIRE BURNED THE GAS METER AND REGULATOR ASSEMBLY AND MELTED THE 5/8" HDPE SERVICE LINE INSIDE THE STTEL RISER, CAUSING A RELEASE OF NATURAL GAS. THE STEEL RISER WAS CUT AND THE HDPE SERVICE LINE WAS PINCHED OFF TO STOP THE FLOW OF GAS. NATURAL GAS SERVICE TO THE STRUCTURE HAD BEEN PREVIOUSLY DISCONTINUED AND THE SERVICE VALVE ON THE RISER WAS CLOSED AND LOCKED. NATURAL GAS DID NOT CONTRIBUTE TO THE CAUSE OF THE FIRE.
2025-01-31 10:21 | YES | YES | 19960079 | 1996-04-24 | 18536 | SOUTHWEST GAS CORP | 48TH STREET AND BASELINE ROAD | TEMPE | MARICOPA | AZ | 85044 | 3 | NO | 2301 | 1996-03-31 | 1 | 0 | 7475 | 5379.998 | 12989.8299 | Null | 1 | 21 |  | 19960401 | 275 | 275 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | DISTRICT REGULATOR STATIO | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API5L | TEXTUBE | 1987 | 1987 | ABOVE GROUND |  | PHILLIP S. ANDREW | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | A VEHICLE WAS WESTBOUND ON BASELINE ROAD. WHEN IT VEERED ACROSS THE EASTBOUND LANES AND COLLIDED WITH AN ABOVE-GROUND REGULATOR STATION. THE DRIVER WAS TRANSPORTED TO THE HOSPITAL AND LATER DIED FROM INJURIES SUSTAINED IN THE COLLISION.
2025-01-31 10:21 | YES | YES | 19960080 | 1996-04-24 | 4499 | ENTEX - DIVISION OF ARKLA INC | 4025 BURKE (4000 BLK.WATTERS) | PASADENA | HARRIS | TX | 77504 | 3 | NO | 1211 | 1995-12-17 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 14 |  |  | 30 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE2306 | DUPONT | 0 | 1976 | UNDER PAVEMENT |  | JOE HURST | 7136545900 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 3/4" PLASTIC SERVICE INE FAILED DUE TO EXTERNAL STRESS FROM IMPROPER BACKFILLING OPERATION BY UNKNOWN PARTY.
2025-01-31 10:21 | NO | NO | 19960083 | 1996-05-20 | 13480 | NIAGARA MOHAWK POWER CORP | 131 EAST WARRINGTON ROAD | SYRACUSE | ONONDAGA | NY | 13205 | 2 | NO | 1320 | 1996-04-15 | 0 | 0 | 60000 | 43183.93 | 104266.1929 | Null | 0 | 20 |  | 19960415 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | BUILDING OWNERS FUEL LINE | OTHER | NOT GIVEN | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LEONARD E. SNOW | 3154601481 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | DAMAGE DIRECTLY ATTRIBUTED TO PROPERTY OWNER WORKING ON GAS FUEL LINES INSIDE BUILDING. INCIDENT LABELED ACCIDENTAL BY CITY OF SYRACUSE FIRE INVESTIGATION TEAM.
2025-01-31 10:21 | YES | YES | 19960084 | 1996-05-17 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 6218 SONHAVEN | SHREVEPORT | CADDO | LA | 71129 | 3 | NO | 207 | 1996-05-01 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 16 |  | 19960501 | 15 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RON SHEPHERD | 3184294162 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | RESIDENCE AT 6218 SONHAVEN, SHREVEPORT, LA, CAUGHT FIRE CAUSING (3) INJURIES AND (2) PERSONS REQUIRING HOSPITALIZATION. CAPTAIN ROBERT MCWHERTER OF SHREVEPORT FIRE DEPARTMENT REPORTED CAUSE OF FIRE WAS NON-GAS RELATED AFTER INVESTIGATION. HOUSE FIRE AT ABOVE ADDRESS; 3 INJURED REQUIRING (2) TO BEHOSPITALIZED, RESULTING IN ONE FATALITY AND ONE LATER RELEASED.
2025-01-31 10:21 | YES | YES | 19960085 | 1996-05-21 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 515 S. PECAN STREET | VIVIAN | CADDO | LA | 71082 | 3 | NO | 110 | 1996-05-09 | 1 | 0 | 0 | 0 | 0 | Null | 2 | 0 |  | 19960509 | 20 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | STEVE BARTLETT | 3184294151 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ELECTRICAL FIRE DOMESTIC RESIDENCE. FRAYED CORD ON ELECTRIC DRYER SHORTED OUT CAUSING FIRE.
2025-01-31 10:21 | YES | NO | 19960086 | 1996-05-21 | 12438 | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | 325 MCKINNON BOULEVARD | MCMINNVILLE | WARREN | TN | 37110 | 2 | NO | 900 | 1996-04-20 | 0 | 0 | 150000 | 107959.8251 | 260665.4824 | Null | 0 | 48 |  | 19960422 | 45 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 | 0.113 | ASTM A53 | GRINNELL | 1990 | 1990 | ABOVE GROUND |  | JAMES E. HODGES | 6155974300 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WIND AND RAIN STORM BLEW DOWN APPROXIMATELY AN 18" DIAMETER TREE IN THE YARDAT 325 MCKINNON. WHEN THE TREE FELL, IT HIT THE METER SET BREAKING THE STEEL PIPE AT THE THREADS JUST DOWNSTREAM OF THE METER STOP, BEFORE THE SERVICE REGULATOR. THE ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE AND AN ESTIMATED $150,000 IN DAMAGE TO THE RESIDENCE RESULTED. NO ONE WAS HOME AT THE TIME OF THE INCIDENT. BECAUSE OF THE FIRE, THE SERVICE LINE HAD TO BE EXCAVATED AND SHUT OFF AT THE STREET. GAS WAS SHUT OFF TO THE HOUSE APPROXIMATELY 48 MINUTESAFTER THE CALL WAS RECEIVED.
2025-01-31 10:21 | NO | NO | 19960087 | 1996-05-28 | 11032 | LACLEDE GAS CO | 952 BARRETT STATION ROAD | KIRKWOOD | ST LOUIS | MO | 63122 | 3 | NO | 852 | 1996-05-04 | 0 | 0 | 60000 | 43183.93 | 104266.1929 | Null | 0 | 30 |  | 19960504 | 14 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY | METER | OTHER | METER | OTHER | TIN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | PAUL B. HUNKER | 3143420528 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | LIGHTNING STRUCK A NEARBY TREE AND TRAVELED TO METER, DAMAGING SAME. OUTSIDEGAS METER WAS SITUATED ON THE SOUTH SIDE OF THE BUILDING AND CAUGHT FIRE.
2025-01-31 10:21 | NO | NO | 19960088 | 1996-05-28 | 12684 | MONTANA - DAKOTA UTILITIES CO | 549 SE 3RD STREET | MALTA | PHILLIPS | MT | 59538 | 3 | NO | 830 | 1996-04-29 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 5 |  | 19960429 | 13 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | OTHER | NOT GIVEEN | STEEL |  | 1 | 0.133 | SCHED 40 |  | 0 | 1996 | ABOVE GROUND |  | RONALD E. BLUM | 7012227924 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | EXPLOSION | Null |  | Null | 0 |  | Null |  |  | POST-INCIDENT INVESTIGATION SHOWED THAT THE INITIAL EXPLOSION WAS NOT CAUSEDBY LEAKAGE FROM JURISDICTIONAL PIPING. EXPLOSION OF UNKNOWN ORIGIN INSIDE BUILDING COLLAPSED ROOF ON METER SET CAUSING LEAKAGE.
2025-01-31 10:21 | NO | NO | 19960089 | 1996-05-29 | 15007 | PACIFIC GAS & ELECTRIC CO | 3-4 MILES EAST OF COALINGA | COALINGA | FRESNO | CA |  | 1 | NO | 1300 | 1996-04-27 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 3 | 0 |  | 19960427 | 198 | 218 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER |  | REGULATOR/METER |  | STEEL |  | 4 | 0 |  | SINGER | 1953 | 1954 | UNDER GROUND OR UNDER WATER |  | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | GRASS FIRE IGNITED WOOD STRUCTURE FAILING REGULATOR CAUSING OVERPRESSURE.
2025-01-31 10:21 | YES | YES | 19960093 | 1996-06-10 | 2596 | COLUMBIA GAS OF OHIO INC | 622 SACKETT STREET & SPRING STREET | MAUMEE | LUCAS | OH | 43537 | 3 | NO | 1054 | 1996-05-10 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19960510 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT GIVEN | OTHER | NOT GIVEN | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DONALD E. WILLIAMS | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INCIDENT IS STILL UNDER INVESTIGATION. AN OUTSIDE AGENCY HAS BEEN ENGAGED. CURRENTLY NATURAL GAS CAN NOT BE CONFIRMED NOR DENIED AS THE CAUSE. A FINAL REVISED REPORT WILL BE FILED AT THE CONCLUSION OF THIS INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19960096 | 1996-06-18 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | SIMMONS ROAD | WEST BRANCH | OGEMAW | MI | 48661 | 1 | NO | 1400 | 1996-05-10 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 0 | 5 |  | 19960520 | 750 | 1300 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | PIG RECEIVER TRAN.LINE | VALVE | CLOSURE DOOR | OTHER | NOT GIVEN | 10 | 0 | 10" STEEL | GROVE - VALVE | 1990 | 1990 | ABOVE GROUND |  | THOMAS P. FUNTSCH | 3135777026 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | DUE TO DESIGN, NO REPRESSURE EQUALIZER LINE.
2025-01-31 10:21 | YES | NO | 19960097 | 1996-06-20 | 15462 | PHILADELPHIA ELECTRIC CO | 16 STEEPLE CHASE DRIVE | DOYLESTOWN | BUCKS | PA | 18901 | 3 | NO | 730 | 1996-05-21 | 0 | 0 | 350000 | 251906.2585 | 608219.4589 | Null | 1 | 2 |  | 19960521 | 49 | 99 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 | ASTM-A53 |  | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | JOSEPH E. HOFFMAN | 6109411529 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 5/21/96 A NATURAL GAS EXPLOSION OCCURED AT 16 STEEPLECHASE DR. INDYLESTOWN, PA. PRIOR TO THE EXPLOSION, AN UNDERGROUND ELECTRIC CABLE FAULTWAS EXPERIENCED IN THE AREA OF 16 STEEPLECHASE DR. THE SOURCE OF THE NATURALGAS WAS A GAS MAIN WHICH HAD BEEN DAMAGED BY THE UNDERGROUND ELECTRIC CABLEFAULT. AS A RESULT OF THE DAMAGE TO THE PIPE, LEAKING NATURAL GAS MIGRATEDINTO THE STRUCTURE LOCATED AT 16 STEEPLECHASE DR. THE ENSUING EXPLOSIONRESULTED IN STRUCTURAL DAMAGE WHICH REQUIRED THE BUILDING TO BE DEMOLISHED.THERE WERE NO INJURIES AS A RESULT OF THE INCIDENT. PER TELEPHONE 7/25/1996,THE CAUSE WILL REMAIN OTHER. UPON CONSULTATION WITH PECO LEGAL, MR. JOE EAGLESTATED THAT THE INCIDENT WAS NOT RELATED TO DAMAGE BY OUTSIDE FORCE.
2025-01-31 10:21 | NO | NO | 19960098 | 1996-06-11 | 2596 | COLUMBIA GAS OF OHIO INC | YORK STREET & OTTER CREEK ROAD | OREGON | LUCAS | OH | 43616 | 1 | NO | 1530 | 1996-05-08 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 29 | 0 |  | 19960508 | 138 | 145 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 20 | 0.25 | GRADE B |  | 0 | 1964 | UNDER GROUND OR UNDER WATER |  | DONALD E. WILLIAMS | 6144606366 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-04-19 | YES | 2 | PAINT | YES |  |  | A CONTRACTOR INSTALLING A WATER LINE STRUCK AND DAMAGED A 20" HIGH PRESSURE STEEL GAS MAIN. THE MAIN HAD BEEN LOCATED, STAKED AND MARKED WITH MARKING PAINT. THE LINE WAS OPERATING AT 138 PSIG. ATTEMPTS TO REPAIR THE LINE BY REDUCINGTHE PRESSURE TO 50 PSIG AND MAKING REPAIRS WITH A CLAMP AND SPLIT-SLEEVE FAILED AND A SECTION THE LINE HAD TO BE REPLACED USING 20" STOPPLE FITTINGS INCREASING THE DAMAGE COSTS BEYOND THE $50,000 REPORTING LEVEL.
2025-01-31 10:21 | YES | NO | 19960099 | 1996-06-24 | 13660 | NORTH SHORE GAS CO | 15366 FAIR LANE DRIVE | LIBERTYVILLE | LAKE | IL | 60048 | 3 | NO | 910 | 1996-05-24 | 0 | 0 | 200000 | 143946.4335 | 347553.9765 | Null | 0 | 20 |  | 19960524 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.25 |  |  | 0 | 1965 | ABOVE GROUND | ADJACENT TO BUILDING | T.C. ZIEGENFUSS | 8472634605 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | YES |  |  | A CAR LOST CONTROL WHILE IT WAS IN THE LEFT INSIDE LANE AND VEERED TO THE RIGHT CROSSING THE RIGHT LAND AND JUMPED THE CONCRETE CURB. CAR CONTINUED OVER THE GRASS EASEMENT, CRASHED THROUGH A 6-FOOT TALL STOCKADE FENCE AND SMALL TREES AND BRUSH AND THEN STRUCK THE GAS METER LOCATED ON THE NORTH SIDE OF THE HOUSE AT 15366 FAIR LANE. THE CRASH TORE OPEN THE GAS LINE AND A FIRE RESULTED WHICH RESULTED WHICH ENGULFED THE CAR AND THE HOUSE. THE HOUSE WAS OCCUPIEDBY THE HOMEOWNER DEBORAH CHARAPATA. SHE REPORTED HEARING AND EXPLOSION AND THEN SMOKE FILLED THE HOUSE. SHE WAS ABLE TO FLEE THE HOUSE WITH 2 CHILDREN WITHOUT INJURY. ALL OCCUPANTS OF THE CAR ALSO ESCAPED WITH MINOR INJURIES (NONEFIRE RELATED) AND WERE TREATED AT THE SCENE AND REFUSED TO BE TAKEN TO A HOSPITAL. THE FIRE DESTROYED THE HOUSE (ESTIMATED AT $180,000).
2025-01-31 10:21 | YES | NO | 19960100 | 1996-06-24 | 3240 | DELMARVA POWER & LIGHT CO | NAAMANS ROAD & SMITH LANE` | WILMINGTON | NEW CASTLE | DE | 19810 | 3 | NO | 1006 | 1996-06-04 | 0 | 0 | 200000 | 143946.4335 | 347553.9765 | Null | 0 | 50 |  | 19960604 | 35 | 60 | BY TEST | 96 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  | DUPONT | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | PHILIP L. PHILLIPS | 3024293846 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-05-30 | YES | 2 | PAINT | YES |  |  | OUTSIDE PARTY NOT HAND DIGGING TO LOCATE AS REQUIRED BY STATE STATUTE. HIGHWAY CONTRACTOR DAMAGED GAS MAIN WHILE EXCAVATING WITH TRACK-HOE. CONTRACTOR WAS EXCAVATING TO INSTALL STORM SEWER. OPERATOR HAD MARKED LINE FOR CONTRACTOR.CONTRACTOR HAD CONFIRMED TO OPERATOR HE WOULD TEST HOLE LINE TO AVOID CONFLICT. CONTRACTOR EXCAVATED WITH 36" TRACKHOE, SERVING 3" GASMAIN. SEVERAL MINUTES LATER GAS IGNITED, DAMAGING TRACK HOE AND OVER HEAD ELECTRIC, PHONE AND CABLE TVE WIRES. FIRE EXTINGUISHED WHEN GAS WAS SHUT OFF. NO EVIDENCE CONTRACTOR HAD DUG TO LOCATE GASOLINE OR TAKEN ALL REASONABLE STEPS NECESSARY TO PROPERLY PROTECTED THE GAS LINE.
2025-01-31 10:21 | NO | NO | 19960103 | 1996-06-26 | 4499 | ENTEX - DIVISION OF ARKLA INC | 6909 JAY | HOUSTON | HARRIS | TX | 77028 | 3 | NO | 20 | 1996-05-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19960527 | 28 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | NOT GIVEN | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JEFFREY A. BISH | 7139678093 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | HOUSE FIRE. FIRE STARTED ON WEST SIDE OF HOUSE NEAR UTILITY ROOM. FIRE SPREADFROM WEST TO EAST DAMAGING METER & REGULATORE ASSEMBLY, INGITING GAS _ NATURALGAS NOT INVOLVED IN INITIAL FIRE. SUPPLEMENTAL REC'D 7/22/1996 INDICATESCHANGE OF CAUSE FROM OTHER TO DAMAGE BY OUTSIDE FORCE.
2025-01-31 10:21 | NO | NO | 19960105 | 1996-07-03 | 15007 | PACIFIC GAS & ELECTRIC CO | 17300 REDWOOD ROAD | CASTRO VALLEY | ALAMEDA | CA |  | 3 | NO | 2145 | 1996-05-31 | 0 | 0 | 25000 | 17993.3042 | 43444.2471 | Null | 0 | 50 |  | 19960531 | 50 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | VEHICLE STRUCK METER LOCATION, CAUSING GAS TO ESCAPE UNDER BUILDING. THE GASUNDER THE BUILDING THEN IGNITED. THE RESULTING EXPLOSION AND FIRE CAUSED EXTENSIVE DAMAGE TO THE HOUSE.
2025-01-31 10:21 | YES | YES | 19960106 | 1996-07-05 | 2596 | COLUMBIA GAS OF OHIO INC | 9 RIVER DRIVE | ATHENS | ATHENS | OH | 45701 | 3 | NO | 1115 | 1996-05-30 | 2 | 0 | 0 | 0 | 0 | Null | 1 | 0 |  | 19960530 | 43 | 50 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | OTHER | NOT GIVEN | STEEL |  | 1.25 | 0 |  | LATTIMER STEVENS | 0 | 1963 | OTHER | OPEN BELL HOLE | DONALD E. WILLIAMS | 6144606366 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | TWO EMPLOYEES ATTEMPTING TO REPLACE A SERVICE LINE CURB VALVE DIED FROM APPARENT ACCIDENTAL ASPHYXIATION EXACT DETAILS ARE UNKNOWN AS THERE WERE NO WITNESSES. EMPLOYEES WERE FOUND IN EXCAVATION WITH BLOWING NATURAL GAS. OLD CURB VALVE HAD BEEN REMOVED FROM THE SERVICE LINE AND A NEW CURB VALVE WAS FOUND INEXCAVATION. CONTRARY TO COMPANY PROCEDURE, THERE WAS NO INDICATION THAT THEEMPLOYEES HAD UTILIZED OXYGEN MONITORS, SUPPLIED AIR PURGING OR VENTILATIONDEVICES TO ASSURE THAT AN OXYGEN DEFICIENT ATMOSPHERE DID NOT EXIST.
2025-01-31 10:21 | NO | NO | 19960107 | 1996-07-05 | 19775 | TWIN COUNTY GAS CO INC | 3211 SOUTH AVENUE D | WILSON | ELLSWORTH | KS | 67490 | 3 | NO | 450 | 1996-05-31 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 0 |  | 19960601 | 10 | 10 | BY TEST | 10 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | NOT GIVEN | OTHER | PVC | 1 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | GENE W. BURNS | 9136582511 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19960108 | 1996-07-08 | 8160 | INTERMOUNTAIN GAS CO | 3610 CLEVELAND BLVD | CALDWELL | CANYON | ID | 83605 | 2 | NO | 1150 | 1996-06-10 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19960610 | 175 | 200 | BY TEST | 300 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | OTHER | NOT GIVEN | STEEL |  | 0.75 | 0.113 | UNKNOWN | UNKNOWN | 1969 | 1969 | ABOVE GROUND |  | ELDON BOOK | 2083776088 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | 3/4" SERVICE PIPE FAILED AT CONTROL POINT WHERE SQUEEZE TOOL WAS IN USE, RESULTING IN ACCIDENTAL IGNITION.
2025-01-31 10:21 | NO | NO | 19960109 | 1996-07-08 | 4473 | ENERGAS CO | FM 1612 1 1/2 MI. N. OF FM 788 |  | HALE | TX | 79073 | 2 | NO | 1102 | 1996-06-22 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | YES | 1 | 15 |  | 19960624 | 25 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC | ABS | 3 | 0.115 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | GARY GREGORY | 8067984477 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1994-03-30 | NO | 0 |  | NO |  |  | DITCH APPEARED TO HAVE SETTLED AND BROKE PIPE. LEAKING GAS MIGRATED INTO STRUCTURE AND WAS IGNITED, POSSIBLY BY ELECTRICAL EQUIPMENT.
2025-01-31 10:21 | YES | NO | 19960113 | 1996-07-17 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 301 DEERCREEK DRIVE | TEXARKANA | MILLER | AR | 71854 | 2 | NO | 715 | 1996-06-15 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 1 | 20 |  | 19960615 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 1 | 0.133 | API5L | TEX TUBE | 1983 | 1983 | ABOVE GROUND |  | ORIS A. KEMP | 5017727146 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | CAR RAN OFF ROAD AND TRAVELED 237FT. HIT METER SETTING & HOUSE CAUSING AN IGNITION AND FIRE. DRIVER SITED FOR D.W.I.
2025-01-31 10:21 | YES | YES | 19960114 | 1996-07-22 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 508 N. MAIN (N. MAIN & BERYL) | SCOTTVILLE | MASON | MI | 49454 | 1 | NO | 1405 | 1996-07-10 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19960710 | 10 | 10 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | SERVICE SADDLE | STEEL |  | 4 | 0 |  |  | 0 | 1959 | OTHER | NOT GIVEN | ROGER J. GREGORY | 3135777045 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | ON 07/10/96, THIS INCIDENT WAS REPORTED TO D.O.T. ON THE BELIEF THAT THE EMPLOYEE'S INJURY REQUIRED INPATIENT HOSPITALIZATION. HOWEVER ON 07/10/96 AT 4:40PM WHEN WE CONFIRMED THE EMPLOYEE HAD BEEN TREATED AND RELEASED ON 07/10/96WE CALLED D.O.T. LT. PETTIFORD AND INFORMED HIM ACCORDINGLY AND ASKED TOCANCEL AND/OR CLOSE OUR ORIGINAL REPORT. WHILE REMOVING THE GAS SERVICESADDLE OFF THE MAIN, GAS LEAKED AND IGNITED FROM UNKNOWN IGNITION SOURCE.
2025-01-31 10:21 | YES | YES | 19960119 | 1996-07-25 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | SOUTH 8TH STREET | PASSAIC | PASSAIC | NJ | 07055 | 4 | NO | 1410 | 1996-06-11 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 2 | 346504 |  | 11.8 | 15 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | NOT GIVEN | OTHER | MALLABLE PLUG | 1 | 0 |  |  | 0 | 0 | OTHER | OPEN TRENCH | WILLARD S. CAREY | 2014307833 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON TUESDAY, JUNE 11, 1996 AT APPROXIMATELY 2:10 P.M., A 1" PLUG ON THE END OFAN 8" DRESSER END CAP WAS INADVERTENTLY REMOVED BY A UTILITY MECHANIC IN ANOPEN EXCAVATION. ONCE THE 1" PLUG WAS REMOVED, A RELEASE OF NATURAL GAS OCCURRED. THIS RELEASE WAS DIRECTED IN THE IMMEDIATE VICINITY OF PIPELINE WELDERIN THE SAME OPEN EXCAVATION WHO WAS IN PROCESS OF BURNING A 2" HOLE THROUGH ANEWLY INSTALLED 12" STEEL MAIN THAT HAD NOT BEEN PLACED INTO SERVICE. THE OPEN ACTYLENE TORCH IGNITED THE ESCAPING NATURAL GAS, ENGULFING BOTH EMPLOYEES AND THE ENTIRE EXCAVATION IN FLAMES. THE TWO EMPLOYEES ARE SERIOUSLY BURNED.
2025-01-31 10:21 | YES | YES | 19960120 | 1996-07-25 | 2416 | CITIZENS UTILITY CO | 2470 APACHE BLVD | NOGALES | SANTA CRUZ | AZ |  | 3 | NO | 815 | 1996-06-28 | 0 | 1 | 700 | 503.8125 | 1216.4389 | Null | 1 | 0 |  |  | 40 | 40 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NOT GIVEN | POLYETHYLENE PLASTIC |  | 1 | 0.128 | PE-3408 | PHILLIPS DRISCO | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RUSSELL L. VALLEIO | 5207617967 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-06-27 | YES | 1 | ONE-CALL- BLUESTAKE | YES |  |  | CALLED IN AS EMERGENCY BLUESTAKE #96261159. DURING LINE (P.E.) SQUEEZE OFF OF 1" LINE, GAS FOREMAN OVERCAME BY GAS FUMES.
2025-01-31 10:21 | YES | YES | 19960121 | 1996-07-26 | 12876 | MOUNTAIN FUEL SUPPLY CO | 898 SOUTH 1650 EAST | SPRINGVILLE | UTAH | UT | 84663 | 3 | NO | 1410 | 1996-07-08 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 39 | 350912 | 19960708 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D 2513 | PLEXCO | 1994 | 1994 | UNDER GROUND OR UNDER WATER |  | EDWARD B. KELSEY | 8015393619 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-07-03 | YES | 3 | PAINT/WIRE FLAG | YES |  |  | ON JULY 8, 1996, MR. RICK ASHCROFT, OWNER/OPERATOR OF CEDAR FENCE COMPANY WAS DIGGING 5-FOOT DEEP FENCE POST HOLES USING A CASE AUGER MACHINE. DURING THEPROCESS HE HIT A 2-INCH PLASTIC DISTRIBUTION MAIN. THIS RESULTED IN A FIRE BURNING MR. ASHCROFT, THE CASE AUGER MACHINE, A 1985 CHEVROLET PICKUP AND CAUSING DAMAGE TO A TREE AND LAWN AREA. ESTIMATED DAMAGE WAS APPROXIMATELY $20,000. MR. ASHCROFT HAD BURNS ON HIS ARMS, LEGS AND CHEST. HE WAS ADMITTED TO UTAH VALLEY REGIONAL MEDICAL CENTER AND LATER TRANSFERRED TO THE UNIVERSITY OF UTAH BURN CENTER. A REQUEST TO THE ONE-CALL CENTER WAS PROCESSED PRIOR TO THISINCIDENT. THESE PIPE MARKS WERE ACCURATE AND VISIBLE AT THE TIME OF THE INCIDENT. UTAH LAW REQUIRES HAND DIGGING WHEN EXCAVATING/DIGGING IN CLOSE PROXIMITY TO NATURAL GAS PIPE LINES.
2025-01-31 10:21 | YES | YES | 19960122 | 1996-08-09 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 525 STATE ST | NEW ORLEANS |  | LA |  | 0 | NO | 1414 | 1996-08-01 | 0 | 1 | 80000 | 57578.5734 | 139021.5906 | Null | 0 | 6 |  | 19960801 | 0.25 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S HOME | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RICHARD TORRES | 5045953750 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | PARTY AT ABOVE MENTIONED ADDRESS WAS ATTEMPTING TO LITE KITCHEN STOVE WHEN EXPLOSION OCCURED, BLOWING THE RIGHT SIDE WALL OUT INTO THE SIDE YARD. PARTY WAS TAKEN TO THE HOSPITAL WITH BURNS.
2025-01-31 10:21 | YES | YES | 19960123 | 1996-07-30 | 1800 | BROOKLYN UNION GAS CO | STILLWELL AVE & NEPTUNE AVE | BROOKLYN | KINGS | NY | 11223 | 4 | NO | 1538 | 1996-07-06 | 0 | 12 | 0 | 0 | 0 | Null | 10 | 27 |  | 19960706 | 0.25 | 0.43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 10 | 0 |  |  | 0 | 1912 | UNDER PAVEMENT |  | FRANK MARCAZZO | 7184032864 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-07-06 | YES | 3 | PAINTED MARKERS | YES |  |  | THIRD PARTY DAMAGE OF 10 INCH CAST IRON LOW PRESSURE GAS MAIN, SUBSEQUENT IGNITION, SOURCE OF WHICH STILL UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 19960124 | 1996-08-01 | 7040 | HAMILTON GAS DEPT, CITY OF | 528 SYCAMORE ST | HAMILTON | BUTLER | OH | 45011 | 3 | NO | 2045 | 1996-07-25 | 0 | 0 | 20000 | 14394.6433 | 34755.3976 | Null | 1 | 0 |  | 19960725 | 0.25 | 0.5 | BY TEST | 10 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE PIPING | OTHER | NONE SPECIFIED | STEEL |  | 1.25 | 0.14 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN LIVER | 5138685901 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | At approximately 8:45p.m. on Thursday, July 25, 1996; I received a phone call from the Clerk-Guard on duty advising me that we had a gas explosion at 528Sycamore Street. I arrived at the scene at approximately 9:15p.m. and immediately inquired of the Utilities Troubleshooter on duty (Clark Robinson) as tothe information he had been able to ascertain. He advised me that the owner of the property (Mr. Green Woolum) had advised him that at approximately 6:00p.m., he had turned the gas on at the meter and lit the pilot lights on the hot water heater and the kitchen stove. The meter and the hot water heater arelocated in a utility room at the front of the house and are separated by a wall. On the piping from the meter to the hot water tank is a tee. On the outlet side of this is a 1/2" shut-off valve and approximately five (5) feet of 3/8" flexible piping which runs through the back wall of the utility room intoa laundry room. This 1/2" shut off valve was in the open position when the Fire Department arrived on the scene. the 3/8" flexible piping was not connected to any appliance and was allowing gas to escape into the house. No one wasin the residence at the time of the accident. From my investigation at the scene, this escaping gas was ignited by the pilot light on the kitchen stove which was the direct cause of the explosion. We have pressure-tested the service line and the house piping and both lines passed the pressure test. I belive the failure of the property owner to close the 1/2" shut off valve prior toturning the gas on at the meter was the direct cause of this accident.
2025-01-31 10:21 | YES | YES | 19960125 | 1996-08-02 | 13480 | NIAGARA MOHAWK POWER CORP | 2475 BRICKYARD ROAD | VAN BUREN | ONONDAGA | NY |  | 2 | NO | 1310 | 1996-07-22 | 0 | 3 | 75000 | 53979.9125 | 130332.7412 | Null | 0 | 35 |  | 19960722 | 7 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY | CUST INTERNAL FUEL LINE | FITTING |  | STEEL |  | 1 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PETER GEATRAKAS | 3154285077 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | While third party was excavating, pulled apart customer-owned fuel line and filled house with gas; unknown ignition caused explosion. Report to DOT PettiOfficer - Fink Beiner. Residential Customer fuel line. CONTRACTOR PULLEDMETER CONNECTION BREAKING LINE INSIDE HOME. HE FAILED TO REQUEST STAKEOUTSERVICE.
2025-01-31 10:21 | YES | YES | 19960126 | 1996-08-12 | 18088 | SALEM, CITY OF | 919 W. ELM | SALEM | MARION | IL | 62881 | 3 | NO | 408 | 1996-07-07 | 0 | 3 | 0 | 0 | 0 | Null | 0 | 30 |  | 19960707 | 0.25 | 16 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | NONE SPECIFIED | OTHER | COPPER | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT ERXLEBEN, JR. | 6185483116 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | It is assumed that the probable cause of the explosion was a disconnectedcopper fuel line to the h ot water heater.
2025-01-31 10:21 | YES | YES | 19960127 | 1996-08-13 | 18116 | SAN JUAN GAS CO | #5 ARECIHO STREET | HATO REY | SAN JUAN | PR | 00919 | 3 | NO | 1115 | 1996-07-15 | 0 | 2 | 30000 | 21591.965 | 52133.0965 | Null | 2 | 10 |  | 19960715 | 25 | 35 | BY TEST | 55 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | SEE DESCRIPTION | STEEL |  | 2.37 | 0.154 | GRADE B |  | 1954 | 1954 | OTHER | BELLHOLE | DONNIE WILLMANN | 7138537471 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | At approximately 11:15am on July 15, 1996, gas under 25 psig ignited from anundetermined source while two San Juan Gas Co. employees were working in a hellhole on Arecibo Street in San Juan, Puerto Rico. The two men were attempting to install a Dresser coupled, 2.375 inch o.d. replacement plastic valve assembly on a 2.375 inch o.d. bare steel main with an operating pressure of 25 psig. The installation, preparatory to inserting plastic pipe inside the main, was being carried out without first isolating the segment of gas main on which they were working. The two men in the bellhole received burn injuries: pme suffered first and second degree burns over 21% of his body and the other received first and second degree burns over 7% of his body. The employee receiving burns over 7% of his body was released from the hospital on August 9, 1996. The other employee will probably be in the hospital at least another 30 days. The supervisor and a consultant received less serious burns and did notrequire hospitalization, but did require medical treatment. Property damage is estimated at less than $30,000. The primary cause of this accident was thefailure to follow San Juan Gas Co. Operations and Maintenance Procedure 2.08which requires isolation of the segment of pipe prior to beginning the process of plastic pipe insertion.
2025-01-31 10:21 | YES | YES | 19960128 | 1996-08-09 | 12350 | MINNEGASCO INC | 171ST STREET & JACKSON TRAIL | LAKEVILLE | DAKOTA | MN | 55044 | 3 | NO | 1000 | 1996-07-09 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19960709 | 50 | 60 | BY TEST | 64 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | TAPPING TEE | FITTING |  | POLYETHYLENE PLASTIC | POLYETHYLENE PLASTIC | 2 | 0.216 | ASTM 02513 | UPONOR | 1994 | 1994 | OTHER | OPEN EXCAVATION | EUGENE SCHULTZ | 6123214756 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | A high-volume tapping tee was being installed, The heating iron did not havea recessed face and went above maximum allowed temp.
2025-01-31 10:21 | YES | NO | 19960130 | 1996-08-20 | 22182 | WASHINGTON GAS LIGHT CO | 802 GREEN STREET | ALEXANDRIA |  | VA | 22314 | 3 | NO | 1621 | 1996-07-17 | 0 | 0 | 650000 | 467825.9087 | 1129550.4236 | YES | 0 | 23 |  | 19960717 | 20 | 25 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | OVERPRESSURING OF CUST PI | OTHER | REGULATOR NOT INSTALLED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN SHEA | 7037505631 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JULY 17, 1996, THE GAS UTILITY COMPANY WAS IN THE PROCESS OF CONVERTING ALOW PRESSURE (7.5" WATER COLUMN) GAS DISTRIBUTION SYSTEM TO A HIGH PRESSURE (20 PSIG) GAS SYSTEM. AT 4:21 P.M.(EST.) AFTER ACHIEVING 20 PSIG GAS DISTRIBUTION PRESSURE, AN EXPLOSION OCCURRED DAMAGING TWO TOWNHOUSE TYPE STRUCTURES. THERE WERE NO INJURIES, AND THE GAS TO THE SYSTEM WAS SHUT DOWN TO MAKE THE AREA SAFE. FUTHER INVESTIGATION REVEALED THAT THE TOWNHOUSE AT 802 GREEN STREET HAD NOT BEEN UPGRADED WITH A HIGH PRESSURE HOUSE REGULATOR, ALLOWING HIGH PRESSURE GAS TO ENTER THE BUILDING.
2025-01-31 10:21 | YES | NO | 19960131 | 1996-08-19 | 12684 | MONTANA - DAKOTA UTILITIES CO | 209 SE 9TH AVE. | SIDNEY | RICHLAND | MT | 59270 | 3 | NO | 1425 | 1996-07-16 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 0 | 20 |  | 19960717 | 0.31 | 2 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | RONALD BLUM | 7012227924 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | BUILDING FIRE | Null |  | Null | 0 |  | Null |  |  | AN INVESTIGATION DETERMINED THAT THE GAS LEAKAGE FROM THE METER SET WAS SECONDARY AND RESULTED WHEN THE BUILDING FIRE DAMAGED THE METER AND REGULATOR. A BUILDING FIRE CAUSED A WALL TO COLLAPSE ON A METER SET CAUSING THE METER SET TO LEAK.
2025-01-31 10:21 | YES | NO | 19960132 | 1996-08-22 | 22756 | WISCONSIN FUEL & LIGHT CO | 310 SEVENTH STREET | WAUSAU | MARATHON | WI | 54403 | 3 | NO | 923 | 1996-07-24 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 0 | 10 |  | 19960724 | 40 | 80 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1963 | WITHIN/UNDER BUILDING |  | DANIEL BEIGHLEY | 7158452141 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-07-23 | NO | 0 | NONE SPECIFIED | YES |  |  | MERRILL GRAVEL & CONSTRUCTION COMPANY, 2505 EAST STURDEVANT STREET, MERRILL,WI 54452, WAS A WAUSAU, WI. THE PROJECT SPANNED SEVEN BLOCKS, FROM FOREST STREET ON THE SOUTH TO FRANKLIN STREET ON THE NORTH. WORK HAD BEEN UNDERWAY FORSEVERAL WEEKS AT THE TIME OF THE INCIDENT. MERRILL GRAVEL & CONSTRUCTION HADCONTACTED DIGGERS HOTLINE ON A NUMBER OF OCCASIONS TO ARRANGE FOR UNDERGROUND FACILITIES TO BE LOCATED AND MARKED. THIS INCLUDED ONGOING RELOCATES AS THEPROJECT PROGRESSED. ON JULY 24, 1996, MERRILL GRAVEL & CONSTRUCTION COMPANY WAS EXCAVATING BELOW SUBGRADE TO REMOVE SOME UNDESIRABLE SOIL BACKFILL ON THEWEST SIDE OF SEVENTH STREET. THE EXCAVATION WAS MADE NEAR THE ALLEY ENTRANCEAT APPROX THE MIDDLE OF THE 300 BLOCK, BETWEEN WASHINGTON AND JEFFERSON STREETS. AT APPROX 9:23 A.M., ANNIE MYER OF MERRILL GRAVEL & CONSTRUCTION NOTIFIED WISCONSIN FUEL & LIGHT CO (WF&L) THAT A STEEL GAS SERVICE HAD BEEN HOOKED IN THE 300 BLOCK OF SEVENTH STREET, WITH GAS LEAKING. WF&L RESPONDED BY DISPATCHING A CONTRACTOR REPRESENTATIVE, AN EMERGENCY REPAIR VEHICLE AND A TWO-PERSON CONSTRUCTION/CREW. AT APPROX 9:33 A.M., A WF&L EMPLOYEE AT THE SITE REPORTED BACK TO THE COMPANY'S RADIO DISPATCHER THAT THE 1 1/4" STEEL SERVICE TO 620 WASHINGTON STREET HAD BEEN SUCCESSFULLY SQUEEZED OFF AND THE LEAK HAD BEEN CONTROLLED. (IT IS CRITICAL TO NOTE HERE THAT ALTHOUGH THE TIME WHICH ELAPSEDBETWEEN THE NOTIFICATION OF THE DAMAGE TO WF&L AND CONTROL OF THE LEAK BY COMPANY PERSONNEL WAS ONLY 10 MINS., IT IS UNKNOWN HOW MUCH TIME PASSED BETWEENTHE POINT AT WHICH THE ACTUAL DAMAGE OCCURRED AND THE TIME AT WHICH WF&L WASNOTIFIED. SEVERAL FACTORS CONTRIBUTED TO THIS DAMAGE OCCURRENCE. FIRST OF ALL, THE 1-1/4" STEEL SERVICE INVOLVED HAD NOT BEEN MARKED BY THE WF&L REPRESENTATIVE IN THE FIELD. IN ADDITION, THE SERVICE WAS NOT SHOWN ON THE WORKING DRAWINGS BEING USED FOR THE STREET RECONSTRUCTION PROJECT BY THE CONTRACTOR. THIS IS BECAUSE THE SERVICE HAD INADVERTENTLY BEEN OMITTED WHEN THE GAS FACILITIES WERE MARKED ON THE PLANS WHICH HAD BEEN SUBMITTED TO THE WF&L DRAFTING DEPARTMENT BY THE RECONSTRUCTION PLANS FOR THE CONTRACTOR PRIOR TO THE PROJECT.THE SERVICE LATERAL WAS SOMEWHAT UNUSUAL, SINCE IT SERVED A BUILDING ON A STREET OTHER THAN THE ONE IN WHICH THE MAIN WAS LOCATED. THE SERVICE TO 620 WASHINGTON STREET, (FIGURE 1), RAN FROM A 6" STEEL MAIN ON SEVENTH STREET, THEN WEST THROUGH THE ALLEY BETWEEN WASHINGTON AND JEFFERSON STREETS. WHEN THIS SERVICE WAS INSTALLED IN 1963, THE EXISTING LOW PRESSURE SYSTEM ON WASHINGTON STREET COULD NOT PROVIDE AN ADEQUATE GAS SUPPLY FOR THE LAUNDROMAT THAT WAS LOCATED THERE. WHEN THE SERVICE LATERAL WAS HOOKED AND PULLED AT THE TIME OF THE ACCIDENT, IT SEPARATED AT A COMPRESSION FITTING LOCATED AT THE ALLEY, ABOUTFIVE FEET WEST OF THE SEVENTH STREET RIGHT-OF-WAY. AT APPROX 9:38 A.M., AFTER THE DAMAGED SERVICE HAD BEEN PINCHED CLOSED AND WF&L PERSONNEL WERE EVALUATING THE EXTENT OF THE DAMAGE TO GAS FACILITIES, AN EXPLOSION OCCURRED WITHIN THE VACANT SINGLE-FAMILY STRUCTURE AT 310 SEVENTH STREET. IT IS BELIEVED THATLEAKING GAS HAD MIGRATED UNDERGROUND FROM THE SEPARATED COMPRESSION FITTING AND PASSED THROUGH THE STONE AND CONCRETE BASEMENT WALL TO ENTER THE STRUCTURE. THERE WERE STANDING PILOT LIGHTS IN OPERATION FOR BOTH THE WATER HEATER AND THE FURNACE AT THE TIME OF THE EXPLOSION. IT IS ASSUMED THAT ONE OF THESE APPLIANCE PROVIDED THE IGNITION SOURCE. THE RESULTING BLAST AND FIRE DESTROYED THE VACANT HOME AND GARAGE AT 310 SEVENTH STREET. ADJACENT STRUCTURES AT 308 SEVENTH STREET AND 629 JEFFERSON STREET SUSTAINED SUBSTANTIAL DAMAGE AS WELL. A DUPLEX ACROSS THE STREET AT 309/311 SEVENTH STREET SUSTAINED COMPARATIVEL
2025-01-31 10:21 | NO | NO | 19960133 | 1996-08-30 | 7040 | HAMILTON GAS DEPT, CITY OF | WEST SIDE OF HAMILTON | HAMILTON | BUTLER | OH | 45013 | 3 | NO | 630 | 1996-08-01 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19960801 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | STEEL |  | 16 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOHN LIVER | 5138685901 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON MONDAY (JULY 29, 1996) I NOTIFIED AL ROSE (GAS SUPV) THAT THE EXISTING 12" GAS MAIN NEEDED TO BE SHUT DOWN FROM CLEVELAND AVE EAST ON N.W. WASHINGTON BLVD. TO WEST ELKTON RD. AND AFTER SHUTING DOWN AND BLEEDING OFF ALL GAS, THECONTRACTOR COULD REMOVE THE OLD 12" CAST IRON PIPE FROM AN EXISTING 12" VALVE ON THE EAST SIDE OF CLEVELAND AVE TO FACILITATE THE INSTALLATION OF NEW 12"STEEL PIPE IN THE ROADWAY. ON TUESDAY (JULY 30, 1996) I LEFT THE JOBSITE AROUND 9:00 AM TO INSTALL A 100# TEST ON A NEW 12" VALVE ON THE EAST SIDE OF CLEVELAND AVE. I ASKED THE CONTRACTOR IF THE OLD 12" CAST IRON MAIN WAS DEAD (NOGAS) AND HE INFORMED ME THAT THE CITY HAD INFORMED THE CONTRACTOR THAT A FLAT STEEL PLATE NEEDED TO BE WELDED ON THE EAST END OF THE 12" VALVE IN CASE SOMEONE SHOULD ACCIDENTLY TURN ON THE VALVE. THE WEST SIDE OF THE EAST VALVE WAS NEVER UNCOVERED AS THE CONTRACTOR WAS TO WELD NEW PIPE INTO THE EAST SIDE OF THE VALVE. ON WEDNESDAY (JULY 31, 1996) WORK CONTINUED FROM THE EAST VALVE HAD BLOWN OFF THE END OF THE MAIN AND PRESSURE WAS DOWN IN THE I.P. SYSTEM MOSTLY NORTH OF N.W. WASHINGTON BLVD. WHEN I ARRIVED AT THE INTERSECTION, THE CONTRACTOR WAS CLEANING UP GRAVEL AND RESETTING PLATES OVER THE DITCH WHICH WERE BLOWN OFF THE HOLE. THE PLATES HAD BEEN OVER THE VALVE AND PART OF THE EXCAVATION FOR NEW PIPE. ON THURSDAY, AUGUST 1, 1996 AT APPROX 6:30AM I WAS ADVISED BY OUR DISPATCHER THAT HE HAD RECEIVED NUMEROUS PHONE CALLS FROM WEST SIDE RESIDENTS AND BUSINESS COMPLAINING OF NO GAS. WE DISPATCHED CREWS TO THE AREA AT APPROX 7:00 A.M., AND AT 7:15 A.M. I WAS ADVISED BY ONE OF OUR CREWS THAT A VALVE AT THE INTERSECTION OF CLEVELAND AVENUE AND N.W. WASHINGTON BLVD. HAD BLOWN OFF THE END OF THE MAIN (16" STEEL MAIN) AND THAT THE PRESSURE WAS VERY LOW IN OUR INTERMEDIATE PRESSURE SYSTEM (7.5 PSIG) ON THE WEST SIDE OF THE CITY. BECAUSE IT APPEARED THAT WE HAD LOST ALL THE PRESSURE IN THIS SYSTEM, WE IMMEDIATELY BEGAN TO SHUT-OFF ALL SERVICES ON THIS SYSTEM PRIOR TO REINSTATING GAS PRESSURE. BY APPROX 11:00 A.M. WE HAD PROCEEDED TO PHYSICALLY ISOLATE 1,896 CUSTS FROM THE SYSTEM. AT THIS POINT WE REACTIVATED GAS PRESSURE TOTHE AREA AND PROCEEDED TO TURN ON AND RELIGHT THE CUSTS WE HAD ISOLATED FROMTHE SYSTEM. WE COMPLETED THE MAJORITY OF THE RELIGHTS BY 2:00 A.M. ON FRIDAY, AUGUST 2, 1996. I HAVE ATTACHED A COPY OF THE INSPECTOR'S REPORT TO THIS REPORT. THE CITY FEELS THE MAIN FACTOR CONTRIBUTING TO THIS SERVICE FAILURE WASTHE CONTRACTOR'S DECISION TO LEAVE THE EXISTING VALVE ON THE END OF THE DEAD-END LINE UNBLOCKED WHILE HE PERFORMED WORK DOWNSTREAM OF THIS VALVE.
2025-01-31 10:21 | YES | YES | 19960134 | 1996-09-16 | 603 | ARKANSAS LOUISIANA GAS CO (ARKLA GAS CO) | 6201 INDUSTRIAL LOOP @289 | SHREVEPORT | SHREVEPORT | LA | 71129 | 3 | NO | 1201 | 1996-08-30 | 0 | 2 | 28039 | 20180.5702 | 48725.3297 | Null | 1 | 0 |  | 19960831 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NONE SPECIFIED | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE 2406 | PLEXCO | 1981 | 1981 | UNDER GROUND OR UNDER WATER |  | BUDDY SIMS | 3184294160 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-08-26 | YES | 0 | PAINT | YES |  |  | A THIRD PARTY BORING CREW DAMAGED ARKLA'S 4" PLASTIC DISTRIBUTION GAS MAIN. TWO OF ARKLA'S CONSTRUCTION WORKERS, JAMES ROBERSON, AGE 56 AND WILLIAM COOKS,JR., AGE 46, WERE ATTEMPTING TO INSTALL A FULL CIRCLE BAND CLAMP OVER THE DAMAGED PIPE WHEN THE GAS IGNITED RESULTING IN BOTH MEN RECEIVING 1ST AND 2ND DEGREES BURNS. THE CAUSE OF IGNITION IS UNKNOWN, HOWEVER STATIC ELECTRICITY ISSUSPECTED. LOUISIANA ONE CALL NOTIFICATION REQUEST #159042. 4" PLASTIC PIPE WAS INCORRECTLY LOCATED AND MARKED.
2025-01-31 10:21 | YES | YES | 19960135 | 1996-09-03 | 6830 | GREY FOREST UTILITIES | INTERSECTION OF BANDERA RD & WHIP-O-WILL | HELOTES | BEXAR | TX | 78023 | 1 | NO | 900 | 1996-08-20 | 0 | 1 | 100000 | 71973.2167 | 173776.9882 | Null | 0 | 30 |  | 19960820 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.602 | 2306 | PHILLIPS | 1978 | 1978 | UNDER GROUND OR UNDER WATER |  | PHILIP FRANCESCO | 2106958781 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-07-15 | YES | 2 | PAINT | NO |  |  | GAS LINE WAS MARKED ON 8/7/96 BY OPERATOR. CONTRACTOR HIT THE GAS MAIN WITH A VERMEER T-800 TRENCHER. THE GAS IGNITED AND BURNED THE TRENCHER AND THE TRENCHER OPERATOR.
2025-01-31 10:21 | YES | YES | 19960136 | 1996-09-10 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 759 VALLEY ROAD | LONG HILL | MORRIS | NJ |  | 4 | NO | 905 | 1996-08-28 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19960828 | 49 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.099 | ASTMD2513 | PHILLIPS | 0 | 1995 | ABOVE GROUND |  | BRIAN WAGAMAN | 9085227406 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-08-12 | YES | 0 | TEMP STAKES AND PAINT | YES |  |  | WHILE USING AN OXYACETYLENE TORCH TO CUT METAL GRATING, A LONG HILL TOWNSHIPBOARD OF EDUCATION EMPLOYEE BURNED A HOLE IN A 1 1/4" PLASTIC 60 PSI DESIGN GAS SERVICE WHICH CAUSED AN IGNITION. THE INDIVIDUAL SUSTAINED SERIOUS BURNS AND WAS TRANSPORTED TO ST. BARNABAS HOSPITAL, LIVINGTON, NJ WHERE HE WAS ADMITTED.
2025-01-31 10:21 | NO | NO | 19960138 | 1996-09-13 | 21030 | VALLEY CITIES GAS SERVICE | SOUTH OF PA 199, @ RR CROSSING | ATHENS | BRADFORD | PA | 18810 | 2 | NO | 710 | 1996-08-07 | 0 | 0 | 0 | 0 | 0 | YES | 8 | 10 |  | 19960807 | 475 | 500 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 |  | REPUBLIC STEEL | 1957 | 1958 | UNDER GROUND OR UNDER WATER |  | TODD MCGOVERN | 7178889664 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | PAINT | YES |  |  | ATHENS TOWNSHIP IS HAVING SANITARY SEWERS INSTALLED IN AN AREA PREVIOUSLY WITHOUT SEWER SERVICE. THE GENERAL CONTRACTOR IS HAROLD R. TRIPP, INC., FROM KULPSVILLE, PA. TO INSTALL THE SEWER UNDER RAILROAD TRACKS BY BORING. THE GENERAL CONTRACTOR HAD PLACED REQUESTS FOR UTILITY LOCATIONS FOR THE ENTIRE PROJECT AND RESUBMITTED THE SAME REQUESTS PERIODICALLY. THE SUBCONTRACTOR PERFORMING THE BORE MADE NO REQUESTS FOR UTILITY LOCATIONS. THE GAS LINES WERE MARKED IN THE AREA IN ACCORDANCE WITH THE REQUEST FROM THE GENERAL CONTRACTOR.
2025-01-31 10:21 | YES | YES | 19960141 | 1996-10-02 | 12180 | MARSHALL COUNTY GAS DISTRICT | 1807 JORDAN STREET | GUNTERSVILLE | MARSHALL | AL | 35976 | 3 | NO | 755 | 1996-08-30 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 30 |  | 19960830 | 15 | 22 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2.25 | 0.025 |  |  | 1954 | 1954 | UNDER PAVEMENT |  | RICHARD LAWSON | 2055820324 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | NO |  | NO | 0 |  | NO |  |  | INVESTIGATION INCOMPLETE AT THIS TIME.
2025-01-31 10:21 | NO | NO | 19960142 | 1996-10-01 | 22182 | WASHINGTON GAS LIGHT CO | WASHINGTON NATIONAL AIRPORT | WASHINGTON |  | DC | 20001 | 3 | YES | 2130 | 1996-08-30 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 25 |  | 19960830 | 20 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NONE SPECIFIED | STEEL | SEE COMMENTS | 1 | 0.133 |  |  | 1950 | 1951 | ABOVE GROUND |  | JAMES BIELAKSI | 7037505566 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | AN AIRPORT SHUTTLE BUS, MOVING SOUTH TO NORTH IN A TUNNEL THAT RUNS BENEATH THE MAIN TERMINAL AT NATIONAL AIRPORT, MOVED TO THE OPERATOR'S RIGHT TO ALLOWCLEARANCE FOR AN APPROACHING LARGER AIRLINE EMPLOYEE SHUTTLE BUS. IN DOING SO, ITS RIGHT SIDE MIRROR MADE CONTACT WITH A 1" NATURAL GAS LINE RUNNING PARALLEL TO THE TUNNEL WALL. THE MIRROR'S IMPACT CAUSED THE GAS LINE TO BE SERVEDAT TWO JOINTS. NATURAL GAS AT 20 PSI ESCAPED INTO THE ATMOSPHERE CREATING A STRONG ODOR THAT WAS PULLED INTO THE TERMINAL BUILDING, CAUSING THE BUILDING TO BE EVACUATED BY THE FIRE DEPARTMENT. RESPONDING WASHINGTON GAS PERSONNELSHUT THE GAS OFF AT AN OUTSIDE STOPCOCK ABOVE THE BROKEN LINE. MATERIALINVOLVED: PIPE INSTALLED BY AIRPORT AUTHORITY.
2025-01-31 10:21 | YES | YES | 19960143 | 1996-09-19 | 11032 | LACLEDE GAS CO | 6050 POINTVIEW LANE | ST. LOUIS | ST. LOUIS | MO | 63123 | 3 | NO | 1340 | 1996-08-25 | 0 | 2 | 95000 | 68374.5559 | 165088.1388 | Null | 0 | 30 |  | 19960825 | 12 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 40 | ASTM B75 |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | PAUL HUNKER | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FRACTURED SERVICE LINE-LAB ANALYSIS IS IN PROCESS TO DETERMINE CAUSE OF FAILURE PER 49 CFR 192.61. LAB ANALYSIS IS IN PROCESS TO DETERMINE CAUSE OF FAILURE PER 49 CFR 192.61. UPON EXCAVATION OF THE SERVICE FOLLOWING THE INCIDENT, A FULL CIRCUMFERENCE BREAK OF THE 1/2 INCH COPPER SERVICE LINE INSERTED IN 3/4 INCH STEEL WAS FOUND. THE INVESTIGATION IS CONTINUING TO ASCERTAIN IF CORROSION, THE EXPLOSION ITSELF, OR CAUSES YET UNKNOWN LED TO THE FAILURE OF THE PIPE.
2025-01-31 10:21 | YES | NO | 19960144 | 1996-10-01 | 15007 | PACIFIC GAS & ELECTRIC CO | 1309 TEHUMA AVENUE | OROVILLE | BUTTE | CA |  | 2 | NO | 50 | 1996-09-02 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 1 | 20 |  | 19960902 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | A HOUSE FIRE WHERE THE FIRE SPREAD TO THE GAS METER SET, MELTING THE REGULATOR AND IGNITING GAS.
2025-01-31 10:21 | YES | NO | 19960152 | 1996-10-21 | 22189 | WASHINGTON NATURAL GAS CO | BEVERLY PARK ROAD & 132 STREET | MUKILTEO | KING | WA | 98275 | 3 | NO | 1237 | 1996-09-16 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 1 | 49 |  | 19960924 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTMD-2513 | PLEXCO | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | DAVID LAGERQUIST | 2062242268 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-09-05 | YES | 3 | PAINT MARKINGS | YES |  |  | THIS WAS AN ON-GOING JOB THAT HAD BEEN ONE-CALLED SEVERAL TIMES. THE GAS MAIN WAS MARKED CORRECTLY JUST 6 DAYS PRIOR TO THE OCCURENCE OF THE DAMAGE. A CONTRACTOR USING A BULLDOZER ON A STREET IMPROVEMENT JOB WAS REMOVING UNSUITABLE MATERIAL FROM A PORTION OF THE ROADBED WHEN HE TORE A 30" X 3" HOLE IN THE TOP OF A 4" PE MAIN. THE ONE-WAY FEED MAIN WAS SQUEEZED OFF ON THE DOWNSTREAMSIDE OF THE BREAK, THEN THE UPSTREAM SIDE, AFTER GAUGES INDICATED NO PRESSURE REMAINED IN THE SYSTEM. THE RESULT WAS A LOSS OF SERVICE TO 1427 CUSTOMERS.THE MAIN WAS REPAIRED BY 18:30, 9/16/96 AND ALL AFFECTED METERS WERE SHUT OFF AND LOCKED BY 03:00 AM, 9/17/96. GAS WAS REINTRODUCED INTO THE SYSTEM AND RELIGHTS BEGAN IMMEDIATELY, UTILIZING EMPLOYEE'S STATIONED THROUGHOUT THE COMPANY THAT HAVE BEEN QUALIFIED TO PERFORM LIGHT-UPS. RESTORATION OF SERVICE WASCOMPLETED TO ALL AVAILABLE CUSTOMERS BY 23:45, 9/17/96. THE ONE-CALL LOCATION CENTER HAD BEEN NOTIFIED OF THE EXCAVATION WORK AND THE GAS MAIN WAS MARKEDON 9/9 AND 9/10/96 IN THE AREA OF DAMAGE. IT DID NOT APPEAR THAT THE MAIN WAS POT-HOLED BY HAND OR THE LOCATION MARKS MAINTAINED BY THE EXCAVATING CONTRACTOR.
2025-01-31 10:21 | YES | NO | 19960153 | 1996-10-16 | 15469 | PHILADELPHIA GAS WORKS | 1919 WALNUT STREET | PHILADELPHIA | PHILADELPHIA | PA | 19103 | 4 | NO | 849 | 1996-09-16 | 0 | 0 | 75000 | 53979.9125 | 130332.7412 | YES | 3 | 44 |  | 19960916 | 0.25 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 20 | 0.625 |  |  | 0 | 1898 | UNDER PAVEMENT |  | BRIAN SCHENK | 2516846372 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-09-05 | YES | 3 | PAINTED MARKS | YES |  |  | THE CONTRACTOR USING THE EQUIPMENT NOTIFIED PHILADELPHIA GAS WORKS THAT THEYWOULD NOT ONLY BE CUTTING THE PAVING AREA AND WOULD NOT BE DEEP ENOUGH TO AFFECT OUR FACILITY. A THIRD PARTY CONTRACTOR WAS USING A VERMEER WHEEL TRENCHING MACHINE TO INSTALL ELECTRIC CONDUIT. THE 20" CAST IRON GAS MAIN WAS PROPERLY MARKED OUT SIX (6) DAYS PRIOR TO THE INCIDENT AND THE CONTRACTOR'S EXCAVATION INITIALLY DID NOT AFFECT PGW'S FACITILITES. HOWEVER, DURING THE OPERATION, THE CONTRACTOR HAD TO MAKE A FIELD CHANGE TO INSTALL THE CONDUIT AROUND AN EXISTING ELECTRIC MANHOLE. WHILE THE OPERATOR OF THE TRENCHING MACHINE WAS "SWINGING" OVER TO ACCOMPLISH THIS CHANGE, THE MACHINE CUT INTO PGW'S 20" LOW PRESSURE CAST IRON GAS MAIN CAUSING AN 8" GOUGE AND SUBSEQUENT IGNITION. PGW AND THE PHILADELPHIA FIRE DEPARTMENT EXTINGUISHED THE FIRE BY 12:35 P.M. AFTERWHICH PGW REPAIRED THE DAMAGE BY REPLACING THAT SEGMENT OF PIPE. TELEPHONIC NOTICE WAS MADE TO MS. SANCHEZ, REPORT #361241 AT 10:47 A.M., SEPT 16, 1996.
2025-01-31 10:21 | YES | YES | 19960154 | 1996-10-18 | 4473 | ENERGAS CO | 321 STAR | HEREFORD | DEAF SMITH | TX |  | 3 | NO | 1120 | 1996-10-01 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19961002 | 12 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CHARLES JONES | 8067984477 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TWO CONTRACT EMPLOYEES SUFFERED BURNS WHEN GAS IGNITED WHILE THEY WRE DISCONTINUING A SERVICE TAP. ONE VICTIM HOSPITALIZED. SOURCE OF GAS AND IGNITION SOURCE ARE BEING INVESTIGATED.
2025-01-31 10:21 | YES | NO | 19960155 | 1996-10-17 | 11680 | LONE STAR GAS CO | 5825 DANA DRIVE | HALTOM CITY | TARRANT | TX | 76117 | 3 | NO | 1159 | 1996-06-05 | 0 | 0 | 70000 | 50381.2517 | 121643.8918 | Null | 0 | 30 |  | 19960605 | 28 | 60 | BY TEST | 90 | CORROSION | CORROSION | INTERNAL | SERVICE LINE |  | REGULATOR/METER |  | OTHER | REG | 0 | 0 | MODEL 733 | FISHER | 1967 | 1967 | ABOVE GROUND |  | ML IMBODEN | 2146702779 | INTERNALLY | OTHER | INTERNAL | OTHER | BROKEN SEAL | NO DATA | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | CORROSION DUE TO WATER INFILTRATION OF ENCLOSED BODY. STRUCTURE FIRE DAMAGE POSSIBLY CAUSED BY OVER PRESSURE OF WATER HEATER PILOT.
2025-01-31 10:21 | YES | NO | 19960156 | 1996-10-08 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 1101 PORTER AVENUE | CHESTERTON | PORTER | IN | 46304 | 3 | NO | 1130 | 1996-09-09 | 0 | 0 | 913000 | 657115.4687 | 1586583.9027 | Null | 0 | 19 |  | 19960909 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 2 | 0 | ANSI B-16 | SPRAGUE | 1966 | 1966 | ABOVE GROUND |  | DJ TOKOLY | 2196474770 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | ON MONDAY, SEPT. 9, 1996, AT APPROX. 11:30A.M., A PAVING CONTRACTOR, PALMER & SONS PAVING, OF LAKE STATION, INDIANA WAS PLACING BLACKTOP THROUGHOUT THE PARKING LOT OF THE CHESTERTON TERRACE APTS. LOCATED AT 1101 PORTER AVENUE, CHESTERTON, IN. WHILE USING THE PAVING MACHINE (APPROX WEIGHT - 17TONS) THE OPERATOR STRUCK A 1" REGULATOR VENT PIPE EXTENDING ABOUT 8" OUT FROM THE WOOD SHED CONTAINING THE GAS METER AND REGULATING EQUIPMENT. THE FORCE OF THE IMPACT ON THE VENT PIPE CAUSED THE DIAPHRAGM AND SPRING CONTAINING PART OF THE PRESSURE REGULATOR TO BREAK OFF, ALLOWING INLET PRESSURE TO ENTER THE DOWNSTREAM PIPING WHICH FED THE APARTMENT COMPLEX. THE ELEVATED PRESSURE RAISED THE PILOT FLAMES OF THE GAS RANGES IN THE APARTMENTS. TWO OF THE FOUR BUILDINGS IN THE COMPLEX ULTIMATELY IGNITED. GAS WAS SHUT OFF TO THE METER SET APPROX. 19 MINUTES AFTER THE REPORT TO THE UTILITY. THE BUILDING FIRES WERE EXTINGUISHED AROUND 4:00PM. THE FIRE RESULTED IN NO INJURIES EXCEPT FOR ONE FIREMAN WHO SUFFERED FROM SMOKE INHALATION. HE WAS TREATED AND RELEASED. ONE OF THE TWO BUILDINGS INVOLVED HAD EXTENSIVE FIRE DAMAGE. THE OTHER BUILDING HAD FIRE DAMAGE TO THREE APARTMENTS. EACH BUILDING CONTAINED 12 APARTMENTS. DAMAGE IS ESTIMATED TO BE $913,000. THE SERVICE REGULATOR WHICH WAS DAMAGED BY THE FORCE EXERTED ON THE VENT PIPE IS A SPRAGUE B-34 MODEL, WITH INTERNAL PRESSURE RELIEF. IT WAS PURCHASED AND INSTALLED IN 1966. THE REGULATOR REDUCED NOMINAL INLET PRESSURE OF 35 PSIG TO 6 INCHES W.C. PRESSURE.
2025-01-31 10:21 | YES | NO | 19960157 | 1996-10-07 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 3820 CLARKE ROAD | MEMPHIS | SHELBY | TN | 38115 | 3 | NO | 1625 | 1996-09-23 | 0 | 0 | 108000 | 77731.0741 | 187679.1473 | Null | 1 | 39 |  | 19960923 | 87 | 99 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | OTHER | SEE COMMENTS | 0.5 | 0.09 | ASTMD-2513 | PHILLIPS DRISCOPIPE | 0 | 1993 | ABOVE GROUND |  | WADE STINSON | 9013673300 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | ABOVE GROUND SERV RISER | YES |  |  | AN OUT OF CONTROL AUTOMOBILE STRUCK GAS METER ASSEMBLY BREAKING SERVICE RISER. THE ESCAPING GAS IGNITED, RESULTING IN EXTENSIVE FIRE DAMAGE TO SAID AUTOMOBILE, A ONE-STORY SINGLE-FAMILY RESIDENTIAL DWELLING, AND ANOTHER AUTOMOBILEPARKED IN DRIVEWAY OF ADJACENT DWELLING. THERE WERE NO PERSONAL INJURIES OR FATALITIES. STEEL RISER WITH INSERTED PE PIPE.
2025-01-31 10:21 | YES | YES | 19960158 | 1996-11-04 | 20211 | UNITED CITIES GAS CO | 9146 W 102 TERR | OVERLAND PARK | JOHNSON | KS | 66210 | 3 | NO | 1854 | 1996-10-03 | 0 | 4 | 50000 | 35986.6084 | 86888.4941 | Null | 1 | 18 |  | 19961003 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE Z306 | DRISCO | 1979 | 1979 | UNDER GROUND OR UNDER WATER |  | D MICHAEL WOOLF | 9137640530 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-09-23 | YES | 2 | PAINT | YES
2025-01-31 10:21 | YES | YES | 19960159 | 1996-10-29 | 11032 | LACLEDE GAS CO | 6232 DARDANELLA AVENUE | ST. LOUIS | ST. LOUIS | MO | 63121 | 3 | NO | 1145 | 1996-10-01 | 0 | 1 | 750000 | 539799.1254 | 1303327.4119 | Null | 0 | 20 |  | 19961001 | 13.5 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL HUNKER | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIRD PARTY REMOVED THE RETAINING BRASS NUT AND WASHER ASSEMBLY FROM LOCK COCK CORE. THIRD-PARTY OCCUPANT STATES THAT HE WAS ATTEMPTING TO TURN ON WATER IN BASEMENT WHEN HE MISTAKENLY REMOVED THE RETAINING BRASS NUT AND WASHER ASSEMBLY FROM THE LOCK COCK NEAR THE GAS AND NATURAL GAS TO ENTER THE RESIDENCE.THE NATURAL GAS WAS IGNITED BY AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 19960160 | 1996-10-24 | 8170 | INTERSTATE POWER CO | 805 S. 8TH ST. | CLEAR LAKE | CERRO GORDO | IA | 50428 | 3 | NO | 1041 | 1996-09-24 | 0 | 1 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 5 |  | 19960924 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | STOVE | OTHER | MANUALLY LIT STOVE | OTHER | STOVE | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JIM HOUSE | 5154232060 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | IPC WAS NOTIFIED OF AN EXPLOSION AT 10:43A.M. SEPT 24, 1996. THE CLEAR LAKE FIRE DEPARTMENT RECEIVED A 911 CALL AT 10:41A.M. THE INCIDENT OCCURRED WITHINTHE HOME OF 805 SOUTH 8TH ST, CLEAR LAKE, IA. IPC'S CLEAR LAKE, IA OFFICE WAS NOTIFIED OF AN EXPLOSION AT 805 SOUTH 8TH ST. BY AN OFF-DUTY INTERSTATE POWER EMPLOYEE. THE CLEAR LAKE OFFICE DISPATCHED TWO COMBINATION SERVICEMEN TO THE SCENE. THE SERVICEMEN ALONG WITH THE CLEAR LAKE AREA MANAGER ARRIVED AT THE SCENE AND IMMEDIATELY CONFERRED WITH THE CLEAR LAKE FIRE AND POLICE DEPARTMENTS. THE EXPLOSION HAD OCCURED IN THE KITCHEN OF THE HOME. THE GAS TO THE HOME WAS SHUT OFF OUTSIDE AT THE METER SET. A MOTORIST WHO WAS TRAVELING ON S. 8TH ST. WHEN THE EXPLOSION HAPPENED, STOPPED AND SHUT OFF THE OUTSIDE GAS COCK. ONE INDIVIDUAL HAD BEEN IN THE HOME AT THE TIME OF THE EXPLOSION AND HE WAS BEING TREATED FOR BURNS BY FIRE AND RESCUE PERSONNEL. HE WAS LATER TAKEN TONORTH IOWA MERCY HOSPITAL IN MASON CITY AND THEN TRANSFERRED TO THE UNIVERSITY OF IOWA HOSPITAL IN IOWA CITY WITH BURNS ON HIS HANDS, FACE, AND BACK. THEAREA MANAGER DISPATCHED ONE OF THE SERVICEMAN TO WHERE THE CLEAR LAKE GAS CREW WAS WORKING. THE CREW WAS WORKING AWAY FROM THEIR TRUCK AND DID NOT HEAR THE INITIAL RADIO MESSAGE. THE SERVICEMAN ALSO NOTIFIED THE IPC GAS DEPARTMENTOFFICE IN MASON CITY, IA.. A LINE CREW WAS DISPATCHED TO THE SCENE TO CUT THE ELECTRICITY AT THE POLE AND ELIMINATE THAT SOURCE OF IGNITION. ONE OF THE SERVICEMEN STARTED TO CHECK THE SERVICE LINE TO THE HOME. HE PROBED ALONG THE SERVICE AT 5' INTERVALS FROM THE HOUSE TO THE PARKING. HE ALSO PROBED ALONG THE NORTH SIDE OF THE HOME. NO GAS WAS FOUND. NEXT HE SOAPED AND CHECKED THE ENTIRE METER SET FOR LEAKS. NO LEAKS WERE FOUND. THE CLEAR LAKE FIRE DEPARTMENT WAS IN CHARGE OF THE SCENE AND THEY HAD PLACED A GAS DRIVEN FAN IN THE YARDTO HELP VENTILATE THE HOME. THE SERVICEMAN CHECKED THE UPSTAIRS OF THE HOME AND FOUND 5% LEL. THE OTHER SERVICEMAN WAS CHECKING THE ADJOINING HOMES FOR GAS. HE COULD NOT GAIN ENTRY INTO 801 S. 8TH ST., SO HE CHECKED THE CRAWL SPACE OF THE HOME FOR GAS. NO GAS WAS FOUND. THE LINE CREW ARRIVED AND PROCEEDED TO CUT THE ELECTRICITY AT THE POLE. BONDED PLUMBING OF CLEAR LAKE WAS CONTACTED TO PERFORM AN INDEPENDENT TEST ON THE CUSTOMER'S PIPING. THE GAS CREW ARRIVED AND REMOVED THE GAS METER AND REGULATOR FOR FUTHER TESTS. THE CREW PLUGGED THE OUTLET OF THE GAS COCK AND LOCKED IT OFF. THE CREW THEN INSTALLED ANOTHER REGULATOR AND PLACED 7" W.C. OF AIR PRESSURE ON THE INSIDE PIPING. THE FIRE DEPARTMENT HAD PULLED OUT THE GAS STOVE AND EXPOSED THE FLEX CONNECTOR. THEFLEX CONNECTOR WAS SOAPED AND NO LEAKS WERE FOUND ON THE CONNECTOR. BONDED PLUMBING ARRIVED AND STARTED TESTING THE INSIDE PIPING AT 30 PSIG. WHILE CHECKING FOR LEAKS IT WAS DISCOVERED THAT THE CUSTOMER HAD AN UNDERGROUND SERVICE TO HIS GARAGE. THE AIR TEST FAILED. THE PRESSURE DROPPED TO 18 PSIG DURING THE ONE HOUR TEST. THE PIPING WAS CAPPED AND THE GAS AND ELECTRICITY TO THE HOME WERE LEFT OFF. THE SERVICMEN BEGAN TAKING ODORANT READS THROUGHOUT THE AREA. THE CUSTOMER AT 811 S. 8TH ST. COMMENTED THAT SHE WAS HAVING DIFFICULTY SMELLING THE GAS BECAUSE SHE STILL SMELLED THE BURNT RAGS FROM THE NEXT DOOR. THE ODORANT WAS FOUND TO BE ADEQUATE. THE PRESSURE RECORDING CHART AT THE CLEAR LAKE OFFICE WAS CHANGED. THE CHART VERIFIED THAT THE SYSTEM PRESSURE AT THETIME OF THE EXPLOSION WAS 60 PSIG. THE FISHER S252 REGULATOR WAS CHECKED AT THE MASON CITY GAS METER SHOP. IT WAS FOUND TO BE OPERATING PROPERLY. THE SPRAGUE 250 TC METER(#130941) WAS CHECKED AT THE MASON CITY GAS METER SHOP. IT WAS FOUND TO BE OPERATING PROPERLY. MR HOWARD WAS THE FIRST PERSON ON THE SCENE
2025-01-31 10:21 | YES | YES | 19960161 | 1996-10-29 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 402 SOUTH MAPLE LANE | WAKARUSA | ELKHART | IN | 46573 | 3 | NO | 1605 | 1996-10-04 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19961004 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | DUPONT | 0 | 1988 | UNDER PAVEMENT |  | DON TOKOLY | 2196474770 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-09-30 | YES | 2 | YELLOW PAINT | YES |  |  | ON OCTOBER 1, 1996, NORTHERN INDIANA PUBLIC SERVICE COMPANY MARKED ITS 2 INCH PE PLASTIC GAS MAIN OPERATING AT 50 PSI ON SOUTH MAPLE LANE, WAKARUSA, INDIANA AT THE REQUEST OF NETWORK FIELD SERVICES. ON FRIDAY, OCTOBER 4, 1996, A SUBCONTRACTOR ON NETWORK FIELD SERVICES BEGAN BORING UNDER SOUTH MAPLE LANE FOR A COMMUNICATION CABLE. THE BORING MACHINE AUGER HIT AND CUT THE 2 INCH PE PLASTIC GAS MAIN. NATURAL GAS ESCAPED FROM THE MAIN AND ENTERED AN UNDISCLOSEDNEARBY STORM SEWER LEAKING DOWN THE SEWER INTO A PUMPING STATION LOCATED 400-500 FEET FROM THE CUT MAIN. MR. DOUG PURDUE, A CITY EMPLOYEE, RESPONDING TO THE ACCIDENT ENTERED THE CITY PUMPING STATION AND APPARENTLY THREW A SWITCH OR TOOK SOME ACTION WHICH IGNITED THE COMBUSTIBLE GAS MIXTURE WITHIN THE BUILDING CAUSING HIMSELF BURNS AND DAMAGE TO THE BUILDING.
2025-01-31 10:21 | YES | YES | 19960162 | 1996-11-04 | 18484 | SOUTHERN CALIFORNIA GAS CO | 188 E MAIN ST | SAN JACINTO | RIVERSIDE | CA |  | 3 | NO | 500 | 1996-10-02 | 0 | 3 | 750000 | 539799.1254 | 1303327.4119 | YES | 6 | 30 |  | 19961002 | 53 | 53 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.188 |  |  | 1953 | 1953 | UNDER PAVEMENT |  | JACK WALDRON | 2132443287 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE AND EXPLOSION AT ABOVE LOCATION RESULTED FROM AT LEAST TWO CAUSES. (1) OUTSIDE CONTRACTOR WORKING FOR CITY OF SAN JACINTO INSTALLED 12" PVC WATER MAIN IN ORDER TO MAINTAIN PROPER DEPTH BENT 3/4" STEEL GAS SERVICE UP AND OVER PVC WATER MAIN. THIS ACTION PLACED THE 3/4" GAS SERVICE IN CONTACT WITH AN ABANDONED 8" STEEL WATER MAIN. (2) ELECTRICAL ARCHING OCCURRED BETWEEN 3/4" GASSERVICE AND ABANDONED 8" WATER MAIN. ON 10/2/96, AT 5:00PM, THE SOUTHERN CA.GAS COMPANY (GAS COMPANY) RECEIVED A REPORT OF A FIRE AND EXPLOSION WITH 3 INJURIES AT THE ABOVE ADDRESS. THE REPORT WAS RECEIVED FROM THE RIVERSIDE COUNTY FIRE DEPT. WITHIN MINUTES A GAS COMPANY PERSON WAS IN ROUTE FROM OUR RAMONA BASE TO ASSIST IN THE INVESTIGATION. UPON ARRIVAL, THE EMPLOYEE FOUND A WALL OF A STRUCTURE BLOWN DOWN AND A FIRE AT THIS ADDRESS. A DISTRIBUTION CREW WAS CALLED TO THE SCENE TO PINPOINT THE LEAK FOR REPAIR. GAS WAS UNDER CONTROLWITHIN 6 1/2 HRS AFTER THEIR ARRIVAL. GAS COMPANY CREWS WERE PROHIBITED FROMDIRECT ACCESS TO THE INCIDENT AREA UNTIL A POLICE INVESTIGATION WAS COMPLETED REGARDING A POSSIBLE BOMBING. THE GAS COMPANY INVESTIGATION INDICATES THAT LEAKAGE TO A 3/4" SERVICE LINE WAS THE DIRECT RESULT OF ELECTRICAL ARCING FROM AN UNKNOWN ELECTRICAL SOURCE BETWEEN THE GAS SERVICE AND AN ABANDONED 8" STEEL WATER MAIN. IN ADDITION THE STRUCTURAL INTEGRITY OF THE SERVICE LINE WAS COMPROMISED BY STRESS INDUCED DURING THE INSTALLATION OF A 12" WATER PIPELINEBY A THIRD PARTY CONTRACTOR (WORKING FOR THE CITY WATER AGENCY) IN 1991. THE SERVICE AND MAIN HAVE BEEN SURVEYED EVERY YEAR SINCE THEIR INSTALLATION IN 1953. DURING THAT PERIOD ONLY ONE LEAK WAS DETECTED (IN 1970) AND THIS LEAK WAS OF A NON-CORROSIVE VARIETY. THE SERVICE AND MAIN WERE LAST SURVEYED ON FEBRUARY 27, 1996. NO LEAKS WERE DETECTED AT THAT TIME. SUBSEQUENT TO THE DISCOVERY OF THE ELECTRICAL ARCING PROBLEM, THE GAS COMPANY INITIATED A WID SPREAD SPECIAL SURVEY IN THE AFFECTED AREA. ONE ADDITIONAL LEAK WAS FOUND FROM AN IDENTICAL ARCING PROBLEM. THE MAIN AND SERVICES IN THE AFFECTED AREA HAVE BEEN ISOLATED FROM FUTURE ELECTRICAL CONTACT. THE INVESTIGATION IS STILL UNDER WAYAND IF ANY SIGNIFICANT FACTS DEVELOP WE WILL SUBMIT AN UPDATED REPORT. PLEASE CALL FIL BERNAL AT (213)244-3283 IF YOU HAVE ANY QUESTIONS REGARDING THIS REPORT.
2025-01-31 10:21 | YES | NO | 19960163 | 1996-10-28 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1416 GLENDALE BLVD | LOS ANGELES | LOS ANGELES | CA |  | 3 | NO | 1400 | 1996-09-27 | 0 | 0 | 300000 | 215919.6502 | 521330.9647 | YES | 0 | 15 |  | 19960927 | 442 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | X42 | US STEEL | 0 | 1981 | UNDER PAVEMENT |  | FA BERNAL | 2132443283 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | PIPELINE WALL RUPTURED IN SEVERAL LOCATIONS ALONG A 226 FOOT AREA DURING A NITROGEN PRESSURE TEST. THE ABRUPT RELEASE OF THE TEST MEDIUM HURLED SOIL, PAVEMENT & DEBRIS INTO THE ADJACENT AREA, DAMAGING SOME STRUCTURES. TESTED PIPELINE NOT COMPLETELY PURGED OF NATURAL GAS. COMPANY ARC WELDER WAS SOURCE OF IGNITION. ON SEPT. 27, 1996 AT APPROX 2:00 P.M. A DISTRIBUTION PIPELINE RUPTUREON GLENDALE BLVD. IN LOS ANGELES, CA DURING A PRESSURE TEST. UPON BURSTING, THE SOIL AND PAVEMENT ABOVE THE PIPELINE WAS DISRUPTED FOR APPROX 260 FEET ALONG THE SURFACE. THE STRENGTH TEST WAS BEING CONDUCTED TO UPRATE THE PIPE FROM A 60 PSIG DELIVERY SYSTEM TO A 228 PSIG SYSTEM. THE TEST MEDIUM WAS NITROGEN SET AT 425 PSIG FOR A ONE HOUR TEST. THE PIPELINE FAILED AT 53 MINUTES AND 45 SECONDS INTO THE TEST. THERE WAS NO NATURAL GAS RELEASE AS A RESULT OF THIS INCIDENT. ALTHOUGH SOME MEDIA GROUPS REPORTED MUTLIPLE INJURIES REQUIRING HOSPITALIZATION, THERE IS IN FACT, ONLY ONE CONFIRMED INJURY. ONE SOUTHERN CA GAS COMP (THE GAS COMPANY) EMPLOYEE WAS SLIGHTLY INJURED WITH MINOR SCRAPES, BRUISES, A PUNCTURED EARDRUM AND A SMALL CUT AT THE TEMPLE AREA OF HIS HEAD. THE EMPLOYEE WAS TREATED AT A LOCAL MEDICAL CENTER AND RELEASED THE SAME AFTERNOON. ADDITIONALLY, FOUR INDIVIDUALS WHO WERE IN NEARBY STRUCTRES, HAVE FILED CLAIMS WITH THE GAS COMPANY REGARDING ALLEGED DIZZINESS AND/OR DUST INHALATION. NONE OF THESE INDIVIDUALS WERE HOSPITALIZED AND THE GAS COMP IS INVESTIGATING THE CLAIMS. AN INVESTIGATION, SPONSORED BY THE GAS COMP, WAS CONDUCTED BY AN OUTSIDE CONSULTANT WHO SPECIALIZES IN PIPELINE FRACTURE MECHANICS (SEE ATTACHED). IT WAS FOUND THAT THE PIPELINE EXPLOSION RESULTED FROM FAILURE TO FOLLOW COMPANY PROCEDURES REGARDING THE FOLLOWING: THE COMPLETE PURGING OF ALLNATURAL GAS FROM A PIPELINE PRIOR TO FILLING IT WITH AN AIR/NITROGEN TEST MEDIUM. WELDING ON THE PIPELINE DURING THE TESTING OPERATION WITH A COMBUSTIBLEMIXTURE PRESENT, THE COMPANY CREW DID NOT FOLLOW ESTABLISHED PROCEDURES RELATIVE TO STRENGTH TESTING. I BELIEVE THAT THIS NARRATIVE, COUPLED WITH FORM RSPA F7100.1 AND THE CONSULTANT'S REPORT, PROVIDES ENOUGH DETAIL TO ANSWER ANY QUESTIONS. HOWEVER, PLEASE FEEL FREE TO CALL FIL BERNAL AT (213)244-3283 IF YOU HAVE ANY QUESTIONS REGARDING OUR REPORT.
2025-01-31 10:21 | YES | NO | 19960165 | 1996-11-08 | 4060 | EAST OHIO GAS CO | N PLUM ST & BERGER ST | EAST CANTON | STARK | OH |  | 3 | NO | 1337 | 1996-10-08 | 0 | 0 | 80000 | 57578.5734 | 139021.5906 | Null | 1 | 40 |  | 19961014 | 0.4 | 1 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | PE 3408 | DRISCO | 0 | 1994 | UNDER PAVEMENT |  | PAUL OLEKSA | 2167366858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | WATER DEPARTMENT EXCAVATED TO PERFORM EMERGENCY REPAIR TO WATER LINE. A BACKHOE SNAGGED AND CUT THE TOP OF A 4-INCH PLASTIC GAS MAIN. WATER ENTERED THE LOW PRESSURE GAS PIPING SYSTEM, CAUSING LOSS OF SERVICE TO 246 CUSTOMERS. THE PIPE WAS REPLACED AND SERVICE WAS RESTORED TO ALL CUSTOMERS. A TELEPHONIC REPORT WAS MADE TO THE PUCO ON 10-08-96 BUT A TELEPHONIC INCIDENT REPORT WAS NOTMADE UNTIL 10-14-96 WHEN IT BECAME APPARENT THAT THE UNUSUALLY HIGH COST OF RESTORING SERVICE DUE TO WATER IN THE PIPING SYSTEM WOULD EXCEED $50,000. ONE-CALL AGENCY WAS CALLED ON THE DAY OF EXCAVATION DUT DAMAGE OCCURRED BEFORE LOCATOR ARRIVED.
2025-01-31 10:21 | YES | YES | 19960177 | 1996-12-02 | 22210 | WASHINGTON WATER POWER CO | 7610 E. NORA | SPOKANE | SPOKANE | WA | 99212 | 3 | NO | 2020 | 1996-11-21 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 6 |  | 19961121 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | PIPE | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ALDYL-A | UPONOR | 1993 | 1993 | ABOVE GROUND |  | MICHAEL FAULKENBERRY | 5094828499 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ELECTRIC FEEDER TURNED OFF REMOTELY AFTER EMERGENCY CALL PLACED TO CENTRAL DISPATCH. ON 11/21/96 AT APPROX 8:20 P.M. JIMMIE DEAN, A GAS CREW FOREMAN, WASKILLED WHEN HE ACCIDENTALLY CAME INTO CONTACT WITH A DOWNED PRIMARY CONDUCTOR. THE GAS CREW, OF WHICH HE WAS A MEMBER, HAD BEEN DISPATCHED TO A GAS ODOR COMPLAINT AT A PRIVATE RESIDENCE AT 7610 E. NORA, SPOKANE, WA. WASHINGTON WATER POWER SUSTAINED EXTENSIVE DAMAGE TO ITS OVERHEAD ELECTRICAL SYSTEMS IN THEGREATER SPOKANE, WA AND COEUR D'ALENE, ID SERVICE TERRITORIES BY AN ICE STORM THAT OCCURRED ON TUESDAY 11/19. REPAIRS WERE UNDERWAY TO THE SYSTEM AT THE TIME OF THIS ACCIDENT AND ARE STILL ONGOING. THE GAS CREW DETERMINED THAT THECAUSE OF THE GAS ODOR WAS A LEAK IN THE BURIED GAS SERVICE CAUSED BY A SHORTTO GROUND FROM THE FALLEN PRIMARY CONDUCTOR. THE GAS CREW WAS AWARE OF THE DOWNED CONDUCTOR IN THE VICINITY OF THE WORK AREA. ALTHOUGH IT WAS NOT KNOWN THAT THE CONDUCTOR WAS STILL ENERGIZED, THE CREW WAS TREATING IT AS A POTENTIAL HAZARD. THE GAS CREW HAT SHUT-IN THE SERVICE AT THE MAIN PRIOR TO THE ACCIDENT AND WAS PLANNING TO RESTORE THE SERVICE THE NEXT MORNING (THE GAS SERVICEWAS NOT NEEDED THAT NIGHT AS THE POWER WAS OUT TO THE RESIDENCE ANYWAY). DURING CLEAN-UP ACTIVITIES, JIMMIE DEAN CAME INTO CONTACT WITH THE LIVE CONDUCTOR. CPR WAS PERFORMED BY HIS COWORKERS UNTIL AN AMBULANCE ARRIVED ON THE SCENEAND HE WAS TRANSPORTED TO VALLEY HOSPITAL IN SPOKANE, WA WHERE HE WAS PRONOUNCED DEAD. THE FATALITY OCCURED BECAUSE OF AN ELECTROCUTION AND WAS NOT A DIRECT RESULT OF A GAS INCIDENT.
2025-01-31 10:21 | NO | NO | 19960178 | 1996-12-16 | 15007 | PACIFIC GAS & ELECTRIC CO | STEPHANIE STREET | LIVINGSTON | MERCED | CA |  | 3 | NO | 2155 | 1996-11-07 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 50 |  | 19961108 | 220 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | REGULATOR/METER |  | OTHER | THROTTLING DIAPHRAGM | 0 | 0 | 102-013 | MOONEY | 1994 | 1994 | OTHER | INSIDE VAULT | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FOREIGN PARTICLES PASSED THROUGH THE FILTER OF A REGULATOR STATION AND DAMAGED THE WORKING AND BACK-UPS REGULATORS, CAUSING THE TRANSMISSION PRESSURE GASTO ENTER INTO THE DISTRIBUTION MAIN SYSTEM. APPARENT CAUSE - REGULATORS FAILED.
2025-01-31 10:21 | NO | NO | 19960179 | 1996-12-09 | 4483 | ENSTAR NATURAL GAS CO | LOT 7 BIRCH BLUFF SUBD. | SOLDOTNA | KENAI PENINSULA BOROUGH | AK | 99669 | 2 | NO | 514 | 1996-12-01 | 0 | 0 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 55 |  | 19961201 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M 8000 | DRISCOPIPE | 1995 | 1995 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON SUNDAY MORNING, DECEMBER 1, 1996, AT 5:14 AM AST, ENSTAR PERSONNEL WERE CALLED TO RESPOND TO A HOUSE FIRE AT LOT 7 BIRCH BLUFF SUBDIVISION IN SOLDOTNA, ALASKA. THE ORIGIN OF THE FIRE WAS DETERMINED TO BE THE SPONTANEOUS COMBUTION OF SOME OILY RAGS. NATURAL GAS WAS NOT INVOLVED IN STARTING THE FIRE. THE FIRE CONSUMED THE SINGLE FAMILY HOME AND IN THE PROCESS BURNED THE NATURAL GAS METER AND RISER. THE 5/8" HDPE SERVICE LINE INSIDE THE STEEL RISER MELTED CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF ANDCAPPED BY ENSTAR PERSONNEL.
2025-01-31 10:21 | YES | NO | 19960180 | 1996-12-05 | 2596 | COLUMBIA GAS OF OHIO INC | 302 SOUTH MAIN STREET | PROSPECT | MARION | OH | 43342 | 3 | NO | 925 | 1996-10-27 | 0 | 0 | 125000 | 89966.5209 | 217221.2353 | Null | 3 | 50 |  | 19961027 | 0.5 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | STEEL |  | 1.25 | 0.191 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | D. LEE REYNOLDS | 6144602261 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 2 |  | YES |  |  | ON SUNDAY, OCTOBER 27, 1996, AT 12:13P.M. OPERATOR RECEIVED A CALL FROM THE BATTLE RUN FIRE DEPT. REQUESTING A PRESSURE CHECK AFTER A FIRE AT THE AMERICAN LEGION POST IN PROSPECT, OH. AFTER ARRIVING AT THE SCENE AND PERFORMING AN INVESTIGATION, IT WAS DETERMINED THE 1.25" STEEL CUSTOMER-OWNED SERVICE LINE PIPE HAD SEVERED CAUSING GAS TO MIGRATE INTO THE BUILDING WHERE AN UNKNOWN SOURCE IGNITED THE GAS JUST BEFORE 9:30A.M. IT WAS FURTHER LEARNED THAT A LARGETREE WAS REMOVED IN FRONT OF THE BUILDING ON OCTOBER 26, 1996. DURING CONSTRUCTION, IT APPEARS THAT HEAVY EQUIPMENT CROSSED OVER THE CUSTOMER-OWNED SERVICE LINE SEVERAL TIMES. DUE TO THE CONDITION OF THE DAMAGED PIPE AND THE SURROUNDING ENVIRONMENT IT APPEARS THAT THE PIPE HAD EXPERIENCED EXCESSIVE LOADINGCAUSING THE PIPE TO SEVER.
2025-01-31 10:21 | YES | YES | 19960181 | 1996-12-17 | 12390 | METROPOLITAN UTILITIES DISTRICT | 129TH & FORT ST | OMAHA | DOUGLAS | NE |  | 4 | NO | 830 | 1996-11-18 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 10 |  | 19961118 | 125 | 125 | BY TEST | 122 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | WELD |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DONALD BLOCKER | 4024498210 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WELD FAILURE
2025-01-31 10:21 | YES | YES | 19960187 | 1996-12-24 | 13710 | NORTHERN ILLINOIS GAS CO | 6127 CHASE | DOWNERS GROVE | DU PAGE | IL | 60515 | 3 | NO | 2347 | 1996-11-30 | 2 | 1 | 100000 | 71973.2167 | 173776.9882 | YES | 0 | 10 |  | 19961201 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING | IN CUSTOMER'S PREMISES | RICHARD WOODARD | 6309838676 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CURRENTLY UNDER INVESTIGATION - CAUSE OF CUSTOMER'S FUEL SYSTEM INSIDE RESIDENCE. CURRENTLY UNDER INVESTIGATION - INSIDE PIPING - CUSTOMER OWNED.
2025-01-31 10:21 | YES | YES | 19960188 | 1996-12-27 | 11032 | LACLEDE GAS CO | 600 HAZEL | POPLAR BLUFF | BUTLER | MO | 63901 | 3 | YES | 2237 | 1996-12-02 | 1 | 0 | 115000 | 82769.1992 | 199843.5365 | Null | 2 | 8 |  | 19961203 | 25 | 28 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NONE SPECIFIED | POLYETHYLENE PLASTIC |  | 1.13 | 0.099 | ASTM 02513 | PHILLIPS/DRISCO PIPE | 0 | 1993 | UNDER GROUND OR UNDER WATER |  | PAUL HUNKER | 3143420528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | WHILE ATTEMPTING TO CLEAR A BLOCKED SEWER, A PRIVATE CONTRACTOR'S SEWER AUGERCONTACTED A 1" DIAMETER PLASTIC GAS SERVICE LINE. THE SERVICE LINE HAD BEENINSTALLED WITH A PNEUMATIC BORING TOOL WHICH TRAVELED THROUGH AN 8" OD SEWERLATERAL APPROX 51" DEEP. GAS ESCAPED FROM THE SERVICE LINE FOR #604 HAZEL THROUGH THE SEWER LATERAL INTO #600 HAZEL AND SUBSEQUENTLY WAS IGNITED BY AN UNDETERMINED SOURCE IN #600 HAZEL, APT. B. SUPPLEMENTAL RECEIVED 1/31/97INDICATES A FATALITY WAS INVOLVED.
2025-01-31 10:21 | YES | NO | 19960189 | 1996-12-17 | 15896 | PROVIDENCE GAS CO | 391 SAMUEL GORTON AVENUE | WARWICK | KENT | RI | 02889 | 3 | NO | 1255 | 1996-11-18 | 0 | 0 | 250000 | 179933.0418 | 434442.4706 | Null | 0 | 35 |  | 19961118 | 9 | 12 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY | SERVICE LINE | VALVE |  | STEEL |  | 1 | 0.179 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GARY MUNROE | 4012725040 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-11-04 | YES | 3 | SEE COMMENTS | YES |  |  | THE LOCATION WAS POINTED OUT AND VERBALLY INDICATED BY THE OPERATOR. D'AMBRACONSTRUCTION WAS INSTALLING SANITARY SEWER MAINS ON SAMUEL GORDON AVENUE IN WARWICK, RI. THE SEWERS WERE BEING INSTALLED AT A DEPTH OF APPROX. 12 FEET. APROVIDENCE GAS COMPANY REPRESENTATIVE INDICATED THE APPROX. LOCATION OF THE NO RECORD SERVICE FOR 391 SAMUEL GORTON AVENUE TO D'AMBRA CONSTRUCTION COMPANY THE MORNING OF NOV. 18TH 1996. AT APPROX. 12:55PM EST THE EXCAVATING EQUIPMENT INSTALLING THE SEWERS STRUCK THE 1" STEEL SERVICE SERVICING NUMBER 391 SMAUEL GORDON AVENUE. THE SERIVE OPERATING AT A PRESSURE OF 35PSIG APPARENTLY BROKE INSIDE THE BASEMENT RELEASING GAS INTO THE HOUSE. THE TWO ADJORNING HOUSES AND AN AUTOMOBILE WERE ALSO DAMAGED. THE IGNITION SOURCE OF THE ESCAPING GAS IS UNKNOWN. THE D'AMBRA BACKHOE OPERATOR INFORMED THE PROVIDENCE GAS COMPANY LINEWALKER THAT THE BACKHOE OPERATOR HAD FOUND THE SERVICE AND AS HE WAS TAKING A BUCKET OF SOIL OUT OF THE TRENCH, HE HIT THE SERVICE WITH A TOOTH OF THE BACKHOE BUCKET. WHEN ASKED WHY HE DID NOT PULL THE SERVICE COMPLETELY OUTOF THE GROUND WHEN HE HIT IT, THE BACKHOE OPERATOR REPLIED THAT HE ASKED FELLOW D'AMBRA EMPLOYEES, WHO WERE IN THE TRENCH, IF THERE WAS GAS IN THE TRENCH, AND THEY INDICATED ONLY A SMALL AMOUNT. THE BACKHOE OPERATOR SAID THE HOUSEEXPLODED ABOUT TWO MINUTES LATER.
2025-01-31 10:21 | YES | YES | 19960193 | 1996-12-30 | 4499 | ENTEX - DIVISION OF ARKLA INC | 301 INDUSTRIAL BLVD., C-21 | LAREDO | WEBB | TX | 78042 | 3 | NO | 1635 | 1996-12-23 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 10 |  | 19961223 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT | TEE | POLYETHYLENE PLASTIC |  | 2 | 0 | SDR ALDYL | DUPONT | 1977 | 1977 | UNDER GROUND OR UNDER WATER |  | EDWARD HORN | 2106436922 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | GAS MAIN WAS DAMAGED BY A BACKHOE WORKING AT THIS LOCATION. COMPANY EMPLOYEES WERE INSTALLING BY-PASS FITTINGS, PRIOR TO SQUEEZING OFF THE 2" MAIN, WHEN GAS WAS IGNITED FROM AN UNDETERMINED SOURCE. PARTY CAUSING DAMAGE WAS LAREDO CITY SEWER DEPARTMENT.
2025-01-31 10:21 | YES | YES | 19960194 | 1997-07-02 | 18116 | SAN JUAN GAS CO |  |  |  | PR |  |  | Null | 0 | 1996-11-21 | 33 | 42 | 5000000 | 3598660.8363 | 8688849.4124 | NO | 0 | 0 |  | 19961121 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | NO DATA |  | NO DATA |  | NO DATA |  |  | 0 |  |  | 0 | 0 | NO DATA |  | REPORT NOT SUBMITTED BY COMPANY. SEE ATTACHMENT |  | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | ATTACHMENT: ADDENDUM - PART I GENERAL REPORT INFORMATION ATTACHMENT -- NOTE: NTSB FOUND THAT NATURAL GAS WAS INVOLVED IN THE ACCIDENT. FOR FURTHER INFORMATION SEE NTIS REPORT NUMBER PB97-916501: TITLE: SAN JUAN GAS COMPANY, INC./ENRON CORP. PROPANE GAS EXPLOSION IN SAN JUAN, PUERTO RICO ON NOVEMBER 21, 1996 (NTSB REPORT NUMBER: PAR-97-01, ADOPTED ON 12/23/1997). PROPERTY DAMAGE/LOSS ESTIMATE: DOLLAR AMOUNT HAS NOT BEEN CONFIRMED DUE TO LITIGATION. ESTIMATED TO BE APPROXIMATELY $5 MILLION DOLLARS. THE GAS SYSTEM DOES NOT OPERATE IN POUNDS PER SQUARE INCH (PSIA). IT WAS OPERATED AS A LOW PRESSURE SYSTEM WHICH WAS APPROX. 10" WATER COLUMN OR 4 OR 5 OUNCES PER SQUARE INCH GUAGE.
2025-01-31 10:21 | YES | YES | 19970001 | 1997-01-13 | 12582 | MISSISSIPPI VALLEY GAS | 3547 WEST CAPITOL STREET | JACKSON | HINDS | MS | 39209 | 3 | NO | 2342 | 1997-01-02 | 0 | 1 | 30000 | 21215.0913 | 51223.1472 | Null | 6 | 18 |  | 19970103 | 23 | 37 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 |  |  | 0 | 1994 | UNDER GROUND OR UNDER WATER |  | PAUL NOEL | 6019616860 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SEE COMMENTS | Null |  | Null | 0 |  | Null |  |  | INADEQUATE SUPPORT UNDER PLASTIC PIPE ALLOWED BACKFILL TO BEND PIPE WHICH CAUSED STRESS AT A POINT WHERE THE PIPE MADE CONTACT WITH METAL STIFFENER IN COMPRESSION FITTING AND RESULTED IN A BREAK IN THE PLASTIC PIPE. LEAKING GAS FROMBROKEN SERVICE LINE MIGRATED INTO RESIDENCE THROUGH SEWER LINE.
2025-01-31 10:21 | YES | YES | 19970002 | 1997-01-13 | 24015 | YANKEE GAS SERVICES CO | 102 BEECHER STREET | SOUTHINGTON | HARTFORD | CT | 06489 | 1 | NO | 1421 | 1996-12-09 | 0 | 1 | 200000 | 143946.4335 | 347553.9765 | Null | 0 | 0 |  | 19961209 | 3.5 | 4 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN | SEE COMMENTS | OTHER | NONE SPECIFIED | CAST IRON |  | 4 | 0.45 |  |  | 0 | 1940 | UNDER PAVEMENT |  | JOSEPH ANCONA | 2035963034 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT THE DATE, TIME AND LOCATION INDICATED IN PART 1 -GENERAL REPORT INFO, A FIRE AND EXPLOSION OCCURRED RESULTING IN ONE INJURY REQUIRING MEDICAL ATTENTION AND PROPERTY DAMAGE OF APPROX $200,000. SUBSEQUENTLY, A NATURAL GAS LEAK WASDISCOVERED ON THE GAS DISTRIBUTION PIPING DESCRIBED IN PART 4 - ORIGIN OF THE INCIDENT. THE EXTENT, IF ANY, TO WHICH THE LEAK IN THE GAS DISTRIBUTION SYSTEM CONTRIBUTED THE FIRE/EXPLOSION IS YET TO BE ESTABLISHED AND IS UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 19970003 | 1997-01-02 | 18532 | SOUTHERN UNION GAS CO | 100 BLOCK HOUSTON AVE | PORT ARTHUR | JEFFERSON | TX | 77642 | 3 | NO | 2230 | 1996-11-29 | 0 | 0 | 5000 | 3598.6608 | 8688.8494 | YES | 0 | 35 |  | 19961129 | 58 | 100 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | RELIEF VALVE | OTHER | RELIEF VALVE | STEEL |  | 6 | 0 | 6"Q8 2952 | FARRIS | 0 | 1963 | ABOVE GROUND |  | JESSE WALLIS | 5123708212 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 11/29/96, SUG WAS NOTIFIED BY THE PORT ARTHUR FIRE DEPT THAT A RELIEF VALVE ON THE DISTRIBUTION SYSTEM WAS RELIEVING GAS AND HAD IGNITED. SUG RESPONDED AND ISOLATED THE VALVE. THE VALVE WAS THEN REMOVED AND TRANSPORTED TO THE SUG SHOP LOCATION FOR EVALUATION. ALL TESTS AND REVIEW OF PRESSURE CHARTS INDICATE NO MALFUNCTION ON THE DISTRIBUTION SYSTEM OR OF THE VALVE. THE PROBABLE CAUSE OF THIS INCIDENT WAS THE FAILURE OF THE ELECTRIC CABLE STRICKING THE RELIEF VALVE CAUSING THE VALVE TO RELEASE GAS AT PRESSURE AND IGNITING THE ESCAPING GAS.
2025-01-31 10:21 | NO | NO | 19970004 | 1997-01-03 | 11680 | LONE STAR GAS CO | 502 CHICKAPOO TRACE | DALLAS | GRAND PRAIRIE | TX | 75051 | 3 | NO | 1650 | 1996-12-03 | 0 | 0 | 0 | 0 | 0 | YES | 7 | 25 |  | 19961203 | 24 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.307 | PE 2306 | NIPAK | 1970 | 1971 | UNDER GROUND OR UNDER WATER |  | ML IMBODEN | 2146702779 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null |  |  | A HOUSE LOCATED AT 502 CHICAPOO TRACE IN GRAND PRAIRIE, TX WAS DESTROYED BY AN EXPLOSION. IMPACT FROM THE EXPLOSION DAMAGED SEVERAL HOUSES IN THE VICINITY. INVESTIGATION BY LONE STAR GAS COMPANY PERSONNEL REVEALED GAS IN THE SEWERVENTS OF THE HOUSES ON EITHER SIDE OF 502 CHICKAPOO TRACE AND IN THE SEWER OF 502 CHICKAPOO TRACE. BAR TESTING OF THE MAIN IN SW 5TH STREET IN FRONT OF 502 CHICKAPOO TRACE INDICATED THE PRESENCE OF GAS, THE SOURCE OF WHICH WAS FOUND TO BE A CRACK IN 3 INCH PE 3306 POLY MAIN. THE LEAK COULD NOT BE RULED OUTAS A FACTOR IN THE EXPLOSION AS NO GAS WAS PRESENT IN THE SEWER OF 502 CHICKAPOO TRACE OR THE VENTS OF THE ADJACENT HOUSES AFTER THE LEAK WAS REPAIRED.
2025-01-31 10:21 | YES | YES | 19970010 | 1997-01-21 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 9 LAWTON ROAD | FOSTER | MCKEAN | PA | 16703 | 2 | NO | 1640 | 1996-10-24 | 0 | 2 | 50000 | 35986.6084 | 86888.4941 | Null | 0 | 30 |  | 19961024 | 45 | 15 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0 |  |  | 0 | 1950 | UNDER GROUND OR UNDER WATER |  | CRAIG WALTON | 4125727792 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CORROSION LEAK ON A 1 1/2" CUSTOMER OWNED SERVICE LINE 17" FROM THE STRUCTURE ALLOWED GAS TO ENTER A HOME. AN EXPLOSION FOLLOWED BY A FIRE WHICH DESTROYED THE SINGLE STORY RESIDENCE. TWO OCCUPANTS WERE HOSPITALIZED FOR TREATMENTOF BURNS. REPORT IS BEING SUPPLEMENTED TO FURNISH INFORMATION WHICH WASOMITTED FROM THE ORIGINAL.
2025-01-31 10:21 | YES | NO | 19970011 | 1997-01-15 | 13650 | NORTH PENN GAS CO | 608 S. MAIN STREET | COUDERSPORT | POTTER | PA | 16915 | 3 | NO | 1055 | 1996-12-11 | 0 | 0 | 250000 | 179933.0418 | 434442.4706 | Null | 0 | 10 |  | 19961211 | 39 | 2 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | METER SET ASSEMBLY | FUEL LINE/SERVICE LINE | OTHER | SEE ATTACHED ADDENDUM | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT BEARD | 6109328458 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON 11/27/96, IN ANTICIPATION OF THE INSTALLATION OF A NEW MAIN ON SOUTH MAINST., A DISTRIBUTION CONSTRUCTION CREW FROM NORTH PENN GAS COMPANY INSTALLED A PORTION OF A NEW SERVICE TO THE RESIDENCE OF 608 SOUTH MAIN ST., COUDERSPORT. THIS SECTION OF SERVICE RAN FROM THE NEW METER LOCATION TO THE CURB AREA. IN ADDITION TO THIS SECTION OF SERVICE, A METER RISER WAS INSTALLED AND PLUGGED. THIS SECTION OF SERVICE WAS SUCCESSFULLY TESTED TO 100 PSIG. THE TEST WASREMOVED AND THE SERVICE CAPPED. ON 12/5, ANOTHER SECTION OF THE SAME SERVICEWAS INSTALLED ALONG WITH THE NEW 4 INCH POLYETHYLENE MAIN. THIS SECTION OF SERVICE RAN FROM THE NEW MAIN, ACROSS SOUTH MAIN ST. TO CURB AREA IN FRONT OF 608 SOUTH MAIN ST. THIS SECTION OF SERVICE WAS NOT CONNECTED TO THE SECTION OF SERVICE OF SERVICE INSTALLED ON 11/27. ON 12/10, A CREW BEGAN INSTALLING FUEL LINE PIPING IN THE BASEMENT OF THE RESIDENCE AT 608 SOUTH MAIN ST. THE CREW ALSO INSTALLED THE RESIDENTIAL METER SET AND TIED THE SET INTO THE FUEL LINE. THE METER VALVE WAS NOT CLOSED AT THIS TIME. THE FUEL LINE INSTALLATION WAS NOT COMPLETED ON 12/10, AND THE FUEL LINE WAS LEFT WITH AN OPEN END INSIDE THE RESIDENCE. ON 12/11, A DIFFERENT CREW RETURNED AND CONNECTED THE TWO SECTIONS OF SERVICE LINE WHICH HAD BEEN INSTALLED ON 11/27 AND 12/5. UPON COMPLETING THIS TIE IN, GAS ENTERED THE SERVICE LINE, METER SET AND FUEL LINE. APPROX ONE HOUR AFTER GAS WAS INTRODUCED TO THE INCOMPLETE FUEL LINE, AND EXPLOSION OCCURRED AT 608 SOUTH MAIN ST. THE OPERATOR HAS LISTED THE CAUSE OF THIS INCIDENT AS OPERATOR ERROR. DAMAGE IS ESTIMATED AT $250,000. ADDITIONAL INFO: ALL MAIN AND SERVICE LINE FACILITIES INVOLVED IN THIS INCIDENT WERE CONSTRUCTED OF POLYETHYLENE. THEREFORE CAHTODIC PROTECTION CONCERNS ARE NOT APPLICABLE.THERE WERE NO FACILITY COMPONENT FAILURES INVOLVED IN THIS INCIDENT. THERE WAS NO DAMAGE BY OUTSIDE FORCES INVOLVED IN THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 19970012 | 1997-01-16 | 13710 | NORTHERN ILLINOIS GAS CO | 121 DIVISION STREET | ST. CHARLES | KANE | IL |  | 3 | NO | 1646 | 1997-01-08 | 0 | 0 | 75000 | 53037.7282 | 128057.8679 | YES | 6 | 59 |  | 19970108 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | SEE COMMENTS | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | OTHER | NONE SPECIFIED | GEORGE WALDVOGEL | 6309838676 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | FACILITIES WERE DAMAGED SOME TIME IN THE PAST. CURRENTLY UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 19970013 | 1997-01-22 | 15233 | CENTRAL PENN GAS CO - DAUPHIN DISTRICT | S.R. 895 | EAST PENN | CARBON | PA | 19363 | 2 | NO | 1030 | 1996-12-21 | 0 | 0 | 100000 | 71973.2167 | 173776.9882 | Null | 1 | 39 |  | 19961221 | 200 | 367 | BY TEST | 600 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NONE SPECIFIED | STEEL |  | 4.5 | 0 |  |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | ROBERT BEARD | 6109328458 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-12-08 | YES | 2 |  | YES |  |  | ON 12/21/96, AN INDIVIDUAL BELIEVED TO BE AN EMPLOYEE OF TROXELL'S TRUCKING,INC., EXCAVATING WITH A BULLDOZER, RUPTURED A FOUR INCH HIGH PRESSURE DISTRIBUTION LINE. THE LINE WHICH WAS OPERATING AT 200 PSIG, SERVES AS THE ONLY FEED TO PFG GAS' DISTRIBUTION SYSTEMS IN JIM THORPE, PA AND LEHIGHTON, PA. THE RUPTURE PROMPTED THE IMMEDIATE SHUTDOWN OF THE PORTION OF THE PFG SYSTEM. APPROX 2000 CUSTOMERS WERE AFFECTED. NO INJURIES RESULTED FROM THIS INCIDENT. THELOCATION OF THE LINE HAD BEEN ACCURATELY MARKED PURSUANT TO THE PA ONE CALL SYSTEM (PA ACT 38). HOWEVER, EXCAVATION DID NOT TAKE PLACE WITHIN THE 10 DAY PERIOD PRESCRIBED BY ACT 38. ITEMS REQUIRING SUPPLEMENTAL REPORT SUBMISSION: THE EXACT AMOUNT OF PROPERTY DAMAGE/LOSS IS NOT KNOW AT THIS TIME. THIS FIGURE IS EXPECTED TO EXCEED $100,000. THE LOSS IS PRIMARILY THE LABOR COST ASSOCIATED WITH RESTORATION OF SERVICE. THE ACTUAL LOSS WILL BE REPORTED AT A LATERDATE. THE WALL THICKNESS AND EXACT SPECIFICATION OF THE PIPE INVOLVED HAS NOT BEEN VERIFIED. TESTS WILL BE CONDUCTED ON THE PIPE TO ENSURE DATA SUBMITTEDON SUPPLEMENTAL REPORTS WILL BE ACCURATE. THIS INCIDENT OCCURRED IN EAST PENN TOWNSHIP, CARBON COUNTY, PA.
2025-01-31 10:21 | NO | NO | 19970014 | 1997-01-21 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 4321 HARVEY | MESQUITE | DALLAS | TX | 75149 | 2 | NO | 1048 | 1996-12-10 | 0 | 0 | 40000 | 28789.2867 | 69510.7953 | Null | 0 | 0 |  | 19961210 | 21 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | WAYNE POWER | 2146702706 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 1-1/4" COMPRESSION COUPLING ON SERVICE TAP WAS LEAKING AND IGNITED WHICH CAUSED DAMAGE TO A HOUSE.
2025-01-31 10:21 | YES | YES | 19970018 | 1997-02-04 | 15359 | PEOPLES NATURAL GAS | 250 W. 4TH STREET | ST. ANSGAR | MITCHELL | IA | 50472 | 3 | NO | 715 | 1997-01-16 | 0 | 1 | 200 | 141.4339 | 341.4876 | Null | 2 | 0 |  | 19970116 | 12 | 15 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | JOINT | TEE | STEEL |  | 0.5 | 0 |  | X-TRUBE | 1966 | 1966 | UNDER GROUND OR UNDER WATER |  | EDWIN HATTER | 4022212546 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | GROUND FROST APPARENTLY CAUSED A X-TRUBE SERVICE LINE BEHIND THE SPORTSMAN BAR TO PULL OUT OF A TEE. GAS MIGRATED INTO THE MEN'S RESTROOM IN THE BACK OF THE BAR. AN EXPLOSION OCCURRED AT THE TIME WHEN THE INDIVIDUAL INJURED LIT A CIGARETTE IN THE RESTROOM BLOWING HIM AND A SECOND INDIVIDUAL THROUGH THE RESTROOM DOOR.
2025-01-31 10:21 | NO | NO | 19970021 | 1997-02-11 | 13710 | NORTHERN ILLINOIS GAS CO | 1016 ASH DRIVE | ST. ANNE | KANKAKEE | IL | 60964 | 3 | NO | 400 | 1997-01-18 | 0 | 0 | 40000 | 28286.7884 | 68297.5295 | Null | 1 | 0 |  | 19970118 | 60 | 60 | BY CFR 192.619(A)(3) | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NOT SPECIFIED | OTHER | NOT SPECIFIED | OTHER | NOT SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING | NOT SPECIFIED | GEORGE WALDVOGEL | 6309838676 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INCIDENT RESULTED FROM AN APPLIANCE INSIDE THE BUILDING. ORIGIN OF THE CAUSEWAS FROM AN APPLIANCE INSIDE THE BUILDING.
2025-01-31 10:21 | NO | NO | 19970022 | 1997-02-20 | 4060 | EAST OHIO GAS CO | 2714 WAYNESBURG RD. S.E. | CANTON | STARK | OH | 44707 | 3 | NO | 823 | 1997-01-20 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 1 | 32 |  | 19970120 | 49 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0 | 0 |  | EAST OHIO GAS | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | PAUL OLEKSA | 2167366858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THE DRIP RISER IS LOCATED IN A GRAVELLED DRIVEWAY OR PARKING AREA NEAR A SMALL COMMERCIAL BUILDING. IT APPEARS THAT RECENTLY THIS AREA WAS REGARDED AND FRESH GRAVEL WAS APPLIED. APPARENTLY THE RISER WAS BUMPED OR PUSHED TO ONE SIDE, CAUSING A CRACK AT ITS CONNECTION TO THE SERVICE LINE. FROST PREVENTED THEGAS FROM VENTING. IT MIGRATED TO THE BUILDING AND AN EXPLOSION FOLLOWED.
2025-01-31 10:21 | YES | NO | 19970023 | 1997-02-20 | 15462 | PHILADELPHIA ELECTRIC CO | 504 EAST GLENOLDEN AVE. | GLENOLDEN | DELAWARE | PA | 19036 | 3 | NO | 1 | 1997-01-21 | 0 | 0 | 400000 | 282867.884 | 682975.2954 | Null | 4 | 19 |  | 19970121 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 | 0.44 |  |  | 0 | 1953 | UNDER PAVEMENT | SEE COMMENTS | ERIC STEIN | 6104906860 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 8" CAST IRON MAIN BREAK UNDER SIDEWALK IN FRONT OF 504 E. GLENOLDEN AVENUE, IN GLENOLDEN, PA RESULTED IN AN EXPLOSION AND FIRE AT 504 AND 502 E. GLENOLDEN AVE. NO DEATHS OR INJURIES KNOWN. THE PROPERTIES AT 504 AND 502 E. GLENOLDEN WERE DESTROYED BY THE EXPLOSION AND/OR FIRE. FURTHER INVESTIGATION IS BEINGCONDUCTED BY THE PA PUC. AREA OF INCIDENT: MAIN LOCATED UNDER SIDEWALK.
2025-01-31 10:21 | YES | NO | 19970024 | 1997-02-20 | 15462 | PHILADELPHIA ELECTRIC CO | 4938 JACKSON DRIVE | BROOKHAVEN | DELAWARE | PA | 19015 | 3 | NO | 2243 | 1997-01-25 | 0 | 0 | 200000 | 141433.942 | 341487.6477 | Null | 3 | 13 |  | 19970126 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.41 |  |  | 0 | 1962 | UNDER GROUND OR UNDER WATER | SEE COMMENTS | ERIC STEIN | 6104906860 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MAIN LOCATED UNDER GRASS AREA BETWEEN CURB AND SIDEWALK. 4" CAST IRON MAIN BREAK GRASSY AREA BETWEEN CURB AND SIDEWALK IN FRONT OF 4938 JACKSON DRIVE, BROOKHAVEN, PA RESULTED IN AN EXPLOSION AND PROPERTY DAMAGE AT THAT LOCATION. NO DEATHS OR INJURIES KNOWN. FURTHER INVESTIGATION IS BEING CONDUCTED BY THE PA PUC. APPARENT CAUSE - CAST IRON MAIN BREAK.
2025-01-31 10:21 | YES | YES | 19970025 | 1997-02-07 | 180 | ALABAMA GAS CORP | 711 EASTWOOD PLACE | VESTAVIA | JEFFERSON | AL | 35233 | 3 | NO | 1000 | 1996-10-17 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19961017 | 11 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | MIKE SWINSON | 2053268309 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ACCORDING TO RODDY SAMPLE WITH M.U.I., A HOME REMODELING COMPANY DAMAGED THESERVICE LINE TO 711 EASTWOOD PLACE AROUND 10:00AM ON OCT.16. TWO EMPLOYEES, MYSON BLOCKER AND ANDRE BLOCKER, ATTEMPTED TO MAKE THE SERVICE LINE SAFE. MYSON LOST CONSCIOUSNESS AND WAS TRANSPORTED BY PARAMEDICS TO THE VA HOSPITAL WHICH WAS FAMILIAR WITH HIS MEDICAL HISTORY ASSOCIATED WITH THE GULF WAR. ANDREBECAME NAUSEATED AND COMPLAINED OF HEADACHES BUT WAS NOT TAKEN TO THE HOSPITAL. ALAGSCO CREWS ARRIVED TO MAKE REPAIRS TO THE SERVICE LINE AND WERE NOT AWARE OF THE INCIDENT. RODDY WAS INFORMED BY MYSON'S MOTHER ON OCT 17 THAT MYSON WAS TO BE TRANSPORTED TO UNIVERSITY HOSPITAL WHERE HE WOULD BE EVALUATED FOR POSSIBLE BRAIN DAMANGE, NUMBNESS, AND PARALYSIS. MYSON'S MOTHER ALSO INFORMED RODDY THAT ANDRE WAS VOMITING AND WAS TAKEN TO AN EMERGENCY ROOM THE MORNING OF OCT 17. ALAGASCO WAS NOT AWARE OF THE INCIDENT UNTL RODDY CALLED RANDY BRIGHT WITH ALAGASCO THE MORNING OF OCT 17.
2025-01-31 10:21 | YES | NO | 19970026 | 1997-02-10 | 20010 | U G I CORP | 2211 CULLUM DRIVE | READING | BERKS | PA | 19601 | 3 | NO | 1157 | 1997-01-15 | 0 | 0 | 250000 | 176792.4275 | 426859.5596 | Null | 0 | 40 |  | 19970115 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1957 | UNDER PAVEMENT |  | FREDERICK KACZOR | 6107963539 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-07-22 | YES | 3 | PAINT - STAKES | YES |  |  | ESCAPING GAS FROM A TWO-INCH FRACTURED MAIN MIGRATED UNDERGROUND INTO THE HOUSE AT 2211 CULLUM DRIVE WHERE IT ACCUMULATED AND SUBSEQUENTLY WAS IGNITED BYAN UNKNOWN SOURCE. THE HOUSE WAS DESTROYED BY THE RESULTING EXPLOSION AND ENSUING FIRE. THERE WERE NO HUMAN INJURIES OR DEATHS INVOLVED. EXCAVATION OF THE TWO-INCH GAS MAIN IN FRONT OF THE DRIVEWAY TO 2209A CULLUM DRIVE REVEALED AFRACTURE. THIS FRACTURE, LOCATED ON THE UNDERSIDE OF THE MAIN AND TOWARD THECURB, EXTENDED APPROX A THIRD OF THE DISTANCE AROUND THE CIRCUMFERENCE OF THE PIPE. ADJACENT TO THE FRACTURE THERE APPEARS TO BE A GOUGE IN THE PIPING. THE FRACTURE AND APPARENT GOUGE WAS POSITIONED WITHIN THE TRENCH AREA OF A RECENTLY INSTALLED SEWER LATERAL. INVESTIGATION OF THE FAILURE MECHANISM IS STILL ONGOING.
2025-01-31 10:21 | YES | NO | 19970031 | 1997-02-25 | 15469 | PHILADELPHIA GAS WORKS | 3648 N. 9TH STREET | PHILADELPHIA | PHILADELPHIA | PA | 19140 | 4 | NO | 1420 | 1997-01-24 | 0 | 0 | 75000 | 53037.7282 | 128057.8679 | Null | 15 | 55 |  | 19970124 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 |  |  | 0 | 1907 | WITHIN/UNDER BUILDING |  | BRIAN SCHENK | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | THE FACTORS BELIEVED TO HAVE CONTRIBUTED TO THIS INCIDENT HAVE BEEN INVESTIGATED BY THE PHILADELPHIA FIRE DEPT. AND THE PHILADELPHIA GAS WORKS (PGW). PWGFOUND A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON GAS MAIN AT 139'6" SOUTH OF THE SOUTH CURB LINE OF ERIC AVENUE AND 3'6" EAST OF THE WEST CURB LINE OF 9THSTREET. THIS MAY HAVE ALLOWED NATURAL GAS TO MIGRATE INTO THE BASEMENT OF 3648 N. 9TH STREET AND MAY HAVE BEEN IGNITED BY AN UNKNOWN SOURCE OF IGNITION.
2025-01-31 10:21 | NO | NO | 19970032 | 1997-02-25 | 15359 | PEOPLES NATURAL GAS | 127 12TH ST. | CLOQUET | CARLTON | MN | 55720 | 3 | NO | 620 | 1997-02-14 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 0 | 15 |  | 19970215 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0 | PE2306 | DUPONT ALDYL A | 1979 | 1979 | ABOVE GROUND |  | BRIAN KROHN | 4022212061 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | METER SET SERVICE REGULATOR APPARETLY OVERPRESSURED THE CUSTOMER'S FUEL LINEPIPING RESULTING IN A FIRE AND EXPLOSION. REGULATOR VENT APPARENTLY FROZEOVER CAUSING OR CONTRIBUTING TO THE INCIDENT. SERVICE REGULATOR ICED OVER.
2025-01-31 10:21 | YES | NO | 19970033 | 1997-03-03 | 2309 | CHESAPEAKE UTILITY CORP | 1300 S. FARMVIEW DRIVE | DOVER | KENT | DE | 19904 | 3 | NO | 1047 | 1997-01-29 | 0 | 0 | 1500000 | 1060754.565 | 2561157.3577 | Null | 0 | 55 |  | 19970129 | 38 | 43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | 3/4 X 3/4 | CENTRAL PLASTIC | 1986 | 1987 | ABOVE GROUND |  | GEORGE LEWIS | 3027346797 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | METER ASSEMBLY WAS STRUCK BY A PASSENGER VEHICLE. THE SERVICE RISER WAS DAMAGED BELOW THE INLET VALVE. THE CAUSE OF THE INCIDENT WAS A VEHICULAR ACCIDENT. A PASSENGER VEHICLE STRUCK AND DAMAGED AN APARTMENT BUILDING AND ADJACENT NATURAL GAS METER SET. A RESULTING FIRE CAUSED AN ESTIMATED 1.5 MILLION IN DAMAGES TO THE APARTMENT BUILDING. THERE WERE NO INJURIES OR FATALITIES.
2025-01-31 10:21 | YES | YES | 19970034 | 1997-03-03 | 2364 | CINCINNATI GAS & ELECTRIC CO | 111 SKOKIAAN DRIVE | FRANKLIN | WARREN | OH |  | 3 | Null | 325 | 1997-01-30 | 0 | 1 | 118000 | 83446.0258 | 201477.7121 | Null | 1 | 53 |  | 19970130 | 18 | 35 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.35 |  |  | 0 | 1955 | UNDER GROUND OR UNDER WATER |  | WILLIAM HOBLITZELL | 5132873921 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE RESPONDING POLICE DEPT REPORTED THAT THERE WAS A HOUSE ON FIRE AND AN INDICATION OF GAS IN THE SEWERS. FOUND WAS A FOUR INCH CAST IRON MAIN BROKEN WHERE THE WATER SERVICE CROSSED THE MAIN. THIS WAS LOCATED APPROX 42' FROM THE FACE OF THE BUILDING & DIRECTLY IN FRONT OF #111 SKOKIAAN DRIVE. APPROX 42' OF THE 4" CI MAIN WAS EXPOSED, INSPECTED AND EVENTUALLY REPLACED. THE PIPE CONDITION WAS GOOD WITH NO EVIDENCE OF CORROSION. THE EXACT CAUSE OF THE BREAK IS UNKNOWN.
2025-01-31 10:21 | YES | YES | 19970035 | 1997-03-07 | 12582 | MISSISSIPPI VALLEY GAS | 2529 UTAH STREET | JACKSON | HINDS | MS | 39213 | 3 | NO | 2142 | 1997-02-24 | 1 | 0 | 75000 | 53037.7282 | 128057.8679 | Null | 0 | 15 |  | 19970224 | 23 | 37 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S HOME | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL NOEL | 6019616860 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FEBRUARY 24, 1997, THE CITY OF JACKSON FIRE DEPT. CALLED OUR COMPANY AT 9:42P.M. REQUESTING ASSISTANCE WITH A HOUSE FIRE AT 2529 UTAH STREET. OUR SERVICE REP. ARRIVED ON THE SCENE AT 9:53 P.M. AND FOUND GAS SERVICE WAS ALREADY CUT OFF AT THE METER. DUE TO EXTENSIVE FIRE DAMAGE INVESTIGATION WAS DELAYED FOR SOME TIME BEFORE IT WAS DETERMINED THAT NATURAL GAS WAS NOT INVOLVED IN THECAUSE OF THE FIRE OR INJURIES THAT RESULTED IN A FATALITY. PRIOR TO DETERMINING THERE WAS NO RELEASE OF NATURAL GAS A TELEPHONIC REPORT WAS MADE IN CASE IT WAS LATER FOUND TO BE A REPORTABLE INCIDENT.
2025-01-31 10:21 | NO | NO | 19970036 | 1997-03-06 | 4483 | ENSTAR NATURAL GAS CO | 821 BOUNTY DR | ANCHORAGE |  | AK | 99515 | 3 | NO | 615 | 1997-02-27 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 0 | 15 |  | 19970227 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON THURSDAY, 02/27/97 AT APPROX. 6:15 AM AST, ENSTAR NATURAL GAS COMP RESPONDED TO A HOUSE FIRE AT 821 BOUNTY DRIVE, ANCHORAGE, AK (LOT 22, BLOCK 13 OCEAN VIEW SUBDIVISION). ANCHORAGE FIRE DEPT OFFICIALS REPORTED THE FIRE ORIGINATED WHEN THE OCCUPANT THREW A SMOLDERING LOG FROM THE FIREPLACE OUTSIDE ON THEDECK AND SUBSEQUENTLY STARTED THE DECK AND HOUSE ON FIRE. THE RESULTING FIREENGULFED THE STRUCTURE. THE FIRE CONSUMED ENSTAR'S REGULATOR AND METER, CAUSING A RELEASE OF NATURAL GAS. THE X-TRUBE SERVICE LINE WAS PINCHED OFF BY FIRE DEPT PERSONNEL AND CAPPED BY ENSTAR PERSONNE. ESTIMATED DAMAGE TO THE STRUCTURE WAS IN EXCESS OF $50,000.
2025-01-31 10:21 | YES | YES | 19970040 | 1997-03-12 | 6342 | GEORGIA NATURAL GAS CO | ANTHONY RD @ EDWARDS AVENUE | MACON | BIBB | GA | 31213 | 3 | NO | 1440 | 1997-02-18 | 1 | 3 | 50 | 35.3585 | 85.3719 | Null | 1 | 15 |  | 19970218 | 54 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | STOPPING EQUIPMENT | STEEL |  | 1.25 | 0 |  |  | 0 | 1963 | UNDER GROUND OR UNDER WATER |  | ROBERT DUVALL | 4045844055 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | WHILE REMOVING A SECTION OF PIPE FROM SERVICE, NATURAL GAS BEGAN ESCAPING AND IGNITED. THREE CREW MEMBERS WERE BURNED REQUIRING HOSPITALIZATION. ONE OF THE CREW MEMBERS DIED FROM THESES INJURIES ON 3/4/97.
2025-01-31 10:21 | YES | YES | 19970041 | 1997-03-18 | 19740 | TRUSSVILLE, UTILITIES BOARD, CITY OF | 9406 PARKWAY EAST | BIRMINGHAM |  | AL | 35235 | 3 | NO | 800 | 1997-03-12 | 0 | 1 | 100000 | 70716.971 | 170743.8238 | Null | 1 | 30 |  | 19970312 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER |  | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | BILLY KIRKLAND | 2056553211 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | Null |  |  | LIQUID BUTYL AND PROPYL MERCAPTAN, TRADE NAME, B.P. CAPTAN, SPILLED FROM A ODORANT STORAGE TANK AS THE RESULT OF AN AUTOMOBILE ACCIDENT. 3RD PARTY DAMAGECAUSED BY AUTOMOBILE ACCIDENT. ON MARCH 12, 1997 A NATURAL GAS ODORIZING LIQUID LINE RUPTURED, SPILLING APPROX 50 GALLONS OF A BUTYL AND PROPLY MERCAPTANMIXTURE ONTO THE SOIL AT THE REFERENCE LOCATION. THE LINE RUPTURE RESULTED FROM AN AUTOMOBILE ACCIDENT INVOLVING TWO CARS. THE DRIVER OF A 1996 NISSAN (CAR "A") TURNED IN FRONT OF A 1995 MONTE CARLO (CAR "B"). CAR "B" HIT CAR "A" AND PUSHED IT INTO A CONCRETE BLOCK COLUMN WHICH IN TURN FELL ONTO A LIQUID ODORANT TANK LOCATED AT A NATURAL GAS REGULATING STATION. EMERGENCY RESPONSE TEAMS WERE DISPATCHED FROM TRUSSVILLE UTILTIES' OPERATION DIV AND SUBSEQUENTLYSTOPPED THE ODORANT LEAK. THE VEHICLES WERE REMOVED FROM THE SITE, AND TWO PEOPLE WERE TRANSPORTED TO A LOCAL HOSPITAL. ONE WAS TREATED AND RELEASED, ANDTHE OTHER PERSON WAS ADMITTED. THE TRUSSVILLE UTILITIES RESPONSE TEAMS PROCEEDED TO NEUTRALIZE THE ODORANT LIQUID BY USING THE M.S.D.A. RECOMMENDED NEUTRALIZING AGENT, LIQUID BEACH. A CHEMICAL WASTE COMPANY WAS CONTRACTED TO DISPOSE OF THE CONTAMINATED SOIL. THE SPILL AREA WAS CONTAINED TO AN APPROX 15 FOOT RADIUS. SOIL WAS EXCAVATED TO A DEPTH OF 8 FEET AT THE SIT. NO MAJOR WATERWAY, RIVERS, CREEKS, OR DRAINAGE DITCHES WERE AFFECTED. THE CLEAN UP OF THE CONTAMINATED SOIL WAS COMPLETED BEFORE ANY STORM WATER RUNOFF PROBLEMS COULD OCCUR.
2025-01-31 10:21 | NO | NO | 19970042 | 1997-03-13 | 2748 | CONSUMERS POWER CO | 310 EAST MADISON STREET | DEWITT | CLINTON | MI | 48820 | 3 | NO | 1648 | 1997-02-16 | 0 | 0 | 60000 | 42430.1826 | 102446.2943 | Null | 0 | 42 |  | 19970217 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | ASTM-A53L | U.S. STEEL | 1960 | 1961 | ABOVE GROUND |  | KENNETH ELENBAAS | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GROUND FACILITY | YES |  |  | CUSTOMER HIT METER ASSEMBLY WITH SNOW PLOW BLADE BREAKING ABOVE GROUND PIPING. GAS ENTERED THROUGH BASEMENT WALL.
2025-01-31 10:21 | YES | YES | 19970043 | 1997-03-11 | 18472 | SOUTHEASTERN MICHIGAN GAS CO | 10423 MIDDLE LANE | CASCO | ST. CLAIR | MI | 48064 | 3 | NO | 2000 | 1997-02-14 | 0 | 1 | 80000 | 56573.5768 | 136595.0591 | Null | 1 | 0 |  | 19970215 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | SERVICE LINE |  | JOINT | COMPRESSION | STEEL | POLYETHYLENE PLASTIC | 0.824 | 0.113 |  |  | 0 | 1989 | ABOVE GROUND |  | THOMAS REILLY | 8109877900 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | THIS INCIDENT OCCURRED ON 2/14/97 AT APPROX 8:00PM WHEN A 1/2" PLASTIC SERVICE LINE SERVICING A MOBILE HOME AT 10423 MIDDLE LANE, CASCO TOWNSHIP SEPARATED FROM A 3/4" METAL HEAD ADAPTOR ABOVE GROUND CAUSING GAS LEAKAGE WHICH MIGRATED UNDERNEATH THIS MOBILE HOME CAUSING THE INCIDENT. THE PLASTIC SERVICE LINE SEPARATING FROM THE HEAD ADAPTOR WAS THE RESULT OF FROST HEAVING.
2025-01-31 10:21 | NO | NO | 19970044 | 1997-03-15 | 13710 | NORTHERN ILLINOIS GAS CO | 3149 PATTON DRIVE | DESPLAINES | COOK | IL | 60016 | 3 | NO | 1041 | 1997-02-22 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 0 | 10 |  | 19970222 | 25 | 25 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GEORGE WALDVOGEL | 6309838676 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | INSIDE APPLIANCE OR PIPING MAY HAVE MALFUNCTIONED RESULTING IN AN EXPLOSION IN THE ATTIC/CHIMNEY AREA. CURRENTLY UNDER INVESTIGATION - CUSTOMER'S INSIDE APPLIANCE OR PIPING.
2025-01-31 10:21 | YES | YES | 19970045 | 1997-03-15 | 11032 | LACLEDE GAS CO | 5922 SOUTH BROADWAY | ST. LOUIS | ST. LOUIS | MO | 63111 | 3 | NO | 1655 | 1997-02-24 | 0 | 1 | 25000 | 17679.2427 | 42685.956 | Null | 0 | 5 |  | 19970224 | 7.7 | 14 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | OTHER | NONE SPECIFIED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL HUNKER | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | NATURAL GAS, FROM AN UNDETERMINED SOURCE, WAS APPARENTLY IGNITED WHEN A FLUORESCENT LIGHT WAS BEING CHANGED IN THE BASEMENT OF THE BUILDING. A LEAK WAS FOUND ON A LOCK VALVE ON THE OUTLET SIDE OF THE METER AND NUMEROUS LEAKS WERE FOUND ON THE CUSTOMER'S FUEL RUN INT THE SHOP AREA. THE NATURAL GAS METER, LOCATED IN THE BASEMENT, WAS USED TO MEASURE THESE LEAKS ON THE CUSTOMER'S FUELRUN. THE LEAK RATE WAS DETERMINED TO BE APPROX 6 CUBIC FEET PER HOUR. THREE MINOR LEAKS WERE ALSO FOUND ON THE INLET METER PIPING. SUBSURFACE LEAK INVESTIGATIONS DID NOT FIND NATURAL GAS AT OR NEAR THE OUTSIDE BUILDING WALL OR AT ANY POINT MIGRATING INTO THE BUILDING. THE PROPERTY OWNER DID NOT ALLOW FOR THE INVESTIGATION TO BE COMPLETED AS ACCESS TO THE PROPERTY WAS DENIED AT ABOUT 1200 HRS ON 2/25/97. ACCESS TO THE PROPERTY CONTINUES TO BE DENIED AS OF MARCH 14, 1997.
2025-01-31 10:21 | YES | NO | 19970048 | 1997-03-15 | 12350 | MINNEGASCO INC | 11410 DOGWOOD ST NW | COON RAPIDS | ANOKA | MN | 55433 | 3 | NO | 130 | 1997-02-21 | 0 | 0 | 350000 | 247509.3985 | 597603.3835 | Null | 1 | 0 |  | 19970221 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | REGULATOR | 0 | 0 | S252 | FISHER | 0 | 0 | ABOVE GROUND |  | EUGENE F SCHULTZ | 6123214756 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | REGULATOR MALFUNCTION POSSIBLY CAUSED BY ICE BUILDUP ON RELIEF VENT. POSSIBLEICE BUILDUP ON REGULATOR RELIEF VENT OF METER SET ASSEMBLY.
2025-01-31 10:21 | NO | NO | 19970049 | 1997-03-15 | 20202 | ULTRAMAR REFINING CO | SOUTHERLAND AVENUE | WILMINGTON | LOS ANGELES | CA |  | 1 | NO | 1500 | 1997-02-19 | 0 | 0 | 20000 | 14143.3942 | 34148.7648 | Null | 0 | 0 |  | 19970224 | 0 | 700 | BY TEST | 1100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | NONE SPECIFIED | STEEL |  | 8 | 0.25 | API 5LGRD |  | 1982 | 1982 | UNDER GROUND OR UNDER WATER |  | TED MEADOWS | 5624916699 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-02-19 | YES | 1 |  | YES |  |  | ROADWAY CONSTRUCTION CO A SUBCONTRACTOR FOR HEATEHOG CONSTRUCTION WHO WAS THEPRIMARY CONTRACTOR FOR THE PORT OF L.A. ON THE "ALAMEDA CORRIDOR PROJECT"PUNCTURED ONE 8" CG-101 FUEL GAS PIPELINE. THIS PIPELINE WAS OUT OF SERVICE ATTHE TIME. PRIOR TO THE LINE BEING OUT OF SERVICE OUR PIPELINES WERE CLEARLYMARKED BY ULTRAMAR LINE MARKERS WHICH INCLUDE THE PHONE NUMBER TO CALL IN AMEMERGENCY. THIS INCIDENT ACTUALLY OCCURRED ON 02/19/97 AT APPROX 1:00PM.HOWEVER, ULTRAMAR WAS NOT NOTIFIED UNTIL 02/21/97 AT APPROX. 7:45AM VIA THELEAK WHEEL. A METTING WAS HELD ON 2/25/97 WITH REP OF ALL PARTIES PRESENTINCLUDING THE STATE FIRE MARSHAL (EMIT COOPER) ROADWAY TOOK FULL BLAME FOROPERATOR OF FRONT-END LOADER BEING OUT OF BOUNDARIES WHICH WERE STANDARD.LINES HAVE BEEN EXPOSED, WARNINGS (4) WERE ISSUED AND PREPARATIONS FOR REPAIROF LINE ARE IN THE WORKS. ROADWAY HAVE AGREED TO COVER ALL REPAIR COSTS.
2025-01-31 10:21 | YES | YES | 19970053 | 1997-04-16 | 7215 | HENDERSON GAS DEPT, CITY OF | INTERSECT. OF MONTEZUMA RD. AND HWY 45 | HENDERSON | CHESTER | TN | 38340 | 1 | NO | 1600 | 1997-03-24 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 45 |  | 19970324 | 300 | 500 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | SEE ATTACHMENT #2 | STEEL |  | 10.75 | 0.25 | API 5L X 42 | AMER STEEL | 1996 | 1996 | UNDER GROUND OR UNDER WATER |  | ROY W HAYLEY | 9019893503 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | WARNING TAPE ABOVE PIPE | YES |  |  | THIS PIPELINE WAS INSTALLED BY A PRIVATE CONTRACTOR HIRED BY THE CITY OFHENDERSON IN CONJUNCTIN WITH THE WIDENING OF STATE RT 45 WHICH WAS BEING DONEFOR THE STATE BY AA SEPERATE CONTRACTOR. NATURAL GAS WAS INTRODUCED INTO THEPIPE 10-09-96. AT THAT TIME THE ROAD CONTRACTOR WAS TOLD TAT NATURAL GAS WASBEING MOVED THROUGH THE PIPE AT 300PSIG AND HE NEEDED TO CONTACT THE HENDERSONUTILITY DEPT. WHENEVER HIS CREWS WERE WORKING OVER OR NEAR THE PIPELINE. THEROAD CONTRACTOR WAS REMINDED OF THIDS SEVERAL TIMES. IN THIS PARTICULARINSTANCE NO NOTIFICATION WAS GIVEN THE HENERSON UITLITY DEPT. PRIOR TOEXCAVATION BEING DONE OVER THIS SEGMENT OF THE PIPE. ATTACHMENT #2. WHILESLOPING MONTEZUMA RD. AT STATE RT. 45, AN EQUIPMENT OPERATOR WHO WAS EMPLOYEDBY JONES BROS. CONSTRUCTION CO. STRUCK A 10" STEEL GAS MAIN. THE NATURAL GASESCAPING FROM THE DAMAGED PIPE IGNITED, INJURED TWO EQUIPMENT OPERATORS, ANDDAMAGED THE EQUIPMENT THEY WERE OPERATING.
2025-01-31 10:21 | YES | YES | 19970054 | 1997-04-15 | 22476 | WESTERN KENTUCKY GAS CO | 511 SMITH STREET | DANVILLE | BOYLE | KY | 40422 | 3 | NO | 1925 | 1997-03-04 | 0 | 5 | 0 | 0 | 0 | Null | 0 | 32 |  | 19970304 | 0.25 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | NO SYSTEM | OTHER | N/A | OTHER | PIPING NOT INVOLVED | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DAVID DOGGETTE | 5026858037 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROX. 1925, 3/4/97 CDT WKG RECIEVED NOTIFICATION FROM A 911 DISPATCHERREGARDING A HOUSE FIRE AT THE STATED ADDRESS IN DANVILLE KENTUCKY. THE CAUSEOF THE FIRE WAS UNKNOWN AT THE TIME AND WKG WAS DISPATCHED TH THE SCENE. THECAUSE OF THJIS INCIDENT IS STILL UNDER INVESTIGATION NY THE COMPANY AS WELL ASTHE STATE FIRE AMRSHALL. THE CITY FIRE MARSHALL HAS ISSUED A PRELIMINARYREPORT. FIVE PEOPLE WERE REPORTED TO BE INJURED AND TAKEN TO AREA HOSPITALS.THE HOUSES ON EACH SIDE OF 511 SMITH STREET WERE ALSO REPORTED TO HAVE FIREDAMAGE, ALONG WITH FOUR VEHICLES. WKG SHUT OFF GAS SERVICE TO HOUSES AT 509AND 511 SMITH STREET.
2025-01-31 10:21 | NO | NO | 19970055 | 1997-04-18 | 12350 | MINNEGASCO INC | 1032 128 AVENUE NE | BLAINE | ANOKA | MN | 55434 | 3 | NO | 1356 | 1997-03-16 | 0 | 0 | 60000 | 42430.1826 | 102446.2943 | Null | 1 | 40 |  | 19970316 | 50 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.161 |  |  | 0 | 1973 | UNDER GROUND OR UNDER WATER |  | EUGENE SCHULTZ | 6123214756 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | YES |  |  | THIS DAMAGE OCCURED IN 1973, WHEN A PLUMBING CONTRACTOR INSTALLED A WATERSERVICE. CORRESPONDENCE RECEIVED 5/27/1997 THAT REVISED THAT DAMAGE OCCURREDIN 1975, NOT 1973.
2025-01-31 10:21 | YES | NO | 19970057 | 1997-04-28 | 4483 | ENSTAR NATURAL GAS CO | LOT 10, BLK 5, SHERWOOD ESTATES #1 | WASILLA | MATANUSKA SUSITNA | AK | 99654 | 2 | NO | 245 | 1997-04-18 | 0 | 0 | 95000 | 67181.1224 | 162206.6327 | Null | 1 | 15 |  | 19970418 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1995 | 1995 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON FRIDAY APRIL 18, 1997 AT APPROX. 2:45 AM AST ENSTAR NATURAL GAS CO.PERSONNEL RESPONDED TO A HOUSE FIRE AT LOT 10 BLOCK 5 SHERWOOD ESTATES NO. 1IN THE MATANUSKA-SUSITNA BOROUGH. THIS LOCATION IS APPROX. 5 MILES NORTHWESTOF THE CITY OF WASILLA, ALASKA. ACCORDING TO TOM HOOD MATANUSKA-SUSITNABOROUGH FIRE CHIEF THE ORIGIN OF THE FIRE IS UNKNOWN BUT NATURAL GAS IS NOTBELIEVED TO HAVE CONTRIBUTED TO THE CAUSE OF THE FIRE. THE INTENSE HEAT FROMTHE FIRE CAUSED 5/87 HDPE SERVICE LINE TO MELT INSIDE THE STEEL RISER CAUSINGA RELEASE OF NATURAL GAS. THE PLASTIC SERVICE LINE WAS PINCHED OFF AND CAPPEDBY BOB LINK, ENSATR SERVICEMAN. ESTIMATED DAMAGE TO THE STRUCTURE WAS APPROX.95,000.
2025-01-31 10:21 | YES | YES | 19970060 | 1997-05-06 | 22567 | WHITE HALL GAS DEPT, CITY OF | 228 BRUCE DRIVE | WHITE HALL |  | IL | 62092 | 3 | NO | 1540 | 1997-03-18 | 0 | 1 | 200000 | 141433.942 | 341487.6477 | Null | 1 | 0 |  | 19970318 | 0.25 | 18 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE PIPING | FITTING |  | OTHER | COPPER TUBING | 0.625 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAY HOWARD | 2173746611 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE FAILURE OF A COPPER FLARE FITTING ON THE TUBING SERVING THE FURNACE CAUSEDBUILD-UP OF GAS IN THE BASEMENT AREA AND ULTIMATE IGNITION.
2025-01-31 10:21 | NO | NO | 19970068 | 1997-05-15 | 6914 | GULF STATES PIPELINE CORP | BONITA HWY 80 | RUSTON | LINCOLN PARISH | LA | 71270 | 3 | NO | 700 | 1997-04-07 | 0 | 0 | 15000 | 10607.5456 | 25611.5736 | Null | 5 | 0 |  | 19970407 | 80 | 717 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | CONTAINMENT WALL | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | GARY SMITH | 3187470878 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 1000 GAL TANK OVERFLOWED THE CONTAINMENT WALL ALLOWING THE Y-GRADE CONDESATETOP FLOW ONTO THE GROUND , THEN OUTSIDE THE CONTAINMENT FENCE OF THE FACILITY.
2025-01-31 10:21 | NO | NO | 19970069 | 1997-05-16 | 31005 | FLORIDA WATER SERVICES | 1805 ULMER LANE | SUNNY HILLS | WASHINGTON | FL | 32428 | 2 | NO | 259 | 1997-04-26 | 0 | 0 | 10000 | 7071.6971 | 17074.3824 | Null | 0 | 20 |  | 19970427 | 9 | 22 | BY TEST | 22 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.5 | 0 | EX-TRUBE TUBING | EX-TRUBE | 1970 | 1971 | ABOVE GROUND |  | HAROLD REGISTER | 9047732802 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | LIGHTNING HIT 1/2" GAS SERVICE IGNITED GAS, BLOWING HOLE IN EX-TRUBING BELOWSERVICE VALVE.
2025-01-31 10:21 | NO | NO | 19970070 | 1997-05-19 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | 2409 KRISTIN AVE. | GILLETTE | CAMPBELL | WY | 82718 | 3 | NO | 1705 | 1997-04-13 | 0 | 0 | 54000 | 38187.1643 | 92201.6649 | Null | 0 | 0 |  | 19970413 | 38 | 38 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | JOINT |  | STEEL |  | 0.75 | 0 | ANODELESS RISER | UNK | 1994 | 1995 | ABOVE GROUND |  | SCOTT EVANS | 3037633457 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | SNOW | NO |  | NO | 0 |  | NO |  |  | THE INCIDENT OCCURED WHEN AN ANODELESS RISER BROKE UPSTREAM OF A METER LOOPSERVING A TRAILER HOUSE. GAS ESCAPED AND WAS IGNITED BY THE TRAILER'S FURNACEOR WATER HEATER AND THE TRAILER WAS DESTROYED. THE APPARENT CAUSE OF THE BREAKWAS A SIGNIFICANT AMOUNT OF HEAVY WET SNOW THAT HAD ACCUMULATED ON TOP OF THEMETER LOOP. THERE WAS NO INDICATION OF DAMAGE CAUSED BY OTHER EXTERNAL FORCESON THE RISER OR METER LOOP. TRAILER HOUSE OWNER RETURNED FROM ERRAND ANDSMELLED GAS OUTSIDE AND INSIDE. WENT OUTSIDE AND COULD HEAR GAS ESCAPING FROMMETER LOOP COVERED BY SNOW DRIFT. THE TRAILER STARTED ON FIRE AND WASDESTROYED. METER LOOP WAS BROKEN OFF ON THREADS BELOW IB. FIRE DEPARTMENTSAID THE STUB WAS CRACKED WHEN THEY ARRIVED. CRACK INDICATED LOOP WAS PUSHEDTOWARD TRAILER.
2025-01-31 10:21 | NO | NO | 19970071 | 1997-05-23 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 1429 FRANKLIN S.E. | GRAND RAPIDS | KENT | MI | 48661 | 1 | NO | 1235 | 1997-04-30 | 0 | 0 | 41752 | 29525.7497 | 71288.9613 | Null | 0 | 10 |  | 19970501 | 150 | 150 | BY TEST | 225 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 24 | 0.25 | API5LX |  | 0 | 1957 | UNDER PAVEMENT |  | ROGER GREGORY | 3135777045 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-04-16 | NO | 2 |  | YES |  |  | ON MAY 1 1997, UPON KNOWLEDGE THAT THE REAPIR COMPLTETED ON APRIL 30 1997 AT10:30 BY MEANS OF A 24" PIPE, TELEPHONIC WAS GIVEN TO THE DOT THAT DAMAGE/LOSSCOULD EXCEED 50,000.00. THE EVALUATION LATER CONCLUDED THE 24" REPAIR CLAMP TOBE PERMANENT REPAIR; RESULTING IN DAMAGE/LOSS LESS THAN THE REPORTED 50,000.THE REVISED TOTAL IS 41,752.00. YOU MAYRETAIN THIS REPORT NO. 385659 AS YUOSEE FIT WITH KNOWLEDGE THAT THE ORIGINAL MAY 1, 1997 NOTICE WAS BASED ONOPERATOR JUDGEMENT.
2025-01-31 10:21 | YES | YES | 19970072 | 1997-06-02 | 1688 | BRADY MUNICIPAL GAS CORP, CITY OF | 1310 S. BRIDGE ST., APT#6 | BRADY | MCCULLOCH | TX | 76825 | 0 | NO | 957 | 1997-01-30 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19970130 | 7 | 8.7 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DANIEL GALINDO | 9155972244 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19970073 | 1997-05-28 | 18416 | SOUTH COAST GAS CO INC | 309 CANAL STREET | LOCKPORT | LAFOURCHE | LA | 70374 | 3 | NO | 500 | 1996-09-26 | 0 | 0 | 60000 | 43183.93 | 104266.1929 | Null | 0 | 30 |  | 19960926 | 60 | 80 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 7.5 | 1.13 |  |  | 0 | 0 | ABOVE GROUND |  | JACQUES ROTOLO | 5045375281 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | A VEHICLE TRAVELING ON CANAL STREET LOST CONTROL AND STRUCK THE METER SETASSEMBLY AND HOUSE AT 309 CANAL ST. THE METER SET WAS BROKEN FROM THE SERVICELINE AND AN INGNITION OF THE NATURAL GAS OCCURED. THE VEHICLE AND THE HOUSESUFFERED FIRE DAMAGE.
2025-01-31 10:21 | NO | NO | 19970074 | 1997-06-03 | 968 | UNIVERSAL NATURAL GAS, INC. | 15213 SADDLEWOOD DR | CONROE | MONTGOMERY | TX | 77384 | 1 | NO | 830 | 1997-05-20 | 0 | 0 | 600 | 424.3018 | 1024.4629 | Null | 0 | 35 |  | 19970523 | 38 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | SDR-10 | NAPCO | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | ROBERT S BARNWELL | 2813634100 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | SPRINKLER SYSTEM INSTALLER TRENCHED INTO 3/4" POLY SERVICE LINE. TRENCHERCAUGHT FIRE. FIRE DEPT. PUT OUT FIRE. NO OTHER DAMAGE OR INJURY.
2025-01-31 10:21 | YES | NO | 19970075 | 1997-05-27 | 30769 | MISSOURI GAS ENERGY | 393 MATTESON | REPUBLIC | GREENE | MO | 64578 | 3 | NO | 1136 | 1997-04-30 | 0 | 0 | 120000 | 84860.3652 | 204892.5886 | Null | 1 | 30 |  | 19970430 | 35 | 39 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | 2406 PIEXCO | RW LYALL CO. | 0 | 1997 | ABOVE GROUND |  | WIILIAM DEAN | 8163605661 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY | LIGHTNING/FIRE | NO |  | NO | 0 |  | NO |  |  | MISSOURI GAS ENERGY'S SERVICEMAN WAS WORKING IN REPUBLIC MISSOURI THE MORNINGOF APRIL 30, 1997 WHEN HE NOTICED SMOKE IN THE SOUTHEAST SIDE OF THECOMMUNITY. HE PROCEEDED TO THE AREA TO INVESTIGATE AND FOUND A NEW HOME, UNDERCONSTRUCTION, ON FIRE AT 1155 HOURS. MEMBERS OF THE CITY OF REPUBLIC FIREDEPT. WERE PRESENT. THE HOUSE WAS TOTALLY INVOLVED IN THE FIRE, AND THEINTENSE HEAT KEPT THEM AT BAY. ORANGE FLAMES FROM A GAS FIRE WERE OBSERVEDCOMING FROM THE GROUND AT THE METER LOOP LOCATION ON THE NORTHEAST CORNER OFTHE HOME, THE GAS METER HAD NOT YET BEEN INSTALLED. THE GAS FIRE WAS SECONDARYTO ONE INITIAL HOUSE FIRE. REFER TO EXHIBITS C AND D. THE SERVICEMAN COULD NOTGET NEAR THE METER LOOP AT THE STRUCTURE. HE CALLED FOR ADDITIONAL MGEPERSONNEL AND ASSISTED THE FIRE DEPT. IN AN EFFORT TO SECURE THE AREA. MGE'SSUPERVISOR ARRIVED AT THE SITE AT 1235 HOURS, THE STRUCTURE HAD BURNED TO THEFOUNDATION BY THIS TIME. A 1/2" IPS PE SERVICE LINE HAD BEEN INSTALLED TOTHIS NEW HOME IN MARCH, 1997. AN R.W. LYALL ANODELESS FLEXIBLE RISER ANDMETER LOOP HAD BEEN INSTALLED AT THE NORTHEAST CORNER OF THE STRUCTURE. THECONTRACTOR BUILDING THE HOME HAD NOT YET REQUESTED A METER TO BE INSTALLED.GAS WAS OFF AT THE STOP AND THE METER LOOP PLUGGED. THE SERVICE LINE WASSERVED FROM A 2" PE MAIN LOCATED IN THE MAIN PARKWAY 18' WEST OF THE CENTERLINE OF MATTESON, OPERATING AT 35 PSIG. THE COMPANY'S CONSTRUCTION ANDMAINTENANCE CREW ARRIVED AT 1380 HOURS AND PROCEEDED TO EXCAVATE THE SERVICETAP. THE SERVICE WAS CUT AND CAPPED AT THE MAIN CONNECTION AT 1324 HOURS. ASTHE SERVICE WAS SHUT OFF, THE GAS FIRE WAS EXTINGUISHED AND THE FIREDEPARTMENT PROCEEDED TO COOL DOWN THE AREA AS WELL AS HOT SPOTS WITHIN THESTRUCTURE. FURTHER INVESTIGATION INDICATED THAT THE PE PIPE MATERIAL INSIDETHE ANODELESS RISER WAS MELTED BY THE HEAT FROM THE HOUSE FIRE. THE FLEXIBLEPORTION OF THE RISER WAS MELTED AND BROKEN WHERE IT ATTACHED TO THE STEELUPRIGHT LEG OF THE GAS RISER. THE GAS WAS LEAKING FROM THE RISER BELOW GRADELINE. BOB CURTIS, DEPUTY FIRE CHIEF, STATED THAT AN EMPLOYEE OF ARGO PLUMBINGWAS SOLDERING PLUMBING FITTINGS WHEN NEARBY CARDBOARD TRASH AND OTHERFLAMMABLE MATERIAL WERE IGNITED IN THE WORK AREA. THE HOME WAS UNDERCONSTRUCTION BY JEFF CASSIDY CONSTRUCTION COMPANY WITH AN ESTIMATED VALUE OF$120,000.
2025-01-31 10:21 | YES | YES | 19970076 | 1997-06-03 | 2364 | CINCINNATI GAS & ELECTRIC CO | 12064 SPRINGFIELD ROAD | CINCINNATI | HAMILTON | OH | 45246 | 4 | NO | 445 | 1997-04-27 | 1 | 0 | 17000 | 12021.8851 | 29026.4501 | Null | 1 | 10 |  | 19970427 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | WILLIAM HOBITZELL | 5132873921 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | VEHICLE BURNED ALONG WITH ITS OCCUPANT. THIS WAS RULED A SUICIDE BY THEHAMILTON COUNTY CORONER. THE METER ASSSEMBLY WAS ADAQUATELY PROTECTED WITH 2"AND CHAIN LINK FENCING. THE INDIVIDUAL WAS OPERATING A MOTOR VEHICLE WITHEXCESSIVE SPEED IN A PARKING AREA. THE VEHICLE WENT OVER THE SIDEWALK AREASTRIKING THE METER AND REGULATOR ASSEMBLY. THIS CAUSED THE M&R TO LEAK, THENATURAL GAS IGNITED.
2025-01-31 10:21 | YES | YES | 19970084 | 1997-06-25 | 14210 | OKLAHOMA NATURAL GAS CO | 12500 ST. ANDREWS, SUITE 2 | OKLAHOMA CITY | OKLAHOMA | OK | 73120 | 3 | NO | 1544 | 1997-06-05 | 0 | 1 | 62000 | 43844.522 | 105861.1708 | Null |  | 23 | 389543 | 19970605 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 |  | 2406/SDR11 | PLEXCO | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | R.L. GAMBRELL | 9185887404 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-05-14 | YES |  | FLAGGED AND PAINTED | Null |  |  | LINE WAS CUT BY TRENCHING MACHINE OPERATOR EXCAVATING BEYOND THE BOUNDRIESOF HIS LINE LOCATE REQUEST.
2025-01-31 10:21 | YES | YES | 19970085 | 1997-06-12 | 15931 | PUBLIC SERVICE CO OF COLORADO | 111 S. KNOX CT | DENVER | DENVER | CO | 80219 | 3 | NO | 1655 | 1997-06-03 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 43 | 389804 | 19970603 | 4.9 | 15 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA | NOT ON SYSTEM | NO DATA |  | NO DATA | [7 empty] | WITHIN/UNDER BUILDING |  | TOMY WILSON | 3035713858 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A SINGLE WOOD FRAME RESIDENCE WAS DESTROYED. THE LONE ELDERLY FEMALEEXPLOSION OCCURRED INSIDE OF STRUCTURE. NO APPARENT OUTSIDE OF STRUCTURESOURCE OF NATURAL GAS. A SINGLE WOOD FRAME RESIDENCE WAS DESTROYED. THELONE ELDERLY FEMALE OCCUPANT WAS TRANSPORTED TO DENVER HEALTH MEDICALCENTER. THE SOURCE COMBUSTIBLE HAS NOT BEEN DETERMINED.
2025-01-31 10:21 | YES | YES | 19970086 | 1997-06-12 | 15469 | PHILADELPHIA GAS WORKS | 3461 RORER STREET | PHILADELPHIA | PHILADELPHIA | PA | 19134 | 4 | Null | 1758 | 1997-05-26 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 18 | 388869 | 19970526 | 0.25 | 0.5 |  | 192.62 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER |  | OTHER | BLACK IRON | 0.5 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRIAN SCHENK | 2156846372 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19970087 | 1997-06-30 | 15007 | PACIFIC GAS & ELECTRIC CO | UNION & LARKIN STREETS | SAN FRANCISCO | SAN FRANSICO | CA | 94110 | 3 | NO | 1140 | 1997-05-15 | 1 | 2 | 173000 | 122340.3598 | 295386.8153 | Null | 3 | 50 | 387385 | 19970515 | 10 | 10 | BY TEST | 10 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 |  | UNKNOWN | UNKNOWN |  |  | UNDER PAVEMENT |  | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-04-15 | YES | 3 | NO ENTRY | YES
2025-01-31 10:21 | YES | NO | 19970097 | 1997-08-06 | 2748 | CONSUMERS POWER CO | 10000 NORTH GENESEE RD | CLIO | GENESEE | MI | 48420 | 1 | NO | 1705 | 1997-07-02 | 0 | 0 | 80000 | 56573.5768 | 136595.0591 | Null | 2 | 10 |  | 19970703 | 0 | 400 | BY TEST | 600 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | ODORIZER | OTHER | BUILDING & PIPING DAMAGED | OTHER | BUILDING | 0 | 0 |  |  | 0 | 1969 | ABOVE GROUND |  | GEARLD MARSHALL | 5177881532 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WINDS FROM TORNADO MOVED ODERIZER BUILDING FROM FOUNDATION CAUSING DAMAGE TOBUILDING AND INTERNAL PIPING. ODERIZER WAS NOT IN OPERATION AT TIME OFINCIDENT. HIGH WINDS FROM TORNADO DAMAGED ODORIZER BUILDING AND PIPING.
2025-01-31 10:21 | YES | YES | 19970098 | 1997-07-14 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) | 873 PETERSBURG | MUNJOR | ELLIS | KS | 67601 | 3 | NO | 1450 | 1997-06-10 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19970610 | 8.5 | 10 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | NO FAILURE | STEEL |  | 1 | 0.133 | CW | UNKNOWN | 0 | 1968 | OTHER | BELL-HOLE | STEVE HAWES | 3037633457 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPLOYEES MOVING METER FROM PROPERTY LINE TO HOUSE, INCLUDING INSTALLATION OFNEW YARD LINE. THE DESIGN OF THE EXISTING FACILITIES REQUIRED THE USE OF ANEXPANDABLE PLUG IN THE SERVICE STUB TO STOP THE FLOW OF GAS. AFTER WELDING AMUELLER "NO BLOW" FITTING TO THE SERVICE STUB TO RECONNECT NEW YARD LINE, THEEMPLOYEES REMOVED THE EXPANDABLE PLUG AND GAS ESCAPED FROM THE OPEN STUB ANDIGNITED. THE SOURCE OF IGNITION WAS NOT APPARENT, BUT WE BELIEVE THAT IT MAYHAVE BEEN UN NOTICED MOLTEN METAL OR MELTED COATING IN THE BELL-HOLE. ONEEMPLOYEE RECIEVED 1ST AND 2ND DEGREE BURNS AND WAS HOSPITALIZED.
2025-01-31 10:21 | YES | YES | 19970099 | 1997-07-10 | 11683 | LONE STAR GAS CO OF TEXAS, INC | 4717 MCKINNEY | DALLAS | DALLAS | TX |  | 3 | NO | 600 | 1997-06-04 | 1 | 0 | 150000 | 106075.4565 | 256115.7358 | YES | 5 | 0 |  | 19970604 | 31 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE | NO FAILURE | STEEL |  | 10 | 0 |  |  | 0 | 1948 | WITHIN/UNDER BUILDING |  | ELLEN WEAVER | 2146702988 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | CORROSION CAUSED A LEAK IN THE PIPELINE AND THE GAS LEAKED INTO THE BUILDING.
2025-01-31 10:21 | NO | NO | 19970100 | 1997-07-09 | 2392 | CITIZENS GAS & COKE UTILITY | 3717 EATS 77TH STREET | INDIANAPOLIS | MARION | IN | 46240 | 1 | NO | 1742 | 1997-06-20 | 0 | 0 | 500 | 353.5849 | 853.7191 | Null | 1 | 18 |  | 19970620 | 25 | 40 | BY CFR 192.619(A)(3) | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | INSULATED UNION STOP | OTHER | MALLEABLE & PLASTIC | 0.75 | 0 | 6317B |  | 0 | 1984 | ABOVE GROUND |  | RANDY PELL | 3179274640 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | NO | 19970101 | 1997-07-21 | 18536 | SOUTHWEST GAS CORP | 534 E HUNTINGTON, #17 | TEMPE | MARICOPA | AZ | 85282 | 3 | NO | 1227 | 1997-06-21 | 0 | 0 | 71000 | 50209.0494 | 121228.1149 | Null | 2 | 22 |  | 19970622 | 30 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER | ABS | 1.25 | 0.098 | ABS1210 | KERONA | 1970 | 1970 | UNDER PAVEMENT |  | PHILLIPS ANDREW | 6024845218 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOTS | Null |  | Null | 0 |  | Null |  |  | TREE ROOTS ENCAPSULATED AN 1 1/4 ABS SERVICE, CAUSING A LEAK TO DEVELOP.IGNITION OCCURED FROM AN UNDETERMINED SOURCE, CAUSING DAMAGE TO APARTMENT #17AT 534 E. HUNTINGTON. SUSEQUENT LABORATORY ANALYSIS CONFIRMED PIPE FAILURE DUETO EXTERNAL STRESS CAUSED BY TREE ROOTS.
2025-01-31 10:21 | NO | NO | 19970102 | 1997-07-18 | 30750 | MIDAMERICAN ENERGY CO | 603 3RD STREET N.W. | WAVERLY | BREMER | IA | 50677 | 3 | NO | 1240 | 1997-06-10 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 13 | 35 |  | 19970610 | 14 | 14 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MONTE JAACKS | 3192914635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-06-04 | YES | 3 | PAINT | YES |  |  | CONTRACTOR WAS DIGGING IN STREET WITH BACKHOE. BACKHOE BUCKET HOOKED ANDPULLED 3/4" SERVICE RESULTING IN DAMAGE TO METER SET IN BASEMENT OF RESIDENCE.THE DAMAGE CAUSED A LEAK IN THE BASEMENT WHICH RESULTED IN THE EXPLOSION.
2025-01-31 10:21 | NO | NO | 19970103 | 1997-07-14 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 2010 E. JEFFERSON (MOBIL GAS STATION) | DETROIT | WAYNE | MI | 48226 | 4 | NO |  | 1997-06-14 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 0 | 0 |  | 19970614 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | NATURAL GAS DIPENSER | OTHER | STAINLESS STEEL TUBE | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER |  | CAROL MATHEWS | 3135777025 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | ON JUNE 14, 1997 A CAR RAN INTO A NATURAL GAS DISPENSER AT A MOBILE GASSTATION. REPAIRS INCLUDED REPLACEMENT IF STAINLESS STELL TUBE FROM COMPRESSORTO DISPENSER REPAIR OF AIR PURGE LINE AND ELECTRICALCONDUIT. THERE WAS NORELEASE OF GAS, AUTOMATIC SHUT OFF. NO VEHICLES WERE BEING FUELED AT THETIME. CAR RAN INTO NATURAL GAS DISPENSER AND KNOCKED DISPENSER OVER.
2025-01-31 10:21 | NO | NO | 19970104 | 1997-07-22 | 4483 | ENSTAR NATURAL GAS CO | BUISNESS BLVED & REGENCY | EAGLE RIVER |  | AK | 99577 | 3 | NO | 1330 | 1997-07-15 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 1 | 15 |  | 19970715 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | DRISCOPE 8000 | PHILLIPS DRISCOPE | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | DAVID BREDIN | 9072643745 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-06-27 | YES | 0 |  | YES |  |  | ON TUESDAY JULY 15 , 1997 AT APPROX. 1:15 PM , ENSTAR GAS CONTROL WAS NOTIFIEDBY MATANUSKA TELEPHONE ASSOC. THAT ONE OF THEIR CREWS HASD DAMAGED A GAS MAINAND IT WAS ON FIRE AT THE INTERSECTION OF REGENCY DRIVE AND BUISNESS BLVD. INEAGLE RIVER ALASKA. UPON ARRIVAL , ENSTAR'S CREW FOUND NATURAL GAS FROM ABROKEN 2" HIGH DENSITY POLETHYLENE GAWS MAIN BLOWING ON FIRE. A JOHN DEERE 310BACKHOE WAS FUULY ENGULFED BY THE FIRE. NO ONE WAS INJURED. ENSTAR CREWSPROCEEDED TO DIG UP AND SQUEEZE OFF THREE GAS MAINS, EACH APPROX. 200' FROMTHE FIRE, TO STYOP THE BLOWING GAS AND EXTINGUISH THE FIRE. THE LAST OF THETHREE SQUEEZE OFFS WAS COMPLETRED AT 2:30 PM AND THE FIRE WAS EXTINGUISHED.MTA HAD REQUESTED LOCATES THRIOOUGH THE LOCATE CALL CENTER OF ALASKA ON JUNE27, 1997. ENSTAR LOCATED ITS FACILITIES ON JULY 7 1997 AS REQUESTED BY MTA.MTA HAD HAND EXPOSED ENSTAR'S 2" MAIN AND IT WAS VISIBLE AT THE TIME OF THEDAMAGE. THE GAS MAIN WAS DAMAGED WHEN MTA INADVERTENTLY DAMAGED AN ELECTRICCABLE IN THE SAME EXCAVATION. THE ELECTRIC CABLE "ARCED" AND MELTED A HOLE INTHE 2" HDPE GAS MAIN. NATURAL GAS WAS RELEASED AND IT WAS IGNITED BY THEARCING ELECTRIC LINE. DAMAGE TO THE AFFECTED UTILITIES AND BACKHOE WASESTIMATED TO BE INEXCESS OF 50,000.
2025-01-31 10:21 | YES | YES | 19970106 | 1997-08-14 | 603 | ARKLA, A NORAM ENERGY COMPANY | 6700 JEFFERSON-PAIGE RD, LOT 26 | SHREVEPORT | CADDO PARISH | LA | 71103 | 3 | NO | 1426 | 1997-07-12 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 10 |  | 19970712 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | TEXTUBE | 1981 | 1981 | UNDER GROUND OR UNDER WATER |  | HOYLE ROGERS | 3184294236 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | THE CONTRACTOR FOR THE MOBILE HOME PARK WAS CLEARING A DITCH WITH A BACKHOEAND CUT A 2" PLASTIC MAIN. THE GAS IGNITED AND THE OPERATOR WAS BURNED.CONTRACTOR CLEANING DITCH WITH BACKHOE AND CUT A 2" PLASTIC LINE.
2025-01-31 10:21 | NO | NO | 19970107 | 1997-08-14 | 603 | ARKLA, A NORAM ENERGY COMPANY | 120 SLOSS AVE | OMAHA | MORRIS | TX | 75571 | 2 | NO | 200 | 1997-07-08 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | YES | 2 | 0 |  | 19970708 | 15 | 0 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 1 | 0.133 | R-19 METER | ROCKWELL | 1988 | 1997 | ABOVE GROUND |  | KYLE HOLOCMB | 9038241304 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | FIRE INVESTIGATORS SAID GAS WAS NOT INVOLVED.HOUSE FIRE HEATED METER ANDREGULATOR TO THE POINT OF MELTING.
2025-01-31 10:21 | YES | NO | 19970110 | 1997-08-21 | 15259 | PENNSYLVANIA GAS & WATER CO | 125 COTTAGE STREET | CARBONDALE | LACKWANNA | PA | 18407 | 3 | NO | 1451 | 1997-08-07 | 0 | 0 | 80000 | 56573.5768 | 136595.0591 | Null | 0 | 24 |  | 19970807 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JAMES GREGER | 7178298866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | A CAR ROLLED DOWN A HILL CRASHED THROUGH A WOODEN FENCE AND KNOCKED OFF A GASREGULATOR AT SAID ADRESS. THE STRUCTURE WAS HEAVILY DAMAGED. IT IS UNKNOWN ATHTIS TIME HOW THE CAR ROLLED DOWN THE HILL.
2025-01-31 10:21 | YES | NO | 19970111 | 1997-08-26 | 2568 | COLORADO SPRINGS, CITY OF | 202 W. ROCKRIMMON BLVD. UNIT H | COLORADO SPRINGS | EL PASO | CO | 80919 | 3 | NO | 1533 | 1997-07-26 | 0 | 0 | 180000 | 127290.5478 | 307338.8829 | Null | 0 | 5 |  | 19970727 | 26 | 34 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMIINUM | 1 | 0 | MODEL 1213B | AMERICAN | 0 | 1974 | ABOVE GROUND |  | WAYNE BOOKER | 7196683505 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | TOWNHOUSE OWNER WAS OPERATING A CHARCOAL SMOKER IN PATIO/CARPORT AREA ANDPUSHED SMOKER AGAINST A CEDAR PRIVACY FENCE, WHICH IGNITED. FLAMES FROM THEBURNING FENCE IMPINGED ON THE GAS SERVICE REGULATOR WHICH FAILED AND ESCAPINGGAS ACCELERATED THE FIRE, WHICH SPREAD TO A CARPORT AND THEN TO THE ROOF OFTHE DWELLING. CLOSING THE SERVICE LINE VALVE CONTROLLED THE FLOW OF GAS.
2025-01-31 10:21 | YES | NO | 19970112 | 1997-08-26 | 2669 | COMMONWEALTH GAS PIPELINE CORP | 5601/5603 RIVERMILL CIRCLE | PORTSMOUTH | NORFOLK | VA | 23703 | 1 | NO | 2117 | 1997-08-03 | 0 | 0 | 200000 | 141433.942 | 341487.6477 | Null | 2 | 58 |  | 19970805 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | NO DATA |  | OTHER | ALUMINUM METER | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DAVID CICORIA | 8043235482 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | VEHICLE | Null |  | Null | 0 |  | Null |  |  | ON AUGUST 3, 1997, AT APPROX. 9:17 PM A TEENAGE BOY LOST CONTROL OF A STOLENCAR. THE CAR JUMPED THE CURB TRAVELED THROUGH A FIVE FOOT WOODEN FENCE ANDCRASHED INTO OUR METER SETTING WHICH RESULTED IN THE RELEASE AND IGNITION OFNATURAL GAS. THE FIRE DESTROYED TWO MODEL HOMES WITH AN ESTIMATED DAMAGE OF200,00. THERE WERE NO INJURIES IN THE ACCIDENT OR FIRE. THE CONDITIONS AT THESCENE ESPECIALLY THE FIRE FIGHTING SITUATION MADE IT DIFFICULT FOR COMPANYPERSONNEL TO SHUT OFF SERVICE. SINCE SHUTTING OFF SERVICE TO THE EFFECTEDBUILDINGS COULD NOT BE EASILY ACCOMPLISHED, THE MAIN FEED ON RIVERSHORE RD.WAS SHUT OFF WHICH INTERRUPTED SERVICE TO 119 CUSTOMERS. SERVICE WAS RESTOREDTO MOST CUSTOMERS BY THE NEXT DAY.
2025-01-31 10:21 | YES | YES | 19970113 | 1997-08-27 | 1209 | BAY STATE GAS CO | CLAPP RD | SCITUATE | PLYMOUTH | MA | 02066 | 3 | NO | 1402 | 1997-08-15 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19970815 | 51 | 99 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | TAPPING MACHINE | STEEL |  | 2 | 0 |  |  | 0 | 1929 | UNDER GROUND OR UNDER WATER |  | MICHAEL LAGHETTO | 5085800100 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A BAY STATE GAS COMPANY EMPLOYEE WAS BURNED WHEN GAS IGNITED DURING A MAINABNDONMENT PROCEDURE. SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | YES | YES | 19970114 | 1997-08-29 | 30769 | MISSOURI GAS ENERGY | I70 AND LEE SUMMIT ROAD | INDEPENDENCE | JACKSON | MO | 64055 | 3 | NO | 1150 | 1997-07-25 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 25 |  | 19970725 | 124 | 155 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | ONKNOWN | STEEL |  | 8 | 0 |  |  | 0 | 1936 | UNDER GROUND OR UNDER WATER |  | WILLIAM DEAN | 8163605661 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JULY 25 1997 AN IGNITION OCCURED IN A SIUTHWESTERN BELL(SWB) MANHOLE ON THEWEST SIDE OF LEE SUMMIT RD. SOUTH OF INTERSTATE 70 IN IDEPENDENCE MISSOURI.THE INCIDENT WAS REPORTED BY THE INDEPENDENCE FIRE DEPT. DISPATCHER TO THEMISSOURI GAS ENERGY DISPATCHER AT 1150 HRS. AS AN IGNITION IN A SEWER. MGEDIPATHCHED SERVICEMAN MC DOWELL AT 1152 AND ARRIVED AT THE SCENE AT 1156. UPONARRIVAL HE OBSERVED THE AREA WHERE THE FLASH FIRE HAD OCCURED. THE FIRE DEPT.CREW THAT WAS STILL AT THE SCENE INFORMED HIM THAT TWO CONTRACT EMPLOYEES WHOWORKED FOR SWB HAD BEEN TRANSPORTED TO LOCAL HOSPITALS. NO FRESH AIR BREATHINGEQUIPMENT OR AIR HANDLING DEVICES WERE OBSERVED AT THE SCENE WHERE THEEMPLOYEES WERE INJURED. THE MANHOLE WHERE THE INJURIES OCCURED IS ABOUT 122'SOUTH OF THE SOUTH RIGHT OF WAY I-70 AND 26' EAST OF THE WEST PROPERTY LINE OFLEE SUMMIT RD. THE SWB CONDUIT SYSTEM RUNS IN A NORTH-SOUTH OF THE WEST SIDEOF LEE SUMMIT RD. IT CONSISTS OF MULTIPLE CONDUITS FOR CABLES THAT ARE APPROX.12' BELOW GROUND SURFACE CONNECTED BY A SERIES OF MANHOLE ACCESS POINTS. THESEACCESS POINTS OPEN INTO A HORIZONTAL VAULT AREA AT THE BOTTOM OF THE MANHOLEWHERE WORK ACTIVITIES ARE PERFORMED. THE COMPANY FACILITIES IN THE AREACONSIST OF A 2" PLASTIC MAIN ALONG THE WEST SIDE OF LEEE SUMMIT RD. APPROX.29' WEST OF THE SWB CONDUIT. THIS DISTRIBUTION MAIN OPERATES AT 5 PSIG AND WASINSTALLED IN 1994. AN 8" BARE STEEL FEEDER LINE INSTALLED IN 1936 BY PANHANDLEEASTERN RUNS IN A NORTH- SOUTH DIRECTION ALONG THE EASDT SIDE OF THE ROADPAVEMENT. THE COMPANY PURCHASED THIS PIPELINE IN NOV. OF 1960. IT HAS AN MAOPOF 155 PSIG AND WAS OPERATING AT 124 PSIG AT THE TIME OF THE INCIDENT. IT HASBEEN CATHODICALLY PROTECTED BY IMPRESSED CURRENT RECTIFIER #325 SINCE 1977. ONTHE DAY OF THE INCIDENT, THE PIPELINE READ A PIPE TO SOIL POTENTIAL OF -0.88V.A 16" COATED STEEL FEEDER LINE IS ALSO LOCATED ON THE EAST SIDE OF LEE SUMMITRD. IT IS 35' EAST OF THE 8' LINE AND FOR THE N=MOST PART RUNS PARALLEL WITHTHE 8" LINE. THE 16" LINE WAS INSTALLED IN 1963 AND IS ALSO UNDER CATHODICPROTECTIN FROM RECTIFIER #325. THE 16" PIPELINE OPERATES AT THE SAME PRESSUREAS THE PIPELINE BETWEEN 110 AND 150 PSIG. LEE SUMMIT RD. LAYS NORTH AND SOUTHAND IS 5 LANE ROAD WITH SHOULDER LANES ON BOTH SIDES AS IT APPROACHES I -70.THIS RAOD INCLINES AS YOU PROCEED NORTH AND IS BRIDGED OVER THE TOP OF I 70.JUST NORTH OF THE INCIDENT SITE IS THE EXIT FROM I-70 EAST TO LEE SUMMIT RD.THE EAST RIGHT OF WAY OF LEE SUMMIT RD. FALLS OFF FROM THE EAST SHOULDER TOTHE EAST PROPERTY LINE AT APPROX. A 2 TO 1 SLOPE.
2025-01-31 10:21 | YES | NO | 19970115 | 1997-08-28 | 11032 | LACLEDE GAS CO | 1414 ANGELICA STREET | ST LOUIS |  | MO | 63107 | 3 | NO | 232 | 1997-07-18 | 0 | 0 | 75000 | 53037.7282 | 128057.8679 | Null | 1 | 33 |  | 19970718 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER |  | OTHER |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL HUNKER | 3143420528 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | REIDENTIAL STRUCTURE EXPLOSION AS A RESULT OF APPARENT NATURAL GAS IGNITION.INVESTIGATION FOUND AN OPEN 3/8 INCH FUEL RUN IN THE BASEMENT OF THERESIDENCE. OPERATOR'S EMPLOYEE HAD RE-ESTABLISHED GAS SERVICE APPROX. 13 HRS.PRIOR TO IGNITION.
2025-01-31 10:21 | NO | NO | 19970118 | 1997-09-03 | 18440 | SOUTH JERSEY GAS CO | NEW YORK AVENUE & BOARDWALK | ATLANTIC CITY | ATLANTIC | NJ | 08401 | 4 | NO | 1514 | 1997-08-05 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 1 | 57 |  | 19970806 | 0.25 | 0.25 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | NO DATA |  | STEEL |  | 1.25 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOHN HOUCK | 6095619000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE OPERATOR IN PREPARING TO REPLACE A LEAKING 1-1/4" BARE STEEL SERVICE WASREMOVING AN EXISTING STEEL SERVICE TEEWHEN LEAKING GAS AROUND THE THREAD AREAOF THE SERVICE TEE IGNITED. CAUSE OF IGNITION IS UNDER INVESTIGATION. AS OFTHIS DATE IT APPEARS THAT A LIGHT BULB ON A DROP LIGHT BEING USED FOR LIGHTBROKE CAUSING A SOURCE OF IGNITION.
2025-01-31 10:21 | YES | YES | 19970119 | 1997-09-02 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 100 BLK. EAST ALTA MESA | FORT WORTH | TARRANT | TX | 76134 | 3 | NO | 830 | 1997-07-30 | 0 | 3 | 15000 | 10607.5456 | 25611.5736 | Null | 0 | 36 |  | 19970730 | 147 | 500 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 2.5 | API5L-GRADE 2 |  | 1986 | 1988 | OTHER | UNDER STREET | ELLEN WEAVER | 2146702986 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-07-21 | YES | 3 | VALVE BOX SIGN | NO |  |  | CITY CONTRACTOR HIT GAS LINE WITH MECHANIZED EQUIPMENT.
2025-01-31 10:21 | NO | NO | 19970121 | 1997-06-26 | 2292 | CHELSEA GAS AUTH | NS 418 AND EW 37 |  | ROGERS | OK | 74016 | 4 | NO | 930 | 1997-06-20 | 0 | 0 | 6000 | 4243.0183 | 10244.6294 | Null | 1 | 0 |  | 19970620 | 55 | 300 | BY TEST | 300 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 |  |  | 1985 | 1986 | UNDER GROUND OR UNDER WATER |  | RICHARD WEBSTER | 9187892404 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-06-20 | YES | 1 |  | YES |  |  | B.J.P. ENTERPRISES INC. LAYING 4" PVC WATER LINE. TRACKHOE KNOCKED HOLE IN TOPOF 6" COATED PIPELINE. CLAMP OFF LEAK TEMPORARALY, WILL MAKE PERMANENT REPAIR6/23/1997.
2025-01-31 10:21 | YES | NO | 19970123 | 1997-09-05 | 4060 | EAST OHIO GAS CO | 25735 LORAIN RD | NORTH OLMSTEAD | CUYAHOGA | OH |  | 3 | NO | 853 | 1997-07-30 | 0 | 0 | 2500000 | 1767924.275 | 4268595.5961 | Null | 0 | 37 |  | 19970730 | 42 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 2 | 0 | 5202/783 | FISHER | 1964 | 1965 | ABOVE GROUND |  | PAUL OLESKA | 2167366858 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | CLEARLY VISIBLE ABOVE | Null |  |  | THE CAUSE OF THE INCIDENT WAS A LARGE COMMERCIAL LAWN MOWER THAT HIT A CLEARLYVISIBLE ABOVE GROUND 2-INCH NATURAL GAS SERVICE REGULATOR. THE IMPACT OF THELAWN MOWER BROKE THE REGULATOR , JAMMING IT IN AN OPEN POSITION AND ALLOWINGAN ELEVATED LEVEL OF GAS TO ENTER THE HOUSELINE( DOWNSTREAM OF THE METER) OFKINGS PATH CONDOMINIUMS. SEVERAL FIRES IGNITED , AND EXTENSIVE FIRE DAMAGEENSUED.
2025-01-31 10:21 | NO | NO | 19970124 | 1997-07-03 | 15462 | PECO ENERGY CO | 300 FRONT STREET | WEST CONSHOHOCTIEN |  | PA | 19428 | 1 | NO | 1300 | 1997-06-06 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19970606 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CITY GATE | OTHER | ODORIZER | NO DATA |  | 0 | 0 |  | YZ INJET | 1993 | 1993 | OTHER | DISTRIBUTION SYSTEM | SCOTT HANSBERRY | 6108326477 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON JUNE 6 , 1997 WE INJECTED TOO MUCH ODORANT INTO OUR NATURAL GASDISTRIBUTION SYSTEM. THE PRIMARY ODERIZER AT THE WEST CONHOHOCKEN GATE STATIONFAILED. DURING THE MANUAL TRANSFER OVER TO THE BACK UP SYSTEM , AN APPARENTOPERATOR ERROR RESULTED IN EXCESS AMOUNTS OF ODORANT BEING INJECTED INTO THEDISTRIBUTION SYSTEM. WE NOTIFIED DOT BECAUSE THERE WAS MEDIA COVERAGE OF THESITUATION. THERE WAS NO DAMAGE INJURIES, OR FATALITIES ASSOCIATED WITH THEEPISODE. THERE WAS NO DANGER TO THE PUBLIC, MERELY, MEDIA COVERAGE OF THESTRONG GAS ODOR.
2025-01-31 10:21 | YES | YES | 19970125 | 1997-09-05 | 15348 | PEOPLES GAS SYSTEM INC | ARBOR GREEN SUBDIVISION | TAMPA | HILLSBOROUGH | FL | 33647 | 3 | NO | 1015 | 1997-08-04 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 15 |  | 19970822 | 34 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | 2408 | PLECO | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | TIMOTHY KASPRZYK | 8132720248 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-07-28 | YES | 1 |  | YES |  |  | CONTRACTOR WAS TRENCHING PARALLEL TO OUR 2" PE MAIN AT APPROX. 12" AWAY.OPERATOR STOPPED TRENCHER TURNED IT AROUND DROPPED CHAIN TO ATRT TRENCHINGAGAIN AND HIT OUR MAIN. HITING MAIN RESULTED IN IGNITION AND CONTRACTOR'SEMPLOYEE SUFFERED BURNS. MAIN WAS MARKED BY PERMANENT MARKERS, TEMPORARYFLAGS, PAINT OFFSET MARKINGS ON CURB AND WARNING TAPE OVER THEMAIN.CONTRACTOR DID COMPLY WITH OSHA CONSTRUCTION STANDARD 1926.651 (B) (2)REQUESTING LOCATION OF OUR LINE BUT FAILED TO COMPLY WITH OSHA 1926.651 (B)WHICH STATES, " WHEN EXCAVATION OPERATIONS APPROACH THE ESTIMATED LOCATION OFUNDERGROUND INSTALLATIONS, THE EXACT LOCATION OF THE INSTALLATION SHALL BEDETERMINED BY SAFE AND ACCEPTABLE MEANS."
2025-01-31 10:21 | NO | NO | 19970127 | 1997-09-02 | 2416 | CITIZENS UTILITY CO | 6500 MACCURDY DR. | PRESCOTT | YAVAPAI | AR | 86031 | 3 | NO | 900 | 1997-07-30 | 0 | 0 | 30000 | 21215.0913 | 51223.1472 | Null | 9 | 5 |  | 19970730 | 55 | 55 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 1.25 | 0.14 | GRADE B |  | 0 | 1988 | ABOVE GROUND |  | RONALD CHURCH | 5204452211 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA | PLUGGING TOOL BLEW OUT WHILE WELDING ON RISER | ON 7/30/1997 AT 8:00 AM TOM BROWN AND CHRIS RICE WENT TO 6500 MACCURDY DR. TORAISE A 1-1/4" STEEL METER STOP OUT OF THE DIRT FOR THE SERVICE DEPT. UPONARRIVAL CONES WERE SET UP TO MARK THE PERIMETER OF THE CONSTRUCTION ZONE ANDONE OF THE TWO FIRE EXTINGUISHERS WERE SET NEAR THE METER TO BE WORKED ON.THE CUSTOMERS WERE NOTIFIED THEIR GAS SERVICE WOULD BE TURNED OFF FOR APPROX.TWO HRS. THE STOP AND RISER WERE DUG OUT BY HAND IN PREPARATION FOR THEPROCEDURE. THE RISER PLUGGING TOOL WHICH HAD BEEN INSPECTED FOR ANY NEEDEDREPAIRS ON MAY 15, 1997 WAS FITTED WITH A NEW 1-1/4 RUBBER PLUG. A FOUR WHEELCOLD CUTTER WAS USED TO CUT THE RISER OFF JUST BELOW THE STOP. THE PRE-CUTBEVELED AND THREADED RISER EXTENSION WAS PLACED OVER THE RISER PLUGGING TOOL.THE PLUGGING TOOL WAS THEN INSERTED INTO THE RISER. THE RISER PLUGGING TOOLWAS TIGHTENED BY HAND AND THEN SNUGGED ADDITIONALLY WITH A PAIR OF SMALLPLIRES TO ASSURE A GOOD SEAL. ( SEE REPORT)
2025-01-31 10:21 | YES | YES | 19970129 | 1997-08-26 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 767 CENTRAL | WYANDOTTE | WAYNE | MI | 48192 | 3 | NO | 1356 | 1997-08-13 | 1 | 1 | 0 | 0 | 0 | Null | 5 | 16 |  | 19970813 | 10 | 10 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0 | 0 | SDR11 |  | 1969 | 1969 | OTHER | VAULT | THOMAS FUNTSCH | 3135777026 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | GAS LEAKING FROM A REPAIR COUPLING ON A 1-1/2 PLASTIC SERVICE MIGRATED INTO ANUNDERGROUND VAULT WHERE IT IGNITED. ORIGINALLY TWO EMPLOYEES WERE HOSPITALIZEDWITH BURN INJURIES. WE HAVE SUBSEQUENTLY LEARNED THAT ONE HAS DIED; WEBELIEVED DUE TO AN INFECTION RECEIVED WHILE IN THE HOSPITAL BEING TREATED.
2025-01-31 10:21 | YES | YES | 19970130 | 1997-08-06 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 1515 SW CARY PARKWAY | CARY | WAKE | NC | 27511 | 3 | NO | 1450 | 1997-08-01 | 0 | 2 | 20000 | 14143.3942 | 34148.7648 | Null | 0 | 3 |  | 19970804 | 2 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER | VALVE LEFT OPEN | STEEL |  | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES HUGHEY | 9198362419 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EMPOLOYEE OF GENERAL CONTRACTED THAT BURT BUILDING WAS ATTEMPTING TO LIGHTCOMMERCIAL DRYER. EMPLOYEE REMOVER A PLUG FROM AN VALVE AND OPENED VALVE TOPURGE AIR FROM NEW GAS LINE IN BUILDING. VALVE WAS LEFT OPEN RESULTING IN ABUILD UP OF NATURAL GAS IN BUILDING WHEN THEN IGNITED. ( SOURCE UNKNOWN)EXPLOSION OCCURED AND INJURED TWO PEOPLE (EMPLOYEES) ATTEMPTING TO LIGHT DRYER.
2025-01-31 10:21 | NO | NO | 19970131 | 1997-08-12 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 4100 GWYNNE RD. | MEMPHIS | SHELBY | TN | 38111 | 3 | NO | 40 | 1997-07-15 | 0 | 0 | 70000 | 49501.8797 | 119520.6767 | Null | 2 | 5 |  | 19970715 | 27 | 30 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | OTHER | COPPER | 0.5 | 0.04 | ASIM B-88 |  | 1974 | 1974 | ABOVE GROUND |  | WADE STINSON | 9013673300 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | LIGHTNING STRUCK THE GAS METER AT THIS RESIDENCE, RUPTURING THE SERVICE RISERAPPROX. SIX INCHES ABOVE GROUND, AND IGNITING THE ESCAPING GAS. THE RESULTINGFIRE DID AN ESTIMATED 70,000 DAMGE TO THE STRUCTURE AND CONTENTS. THERE WERENO PERSONAL INJURIES.
2025-01-31 10:21 | NO | NO | 19970136 | 1997-09-10 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 416 TEXAS | SOUTH HOUSTON | HARRIS | TX | 77587 | 3 | NO | 142 | 1997-08-08 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 5 | 18 |  | 19970808 | 32 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | API 5L | UNK. | 0 | 1946 | UNDER GROUND OR UNDER WATER |  | JEFFREY BISH | 7139678093 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | SERVICE LINE WAS PULLED FROM COMPRESSION COUPLING AND ESCAPING GAS IGNITED.UNKNOWN FORCE PULLED SERVICE LINE FROM COMPRESSION COUPLING, ESCAPING GAS WASIGNITED.
2025-01-31 10:21 | NO | NO | 19970138 | 1997-09-22 | 11680 | LONE STAR PIPELINE CO (TRANSMISSION DIVISION) | PIONEER AND N. BELTINE | IRVING | DALLAS | TX | 75061 | 3 | NO | 1600 | 1997-08-15 | 0 | 0 | 68000 | 48087.5403 | 116105.8002 | Null | 6 | 0 |  | 19970815 | 20 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0 |  |  | 0 | 1985 | UNDER PAVEMENT |  | ELLEN WEAVER | 2146702986 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-07-17 | YES | 1 | OTHER - FLAGS AND PAINT | NO |  |  | CONTRACTOR DRILLED INTO A 6" POLY MAIN.
2025-01-31 10:21 | YES | NO | 19970141 | 1997-09-16 | 2568 | COLORADO SPRINGS, CITY OF | 4247 AND 4249 GILLS MILL CT. | COLORADO SPRINGS | EL PASO | CO | 80910 | 3 | NO | 1447 | 1997-08-24 | 0 | 0 | 250000 | 176792.4275 | 426859.5596 | Null | 0 | 10 |  | 19970825 | 15 | 29 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 1 | 0 | MOD B-32R | SPAGUE | 0 | 1969 | ABOVE GROUND |  | WAYNE BOOKER | 7196683505 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APART. RESIDENT WAS OPERATING AN ELECTRIC RANGE INSIDE UNIT #4249 WHICHRESULTED IN A GREASE FIRE. THE FIRE SPREAD THROUGHOUT THE UNIT AND ALONG APATIO FENCE. FLAMES FROM THE BURNING FENCE INPINGED ON THE GAS SERVICEREGULATIONS OF UNITS 4249 AND 4247, WHICH FAILED. ESCPING GAS ACCLERATED THEFIRE. CLOSING THE SERVICE LINE VALVES CONTROLLED THE FLOW OF GAS.
2025-01-31 10:21 | YES | YES | 19970142 | 1997-09-18 | 1088 | BALTIMORE GAS & ELECTRIC CO | 307 AMMUNITION AVENUE | ODENTON | ANNE ARUNDEL | MD | 21113 | 3 | NO | 1051 | 1997-08-27 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 49 |  | 19970827 | 97 | 99 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6.25 | 0.09 | ASTM D 2513 | DRISCO 8000 | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | DONALD SHRADER | 4102915130 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | PAINT ON CURB | YES |  |  | ON AUGUST 27, 1997 AT 1051 ANNE ARUNDEL COUNTY FIRE DEPT. REPORTED A NATURALGAS PIPE ON FIRE WITH PERSONAL INJURIES INVOLVED. BALTIMORE GAS AND ELECRICRECIVED THE CALL AT 1051 DISPATHCHING A GAS MECHANIC TO THE SCENE. ARRIVING ONSCENE AT 11:10 BALTIMORE GAS AND ELECTRIC GAS MECHANIC FOUND A GAS SERVICELINE GOING TO 307 AMMUNITION AVE DAMAGED AND FIRE. PLUMBER MR. GRIGORYRUBINSHTEYN WORKING FOR TECHNO-MAGIC PLUMBING AND HEATING CO. WAS REPARING ALEAKING WATER SERVICE USING AN ACETYLENE TORCH. WHILE IN THE OPEN DITCH, THEPLUMBER DID NOT REALIZE THE GAS PIPE WAS NEAR HIS WORK, HE MELTED THE 5/8 INCHPLASTIC GAS SERVICE WITH THE TORCH CAUSING IGNITION OF THE GAS. THE PLUMBERRECIEVED SECOND AND THIRD DEGREE BURNS TO BOTH ARMS AND WAS SENT TO BAYVIEWBURN CENTER IN BALTIMORE MARYLAND, WHERE HE STAYED OVERNIGHT. THE GAS FIREALSO MELTED THE UNDERGROUND ELECTRICAL SERVICE TO THE BUILDING. THE GAS WASSHUT OFF AT 1140 AND RESTIRATION OF GAS SERVICE STARTED.
2025-01-31 10:21 | NO | NO | 19970143 | 1997-09-22 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 7101 LAPASEO | HOUSTON | HARRIS | TX | 77087 | 3 | NO | 430 | 1997-08-17 | 0 | 0 | 5000 | 3535.8485 | 8537.1912 | Null | 1 | 3 |  | 19970817 | 30 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 1 | 0.133 | API 5L | UNK. | 0 | 1948 | UNDER GROUND OR UNDER WATER |  | JEFFREY BISH | 7139678093 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | A ONE INCH I.P. STEEL SERVICE LINE CRACKED AT THREADED ELL, RELEASING GASUNDERGROUND NEAR BUILDING.
2025-01-31 10:21 | NO | NO | 19970145 | 1997-10-06 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | JONESVILLE PIPELINE |  | HARRISON | TX |  | 2 | NO | 1015 | 1997-09-03 | 0 | 0 | 8000 | 5657.3577 | 13659.5059 | YES | 0 | 45 |  | 19970903 | 85 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1 | 0 |  |  | 0 | 1989 | ABOVE GROUND |  | GEORGE CARLILE | 9039357943 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | BUSHHOG OPERATOR EMPLOYED BY KOCH RAN OVER BARRICADED METER BREAKING NIPPLEOFF ABOVE SHUT OFF VALVE. ESCAPING GAS IGNITED AND DAMAGED TRACTOR. ALSO,FLASH BURNED TRACTOR OPERATOR ON HANDS AND ARMS. DOCTOR SAID ABOUT LIKE A BADSUNBURN.
2025-01-31 10:21 | YES | YES | 19970147 | 1997-10-09 | 18536 | SOUTHWEST GAS CORP | 2025 W. TURNEY AVE. | PHOENIX | MARICOPA | AZ | 85015 | 3 | NO | 1941 | 1997-09-11 | 0 | 11 | 276500 | 195532.4248 | 472106.6729 | Null | 3 | 1 |  | 19970911 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | OTHER | PVC | 2 | 0.113 | ASTMD2513 | KERONA | 1971 | 1971 | UNDER GROUND OR UNDER WATER |  | PHILLIPS ANDREW | 6024845218 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | ELECTRIC CABLE INSTALLED DIRECTLY IN CONTACT WITH | AN ELECTRIC CABLE WAS INSTALLED IMMEDIATLEY ABOVE AND IN CONTACT WITH THE2"PVC GAS MAIN . THE CABLE HAD A SHORT, OR GROUND FAULT, MELTING THE PLASTICGAS MAIN. THE ESCAPING GAS WAS IGNITED BY AN UNKNOWN SOURCE WHICH DAMAGED ONEAPRTMENT BUILDING THAT CONTAINED TWO UNITS. ELEVEN PEOPLE WERE TRANSPORTED TOHOSPITALS AND NINE HAVE SINCE BEEN RELEASED.
2025-01-31 10:21 | YES | NO | 19970148 | 1997-10-06 | 8040 | ILLINOIS POWER CO | 601 S. BROAD ST. | KNOXVILLE | KNOX | IL | 61448 | 0 | NO | 1202 | 1997-09-24 | 0 | 0 | 100000 | 70716.971 | 170743.8238 | Null | 6 | 48 |  | 19970924 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | SDR11 | PLEXCO | 0 | 1979 | UNDER GROUND OR UNDER WATER |  | DON JOHNSON | 2174247001 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-09-17 | YES | 3 | FLAGS&PAINT | YES |  |  | DIRECTIONAL BORING UNIT CUT 5/8" PLASTIC SERVICE GAS MIGRATED THROUGH BURIEDTILE INTO HOME AND WAS IGNITED BY AN UNIDENTIFIED SOURCE.
2025-01-31 10:21 | YES | NO | 19970149 | 1997-09-29 | 11800 | LOUISIANA GAS SERVICE CO | 6736 ARTHUR STREET | METAIRIE | JEFFERSON | LA | 70003 | 4 | NO | 1120 | 1997-08-28 | 0 | 0 | 121500 | 85921.1198 | 207453.746 | Null | 6 | 0 |  | 19970828 | 65 | 100 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | JOINT | THREADED | STEEL |  | 2 | 0.154 | SCHEDULE 40 |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | LEON HINSON | 5043747265 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null |  |  | MOST PROBABLE SCENARIO FOR FIRE EVENT - THIS AREA HAS A HISTORY OF SOILSUBSIDENCE. ALSO, THERE HAS BEEN NEW DRAINAGE CONSTRUCTION DONE ON ARTHURSTREET AND CROSS STREET EISENHOWER WITHIN THE PAST YEAR. IT IS PROBABLE THATSUBSIDENCE AND/OR RECENT CONSTRUCTION IN THE AREA STRESSED THE THREADEDCONNECTION BETWEEN THE MAIN AND VALVE CAUSING BREAK. BECAUSE OF SUBSIDENCE ANDEXCESSIVELY DRY SOIL CONDITIONS, GAS MIGRATED UNDERNEATH 6737 ARTHUR STREETAND SURFACED BETWEEN ABUTTING SLABS VERY NEAR THE GAS WATER HEATER. THE GASPILOT ON THE WATER HEATER APPARENTLY WAS THE IGNITION SOURCE.
2025-01-31 10:21 | NO | NO | 19970150 | 1997-10-15 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | WOODWARD AVENUE AND SEARS STREET | HIGHLAND PARK | WAYNE | MI | 48203 | 3 | NO | 1152 | 1997-09-20 | 0 | 0 | 8061 | 5700.495 | 13763.6596 | YES | 0 | 22 |  |  | 50 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | SHUT OFF VALVE BROKEN | STEEL |  | 1 | 0.133 |  |  | 0 | 1957 | UNDER PAVEMENT |  | ROGER GREGORY | 3135777045 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | ON SEPT 20, 1997 THE INCIDENT WAS REPORTED TO DOT DUE TO OPERATORJUDGEMENT/EMRGENCY ACTION DUE TO 50 PSIG OF NATURAL GAS BLOWING INTO THEATMOSPHERE. WOODWARD AVENUE BEING TOTALLY BLOCKEDTO TRAFFIC BOTH NORTH ANDSOUTHBOUND, POLICE AND FIRE PERSONNEL ON SITE, INCLUDING EXTENSIVE TV MEDIACOVERAGE. THE REPAIR METHOD ANTICIPATED DAMAGE TO THE 12" PAS SERVICE LINE.HOWEVER, THE 12" GAS SERVICE LINE WAS NOT BROKEN AND FINAL REPAIRS WERECALCULATED AT 8,061.43. YOU MASY RETAIN THIS REPORT NO. 404428 AS YOU SEE FITWITH KNOWLEDGE THAT THE ORIGINAL SEPT. 20 ,1997 NOTICE WAS BASED ON OPERATORJUDGEMENT.
2025-01-31 10:21 | YES | YES | 19970151 | 1997-10-16 | 4060 | EAST OHIO GAS CO | CORNER OF SHAW AVE. & WELTON RD. | EAST CLEVELAND | CUYAHOGA | OH | 44112 | 3 | NO | 1640 | 1997-09-16 | 0 | 3 | 5000 | 3535.8485 | 8537.1912 | Null | 0 | 50 |  | 19970916 | 0.5 | 1 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE | SHUT OFF VALVE BROKEN | STEEL |  | 2 | 0 |  |  | 0 | 1913 | OTHER | VAULT | CLARENCE MOORE | 2167366835 | EXTERNALLY | GENERAL CORROSION |  | OTHER | ATMOSPHERIC | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A 2 INCH LOW PRESSURE BARE STEEL GAS MAIN EXTENMDED THROUGH AN ELECTRICUTILITY VAULT. DURING A BAND CLAMP REPAIR OPERATION, THE PIPE FAILED AS ARESULT OF SEVERE ATMOSPHERIC CORROSION. TWO EMPLOYEES WERE OVERCOME BYESCAPING NATURAL GAS. A SUPERVISOR CALLED FOR HELP AND THE TWO EMPLOYEES WERERESCUED BY A FIREMAN. THE FIREMAN WAS ALSO OVERCOME. THREE MEN WERE TAKEN TO ALOCAL HOSPITAL, KEPT OVERNIGHT, AND RELEASED THE NEXT DAY. THE LOW PRESSUREMAIN WAS REPLACED IN ANOTHER LOCATION.
2025-01-31 10:21 | YES | NO | 19970153 | 1997-10-28 | 15259 | PENNSYLVANIA GAS & WATER CO | 1031 KELLER STREET | SUNBURY STREET | NORHTUMBERLAND | PA | 17801 | 3 | NO | 1511 | 1997-10-04 | 0 | 0 | 90000 | 63645.2739 | 153669.4415 | Null | 1 | 56 |  | 19971004 | 11 | 1 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.133 | SCHED.40 |  | 0 | 0 | UNDER PAVEMENT |  | JAMES GREGER | 7178298866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-09-10 | NO | 0 |  | Null |  |  | ON OCTOBER 1, 1997 THE SUNBURY MUNICIPAL WATER DEPT. WAS WORKING ON KELLERSTREET AND HIT AN ACTIVE GAS SERVICE. AT THIS TIME, THE DAMAGED SECTION OFPIPE WAS CUT OUT AND CAPPED BY PG ENERGY'S PERSONNEL ALLOWING TH EWATERCOMPANY TO CONTINUE IT'S WORK. THE REMAINING SERVICE OFF A 3" LOW PRESURESTEEL MAIN WAS SCHEDULED FOR ABANDOMENT ON 10/6/97. AT THE TIME OF THEINCIDENT, 10/4/97, IT WAS DISCOVERED, AFTER EXCAVATION THAT THE EXISTINGSERVICE TEE WAS CRACKED AT THE MAIN WHICH WAS THE PROBABLE SOURC OF LEAKAGECAUSING THIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19970158 | 1997-12-10 | 11032 | LACLEDE GAS CO | 5530 DUGAN STREET | ST LOUIS |  | MO | 63110 | 3 | NO | 2245 | 1997-11-05 | 0 | 1 | 50000 | 35358.4855 | 85371.9119 | Null | 8 | 45 |  | 19971106 | 0.3 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.475 |  |  | 0 | 1927 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER, JR./ASSOCIATE GENERAL COUNSEL | 3143420528 | [6 empty] | Null |  | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null |  |  | EXTERNAL STRESSES ON A SIX-INCH CAST IRON LOW PRESSURE MAIN CAUSED A FRACTUREOF APPROXIMATELY 85% AROUND THE CIRCUMFERENCE.
2025-01-31 10:21 | YES | YES | 19970159 | 1997-12-11 | 12642 | MOBILE GAS SERVICE CORP | 1254 STATE STREET | MOBILE | MOBILE | AL | 36603 | 3 | NO | 1815 | 1997-11-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 49 |  | 19971111 | 30 | 57 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1955 | UNDER GROUND OR UNDER WATER |  | JIMMIE L. BUTLER, DIRECTOR OF ENGINEERING | 3344504617 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE DISTRIBUTION SYSTEM RECEIVED CONSTRUCTION DAMAGE FROM A CONTRACTOR WHICHRESULTED IN A RELEASE OF GAS. BASED ON INVESTIGATION TO DATE, THE EVIDENCE ISRESULTED IN A RELEASE OF GAS. BASED ON INVESTIGATIONS TO DATE, THE EVIDENCENOT SUGGESTIVE OF A NATURAL GAS FIRE OR EXPLOSION OR INJURY RESULTING FROM THEIS NOT SUGGESTIVE OF A NATURAL GAS FIRE OR EXPLOSION OR INJURY RESULTING FROMGAS LEAK.THE GAS LEAK.
2025-01-31 10:21 | YES | YES | 19970160 | 1997-11-17 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 40TH STREET & VERMONT AVE | LOUISVILLE | JEFFERSON | KY | 40211 | 3 | NO | 1345 | 1997-09-18 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 0 |  | 19971112 | 0.38 | 0.5 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0 |  |  | 0 | 1924 | UNDER PAVEMENT |  | SCOTT D. CUTLIP, MANAGER GAS ENGINEERING | 5026272433 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | SECTION OF MAIN HAS BEEN REPLACED. IGNITION OF GAS OCCURRED DURING LEAKPART A - SECTION OF MAIN HAS BEEN REPLACED. IGNITION OF GAS OCCURRED DURINGLEAK REPAIR. SOURCE OF IGNITION NOT DETERMINED.REPAIR. SOURCE OF IGNITION NOT DETERMINED.
2025-01-31 10:21 | YES | YES | 19970161 | 1997-11-13 | 30750 | MIDAMERICAN ENERGY CO | 3601 WEST 4TH STREET | SIOUX CITY | WOODBURY | IA |  | 3 | NO | 800 | 1997-08-13 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 1 |  | 19970813 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | PE 3408 | PLEXCO-YELLOWSTRIPE | 1988 | 1988 | OTHER | BURIED PIPE EXPOSED TRENC | DAVID C. GRIGSBY - PROJECT ENGINEER | 7122777448 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | PIPELINE CONTRACTOR WAS RELEASING RESIDUAL PRESSURE TO RETIRE A GAS MAIN WHENAN ACCIDENTAL IGNITION OCCURRED IN A TRENCH. ONE CONTRACTOR EMPLOYEESUSTAINED BURNS ON HIS FOREARMS AND REQUIRED IN-PATIENT HOSPITALIZATION.STATIC ELECTRICITY IS SUSPECTED AS THE CAUSE AS THE CAUSE OF THE IGNITION.STATIC ELECTRICITY IS SUSPECTED AS THE CAUSE OF THE IGNITION.
2025-01-31 10:21 | YES | YES | 19970162 | 1997-11-12 | 30750 | MIDAMERICAN ENERGY CO | 2635 1ST STREET COURT | EAST MOLINE | ROCK ISLAND | IL |  | 4 | NO | 1730 | 1997-10-05 | 1 | 5 | 50000 | 35358.4855 | 85371.9119 | Null | 0 | 30 |  | 19971005 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | ROBERT HENDRIX, MANAGER OPERATIONS - ILLINOIS/QUAD CITIES | 3097933652 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE INCIDENT IS STILL UNDER INVESTIGATION. THE INVESTIGATION HAS NOTINDICATED NATURAL GAS FROM MIDAMERICAN PIPELINE AS THE CAUSE TO DATE.
2025-01-31 10:21 | YES | NO | 19970163 | 1997-11-12 | 18484 | SOUTHERN CALIFORNIA GAS CO | 329 LAFAYETTE ST | GLENDALE | LOS ANGELES | CA | 91204 | 3 | NO | 1430 | 1997-10-13 | 0 | 0 | 250000 | 176792.4275 | 426859.5596 | Null | 7 | 51 |  | 19971013 | 40 | 50 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ADYL-A | DUPONT | 1979 | 1979 | UNDER PAVEMENT |  | JACK C. WALDEN - SAFETY ENGINEER | 2132443287 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AXIAL CRACKS DEVELOPED ALONG 2" PE MAIN DUE TO TREE ROOTS. TREE ROOTPART 3 - AXIAL CRACKS DEVELOPED ALONG 2" PE MAIN DUE TO TREE ROOTS. PART D -TREE ROOT ENTANGLEMENT RESULTED IN AXIAL CRACKS DEVELOPING ON 2" PE MAINENTANGLEMENT RESULTED IN "AXIAL" CRACKS DEVELOPING ON 2" PIPE PE MAIN.LEAKING GAS MIGRATED TO "LIT" FLOOR FURNACE RESULTING IN IGNITION. NOINJURIES MAJOR DAMAGE TO RESIDENCE. ATTACHED - ON OCTOBER 13, 1997 ATAPPROXIMATELY 2:30 PM,. A CRACKED DISTRIBUTION PLASTIC (POLYETHELENE) PIPELINEINJURIES. MAJOR DAMAGE TO RESIDENCE.ON LAFAYETTE STREET IN GLENDALE CALIFORNIA RELEASED NATURAL GAS INTO AATTACHED - ON OCTOBER 13, 1997 ATRESIDENCE AT 329 LAFAYETTE CAUSING AN EXPLOSION AND DAMAGE TO THE RESIDENCE.THERE WERE NO INJURIES OR DEATHS RESULTING FROM THIS INCIDENT. ANINVESTIGATION BY THE SOUTHERN CALIFORNIA GAS COMPANY (THE GAS COMPANY), WASCONDUCTED TO DETERMINE THE CAUSE OF THE EXPLOSION. IT WAS DISCOVERD THAT THELEAK WAS THE RESULT OF ROOT DAMAGE FROM A NEARBY TREE IN THE PARKWAY OF THELAFAYETTE STREET. A CAROB TREE ROOT GREW INTO THE BORE HOLE OF THE ORIGINALPIPE INSTALLATION, GREW AROUND THE PLASTIC PIPE AND EVENTUALLY CRUSHED THEPIPEWALL ENOUGH TO CAUSE CRACK PROPAGATION TO THE OUTSIDE WALL ALLOWING GAS TOESCAPE INTO THE SOIL. THE GAS MIGRATED TOWARD THE STRUCTURE AND WAS IGNITEDBY A FLOOR FURNACE AT THIS ADDRESS. NINETY-FIVE FEET OF PLASTIC PIPE WASREMOVED FOR TESTING. THE TESTS REVEALED THAT THE PIPE IS IN EXCELLENT SHAPE.THE LOS ANGELES OFFICE OF THE CALIFORNIA PUBLIC UTILITIES COMMISSION UTILITIESSAFETY BRANCH SENT AND ENGINEER OUT TO THE INCIDENT TO INVESTIGATE. THEENGINEER HAS NOT YET CLOSED HIS INVESTIGATION BUT HAS NOT FOUND ANYDISCREPANCIES IN THE GAS COMPANY'S PROCEDURES OR OPERATIONS.
2025-01-31 10:21 | NO | NO | 19970164 | 1997-11-10 | 11720 | LONG ISLAND LIGHTING CO | 2 GATEWAY COURT | BAYVILLE | NASSAU | NY | 11709 | 4 | NO | 1410 | 1997-10-07 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 9 |  | 19971008 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | CONSUMER OWNED PIPING | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS E. LUPSKI, CODE AND SPECIFICATION ENGINEER | 5165454400 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | THIS INCIDENT WAS INVESTIGATED BY THE NASSAU COUNTY OFFICE OF THE FIREMARSHAL. A LANDSCAPE CONTRACTOR DISCONNECTED A SECTON OF CONSUMER OWNED GASMARSHAL. A LANDSCAPE CONTRACTOR DISCONNECTED A SECTION OF CONSUMER OWNED GASPIPE FROM THE OUTSIDE WALL OF 2 GATEWAY COURT CAUSING GAS TO ESCAPE INTO THEBASEMENT OF THE BUILDING WHICH RESULTED IN AN EXPLOSION AND FIRE. LILCOFACILITIES WERE INVOLVED IN THIS INCIDENT. THREE PEOPLE WERE HOSPITALIZED ASFACILITIES WERE NOT INVOLVED IN THIS INCIDENT. THREE PEOPLE WERE HOSPITALIZEDA RESULT OF THIS INCIDENT WHICH ALSO CAUSED STRUCTURAL DAMAGE IN EXCESS OFAS A RESULT OF THIS INCIDENT WHICH ALSO CAUSED STRUCTURAL DAMAGE IN EXCESS OF$50,000 TO 2 GATEWAY COURT.
2025-01-31 10:21 | YES | NO | 19970165 | 1997-11-03 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 62460 CAMPGROUND ROAD | WASHINGTON TOWNSHIP | MACOMB | MI | 48094 | 3 | NO | 1445 | 1997-10-18 | 0 | 0 | 1400000 | 990037.594 | 2390413.5338 | Null | 0 | 1 |  | 19971018 | 1280 | 1970 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CRANK-END UNLOADER VALVE | OTHER | CRANK-END UNLOADER VALVE | OTHER |  | 0 | 0 |  | HOERBIGER | 1995 | 1995 | WITHIN/UNDER BUILDING |  | CAROL F. MATHEWS (SR. INVESTIGATOR) | 3135777025 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE CRANK-END UPLOADER VALVE FAILED. A FAILURE OCCURRED WHEN THE CRANK-ENDA FAILURE OCCURRED WHEN THE CRANK-END UNLOADER VALVE BLEW OFF THE COMPRESSORALLOWING NATURAL GAS TO FLOW AT HIGH PRESSURE INSIDE THE BUILDING. THEUNLOADER VALVE BLEW OFF THE COMPRESSOR ALLOWING NATURAL GAS TO FLOW AT HIGHLEAKING GAS THEN IGNITED FROM AN UNKNOWN SOURCE. THE COMPRESSOR BUILDING WASDESTROYED. THE SYSTEM (EDS) SHUT DOWN THE STATION IMMEDIATELY WHICHPRESSURE INSIDE THE BUILDING. THE LEAKING GAS THEN IGNITED FROM AN UNKNOWNCONTROLLED THE LOSS OF GAS.SOURCE. THE COMPRESSOR BUILDING WAS DESTROYED. THE SYSTEM (EDS) SHUT DOWNTHE STATION IMMEDIATELY WHICH CONTROLLED THE LOSS OF GAS.
2025-01-31 10:21 | YES | NO | 19970166 | 1997-11-03 | 4483 | ENSTAR NATURAL GAS CO | LOT 6A BLOCK 3 BIRCH HABOR #2 SUB. | MATANUSKA | SUSITNA BOROUGH | AK | 99654 | 2 | NO | 2344 | 1997-10-23 | 0 | 0 | 150000 | 106075.4565 | 256115.7358 | Null | 1 | 0 |  | 19971024 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER | CRANK-END UNLOADER VALVE | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1994 | 1994 | ABOVE GROUND |  | DREW W. SMITH, SENIOR ENGINEER | 9072643744 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | A WOOD STOVE CAUSED A STRUCTURAL FIRE WHICH MELTED A 5/8" S/L INSIDE A STEELRISER.
2025-01-31 10:21 | YES | YES | 19980001 | 1997-12-18 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 9318 FILLMORE ROAD | SUMNER | GRATIOT | MI | 48889 | 3 | NO | 1012 | 1997-11-16 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 9 |  | 19971116 | 832 | 1000 | BY TEST | 1500 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | OTHER |  | FITTING |  | OTHER | 1/2" STAINLESS STEEL TUBI | 0.5 | 0.035 | ASTM-A269 | BRAUTCO | 0 | 1997 | WITHIN/UNDER BUILDING |  | GEORGE A. VALIENCE | 3135777029 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A PIECE OF 1/2" STAINLESS STEEL TUBING PULLED OUT OF A COMPRESSION FITTINGALLOWING NATURAL GAS TO FLOW AT HIGH PRESSURE INSIDE THE COMPRESSOR BUILDING.THE THEN LEAKING NATURAL GAS IGNITED FROM AN UNKNOWN SOURCE DAMAGING THECOMPRESSOR BUILDING AND INJURING 2 EMPLOYEES. ONE WAS TREATED AND RELEASEDFOR MINOR BURNS TO FACE AND HAND. ONE WAS HOSPITALIZED WITH SECOND DEGREEBURNS TO FACE AND HANDS.
2025-01-31 10:21 | YES | YES | 19980002 | 1998-01-27 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | PRESTON AT MEEK (EAST DIST) | HOUSTON | HARRIS | TX | 77002 | 3 | NO | 1500 | 1997-12-23 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19971223 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | VALVE |  | STEEL |  | 10 | 0 |  |  | 0 | 1925 | OTHER | VALVE PIT | JEFFREY A. BISH | 7139678093 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19980003 | 1997-12-23 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 7421 WILLIS | FORT WORTH | TARRANT | TX |  | 3 | NO | 1202 | 1997-11-10 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 19 |  | 19971110 | 26 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.09 | PE 2306 |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2146702986 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AN INDIVIDUAL WAS ATTEMPTING TO INSTALL AN ILLEGAL BYPASS AND WAS USING A TARPTO CONCEAL HIS ACTIVITY WHEN HE DIED.
2025-01-31 10:21 | NO | NO | 19980004 | 1997-12-30 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 6809 AVE. F | HOUSTON | HARRIS | TX | 77011 | 3 | NO | 2256 | 1997-12-02 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 24 |  | 19971203 | 35 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE2406 |  | 0 | 1989 | ABOVE GROUND |  | JEFFREY A. BISH | 7139678093 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | FIRE SPREAD FROM GARAGE APARTMENT TO HOUSE - HEAT MELTED 1/2" - PLASTIC PIPECAUSING GAS TO ESCAPE AND IGNITE.
2025-01-31 10:21 | YES | NO | 19980005 | 1997-12-30 | 603 | ARKLA, A NORAM ENERGY COMPANY | 216 PINE FOREST | WAKE WILLAGE | BOWIE | TX | 75501 | 1 | NO | 130 | 1997-12-01 | 0 | 0 | 120000 | 84860.3652 | 204892.5886 | Null | 0 | 10 |  | 19971201 | 20 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | KYLE HOLCOMB | 9038241304 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER WAS COOKING ON AN ELECTRIC RANGE WHEN THE GREASE CAUGHT FIRE,RESULTING IN DAMAGE TO THE HOUSE AND TWO VEHICLES.
2025-01-31 10:21 | YES | NO | 19980006 | 1998-01-20 | 18532 | SOUTHERN UNION GAS CO | 817 LIVE OAK STREET | JACKSBORO | JACK | TX | 76458 | 3 | NO | 1103 | 1997-12-15 | 0 | 0 | 357000 | 252459.5865 | 609555.4511 | YES | 2 | 13 |  | 19971215 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | PAUL R. JOHNSON | 9403257164 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | CONTRACTOR WAS USING ASPHALT SCRAPER TO PREPARE ROAD SURFACE FOR RE-PAVINGWHEN EQUIPMENT STRUCK AND DAMAGED A 2" WRAPPED STEEL CAUSING LEAKAGE. GASIGNITED, RESULTING IN MAJOR FIRE DAMAGE TO EQUIPMENT. FIRE DEPARTMENTRESPONDED AND WAS ON SCENE IN CONTROL OF FIRE AND EXPOSURES WITHIN 17MINUTES. GAS SERVICE WAS BY-PASSED AND LEAK WAS ISOLATED FROM SOURCE BY1:16PM. DAMAGED PIPE WAS THEN REPLACED AND SERVICE RESTORED BY 3:45PM.
2025-01-31 10:21 | YES | NO | 19980008 | 1997-12-24 | 4060 | EAST OHIO GAS CO | 5243 MAPLE SPRINGS DRIVE | SOUTH RUSSELL | GEAUGA | OH | 44022 | 3 | NO | 859 | 1997-12-09 | 0 | 0 | 380000 | 268724.4898 | 648826.5306 | Null | 0 | 30 |  | 19971209 | 58 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | SCREW | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | CLARENCE W. MOORE | 2167366835 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A SEWER CONTRACTOR PERFORMED WORK AT THE SITE OF THE INCIDENT WITHOUTCONTACTING "OUPS" TO HAVE THE LOCATION OF THE SERVICE LINE MARKED. DURING THEWORK PERFORMED BY THE SEWER CONTRQACTOR, THE STEEL GAS SERVICE LINE WASUNDERMINED. THE GAS SERVICE LINE WAS BENT DOWNWARD CAUSING THE PIPE TO BREAKAT THE ROOT OF A THREAD AT A SCREW COUPLING. GAS APPARENTLY MIGRATED ALONGTHE SEWER TO THE HOUSE.
2025-01-31 10:21 | YES | YES | 19980009 | 1997-12-15 | 18472 | SEMCO ENERGY GAS COMPANY | #52 BILLY DRIVE | BEDFORD TOWNSHIP | CALHOUN | MI |  | 3 | NO | 1133 | 1997-11-13 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 18 |  | 19971113 | 25 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA | BELL | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | SDR 11 | DU PONT | 1991 | 1992 | UNDER GROUND OR UNDER WATER |  | THOMAS M. REILLY | 8109877900 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | HOMEOWNER (TIMOTHY D. DAVIS) WAS ASPHYXIATED WHILE ATTEMPTING AN UNAUTHORIZEDBY-PASS OF A 3/4" PE SERVICE LINE. MR. DAVIS WAS OUTSIDE LAYING ON THE GROUNDWITH HIS HEAD AND ARMS IN A SMALL HOLE HE HAD EXCAVATED. HE HAD CUT INTO THELIVE SERVICE WITHOUT ATTEMPTING TO CONTROL THE FLOW. THE ESCAPING NATURAL GASDISPLACED THE OXYGEN RESULTING IN ASPHYXIATION.
2025-01-31 10:21 | NO | NO | 19980010 | 1998-01-28 | 4483 | ENSTAR NATURAL GAS CO | L9, B1 SLEEPY HOLLOW SUBDIVISION | KENAI | PENINSULA BOROUGH | AK | 99669 | 2 | NO | 432 | 1998-01-22 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 1 | 30 |  | 19980122 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1996 | 1996 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | NO | NO | 19980011 | 1998-01-20 | 4483 | ENSTAR NATURAL GAS CO | L 21, B2 FAIRVIEW ESTATES, ADD #1 | MATANUSKA | SUSITNA BOROUGH | AK |  | 3 | NO | 1605 | 1998-01-13 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 1 | 0 |  | 19980113 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | DRISCOPIPE 8000 | PHILLIPS | 1991 | 1991 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | NO | NO | 19980012 | 1998-01-27 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 5TH AVE. BETWEEN 19TH & 20TH | NEW YORK CITY |  | NY | 10011 | 4 | NO | 930 | 1998-01-02 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19980102 | 0.32 | 0.43 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 24 | 0.75 | N/A | N/A | 0 | 1871 | UNDER GROUND OR UNDER WATER |  | ANTHONY B. CODNER | 2124601103 | [6 empty] | Null |  | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | Null |  | Null | 0 |  | Null |  |  | A 48" WATER MAIN BREAK UNDERMINED THE STREET. THE ROADBED COLLAPSED ANDSEVERED A 24" LOW PRESSURE CAST IRON MAIN. THE MAIN SUBSEQUENTLY IGNITED.
2025-01-31 10:21 | NO | NO | 19980013 | 1997-12-23 | 6920 | ENTERGY GULF STATES | 5141 BRECKENRIDGE ST | BATON ROUGE |  | LA | 70805 | 2 | NO | 1132 | 1997-12-08 | 0 | 0 | 50000 | 35358.4855 | 85371.9119 | Null | 0 | 0 |  | 19971208 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | CURTIS HART | 5043543143 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19980015 | 1998-01-21 | 603 | ARKLA, A NORAM ENERGY COMPANY | 2720, 2724, 2730 MORNINGSIDE DRIVE | SHREVEPORT | CADDO | LA | 71108 | 3 | NO | 1650 | 1997-12-23 | 0 | 4 | 125000 | 88396.2137 | 213429.7798 | Null | 2 | 45 |  | 19971223 | 17 | 60 | BY TEST | 0 | OTHER | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.25 | 2" GLAND TYPE | MC WAYNE | 1946 | 1946 | UNDER GROUND OR UNDER WATER |  | HOYLE T. ROGERS | 3184294236 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | ARKLA PERSONNEL WERE NOTIFIED AT 4:50 PM AND ARRIVED ON SITE AT APPROXIMATELY5:08 PM. FURTHER INVESTIGATION REVEALED A COLD BREAK ON A 2" CAST IRON GASMAIN BETWEEN 2720 AND 2724 MORNINGSIDE DR. THE FLOW OF NATURAL GAS WASTERMINATED AT APPROXIMATELY 7:35 PM. AN ESTIMATED 110 MCF OF NATURAL GAS WASRELEASED INTO THE GROUND AROUND THE 54" DEEP CAST IRON MAIN. THE SIDING ON2720 MORNINGSIDE WAS DAMAGED FROM RADIANT HEAT CREATED BY THE FIRE AT 2724MORNINGSIDE. THERE WERE NO INJURIES AT THIS ADDRESS. ESTIMATED DAMAGES BYTHE SHREVEPORT FIRE DEPARTMENT TO THE THREE STRUCTURES AND THREE VEHICLES IS$125,000.00 ESTIMATED DAMAGES TO ARKLA'S FACILITIES IS 9,051.00, INCLUDINGTHE NATURAL GAS THAT WAS LOST.
2025-01-31 10:21 | YES | YES | 19980016 | 1998-01-28 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 805 AYERS STREET | MEMPHIS | SHELBY | TN | 38107 | 3 | NO | 1948 | 1997-12-27 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 0 |  | 19971227 | 0.36 | 0.43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | JOINT | BELL | CAST IRON |  | 6 | 0.38 |  |  | 0 | 1930 | OTHER | WATER METER BOX | BARBARA A. WILSON | 9013201401 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MR. LUTHER WATKINS WAS ATTEMPTING TO SHUT OFF THE WATER METER AT 805 AYERSSTREET, AND LIT A MATCH TO LOOK INSIDE THE WATER METER BOX. A FLASH FIREOCCURRED, WHICH INJURED MR. WATKINS. HE WAS TAKEN BY HIS WIFE TO ST. JOSEPHHOSPITAL BUT WAS NOT ADMITTED. HE WAS LATER ADMITTED TO THE MED BURN CENTERWITH SECOND DEGREE BURNS. A CUSTOMER SERVICE REPRESENTATIVE TESTED FOR ANDDETECTED NATURAL GAS IN THE WATER METER BOX. THE SERVICE AT 805 AYERS ST. WASBAR HOLED AND PRESSURE TESTED, BUT NO LEAK WAS DETECTED. FURTHER TESTINGDETERMINED THE LEAKING GAS WAS FROM TWO BELL JOINTS ON THE CAST IRON MAIN INAYERS ST. THE INCIDENT WAS REPORTED BY LEONARD PHILLIPS TO GLYNN BLANTON, TRAAND TO BLANCHARD, WASHINGTON, D.C. EMERGENCY RESPONSE CENTER, REPORT#417337.
2025-01-31 10:21 | NO | NO | 19980017 | 1998-01-21 | 2416 | CITIZENS UTILITY CO | 1741 N. GRAND AVENUE | NOGALES | SANTA CRUZ | AZ | 85621 | 4 | NO | 955 | 1997-11-26 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19971128 | 0 | 40 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | OTHER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | RUSSELL L. VALLEJO | 5207617967 | [6 empty] | Null |  | NO DATA |  | NO |  | YES | 0 |  | NO |  |  | SEE NARRATIVE ATTACHED TO REPORT.
2025-01-31 10:21 | NO | NO | 19980018 | 1998-01-12 | 15294 | PENSACOL, CITY OF | 109 ESCALONA AVENUE | PENSACOLA | ESCAMBIA | FL | 32503 | 3 | NO | 545 | 1997-12-09 | 0 | 0 | 45000 | 31822.6369 | 76834.7207 | Null | 0 | 40 |  | 19971209 | 55 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | RANGE CONNECTOR INSIDE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | DONALD E BAISDEN | 8504745316 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BASED ON INFORMATION PROVIDED BY THE PENSACOLA FIRE DEPARTMENT AND THE STATEFIRE MARSHALL, THE PROBABLE CAUSE OF THIS INCIDENT WAS A BROKEN RANGECONNECTOR THAT LEAKED GAS THAT IS PRESUMED TO HAVE IGNITED FROM THE RANGEPILOTS.
2025-01-31 10:21 | YES | NO | 19980026 | 1998-02-03 | 30750 | MIDAMERICAN ENERGY CO | 4205 SW PARK, BLDG. E 14 | DES MOINES | POLK | IA | 50321 | 4 | NO | 239 | 1997-12-23 | 0 | 0 | 150000 | 106075.4565 | 256115.7358 | Null | 1 | 10 |  | 19971223 | 10 | 10 | BY TEST | 10 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | NO DATA |  | NO DATA |  | 1 | 0.133 | METER | WESTINGHOUSE | 1975 | 1981 | ABOVE GROUND |  | FRANK DE LOUIS | 5152812457 | NO DATA | NO DATA |  | OTHER | ARSON | NO DATA | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE TELEPHONIC REPORT IS RETRACTED. THE CAUSE OF THE INCIDENT WAS NOT NATURALGAS FROM MID AMERICAN ENERGY COMPANY PIPING. IT WAS PROCLAIMED BY THE IOWASTATE FIRE MARSHALL TO BE CAUSED BY ARSON.
2025-01-31 10:21 | NO | NO | 19980047 | 1998-01-04 | 3110 | DANVILLE GAS DEPT | 148 WENDELL SCOTT DR. | DANVILLE |  | VA | 24540 | 3 | NO | 2330 | 1998-01-01 | 0 | 0 | 48000 | 33525.5271 | 80946.2936 | Null | 2 | 45 |  | 19980102 | 30 | 0 |  | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1958 | UNDER PAVEMENT |  | JAMES S. HARR , INTERIM DIRECTOR | 8047995280 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AT APPROXIMATELY 7:00 PM ON JANUARY 1, 1998, WATER AND GAS DISPATCH RECEIVED APHONE CALL FROM 148 WENDELL SCOTT DRIVE A STRONG GAS ODOR OUTSIDE OF THERESIDENCE. AT 7:10 PM, DARYL SMITH TECHNICIAN, ARRIVED AT THE SITE. UPONARRIVAL AT THE SITE, DARYLE WAS MET AT THE CURB BY A GENTLEMEN WHICH SHOWEDHIM A PLACE ALONG THE CURB WHERE THE GAS COULD BE SEEN BUBBLING THROUGH THEWATER RUNNING DOWN THE CURB. DARYL ASKED THE GENTLEMAN IF THEY HAD NOTICEDANY GAS SMELL INSIDE THEIR RESIDENCE. THE GENTLEMEN REPLIED NO. DARYLECALLED WATER AND GAS DISPATCH AT APPROXIMATELY 7:12 PM. AND ASKED THEM TOHAVE PAUL CROWDER, CONSTRUCTION SUPERVISOR, COME TO THE SITE. DARYLE CHECKEDAROUND THE FOUNDATION OF THE HOUSE, THE GAS METER , GAS SERVICE , AND WATERMETER BOX WITH A GAS DETECTION INSTRUMENT AND FOUND NO GAS. UPON ARRIVAL AT7:30 PM. PAUL BEGAN INSPECTING THE SITE IN ORDER TO MAKE REPAIRS. HE NOTICEDAN UNDERGROUND PHONE LINE. PAUL THEN CALLED DISPATCH TO HAVE THEM CONTACTTOGER LITTLE, CONSTRUCTION SUPERVISOR, TO HELP LOCATE THE GAS MAIN AND OTHERUNDERGROUND UTILITIES. AT APPROXIMATELY 8:20 PM, JIM HARR, DIRECTOR OF WATERAND GAS DISTRIBUTION ARRIVED AT THE SITE. AT APPROXIMATELY 8:20 SOMEONE FROMTHE RESIDENCE CAME OUTSIDE STATING THAT THEY HAD NO HEAT AND WANTED TO KNOWWHEN WE WOULD HAVE THE GAS TURNED BACK ON. PAUL AND JIM EXPLAINED THAT GASLEAK SHOULD HAVE NO EFFECT ON HER SERVICE. WHEN ASKED IF SHE HAD ANY OTHERAPPLIANCES WHICH RAN ON GAS, SHE REPLIED SHE HAS A COOK STOVE AND THAT THEYHAD TRIED IT AND IT WORKED. THEY INFORMED HER THAT WE WOULD HAVE THE SERVICETECHNICIAN RETURN. AT 8:25 PM, DARYLE SMITH RETURNED AND ENTERED AND ENTEREDTHE RESIDENCE TO CHECK THE FURNACE. HE WAS GREETED BY THE SAME GENTLEMAN ASHIS FIRST VISIT. DARYLE STATED THAT HE SMELLED NO ODOR INSIDE THE HOUSE.THE GENTLEMAN LED DARYLE TO THE BASEMENT WHERE HE LOCATED THE FURNACE ANDNOTICED THAT THE PILOT WAS OUT. HE LIT THE PILOT AND NOTICED THAT IT WAS NOTBURNING CORRECTLY AS IF THE PILOT ORIFICE WAS MISSING WHICH WAS CAUSING THEPILOT TO BE TOO HIGH AND THE FLAM WAS YELLOW. HE ALSO NOTICED ONE OF THECOMBUSTION CHAMBERS WAS STOPPED UP WITH SOOT CAUSING FUMES AROUND THEFURNACE. AT THET POINT, DARYLE TURNED OFF THE FURNACE AND NOTIFIED THECUSTOMER THAT THE FURNACE MUST BE CLEANED OUT. HE THEN TURNED THE GASS OFFTO THE FURNACE. THE GENTLEMAN AND HIS WIFE STATED MRS. GANT COULD STAY WITHTHEM FOR THE NIGHT AND THAT THEY WOULD BE LEAVING THE RESIDENCE SHORTLY. JIMHARR LEFT THE SITE AT APPROXIMATELY 9:30 PM. PAUL AND ROGER HAD CALLED INTWO CONSTRUCTION WORKERS AND STARTED ATTEMPTING TO PINPOINT THE LOCATION OFTHE LEAK. WHILE STILL ATTEMPTING TO LOCATE THE SOURCE OF THE LEAK, ANEXPLOSION OCCURRED AT APPROXIMATELY 11:30 PM. PAUL CONTACTED EMERGENCYSREVICES AND WATER AND GAS DISPATCH WHILE THE OTHER EMPLOYEES TURNED OFF GASTO WENDELL SCOTT DRIVE FROM THIRD AVENUE TO ARNETT BOULEVARK. THE FIREDEPARTMENT HAD THE FIRE EXTINGUISHED BY 2:30 AM. AT THAT TIME, AFTERDISCUSSION WITH THE FIRE DEPARTMENT, JIM HARR MADE THE DECISION NOT TO RESTOREGAS SERVICE OR ATTEMPT TO MAKE A REPAIR SINCE LOCATING THE LEAK WOULD REQUIRERESTORING GASS PRESSURE TO THE MAIN. IT WAS FELT THIS WOULD BE AN UNSAFESITUATION WITH THE FIRE STILL POSSIBLY SMOLDERING. INSTEAD THE REPAIR WOULDBE AFTER SUNRISE. AT 8:00 AM. ON JANUARY 2,1998 IM CONTACTED B.G. LEWIS, FIRECHIEF, WHO MET DOUG YOUNG, DIRECTOR OF EMERGENCY SREVICES , AND JIM HARR ATTHE SITE AT 8:20AM. IT WAS DECIDED TO EVALUATE THE RESIDENCE OF WENDELL SCOTTDRIVE FROM ARNETT BOULVARD TO THIRD AVENUE AND TO DISCONTINUE ELECTRIC SERVICE
2025-01-31 10:21 | NO | NO | 19980048 | 1998-01-30 | 15259 | PENNSYLVANIA GAS & WATER CO | INTERSECTION OF MAIN ST. & CHURCH ST. | DURYEA | LUZERNE | PA | 18641 | 3 | NO | 1710 | 1998-01-12 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 1 | 40 |  | 19980112 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.219 | GRADE B | UNKNOWN | 1966 | 1967 | UNDER PAVEMENT |  | JAMES M GREGER | 7128298835 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | PENNSYLVANIA POWER & LIGHT'S ELECTRIC HIGH VOLTAGE POWER LINE FELL TO THEGROUND AT THE INTERSECTION OF MAIN AND CHURCH STREETS. AT SAID INTERSECTION,PG ENERGY HAS A 6" INTERMEDIATE PRESSURE STEEL GAS MAIN. THIS GAS MAIN WASAPPROXIMATELY 4' DEEP. WHEN THE OVERHEAD HIGH VOLTAGE LINE FELL IT BEGANARCING AND WHILE DOING SO, CAME IN CONTACT WITH A WATER GATE BOX. AS A RESULTOF THIS CONTACT, 12000 VOLTS OF ELECTRICITY WAS TRANSFERRED TO SAID WATER GATEBOX WHICH ACTED AS A CONDUCTER DISCHARGING SAID VOLTAGE THROUGH ITSELF ANDONTO THE 6" STEEL GAS MAIN WHERE THE CURRENT AGAIN DISCHARGED CAUSING A 1/2"HOLE IN THE GAS LEAKAGE AND A FIRE.
2025-01-31 10:21 | YES | YES | 19980049 | 1998-01-29 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1803 HANKS | LUFKIN | ANGELINA | TX | 75904 | 3 | NO | 1115 | 1998-01-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 45 |  | 19980111 | 22 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2406 | DUPONT | 1977 | 1977 | UNDER GROUND OR UNDER WATER |  | MARK EARWOOD | 4096346656 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | YES | 0 |  | YES |  |  | THE CITY OF LUFKIN HAD BROKEN A 2 INCH PLASTIC MAIN WHILE ATTEMPTING TOREPAIR A WATER LINE ATTHE LOCATION. THE ENTEX SERVICEMAN RESPONDED ANDREALIZED IT WAS A MAIN. HE CALLED A CREW LEADER AT APPROXIMATELY 10:55 AM TOASK THAT A CREW COME OUT AND REPAIR THE LINE. AFTER BEING TOLD BY THE CREWLEADER NOT TO ENTER THE EXCAVATIION, THE SERVICEMAN HAD THE CITY DIP WATEROUT OF THE HOLE, THEN PUT ON HIS FLASH SUIT AND ENTERED THE HOLE IN ATTEMPTTO SQUEEZE OFF THE FLOW GAS. HE WAS APPARENTLY OVERCOME FROM GAS INHALATION.CITY PERSONEL PULLED HIM FROM THE HOLE AND ADMINSTERED CPR AND CALLED FORAMBULANCE. HE HAS FULLY RECOVERED AND HAS BEEN DISCHARGED FROM THE HOSPITAL.
2025-01-31 10:21 | YES | NO | 19980051 | 1998-02-09 | 30750 | MIDAMERICAN ENERGY CO | 5200 E P TRUE PARKWAY | WEST DES MOINES | DES MOINES | IA | 50266 | 4 | NO | 1001 | 1998-01-05 | 0 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 4 | 0 |  | 19980105 | 25 | 25 | BY TEST | 25 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | FRANK DELOUIS | 5152812457 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE CAUSE OF THE INCIDENT IS UNKNOWN AND THE INCIDENT IS STILL UNDER
2025-01-31 10:21 | NO | NO | 19980052 | 1998-02-10 | 22189 | PUGET SOUND ENERGY | 14312 W THORNE LANE SW | TACOMA | PIERCE | WA | 98498 | 3 | NO | 2025 | 1998-01-11 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 0 | 0 |  | 19980111 | 40 | 45 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | UNKNOWN | DOUGLAS DAMM | 2062242396 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | APARTMENT FIRE REPORTED TO OPERATOR BY LOCAL FIRE DEPARTMENT. THEY INDICATEDTHAT NATURAL GAS MAY BE INVOLVED. ACESS TO SITE DENIED. INVESTIGATION ISUNDERWAY, WITH NO CONCLUSION AT THIS TIME. ENCLOSED IS THE RSPA F 7100.0"INCIDENT REPORT - GAS DISTRIBUTION" FORM ON WHICH WE HAVE PROVIDED DETAILS OFAN INCIDENT THAT OCCURRED ON JANUARY 11,198 IN THE TILLICUM AREA OFUNICORPORATED PIERCE COUNTY, THAT RESULTED IN PROPERTY DAMAGE ESTIMATED TOEXCEED $50,000. THE PIERCE COUNTY FIRE DEPARTMENT REPORTED AN APARTMENT TOPUGET SOUND EMERGY'S OPERATIONS DISPATCH OFFICE AND INDECATED THAT NATURAL GASMAY BE INVOLVED. ON ARRIVAL PSE PERSONNEL FOUND THAT THE FIRE DEPARTMENTHAD TURNED OFF THE GAS TO THE APARTMENT BY CLOSING THE VALVE AT THE METERASSEMBLY. BECAUSE THE FIRE MARSHALL HAD INITIATED AND INVESTIGATION, WE WERENOT ALLOWED ACCESS. TO DATE CAUSATION HAS NOT BEEN DETERMINED. THEWASHINGTON UTILITIES AND TRANSPORTATION COMMISSION'S PIPELINE SAFETY HASREQUESTED INFORMATION FROM PSE REGUARDING THIS INCIDENT. BECAUSE PROPERTYDAMAGE TO THE APARTMENT IS ESTIMATED TO EXCEED $50,000 AND THE FIREDEPARTMENT INDICATED POSSIBLE NATURAL GAS INVOLVEMENT, THE NATIONAL RESPONSECINTER WAS NOTIFIED AT 22:35 HOURS GAS INVOLVMENT CENTER WAS NOTIFIED AT22:35 HOURS ON JANUARN ON JANUARY 11 1998 AS REQUIRED BY CFR 191.5 ASUPPLEMENTAL REPORT WILL BE SUBMITTED AS REQUIRED.
2025-01-31 10:21 | YES | YES | 19980053 | 1998-02-11 | 18416 | SOUTH COAST GAS CO INC | 5462 HWY 56 | CHAUVIN | TERREBONNE | LA | 70344 | 3 | NO | 720 | 1998-01-15 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 20 |  | 19980115 | 0.25 | 0 | BY TEST | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOM PIPING | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JACQUES ROTOLO | 5045375281 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A GAS VALVE ON THE CUSTOMER PIPING WAS OPEN IN THE KITCHEN, WHICH ALLOWEDNATURAL GAS TO ACCUMALATE IN THE DWELLING. THE IGNITION OF THE NATURAL GASWAS CAUSED BY THE OPERATION OF THE CENTRAL HEATING UNIT.
2025-01-31 10:21 | YES | YES | 19980054 | 1998-02-12 | 18536 | SOUTHWEST GAS CORP | 319 E. INDIAN SCHOOL RD. | PHOENIX | MARICOPA | AZ | 95012 | 3 | NO | 245 | 1998-01-15 | 0 | 1 | 714611 | 499118.9679 | 1205106.4961 | Null | 5 | 27 |  | 19980115 | 30 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PHILLIPS | 1992 | 1992 | UNDER PAVEMENT |  | PHILLIP S ANDREW | 6024845222 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-01-07 | YES | 3 | TEMPORARY PAINT | YES
2025-01-31 10:21 | YES | NO | 19980056 | 1998-02-18 | 15007 | PACIFIC GAS & ELECTRIC CO | 12137 FOLSOM BLVD | SACRAMENTO | SACRAMENTO | CA |  | 3 | NO | 1050 | 1997-12-29 | 0 | 0 | 100000 | 70716.971 | 170743.8238 | Null | 2 | 0 |  | 19971229 | 205 | 274 | BY TEST | 450 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 8 | 0.172 | API5LX42 ERW |  | 0 | 1987 | UNDER PAVEMENT |  | SHAN BHATTACHARYA | 4159736999 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-12-22 | YES | 3 | SURFACE MARKINGS | YES |  |  | DUE TO MAPPING IRREGULARITY, FACILITY WAS MARKED 57 INCHES AWAY FROM ITSLOCATION. MAP SHOWED LOCATION OF TEST LEADS INCORRECTLY & LOCATOR MARKED THEWRONG LINE. TWO LINES WERE IN THE AREA. INDICATOR MARKED ONE LINE TWICE.
2025-01-31 10:21 | YES | NO | 19980057 | 1998-02-19 | 18536 | SOUTHWEST GAS CORP | 5000 ARIZONA MILLS CIRCLE | TEMPE | MARICOPA | AZ | 85282 | 3 | NO | 1059 | 1998-01-26 | 0 | 0 | 163000 | 113847.1025 | 274880.122 | Null | 1 | 46 |  | 19980126 | 30 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | PIPE PULLED OUT MECHANICL | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PHILLIPS | 1997 | 1997 | UNDER PAVEMENT |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | GAS MAINS AND SERVICES WERE INSTALLED EARLY IN 1997 TO SERVE THE ARIZONAMILLES MALL. DURING SUBSEQUENT CONSTRUCTION ACTIVITY FOR THE MALL FACILITIES,ALONG 2" MAIN STUB SUFFERED SURFACE DAMAGE AND A FITTING WAS FORCEDLONGITUDINALLY ALONG THE MAIN, WHICH CREATED A LEAK PATH. THE LEAK WASDESCOVERED DURING A SCHEDULED LEAK SURVEY AND RESULTED IN EVACUATION OF ASMALL PORTION OF THE MALL. NO INJURIES OR SIGNIFICANT PROPERTY DAMAGEOCCURRED AS A RESULT OF THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 19980058 | 1998-02-23 | 4483 | ENSTAR NATURAL GAS CO | LOT 5 BLK 8 EAGLE RIVER HEIGHTS | EAGLE RIVER |  | AK | 99577 | 3 | NO | 1630 | 1998-02-13 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 1 | 0 |  | 19980213 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | NO DATA | PIPE PULLED OUT MECHANICL | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M8000 | PHILLIPS DRISCOPIPE | 1976 | 1976 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON FRIDAY AFTERNOON, FEBUARY 13, 1998 AT 4:30 PM AST, ENSTAR PERSONNEL WERECALLED TO RESPOND TO A HOUSE FIRE AT LOT 5, BLOCK 8, EAGLE RIVER HEIGHTS EAGLERIVER ALASKA. THE ORIGIN OF THE FIRE IS UNKNOWN. THE FIRE CONSUMED THE SINGLEFAMILY HOME AND IN THE PROCESS BURNED THE NATURAL GAS METER AND RISER. THE5/8" HDPE SERVICE LINE INSIDE THE STEEL RISER MELTED CAUSING A RELEASE OFNATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED. NATURALGAS DID NOT CONTRIBUTE TO THE CAUSE OF THE FIRE.
2025-01-31 10:21 | YES | NO | 19980059 | 1998-02-27 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | AUSTIN @CLAY ST (EAST DIST) | HOUSTON | HOUSTON | TX | 77002 | 3 | NO | 1207 | 1998-01-27 | 0 | 0 | 117492 | 82062.109 | 198136.2901 | Null | 7 | 53 |  | 19980127 | 35 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | PIPE PULLED OUT MECHANICL | CAST IRON |  | 16 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | JEFFREY A BISH | 7139678093 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-01-19 | YES | 3 | YELLOW PAINT | NO |  |  | REPORTED TO DEPARTMENT OF TRANSPORTATION2/3/98 14:48 MR. MASON
2025-01-31 10:21 | YES | NO | 19980061 | 1998-03-04 | 18536 | SOUTHWEST GAS CORP | 1495 GRINNEL AVE | LOVELOCK | PERSHING | NV | 89419 | 3 | NO | 1500 | 1998-02-04 | 0 | 0 | 247850 | 173110.4562 | 417969.5597 | Null | 3 | 30 |  | 19980205 | 27 | 43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | PIPE PULLED OUT MECHANICL | OTHER PLASTIC |  | 2 | 0.1 | 2110SCH A |  | 1965 | 1965 | UNDER PAVEMENT |  | LARRY GIBSON | 7024235554 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1997-07-30 | YES | 3 | MARKING PAINT | YES |  |  | THERE WAS CONSTRUCTION ACTIVICTIES FOR THE INSTALLATION OF A SEWER LINE DURINGJULY 1997. SEWER CROSSED UNDER AN EXISTING 2' PVC GAS MAIN. IMPROPERCOMPACTION AROUND A 2" SHORT STOP FITTING CAUSED A FAILURE ON THE 2" PVCMAIN. GAS MIGRATED INTO THE AREA OF TWO STORY HOME AND UNKNOWN IGNITIONSOURCE RESULTED IN DAMAGES. NO INJURIES RESULTED FROM THIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19980062 | 1998-03-04 | 10037 | WESTERN RESOURCES INC (AKA KPL CO. OR GAS SERVICE) | 5523 HADLEY | MERRIAM | JOHNS | KS | 66202 | 3 | NO | 1340 | 1997-10-03 | 0 | 1 | 110000 | 77788.6681 | 187818.2062 | Null | 2 | 30 |  |  | 20 | 68 | BY TEST | 110 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | POLYETHYLENE PLASTIC |  | 0.88 | 0 | 8000 | PHILLIP DISCO | 1995 | 1996 | UNDER PAVEMENT |  | JAMES M FALLON | 7852713910 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | PAINTED | YES |  |  | A 7/8 INCH PLASTIC SERVICE LINE WAS INADVERTENTLY INSTALLED BY A CONTRACTORTHROUGH A SANITARY SEWER LINE. WHILE PERFORMING MAINTENANCE CLEANING OF THESEWER, A THIRD PARTY CUT THE PLASTIC SERVICE LINE WHICH APPARENTLY ALLOWEDNATURAL GAS TO MIGRATE THROUGH A SEWER SERVICE LINE INTO THE STRUCTURE. ANUNKNOWN SOURCE IN THE STRUCTURE APPARENTLY IGNITED THE NATURAL GAS RESULTINGIN STRUCTURAL DAMAGE TO THE RESIDENCE AND INJURY TO ONE PERSON REQUIRINGOUT-PATIENT TREATMENT.
2025-01-31 10:21 | YES | YES | 19980064 | 1998-03-27 | 941 | NICOR EXPLORATION CO | 318 N DRYEN AVE | ARLINGTON HEIGHTS | COOK | IL | 60004 | 3 | NO | 1400 | 1998-03-04 | 0 | 1 | 150000 | 104767.2722 | 252957.1675 | Null | 0 | 50 |  | 19980304 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | GEORGE WALDVOGEL | 6309838676 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A DRYER FLEX CONNECTOR FAILED RESULTING IN A FIRE AND EXPLOSION INSIDE THEUTILITY ROOM AND KITCHEN AREA AT 318 N DRYDEN AVE.
2025-01-31 10:21 | YES | NO | 19980065 | 1998-03-13 | 12876 | QUESTAR GAS COMPANY | 7155 LITTLE BELLE COURT | PARK CITY | SUMMIT | UT | 84060 | 3 | NO | 1410 | 1998-02-24 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 0 | 30 |  | 19980224 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | METERS | 0 | 0 | ANSIB109.1 |  | 0 | 0 | ABOVE GROUND |  | EDWARD B KELSEY | 8013243619 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | ICE AND SNOW | Null |  | Null | 0 |  | Null |  |  | FOR YOUR INFORMATION, JUST PRIOR TO FEBRUARY 24, 1998. PARK CITY HAD RECEIVEDRECORD - BREAKING ACCUMALATIONS OF SNOW. ON FEBRUARY 24, 1998, ICE AND SNOWSLUFFED OF THE ROOF OF A CONDOMINIUM LOCATED AT 7155 LITTLE BELLE COURT, PARKCITY, UTAH, AND FELL APPROXIMATELY 18-20 FEET,LANDING ON A STEEP SLOPE ANDSLIDING IN A DOWNWARD DIRECTION INTO TWO METERS THAT WERE INSTALLED AT THESIDE OF THE CONDOMINIUM BUILDING. THE FORCE OF THE ICE STRIKING THE METERSCAUSED DAMAGE TO BOTH METERS, ALLOWING GAS TO ESCAPE. THE GAS MIGRATED INTOTHE CONDOMINIUM AND WAS INGNITED, CAUSING AN WXPLOSION AND FIRE. IT WASINITIALLY THOUGHT THAT THE RESULTING DAMAGE COULD EXCEED $200,000; HOWEVER,THE PARK CITY FIRE DEPARTMENT HAS DOWNGRADED THE DAMAGE TO AN ESTIMATED$100,000. THIS CONDOMINIUM HAS A ROOF OVERHANG OF APPROXIMATELY 30 INCHES.THE METERES WERE PLACED UNDER THIS OVERHANG AND WERE NOT ON THE SIDE OF THEBUILDING WHERE NORMAL SNOW AND / OR ICE WOULD FALL ONTO THEM. THE CONDOMINIUMWAS NOT OCCUPIED AT THE TIME OF THE EXPLOSION/FIRE, NO INJURIES WEREREPORTED. MR. AL ZADEH UTAH DIVISION OF PUBLIC SAFETY, PIPELINE SAFETYSECTION, FOR THE STATE OF UTAH, WAS PROMPTLY NOTIFIED AND HAS INVESTIGATEDTHIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19980066 | 1998-03-18 | 1209 | BAY STATE GAS CO | 59 GEORGE STREET | ATTLEBORO | BRISTOL | MA | 02703 | 3 | NO | 1011 | 1998-03-04 | 2 | 5 | 300000 | 209534.5445 | 505914.335 | Null | 2 | 19 |  | 19980304 | 0.25 | 0.5 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | TH | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | FW ST. CYR MANAGER ENGINEERING | 5085800100 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-03-02 | YES | 3 | TEMP PAINT ON STREET | YES |  |  | PIPELINE MARK ON STREET WAS NOT CORRECT.
2025-01-31 10:21 | YES | NO | 19980067 | 1998-04-03 | 2748 | CONSUMERS POWER CO | 8275 MAIN STREET | WHITMORE LAKE |  | MI | 48189 | 1 | NO | 1120 | 1998-02-26 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 1 | 50 |  | 19980226 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.062 | ASTM 2513 | PHILLIPS | 1991 | 1992 | UNDER GROUND OR UNDER WATER |  | ROBERT S WELSH, LEAD SENIOR ENGINEER | 5177880635 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | CONTRACTOR EXCAVTING FOR WATER LINE AND DAMAGED A 3/4" STEEL LINE. THESERVICE BROKE BELOW GROUND ON THE 5/8" PLASTIC SERVICE RISER TO THE METER.
2025-01-31 10:21 | YES | NO | 19980068 | 1998-03-31 | 15007 | PACIFIC GAS & ELECTRIC CO | 2108 SCHOOL STREET | PINOLE | CONTRA COSTA | CA | 94564 | 3 | NO | 914 | 1998-02-17 | 0 | 0 | 500000 | 349224.2408 | 843190.5583 | Null | 2 | 58 |  | 19980217 | 45 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | OTHER | COPPER | 0.5 | 0 |  |  | 0 | 1952 | UNDER PAVEMENT |  | SHAN BHATTACHARAYA, VICE PRESIDENT | 4159736998 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-02-03 | YES | 1 |  | YES |  |  | THE WATER COMPANY'S ( EAST BAY MUNICIPAL UTILITY DESRICT) CONSTRUCTIONPERSONNEL WHILE EXCAVATING A TRENCH WITH A BACKHOE PULLED A 1/2 INCH COPPERSERVICE OUT OF THE SERCICE TEE LOCATED ON A SIX INCH MAIN. THE ESCAPINGNATURE GAS MIGRATED UNDERNEATH THE ADJACEMT BUILDING WHICH SUBSEQUENTLYRESULTED IN A EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | NO | 19980078 | 1998-04-09 | 11032 | LACLEDE GAS CO | 732 BERGERAC DRIVE | CREVE COUER | ST LOUIS | MO | 63141 | 3 | NO | 2350 | 1998-03-13 | 0 | 0 | 190000 | 132705.2115 | 320412.4121 | Null | 8 | 0 |  | 19980314 | 21 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0.04 | ASTM B-88 |  | 0 | 1963 | WITHIN/UNDER BUILDING |  | PAUL B HUNKER | 3143420528 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE TEE CONNECTION TO THE MAIN. THE SERVICE LINE SECTION WAS REMOVED AND SENTFOR METALLURGICAL ANALYSIS TO DETERMINE THE CAUSE OF FAILURE IN ACCORDANCEWITH 192.617.
2025-01-31 10:21 | YES | YES | 19980079 | 1998-04-13 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 11105 BELLAIRE BLVD. (WEST DIST) | HOUSTON | HARRIS | TX | 77072 | 3 | NO | 1510 | 1998-03-11 | 0 | 2 | 0 | 0 | 0 | Null | 1 | 39 |  | 19980311 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | VALVE DISASSEMBLED | STEEL |  | 4 | 0 | API6D | ROCKWELL NORDSTOM | 0 | 1973 | ABOVE GROUND |  | JEFFREY A BISH-DIVISION | 7139678093 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO |  |  | AN ENTEX LOCK WAS CUT OFF A 4" SERVICE VALVE AND THE VALVE WAS DISASSEMBLEDRESULTING IN A RELEASE OF NATURAL GAS. THE NATURAL GAS WAS IGNITED AS ANATTEMPT TO MOVE A NEARBY VEHICLE.
2025-01-31 10:21 | YES | NO | 19980080 | 1998-04-13 | 2288 | CHATTANOOGA GAS CO | FLEETWOOD DRIVE | LOOKOUT MOUNTAIN | HAMILTON | TN | 37350 | 3 | NO | 1420 | 1998-03-24 | 0 | 0 | 250000 | 174612.1204 | 421595.2791 | Null | 0 | 50 |  | 19980324 | 28 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4.5 | 0.156 | API-5LB |  | 0 | 1955 | UNDER PAVEMENT |  | WESLEY J PITMAN | 4234904256 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A CONTRACTOR RUPTURED A 4" STEEL NATURAL GAS MAIN WITH A ROCK SAW WHILEINSTALLING A SEWER LINE. THE ESCAPING GAS IGNITED DAMAGING THE ROCK SAW.
2025-01-31 10:21 | YES | NO | 19980081 | 1998-04-17 | 1088 | BALTIMORE GAS & ELECTRIC CO | 10473 SCAGGSVILLE RD |  | HOWARD | MD | 20723 | 3 | NO | 1738 | 1998-03-31 | 0 | 0 | 400000 | 279379.3927 | 674552.4466 | Null | 1 | 25 |  | 19980401 | 85 | 100 | BY TEST | 150 | OTHER | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DENNIS C BLESSING | 4102985850 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | NO |  |  | ON 3/31/1998 WE RECEIVED A CALL FROM HOWARD COUNTY FD. OF A BUILDING FIRE.OUR SERVICE PERSON ARRIVED AT 17:59 AND REPORTED THAT THE BUILDING WAS FULLYINVOLVED AND THE GAS METER ISTALLATION WAS ON FIRE. IT COULD NOT BE TURNEDOFF AND SHE NEEDED SURVEY AND REPAIR TO CUT THE SERVICE OFF. THE SERVICE WASPINCHED OFF AT 19:24. WORKING WITH THE STATE FIRE MARSHALL ON 4/01/1998 ITWAS DETERMINED THAT NATURAL GAS WAS NOT THE CAUSE OF THE FIRE. THE CAUSE WASDERTERMINED TO BE SPONTANEOUS COMBUSTION FROM BAGS OF MULSH STORED UNDER AWOODEN PORCH.
2025-01-31 10:21 | YES | NO | 19980082 | 1998-04-17 | 12350 | MINNEGASCO INC | TOWN OF ST PETER | ST PETER | NICOLLET | MN | 56082 | 3 | NO | 1700 | 1998-03-29 | 0 | 0 | 75000 | 52383.6361 | 126478.5837 | Null | 2 | 30 |  | 19980330 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | EUGENE F SCHULTZ CODES & STDS ENGINEER | 6123214756 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TORNADO | Null |  | Null | 0 |  | Null |  |  | TORNADO UPROOTED TREES AND DEMOLISHED BUILDINGS. TREES AND BUILDING FELL ONMETER SETS AND REGULATOR STATIONS. TREE ROOTES DAMAGED MAINS AND SERVICE WHENTREES WENT DOWN.
2025-01-31 10:21 | YES | YES | 19980083 | 1998-04-17 | 11032 | LACLEDE GAS CO | 401 PRALLE LANE | ST CHARLES | ST CHARLES | MO | 63303 | 3 | NO | 1439 | 1998-03-17 | 0 | 2 | 100000 | 69844.8482 | 168638.1117 | Null | 7 | 50 |  | 19980317 | 16 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0 |  |  | 0 | 1961 | WITHIN/UNDER BUILDING |  | PAUL B HUNKER | 3143420528 | EXTERNALLY | GENERAL CORROSION |  | OTHER | CHEMICAL | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | VISUAL INSPECTION FOUND A CORROSION HOLE ON THE COPPER SERVICE LINE BODY ATTHE TEE CONNECTION TO THE MAIN SERVING 358 PRALLE LANE. THIS LOCATION WAS INTHE RIGHT OF WAY ADJACENT TO THE PROPERTY OF 401 PRALLE LANE. THE SERVICE LINESECTION WAS REMOVED AND SENT FOR SENT FOR METALLURGICAL ANALYSIS TO DETERMINETHE CAUSE OF FAILURE IN ACCORDANCE WITH 192.617
2025-01-31 10:21 | YES | YES | 19980086 | 1998-04-21 | 1184 | BAY CITY MUNICIPAL GAS SYSTEM | 3501 SEVENTH STREET | BAY | MATAGORDA | TX | 77414 | 3 | NO | 1715 | 1998-04-07 | 0 | 1 | 5000 | 3492.2424 | 8431.9056 | Null | 0 | 15 |  | 19980407 | 19 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | DAMAGED BY OCCUPANT | OTHER | COPPER TUBBING | 38 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | WILLIAM E ROE | 4092452311 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | OCCUPANT RENTED ROOM #36 OF THE FLAMINGO MOTEL AND ATTEMPTED TO COMMIT SUICIDEBY BLOCKING CEILING VENT WITH BATH TOWEL, CLOSING DOOR TO BATHROOM AND SEALINGDOOR WITH QUILT AND THEN ATTEMPTING TO REMOVE BATHROOM WALL HEATER WITHCRESENT WRENCH AND IN DOING SO HE BROKE CONNECTOR ALLOWING GAS INTO CONFINEDSPACE. IT APPEARS THAT HE THEN LIT A LIGHTER AND EXPLOSION AND SUBSEQUENTFIRE OCCURRED. OCCUPANT THEN RAN OUT OF THE MOTEL ROOM THROUGH THE FIREBURNING HIM OVER 95% OF HIS BODY. HE WAS LIFE FLIGHTED TO A BURN UNIT WHEREHE REMAINS AT THIS TIME. POLICE HAVE RULED THE INCIDENT AN ATTEMPTED SUCIDE.
2025-01-31 10:21 | YES | YES | 19980088 | 1998-04-28 | 15007 | PACIFIC GAS & ELECTRIC CO | US 101 .5 MILE SOUTH OF SOLEDAD PRISON | SOLEDAD | MONTEREY | CA |  | 3 | NO | 130 | 1998-03-15 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 17 |  | 19980315 | 60 | 60 | BY TEST | 102 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR SET | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 | RBS SMLS |  | 0 | 1952 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736998 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | YES |  |  | DRUNK DRIVER DROVE OFF U.S. 101, WENT THROUGH THE FREEWAY CHAIN LINK FENCE ANDHIT A GAS REGULATOR SET THAT WAS 30 FEET FROM THE DRY AND STRAIGHT ROADWAY.THE CAGE OVER THE SET WAS MOVED OFF BY THE VECHICLE. THE VEHICLE CONTINUEDANOTHER 5 FEET UNTIL IT WASSTOPPED BY A PRIMARY UTILITY POLE. THE CAR WASWRAPPED AROUND THE POLE. THE VEHICLE SNAPPED THE REGULATOR SET ON THEDOWNSTREAM SIDE; HOWEVER, THE UPSRTEAM VALVE WAS STILL OPERABLE AND USED TOSHUT OF THE GAS.
2025-01-31 10:21 | YES | NO | 19980104 | 1998-05-22 | 21190 | VERMONT GAS SYSTEMS INC | 22-26 HAYWARD STREET | BURLINGTON | CHITTENDEN | VT | 05402 | 3 | NO | 1730 | 1998-05-09 | 0 | 0 | 225000 | 157150.9084 | 379435.7512 | Null | 0 | 15 |  | 19980509 | 60 | 100 | BY TEST | 150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | BODY OF PIPE | THREADS | STEEL |  | 0.75 | 0.113 | A53 | MANIFOLD SITE BUILT | 1990 | 1990 | ABOVE GROUND |  | DAVID A ATTIG | 8028634511 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19980105 | 1998-06-01 | 15518 | PIEDMONT NATURAL GAS CO INC | 5814 RUDD STATION ROAD | BROWNS SUMMIT |  | NC |  | 3 | NO | 800 | 1998-05-01 | 1 | 2 | 100000 | 69844.8482 | 168638.1117 | Null | 1 | 0 |  | 19980501 | 60 | 75 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING | THREADS | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | STYLE 399 | DRESSER | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | RONALD W COBB | 7043643120 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-04-01 | YES | 3 | PAINT | YES
2025-01-31 10:21 | NO | NO | 19980106 | 1998-04-30 | 18536 | SOUTHWEST GAS CORP | 5035 SOUTH 20 PLACE | PHOENIX | MARICOPA | AZ | 85004 | 3 | NO | 1332 | 1998-04-05 | 0 | 0 | 70000 | 48891.3937 | 118046.6782 | Null | 0 | 58 |  | 19980405 | 30 | 40 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER | THREADS | OTHER | REGULATOR | 0 | 0 |  | RELIANCE | 1971 | 0 | ABOVE GROUND |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19980108 | 1998-05-07 | 18176 | SELMER NATURAL GAS SYSTEM | OAK AT POPLAR | SELMER | MCNAIRY | TN | 38375 | 2 | NO | 1058 | 1998-03-31 | 0 | 2 | 0 | 0 | 0 | Null | 3 | 0 |  | 19980331 | 15 | 36 | BY TEST | 54 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE | THREADS | STEEL |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RICHARD ASHE | 9016457928 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19980110 | 1998-05-13 | 13800 | NORTHERN UTILITIES INC (ALLIED GAS DIV) | SABBATUS @ EAST AVE | LEWISTON | ANDROSCOGGIN | ME | 04240 | 3 | NO | 200 | 1998-04-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 4 |  |  | 1.54 | 0.43 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | OTHER | DISTRICT REGULATOR CTRL | BODY OF PIPE | DAMAGED BY OCCUPANT | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE2406 | PLEXCO | 1990 | 1990 | UNDER PAVEMENT |  | CURTIS G BLAKE | 5088367250 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19980111 |  | 4483 | ENSTAR NATURAL GAS CO | LOT B 13, SEC 16, T18N, RE SM | MATANUSKA |  | AK | 99654 | 2 | NO | 1722 | 1998-04-24 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 1 | 43 |  | 19980424 | 55 | 60 |  | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER | DAMAGED BY OCCUPANT | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | PHILLIPS DRISCOPIPE | 1994 | 1994 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | NO | 19980112 | 1998-06-04 | 13280 | NEW HARMONY GAS DEPT, TOWN OF | 521 MAIN ST | NEW HARMONY | POSEY | IN | 47631 | 3 | NO | 1000 | 1998-05-11 | 0 | 0 | 500000 | 349224.2408 | 843190.5583 | Null | 0 | 30 |  | 19980511 | 16 | 16 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING | DAMAGED BY OCCUPANT | STEEL |  | 1 | 0.133 | API5L |  | 0 | 1957 | OTHER | UNDER CONCRETE | KARLA L ATKINS | 8126824846 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | YES | 3 | PAINT | YES
2025-01-31 10:21 | YES | YES | 19980116 | 1998-06-15 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 210 CHURCH STREET | FREDERICKSBURG | SPOTSYLVANIA | VA | 22408- | 1 | NO | 718 | 1998-05-16 | 1 | 0 | 120000 | 83813.8178 | 202365.734 | NO | 0 | 27 |  | 19980516 | 56 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.05 | 0.09 | PE2306 | PLEXCO | 1977 | 1979 | UNDER GROUND OR UNDER WATER |  | NORMAN G DUREN | 8043235312 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1998-05-11 | YES | 0 |  | YES | NO DATA |  | THE OWNER OF THE HOME AT 210 CHURCH STREET OR HIS REPRESENTATIVE DROVE A GROUND ROD THROUGH THE PLASTIC SERVICE LINE SERVING THE 210 CHURCH STREET ADDRESS. GAS ESCAPED FROM THE SERVICE LINE (AS A RESULT OF THE UNDERGROUND FACILITY DAMAGE), MIGRATED INTO THE STRUCTURE, WAS IGNITED, AND AN EXPLOSION LEVELED THE STRUCTURE, SEVERELY BURNING THE OCCUPANT. THE STRUCTURE IN QUESTION HAD NO POWER. THE OWNER OF THE STRUCTURE WAS IN THE PROCESS OF REMODELING THE STRUCTURE. THE INDIVIDUAL WAS UTLIZING TEMPORARY POWER PROVIDED BY AN ELECTRICAL EXTENSION CORD COUPLED TO AN OUTLET LOCATED AT A RESIDENCE NEXT DOOR TO THE HOME IN QUESTION. THE OWNER WAS UTILIZING AN ELECTRICAL SAW INSIDE THE STRUCTURE, WHEN THE EXPLOSION AND FIRE OCCURRED. COLUMBIA GAS OF VIRGINIA BELIEVES THE SOURCE OF IGNITION TO BE THE ELECTRICAL SAW. A REQUEST FOR LOCATING AND MARKING HAD BEEN PROVIDED TO THE ONE CALL NOTIFICATION CENTER, FOR THE PURPOSE OF DRIVING GROUND RODS AT THE ADDRESS OF THE INCIDENT. A CONTRACT LOCATING COMPANYING (NOCUTS) ENGAGED BY COLUMBIA GAS OF VIRGINIA, APPARENTLY MIS-MARKED THE LOCATION OF THE GAS SERVICE TO 210 CHURCH STREET
2025-01-31 10:21 | YES | NO | 19980117 | 1998-06-11 | 30769 | MISSOURI GAS ENERGY | 301 W 13TH STREET | KANSAS CITY | JACKSON | MO | 64105 | 4 | NO | 2203 | 1998-05-15 | 0 | 0 | 212641 | 148518.7836 | 358593.767 | Null | 0 | 22 |  | 19980515 | 55 | 58 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | THREADS | STEEL |  | 2 | 0 |  |  | 0 | 1993 | ABOVE GROUND |  | WILLIAM DEAN | 8163605661 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | YES | 19980118 | 1998-06-15 | 10320 | KOKOMO GAS & FUEL CO | 1644 WEST 300 NORTH | KOKOMO | HOWARD | IN | 46902 | 0 | NO | 1036 | 1998-05-21 | 0 | 1 | 500 | 349.2242 | 843.1906 | Null | 1 | 0 |  | 19980525 | 40 | 0 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | NO DATA | THREADS | STEEL |  | 1.25 | 0 |  |  | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | EDWARD L BROWN | 7654594101 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 19980121 | 1998-06-22 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 427 JEFFERSON STREET | MOUNT LEBANON | ALLEGHENY | PA | 15102 | 4 | NO | 806 | 1998-04-20 | 0 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 0 | 20 |  | 19980420 | 25 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0 | BARE STEEL | UNKNOWN | 1893 | 1893 | UNDER GROUND OR UNDER WATER |  | ROBERT T BURROWS | 4125727107 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | COLLAPSE OF LARGE MATURE | Null |  | Null | 0 |  | Null |  |  | THERE WERE NO INJURIES ASSOCIATED WITH THE EXPLOSION AND FIRE THAT CAUSEDDAMAGE IN EXCESS OF $50,000 WITH TOTAL DAMAGES ESTIMATED AT $200,000. THISFAILURE WAS A RESULT OF A LARGE MATURE TREE THAT COLLAPSED CAUSING COLUMBIA'S4-INCH BARE STEEL MEDIUM PRESSURE PIPELINE TO FAIL AT AN ADJACENT LOCATIONTHAT PASSED THROUGH A SEWERE MAIN. THE SEWER DROP HAD BEEN INSTALLED AROUNDOUR MEDIUM PRESSURE LINE WITHOUT OUR KNOWLEDGE. THE 4-INCH MAIN WITHIN THESEWER MANHOLE FAILED AS A RESULT OF ADDITIONAL STRESS CAUSED BY THE ROOT OFTHE FALLEN TREE ON THE ADJACENT PIPELINE RESULTING IN THE INTRODUCTION OF GASINTO THE SEWER SYSTEM THAT SUBSEQUENTLY ENTERED HOMES ALONG JEFFERSON.
2025-01-31 10:21 | YES | YES | 19980122 | 1998-06-23 | 13041 | NASHVILLE GAS CO | CHICKASAW DRIVE | BRENTWOOD | WILLIAMSON | TN | 37027 | 2 | NO | 945 | 1998-05-20 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 15 |  | 19980520 | 98 | 125 | BY TEST | 265 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | BYPASS LINE CONNECTION | FITTING |  | OTHER | MALLEABLE IRON COUPLING | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JOHN L CLARK JR | 6157341709 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | BYPASS LINE FOR ROUTINE MAIN REPAIR BECAME DISCONNECTED FROM UPSTREAM MACHINEAND GAS RELEASE WAS IGNITED BY WELDER'S TORCH.
2025-01-31 10:21 | YES | NO | 19980123 | 1998-06-23 | 15358 | PEOPLES NATURAL GAS CO | 7150 ALEGRE CIRCLE | EL PASO |  | CO | 80817 | 3 | NO | 1500 | 1998-06-15 | 0 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 0 | 5 |  | 19980616 | 25 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CAST ALUMINUM | 0 | 0 |  | ROCKWELL | 0 | 0 | WITHIN/UNDER BUILDING |  | GEORGE M PETERSON | 7193923818 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | GAS REGULATOR WAS TAMPERED WITH AND DAMAGED BY CHILDREN CAUSING IT TO STICKOPEN AND OVERPRESSURE HOUSE PIPING SYSTEM.
2025-01-31 10:21 | NO | NO | 19980125 | 1998-06-24 | 792 | ATLANTA GAS LIGHT CO | US 41 SOUTH OF I-285 | SMYRNA | COBB | GA | 30339 | 3 | NO | 1423 | 1998-05-27 | 0 | 0 | 55000 | 38414.6665 | 92750.9614 | Null | 0 | 33 |  | 19980527 | 180 | 300 | BY TEST | 500 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6.625 | 0.188 | API-5L B | UNKNOWN | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | PHYLLIS W STALLINGS | 7704235720 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-05-12 | NO | 0 |  | YES |  |  | A CONTRACTOR RUPTURED A 6" STEEL NATURAL GAS MAIN WITH A TRACKHOE WHILEWIDENING THE HIGHWAY.
2025-01-31 10:21 | YES | YES | 19980127 | 1998-06-30 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 217-26 75TH AVE | NEW YORK | QUEENS | NY | 11361 | 4 | NO | 923 | 1998-06-16 | 0 | 1 | 10000 | 6984.4848 | 16863.8112 | YES | 0 | 7 |  | 19980616 | 58 | 80 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.25 | D-2513 | DRISCOPIPE | 1996 | 1996 | UNDER GROUND OR UNDER WATER |  | ANTHONY B CODNER | 2124601103 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A CONTRACTOR, WORKING ON THE INSTALLATION OF A SPRINKLER SYSTEM SEVERED A 2"HIGH-PRESSURE SERVICE WITH A DITCH WITCH. THE SERVICE SUBSEQUENTLY IGNITED.THERE WAS NO MARKOUTS AS PER CODE 753.
2025-01-31 10:21 | NO | NO | 19980128 | 1998-06-30 | 18536 | SOUTHWEST GAS CORP | 1109 WEST GROVE PKWY | TEMPE | MARICOPA | AZ | 85283 | 3 | NO | 258 | 1998-06-03 | 0 | 0 | 12915 | 9020.4621 | 21779.6121 | YES | 3 | 15 |  | 19980603 | 30 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.318 | ASTM D2513 | PHILLIPS | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | YES | 19980129 |  | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 7418 ESTATES WAY | ROWLETT | DALLAS | TX | 75088 | 3 | NO | 1516 | 1998-05-12 | 0 | 2 | 0 | 0 | 0 | YES | 0 | 0 |  | 19980512 | 18 | 55 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE-2306 | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2146702986 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | CONTRACTOR WAS IN THE PROCESS OF INSTALLING A BAND | A CONTRACTOR WAS IN THE PROCESS OF INSTALLINGA BAND CLAMP WHEN GAS IGNITED.
2025-01-31 10:21 | YES | YES | 19980133 | 1998-06-22 | 6790 | GREENVILLE UTILITIES COMMISSION | 719 HOOKER ROAD | GREENVILLE | PITT | NC | 27835 | 3 | NO | 1605 | 1998-06-02 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 17 |  | 19980602 | 48 | 50 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD2513 | PLEXCO | 1995 | 1998 | UNDER GROUND OR UNDER WATER |  | CHRISTOPHER P WROCKLAGE | 2525511592 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DURING A ROUTINE PURGING OF AIR WITH GAS, IGNITION OF THE EXIT GASES OCCURREDBY UNKNOWN CAUSE.
2025-01-31 10:21 | YES | NO | 19980134 | 1998-07-06 | 22182 | WASHINGTON GAS LIGHT CO | 11709 NORTH MARLTON AVE | UPPER MARLBORO |  | MD | 20772 | 3 | NO | 351 | 1998-06-02 | 0 | 0 | 250000 | 174612.1204 | 421595.2791 | Null | 2 | 9 |  | 19980602 | 50 | 55 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  | AMERICAN | 1996 | 1996 | WITHIN/UNDER BUILDING |  | JOHN H FLUHARTY | 2026246059 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | NO | 19980135 | 1998-07-02 | 13850 | NORTHWESTERN PUBLIC SERVICE CO |  | SPENCER | MCCOOK | SD | 57374 | 3 | NO | 2044 | 1998-05-30 | 0 | 0 | 75000 | 52383.6361 | 126478.5837 | YES | 0 | 36 |  | 19980531 | 22 | 30 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | EDWIN HIGHLAND | 6053537510 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TORNADO | Null |  | Null | 0 |  | Null |  |  | TORNADO STRUCK SPENCER S.D. DESTROYING METER FITS.
2025-01-31 10:21 | YES | NO | 19980141 | 1998-07-16 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1900 STATE ST @ SILVER EAST DIST | HOUSTON | HARRIS | TX | 77007 | 3 | NO | 1554 | 1998-06-23 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 2 | 15 |  | 19980623 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 |  | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | JEFFREY A BISH | 7139678093 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-05-22 | YES | 2 |  | NO |  |  | THIRD PARTY INSTALLING WATER LINE HIT & DAMAGED 2" IP PLASTIC MAIN CAUSING GASTO ESCAPE & IGNITE.
2025-01-31 10:21 | YES | YES | 19980142 | 1998-07-16 | 1209 | BAY STATE GAS CO | 55 HOOD STREET | SPRINGFIELD | HAMPDEN | MA | 01104 | 4 | NO | 215 | 1998-07-01 | 0 | 1 | 115000 | 80321.5754 | 193933.8284 | Null | 1 | 0 |  | 19980701 | 0.33 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE PIPING | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | MICHAEL KNODLER | [7 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE HOMEOWNER ATTEMPTED SUICIDE BY TAKING A NIP AND CAP OFF AN INSIDE HOUSELINE AT THE FURNACE. THE HOUSE BLEW UP CAUSING HIS INJURIES AND THEDESTRUCTION OF HOUSE.
2025-01-31 10:21 | NO | NO | 19980145 | 1998-07-27 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 911 MCCLURE RD | MEMPHIS | SHELBY | TN | 38116 | 3 | NO | 1100 | 1998-07-02 | 0 | 0 | 70000 | 48891.3937 | 118046.6782 | Null | 1 | 0 |  | 19980702 | 85 | 99 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | LEONARD PHILLIPS | 9013201401 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | PRIVATE VEHICLE LEFT THE ROADWAY AND STRUCK THE NORTWEST CORNER OF THERESIDENCE LOCATED AT 911 MCCLURE RD. THE COLLISION DESTROYED THE GAS METERCENTER, RELEASING AND IGNITING GAS UNDER AND AROUND THE HOUSE AT THE POINT OFIMPACT. THE FIRE DESTROYED THE VEHICLE AND SUBSTANTIALLY DAMAGED THE HOME.THE FIRE MARSHALL PROVIDED THE ESTIMATE OF DAMAGE.
2025-01-31 10:21 | YES | NO | 19980146 | 1998-07-13 | 13580 | NORTH CAROLINA NATURAL GAS CORP | 234 CALHOUN DRIVE | WILMINGTON | NEW HANOVER | NC | 28401 | 3 | NO | 2010 | 1998-06-16 | 0 | 0 | 80000 | 55875.8785 | 134910.4893 | Null | 1 | 40 |  | 19980616 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC |  | 0.75 | 0.09 | N311PU | KRALOY | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | TED HODGES | 9103236249 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | SERVICE LINE WAS CUT BY MR. KEITH COLLINS WHILE DIGGING. GAS MIGRATED INTOTHE HOUSE AND WAS IGNITED.
2025-01-31 10:21 | NO | NO | 19980149 | 1998-07-21 | 20211 | UNITED CITIES GAS CO | HOLLY STREET AT C STREET | ELIZABETHTON | CARTER | TN | 37643 | 3 | Null | 1238 | 1998-06-18 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 19980618 | 30 | 30 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | BOBBY W COX | 4234611803 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | YES |  |  | THIS WAS NOT A REPORTABLE INCIDENT DUE TO NO PROPERTY DAMAGED OTHER THAN2'SECTION OF 2" PLASTIC MAIN. ALSO, NO INJURIES OCCURRED. THE CALL WAS MADEIN ORDER TO REPORT WITHIN TWO HOUR TIME LIMIT; OPERATOR WAS UNSURE OF EXTENTOF DAMAGE OR INJURIES AT THAT TIME. DUE TO FIRE DID NOT KNOW IF FIRE WOULDSPREAD TO STRUCTURES OR EQUIPMENT.
2025-01-31 10:21 | YES | YES | 19980150 | 1998-08-18 | 18116 | SAN JUAN GAS CO | PONCE DE LEON AT AVE A | SANTURCE |  | PR | 00907 | 4 | NO | 430 | 1998-07-11 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 5 |  | 19980711 | 25 | 60 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | STEEL |  | 6 | 0 |  |  | 0 | 0 | OTHER | IN AN EXCAVATION | ROBERTO RIOS | 7877222250 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION
2025-01-31 10:21 | NO | NO | 19980153 | 1998-08-07 | 8070 | INDIANA GAS CO INC | 310 COUNTY LINE RD | ATLANTA |  | IN | 46031 | 3 | NO | 1900 | 1998-07-11 | 0 | 0 | 70000 | 48891.3937 | 118046.6782 | Null | 2 | 0 |  | 19980711 | 60 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 1.25 | 0.025 | GRADE B |  | 1949 | 1950 | UNDER GROUND OR UNDER WATER |  |  | 3173210518 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-06 | YES | 0 |  | YES |  |  | AN 1 -1/4 STEEL SERVICE WAS PULLED FROM A DRESSER COUPLING ALLOWING NATURALGAS TO INFILTRATE THE STORM SEWER AND ULTIMATELY THE STRUCTURE AT 310 COUNTYLINE RD IN ATLANTA, IN. THE GAS WAS IGNITED BY AN UNIDENTIFIED IGNITIONSOURCE, WHICH RESULTED IN A EXPLOSION AND FIRE. A REQUEST FOR FACILITYLOCATES WAS MADE BY THE INDIVIDUAL DOING THE CONSTRUCTION. THE INDIANA GASINVESTIGATION INTO THIS INCIDENT REVEALS THAT ALL INDIANA GAS FACILITIES ONTHE PROPERTY NOTED ABOVE WERE NOT CORRECTLY LOCATED. APPROPRIATE STEPS AREBEING TAKEN TO REMEDY THE SITUATION SO THAT SIMILAR SITIUATION MIGHT NOT OCCUR.
2025-01-31 10:21 | YES | YES | 19980154 | 1998-08-07 | 8070 | INDIANA GAS CO INC | 1013 LINDEN DR | LAFAYETTE | TIPPECANOE | IN | 47905 | 3 | NO | 1230 | 1998-07-15 | 1 | 0 | 70000 | 48891.3937 | 118046.6782 | Null | 0 | 15 |  | 19980715 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINE | OTHER | NONE | OTHER | COPPER | 0.375 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  |  | 3173210518 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER FUEL LINE FOUND TO BE OPEN. ALL INDIANA GAS CO. FACILITIES OK.
2025-01-31 10:21 | YES | YES | 19980155 | 1998-08-03 | 1086 | BALTIMORE CITY, HOUSING AUTH OF | 6939 REISTERSTOWN RD | BALTIMORE |  | MD | 21215 | 3 | NO | 2320 | 1998-07-23 | 0 | 1 | 0 | 0 | 0 | Null | 5 | 37 |  | 19980723 | 6 | 10 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | NO DATA | NONE | POLYETHYLENE PLASTIC |  | 16 | 0.5 |  |  | 0 | 1957 | UNDER GROUND OR UNDER WATER |  | DENNIS BLESSING | 4102915850 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 2320 HOURS WHILE REPLACING 1 1/4 TEE ON 16' CAST IRON MAINTHE GAS IGNITED. TWO POSSIBLE SOURCES OF IGNITION ARE BEING INVESTIGATED.ONE SOURCE IS A HALOGEN LIGHT USED BY THE CREW AND THE OTHER SOURCE IS STATICELECTRIC CHARGES FROM THE PLASTIC PIPE. A BALTIMORE GAS ELECTRIC EMPLOYEEWORKING IN THE EXCAVATION WAS BURNT AND WAS TRANSPORTED TO BAYVIEW HOSPITAL INCRITICAL CONDITION.
2025-01-31 10:21 | YES | YES | 19980170 | 1998-08-18 | 920 | NATGAS INC. | 402 AVE J | OZONA | CROCKETT | TX | 76943 | 1 | NO | 830 | 1998-08-05 | 0 | 3 | 50000 | 34922.4241 | 84319.0558 | Null | 0 | 30 |  | 19980805 | 502 | 60 | BY TEST | 60 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUSE | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | OTHER | UNDER HOUSE | ED HALE | 9153922201 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CUSTOMER SMELLED GAS IN HOUSE, OPENED WINDOW AND LIGHT LIGHTER TO FIND LEAK.HOUSE EXPLODED.
2025-01-31 10:21 | YES | NO | 19980171 | 1998-08-19 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 8 MILES SOUTHEAST OF TUCUMCARI | TUCUMCARI | QUAY | NM | 88401 | 1 | NO | 920 | 1998-07-20 | 0 | 0 | 75000 | 52383.6361 | 126478.5837 | Null | 1 | 50 |  | 19980720 | 250 | 300 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | GRADE B |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DOUGLAS J. BEEVERS | 5054612715 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THIRD PARTY OPERATING MAINTAINER GRADING BARDITCH CUT MAINLINE 8 MILESSOUTHEAST OF TUCUMCARI NEAR CANAL CROSSING. PNM GAS SERVICE'S SOLE NATURAL GASDISTRIBUTION PIPELINE SUPPLYING THE TOWN OF TUCUMCARI, NM, WAS DAMAGED BY ATHIRD PARTY APPROXIMATELY 8 MILES SOUTHEAST OF TOWN. THE EMERGENCY REPAIROF THE PIPELINE WAS NOT ACCOMPLISHED IN TIME TO CONTINUE SUPPLYING THE TOWN.APPROXIMATELY 2,700 CUSTOMERS WERE WITHOUT NATURAL GAS SERVICE FROM ONE TOTHREE DAYS, DUE TO THE TIME IT TOOK TO PURGE THE PIPELINE SYSTEM AND RELIGHTEACH INDIVIDUAL CUSTOMER.
2025-01-31 10:21 | YES | YES | 19980172 | 1998-08-19 | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | 100 BLOCK OF LAKE SUMMIT DRIVE | CHAPIN | LEXINGTON | SC | 29036 | 3 | NO | 1005 | 1998-08-12 | 0 | 2 | 0 | 0 | 0 | Null | 2 | 10 |  | 19980812 | 10 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | ASTM D-2513 | PLEXCO | 1988 | 1988 | UNDER GROUND OR UNDER WATER |  | STUCKEY J.STOUDMIRE | 8032179860 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-30 | YES | 3 | YELLOW PAINT | YES |  |  | A THIRD PARTY UTILITY CONTRACTOR DAMAGED A FOUR INCH PLASTIC DISTRIBUTION MAINWHILE INSTALLING A FIBER OPTIC TELEVISION CABLE. SCE&G'S RESPONDING EMPLOYEESATTEMPTED TO SLOW THE FLOW OF ESCAPING GAS BY INSTALLING A SPLIT SLEEVE/CLAMPOVER THE 2 1/2 BY 5 INCH TEAR. WHILE IN THE PROCESS OF DOING THIS, ANAPPARENT STATIC ELECTRICITY DISCHARGE IGNITED THE BLOWING GAS. CONSEQUENTLY,FIVE EMPLOYEES WERE BURNED RESULTING IN THE HOSPITALIZATION OF TWO.
2025-01-31 10:21 | YES | YES | 19980173 | 1998-08-24 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 816 CENTER ST | PASADENA | HARRIS | TX | 77506 | 3 | NO | 930 | 1998-07-20 | 1 | 3 | 95000 | 66352.6058 | 160206.2061 | YES | 0 | 48 |  | 19980720 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1937 | UNDER GROUND OR UNDER WATER |  | JEFFREY A. BISH | 7139678093 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-10 | YES | 0 |  | Null |  |  | THIRD PARTY CONTRACTOR PULLED A MARKED 1 1/4' L.P. STEEL SERVICE LINE, SERVING815 CENTER ST FROM A 2' L.P. STEEL MAIN LINE. GAS MIGRATED TO 816 CENTERWHERE AND EXPLOSION & FIRE OCCURRED.
2025-01-31 10:21 | NO | NO | 19980174 | 1998-08-11 | 31148 | SIENERGY, LP | 9722 HAVILAND |  | FORT BEND | TX | 77459 | 3 | NO | 1915 | 1998-07-08 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 |  | 19980709 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | PE2406 | UPONOR ALDYL | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | RICHARD L. HERWECK | 5124489099 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-06-30 | NO | 0 |  | YES |  |  | ACCORDING TO "NOTICE OF INTENT TO EXCAVATE" DIGGING WAS TO BEGIN 7//14/1998.ONE WEEK AFTER DAMAGE LINE LOCATION WAS SCHEDULED 7/13/1998.
2025-01-31 10:21 | NO | NO | 19980177 | 1998-08-28 | 18536 | SOUTHWEST GAS CORP | CENTINIAL PARK ROAD SOUTH OF HWY 60 | WENDEN |  | AZ | 85357 | 2 | NO | 930 | 1998-07-29 | 0 | 0 | 22928 | 16014.0268 | 38665.3462 | Null | 1 | 55 |  | 19980729 | 485 | 496 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 1973 | 1973 | UNDER GROUND OR UNDER WATER |  | PHILLIP S. ANDREWS | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | A TRENCHER WAS EXCAVATING NEAR WENDEN, ARIZONA, WHEN IT DAMAGED A 2"HIGH-PRESSURE STEEL PIPELINE. THE EXCAVATOR WAS TRENCHING WITHOUT A LINELOCATE REQUEST. AS A RESULT OF THE DAMAGE, 439 CUSTOMERS WER TEMPORARILY OUTOF SERVICE. THE LINE IS MARKED WITH PERMANENT LINE MARKERS IN ACCORDANCE WITH49 CFR, PART 192.707. THIS MAIN WAS ACQUIRED BY ARIZONA PUBLIC SERVICE FROMEL PASO NATURAL GAS IN 1973.
2025-01-31 10:21 | YES | YES | 19980179 |  | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 1032 SPRING CREEK | DENTON | DENTON | TX | 76201 | 3 | NO | 1550 | 1998-07-30 | 0 | 1 | 30000 | 20953.4544 | 50591.4335 | YES | 0 | 50 |  | 19980730 | 54 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | PLEXCO | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | RON HASKOVEC | 2148122469 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-17 | YES | 3 | FLAGS AND PAINT | NO |  |  | A BACKHOE CUT INTO A 2 INCH POLY PIPE, RESULTING IN GAS IGNITION. THE BACKHOEDRIVER WAS INJURED AND THE BACKHOE WAS DAMAGED DUE TO THE FIRE.
2025-01-31 10:21 | NO | NO | 19980180 |  | 22189 | PUGET SOUND ENERGY | SR 526 & 44 AVE W | MUKILTEO | SNOHOMISH | WA | 98275 | 3 | NO | 1522 | 1998-07-31 | 0 | 0 | 51885 | 36238.9995 | 87497.8842 | Null | 4 | 20 |  | 19980821 | 240 | 320 | BY TEST | 448 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 8.62 | 0.188 | GRADE B |  | 0 | 1966 | OTHER | EXPOSED IN EXCAVATION | DOUGLAS DAMM | 2062242396 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1996-04-01 | YES | 2 |  | YES |  |  | ROAD IMPROVEMENT CONTRACTOR STRUCK 3/4" TEE ON A 8" SUPPLY MAIN (240 PSIG)WHILE REMOVING UNSUITABLE MATERIAL. CONTRACTOR THOUGHT LINE WAS ABANDONED,SIMILAR TO PIPE NEARBY. LINE WAS ACTIVE. REPAIR REQUIRED REDUCTION OFPRESSURE TO 150 PSIG. TEMPORARY CLAM INSTALLED, FOLLOWED BY PERMANENT REPAIRLATER. FOR ADDITIONAL INFORMATION SEE ATTACHED REPORT. A CONTRACTOR WASREMOVING UNSUITABLE MATERIAL AS PART OF A ROAD IMPROVEMENT PROJECT JUST WESTOF THE BOEING PLAT ON STATE ROUTE (SR) 526, ALSO KNOWN AS 84 ST SW, AT THEINTERSECTION OF 44 AV W IN SNOHOMISH COUNTY. THEY HAD EXCAVATED ABOUT 30" OFMATERIAL WHEN THEY ENCOUNTERED A PIECE OF 8" GAS PIPE THAT HAD BEEN ABANDONEDPREVIOUSLY TO ACCOMMODATE THE ROAD IMPROVEMENT. AS THEY CONTINUED TO EXPANDTHE AREA OF UNSUITABLE MATERIAL REMOVAL THEY EXPOSED ANOTHER 8" PIPE THAT THEYALSO ASSUMED WAS ABANDONED ALTHOUGH THIS MAIN WAS ACTIVE. THEY CONTINUED TOEXPOSE THE LINE WITHOUT TAKEN PRECAUTIONS, AND FINALLY A 3/4" TEE WAS BROKENOFF THE 8" MAIN, WHICH WAS A SUPPLY MAIN OPERATING AT 240 PSIG. IN ORDER TOSAFELY INSTALL A TEMPORARY REPAIR SLEEVE, PRESSURE IN THE LINE WAS REDUCED TO150 PSIG, WITH NO IMPACT ON CUSTOMERS. THIS TOOK APPROXIMATELY 3 1/2 HOURS,DURING WHICH TIME THE SURROUNDING AREA WAS SECURED AND MONITORED BY PSEPERSONNEL AND LOCAL FIRE AND POLICE AGENCIES. THE REPAIR SLEEVE WAS THEINSTALLED. THE PERMANENT REPAIR OF THE DAMAGED LINE BEGAN ON AUGUST 5, 1998AND WAS COMPLETED AT 18:00 HOURS ON AUGUST 8TH. THERE WERE NO EVACUATIONS,CUSTOMER LOSSES OR INJURIES, NOR WAS ANY PROPERTY DAMAGED EXCEPT FOR THE 8"GAS MAIN. THE TOTAL COST OF THE INCIDENT IS NOW ESTIMATED TO BE $51,885.THIS INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AT 9:25 HRS ONAUGUST 21, 1998. LT. HUDSPETH TOOK THE CALL AND ASSIGNED REPORT NUMBER451611. THE DELAY IN NOTIFICATION WAS BECAUSE WE SIGNIFICANTLY UNDERESTIMATEDTHE COST OF LOST GAS.
2025-01-31 10:21 | YES | NO | 19980181 |  | 21349 | VIRGINIA NATURAL GAS | 102 PHEASANT WATCH |  | YORK | VA | 23692 | 3 | NO | 1556 | 1998-08-19 | 0 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 0 | 24 |  | 19980819 | 32 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | DONALD L WHITE | 7574552032 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | FIRE AT A RESIDENTIAL TOWNHOUSE UNIT WAS CAUSED BY AN ELECTRICAL SHORT CIRCUITAT THE ELECTRICAL METER BASE WHICH SUBSEQUENTLY MELTED DOWN THE CUSTOMER'S GASMETER AND SERVICE REGULATOR.
2025-01-31 10:21 | YES | YES | 19980182 | 1998-09-08 | 2700 | CONNECTICUT NATURAL GAS CORP | 235 HIGH STREET | NEW BRITAIN | HARTFORD | CT | 06051 | 3 | NO | 2331 | 1998-08-22 | 0 | 1 | 100000 | 69844.8482 | 168638.1117 | Null | 0 | 22 |  | 19980823 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | UNDER INVESTIGATION | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LOUIS P RICCELLI JR | 8607273287 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON AUGUST 22, 1998, AT APPROXIMATELY 2331 HOURS, CONNECTICUT NATURAL GAS CORP(CNG) RECEIVED NOTIFICATION FROM THE CITY OF NEW BRITAIN FIRE DEPARTMENT OF AHOUSE THAT WAS ON FIRE, APPARENTLY FROM AN EXPLOSION, AT 235 HIGH STREET. CNGRESPONDED AND HAD A REPRESENTATIVE ON SITE AT 2353 HOURS. ONE RESIDENT OF THETWO FAMILY HOUSE #235 HIGH STREET WAS INJURED AND TAKEN TO THE HOSPITAL. CNGPERSONNEL WORKING WITH THE CITY OF NEW BRITAIN FIRE DEPARTMENT, THECONNECTICUT STATE FIRE MARSHAL, AND GAS PIPELINE SAFETY UNIT (GPSU), CUT OFFTHE GAS SERVICE SUPPLYING #235 HIGH STREET AND PERFORMED LEAK SURVEY ANALYSISAT THE DIRECTION OF THE GPSU. THE SURVEY AND TESTING OF GAS FACILITIESINDICATED NO LEAKS. ADDITIONALLY, THE CUT OFF GAS SERVICE SUPPLYING 235 HIGHSTREET WAS SUBJECTED TO AIR PRESSURE TEST FROM THE MAIN TO THE BASEMENT TEEWITH NO LEAKAGE FOUND. THE CONTINUING INVESTIGATION IS UNDER THE AUTHORITY OFTHE STATE FIRE MARSHAL AND THE GAS PIPELINE SAFETY UNIT.
2025-01-31 10:21 | NO | NO | 19980183 | 1998-09-08 | 30629 | ONEOK SERVICES INC | 12419 W 95TH ST | LENEXA | JOHNSON | KS | 66214 | 3 | NO | 1542 | 1998-08-12 | 0 | 0 | 15000 | 10476.7272 | 25295.7167 | Null | 1 | 3 |  | 19980812 | 50 | 55 | BY TEST | 110 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | UNDER INVESTIGATION | STEEL |  | 4 | 0.156 | API 5L GRADE B |  | 0 | 1976 | UNDER PAVEMENT |  | JAMES M FALLON | 9132713910 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-29 | YES | 3 | PAINTED | YES |  |  | THE COMPANY'S 4" STEEL PIPELINE WAS DAMAGED BY A THIRD PARTY CONTRACTOR WHILEAUGERING ACROSS A STREET WHICH RESULTED IN INTERRUPTION OF SERVICE TO 286CUSTOMERS.
2025-01-31 10:21 | YES | NO | 19980190 | 1998-09-07 | 11032 | LACLEDE GAS CO | 10011 ST CHARLES ROCK RD | ST. ANN | ST LOUIS | MO | 63074 | 3 | NO | 1530 | 1998-08-20 | 0 | 0 | 75000 | 52383.6361 | 126478.5837 | Null | 1 | 50 |  | 19980820 | 15 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 2 | 0.154 | API5L |  | 0 | 1963 | UNDER PAVEMENT |  | PAUL B HUNKER JR | 3143420528 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A BACKHOE OPERATED BY THE CITY OF ST. ANN, MISSOURI, PULLED A TWO INCH COATEDAND CATHODICALLY PROTECTED STEEL MAIN FROM A COMPRESSION COUPLING WHILEEXCAVATING TO PERFORM A STORM SEWER REPAIR.
2025-01-31 10:21 | NO | NO | 19980191 | 1998-09-16 | 18536 | SOUTHWEST GAS CORP | 1320 DARTMOUTH | LOVELOCK | PERSHING | NV | 89419 | 3 | NO | 1430 | 1998-08-23 | 0 | 0 | 43898 | 30660.4914 | 74028.7583 | YES | 4 | 15 |  | 19980823 | 43 | 43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC |  | 2 | 0.113 | 2110 SCH A |  | 0 | 1965 | WITHIN/UNDER BUILDING |  | TOM MOESSNER | 7024235594 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A LEAK IN A 2" PVC GAS MAIN RESULTED IN GAS MIGRATING INTO A SINGLE FAMILYRESIDENCE (VACANT) AT 1320 DARTMOUTH STREET, LOVELOCK, NV. AN UNKNOWNIGNITION SOURCE CAUSED AN EXPLOSION WHICH RESULTED IN STRUCTURAL DAMAGE TO THEVACANT HOUSE. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION. THE PIPEHAS BEEN SENT TO AN INDEPENDENT THIRD PARTY LAB FOR ANALYSIS.
2025-01-31 10:21 | NO | NO | 19980192 | 1998-09-15 | 1800 | BROOKLYN UNION GAS CO | 460 WAVERLY AVE | PATCHOGUE | SUFFOLK | NY | 11772 | 4 | NO | 647 | 1998-08-08 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 19 |  | 19980808 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | PROPANE TANKS | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | RONALD J PEZLK | 5165455624 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | MARKETSPAN NATURAL GAS FACILITIES WERE NOT INVOLVED.
2025-01-31 10:21 | YES | NO | 19980193 | 1998-09-14 | 15084 | PALO ALTO, CITY OF | 4103 WILKIE WAY | PALO ALTO | SANTA CLARA | CA | 94306 | 3 | NO | 2230 | 1998-08-29 | 0 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 3 | 30 |  | 19980831 | 20 | 25 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | OTHER | ABS-SWP | 2 | 0.132 |  |  | 0 | 1961 | WITHIN/UNDER BUILDING |  | RODGER JENSEN | 6504966932 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT APPROXIMATELY 2230 HOURS ON AUGUST 29, 1998, THE PALO ALTO FIRE DEPARTMENTRESPONDED TO A REPORTED GARAGE FIRE AT 4103 WILKIE WAY, PALO ALTO, CA. UPONARRIVAL THE FIRE DEPARTMENT LOCATED AND EXTINGUISHED FLAMES IN THE GARAGE ANDTHE ATTIC AREA ABOVE THE KITCHEN AND LIVING ROOM AREAS. AT APPROXIMATELY 2330HRS, A FIREFIGHTER NOTICED BUBBLES IN THE GUTTER IN FRONT OF THE HOUSE.CONCERNED THAT THE CAUSE OF THE BUBBLES MAY HAVE BEEN A NATURAL GAS LEAK, HENOTIFIED THE UTILITY CONTROL CENTER TO DISPATCH THE GAS EMERGENCY STANDBYPERSON. THE GAS STANDBY PERSON WAS ON SCENE AT 2345 HRS AND IMMEDIATELY BEGANSURVEYING THE AREA WITH HIS GMI LEAK DETECTOR. 100% GAS WAS FOUND IN THE AREAOF THE BUBBLES, 60% WAS FOUND IN THE ADJACENT SEWER MANHOLE AND STORM DRAIN.WHILE THE GAS LEAK SURVEY WAS BEING CONDUCTED THE FIREFIGHTHERS NOTICE THATTHERE WAS AN INCREASE IN SMOKE COMING FROM THE WALL AREA BETWEEN THE KITCHENAND THE GARAGE. THEY CUT A HOLE IN THE KITCHEN FLOOR EXPOSING THE CRAWLSPACE. THEY SAW SEVERAL SMALL FLAMES BURING IN THE SOIL. THE FLAMES WERE NOTCAUSING DAMAGE AND WERE ALLOWED TO BURN. THE GAS MAIN ON WILKIE WAY AT W.MEADOW WAS EXPOSED AND AN PE PORTION OF THE MAIN WAS SQUEEZED OFF. THE OTHEREND OF THE MAIN WAS VALVED OFF, DISCONTINUING THE FLOW OF GAS IN THE MAIN. ASSOON AS THE GAS MAIN WAS CLOSED OFF, THE FLAMES UNDER THE HOUSE STARTED TODECREASE AND WERE ALLOWED TO BURN THEMSELVES OUT. A FIRE CREW AND GASUTILITY PERSONNEL REMAINED ON THE SCENE THROUGHOUT THE NIGHT AND INTO THE NEXTDAY MONITORING CONDITIONS. THE CAUSE OF THE GAS LEAK WAS DETERMINED TOBE SPLITS IN A SECTION OF 2" ABS-SWP PIPE INSTALLED IN 1961.
2025-01-31 10:21 | NO | NO | 19980198 | 1998-09-28 | 31097 | ISLAND ENERGY | BUILDING 523 WALNUT AVE | VALLEJO | SOLANO | CA | 94592 | 3 | YES | 1045 | 1998-09-14 | 0 | 0 | 8000 | 5587.5879 | 13491.0489 | YES | 1 | 15 |  |  | 27 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | NIPAK | 1978 | 1980 | UNDER GROUND OR UNDER WATER |  | WILLIAM PLUMMER | 7075625000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-09-08 | YES | 3 | ONE CALL MARKING | YES |  |  | THROUGH INVESTIGATION OF THE INCIDENT IT IS FOUND THAT THE CONTRACTOR, SSPORTSENVIRONMENTAL, HAD INEXPERIENCED BACK-HOE OPERATORS, AND/OR NO SPOTTERS ORFOREMAN ON THE SITE AT THE TIME. I HAVE TALKED TO PERSONNEL ABOUT THEEXCAVATION OF UTILITIES IN THE AREA IN THE PAST, BUT THE DISREGARDED MYSUGGESTIONS. THE CONTRACTOR DID NOT HAD DIG IN THE AREA OF THE UTILITY(GAS). NO CAUSE OR ANY EXPLANATION AS HOW THE INCIDENT HAPPENED. THE FIREDEPARTMENT WAS CALLED TO THE SCENE BY THE CONTRACTOR AND THE AREA WASEVACUATED. THE CONTRACTOR WORKS FOR EFA WEST, A DEPARTMENT OF NAVY CARETAKERFOR MARE ISLAND. THIS IS THE SECOND OF THREE BROKEN GAS LINES BY THISCONTRACTOR. THE CONTRACTOR DID GET A ONE CALL REQUEST AND THE GAS LINE WASCLEARLY MARKED IN ASPHALT WITH YELLOW MARKING PAINT WITH A "G" IN YELLOW AND ALINE 2 FEET LONG.
2025-01-31 10:21 | NO | NO | 19980199 | 1998-09-28 | 31097 | ISLAND ENERGY | 7TH & CEDAR | VALLEJO | SOLANO | CA | 94592 | 3 | YES | 745 | 1998-09-15 | 0 | 0 | 8000 | 5587.5879 | 13491.0489 | YES | 0 | 45 |  |  | 27 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | NIPAK | 1978 | 1980 | UNDER GROUND OR UNDER WATER |  | WILLIAM PLUMMER | 7075625000 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-09-08 | YES | 3 | ONE CALL MARKING | YES
2025-01-31 10:21 | NO | NO | 19980200 | 1998-09-28 | 18536 | SOUTHWEST GAS CORP | 47TH ST & JOMAX RD | PHOENIX | MARICOPA | AZ | 85024 | 3 | NO | 856 | 1998-08-07 | 0 | 0 | 40288 | 28139.0924 | 67940.9224 | Null | 0 | 59 |  | 19980807 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTM D2513 | PHILLIPS | 1994 | 1994 | UNDER GROUND OR UNDER WATER |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-08-05 | YES | 3 | PAINT | YES |  |  | A CONTRACTOR WAS TRENCHING FOR CABLE INSTALLATION AND DAMAGED A 4"DISTRIBUTION MAIN. THE CONTRACTOR HAD REQUESTED BLUE STAKE AND THE LINE WASMARKED. AN OUTAGE OF APPROXIMATELY 1300 CUSTOMERS OCCURRED. REGARDING PARTB, 2(B): THE GAS MAIN WAS MARKED AT THE WRONG LOCATION. THE MARKS WEREAPPROXIMATELY 30" FROM THE ACTUAL MAIN.
2025-01-31 10:21 | YES | YES | 19980201 | 1998-09-25 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | 518 REBECCA STREET | MCKEESPORT | ALLEGHENY | PA | 15132 | 2 | NO | 1817 | 1998-09-07 | 1 | 0 | 85000 | 59368.1209 | 143342.3949 | Null | 23 | 15 |  | 19980908 | 18 | 30 | BY TEST | 90 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 |  | DRESSER | 0 | 1971 | UNDER PAVEMENT |  | JOHN S HORENSKY | 4125535398 | EXTERNALLY | LOCALIZED PITTING |  | NO DATA |  | COATED | YES | 1981 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19980202 | 1998-09-29 | 18536 | SOUTHWEST GAS CORP | 40TH STREET & ROESER RD | PHOENIX | MARICOPA | AZ | 85040 | 3 | NO | 47 | 1998-08-31 | 0 | 0 | 8481 | 5923.5416 | 14302.1982 | YES | 2 | 30 |  | 19980831 | 275 | 275 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 | API 5L GRADE B | CSI | 1996 | 1996 | ABOVE GROUND |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | A CAR COLLIDED WITH AN ABOVE GROUND BLOW OFF STACK, DAMAGING A 1/2" DIAMETERGAUGE TAP. THE TRANSMISSION PIPELINE WAS REMOVED FROM SERVICE TO MAKEPERMANENT REPAIRS.
2025-01-31 10:21 | YES | YES | 19980203 | 1998-09-25 | 15518 | PIEDMONT NATURAL GAS CO INC | 13200 CHASEWATER DR | CHARLOTTE | MECKLENBURG | NC | 28277 | 3 | NO | 1952 | 1998-08-26 | 0 | 1 | 1000 | 698.4485 | 1686.3811 | Null | 2 | 40 |  | 19980827 | 60 | 75 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | NO DATA |  | 0.5 | 0.09 | PE2406 | PLEXCO | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | RONALD W COBB | 7043643120 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-08-23 | YES | 3 | PAINT | YES |  |  | AN EMPLOYEE OF ALLTEL COMMUNICATIONS EMPLOYEE WAS COATING A COMMUNICATIONSCABLE. THE COATING PROCESS REQUIRED THE USE OF A PROPANE TORCH. THE WORKERINADVERTENTLY EXPOSED THE POLYETHYLENE GAS PIPING TO THE TORCH FLAME. THEPIPE MELTED ALLOWING THE GAS TO ESCAPE; THE PROPANE TORCH THEN IGNITED THEESCAPING GAS. THE WORKER SUSTAINED FIRST AND SECOND DEGREE BURNS.
2025-01-31 10:21 | YES | YES | 19980204 | 1998-09-22 | 4060 | EAST OHIO GAS CO | 396 DOUGLAS ST | AKRON | SUMMIT | OH | 44314 | 3 | NO | 830 | 1998-08-14 | 0 | 1 | 45000 | 31430.1817 | 75887.1502 | Null | 0 | 15 |  | 19980814 | 0.5 | 1 | BY CFR 192.619(A)(3) | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.145 | API 5L | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN D HOGAN | 2167366857 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | SERVICE LINE WAS PULLED FROM CONNECTION AT HOUSE. THE PERSON OPERATING THEBACKHOW WAS THE SON OF THE BUILDING OWNER. NO ONE HAD CALLED OHIO UTILITIESPROTECTION TO HAVE LINE LOCATED.
2025-01-31 10:21 | YES | NO | 19980205 | 1998-09-19 | 15259 | PENNSYLVANIA GAS & WATER CO | 31 ALPINE DRIVE | MOOSIC | LACKAWANNA | PA | 18507 | 2 | NO | 831 | 1998-08-31 | 0 | 0 | 150000 | 104767.2722 | 252957.1675 | Null | 0 | 56 |  | 19980831 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JAMES M GREGER | 7178298866 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | CONTRACTOR WAS OPERATING A MOTORIZED MANLIFT NEXT TO THE GARAGE (GUEST HOUSE),LOST CONTROL OF HIS MACHINE AS HE TRIED TO STEER IT DOWN AN EMBANKMENT. ASTHE MANLIFT SLID DOWN THE HILL, IT HIT A METER SET (WHICH WAS AN AL425 WITH A1 1/4" RISER) SEVERING IT OFF BEFORE THE REGULATOR. WHEN THE OPERATOR TURNEDTHE MANLIFT OFF, IT BACKFIRED AND IGNITED THE ESCAPING GAS. THE GUEST HOUSEAND GARAGE WERE DESTROYED IN THE FIRE WHICH FOLLOWED.
2025-01-31 10:21 | NO | NO | 19980206 | 1998-09-18 | 15007 | PACIFIC GAS & ELECTRIC CO | 3463 STONE RIVER CIRCLE | STOCKTON | SAN JOAQUIN | CA | 95219 | 3 | NO | 609 | 1998-08-27 | 0 | 0 | 51000 | 35620.8726 | 86005.4369 | Null | 1 | 10 |  | 19980827 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.5 | 0.145 |  |  | 0 | 0 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736998 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | THIS INCIDENT WAS CAUSED BY A CAR BEING RECKLESSLY DRIVEN BY THE PROPERTYOWNER, WHO RAN HER VEHICLE INTO THE GAS METER. THE GAS METER WAS LOCATED INAN AREA NOT NORMALLY ACCESSIBLE TO VEHICLES. THE INCIDENT IS STILL UNDERINVESTIGATION BY THE STOCKTON FIRE DEPARTMENT. THEIR FINAL REPORT ANDDETERMINATION OF THE CAUSE OF THE IGNITION HAS NOT BEEN RELEASED. PLEASECONTACT BRIAN LEARY AT 415-973-8180 IF YOU HAVE ANY QUESTIONS.
2025-01-31 10:21 | YES | NO | 19980207 | 1998-09-18 | 15931 | PUBLIC SERVICE CO OF COLORADO | 2054 & 2044 S OSWAGO WAY | AURORA |  | CO |  | 3 | NO | 1450 | 1998-08-18 | 0 | 0 | 300000 | 209534.5445 | 505914.335 | Null | 1 | 8 |  | 19980819 | 58 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | ASTM D2513 |  | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | JOHN STEVENSON | 3035713887 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES |  |  | 3RD PARTY MELTED P. E. D. MAIN WITH WELDING TORCH AND CAUSED FIRE.
2025-01-31 10:21 | YES | NO | 19980210 | 1998-10-06 | 4483 | ENSTAR NATURAL GAS CO | TRACT C, NOLEN'S KNOLL SUB. SHCROCK PITT | WASILLA |  | AK | 99654 | 3 | NO | 307 | 1998-09-30 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 0 | 43 |  | 19980930 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1994 | 1994 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON WEDNESDAY MORNING, SEPTEMBER 30, 1998 AT APPROXIMATELY 3:07 AM AST, ENSTARNATURAL GAS COMPANY RESPONDED TO A HOUSE FIRE AT TRACT C, NOLEN'S KNOLLSUBDIVISION, WASILLA, ALASKA. FIRE DEPARTMENT OFFICIALS REPORTED THE FIREORIGINATED FROM A CANDLE LIT BY A CHILD IN THE BASEMENT OF THE STRUCTURE. THERESULTING FIRE ENGULFED THE STRUCTURE. THE FIRE CONSUMED ENSTAR'S REGULATOR,METER AND RISER. THE POLYETHYLENE GAS SERVICE LINE INSIDE THE STEEL RISERMELTED, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE PINCHED OFF THECAPPED BY ENSTAR PERSONNEL AT 3:50 AM AST. ESTIMATED DAMAGE TO THE STRUCTUREWAS IN EXCESS OF $100,000.
2025-01-31 10:21 | NO | NO | 19980211 | 1998-10-06 | 180 | ALABAMA GAS CORP | 2300 TWELVE OAKS DRIVE | BIRMINGHAM | JEFFERSON | AL | 35244 | 3 | NO | 231 | 1998-08-24 | 0 | 0 | 65000 | 45399.1513 | 109614.7726 | Null | 1 | 10 |  | 19980824 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | DRISCO | 0 | 1996 | NO DATA |  | RON TAYLOR | 2053269228 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | PAINT | YES |  |  | GAS LINE MARKET INCORRECTLY.
2025-01-31 10:21 | YES | YES | 19980212 | 1998-10-05 | 11683 | LONE STAR GAS CO OF TEXAS, INC | 2422 LAKESHORE | GRAND PRAIRIE | DALLAS | TX | 75071 | 3 | NO | 955 | 1998-09-01 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 5 |  | 19980901 | 23 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2306 | DUPONT | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RON HASKOVEC | 2148122469 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-08-31 | NO | 0 |  | NO |  |  | A LONE STAR GAS CONTRACTOR (BUKEEN) LOCATED A GAS LINE ON THE WRONG SIDE OFTHE ROAD. RCA PLUMBING COMPANY CUT INTO A 2 INCH GAS LINE WHILE DIGGING ASEWER LINE IN THIS WORK AREA. A LONE STAR GAS EMPLOYEE, WHILE WORKING TO STOPTHE FLOW OF NATURAL GAS, WAS OVERCOME BY THE GAS AND HOSPITALIZED FOR FOURDAYS.
2025-01-31 10:21 | NO | NO | 19980213 | 1998-10-02 | 18696 | SUGAR HILL NATURAL GAS SYSTEM, CITY OF | 405 WINDING ROSE DRIVE | SUWANEE | GWINNETT | GA | 30024 | 0 | NO | 1220 | 1998-09-17 | 0 | 0 | 0 | 0 | 0 | Null | 0 | 10 |  | 19980918 | 45 | 45 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOHNNY UPCHURCH | 7702712137 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-09-02 | YES | 2 |  | YES |  |  | GAS LINE MARKED PROPERLY. CONTRACTOR DID NOT POT HOLE BEFORE USING TRENCHER.
2025-01-31 10:21 | YES | YES | 19980214 |  | 1640 | BOSTON GAS CO | 8 ASHTON STREET | BOSTON | SUFFOLK | MA |  | 3 | NO | 1111 | 1998-08-26 | 1 | 0 | 750000 | 523836.3612 | 1264785.8374 | Null | 1 | 17 |  | 19980826 | 0.03 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0 |  |  | 0 | 1928 | OTHER | UNDER PREVIOUSLY EXCAVATE | DANIEL F MCNAMARA | 7817943501 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-10 | YES | 3 | PAINT | NO |  |  | ON AUGUST 26, 1998 AT 11:09 AM, AN EXPLOSION AND FIRE OCCURRED 8 ASHTONSTREET, DORCHESTER, BOSTON DEMOLISHING A THREE STORY, WOODEN, RESIDENTIALDWELLING. A SUBSEQUENT LEAK INVESTIGATION WAS CONDUCTED AND A SIX-INCH CASTIRON MAIN WAS FOUND TO BE CIRCUMFERENTIALLY FRACTURED IN TWO LOCATIONSAPPROXIMATELY 20 FEET APART. THESE BREAKS WERE BOTH LOCATED IN AN AREA THATHAD BEEN RECENTLY EXCAVATED AND BACKFILLED DURING A WATER, SEWER, AND DRAINRELAY PROJECT. THE INCIDENT OCCURRED WHILE THE CONTRACTOR WAS USING AVIBRATORY ROLLER TO COMPACT THE TRENCH IN PREPARATION FOR ASPHALT PAVING.THIS INCIDENT IS CURRENTLY BEING INVESTIGATED BY THE BOSTON GAS COMPANY ANDTHE STATE OF MASSACHUSETTS' DEPARTMENT OF TELECOMMUNICATIONS AND ENERGY.
2025-01-31 10:21 | YES | NO | 19980217 | 1998-10-19 | 4483 | ENSTAR NATURAL GAS CO | 3938 COPE STREET | ANCHORAGE |  | AK | 99503 | 3 | NO | 2010 | 1998-10-09 | 0 | 0 | 500000 | 349224.2408 | 843190.5583 | Null | 1 | 25 |  | 19981009 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.09 | M-8000 | DRISCOPIPE | 1997 | 1997 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON FRIDAY EVENING, OCTOBER 9, 1998 AT APPROXIMATELY 8:10 PM AST, ENSTARNATURAL GAS COMPANY RESPONDED TO A 30 UNIT APARTMENT FIRE AT 3938 COPE STREET,ANCHORAGE, ALASKA. THE FIRE CONSUMED ENSTAR'S REGULATOR, METER AND RISER.THE POLYETHYLENE GAS SERVICE LINE INSIDE THE STEEL RISER MELTED, CAUSING ARELEASE OF NATURAL GAS. THE SERVICE LINE WAS PINCHED OFF AND CAPPED BY ENSTARPERSONNEL AT 9:35 PM AST. FIRE DEPARTMENT OFFICALS HAVE TENTATIVELYATTRIBUTED THE CAUSE OF THE FIRE TO CHILDREN PLAYING WITH MATCHES IN A STORAGESHED THAT WAS ATTACHED TO THE APARTMENT BUILDING. ESTIMATED DAMAGE TO THESTRUCTURE WAS IN EXCESS OF $500,000.
2025-01-31 10:21 | YES | NO | 19980218 | 1998-10-01 | 6370 | GIBSON COUNTY UTIL DIST | 37 GREEN ACRES | TRENTON | GIBSON | TN |  | 2 | Null | 1909 | 1998-09-08 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | NO | 0 | 0 |  | 19980909 | 0 | 0 |  | 1000 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE APPLIANCE PIPING | NO DATA |  | STEEL |  | 0.5 | 0.109 |  |  | 0 | 1990 | WITHIN/UNDER BUILDING |  | GEORGE R DAVIS | 9018551441 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | APPROXIMATELY 19:09 HRS, TUESDAY, SEPTEMBER 8,1998, RECEIVED A TELEPHONE CALLFROM CENTRAL CONTROL STATING THEIR HAD BEEN A GAS EXPLOSION AT GREEN ACRESAPARTMENTS LOCATED ON THE GIBSON ROAD INSIDE TRENTON CITY LIMITS. THEDISPATCHER ON DUTY STATED THAT ALL AVAILABLE GAS PERSONNEL WERE NEEDED AT THISLOCATION AS SOON AS POSSIBLE. IMMEDIATELY, I ADVISED CENTRAL CONTROL THAT T-1WAS IN ROUTE. UPON ARRIVAL, STANDING IN FRONT OF THE APARTMENTS, IIMMEDIATLEY VIEWED WHAT APPEARED TO BE SINGLE LEVEL-DOUBLE APARTMENTDWELLING. THE WEST SIDE APARTMENT HAD BY SOME MEANS BEEN DEMOLISHED. THEROOF STRUCTURE WAS GONE AND THE WALLS ON THE NORTH AND WEST SIDE OF THEBUILDING WERE ALSO DEMOLISHED. PROCEEDING AROUND TO THE SOUTH (REAR) OF THEBUILDING I ALSO NOTICED THIS WALL HAD SUSTAINED THE SAME TYPE OF DAMAGE. ATRENTON FIREFIGHTER ADVISED ME THAT NO ONE WAS IN EITHER DWELLING AT THE TIMEOF OCCURANCE NOR DID ANYONE GET HURT. FURTHER EVALUATION AROUND THE METERHOOK-UP REVEALED THAT BY SOME MEANS A 1/2 IN X 1/2 IN APPLIANCE SHUT OFF VALVEWAS IN THE OPEN POSITION. (SEE PICTURES) A PORTION OF 1 IN. PIPE WASVISIABLE FROM WHERE WE WERE STANDING. UPON VIEWING THIS PIPE WE FOUND THATTHE PIPE WAS BROKEN INTO AND THE THREADS WERE STILL IN THE 1 IN. 90 DEGREEELBOW. APPARENTLY THE INPACT AND THE WALL FALLING HAD THUS BROKEN THISSECTION OF PIPING. (SEE PICTURES) THE SERVICE LINE VALVE WAS CUT OFF AND LATERBUDDY AND I FOUND THIS WAS DONE BY THE TRENTON FIRE DEPARTMENT. ALL FITTINGSWERE SPRAYED WITH A SOUP SOLUTION, WHICH IS PROVIDED BY G.C.U.D. FOR THEPURPOSE OF HELPING DETECT LEAKAGE. LATER I REQUESTED TRENTON FIRE CHIEF BARRYGREEN TO ACCOMPANY ME TO THE TWO METERS IN THE REAR OF THE DWELLING SO I COULDLOCK EACH SERVICE LINE VALVE. ONE METER WAS LOCATED ON APARTMENT NUMBER 37AND THE OTHER ON APARTMENT. MR. JARINIGAN AND I REQUESTED THAT CHIEF BARRYGREEN OF THE TRENTON FIRE DEPARTMENT CALL THE FIRE MARSHALL FOR OUR DISTRICTTO INVESTIGATE THE OCCURANCE. LATER CHIEF GREEN ADVISED US THAT THE FIREMARSHAL HAD BEEN CALLED AND WOULD BE AT THIS LOCATION AS SOON AS HE COULDDRIVE FROM WEAKLEY COUNTY. AT APPROXIMATELY 21:31 HRS I LEFT THE SCENE INROUTE HOME.
2025-01-31 10:21 | YES | YES | 19980219 | 1998-10-14 | 18112 | SAN DIEGO GAS & ELECTRIC CO | CAMPO ROAD (HWY94) WEST OF JAMACHA BLVD |  | SAN DIEGO | CA |  | 1 | NO | 714 | 1998-08-11 | 0 | 1 | 138000 | 96385.8905 | 232720.5941 | Null | 1 | 1 |  | 19980811 | 370 | 400 | BY TEST | 640 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | API5LX46 |  | 1981 | 1981 | UNDER PAVEMENT |  | ROGER W SPRENGER | 6195472023 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-07-07 | YES | 3 | PAINT MARKS ON ROAD | YES |  |  | ON THE DAY OF THE INCIDENT, THE CONTRACTOR DID NOT EXPOSE THE GAS PIPE AT THECROSSING OF BORING OR REQUEST SDG&E STANDBY.
2025-01-31 10:21 | YES | YES | 19980220 | 1998-10-14 | 31159 | KANSAS GAS SERVICE | 5301 W 129TH | OVERLAND PARK | JOHNSON | KS | 66224 | 3 | NO | 1225 | 1998-09-08 | 0 | 1 | 60000 | 41906.9089 | 101182.867 | Null | 0 | 33 |  | 19980908 | 30 | 58 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | 2406 | PLEXCO | 1997 | 1998 | UNDER GROUND OR UNDER WATER |  | JAMES M FALLON | 9132713910 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A THIRD PARTY EXCAVATOR WAS OPERATING A TRENCHING MACHINE TO INSTALL ATELEPHONE CABLE. THE TRENCHING MACHINE OPERTOR SEVERED A 4" PLASTIC GAS MAINWHICH RESULTED IN THE IGNITION OF NATURAL GAS CAUSING INJURY TO THE MACHINEOPERATOR AND DAMAGE TO THE TRENCHING MACHINE.
2025-01-31 10:21 | NO | NO | 19980226 | 1998-10-26 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 313 TILDEN DR | PASADENA | HARRIS | TX | 77506 | 3 | NO | 258 | 1998-09-14 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 28 |  | 19980914 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 1.25 | 0.165 | API 5L |  | 0 | 1952 | ABOVE GROUND |  | JEFFREY A BISH | 7139678093 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | HEAT FROM BURING HOUSE DAMAGED METER SET ASSEMBLY AND ESCAPING GAS IGNITED.
2025-01-31 10:21 | YES | NO | 19980227 | 1998-10-26 | 31163 | NORTH LITTLE ROCK HOUSING AUTHORITY | 701 WEST 18TH STREET, APT 87-94 | NORTH LITTE ROCK | PULASKI | AR | 72114 | 0 | YES | 1835 | 1998-10-12 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 1 | 0 |  | 19981012 | 10 | 60 |  | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 | 0.25 |  |  | 1973 | 1973 | UNDER GROUND OR UNDER WATER |  | RICHARD E ELLIOTT | 5017588781 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA |  | THE SYSTEM OWNER/OPERATOR, THE HOUSING AUTHORITY OF THE CITY OF NORTH LITTLEROCK, ARKANSAS, CONTRACTED WITH SATTERFIELD PIPELINE, INC. TO INSTALL NEWUNDERGROUND GAS PIPING AT THREE FAMILY PUBLIC HOUSING DEVELOPMENTS ITOPERATES. THE NORTH LITTLE ROCK HOUSING AUTHORITY PROVIDED TO SATTERFIELDPIPELINE COPIES OF ALL UTILITY MAPS AND AS-BUILT DRAWINGS. APPARENTLY, THECONTRACTOR WAS OPERATING A BORING MACHINE TO TUNNEL FOR NEW PIPING PARALLEL TOEXISTING GAS PIPING, AND THE BORING BIT CAME TOO CLOSE TO THE EXISTING PIPINGAND CONTACTED IT, CAUSING A HOLE APPROXIMATELY 1.5 INCHES IN DIAMETER TO BEOPENED IN THE EXISTING STEEL PIPING. GAS AT APPROXIMATELY 10 PSI WASRELEASED, APPROXIMATELY 36" UNDERGROUND, APPROXIMATELY 10 FEET FROM A BUILDINGFOUNDATION. GAS APPARENTLY POCKETED AND COLLECTED UNDER THIS BUILDING FOR ASHORT TIME. SOON AFTER, SOME UNKNOWN IGNITION SOURCE IGNITED THE GAS, CAUSINGEXTENSIVE DAMAGE TO THE BUILDING. IN MY OPINION, THE CONTRACTOR WAS ACTINGWITH CAUTION, BUT COULD HAVE PERHAPS DONE A BETTER JOB LOCATING AND VERIFYINGTHE DEPTH AND LOCATION OF THE EXISTING PIPING. THE BORING DEPTH SHOULD HAVEPERHAPS BEEN DEEPER, AND NOT HAVE AS CLOSELY PARALLELED THE EXISTING PIPING.
2025-01-31 10:21 | YES | YES | 19980228 | 1998-10-22 | 18440 | SOUTH JERSEY GAS CO | 119 GARFIELD AVE | PINEHURST | GALLOWAY | NJ | 08201 | 4 | NO | 1725 | 1998-10-08 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 9 |  | 19981008 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | DUPONT | 0 | 1972 | UNDER PAVEMENT |  | A M TETTO | 6095619000 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE EXCAVATING TO PINPOINT A GAS LEAK, AN EMPLOYEE USING A SMALL BACKHOEACCIDENTLY STRUCK AND PUNCTURED A 2" PLASTIC GAS MAIN OPERATING AT 40 PSIG.THE GAS IGNITED BY AN UNKNOWN SOURCE INJURING THE MACHINE OPERATOR AND CAUSINGSLIGHT DAMAGE TO A HOUSE AND PARKED VEHICLE. THE GAS BURNED FOR APPROXIMATELY2 HOURS UNTIL GAS WAS SHUT OFF AND SQUEEZED OFF FROM ALL SOURCES.
2025-01-31 10:21 | YES | YES | 19980229 | 1998-10-19 | 7348 | HOPE GAS INC | COUNTY ROUTEE 17 (ORAL LAKE ROAD) | BRIDGEPORT | HARRISON | WV | 26330 | 3 | NO | 420 | 1998-10-04 | 1 | 2 | 0 | 0 | 0 | Null | 1 | 55 |  | 19981004 | 40 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1982 | ABOVE GROUND |  | THOMAS C YOKUM | 3046238909 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | AUTOMOBILE LEFT ROADWAY, FLIPPED OVER LANDING ON AND SHEARING OFF METER RISERSCAUSING RELEASE OF GAS FOLLOWED BY IGINTION.
2025-01-31 10:21 | NO | NO | 19980230 | 1998-11-10 | 18594 | SPUR, CITY OF | FULLER PLANT |  |  | TX |  |  | Null | 100 | 1998-10-20 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 0 | [6 empty] | OTHER | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | SUPLER | OTHER |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | OTHER |  | NOT GIVEN |  | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19980231 | 1998-11-10 | 2748 | CONSUMERS POWER CO | 8232 DEERWOOD CIRCLE | CLARKSTON | OAKLAND | MI | 48348 | 3 | NO | 1357 | 1998-10-19 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 33 |  | 19981019 | 55 | 60 | BY TEST | 97 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.062 | ASTMD2513 | PHILLIPS | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | JERRY F HOLWERDA | 5177881835 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | AMERITECH EMPLOYEES WORKING IN EXCAVATION WITH TORCH MELTED PLASTIC GASSERVICE LINE AND IGNITED GAS CAUSING INJURIES.
2025-01-31 10:21 | NO | NO | 19980232 | 1998-11-05 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 1 HAWTHORNE AVE APARTMENT 4A | YONKERS | WESTCHESTER | NY | 10701 | 4 | NO | 2126 | 1998-10-07 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 0 | 11 |  | 19981007 | 0.2 | 0.4 |  | 0 | CORROSION | CORROSION | EXTERNAL | OTHER | HOUSE PIPE | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ANTHONY B CODNER | 2124601103 | EXTERNALLY | GENERAL CORROSION |  | OTHER |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | A CORRODED SECTION OF CUSTOMER OWNED HOUSE PIPING IN THE WALL OF APT 3A OF A 4STORY APARTMENT BUILDING, RESULTING IN A EXPLOSION IN APT 4A. ONE WOMANRECEIVE MINOR BURNS AND WAS TREATED AND RELEASED. WE ARE INVESTIGATING TODETERMINE WHETHER THE ACTIONS OF AN EMPLOYEE TURNING ON THE GAS METER TO APT4A MIGHT HAVE PREVENTED THE INCIDENT.
2025-01-31 10:21 | YES | NO | 19980233 | 1998-11-06 | 22210 | WASHINGTON WATER POWER CO | 6322 DISTRICT 2 RD PRIVATE G | BONNERS FERRY |  | ID | 83805 | 3 | NO | 326 | 1998-10-11 | 0 | 0 | 150000 | 104767.2722 | 252957.1675 | Null | 1 | 20 |  | 19981011 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.9 |  | RISER FIELD FABRICATION | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | MICHAEL J FAULKENBERRY | 5094958499 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON OCTOBER 11, 1998, WASHINGTON WATER POWER, AN ELECTRIC AND NATURAL GASDISTRIBUTION UTLITY, RECEIVED NOTIFICATION BY THE FIRE DEPARTMENT THAT NATURALGAS WAS INVOLVED IN A RESIDENTIAL FIRE AT 6322 DISTRICT 2 RD. PRIVATE G,BONNERS FERRY, ID. DAVID W. KUHNS, THE HOMEOWNER WAS ON THE PROPERY, BUT NOTWITHIN THE HOME WHEN THE FIRE IGNITED. OUR DISPATCHER SENT A GAS SERVICEMANWHO SQUEEZED THE SERVICE TO SHUT-OFF THE FLOW OF GAS AT THE MAIN. IT WASEVIDENT UPON HIS ARRIVAL THAT GAS WAS LEAKING FROM THE SERVICE BETWEEN THESERVICE TAP AT THE MAIN AND THE SERVICE RISER VALVE. IT WAS LATER DETERMINEDTHAT THE GAS WAS LEAKING FROM THE WEATHER SEAL IN THE BURIED PORTION OF THERISER APPROXIMATELY 5 FEET FROM THE HOUSE FOUNDATION. THE FOLLOWING DAY,WASHINGTON WATER POWER PERSONNEL IN THE PRESENCE OF THE BONNERS FERRY FIRECHIEF, INITIATED A THOROUGH INVESTIGATION TO DETERMINE THE CAUSE OF THISINCIDENT. THE SOURCE OF THE GAS LEAK WAS DETERMINED TO BE AN 1/8-INCHDIAMETER HOLE IN THE 1/2 INCH POLYETHYLENE PIPING WITHIN THE GAS RISERCASING, APPROXIMATELY 6-INCHES BELOW THE METER VALVE AT WHAT WOULD HAVE BEENGROUND LEVEL. THE AREA OF FAILURE APPEARS TO HAVE OCCURRED INSTANTANEOUSLYDUE TO AN ELECTRICAL FAULT (WE BELIEVE MOST LIKELY A LIGHTING STRIKE). THEPIPE IS MELTED ONLY AT THIS LOCATION AND ONLY ON ONE SIDE OF THE PIPE. THETRACER WIRE SHOWED EVIDENCE OF ELECTRICAL ARCING AT THIS LOCATION ALSO. THEFIRE DID NOT CONSUME THE METER SO IT IS NOT LIKELY THAT SUFFICIENT HEAT WAS INTHIS AREA TO HAVE CAUSED THIS LEAK. IT APPEARS THAT LIGHTNING MAY HAVE BEENIN THE AREA ON OCTOBER 8, 1998, THREE DAYS PRIOR TO THIS INCIDENT. GASODORANT WAS AT ADEQUATE LEVELS AT THE TIME OF THE INCIDENT. HOWEVER, ITAPPEARS THAT THE HOWEOWNER RECENTLY HAD SURGERY WHICH AFFECTED HIS SENSE OFSMELL. AS REPORTED IN MY TELEPHONIC REPORT, THERE WAS NO INJURY AS A RESULTOF THIS INCIDENT.
2025-01-31 10:21 | YES | YES | 19980234 | 1998-11-04 | 2596 | COLUMBIA GAS OF OHIO INC | 2930 FIRELANDS BLVD | PORT CLINTON | OTTAWA | OH | 43452 | 3 | NO | 1135 | 1998-09-09 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 18 |  | 19980909 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 1 | 0 |  | DRISCO | 0 | 1982 | UNDER GROUND OR UNDER WATER |  | MICHAEL D RAMSEY | 4192485269 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-09-03 | YES | 3 | YELLOW MARKING PAINT | YES |  |  | CONTRACTOR WAS WORKING AROUND A 1-INCH EXPOSED SERVICE LINE. THE CONTRACTORSEVERED THE SERVICE LINE. A CONTRACTOR EMPLOYEE WAS BURNED WHEN THE BLOWINGGAS IGNITED.
2025-01-31 10:21 | NO | NO | 19980235 | 1998-11-04 | 15007 | PACIFIC GAS & ELECTRIC CO | S DOWNER AVE S/O W. ELKHORN AVE | BURREL | FRESNO | CA | 93607 | 1 | NO | 1159 | 1998-10-09 | 0 | 0 | 55000 | 38414.6665 | 92750.9614 | Null | 1 | 26 |  | 19981009 | 600 | 650 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.281 | X-42, ERW |  | 0 | 1953 | UNDER GROUND OR UNDER WATER | [9 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-10-05 | NO | 0 |  | YES |  |  | EXCAVATOR NOTIFIED UNDERGROUND SERVICE ALERT (USA) TO MARK FACILITIES ON10/5/98. USA NOTIFIED OPERATOR ON 10/5/98 REGARDING REQUEST TO MARKFACILITIES. OPERATOR DID NOT MARK FACILITIES. FARMER RIPPING FARM LAND HITPIPELINE ON 10/9/98.
2025-01-31 10:21 | NO | NO | 19980236 | 1998-11-04 | 1800 | BROOKLYN UNION GAS CO | 4547B AUSTIN BLVD | ISLAND PARK | NASSAU | NY | 11558 | 4 | NO | 1300 | 1998-10-03 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 2 |  | 19981003 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | PIZZA OVEN | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | E S PAPADOULLAS | 5165454982 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | MARKETSPAN NATURAL GAS FACILITIES WERE NOT INVOLVED.
2025-01-31 10:21 | YES | YES | 19980237 | 1998-11-04 | 5700 | FULTONDALE GAS BOARD | 1073 PINE MEADOW DRIVE | GARDENDALE |  | AL | 35068 | 3 | NO | 1000 | 1998-10-15 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19981015 | 25 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 1 | 11 | ASTM D-251 | DRISCO | 1996 | 1997 | UNDER GROUND OR UNDER WATER |  | LESLIE D SHIPP | 2058416456 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A COMPANY SERVICE EMPLOYEE, MIKE HORSLEY, WAS IN THE PROCESS OF MAKING ASERVICE TAP. A 1' CROSS OVERLINE, UNDER PRESSURE 25#, WAS CUT IN ORDER TOMAKE THE TIE IN. A TEMPORARY ELECTRICAL SERVICE BOX LOCATED ABOUT THREE FEETFROM BELL HOLE WAS BEING USED BY CONSTRUCTION WORKER. IT APPEARS THE IGNITIONPOINT WAS FROM THE ELECTRICAL SERVICE PANEL. MR. HORSLEY RECEIVED THIRDDEGREE BURNS ON THE FACE AND WAS KEPT OVERNIGHT IN THE HOSPITAL FOROBSERVATION. AS OF THIS DATE, MR HORSLEY IS RECOVERING AT HOME.
2025-01-31 10:21 | YES | YES | 19980238 | 1998-10-27 | 4483 | ENSTAR NATURAL GAS CO | 1820 BELLEVUE LOOP | ANCHORAGE |  | AK | 99515 | 3 | NO | 548 | 1998-10-24 | 0 | 1 | 500000 | 349224.2408 | 843190.5583 | Null | 2 | 6 |  | 19981024 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1983 | 1983 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON SATURDAY MORNING, OCTOBER 24, 1998, AT APPROXIMATELY 5:38 AM EST, ENSTARNATURAL GAS COMPANY WAS NOTIFIED OF AN EXPLOSION AND FIRE AT 1820 BELLEVUELOOP, ANCHORAGE, AK 99515. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WEREDISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A ZERO LOT-LINE HOME ONFIRE. HEAT FROM THE FIRE MELTED 5/8" POLYETHYLENE SERVICE LINE INSIDE THESTEEL RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP,PINCHED OFF AND CAPPED. THE CAUSE OF THE EXPLOSION AND RESULTING FIRE WASFROM NATURAL GAS ESCAPING FROM THE CUSTOMER'S HOUSE LINE. A 1/2" CAP WASFOUND MISSING FROM A DRIP LEG ON THE CUSTOMER'S HOUSE LINE SUPPLYING NATURALGAS TO THE FURNACE. NATURAL GAS FROM ENSTAR'S DOT REGULATED FACILITIES DIDNOT CAUSE OR CONTRIBUTE TO THE EXPLOSION OR FIRE.
2025-01-31 10:21 | YES | YES | 19980245 | 1998-11-11 | 18536 | SOUTHWEST GAS CORP | 4400 S GREENFIELD ROAD | GILBERT | MARICOPA | AZ | 85296 | 3 | NO | 1204 | 1998-10-13 | 0 | 1 | 1150 | 803.2158 | 1939.3383 | Null | 1 | 1 |  | 19981013 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTMD2513 | PHILLIPS | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-10-01 | YES | 3 | PAINT | YES |  |  | A CONTRACTOR WAS EXCAVATING A TRENCH LINE WITH A BACKHOE AND UTLIZING A TRENCHBOX. THE BACKHOE DAMAGED A 4' PE MAIN, WHICH WAS ALREADY EXPOSED. ONE OF THECONTRACTOR'S EMPLOYEES WAS INJURED WHILE TRYING TO ESCAPE FROM THE TRENCH.THE EMPLOYEE WAS ADMITTED TO THE HOSPITAL FOR OVERNIGHT OBSERVATION.
2025-01-31 10:21 | NO | NO | 19980246 | 1998-11-04 | 15931 | PUBLIC SERVICE CO OF COLORADO | 2804 3RD ST | BOULDER | BOULDER | CO | 80301 | 0 | NO | 918 | 1998-10-05 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 0 | 40 |  | 19981006 | 7 | 14.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0 | SCHO40 |  | 0 | 1949 | UNDER GROUND OR UNDER WATER |  | DOUGLAS MATZICK | 3039382281 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | ON OCTOBER 5, 1998 AT APPROXIMATELY 9:00 AM AN ELECTRICAL DISTRIBUTIONCONTRACTOR INSTALLING UNDERGROUND CONDUIT PULLED A 3/4' MW STEEL SERVICE LINETO 2804 3RD ST, BOULDER COLORADO. THE SERVICE LINE WAS BROKEN AND SEPARATEDAT 3/4" X 3/4" 90 DEGREE ELL AT THE BASE OF THE SERVICE RISER. THE SEPARATIONOF THE SERVICE LINE WAS APPROXIMATELY 30" FROM THE BUILDING WALL. ATAPPROXIMATELY 9:18 AM THE STRUCTURE BECAME INVOLVED IN FIRE THAT WAS SUPPORTEDBY ESCAPING GAS FROM BROKEN SERVICE LINE. GAS SERVICE TO THE STRUCTURE WASTERMINATED AT 9:55 AM BY SQUEEZING THE LINE CLOSED.
2025-01-31 10:21 | YES | NO | 19980247 | 1998-11-16 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 1413 LACKLAND | ARLINGTON | TARRANT | TX | 76010 | 3 | NO | 1718 | 1998-10-10 | 0 | 0 | 110000 | 76829.333 | 185501.9228 | YES | 11 | 40 |  | 19981010 | 25 | 45 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | FITTING |  | OTHER | STEEL TO POLY COMPRESSION | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RON HASKOVEC | 2148122469 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | GROUND SHIFTING | Null |  | Null | 0 |  | Null |  |  | THE PIPING IN A COMPRESSION COUPLING, ON THE SERVICE TAP FOR THE DWELLING AT1412 LACKLAND (ACROSS THE STREET FROM THE INCIDENT LOCATION), WAS PULLED OUTOF ITS FITTING, WITH A GAS LEAK ENSUING FROM THAT COMPRESSION COUPLING. THEOPERATOR BELIEVES THAT EARTH MOVEMENT, SPECIFICALLY GROUND SHIFTING, CAUSEDTHE PIPING TO SEPARATE FROM THE COMPRESSION COUPLING. THE OPERATOR ALSOWISHES TO NOTE THAT ON SEPTEMBER 13, 1998, THE CUSTOMER AT THE INCIDENTLOCATION HAD REPORTED SMELLING GAS AT HIS RESIDENCE. IN RESPONSE, THEOPERATOR INVESTIGATED AND FOUND A GRADE 2 LEAK ON THE SERVICE LINE FOR THEDWELLING AT 1412 LACKLAND. THE OPERATOR FOUND NO CONCENTRATION OF GAS,HOWEVER, NEAR THE RESIDENCE AT THE SUBJECT LOCATION, OR IN THE SEWER AT THATRESIDENCE, EITHER ON SEPTEMBER 13 OR WHILE INVESTIGATING A SUBSEQUENT REPORTOF GAS SMELLS MADE BY A MEMBER OF THE PUBLIC ON SEPTEMBER 17.
2025-01-31 10:21 | NO | NO | 19980250 | 1998-12-01 | 15329 | PEOPLES GAS LIGHT & COKE CO | 1501-07 N CLYBOURN AV | CHICAGO | COOK | IL | 60610 | 4 | NO | 1115 | 1998-10-30 | 0 | 0 | 0 | 0 | 0 | Null | 2 | 0 |  | 19981030 | 20 | 25 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 24 | 0.76 |  |  | 0 | 1954 | OTHER | SEWER TRENCH EXCAVATION | GLEN ARMSTRONG | 3122404713 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-10-29 | YES | 3 | TEMPORARY FLAGS & SPRAY | YES |  |  | SEWER CONTRACTOR RUPTURED A 24" CAST IRON MEDIUM PRESSURE MAIN. ESCAPING GASIGNITED FROM UNKNOWN SOURCE AND FIRE DAMAGED AN ADJACENT BUILDING.
2025-01-31 10:21 | YES | NO | 19980251 | 1998-11-23 | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | 1/2 MILE S HICKORY HILL & HOLMES RD | MEMPHIS | SHELBY | TN | 38141 | 3 | NO | 1430 | 1998-10-27 | 0 | 0 | 120000 | 83813.8178 | 202365.734 | Null | 1 | 0 |  | 19981027 | 620 | 900 | BY TEST | 1350 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 24 | 0.344 | API 5L X 65 | STUPP CORPORATION | 1993 | 1994 | UNDER GROUND OR UNDER WATER |  | GENE A CRAWFORD | 9013201420 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES |  |  | M & H CONSTRUCTION HIT 24" GAS LINE; THERE WAS NO LOCATE CALLED TO TENNESSEONE CALL.
2025-01-31 10:21 | NO | NO | 19980252 | 1998-11-24 | 2309 | CHESAPEAKE UTILITY CORP | 1300 S FARMVIEW DRIVE | DOVER | KENT | DE | 19904 | 3 | NO | 1730 | 1998-11-09 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 0 | 49 |  | 19981113 | 39 | 43 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | 3/4 | CENTRAL PLASTICS | 1986 | 1987 | ABOVE GROUND |  | MARK FORESMAN | 3027346710 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | YES |  |  | METER ASSEMBLY WAS STRUCK BY A PASSENGER VEHICLE. THE SERVICE RISER WASDAMAGED BELOW THE INLET VALVE. THE CAUSE OF THE INCIDENT WAS A VEHICULARACCIDENT. A PASSENGER VEHICLE STRUCK AND DAMAGED AN APARTMENT BUILDING ANDADJACENT NATURAL GAS METER SET. A RESULTING FIRE CAUSED AND ESTIMATED$50,000 IN DAMAGES TO THE APARTMENT BUILDING. THERE WERE NO INJURIES ORFATILITIES.
2025-01-31 10:21 | YES | YES | 19980253 | 1998-12-03 | 2364 | CINCINNATI GAS & ELECTRIC CO | 3024 VEAZEY AVE | CINCINNATI | HAMILTON | OH | 45238 | 4 | NO | 1038 | 1998-10-27 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 0 |  | 19981027 | 10 | 35 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1940 | UNDER GROUND OR UNDER WATER |  | SUSAN M GILB | 5132872752 | EXTERNALLY | LOCALIZED PITTING |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19980254 | 1998-11-27 | 19587 | TRANS LOUISIANA GAS CO INC | 2300 GARRETT ROAD LOT 50 | MONROE | OUACHITA | LA | 71202 | 3 | NO | 1710 | 1998-11-10 | 0 | 1 | 30000 | 20953.4544 | 50591.4335 | Null | 4 | 40 |  | 19981110 | 27 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | FUSION | POLYETHYLENE PLASTIC |  | 1 | 0.12 | P E 2306 | PLEXCO | 1982 | 1982 | WITHIN/UNDER BUILDING |  | THOMAS G MEYERS | 3182684417 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 1" POLY PIPE WAS INSERTED INTO 4" PVC IN 1982 WHEN A MASTER TRAILER PARKREQUESTED INDIVIDUAL METERS. THE 4" PVC PIPE WAS CUT FOR EACH RISERINSTALLATION. A PARTIAL FRACTURE IN OR ADJACENT TO A FUSION JOINT OCCURREDPOSSIBLY FROM LONG TERM STRESS ON JOINT WITH RECENT EXTERNAL FORCES ON RISER.GAS ESCAPED AND MIGRATED UNDER ALL ELECTRIC MOBILE HOME WITH TIGHT SKIRTING.RESIDENT CAME HOME, SMELLED GAS AND PROCESSED TO LIGHT CIGARETTE. THESUBSEQUENT EXPLOSION AND FIRE DESTROYED THE MOBILE HOME. THE RESIDENT WASHOSPITALIZED FOR BURNS TO FACE AND HANDS.
2025-01-31 10:21 | YES | YES | 19980256 | 1998-12-09 | 16020 | QUITMAN GAS DEPT, CITY OF | 405 E GREENWOOD AVE | QUITMAN | BROOKS | GA | 31643 | 3 | NO | 1048 | 1998-11-22 | 1 | 0 | 0 | 0 | 0 | Null | 0 | 15 |  | 19981123 | 0 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | SUPPLY LINE INSIDE HOUSE | OTHER | UNCAPPED GAS LINE INSIDE | STEEL |  | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | TONY MCRAE | 9122634166 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON OCTOBER 23, 1998 THE RESIDENT, JOSEPH GRIFFIN, WAS INFORMED BY THE CITYMETER READER DEPT THAT THEY WOULD NOT TURN HIS GAS METER ON BECAUSE THERE WASA GAS LEAK INSIDE HIS HOUSE. ON NOV. 22, 1998 THE QUITMAN FIRE DEPARTMENTRESPONDED TO A FIRE AT THE RESIDENTS OF JOSEPH GRIFFIN, INVESTIGAION REVEALEDTHAT HIS GAS METER HAD BEEN TURNED ON BY UNKNOWN PERSON. MR. GRIFFIN STATEDTO EMERGENCY PERSONNEL THAT HE HAD LIT A SPACE HEATER AND THEN ATTEMPTED TOTURN ON A FAN WHEN AN EXPLOSION OCCURRED. INVESTIGATION REVEALED GAS WAS NOTTURNED ON BY CITY EMPLOYEES.
2025-01-31 10:21 | YES | YES | 19981047 | 1998-07-20 | 603 | ARKLA, A NORAM ENERGY COMPANY | 765 SHREVEPORT BARKSDALE HWY | SHREVEPORT | CADDO | LA | 71101 | 1 | NO | 1032 | 1998-07-13 | 0 | 1 | 120000 | 83813.8178 | 202365.734 | Null | 1 | 30 |  | 19980713 | 19.5 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.14 | PE2406 |  | 1987 | 1988 | WITHIN/UNDER BUILDING |  | ROBERT KIDD | 3184294230 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | 2" POLY PIPE DEVELOPED CRACK. PIPE WAS INSTALLED BY CUSTOMER'S PLUMBER.
2025-01-31 10:21 | YES | YES | 19990001 | 1999-01-11 | 18536 | SOUTHWEST GAS CORP | 1402 E ST. LOUIS AVE | LAS VEGAS | CLARK | NV | 89104 | 3 | NO | 1500 | 1998-12-10 | 0 | 1 | 147825 | 103248.1468 | 249289.2886 | Null | 0 | 25 |  | 19981210 | 43 | 43 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | SEE PART 3 | OTHER PLASTIC |  | 0.375 | 0.062 |  | KRALOY | 0 | 1964 | UNDER GROUND OR UNDER WATER |  | PAUL JOHNSON | 7023652102 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A HOUSE, LOCATED AT 1402 E ST. LOUIS, WAS DAMAGED ON DECEMBER 10, 1998.ADDITIONAL RESIDENCES SUSTAINED DAMAGE THAT RANGED FROM EXTENSIVE STRUCTURALDAMAGE ON ONE HOUSE TO BROKEN WINDOWS ON A SECOND RESIDENCE. SOUTHWEST GASCORPORATION PERSONNEL RESPONDED TO THE SCENE OF THE ACCIDENT UPON NOTIFICATIONFROM THE LAS VEGAS FIRE DEPARTMENT. THE RESPONDING SOUTHWEST GASCREW WAS INFORMED UPON ARRIVAL BY THE LAS VEGAS FIRE DEPARTMENT OF A FIREWHICH APPEARED TO INVOLVE NATURAL GAS IN THE AREA OF THE METER AT 1402 E ST.LOUIS. THE SERVICE THAT FED NATURAL GAS TO THE HOUSE WAS EXCAVATED AND THEFLOW OF GAS TO THE METER WAS ELIMNATED BY CUTTING AND CAPPING THE SERVICE.THE CAUSE OF THE ACCIDENT IS UNDER INVESTIGATION. A SECTION OF THE GASSERVICE LINE WAS REMOVED AND SENT TO AN INDEPENDENT THIRD PARTY LAB.
2025-01-31 10:21 | YES | NO | 19990002 | 1999-01-06 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 1305 DALE | GARLAND | DALLAS | TX | 75040 | 3 | NO | 4 | 1998-12-05 | 0 | 0 | 85000 | 59368.1209 | 143342.3949 | Null | 13 | 0 |  | 19981205 | 19 | 55 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 1.25 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RON HASKOVEC | 2148122469 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | GROUND SHIFTING | Null |  | Null | 0 |  | Null |  |  | THE OPERATOR BELIEVES THAT EARTH MOVEMENT, SPECIFICALLY GROUND SHIFTING,CAUSED THE PIPING TO SEPARATE FROM THE COMPRESSION COUPLING OF A SERVICE TAP.THIS IS BELIEVED TO HAVE RESULTED IN A RELEASE OF GAS, WHICH MIGRATED INTO THEDWELLING AT 1305 DALE. IT REMAINS UNDETERMINED WHAT CAUSED THE GAS TO IGNITE.
2025-01-31 10:21 | NO | NO | 19990003 | 1999-01-04 | 18484 | SOUTHERN CALIFORNIA GAS CO | 5601 E LINCOLN AVE | CYPRESS | ORANGE | CA |  | 3 | NO | 1154 | 1998-12-04 | 0 | 0 | 55000 | 38414.6665 | 92750.9614 | Null | 3 | 36 |  | 19981207 | 44 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | COUPLING | STEEL |  | 8 | 0.25 |  |  | 0 | 1947 | UNDER PAVEMENT |  | W JEFF KOSKIE | 2132443283 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-12-02 | YES | 3 | PAINT OF PAVEMENT | YES |  |  | CONTRACTOR, USING TRACK MOUNTED TRENCHER HIT LINE, CUTTING THROUGH TOP OFMAIN. LINE WAS PROPERLY MARKED AND HAD BEEN EXPOSED AT POINT OF CONTACTBEFORE TRENCHING BEGAN. TOTAL LOSS IS EXPECTED TO BE APPROX. $55K.
2025-01-31 10:21 | YES | NO | 19990004 | 1998-12-28 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 4109 MALLARD LANDING CIRCLE | MIDLOTHIAN | CHESTERFIELD | VA | 23112 | 3 | NO | 658 | 1998-11-30 | 0 | 0 | 250000 | 174612.1204 | 421595.2791 | Null | 2 | 25 |  | 19981130 | 56 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT | THREADED | STEEL |  | 1 | 0.133 | API 5L | LANCASTER | 1992 | 1992 | ABOVE GROUND |  | NORMAN G DUREN | 8043235312 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A VEHICLE PARKED IN AN APARTMENT COMPLEX PARKING LOT ADJACENT TO 4109 MALLARDLANDING CIRCLE, JUMPED A CONCRETE CURB AND TRAVELED APPROXIMATELY 27 FEETACROSS A GRASSY AREA, PRIOR TO STRIKING AN ABOVE GROUND METER SETTING. THEVEHICULAR DAMAGE TO THE METER SET ASSEMBLY WAS A RESULT OF ERROR ON BEHALF OFTHE MOTOR VEHICLE OPERATOR. THE SUBSEQUENT FIRE AND ASSOCIATED WATER DAMAGERESULTED IN TOTAL DAMAGES TO THE STRUCTURE IN EXCESS OF $50,000 THEREBY,NECESSITATING AN INCIDENT REPORT BE FILED.
2025-01-31 10:21 | YES | NO | 19990016 | 1999-01-19 | 2748 | CONSUMERS POWER CO | 10 WEST MICHIGAN | GALESBURG | KALAMAZOO | MI | 49053 | 3 | NO | 626 | 1998-12-15 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 1 | 11 |  | 19981215 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER | WROUGHT IRON | 2 | 0.154 | API 5L |  | 0 | 1929 | UNDER PAVEMENT |  | JERRY F. HOLWERDA | 5177881835 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | BASED ON PRELIMINARY INVESTIGATION, GAS FROM A BROKEN MAIN MIGRATED INTOBUILDING AND WAS IGNITED BY UNKNOWN SOURCE CAUSING EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | YES | 19990017 | 1999-01-19 | 30822 | ASSOCIATED NATURAL GAS COMPANY | 200 W CHERRY | BLYTHEVILLE | MISSISSIPPI | AR | 72316 | 1 | NO | 1430 | 1998-12-14 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19981214 | 20 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | NO DATA |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 0 | ABOVE GROUND |  | BILL STUART | 8707639260 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | WHILE IN PROCESS OF DISCONTINUING PORTION OF 1 1/4 GAS LINE, EMPLOYEEINSTALLED A HYDRAULIC STEEL SQUEEZE-OFF MACHINE TO CURTAIL GAS FLOW. AFTERSEVERING GAS PIPE DOWN STREAM OF SQUEEZE-OFF, EMPLOYEE WAS IN PROCESS OFSEALING END OF PIPE BY ACETYLENE WELDING. DURING THIS ACTION, GAS LINESEPARATED AT POINT OF SQUEEZE-OFF CREATING IGNITION.
2025-01-31 10:21 | YES | YES | 19990018 | 1999-01-12 | 13782 | NORTHERN STATES POWER CO | 29 COURT HOUSE SQUARE | ST. CLOUD | STEAMS | MN | 56301 | 3 | Null | 1130 | 1998-12-11 | 4 | 1 | 5000000 | 3492242.4082 | 8431905.5828 | Null | 0 | 52 |  | 19981211 | 58 | 64 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | ASTM D2513 | DUPONT | 0 | 1982 | UNDER PAVEMENT |  | NICK J BOOSALIS | 6512292317 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-12-04 | YES | 3 | PAINT | YES |  |  | A UTILITY POLE ANCHOR, BEING INSTALLED BY A THIRD PARTY CONTRACTOR, CAME INTOCONTACT WITH THE POLYETHYLENE GAS SERVICE LINE FOR 29 COURT HOUSE SQUARE. THEANCHOR DAMAGED THE SERVICE LINE CAUSING GAS TO ESCAPE. GAS EXPLODED AFTERENTERING INTO THE ADJOINING BUILDING AT 30 9TH AVENUE NORTH.
2025-01-31 10:21 | YES | NO | 19990019 | 1999-01-11 | 11800 | LOUISIANA GAS SERVICE CO | 1000 ARIS AVENUE | METAIRIE | JEFFERSON | LA | 70005 | 4 | NO | 940 | 1998-12-03 | 0 | 0 | 150000 | 104767.2722 | 252957.1675 | Null | 6 | 0 |  | 19981203 | 70 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | SCHEDULE 40 |  | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | LEON T HINSON | 5043747265 | [6 empty] | Null |  | NO DATA |  | NO |  | NO | 0 |  | YES |  |  | MOST PROBABLE SCENARIO FOR EXPLOSION EVENT- FENCING CONTRACTOR WAS INSTALLINGA GATE. WHILE USING A JACKHAMMER TO BREAK THROUGH CONRETE ALONG SIDE THERESIDENCE, HE STRUCK AND BROKE THE 3/4' STEEL SERVICE LINE SERVING THE SUBJECTRESIDENCE. ESCAPING GAS ENTERED THE RESIDENCE THROUGH THE ROOF EAVE VENTS.THE GAS ENCOUNTERED AND UNDETERMINED IGNITION SOURCE, WHICH TOUCHED OFF THEEXPLOSION. GAS HAD BEEN TURNED OFF AT THE METER TEN MINUTES PRIOR TO THEEXPLOSION THEREBY REMOVING ANY PILOT LIGHT AS A POSSIBLE IGNITION SOURCE.
2025-01-31 10:21 | YES | YES | 19990020 | 1998-12-22 | 2748 | CONSUMERS POWER CO | 4201 BROWNELL AVENUE | FLINT | GENESEE | MI | 48504 | 3 | NO | 850 | 1998-11-19 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 25 |  | 19981119 | 55 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.113 | ASTM A53L | U S STEEL | 1955 | 1956 | WITHIN/UNDER BUILDING |  | JERRY F HOLWERDA | 5177881835 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXPLOSION & FIRE OCCURRED AT BLDG WHILE CO. CREW WAS REPLACING GAS SERVICERISER. EMPLOYEES DID NOT FOLLOW CO. WORK PROCEDURES TO LOCATE & CLOSE THESERVICE VALVE PRIOR TO EXCAVATION THE SERVICE RISER.
2025-01-31 10:21 | YES | NO | 19990021 | 1998-12-23 | 18532 | SOUTHERN UNION GAS CO | 1919 WEST 39TH STREET | AUSTIN | TRAVIS | TX | 78731 | 3 | NO | 1215 | 1998-11-18 | 0 | 0 | 75000 | 52383.6361 | 126478.5837 | Null | 0 | 5 |  | 19981118 | 35 | 60 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER |  | 1 | 0 | MODEL R-8100 | REYNOLDS | 1954 | 0 | WITHIN/UNDER BUILDING |  | SHANTEL H NORMAN | 5124651113 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | CONTRACT PAINTER HIRED BY PROPERTY OWNER WAS ALLEGEDLY ATTEMPTING TO TURN OFFWATER SERVICE TO THE RESIDENCE WHEN HE GAINED ACCESS TO A BELOW GROUND METERBOX SET AT A CURB NEAR THE RESIDENCE. THIS INDIVIDUAL MISTOOK THE GAS METERAND REGULATOR LOCATED IN THE "CURB" BOX FOR THE WATER METER. HE THENPROCEEDED TO MANIPULATE THE GAS REGULATOR IN A MANNER THAT APPEARED TO HAVEALLOWED AN ELEVATED PRESSURE TO FLOW DOWNSTREAM THROUGH THE METER AND INTO THEHOUSE PIPING. THIS INCREASE IN PRESSURE IS REPORTED BY THE FIRE INVESTIGATORTO HAVE CAUSED FLAME ROLLOUT AT THE BURNER TO THE WATERHEATER WHICH IGNITEDCOMBUSTIBLES LOCATED WITHIN THE CLOSET. FIRE SPREAD THROUGHOUT THE STRUCTURECAUSING FIRE DAMAGE TO STRUCTURE AND CONTENTS.
2025-01-31 10:21 | NO | NO | 19990022 | 1998-12-17 | 4483 | ENSTAR NATURAL GAS CO | HICKORY STREET, LOT 10 BLK AURORA HILLS |  | MATANUSKA-SUSITNA | AK | 99645 | 2 | Null | 1925 | 1998-12-07 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 1 | 25 |  | 19981207 | 55 | 60 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1997 | 1997 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON MONDAY EVENING, DECEMBER 7, 1998 AT APPROXIMATELY 7:25 PM AST, ENSTARNATURAL GAS COMPANY WAS ASKED TO RESPOND TO A HOUSE FIRE AT LOT 10 BLOCK 4,AURORA HILLS, SUBDIVISION, IN THE MATANUSKA SUSITNA BOROUGH NEAR PALMER,ALASKA. THE FIRE BURNED ENSTAR'S SERVICE LINE RISER. THE POLYETHYLENE GASSERVICE LINE INSIDE THE STEEL RISER MELTED, CAUSING A RELEASE OF NATURAL GAS.THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED BY ENSTAR PERSONNEL AT8:50 PM AST. THE HOUSE WAS STILL UNDER CONSTRUCTION AND NO METER WAS SET ATTHIS LOCATION AT THE TIME OF THE FIRE. FIRE DEPARTMENT OFFICALS SUSPECT THECAUSE OF THE FIRE TO A PORTABLE HEATER OR POSSIBLY A WOOD STOVE. ESTIMATEDDAMAGE TO THE STRUCTURE WAS APPROXIMATELY $50,000.
2025-01-31 10:21 | YES | NO | 19990023 | 1998-12-17 | 4483 | ENSTAR NATURAL GAS CO | WEST COTTONWOOD DRIVE, LOT 28 |  | MATANUSKA-SUSITNA | AK | 99645 | 2 | NO | 612 | 1998-12-10 | 0 | 0 | 100000 | 69844.8482 | 168638.1117 | Null | 1 | 38 |  | 19981210 | 55 | 60 | BY TEST | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1997 | 1997 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | ON THURSDAY MORNING, DECEMBER 10, 1998 AT APPROXIMATELY 6:12 AM AST, ENSTARNATURAL GAS COMPANY WAS ASKED TO RESPOND TO A HOUSE FIRE AT LOT 28 BLOCK 12,COTTONWOOD SHORES SUBDIVISION, IN THE MATANUSKA SUSITNA BOROUGH NEAR PALMER,ALASKA. THE FIRE BURNED ENSTAR'S SERVICE LINE RISER. THE POLYETHYLENE GAS7:50 AM AST. FIRE DEPARTMENT OFFICIALS BELIEVE PROPANE FROM A LEAKING TANKSTORED IN THE GARAGE IGNITED AND EXPLODED, CAUSING THE FIRE. ESTIMATED DAMAGETO THE STRUCTURE WAS APPROXIMATELY $100,000.
2025-01-31 10:21 | YES | NO | 19990024 | 1998-12-29 | 1640 | BOSTON GAS CO | 52 CANTERBURY STREET | HINGHAM | PLYMOUTH | MA |  | 3 | NO | 716 | 1998-11-24 | 0 | 0 | 250000 | 174612.1204 | 421595.2791 | Null | 0 | 56 |  | 19981124 | 45 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1 | 0 |  |  | 0 | 1947 | WITHIN/UNDER BUILDING |  | DANIEL F MCNAMARA | 6177235512 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-11-20 | NO | 0 |  | YES |  |  | ON NOVEMBER 24, 1998 AT APPROXIMATELY 7:16 AM, AN EXPLOSION AND FIRE OCCURREDAT 52 CANTERBURY STREET, HINGHAM, MA, DEMOLISHING A SINGLE FAMILY WOOD FRAME,RESIDENTIAL DWELLING. THE INCIDENT OCCURRED WHILE A THIRD-PARY EXCAVATOR,DIGGING WITH A LARGE TRACK EXCAVATOR ON PRIVATE PROPERTY ADJACENT TO THE HOUSEFOUNDATION TO INSTALL A SEWER LATERAL, STRUCK A ONE INCH STEEL GAS SERVICELINE OPERATING AT APPROXIMATELY 45 PSIG. THE ONE INCH STEEL GAS SERVICE LINEWAS PULLED OUTSIDE THE FRONT FOUNDATION WALL AND SUBSEQUENTLY BROKE AT THEINLET FITTING TO THE SERVICE REGULATOR ON THE INSIDE SERVIE RISER. THEEXCAVATOR IMMEDIATELY EVACUATED THE TWO RESIDENTS OF THE DWELLING AND THEEXPLOSION AND FIRE OCCURRED WITHIN MINUTES OF HIS STRIKING THE ON INCH STEELGAS SERVICE. THIS INCIDENT IS CURRENTLY BEING INVESTIGATED BY THE BOSTON GASCOMPANY AND THE COMMONWEALTH OF MASSACHUSETTS DEPARTEMENT OFTELECOMMUNICATIONS AND ENERGY.
2025-01-31 10:21 | NO | NO | 19990025 | 1999-01-15 | 603 | ARKLA, A NORAM ENERGY COMPANY | 5 MILES N OF REED OK | RIMROCK |  | OK |  | 1 | NO | 330 | 1998-07-29 | 0 | 0 | 5000 | 3492.2424 | 8431.9056 | Null | 0 | 0 |  |  | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | CUT LINE | OTHER PLASTIC |  | 0 | 0 |  |  | 0 | 0 | OTHER |  | STEVE BEAUCHAMP | 5802505413 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | LINE MARKERS | YES |  |  | DUG INTO LINE COUNTY DEPT.
2025-01-31 10:21 | NO | NO | 19990027 | 1999-01-25 | 8010 | IBERVILLE PARISH NATURAL GAS SYSTEM | ISLAND DEVELOPMENT - HWY 77 | PLAQUEMINE | IBERVILLE | LA | 70764 | 3 | NO | 830 | 1999-01-19 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 15 |  | 19990119 | 50 | 60 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DINAH ROCKFORTE | 2256875152 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | Null
2025-01-31 10:21 | NO | NO | 19990028 | 1999-02-10 | 603 | ARKLA, A NORAM ENERGY COMPANY |  | BEEBE | WHITE | AR |  | 3 | NO | 2100 | 1999-01-22 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 |  | 19990122 | 30 | 60 | BY TEST | 60 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0.0075 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | MARK NELSON | 50 2682434 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TORNADO | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | NO | 19990029 | 1999-02-09 | 2332 | CHEYENNE LIGHT FUEL & POWER | 521 E 21ST STREET | CHEYENNE | LARAMIE | WY | 82001 | 3 | NO | 2330 | 1999-01-29 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | Null | 0 | 20 |  | 19990201 | 12 | 12 | BY CFR 192.619(A)(3) | 0 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | JOINT | SCREWED | STEEL |  | 1 | 0.133 | API 5L |  | 0 | 1955 | UNDER PAVEMENT |  | DAVID B MCCLINTOCK | 3077782168 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 19990030 | 1999-02-09 | 18536 | SOUTHWEST GAS CORP | 104TH STREET & THUNDERBIRD ROAD | SCOTTSDALE | MARICOPA | AZ | 85239 | 3 | NO | 1205 | 1999-01-15 | 0 | 0 | 66500 | 45874.9836 | 110763.6542 | Null | 2 | 10 |  | 19990118 | 391 | 400 | BY TEST | 600 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | SCREWED | STEEL |  | 8 | 0.25 |  |  | 1994 | 1994 | UNDER GROUND OR UNDER WATER |  | PHILLIP S ANDREW | 6024845218 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES
2025-01-31 10:21 | YES | YES | 19990031 | 1999-02-01 | 15679 | PLAQUEMINE, CITY OF | CORNER OF MARSHALL & IRON FARM | PLAQUEMINE | IBERVILLE | LA | 70764 | 3 | NO | 1000 | 1999-01-18 | 0 | 1 | 0 | 0 | 0 | Null | 0 | 10 |  | 19990118 | 35 | 50 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | EQUIPMENT PUNCTURE | STEEL |  | 3 | 0.25 |  |  | 0 | 0 | UNDER PAVEMENT |  | RONNIE ROCKFORTE | 2256872461 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19990032 | 1999-02-02 | 15259 | PENNSYLVANIA GAS & WATER CO | 70 NORTH CHURCH STREET | CARBONDALE | LACKAWANNA | PA | 18407 | 3 | NO | 1109 | 1999-01-07 | 0 | 1 | 105000 | 72434.1847 | 174889.9804 | Null | 2 | 21 |  | 19990107 | 55 | 60 | BY TEST | 100 | CORROSION | CORROSION | UNSPECIFIED CORROSION | MAIN |  | OTHER | MAXI GRIP COUPLING | STEEL |  | 6 | 0 | CLASS 1 | COUPLING SYS, INC | 1985 | 1986 | UNDER PAVEMENT |  | JAMES M GREGER | 5708298866 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19990033 | 1999-01-25 | 603 | ARKLA, A NORAM ENERGY COMPANY | 4TH & DEWEY | BLACKWELL | KAY | OK | 74631 | 1 | NO | 155 | 1999-01-23 | 0 | 0 | 5000 | 3449.2469 | 8328.0943 | Null | 2 | 30 |  | 19990125 | 20 | 29 | BY TEST | 29 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REG STATION | REGULATOR/METER | MAXI GRIP COUPLING | STEEL |  | 2 | 0.125 |  |  | 0 | 1991 | ABOVE GROUND |  | ANTHONY CHANEY | 5803661132 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | Null | 1 |  | NO
2025-01-31 10:21 | YES | YES | 19990034 | 1999-01-28 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 121 BATAVIA | RIVER ROUGE | WAYNE | MI | 48218 | 3 | NO | 400 | 1998-12-25 | 1 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 0 | 0 |  | 19981225 | 5 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINE | OTHER | UNKNOWN | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS P FUNTSCH | 3135777026 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19990035 | 1999-01-25 | 14210 | OKLAHOMA NATURAL GAS CO | 711 MAPLE STREET | ALVA | WOODS | OK | 73717 | 3 | NO | 400 | 1998-12-27 | 1 | 0 | 0 | 0 | 0 | Null | 7 | 0 |  | 19981227 | 45 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT | BUTT FUSED | POLYETHYLENE PLASTIC |  | 4 | 0.391 | 2306 SDR11.5 | PHILLIPS | 1984 | 1984 | UNDER PAVEMENT |  | WILLIAM P KIMLER | 5802492233 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 19990036 | 1999-01-20 | 3510 | DOUGLAS GAS DEPT, CITY OF | 524 EAST RAILROAD STREET | DOUGLAS | COFFEE | GA | 31534 | 1 | YES | 2210 | 1999-01-11 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | Null | 0 | 31 |  | 19990112 | 4 | 18 | BY TEST | 18 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA | BUTT FUSED | OTHER | DRYER INSIDE BUILDING | 1.5 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS ADAMS | 9123893427 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19990037 | 1999-01-20 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 608 SUMMER | LAMPASAS | LAMPASAS | TX | 76550 | 3 | NO | 1348 | 1998-12-09 | 0 | 1 | 40000 | 27937.9393 | 67455.2447 | YES | 4 | 39 |  | 19981209 | 17 | 30 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 1 | 0 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RON HASKOVER | 2148122469 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1998-10-06 | YES | 3 | YELLOW PAINT AT MAIN LINE | YES
2025-01-31 10:21 | NO | NO | 19990038 | 1999-01-20 | 18484 | SOUTHERN CALIFORNIA GAS CO | 11307 WASHINGTON BLVD | CULVER CITY |  | CA |  | 3 | NO | 1503 | 1998-12-17 | 0 | 0 | 50000 | 34922.4241 | 84319.0558 | Null | 4 | 37 |  | 19981217 | 0 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0 |  |  | 0 | 0 | UNDER PAVEMENT |  | W JEFF KOSKIE | 2132443283 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | PAINT ON STREET & SIDE | Null
2025-01-31 10:21 | YES | NO | 19990043 | 1999-02-18 | 20211 | UNITED CITIES GAS CO | FAIRVIEW RD | WYTHEVILLE | WYTHE | VA | 24382 | 3 | NO | 216 | 1999-01-03 | 0 | 0 | 500000 | 344924.6889 | 832809.4303 | Null | 3 | 25 |  | 19990103 | 849 | 1250 | BY CFR 192.619(A)(3) | 1900 | CORROSION | CORROSION | UNSPECIFIED CORROSION | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JOE BLAVLOCK | 5407821501 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | NO | NO | 19990044 | 1999-02-24 | 15462 | PECO ENERGY DISTRIBUTION CO. | CONCORD ROAD AND I95 | CHESTER | DELAWARE | PA | 19013 | 1 | NO | 1201 | 1998-05-28 | 0 | 0 | 70654 | 49348.179 | 119149.5714 | Null | 1 | 52 |  | 19990209 | 20 | 20 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER | WROUGHT IRON | 8 | 0.329 |  |  | 0 | 1911 | UNDER GROUND OR UNDER WATER |  | ANDREW F BARTNIK | 6103802628 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | A CONTRACTOR WORKING FOR THE "CSX" WAS INSTALLING FIBER OPTIC CABLE PARALLELTO THE RAILROAD TRACKS IN CHESTER, PENNSYLVANIA. USING EARTH MOVING EQUIPMENT,AN 8-INCH WROUGHT IRON NATURAL GAS MAIN WAS STRUCK AND RUPTURED. THE UTILITYRIGHT-OF-WAY INTERSECTS WITH THE RAILROAD NEAR CONCORD ROAD AND I95. NODEATHS OR INJURIES WERE REPORTED.
2025-01-31 10:21 | YES | YES | 19990045 | 1999-02-25 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 5119 NORTHRIDGE | HOUSTON | HARRIS | TX | 77033 | 3 | NO | 852 | 1999-01-19 | 0 | 1 | 75000 | 51738.7033 | 124921.4145 | Null | 0 | 22 |  | 19990119 | 41 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | UNSPECIFIED CORROSION | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | NO DATA |  | JEFFREY A BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | AN EXPLOSION OCCURRED AT 5119 NORTHRIDGE. SEVERAL HOMES IN THE AREA WEREDAMAGED. THE SOURCE AND ORIGIN OF FUEL AND IGNITION SOURCE ARE UNDETERMINEDAT THIS TIME. OUR INVESTIGATION IS CONTINUING.
2025-01-31 10:21 | YES | YES | 19990046 | 1999-02-24 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 500 FT SOUTH OF SR#503 AT HIGHWAY 285 |  | SANTA FE | NM | 87505 | 3 | YES | 1340 | 1999-02-02 | 0 | 1 | 7500 | 5173.8703 | 12492.1415 | Null | 0 | 42 |  | 19990202 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.125 | A-25 | UNKNOWN | 1958 | 1973 | UNDER GROUND OR UNDER WATER |  | JOEL LEVINE | 5052414527 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1999-01-26 | YES | 3 | PAINT ON CONCRETE BARRIER | YES |  |  | ON FEBRUARY 2, 1999 AT1:40 PM, A.S.HORNER CALLED KYLE SAGER TO INFORM HIM THATTHEY HAD JUST HIT, AND BROKE, A GAS LINE. KYLE DISPATCHED A SERVICEMAN ANDHIS C&M CREW TO THE INCIDENT, WHICH WAS APPROXIMATELY 500 DEGREES SOUTH OF THEINTERSECTION OF US 285 AND S.R. 503. UPON ARRIVAL, PNM PERSONNEL GOT READY TOWELD A FITTING ONTO THE SEVERED MAIN TO PLUG OFF THROUGH, WHEN THE ESCAPINGGAS IGNITED. PNM PERSONNEL THEN MOVED ABOUT SIXTY FEET AWAY FROM WHERE THEWAS BURNING, AND EXPOSED THE MAIN. ONCE EXPOSED, THEY WELDED A 2" SHORTGAS WAS BURNING, AND EXPOSED THE MAIN. ONCE EXPOSED, THEY WELDED A 2" SHORTSTOPPER ONTO THE MAIN THROUGH WHICH THEY PLUGGED THE MAIN, AND STOPPED THEESCAPING GAS, AND IN DOING SO EXTINGUISHED THE FIRE. THE C&M FOREMAN WAS THENLOOKED AT BY PARAMEDICS AND IT WAS DECIDED TO TAKE HIM TO THE HOSPITAL FOR ACLOSER EXAMINATION. ONCE AT THE HOSPITAL, THE DOCTOR WHO EXAMINED HIM DECIDEDTO KEEP HIM OVER NIGHT FOR OBSERVATION. HE WAS RELEASED THE NEXT MORNING,WITH BURNS TO HIS FACE AND NECK AREA.
2025-01-31 10:21 | NO | NO | 19990047 | 1999-02-17 | 13710 | NICOR GAS CO. | 7603 BRISTOL LANE | HANOVER PARK | COOK | IL | 60103 | 3 | YES | 800 | 1999-02-03 | 0 | 0 | 25000 | 17246.2344 | 41640.4715 | Null | 1 | 45 |  | 19990203 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.29 | 1/2" CTS | DRISOPIPE | 1998 | 1999 | UNDER GROUND OR UNDER WATER |  | GEORGE WALDVOGEL | 6309838676 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | Null |  | Null |  |  | Null |  |  | A FAULT OR SHORT ON AN ELECTRICAL SERVICE LINE MELTED THE PLASTIC GAS SERVICELINE RESULTING IN AN IGNITION AND FIRE. SIX UNIT BUILDING WAS EXTENSIVELYDAMAGED ALONG WITH PERSONAL PROPERTY/FURNITURE, AND NO PERSONAL INJURIES ORFATALITIES.
2025-01-31 10:21 | YES | NO | 19990048 | 1999-02-23 | 13710 | NICOR GAS CO. | 2050 N BROADWAY STREET | CRESTHILL | WILL | IL | 60435 | 3 | NO | 744 | 1999-02-14 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | Null | 0 | 30 |  | 19990214 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 | B34-IMRV | SPRAGUE | 1976 | 1977 | WITHIN/UNDER BUILDING |  | GEORGE WALDVOGEL | 6309838676 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | EXTENSIVE FIRE DAMAGE TO THE BOILER BUILDING AND CONTENTS WITHIN THE BUILDING(I.E., GAS BOILERS AND AIR COMPRESSORS, CUSTOMER FUEL LINES) WERE OVERPRESSURIZED. THE SERVICE REGULATOR IS UNDER INVESTIGATION AS A POSSIBLE CAUSE.
2025-01-31 10:21 | YES | YES | 19990049 | 1999-02-22 | 2748 | CONSUMERS POWER CO | 10520 GROOMES DRIVE | WHITMORE LAKE |  | MI | 48189 | 3 | Null | 2211 | 1999-01-15 | 1 | 0 | 0 | 0 | 0 | Null | 1 | 39 |  | 19990116 | 50 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API-5L |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | JERRY F. HOLWERDA | 5177881835 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | BASED ON PRELIMINARY INVESTIGATION, GAS FROM A DAMAGED MAIN MIGRATED INTOBUILDING AND WAS IGNITED BY AN UNKNOWN SOURCE CAUSING AN EXPLOSION AND FIRE.MATTERS CONTAINED ON THIS PAGE OF THE FORM ARE STILL UNDER INVESTIGATION.WHEN CONCLUSIONS AS TO THE CAUSE OF THE BREAK ARE DRAWN, THIS PAGE OF THE FORMWILL BE UPDATED AND COMPLETED.
2025-01-31 10:21 | YES | YES | 19990052 | 1999-03-04 | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 13 CLIFFORD STREET | BINGHAMTON | BROOME | NY | 13901 | 3 | NO | 1432 | 1999-02-07 | 0 | 1 | 50000 | 34492.4689 | 83280.943 | Null | 7 | 22 |  | 19990207 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 |  | UNIL | 1926 | 1927 | WITHIN/UNDER BUILDING |  | ANDREW G SOLOMON | 6077624711 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | GAS (NATURAL) LEAK EMINATING FROM CRACKED 4" CAST IRON MAIN MIGRATED INTOBASEMENT OF DWELLING AT 13 CLIFFORD STREET. OCCUPANT IGNITED GAS BY SWITCHINGON LIGHT IN BASEMENT. RESULTING EXPLOSION DEMOLISHED DWELLING AND INJUREDOCCUPANT WHO WAS TREATED FOR BURNS AT THE HOSPITAL. EXPLOSION TOTALLYDESTROYED #13 CLIFFORD STREET HOME AND SEVERAL OTHERS. SPECIMAN OF CAST IRONPIPE IS BEING SENT TO METALLURGIST FOR ANALYSIS.
2025-01-31 10:21 | YES | NO | 19990053 | 1999-03-03 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 1925 AVENUE G | ANSON | JONES | TX | 79601 | 3 | NO | 158 | 1999-02-01 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | YES | 0 | 34 |  | 19990201 | 16 | 20 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.237 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | RON HASKOVEC | 2148122469 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | YES | 1964 | NO DATA |  | Null |  | Null |  |  | Null |  |  | CORROSION CAUSED A NATURAL GAS PIPE TO LEAK. THE OPERATOR BELIEVES THAT ANAPPARENT GAS ACCUMULATION AT THE SUBJECT RESIDENCE IGNITED.
2025-01-31 10:21 | NO | NO | 19990058 | 1999-03-04 | 1209 | BAY STATE GAS CO | PARK ST @ HIGHLAND AVE | LAWRENCE | ESSEX | MA | 01842 | 4 | NO | 630 | 1999-02-24 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 0 |  | 19990224 | 93 | 99 | BY CFR 192.619(A)(3) | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | FITTING |  | STEEL |  | 12 | 0.26 | API5L-X42 | CONSOLIDATED PIPE CO | 1998 | 1998 | OTHER | IN OPEN TRENCH | TIMOTHY A RICKFORD | 8005523047 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON FEBRUARY 23, 1999 AT 10" BARE STEEL MAIN WAS BEING RETIRED IN CONJUCTIONWITH THE INSTALLATION OF A NEW 12" COATED STEEL MAIN ON PARK STREET, LAWRENCE,MA. THIS INVOLVED INSTALLING LINE STOPPERS AT TWO LOCATIONS TO ISOLATE THEMAIN BEING RETIRED. AFTER CUTTING THE MAIN, IT WAS DETERMINED THAT AT 12"DRESSER END CAP WOULD BE INSTALLED BECAUSE OF THE STOPPERS NOT BEING BUBBLETIGHT. THE END CAP WAS INSTALLED AND STRAPPED WITH TWO 1" X .125" WELDEDSTEEL STRAPS. THE EXCAVATION WAS LEFT OPEN BUT PLATED AS ADDITIONAL WORK WASBE TO BE DONE AT THE LOCATION. AT APPROXIMATELY 6:30 AM ON FEBRUARY 24, 1999,THE END CAP PULLED OUT FROM THE END OF THE 12" MAIN BY BREAKING THE STRAPSTHAT HAD BEEN INSTALLED TO RESTRAIN THE FITTING.
2025-01-31 10:21 | YES | YES | 19990059 | 1999-03-04 | 1209 | BAY STATE GAS CO | 79 ASHLEY ST | SPRINGFIELD |  | MA |  | 1 | NO | 2258 | 1999-02-18 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 0 |  | 19990219 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0 |  |  | 0 | 1897 | UNDER PAVEMENT |  | THEODORE DULCHINOS | 4137819200 | [6 empty] | Null |  | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null |  |  | RESPOND TO A PUBLIC ODOR COMPLAINT AT #76 ASHLEY ST SPRINGFIELD. SERVICE TECHFOUND GAS IN HOUSE AND EVACUATED. LADY AT #79 CAME OUT OF HER HOUSE. TECHWENT IN AN FOUND FIRE AT ELECTRIC BOX AND EVACUATED. CHECKED OTHER HOUSES ANDEVACUATED 6 MORE HOUSES. CREW FOUND BROKEN 4" CAST IRON MAIN AND MADEREPAIR. TWO PEOPLE AT #79 SMELLED GAS IN BASEMENT. LADY TURNED ON OVERHEADLIGHT SWITCH WHICH IGNITED THE GAS AND FLASHED. BOTH WERE SENT TO THEHOSPITAL, ONE OF WHICH STAYED OVERNIGHT. OTHER THAN THE FIRE IN THE BASEMENTAT THE ELECTRICAL BOX, THE WINDOWS ON THE SIDE PORCH BLEW OUT AND THERE WASSOME STRUCTURAL DAMAGE TO THE FRONT OF THE HOUSE. THE MEDIA WAS ON THE SCENE.
2025-01-31 10:21 | YES | YES | 19990060 | 1999-02-11 | 1800 | BROOKLYN UNION GAS CO | LAFAYETTE AVE/BEDFORD AVE | BROOKLYN | KINGS | NY | 11238 | 4 | NO | 2039 | 1999-01-13 | 0 | 2 | 0 | 0 | 0 | Null | 0 | 6 |  | 19990209 | 0.25 | 0.4 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | CAST IRON |  | 8 | 0.46 |  |  | 0 | 1933 | OTHER | WITHIN EXCAVATION | FRANK J MARCAZZO | 7184032864 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | A FLASH FIRE OCCURRED FROM THE IGNITION OF A CRACKED 8" CAST IRON (0.25 PSIGOPERATING PRESSURE) GAS MAIN IN AN OPEN EXCAVATION. THREE BROOKLYN UNIONEMPLOYEES WERE INJURED, TAKEN TO THE HOSPITAL TREATED FOR BURNS, TWO ASINPATIENTS, ONE TREATED AND RELEASED. THIS WAS THE SCENE OF A GAS OUTAGE,CAUSED BY WATER ENTERING THE GAS MAIN FROM A BROKEN WATER MAIN. THE CAUSE OFTHE IGNITION IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19990061 | 1999-03-10 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 489 GROVE STREET | WHEATFIELD | JASPER | IN | 46392 | 3 | NO | 725 | 1999-02-09 | 0 | 2 | 125000 | 86231.1722 | 208202.3576 | Null | 3 | 0 |  | 19990209 | 300 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ASTM D2513 | UPONOR | 1997 | 1998 | UNDER GROUND OR UNDER WATER |  | DON J TOKOLY | 2196474770 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | AT 6:01 AM ON TUESDAY, FEBRUARY 9, 1999, NORTHERN INDIANA PUBLIC SERVICECOMPANY (NIPSCO) WAS NOTIFIED OF A POTENTIAL NATURAL GAS LEAK ALONG CENTERSTREET NEAR THE COMPANY'S WHEATFIELD-SOUTH REGULATOR STATION IN THE TOWN OFWHEATFIELD, INDIANA. THE GAS SERVICEMAN ARRIVED ON THE SCENE AT 7:13 AM ANDDISCOVERED GAS LEAKING FROM THE REGULATOR VENTS AT THE WHEATFIELD-SOUTHSTATION. THE WHEATFIELD-SOUTH REGULATOR STATION, BUILT IN 1966, IS ONE OF TWOREGULATOR STATIONS SUPPLYING THE TOWN OF WHEATFIELD. THE OTHER STATION,WHEATFIELD-NORTH, WAS RECENTLY CONSTRUCTED AND ACTIVATED TO MAINTAINACCEPTABLE DISTRIBUTION PRESSURE TO THE TOWN. BOTH STATIONS ARE A 4-REGULATORCONFIGURATION, CONTAINING OPERATOR AND MONITOR REGULATORS IN PARRALLEL RUNS.WHEATFIELD-NORTH ALSO CONTAINS A RELIEF VALVE ON THE DISTRIBUTION SIDE.REGULATORS AT EACH STATION ARE SET TO PROVIDE 50 PSIG INTO THE WHEATFIELDDISTRIBUTION SYSTEM. THE SERVICEMAN RADIOED CENTRAL DISPATCH REQUESTING FIELDASSISTANCE FROM THE GAS SYSTEMS OPERATIONS DEPARTMENT (GSO), THE GROUP THATMAINTAINS THE REGULATOR STATIONS. AFTER THIS REQUEST FOR ASSISTANCE, ATAPPROXIMATELY 7:25AM, AN EXPLOSION OCCURRED AT THE HOME OF MS. SANDRA GOTT,489 GROVE STREET, IN WHEATFIELD. FIVE OCCUPANTS IN THE HOME WERE TAKEN TO THEHOSPITAL FOR TREATMENT. (THREE OCCUPANTS WERE RELEASED LATER THAT SAME DAY,ONE WAS RELEASED SEVERAL DAYS LATER, AND ONE REMAIN HOSPITALIZED.) THE GASSERVICEMAN'S FIELD ASSESSMENT WAS RELAYED TO THE GAS OPERATING CENTER (GOC)WHICH INSTRUCTED HIM TO CLOSE THE VALVES AT THE WHEATFIELD-SOUTH REGULATORSTATION, TAKING IT OUT OF SERVICE. THE SERVICEMAN CLOSED THE VALVES AT THEREGULATOR STATION BUT REPORTED THAT GAS WAS STILL LEAKING FROM THE REGULATORVENTS. A TECHNICIAN FROM THE GSO DEPARTMENT ARRIVED AT WHEATFIELD-SOUTHSHORTLY AFTER 8AM AND OBSERVED THE PRESSURE CHART RECORDER WAS READING INEXCESS OF THE 150 PSIG RANGE OF THE INSTRUMENT. THE TECHNICIAN THEN DROVE TOTHE WHEATFIELD-NORTH STATION TO ASSESS THE SITUATION AT THAT LOCATION. UPONARRIVING AT THE WHEATFIELD-NORTH REGULATOR STATION THE TECHNICIAN NOTED THATTHE RELIEF VALVE ON THE DISTRIBUTION SIDE OF THE STATION WAS VENTING GAS TOTHE ATMOSPHERE. USING AND INDICATING PRESSURE GAUGE HE FOUND THE PRESSURE ONTHE DISTRIBUTION SYSTEM AT THAT SITE IN EXCESS OF THE 300 PSIG RANGE OF THEGAUGE. AT APPROXIMATELY 8:15AM THE TECHNICIAN CLOSED THE VALVES TO THEWHEATFIELD_NORTH REGULATOR STATION, TAKING IT OUT OF SERVICE. FIELDMAINTENANCE PERSONNEL FROM THE GSO DEPARTMENT ARRIVED ON THE SCENE AND BEGANTO REMOVE A BLIND FLANG TO A BLOW-OFF VALVE ON THE DISTRIBUTION SIDE OF THEWHEATFIELD-SOUTH STATION. BY 8:45AM THE BLOW-OFF VALVE WAS OPENED ANDRELEASING GAS FROM THE DISTRIBUTION SYSTEM. BY 9:15AM DISTRIBUTION PRESSUREWAS FULLY RELIEVED. NIPSCO PERSONNEL BEGAN DEVELOPING AN INCIDENT ASSESSMENTAND RESTORATION STRATEGY. OVER THE FOLLOWING HOURS MEMBER OS THE GSODEPARTMENT INVESTIGATED THE CAUSE OF THE OVERPRESSURE SITUATION. FOLLOWINGREACTIVATION OF THE WHEATFIELD-SOUTH STATION A LEAK SURVEY OF THE ENTIRESYSTEM WAS PERFORMED. LOCAL DISTRIBUTION CONSTRUCTION AND MAINTENANCEPERSONNEL STARTED CUSTOMER RELIGHTS AT APPROXIMATELY 4:30 PM TUESDAY, WHICHWERE COMPLETED BY 5PM WEDNESDAY. ALL SERVICE REGULATORS ON METER SETS WEREREPLACED BEFORE RESTORING SERVICE TO INDIVIDUAL HOMES. INVESTIGATION INTO THECAUSE OF THE BUILD-UP OF PRESSURE IN THE DISTRIBUTION SYSTEM IS ON-GOING.UNTIL THE INVESTIGATION IS COMPLETED, THE EXACT CAUSE REMAINS UNKNOWN BUT MAYINCLUDE MALFUNCTION OF THE OPERATOR AND MONITOR REGULATORS AND INADEQUATERELIEF VALVE VENTING AT THE WHEATFIELD-NORTH REGULATOR STATION. INVESTIGATIONINTO THE CAUSE OF THE EXPLOSION AT 489 GROVE STREET ALSO CONTINUES. TO DATE,THE INVESTIGATION HAS UNCOVERED THE PRESENCE OF NICKS AND GOUGES IN THEPLASTIC GAS SERVICE LINE NEAR THE HOUSE CRAWL SPACE.
2025-01-31 10:21 | YES | NO | 19990065 | 1998-04-15 | 792 | ATLANTA GAS LIGHT CO | 211 VALLEY BROOK DRIVE | WOODSTOCK | CHEROKEE | GA | 30188 | 3 | NO | 725 | 1998-03-20 | 0 | 0 | 200000 | 139689.6963 | 337276.2233 | Null | 0 | 15 |  | 19980320 | 0.25 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0 | 0 | 3/4" UNION |  | 0 | 1987 | ABOVE GROUND |  | WILLIAM H PARK | 7709265792 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | YES |  |  | A 3/4" STEEL INSULATED UNION DOWNSTREAM OF THE NATURAL GAS METER WAS DAMAGEDBY LIGHTING. THE ESCAPING GAS IGNITED DAMAGING THE HOUSE.
2025-01-31 10:21 | YES | NO | 19990066 | 1999-03-09 | 31202 | RELIANT ENERGY - ARKLA | 8401 QUAIL HOLLOW | TEXARKANA | BOWIE | TX | 75501 | 2 | NO | 800 | 1999-02-09 | 0 | 0 | 200000 | 137969.8756 | 333123.7721 | Null | 0 | 20 |  | 19990209 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | HOUSE | OTHER | NONE | OTHER | UNKNOWN | 0 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | KYLE HOLCOMB | 7038241304 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null |  |  | HOUSE FIRE THAT IS STILL UNDER INVESTIGATION. GAS IS NOT INVOLVED. CALL WASMADE DUE TO THE PROPERTY VALVE.
2025-01-31 10:21 | YES | NO | 19990067 | 1999-03-18 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 4300 GESSNER | HOUSTON | HARRIS | TX | 77041 | 3 | NO | 1700 | 1999-02-18 | 0 | 0 | 222850 | 153732.9339 | 371183.1631 | YES | 2 | 50 |  | 19990218 | 43 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | NONE | POLYETHYLENE PLASTIC |  | 6 | 0.576 | D2513 |  | 0 | 1998 | UNDER PAVEMENT |  | JEFFREY A BISH | 7139678093 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | YES |  |  | THIRD PARTY DOING RECONSTRUCTION ROAD WORK DAMAGED A 6" IP PLASTIC MAIN ANDESCAPING GAS IGNITED.
2025-01-31 10:21 | YES | YES | 19990068 | 1999-03-22 | 19080 | PEOPLES GAS CO | 11762 HARBORSIDE CIRCLE | SEMINOLE | PINELLAS | FL | 33773 | 1 | NO | 1700 | 1999-03-12 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 0 |  | 19990315 | 60 | 66 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE | NONE | POLYETHYLENE PLASTIC |  | 0.84 | 0.09 | ANSI B31.8 | CONTINENTAL INDUSTRIES | 0 | 1984 | UNDER GROUND OR UNDER WATER |  | TIMOTHY J KASPRZYK | 8132284831 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | TELEPHONE EMPLOYEE WAS USING A TORCH TO INSTALL A "SHRINK SLEEVE" AROUND ATELEPHONE CABLE IMMEDIATELY ADJACENT TO AND BELOW THE SERVICE LINE.
2025-01-31 10:21 | YES | YES | 19990071 | 1999-03-25 | 11032 | LACLEDE GAS CO | 688 MERAMEC STATION ROAD | VALLEY PARK | ST LOUIS | MO | 63088 | 3 | NO | 1600 | 1999-02-22 | 1 | 0 | 0 | 0 | 0 | Null | 2 | 40 |  | 19990222 | 38 | 60 | BY CFR 192.619(A)(3) | 0 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0.04 | ASTM B-88 |  | 0 | 1965 | WITHIN/UNDER BUILDING |  | PAUL B HUNKER | 3143420528 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null |  |  | Null |  |  | VISUAL INSPECTION FOUND A CORROSION HOLE ON THE BODY OF THE COPPER SERVICELINE AT THE TEE CONNECTION TO THE MAIN SERVING 688 MERAMEC STATION ROAD. THISLOCATION WAS IN THE RIGHT-OF-WAY OF JEFFERSON AVENUE ADJACENT TO THE PROPERTYOF 688 MERAMEC STATION ROAD. THE SERVICE LINE SECTION WAS REMOVED AND WILLUNDERGO METALLURGICAL ANALYSIS TO DETERMINE THE CAUSE OF FAILURE IN ACCORDANCEWITH 49CFR 192.617.
2025-01-31 10:21 | YES | YES | 19990072 | 1999-03-23 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 2634 14TH | DETROIT | WAYNE | MI | 48216 | 3 | NO | 1525 | 1999-03-15 | 0 | 1 | 0 | 0 | 0 | Null | 2 | 45 |  | 19990315 | 0.25 | 10 |  | 0 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0 |  |  | 0 | 1894 | UNDER PAVEMENT |  | THOMAS P FUNTSCH | 3135777026 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | DISTRIBUTION EMPLOYEES WERE CUTTING AND CAPPING A SERVICE. THEY INADVERTENTLYBROKE OFF THE SERVICE TEE ON 12' CAST IRON MAIN AT 1/4# PRESSURE. THEY WEREIN THE PROCESS OF CLEANING OFF THE MAIN WHEN THE LEAKING NATURAL GAS IGNITED.THE SOURCE OF IGNITION IS UNKNOWN. INJURIED WERE: ROBERT KARAFFA, GARYKNUCKEY, AND ROBERT KOWALSKI. ALL THREE WERE TRANSPORTED TO RECEIVINGHOSPITAL BY EMS.
2025-01-31 10:21 | YES | YES | 19990073 | 1999-03-25 | 1736 | BRIDGEPORT UTILITIES BOARD | 406 ALABAMA AVE | BRIDGEPORT | JACKSON | AL | 35740 | 3 | NO | 1002 | 1999-01-22 | 4 | 5 | 0 | 0 | 0 | NO | 0 | 15 | 471468 | 19990122 | 35 | 35 | BY TEST | 35 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | NO DATA |  | 0.75 | 0 |  |  | 0 | 1958 | WITHIN/UNDER BUILDING |  | WILLIAM J HUGHES | 2564952471 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | SERVICE LINE WAS PULLED BY EXCAVATOR'S BACKHOE. AS A RESULT THE SERVICE LINE(3/4" GALV.) WAS BROKEN UNDERGROUND AT THE RISER.
2025-01-31 10:21 | YES | YES | 19990076 | 1999-04-05 | 15469 | PHILADELPHIA GAS WORKS | 3600 GAUL STREET | PHILADELPHIA | PHILADELPHIA | PA | 19134 | 4 | NO | 650 | 1999-03-07 | 0 | 8 | 500000 | 344924.6889 | 832809.4303 | Null | 0 | 45 |  | 19990307 | 0.25 | 0.5 |  | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.485 |  |  | 0 | 1928 | UNDER PAVEMENT |  | BRIAN C SCHENK | 2156846372 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | TREE ROOTS | Null |  | Null | 0 |  | Null |  |  | THE FACTORS BELIEVED TO HAVE CONTRIBUTED TO THIS INCIDENT HAVE BEENINVESTIGATED BY THE PHILADELPHIA FIRE MARSHALLS' OFFICE AND THE PHILADELPHIAGAS WORKS (PGW). PGW FOUND A CIRCUMFERENTIAL BREAK ON A 6" CAST IRON MAIN ATTHE SERVICE TO 3587 GAUL AND LOCATED 47' 9" SOUTH OF THE SOUTH CURB LINE OFVENANGO STREET. THE INVESTIGATION ALSO FOUND A LARGE TREE WITH SEVERAL OF ITSLARGE ROOTS OVERGROWN AROUND THE GAS MAIN. IT IS BELIEVED THAT THEIMPINGEMENT OF THESE ROOTS CONTRIBUTED TO THE BREAK. THIS BREAK IN THE CASTIRON MAY HAVE ALLOWED NATURAL GAS TO MIGRATE INTO THE BASEMENTS OF 3587, 3589AND/OR 3591. THE CAUSE OF IGNITION IS UNKNOWN AT THIS TIME.
2025-01-31 10:21 | YES | YES | 19990077 | 1999-04-05 | 15469 | PHILADELPHIA GAS WORKS | 400 CHANDLER STREET | PHILADELPHIA | PHILADELPHIA | PA | 19111 | 4 | NO | 1018 | 1999-03-06 | 0 | 2 | 200000 | 137969.8756 | 333123.7721 | Null | 0 | 32 |  | 19990306 | 0.25 | 0.5 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | FLEXIBLE CONNECTION/OVEN | OTHER | FLEXIBLE CONNECTOR | 0.75 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | BRIAN C SCHENK | 2156846372 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | THE PHILADELPHIA FIRE MARSHALL'S OFFICE HAS CONCLUDED THAT THAT A FAILURE OFTHE 3/4" FLEXIBLE TUBING FOR THE WALL OVEN UNIT WAS THE CAUSE OF THEINCIDENT. THE INVESTIGATION FOUND THIS UNIT TO BE SEVERELY DAMAGED WITH THEEND CONNECTION VERY LOOSE. THE APPARENT CAUSE OF IGNITION WAS DETERMINED TOBE THE REFRIGERATOR COMPRESSOR MOTOR.
2025-01-31 10:21 | YES | YES | 19990078 | 1999-03-30 | 30736 | UGI UTILITIES INC | 211 S 3RD AVENUE | WEST READING | BERKS | PA | 19611 | 3 | NO | 805 | 1999-03-08 | 1 | 4 | 290000 | 200056.3196 | 483029.4695 | Null | 1 | 5 |  | 19990308 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT | THREADED | STEEL |  | 0.75 | 0.113 | UNKNOWN | UNKNOWN | 0 | 1960 | WITHIN/UNDER BUILDING |  | JEFFREY C FREY | 6107365434 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1999-02-28 | YES | 3 | PAINT | YES |  |  | ON MARCH 8, 1999, AT 8:05 HOURS, UGI UTILITIES, INC RECEIVED A CALL THATCONTRACTOR HIT THE GAS LINE AT 213 S. 3RD AVENUE, WEST READING. THECONTRACTOR, WEXCON, INC. HIT THE 3/4" XTC COATED STEEL MEDIUM PRESSURE SERVICELINE, FEEDING A SIX UNIT APARTMENT BUILDING. THE GAS LINE BROKE AT A 90DEGREE THREADED ELL FITTING AT THE SERVICE ENTRANCE TO THE BUILDING. THEESCAPING GAS WAS IGNITED RESULTING IN A FIRE DESTROYING THE BUILDING. THEREWAS ONE FATALITY AND FOUR INJURIES.
2025-01-31 10:21 | NO | NO | 19990079 | 1999-03-29 | 4060 | EAST OHIO GAS CO | 7995 JOHNNYCAKE RIDGE RD | MENTOR | LAKE | OH | 44076 | 0 | Null | 850 | 1999-03-01 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | Null | 0 | 15 |  | 19990301 | 40 | 50 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE | THREADED | POLYETHYLENE PLASTIC |  | 6.625 | 0.576 | SDR 13.5 | DRISCO | 1998 | 1999 | UNDER GROUND OR UNDER WATER |  | CLARENCE W MOORE | 2167366835 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES | 1999-02-25 | YES | 2 |  | YES |  |  | SEWER CONTRACTOR HIT 6" PLASTIC MAINLINE. CONTRACTOR FAILED TO OBSERVEPROPERLY MARKED PIPELINE (OUPS). LINE HAD OIL IN IT THAT SPRAYED ONTO PUBLICAND PRIVATE PROPERTY. OIL WAS TESTED FOR PCB. AREA WAS ENVIRONMENTALLYCLEANED UP.
2025-01-31 10:21 | NO | NO | 19990083 | 1999-04-14 | 13782 | NORTHERN STATES POWER CO | 659 JEFFERSON AVE | ST PAUL | RAMSEY | MN | 55102 | 3 | NO | 100 | 1999-03-11 | 0 | 0 | 70000 | 48289.4565 | 116593.3202 | Null | 0 | 9 |  | 19990311 | 56 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  | FISHER | 1980 | 1981 | ABOVE GROUND |  | NICK J BOOSALIS | 6512292317 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | MELTING SNOW --> ICE | Null |  | Null | 0 |  | Null |  |  | WATER, ASSUMED TO BE FROM MELTING SNOW ON ROOF, FROZE AROUND A FISHER S254SERVICE REGULATOR, INCLUDING THE VENT OPENING WHICH WAS POINTING DOWN. EXCESSPRESSURE OCCUURED IN THE HOUSEPIPING. GAS ESCAPED FROM HOUSEPIPING AND WASIGNITED BY AN UNDETERMINED SOURCE OF IGNITION.
2025-01-31 10:21 | NO | NO | 19990084 | 1999-04-14 | 13782 | NORTHERN STATES POWER CO | 941 EDMUND AVE | ST PAUL | RAMSEY | MN | 55104 | 3 | NO | 607 | 1999-03-13 | 0 | 0 | 60000 | 41390.9627 | 99937.1316 | NO | 0 | 32 |  | 19990313 | 56 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  | FISHER | 1979 | 1980 | ABOVE GROUND |  | NICK J BOOSALIS | 6512292317 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | WATER, ASSUMED TO BE FROM MELTING SNOW ON ROOF, FROZE ON THE VENT SCREEN(POINTING DOWN) OF A FISHER S254-4 SERVICE REGULATOR. EXCESS PRESSUREOCCURRED IN THE HOUSEPIPING. GAS ESCAPED FROM HOUSEPIPING AND WAS IGNITED BYUNDETERMINED SOURCE OF IGNITION.
2025-01-31 10:21 | NO | NO | 19990085 | 1999-04-16 | 14210 | OKLAHOMA NATURAL GAS CO | NW/4 SECTION 11-T02N-R23W | DUKE | JACKSON | OK | 73532 | 1 | NO | 200 | 1999-03-13 | 0 | 0 | 59500 | 41046.038 | 99104.3222 | Null | 2 | 30 |  | 19990314 | 419 | 500 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR SETTING | REGULATOR/METER |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JIM KUNKEL | 4055566401 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null |  |  | ON SATURDAY, MARCH 13, 1999, A MONITOR REGULATOR STATION SERVING THE REPUBLICGYPSUM PLANT FROM OUR HIGH-PRESSURE DISTRIBUTION SYSTEM FAILED IN THE OPENEDPOSITION. THE MALFUNTION APPARENTLY WAS CAUSED BY AN APPARENT WATER VAPOR INTHE GAS STREAM FREEZING THE REGULATOR CONTROLS. THIS RESULTED IN 419 PSIG OFGAS PRESSURE ENTERING THE CUSTOMER'S EXTENSIVE PLANT PIPING SYSTEM RATED AT 60PSIG MAOP. OUR TECHNICIANS RESPONDED TO THE REMOTE LOCATION, ISOLATED THEPLANT PIPING, AND PERFORMED MAINTENANCE ON THE MONITOR SETTING TO GET IT INPROPER WORKING CONDITION. DURING THIS PERIOD, PLANT PERSONNEL WERE REPLACINGSOME OF THEIR INTERNAL REGULATORS AND ISOLATING VARIOUS PIPING SYSTEMS FROMTHE MAIN PLANT PIPING IN ORDER TO GET THE PLANT BACK IN OPERATION. THE PLANTPERSONNEL ASSURED US THAT REPAIRS WERE MADE AND PIPING WAS IN PROPER ORDERAND HAD OUR TECHNICIANS INITIATE SERVICE TO THE PLANT AFTER A 40 PSIG LEAKCHECK WAS PERFORMED. SEVERAL MINUTES AFTER THE TECHNICIANS LEFT THELOCATION, THE MONITOR REGULATOR SETTING ONCE AGAIN MALFUNCTIONED AND OVERPRESSURED THE PLANT PIPING. OUR TECHNICIANS RETURNED AND ISOLATED THE PLANTPIPING DETECTED GAS ODOR. IT APPEARED THAT SOME PLANT PIPING HAD EITHER BEENSUBSEQUENTLY DAMAGED OR THAT THE PLANT PERSONNEL HAD OPENED VALVES ANDALLOWED GAS INTO THE PREVIOUSLY DAMAGED, BUT ISOLATED SEGMENTS OF THEIRSYSTEM. AT THIS POINT, WE SOLICITED ASSISTANCE FROM THE FIRE MARSHALL TOENSURE THE FULL COOPERATION OF THE PLANT PERSONNEL THAT WOULD ENABLE US TODETERMINE THE EXTENT OF ANY PIPING DAMAGE AND THE OPERATIONAL CHARACTERISTICSOF THEIR SYSTEM. AFTER SURVEYING THEIR SYSTEM PIPING, CHECKING FOR LEAKS,AND DETERMINING WHAT POSSIBLE DAMAGES THAT COULD HAVE TAKEN PLACE, WE MADE AMANAGEMENT DECISION TO REPLACE ALL OF THE UNDERGROUND PLANT PIPING TOELIMINATE ANY POSSIBLITY OF AN UNDETECTED SAFETY PROBLEM. THIS WAS NOT APOPULAR DECISION AT THIS TIME WITH THE PLANT MANAGER OR OWNER WHOSE PRIMARYCONCERN WAS PLANT PRODUCTIVITY RATHER THAN SAFETY. GATHERING MATERIAL,FINDING A CONTRACTOR WHO COULD HANDLE THE WORK ON SHORT NOTICE, NEGOTIATING ACONTRACT PRICE, GETTING THE MATERIAL TO SUCH A REMOTE LOCATION, AND REPLACINGTHE PLANT PIPING IN ADDITION TO REBUILDING OUR MONITOR REGULATOR SETTING OVERA WEEKEND WAS A LABORIOUS PROCESS THAT CONSUMED SEVERAL HOURS. DURING THISPERIOD, WE NOTIFIED THE OKLAHOMA CORPORATION COMMISION PIPELING SAFETYREPRESENTATIVE OF THE INCIDENT ON MARCH 13, 1999. ON MARCH 14, 1999, WECONCLUDED FROM ITEMIZING THE MAN HOURS, MATERIAL COST, ETC., INVOLVED WITHOUR PRECAUTIONARY ACTIONS AND REMEDIATION THAT COSTS MIGHT EXCEED $50,000 ANDREPORTED THE INCIDENT TO THE NATIONAL RESPONSE CENTER.
2025-01-31 10:21 | YES | NO | 19990087 | 1999-04-20 | 18308 | SIERRA PACIFIC POWER CO | 355 BROADWAY | RENO | WASHOE | NV | 89502 | 3 | NO | 2049 | 1999-03-16 | 0 | 0 | 130000 | 89680.4191 | 216530.4519 | Null | 0 | 45 |  | 19990316 | 38 | 40 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | API 5L |  | 0 | 1963 | UNDER PAVEMENT |  | KIMBERLY RALEY | 7758343265 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES |  |  | AN IGNITION OCCURRED DUE TO A RELEASE OF NATURAL GAS FROM A DAMAGED 3/4"WELDED X-TRU COAT PIPE. DAMAGE TO PIPE WAS CAUSED BY AN UNKNOWN 3RD PARTY.
2025-01-31 10:21 | YES | NO | 19990088 | 1999-04-27 | 2748 | CONSUMERS POWER CO | 1434 EAST JOLLY ROAD | LANSING | INGHAM | MI | 48910 | 3 | NO | 555 | 1999-03-19 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | Null | 1 | 23 |  | 19990319 | 53 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | SERVICE VALVE | JOINT |  | CAST IRON |  | 1.25 | 0.151 | MSS SP-78 | PHILLIPS | 1992 | 1992 | ABOVE GROUND |  | JERRY F HOLWERDA | 5177881835 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | TWO BOLTS WERE REMOVED FROM FLANGE AT SERVICE VALVE IN WHAT APPEARS TO BESABOTAGE. APPARENTLY, GAS LEAKING FROM THE FLANGE IGNITED, CAUSING A FIREWHICH DESTROYED THE BUILDING (GREENHOUSE).
2025-01-31 10:21 | YES | NO | 19990089 | 1999-04-27 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | 1305 DALE | GARLAND | DALLAS | TX | 75040 | 3 | NO | 4 | 1998-12-05 | 0 | 0 | 85000 | 59368.1209 | 143342.3949 | YES | 13 | 0 |  | 19981205 | 19 | 55 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT | COUPLING | STEEL |  | 1.25 | 0 | UNKNOWN | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | RON HASKOVER | 2148122469 | [6 empty] | Null |  | EARTH MOVEMENT: OTHER | GROUND SHIFTING | Null |  | Null | 0 |  | Null |  |  | THE OPERATOR BELIEVES THAT EARTH MOVEMENT, SPECIFICALLY GROUND SHIFTING,CAUSED THE PIPING TO SEPARATE FROM THE COMPRESSION COUPLING OF A SERVICE TAP.THIS IS BELIEVED TO HAVE RESULTED IN A RELEASE OF GAS, WHICH MIGRATED INTO THEDWELLING AT 1305 DALE. IT REMAINS UNDETERMINED WHAT CAUSED THE GAS TO IGNITE.
2025-01-31 10:21 | YES | NO | 19990090 | 1999-04-30 | 15518 | PIEDMONT NATURAL GAS CO INC | 1915 REXFORD ROAD | CHARLOTTE | MECKLENBURG | NC | 28211 | 3 | NO | 1103 | 1999-03-31 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | Null | 1 | 7 |  | 19990331 | 60 | 75 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 | FILTER | AMERICAN | 1988 | 1988 | ABOVE GROUND |  | RONALD W COBB | 7043643120 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | Null |  |  | CAR STRUCK METER SET.
2025-01-31 10:21 | NO | NO | 19990091 |  | 15931 | PUBLIC SERVICE CO OF COLORADO | 23038 ISOLETA RD | INDIAN HILLS | JEFFERSON | CO | 80454 | 1 | Null | 100 | 1999-04-23 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | Null | 1 | 0 |  | 19990423 | 0 | 0 |  | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | BARBARA A BOGER | 3036713824 | [6 empty] | Null |  | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | DUE TO HEAVY SNOW A BRANCH FROM EVERGREEN TREE BROKE FROM THE TREE, FALLING ONMETER SET, PULLING FITTINGS FROM PUBLIC SERVICE GAS SERVICE PIPE AND HOUSEFUEL LINE. MOST LIKELY A FITTING INSIDE THE HOUSE ALSO PULLED AND CAUSED AGAS LEAK, WITH IGNITION FROM A PILOT LIGHT INSIDE. NO ONE WAS INJURED OREVACUATED FROM NEIGHBORING HOMES.
2025-01-31 10:21 | YES | YES | 19990092 | 1999-05-18 | 15931 | PUBLIC SERVICE CO OF COLORADO | 19401 E 45TH AVE | DENVER | DENVER | CO | 80239 | 3 | NO | 1225 | 1999-05-03 | 0 | 1 | 125000 | 86231.1722 | 208202.3576 | Null | 7 | 30 |  |  | 40 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | OTHER | 3/4" UNION | POLYETHYLENE PLASTIC |  | 4 | 0.391 | 2H06 ASTMD2513 | PLEXCO | 0 | 1983 | WITHIN/UNDER BUILDING |  | RANDY UTECHT | 3035713911 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null | OTHER | UNDETERMINED
2025-01-31 10:21 | YES | YES | 19990093 | 1999-05-14 | 13710 | NICOR GAS CO. | 91 STRAW FLOWER CT | ROMEOVILLE | WILL | IL | 60441 | 3 | Null | 1435 | 1999-04-29 | 0 | 2 | 1500 | 1034.7741 | 2498.4283 | NO | 1 | 32 |  | 19990429 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | ASTM 2513 | PHILIP DRISCO | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | GEORGE WALDVOGEL | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-04-23 | YES | 3 | 1999-04-23 | YES | NO DATA
2025-01-31 10:21 | YES | NO | 19990094 | 1999-05-14 | 15342 | PEOPLES GAS SYSTEM INC | 5641 FIRST AVENUE NORTH | ST PETERSBURG | PINELLAS | FL | 33710 | 1 | NO | 2034 | 1999-03-15 | 0 | 0 | 80000 | 55187.9502 | 133249.5088 | Null | 0 | 7 |  | 19990506 | 15 | 19 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | TIMOTHY J KASPRZYK | 8132284831 | [6 empty] | Null |  | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null
2025-01-31 10:21 | YES | YES | 19990095 | 1999-05-25 | 11682 | LONE STAR GAS CO (DISTRIBUTION DIVISION) | BIRCH & S. CONNALLY | ELM MOTT | MCLENNAN | TX | 76640 | 2 | NO | 1730 | 1999-04-19 | 0 | 1 | 0 | 0 | 0 | Null | 1 | 30 |  | 19990419 | 13 | 15 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE 2406 | UNKNOWN | 0 | 1993 | UNDER GROUND OR UNDER WATER |  | RON HOSKOVEC | 2148122469 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES
2025-01-31 10:21 | NO | NO | 19990096 | 1999-05-25 | 15931 | PUBLIC SERVICE CO OF COLORADO | 3404 E HARMONY ROAD | FORT COLLINS | LARIMER | CO | 80525 | 3 | NO | 1646 | 1999-05-19 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 44 |  | 19990519 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 3 | 0.156 | GRADE B |  | 1984 | 1985 | UNDER GROUND OR UNDER WATER |  | RANDY BLANK | 9702257847 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | NO | 3 | NO MARKING-MISSED LOCATE | YES
2025-01-31 10:21 | YES | YES | 19990098 | 1999-06-03 | 18456 | SOUTHEAST ALABAMA GAS DISTRICT | 619 DAVIS LANE | EUFAULA | BARBOUR | AL | 36027 | 3 | NO | 1428 | 1999-05-01 | 0 | 1 | 90000 | 62086.444 | 149905.6974 | Null | 1 | 45 |  | 19990501 | 27 | 50 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.5 | 0 |  | POLY ARK | 0 | 1987 | UNDER GROUND OR UNDER WATER |  | ARNIE C COBB JR | 3342224177 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | YES |  | Null | 3 | YELLOW PAINT AND FLAGS | YES
2025-01-31 10:21 | YES | NO | 19990099 | 1999-06-08 | 14210 | OKLAHOMA NATURAL GAS CO |  | OKLAHOMA CITY | OKLAHOMA | OK |  | 0 | Null | 1800 | 1999-05-03 | 0 | 0 | 1000000 | 689849.3779 | 1665618.8605 | YES | 0 | 0 |  | 19990503 | 0 | 0 |  | 0 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  | 0 | 0 |  |  | 0 | 0 | ABOVE GROUND |  | JIM KUNKEL | 4055566401 | [6 empty] | Null |  | NO DATA |  | Null |  | Null |  |  | Null
2025-01-31 10:21 | YES | YES | 19990102 | 1999-06-16 | 22182 | WASHINGTON GAS LIGHT CO |  | SOUTH RIDING | LOUDOUN | VA | 22021 | 3 | Null | 27 | 1998-07-07 | 1 | 1 | 380000 | 265410.423 | 640824.8243 | NO | 3 | 30 |  | 19980707 | 31 | 60 |  | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTMD2413 | DRISCO PIPE | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | JAMES O BIELASKI | 7037505566 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 19990103 | 1999-06-28 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 2900 FERN VALLEY ROAD | LOUISVILLE | JEFFERSON | KY | 40213 | 4 | NO | 1005 | 1999-06-04 | 0 | 0 | 70000 | 48289.4565 | 116593.3202 | Null | 0 | 30 |  | 19990604 | 35 | 35 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | CONNECTIONS TO METER | STEEL |  | 3 | 0.216 | ASTM A106/105 |  | 0 | 1969 | ABOVE GROUND |  | JOSEPH RYAN | 5026272433 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GROUND METER SET | YES |  |  | AT APPROXMATELY 10:00 A.M. ON 6/4/99, CSX EMPLOYEES WERE BACKING ELEVEN BOXCARS INTO THE DIXIE WAREHOUSE AT 2900 FERN VALLEY ROAD. THE ENGINEER WASVIRGIL BYBEE AND THE SWITCHMAN WAS LOUIS STARR. MR. STARR WAS COUNTING OFFCARS TO MR. BYBEE OVER A HAND HELD RADIO. MR. STARR STATED THAT HE RADIOEDMR. BYBEE TO STOP SEVERAL TIMES. MR. BYBEE STATED THAT HE DID NOT HEAR MR.STARR. AT THIS TIME THE RAIL STOP GAVE WAY AND ALLOWED THE TRAIN TO KEEPGOING UNTIL THE END CAR WENT THROUGH THE NORTH WALL OF THE BUILDING. THEBUILDING IS A LARGE WAREHOUSE CONSTRUCTED OF PRE-FABRICATED CONCRETE WALLS.WHEN THE WALL GAVE WAY IT CAME DOWN BASICALLY IN ONE PIECE. NEXT TO THE WALLWAS THE ABOVE GRADE METER SET FOR THE BUILDING. THE FORCE AND WEIGHT OF THEWALL DAMAGED THE METER PIPING CAUSING GAS TO ESCAPE.
2025-01-31 10:21 | YES | YES | 19990106 | 1999-06-30 | 12878 | MOUNTAINEER GAS CO | 901 BRIDGE ROAD | CHARLESTON | KANAWHA | WV | 25314 | 3 | NO | 1304 | 1999-06-03 | 0 | 1 | 0 | 0 | 0 | Null | 3 | 17 |  | 19990609 | 43 | 60 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.136 |  | DRESSER | 0 | 1958 | UNDER PAVEMENT |  | THEODORE A ROSE | 3043470549 | [6 empty] | Null |  | OUTSIDE/THIRD PARTY |  | NO |  | NO | 3 | SEE B-3 | YES |  |  | THE CITY OF CHARLESTON STREET DEPARTMENT CALLED MOUNTAINEER GAS COMPANY (MGC)ON JUNE 3, 1999 AT 11:21 A.M. TO REPORT DAMAGE TO A NATURAL GAS FACILITY. MGCFOUND AN 1 1/4" STEEL SERVICE LINE PULLED OUT OF A BOLTED DRESSER COUPLING,THE SEPARATION WAS CAUSED BY THE CITY OF CHARLESTON STREET CREW WHILE DRIVINGA VERTICAL I-BEAM GUARD RAIL DIRECTLY ABOVE THE 1 1/4" SERVICE LINE. THEDIRECT IMPACT OF THE I-BEAM RESULTED IN SEPARATING THE SERVICE LINE AT THEDRESSER COUPLING, WHICH ALLOWED NATURAL GAS TO BE RELEASED. AT 11:56 A.M., AMGC SUPERVISOR ARRIVED AT THE SITE AND ARRANGED TRAFFIC CONTROL. AT 12:15P.M. THE FIRST MGC CREW ARRIVED AT THE JOB SITE. THIS MGC CREW IMMEDIATELYSECURED THE WORK AREA WITH ROAD CLOSED SIGNS. THE MGC CREW USING A SOCKETWRENCH THEN BEGAN REMOVING THE GUARDRAIL BOLTS DIRECTLY OVER THE LEAK AREA SOTHAT EXCAVATING FOR REPAIRS COULD BEGIN. AT 1:04 P.M. THE GAS IGNITED DUE TOA CHARLESTON CITY EMPLOYEE ATTEMPTING TO REMOVE BOLTS FROM THE GUARDRAIL(APPROXIMATELY 10 FEET FROM THE LEAK AREA) WITH AN ELECTRIC IMPACT WRENCH.THE MGC PERSONNEL AT THE WORK SITE WERE UNAWARE OF THE ABOVE ACTION IN TIME TOPREVENT IGNITION. AS A RESULT OF THE GAS IGNITION, TWO CHARLESTON CITYEMPLOYEES WERE BURNED. ONE REQUIRED INPATIENT HOSPITALIZATION AND ONE WASTREATED AND RELEASED.
2025-01-31 10:21 | YES | YES | 19990109 | 1999-07-01 | 15518 | PIEDMONT NATURAL GAS CO INC |  | CHARLOTTE | MECKLENBURG | NC |  | 3 | Null | 1645 | 1999-05-27 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 30 | 485391 | 19990527 | 60 | 75 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 |  |  | 1956 | 1956 | UNDER GROUND OR UNDER WATER |  | RONALD W COBB, MANAGER MATERIALS MGMT | 7043643120 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | IN ATTEMPTING TO REPLACE A STEEL SERVICE LINE WITH PLASTIC, THERE WAS ACCIDENTAL IGNITION. THE PROBABLE SOURCE OF IGNITION WAS STATIC CHARGES ON THE PLASTIC.
2025-01-31 10:21 | NO | NO | 19990110 | 1999-07-01 | 15931 | PUBLIC SERVICE CO OF COLORADO | CHERRYSIDE DR & EMILY LN | FRISCO | SUMMIT | CO | 80443 | 3 | NO | 1135 | 1999-06-25 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 10 | 488894 | 19990625 |  |  |  |  | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | BARBARA BOGER, INVESTIGATOR | 3036713824 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-06-24 | YES | 0 |  | YES | NO DATA |  | CONTRACTOR CT 3" PE GAS DISTRIBUTION MAIN. CONTRACTOR COMPLETING EXCAVATION CUT 3" PE GAS DISTRIBUTION. DUE TO GAS LEAK CHERRYSIDE DRIVE WAS CLOSED TO TRAFFIC FOR APPROXIMATELY 2 HOURS WHILE REPAIRS WERE MADE. CHERRYSIDE DRIVE IS NOT A MAIN ROAD.
2025-01-31 10:21 | YES | NO | 19990111 | 1999-07-15 | 18472 | SEMCO ENERGY GAS COMPANY |  | BATTLE CREEK | CALHOUN | MI | 49017- | 3 | NO | 1430 | 1999-06-15 | 0 | 0 | 370000 | 255244.2698 | 616278.9784 | NO | 0 | 30 | 487580 | 19990615 | 14 | 0.5 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | MAIN TIE IN | STEEL | [5 empty] | 0 | 0 | UNDER GROUND OR UNDER WATER |  | STEPHEN R MAKOWSKI, VP TECHNICAL SERVICES | 8109877900 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION
2025-01-31 10:21 | YES | NO | 19990112 | 1999-07-21 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS |  | ALBUQUERQUE | BERNALILLO | NM | 87106- | 3 | NO | 125 | 1999-06-29 | 0 | 0 | 525000 | 362170.9234 | 874449.9018 | NO | 4 | 20 | 489281 | 19990629 | 60 | 60 |  | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.141 | API 5L B | LONE STAR STEEL | 1978 | 1979 | UNDER GROUND OR UNDER WATER |  | GARY HOWARD, MGR, GAS MEASUREMENT | 5052414524 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-06-21 | YES | 2 |  | YES | NO DATA |  | AT APPROXIMATELY 1:25 A.M. ON JUNE 29, 1999, A D-10 CATERPILLAR BULLDOZER OWNED BY SEMA CONSTRUCTION AND OPERATED BY A PERSON NAMED MIKE MATHIAS HIT A 4" DISTRBUTION GAS MAIN IN A ROAD AT THE INTERSECTION OF ACCESS ROAD "B" AND GEORGE STREET SE IN ALBUQUERQUE, NEW MEXICO. THE GAS MAIN WAS IN AN OPEN EXCAVATION THAT WAS USED TO IDENTIFY FOR THE CONTRACTOR THE PRECISE DEPTH AND LOCATION OF THE GAS MAIN. THE BULLDOZER OPERATOR, WHILE TRYING TO BACK THE BULLDOZER OUT OF THE EXCAVATION, CAUGHT THE STEEL PIPE WITH THE BULLDOZER TRACKS AND SEVERED THE 4" DISTRIBUTION MAIN. THE OPERATOR EXITED THE VEHICLE, UNHARMED, WITHOUT SHUTTING THE ENGINE OFF. THE ENGINE CONTINUED TO RUN UNTIL IT IGNITED THE GAS FROM THE RUPTURED GAS MAIN. THE SUBSEQUENT FIRE COMPLETELY ENGULFED AND DESTROYED THE BULLDOZER. WHILE TRYING TO BACK THE BULLDOZEER OUT OF THE EXCAVATION, CAUGHT THHE STEEL PIPE WITH THE BULLDOZER, TRACKS AND SEVERED THE 4" DISTRIBUTION MAIN. THE OPERATOR EXITED THE VEHICLE, UNHARMED, WIHOUT SHUTTING THE ENGINE OFF. THE ENGINE CONTINUED TO RUN UNTIL IT IGNITED THE GAS FROM THE RUPTURED GAS MAIN. THE SUBSEQUENT FIRE COMPLETELY ENGULFED AND DESTROYED THE BULLDOZER. THE CONTRACTOR NOTIFIED PNM METRO GAS DISPATCH AT 1:29 A.M. AND REPORTED THAT THE GAS MAIN WAS RUPTURED AND WAS ON FIRE. GAS DISPATCH NOTIFIED THE ALBUQUERQUE FIRE DEPARTMENT. A PNMGS EMERGENCY C & M TRUCK WAS DISPATCHED AT 1:35 A.M. AND ARRIVED ON THE SCENE AT 1:49 A.M. AT THIS TIME, IT WAS OBSERVED THAT THE BULLDOZER WAS STILL IN THE DITCH AND WAS FULLY ENGULFED IN THE FIRE RESULTING FROM THE GAS IGNITING. GAS DISPATCH WAS NOTIFIED THAT C & M CREWS AND EQUIPMENT WERE NEEDED AT THE SITE TO EXCAVATE THE MAIN SOME DISTANCE ON EITHER SIDE OF THE RUPTURE AND SQUEEZE THE STEEL MAIN SHUT WITH HYDRAULIC PIPE SQUEEZERS. TWO C & M CREWS WERE CALLED OUT AND RESPONDED TO THE SCENE. AT 5:45 A.M., THE BLOWING LINE WAS CONTROLLED AND THE FIRE WAS EXTINGUISHED. THE BULLDOZER, VALUED AT $500,000 WAS CONSIDERED A TTAL LOSS. THE BULLDOZER WAS UNHARMED. ON THE PREVIOUS MORNING, JUNE 28, 1999, PNM GAS SERVICES PERSONNEL SPOTTED AND MARKED THE LOCATION OF A 4" DISTRIBUTION GAS MAIN AT A CONSTRUCTION SITE AT THE INTERSECTION OF ACCESS ROAD "B" AND GEORGE ST SE AT THE REQUEST OF SEMA CONSTRUCTION COMPANY. ON THE AFTERNOON OF JUNE 28, 1999, A SEMA CREW, WITH THE ASSISTANCE OF PNM GAS SERVICES PERSONNEL, EXCAVATED A BELLHOLE ON THE 4" STELL DISTRIBUTION GAS MAIN IN ORDER TO DETERMINE THE PRECISE LOCATION AND DEPTH OF THE GAS MAIN. AT 7 P.M. THAT SAME DAY, THE SEMA CONSTRUCTION SUPERVISOR BRADLEY BARNISH CONDUCTED A HAZARD AWARENESS SESSION WITH THE EQUIPMENT OPERATORS AT THE JOB-SITE. SUBJECTS COVERED INCLUDED NOTIFICATION CONCERNING THE OPEN GAS MAIN EXCAVATION AND INSTRUCTION TO "STAY AWAY FROM THE POTHOLE". THIS PARTICULAR OPERATOR, ACCORDING TO WITNESSES, WAS WARNED TO STAY AWAY FROM THE GAS MAIN EXCAVATION LATER THAT EVENING WHEN HE GOT TOO CLOSE.
2025-01-31 10:21 | YES | NO | 19990113 | 1999-07-26 | 2748 | CONSUMERS POWER CO |  | HOWELL | LIVINGSTON | MI | 48843 | 3 | NO | 1224 | 1999-06-25 | 0 | 0 | 500000 | 344924.6889 | 832809.4303 | NO | 0 | 56 |  | 19990625 | 50 | 60 |  | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTM D2513 | PHILLIPS | 1991 | 1991 | UNDER GROUND OR UNDER WATER |  | JERRY F HOLWERDA, PRINCIPAL ENGINEER | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-06-16 | YES | 0 |  | YES | NO DATA |  | CONTRACTOR INSTALLING TELEPHONE CABLE, STRUCK GAS MAIN. ESCAPING GAS ENTERED BUILDINGS AND IGNITED.
2025-01-31 10:21 | NO | NO | 19990115 | 1999-07-27 | 12642 | MOBILE GAS SERVICE CORP |  | MOBILE | MOBILE | AL | 36603 | 3 | NO | 1045 | 1999-06-28 | 0 | 0 | 70000 | 48289.4565 | 116593.3202 | NO | 0 | 12 | 489400 | 19990629 | 30 | 54 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JIMMIE L BUTER | 3344504617 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-06-16 | YES | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 19990117 | 1999-07-28 | 2120 | CARTERSVILLE GAS DEPT, CITY OF | 3403 KINGSTON HWY NE | ROME | FLOYD | GA | 30161- | 3 | Null | 1752 | 1999-07-15 | 0 | 7 | 0 | 0 | 0 | NO | 6 | 38 |  | 19990715 | 30 | 60 |  | 125 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.154 |  |  | 0 | 1957 | UNDER PAVEMENT |  | GARY W RIGGS | 7703875642 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-12 | NO | 0 |  | YES | NO DATA |  | CONTRACTOR INSTALLING UNDERGROUND GASOLINE TANKS HIT NATURAL GAS LINE.
2025-01-31 10:21 | YES | NO | 19990118 | 1999-08-03 | 2748 | CONSUMERS POWER CO | 4313 PAINE | MIDLAND | MIDLAND | MI | 48642 | 3 | NO | 936 | 1999-07-07 | 0 | 0 | 90000 | 62086.444 | 149905.6974 | NO | 0 | 24 | 492431 | 19990707 | 50 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.113 | ASTM A53 |  | 1958 | 1958 | WITHIN/UNDER BUILDING |  | JERRY F HOLWERDA | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-01 | Null | 0 |  | YES | NO DATA |  | SEWER CONTRACTOR HIT AND PULLED SERVICE, DAMAGING INSIDE PIPE. ESCAPING GAS IGNITED BY UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 19990119 | 1999-08-04 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 5002 LIVERPOOL TURNPIKE | EMIGSVILLE | YORK | PA | 17318 |  | NO | 1000 | 1999-07-09 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 15 | 490712 | 19990709 | 452 | 175 | BY CFR 192.619(A)(3) |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | OTHER | OPERATOR | STEEL | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT P JOHNSON | 4125724450 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EMPLOYEE INADVERTENTLY TURNED OFF SUPPLY PRESSURE TO CONTROLLERS PRIOR TO SHUTTING OFF THE DISTRIBUTION OUTLET VALVE. BOTH MONITOR AND CONTROL REGULATORS OPENED INTRODUCING 452 PSIG INTO A 175 PSIG MAOP SYSTEM.
2025-01-31 10:21 | YES | NO | 19990121 | 1999-08-09 | 22182 | WASHINGTON GAS LIGHT CO | 12903 BARNWELL PLACE | UPPER MARLBORO | PRINCE GEORGE | MD | 20772 | 3 | Null | 1604 | 1999-07-06 | 0 | 0 | 155000 | 106926.6536 | 258170.9234 | NO | 0 | 41 |  | 19990707 | 50 | 55 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM |  |  |  | AMERICAN | 1994 | 1994 | ABOVE GROUND |  | JOHN H FLUHARTY JR, SAFETY SPECIALIST | 2026246059 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE FIRE WITH SECONDARY GAS INVOLVEMENT FROM OUTSIDE METER
2025-01-31 10:21 | YES | NO | 19990122 | 1999-08-06 | 22189 | PUGET SOUND ENERGY | 228 ST SE & 39 AV SE | BOTHELL | SNOHOMISH | WA | 9 8201 | 3 | Null | 1013 | 1999-07-22 | 0 | 0 | 87447 | 60325.2585 | 145653.3725 | NO | 6 | 45 | 492432 | 19990723 | 45 | 45 |  | 96 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.491 | PE 3408 SDR 13.5 | PLEXCO | 0 | 1995 | UNDER GROUND OR UNDER WATER |  | DOUGLAS DAMM, STANDARDS DEVELOPMENT | 2062242396 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-20 | YES | 3 | 1999-07-20 | Null | NO DATA |  | SEE COVER LETTER AND PARTS (3) AND D ON BACK OF FORM FOR ADDITIONAL INFORMATION.
2025-01-31 10:21 | YES | YES | 19990124 | 1999-01-29 | 603 | ARKLA, A NORAM ENERGY COMPANY | 23RD & LEE | LAWTON | COMANCHE | OK | 73501- | 3 | NO | 2315 | 1998-10-08 | 1 | 0 | 10000 | 6984.4848 | 16863.8112 | NO | 0 | 30 | 459250 | 19981009 | 50 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.11 |  |  | 0 | 0 | ABOVE GROUND |  | STEVE BEAUCHAMP | 5802505413 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | Null | NO DATA |  | HIT METER BY CAR
2025-01-31 10:21 | YES | NO | 19990126 | 1999-08-17 | 4483 | ENSTAR NATURAL GAS CO | 801 TINA LANE | MATANUSKA-SUSITNA |  | AK | 99645- | 2 | NO | 55 | 1999-08-07 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | NO | 1 | 35 | 494252 | 19990807 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPE | 1992 | 1992 | ABOVE GROUND |  | DAVID W BREDIN, MANAGER | 9042643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY MORNING, AUGUST 7, 1999, AT APPROXIMATELY 12:55 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A FIRE AT 801 TINA, NEAR PALMER, ALASKA. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A SINGLE FAMILY HOME ON FIRE. HEAT FROM THE FIRE MELTED THE 5/8" POLYETHYLENE SERVICE LINE INSIDE THE STEEL RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED AT 2:30 AM AST. THE CAUSE OF THE FIRE IS SUSPECTED TO BE ARSON. NATURAL GAS FROM ENSTAR'S FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 19990127 | 1999-08-16 | 30769 | MISSOURI GAS ENERGY | 12TH AND WALNUT STREET | KANSAS CITY |  | MO | 64106 | 4 | Null | 310 | 1999-07-06 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 20 | 490245 | 19990706 | 31 | 2.2 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 2 | 0.216 | UNKNOWN | UNKNOWN | 0 | 0 | UNDER PAVEMENT |  | WILLIAM R DEAN | 8163605661 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-04-02 | NO | 0 |  | YES | NO DATA |  | SEE PART D AND ATTACHED NARRATIVE
2025-01-31 10:21 | YES | YES | 19990128 | 1999-08-20 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 71 WEAVER STREET | SCARSDALE | WESTCHESTER | NY | 1 05 83 | 3 | NO | 12 | 1999-07-19 | 0 | 3 | 0 | 0 | 0 | NO | 3 | 21 | 491816 | 19990719 | 60 | 99 |  |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | NO DATA |  | OTHER | COPPER TUBING | 0.5 |  |  |  | 0 | 1962 | UNDER GROUND OR UNDER WATER |  | LUKE MONAGHAN | 2124603024 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE RESPONDING CREW FOUND A DOWNED ENERGIZED 13 KV FEEDER CABLE THAT IGNITED SMALL FIRES ALONG THE CURB LINE AND LAWN AREA TO THE ABOVE ADDRESS. ACCESS TO THE CURB VALVE WAS NOT AVALIABLE DUE TO THE FIRE. THE CREW WAS ABLE TO TURN OFF AND LOCK THE HEAD OF SERVICE VALVE TO THE PRIVATE HOME. COMPANY FORCES RESPONSED TO DE-ENERGIZE THE FEEDER CABLE AND EXCAVATE TO MAKE SHUTDOWN AT THE SERVICE TEE. WHILE EXCAVATING WITH A TRUCK MOUNTED BACKHOE THE OPERATOR SEVERED A 1/2 COPPER TUBE SERVICE. THE SERVICE PIPE WAS CRIMPED TO SECURE THE LEAK. THIS EXTINGUISHED THE FIRE ON THE LAWN AND CURB LINE. WHILE TRYING SEVERL ATTEMPTS TO STOP THE COMPLETE FLOW OF GAS AT THE MAIN CONNECTION THE GAS IGNITED FROM AN UNKNOWN SOURCE AND INJURED FIVE EMPLOYEES. MAIN VALVES WERE THEN SHUTDOWN AND THIS SECURED THE LEAK. PERMANENT REPAIRS WERE MADE AND SERVICE WAS RESTORED 11:14 HOURS. THERE WERE SERVICE INTERRUPTIONS TO 30 PRIVATE HOMES. FIVE EMPLOYEES INJURED: TWO WERE TREATED AND RELEASED, WHILE THREE WERE HOSPITALIZED.
2025-01-31 10:21 | YES | NO | 19990129 | 1999-08-25 | 1088 | BALTIMORE GAS & ELECTRIC CO | 9411 PHILADELPHIA RD | BALTIMORE |  | MD | 21227- | 3 | NO | 1330 | 1999-08-10 | 0 | 0 | 300000 | 206954.8134 | 499685.6582 | NO | 0 | 30 | 494598 | 19990810 | 97 | 99 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | D2513 | DRISCO | 1991 | 1992 | UNDER GROUND OR UNDER WATER |  | DONALD L SHRADER | 4102915130 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-26 | YES | 3 | PAINTED MARKING | YES | NO DATA |  | IT WAS APPARENT THAT THE FINAL GRADE HAD BEEN ESTABLISHED SHORTLY AFTER THE UTILITIES WERE INSTALLED IN 1992. THE 2" HIGH PRESSURE GAS LINE (99 PSIG) WAS LOCATED AND MARKED ON 7/27/99. THE GRADE HAD BEEN LOWERED SINCE THE ORIGINAL ESTABLISHED GRADE AND WHEN THE SS250 CATERPILLAR GRADER WAS OPERATED OVER THE 2" GAS MAIN, THE WAS SEVERED. THE RELEASE OF GAS WAS APPARENTLY IGNITED FROM A SPARK FROM THE GRADER.
2025-01-31 10:21 | YES | YES | 19990130 | 1999-08-23 | 909 | AUSTELL NATURAL GAS SYSTEM, CITY OF | 1751 ANDERSON MILL RD | AUSTELL | COBB | GA | 3 0106 | 3 | Null | 1545 | 1999-08-03 | 1 | 0 | 175000 | 120723.6411 | 291483.3006 | NO | 0 | 35 | 493715 | 19990803 | 42 | 59 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5L | UNKNOWN | 1983 | 1983 | UNDER GROUND OR UNDER WATER |  | E GERALD HARMON, GENERAL MANAGER | 7709481841 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-20 | Null | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 19990131 | 1999-08-30 | 15462 | PECO ENERGY CO | 104 SIGNAL HILL CT | NORTH WALES |  | PA | 19454- | 3 | NO | 1424 | 1999-08-04 | 0 | 0 | 800000 | 551879.5023 | 1332495.0884 | NO | 0 | 50 |  | 19990805 | 46 | 99 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | METER SET |  |  | ALI 175 | AMERICAN METER | 0 | 1994 | ABOVE GROUND |  | MICHAEL P KELLER | 2159563105 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 19990132 | 1999-08-27 | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO |  | NORTH AUGUSTA |  | SC | 2 9861 | 3 | NO | 1100 | 1999-07-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 | 492961 | 19990728 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | WILLIAM D LYNETT JR | 8036426291 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | UPON COMPLETE INVESTIGATION IT WAS DETERMINED NATURAL GAS WAS NOT INVOLVED/INITIALLY REPORTED AS A NATURAL GAS EXPLOSION. THIS WAS HOUSE FIRE INITIALLY REPORTED TO BE CAUSED BY A GAS LEAK ON THE CUSOMTER'S COOK STOVE. AN EXPLOSION WAS ALSO REPORTED. FURTHER INVESTIGATION DETERMINED THIS FIRE TO BE CAUSE BY AND ELECTRIC TOASTER.
2025-01-31 10:21 | YES | NO | 19990133 | 1999-08-27 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) |  | MANISTEE | MANISTEE | MI | 4 9660 | 3 | NO | 854 | 1999-08-02 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | NO | 1 | 9 | 493539 | 19990802 | 0.25 | 0.25 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINES | BODY OF PIPE |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS P FUNTSCH, CLAIMS INVESTIGATOR | 3135777026 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | LEAKING GAS FROM THE CUSTOMER'S FUEL LINE IGNITED FROM AN UKNOWN SOURCE.
2025-01-31 10:21 | YES | NO | 19990134 | 1999-08-26 | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | HUDSON RIVER NORTH OF MID-HUDSON BRIDGE | POUGHKEEPSIE | DUTCHESS | NY | 1 2601 | 3 | NO | 904 | 1999-08-08 | 0 | 0 | 10000000 | 6898493.7787 | 16656188.6051 | NO | 1 | 50 | 494330 | 19990808 | 57 | 60 |  | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.5 |  |  | 0 | 1931 | UNDER GROUND OR UNDER WATER |  | DAVID W MERTE, DIRECTOR GAS OPERATIONS | 9144865521 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 19990135 | 1999-09-02 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 38-32 MORLOT AVENUE | FAIR LAWN | BERGEN | NJ |  | 3 | NO | 1800 | 1999-07-31 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 15 | 493466 | 19990801 | 0.25 | 0.25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 | 0.76 | ASAA21.7 | UNKNOWN | 0 | 1955 | UNDER PAVEMENT |  | PETER A CISTARO, VICE PRESIDENT | 9734305100 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990140 | 1999-09-21 | 11720 | KEYSPAN ENERGY CORP |  | GARDEN CITY | NASSAU | NY | 1 1530 | 4 | NO | 1530 | 1999-08-17 | 0 | 3 | 0 | 0 | 0 | NO | 4 | 0 | 495398 | 19990817 | 60 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | TAPPING EQUIPMENT | STEEL |  | 4 | 0.25 | UNKNOWN | UNKNOWN | 1930 | 1930 | UNDER PAVEMENT |  | ERNEST S PAPADOULLAS, DIRECTOR | 5165455625 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990141 | 1999-09-03 | 15007 | PACIFIC GAS & ELECTRIC CO | 3625 BERNARD STREET | BAKERSFIELD | KERN | CA | 93306- | 3 | NO | 1330 | 1999-08-06 | 0 | 1 | 78000 | 53808.2515 | 129918.2711 | NO | 1 | 15 | 494212 | 19990806 | 45 | 51 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | OTHER | ALDYL A | 3 | 0.304 | ALDYL A | DUPONT | 1972 | 1972 | UNDER PAVEMENT |  | SHAN BHATTACHARYA, VP DIST | 4169736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 19990142 | 1999-09-10 | 8040 | ILLINOIS POWER CO | 912 W DANIEL | CHAMPAIGN | CHAMPAIGN | IL | 6 1821 | 3 | Null | 32 | 1999-08-13 | 0 | 0 | 150000 | 103477.4067 | 249842.8291 | NO | 3 | 15 | 495269 | 19990816 | 56 | 60 |  | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | PIPE | POLYETHYLENE PLASTIC |  | 1.12 | 0.99 | PE2406 | UNKNOWN | 0 | 1977 | UNDER GROUND OR UNDER WATER |  | D R JOHNSON, DIRECTOR | 2174247001 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990144 | 1999-09-03 | 18484 | SOUTHERN CALIFORNIA GAS CO | 3401 MEADOWBROOK | COSTA MESA | ORANGE | CA |  | 3 | NO | 1535 | 1999-08-03 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 5 | 493744 | 19990803 | 40 | 60 | BY TEST |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 |  | PE |  | 0 | 0 | UNDER PAVEMENT |  | W JEFF KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-30 | YES | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 19990145 | 1999-09-03 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 303 MULBURRY ST NE | ALBUQUERQUE | BERNALILLO | NM | 87102- | 3 | NO | 1300 | 1999-08-05 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | NO | 0 | 25 | 494030 | 19990805 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | CHEVRON (PLEXCO) | 1999 | 1999 | UNDER PAVEMENT |  | DAVID QUINTANA, STAFF ENGINEER | 5052414563 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 19990146 | 1999-09-08 | 11032 | LACLEDE GAS CO | 13358 MANCHESTER RD | DES PERES | ST LOUIS | MO | 63131- | 3 | NO | 1102 | 1999-07-26 | 0 | 0 | 86554 | 59709.2231 | 144165.9749 | NO | 3 | 23 |  | 19990726 | 148 | 300 | BY TEST | 555 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.25 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | PAUL B HUNKER, JR ASST VICE PRESIDENT | 3143420528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-07-14 | YES | 1 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 19990147 | 1999-09-16 | 2596 | COLUMBIA GAS OF OHIO INC | BENORE & N MATZINGER RD | TOLEDO | LUCAS | OH | 43612- |  | Null | 1550 | 1999-08-17 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 0 | 495391 | 19990817 | 45 | 58 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC | [5 empty] | 0 | 0 | OTHER | IN EXCAVATION | ROBER MEEKINS, PLANT MANAGER | 4192528009 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION
2025-01-31 10:21 | YES | YES | 19990148 | 1999-09-17 | 30769 | MISSOURI GAS ENERGY | 101 EAST 41ST STREET | KANSAS CITY | JACKSON | MO | 6 4111 | 3 | Null | 2005 | 1999-07-26 | 0 | 3 | 0 | 0 | 0 | NO | 2 | 5 | 492803 | 19990726 | 48 | 56 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | VALVE |  | OTHER | BRASS | 2 |  | STOPCOCK VALVE | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | WILLIAM R DEAN, MANAGER | 8163605661 | [6 empty] | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | MATERIAL FAILURE
2025-01-31 10:21 | YES | YES | 19990149 | 1999-09-15 | 13710 | NORTHERN ILLINOIS GAS CO | 7733 GRAND AVE (ALLEY) | ELMWOOD PARK | COOK | IL | 6 0707 | 3 | Null | 1630 | 1999-09-04 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 497607 | 19990905 |  |  |  | 25 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.5 |  |  | 0 | 1926 | OTHER | TELEPHONE MANHOLE | GEORGE WALDVOGEL, COORDINATOR TECH | 6308388676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | NATURAL GAS LEAK MIGRATED INTO A TELEPHONE MANHOLE. SEVERAL CHILDREN WERE PLAYING WITH MATCHES AND IGNITED THE GAS. ONE OF THE CHILDREN RECEIVED 1ST AND 2ND DEGREE BURNS TO HIS FACE & LEGS.
2025-01-31 10:21 | YES | YES | 19990150 | 1999-09-22 | 4060 | EAST OHIO GAS CO | 6143 MILL ST | KINGSVILLE | ASHTABULA | OH |  | 1 | NO | 1637 | 1999-08-21 | 0 | 2 | 60000 | 41390.9627 | 99937.1316 | NO | 5 | 23 | 495887 | 19990821 | 52 | 60 |  | 90 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API-5L | UNKNOWN | 1955 | 1956 | WITHIN/UNDER BUILDING |  | CLARENCE W MOORE | 2167366835 | EXTERNALLY | GENERAL CORROSION |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 19990154 | 1999-10-05 | 31202 | RELIANT ENERGY - ARKLA | CHOCTAW LANE | MCALESTER | PITTSBURG | OK |  | 2 | NO | 1700 | 1999-08-26 | 0 | 0 | 378000 | 260763.0648 | 629603.9293 | NO | 1 | 0 |  | 19990826 | 28 | 6 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 2 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | R L MYERS | 5802505400 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-08-20 | NO | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990155 | 1999-10-01 | 4473 | ENERGAS CO | 2713 W 9TH | AMARILLO | POTTER | TX | 79106- | 3 | NO | 912 | 1999-09-13 | 0 | 1 | 4000 | 2759.3975 | 6662.4754 | NO | 0 | 28 | 498690 | 19990914 | 0.5 | 1 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API 5L B |  | 0 | 0 | UNDER PAVEMENT |  | CHARLES S JONES | 8067984466 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A GAS LEAK WAS DISCOVERED 18 FEET FROM RESIDENCE. CUSTOMER LIT CIGARETTE AND WAS BURNED FROM A FLASH FIRE.
2025-01-31 10:21 | YES | NO | 19990156 | 1999-09-30 | 792 | ATLANTA GAS LIGHT CO | 3266 MEDLOCK BRIDGE ROAD | NORCROSS | GWINNETT | GA | 3 0071 | 3 | Null | 1255 | 1999-08-31 | 0 | 0 | 1500000 | 1034774.0668 | 2498428.2908 | NO | 0 | 38 | 497040 | 19990831 | 60 | 60 |  | 110 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.391 | ASTM D2513 | UNKNOWN | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | MICKEY WATTS, DISTRIBUTION SUPERVISOR | 7704182261 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO | 1999-08-24 | Null | 0 |  | YES | NO DATA |  | A 4" PLASTIC NATURAL GAS SERVICE WAS RUPTURED WHEN A CONTRACTOR WAS MAKING A DIRECTIONAL BORE WHILE INSTALLING CABLE TV. THE ESCAPING GAS IGNITED DESTROYING A TRENCHER AND A 10 UNIT APARTMENT BUILDING.
2025-01-31 10:21 | YES | NO | 19990157 | 1999-10-05 | 15007 | PACIFIC GAS & ELECTRIC CO | 4275 EAST WOODWARD AVENUE | FRESNO | FRESNO | CA | 9 3702 | 3 | Null | 1915 | 1999-09-08 | 0 | 0 | 179000 | 123483.0386 | 298145.776 | NO | 0 | 15 | 498054 | 19990908 | 0.25 | 5 |  | 10 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | CUSTOMER METERS | REGULATOR/METER |  | OTHER | ALUMINUM |  |  | ANSI B109.1 | AMERICAN METER | 1985 | 1986 | ABOVE GROUND |  | SHAN BHATTACHARYA, VP DIST | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ACCORDING TO FRESNO FIRE DEPARTMENT INVESTIGATORS, KIDS PLAYING WITH MATCHES IGNITED A STRUCTURE FIRE IN A STORAGE ROOM OF AN APARTMENT BUILDING. THE STRUCTURE FIRE DAMAGED A 9 GAS METER MANIFOLD SET AND GAS IGNITED.
2025-01-31 10:21 | NO | NO | 19990162 | 1999-10-08 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 101 FENLEY AVENUE | LOUISVILLE | JEFFERSON | KY | 4 0207 | 3 | NO | 1744 | 1999-09-08 | 0 | 0 | 0 | 0 | 0 | YES | 4 | 46 | 498144 | 19990909 | 83 | 99 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | PIPE NIPPLE ON BLOWDOWN | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | ASTM A106/105 | CBOMANU | 0 | 1970 | NO DATA |  | JOSEPH RYAN, MANAGER | 5026272433 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990163 | 1999-10-07 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 1811 WEST BROADWAY | LOUISVILLE | JEFFERSON | KY | 4 0203 | 4 | Null | 615 | 1999-09-03 | 1 | 0 | 60000 | 41390.9627 | 99937.1316 | NO | 1 | 15 | 497397 | 19990903 | 35 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.133 | ASTM A106/105 |  | 0 | 1998 | ABOVE GROUND |  | JOSEPH RYAN, MANAGER | 5026272433 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE ATTACHMENT
2025-01-31 10:21 | NO | NO | 19990166 | 1999-10-25 | 31202 | RELIANT ENERGY - ARKLA | HWY 66 & HWY 34 | ELK CITY | CANUTE | OK | 73626- | 3 | NO | 910 | 1999-10-05 | 0 | 0 | 1807 | 1246.5578 | 3009.7733 | YES | 1 | 0 | 501269 | 19991005 | 50 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 3 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ILLEGIBLE | 5803534400 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 19990167 | 1999-10-25 | 12582 | MISSISSIPPI VALLEY GAS | 3883 LOST LAKE CIRCLE | JACKSON | HINDS | MS | 39212- | 3 | NO | 1412 | 1999-10-04 | 0 | 0 | 26000 | 17936.0838 | 43306.0904 | YES | 1 | 0 | 501187 | 19991004 | 20 | 35 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | TR 418 | PLEXCO | 0 | 1979 | UNDER GROUND OR UNDER WATER |  | DAN W OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-09-27 | YES | 3 | YELLOW PAINT | YES | NO DATA
2025-01-31 10:21 | YES | NO | 19990168 | 1999-10-21 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 3104 POMEROY DRIVE | LOUISVILLE | JEFFERSON | KY | 4 0220 | 3 | Null | 512 | 1999-09-20 | 0 | 0 | 150000 | 103477.4067 | 249842.8291 | NO | 0 | 51 | 499343 | 19990920 | 20 | 20 |  | 35 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | GAS DRYER PIPING | OTHER | NO FAILURE | STEEL |  | 0.75 |  |  |  | 0 | 0 | OTHER | RESIDENTIAL DWELLING BASEMENT | JOSEPH R RYAN | 5026272433 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 19990169 | 1999-10-21 | 13480 | NIAGARA MOHAWK POWER CORP | 134 W BISSELL ST | SYRACUSE | ONONDAGA | NY | 1 3205 | 2 | NO | 1957 | 1999-09-20 | 0 | 0 | 30000 | 20695.4813 | 49968.5658 | NO | 1 | 0 | 499488 | 19990920 | 0.25 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FURNACE | NO DATA |  | STEEL |  |  |  | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS J GILBERT | 3154601148 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | DAMAGE DIRECTLY RELATED TO INTERAL EXPLOSION AND FIRE NEAR CUSTOMERS APPLIANCES.
2025-01-31 10:21 | NO | NO | 19990170 | 1999-10-21 | 13480 | NIAGARA MOHAWK POWER CORP | 29 BUHRMASTER RD | LATHAM | ALBANY | NY | 12110 | 3 | NO | 852 | 1999-09-20 | 0 | 0 | 45000 | 31043.222 | 74952.8487 | NO | 1 | 23 |  | 19990920 | 20 | 60 |  | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 8 | 0.639 | ASTM D-2513 | PHILLIPS DRISCOPIPE | 1994 | 1995 | OTHER | PAVEMENT SHOULDER | BRYAN R BUCK | 5814333375 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-09-15 | YES | 3 | 1999-09-15 | YES | NO DATA
2025-01-31 10:21 | NO | NO | 19990175 | 1999-10-28 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 227 PETHEL STREET | KANNAPOLIS | ROWAN | NC | 28081- | 3 | NO | 630 | 1999-10-11 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | NO | 1 | 45 | 501910 | 19991011 | 60 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0.75 |  | cboSpec | CBOMANU | 0 | 1983 | ABOVE GROUND |  | BOB GARRETT | 7047234314 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990176 | 1999-10-29 | 2416 | CITIZENS UTILITY CO | 504 HAVASUPAI | FLAGSTAFF | COCONINO | AZ | 8 6001 | 3 | NO | 336 | 1999-10-22 | 0 | 2 | 0 | 0 | 0 | NO | 3 | 11 | 503292 | 19991022 | 58 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 1 | 0.113 |  |  | 0 | 1954 | ABOVE GROUND |  | NATHAN C SHELLEY, DISTRICT MANAGER | 5202262266 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | VEHICLE LEFT ROADWAY AND EASEMENT. STRUCK GARGE AND METER LOGS.
2025-01-31 10:21 | NO | NO | 19990177 | 1999-11-15 | 31348 | TXU GAS DISTRIBUTION | 1216 HORIZON | RICHARDSON | DALLAS | TX | 75081- | 3 | NO | 826 | 1999-10-25 | 0 | 0 | 55000 | 37941.7158 | 91609.0373 | YES | 2 | 0 | 503525 | 19991025 | 22 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR | REGULATOR/METER |  | OTHER |  |  |  |  | NO DATA | 0 | 0 | OTHER | ABOVE GROUND FACILITY THAT WAS BURNED | ELLEN WEAVER | 2155334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | ABOVE GROUND FACILITY | YES | NO DATA |  | A THIRD PARTY CONTRACTOR PERFORMED EXCAVATION WORK FOR THE HOMEOWNER. DURING THE COURSE OF THE EXCAVATION, THE REGULATOR WAS BURIED. THE BURIED REGULATOR FAILED, GAS IGNITED, AND THE RESIDENCE BURNED.
2025-01-31 10:21 | YES | NO | 19990178 | 1999-11-12 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 3460 NORTH HERMITAGE ROAD | SHARPSVILLE | MERCER | PA | 16150- | 2 | NO | 1327 | 1999-03-04 | 0 | 0 | 200000 | 137969.8756 | 333123.7721 | NO | 0 | 6 | 475880 | 19990304 | 6 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | CAST IRON |  |  |  | MODEL 107 | ROCKWELL | 1955 | 1956 | ABOVE GROUND |  | CONRAD L DONELSON, SUPERINTENDENT | 8148718341 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990180 | 1999-11-18 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 1625 SHERMAN BLVD | FORT WAYNE | ALLEN | IN | 46808- | 3 | NO | 625 | 1999-10-16 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 5 | 502711 | 19991018 | 45 | 60 |  | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | METER SET AND RISER | STEEL |  | 0.75 | 0.113 | ASTM A53 | CBOMANU | 1996 | 1996 | ABOVE GROUND |  | DON J TOKOLV | 2196474770 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA
2025-01-31 10:21 | NO | NO | 19990181 | 1999-11-22 | 12582 | MISSISSIPPI VALLEY GAS | CLINTON CENTER DRIVE | CLINTON | HINDS | MS |  | 3 | NO | 1130 | 1999-11-05 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 10 | 504846 | 19991105 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 |  | PHILLIPS | 0 | 1999 | UNDER GROUND OR UNDER WATER |  | DAN W OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 19990182 | 1999-11-22 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | BLAIRTOWN HALL ROAD/MAYFIELD TRAIL | PARADISE | GRAND TRAVERSE | MI | 49666- | 4 | NO | 920 | 1999-10-27 | 0 | 1 | 75000 | 51738.7033 | 124921.4145 | NO | 0 | 50 | 503801 | 19991027 | 600 | 1050 | BY TEST | 1994 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | OTHER | GATHERING SYSTEM | OTHER | NONE | STEEL |  | 6 | 0.25 |  |  | 0 | 1975 | ABOVE GROUND |  | GEORGE A VALRANCE, MGR | 3135777029 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION
2025-01-31 10:21 | YES | NO | 19990185 | 1999-11-24 | 18484 | SOUTHERN CALIFORNIA GAS CO | 3996 FRANDON CT | SIMI VALLEY | LOS ANGELES | CA |  | 3 | NO | 1232 | 1999-10-21 | 0 | 0 | 75000 | 51738.7033 | 124921.4145 | NO | 0 | 0 | 503224 | 19991021 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 |  |  | DUPONT | 1971 | 1971 | ABOVE GROUND |  | W J KOSKIE, SAFETY SYSTEMS CONSULTANT | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | 0 | Null |  | Null | 0 |  | Null | NO DATA |  | ROOTS DAMAGED 1/2" PLASTIC SERVICE. MIGRATING GAS IGNITED GARAGE OF SINGLE FAMILY HOME.
2025-01-31 10:21 | YES | YES | 19990186 | 1999-11-24 | 8160 | INTERMOUNTAIN GAS CO | 101 SUNRISE | SUN VALLEY | BLAINE | ID | 83353- | 2 | NO | 1045 | 1999-10-27 | 0 | 1 | 1000000 | 689849.3779 | 1665618.8605 | NO | 1 | 15 | 503856 | 19991027 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.34 | 0.095 | ASTM D2513 | DUPONT ALDY A | 0 | 1978 | UNDER GROUND OR UNDER WATER |  | RICHARD L BEAN, MANAGER | 2083776126 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-10-19 | YES | 3 | PAINT ON GROUND | YES | NO DATA |  | ON OCTOBER 27, 1999 AT 101 SUNRISE IN SUN VALLEY, IDAHO A TREE REMOVAL SUBCONTRACTOR TO A LANDSCAPE CONTRACTOR SEVERED A 3/4 POLYETHYLENE NATURAL GAS SERVICE LINE WHILE IN THE PROCESS OF EXCAVATING A TREE. THE SEVERING OF THE SERVICE LINE APPARENTLY ALLOWED NATURAL GAS TO MIGRATE INTO A HOME NEXT DOOR LOCATED AT 103 SUNRISE. IT IS BELIEVED THAT AN UNKNOWN SOURCE OF IGNITION AT 103 SUNRISE IGNITED THE NATURAL GAS, CAUSING AN EXPLOSION AND SUBSTANTIALLY DAMAGING THAT HOUSE. THE RESIDENCE LOCATED AT 101 SUNRISE WAS DESTROYED BY FIRE, THE PROBABLE CAUSE OF WHICH WAS THE EXPLOSION NEXT DOOR, AT 103 SUNRISE.
2025-01-31 10:21 | YES | YES | 19990187 | 1999-11-19 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 60TH & THORNAPPLE | CASCADE | KENT | MI | 49512- | 2 | NO | 1038 | 1999-10-28 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 58 | 503945 | 19991028 | 60 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 |  | PLEXCO | 0 | 1995 | UNDER GROUND OR UNDER WATER |  | THOMAS P FUNTSCH SR, CLAIMS INVESTIGATOR | 3135777026 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | CONTRACTOR USING POWER EQUIPMENT STRUCK AND CUT THE GAS MAIN.
2025-01-31 10:21 | YES | YES | 19990188 | 1999-11-29 | 5690 | FULTON MUNICIPAL GAS SYSTEM |  | FULTON |  | MS |  |  | NO | 0 | 1999-11-17 | 0 | 1 | 25000 | 17246.2344 | 41640.4715 | NO | 0 | 30 | 506188 | 19991117 | 30 | 40 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER |  | OTHER PLASTIC |  | 0.75 |  | 24D6 | DRISCO | 0 | 1997 | WITHIN/UNDER BUILDING |  | DAN PATE, UTILITIES MGR | 6018629004 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE MAN SAID HE LITE A CIGARETTE AND BLEW UP THE HOUSE.
2025-01-31 10:21 | NO | NO | 19990189 | 1999-11-30 | 13570 | NORTH CAROLINA GAS SERVICE | 1308 MARYLAND AVE | EDEN | ROCKINGHAM | NC | 27288- | 3 | NO | 320 | 1999-10-30 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | NO | 3 | 22 | 504192 | 19991030 | 55 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | OTHER | ALUMINUM | 0.75 |  | 175 METER | SPRAGUE | 1968 | 1992 | ABOVE GROUND |  | LAWRENCE A POLL | 3363498234 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 19990192 | 1999-12-07 | 18440 | SOUTH JERSEY GAS CO | 202 E GREENFIELD AVE | PLEASANTVILLE | ATLANTIC | NJ | 08232- | 4 | NO | 1445 | 1999-11-15 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | NO | 0 | 30 | 505854 | 19991115 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMERS HOUSE LINE | BODY OF PIPE |  | STEEL |  | 1 |  |  |  | 0 | 1930 | WITHIN/UNDER BUILDING |  | A M TETTO, VP DISTRIBUTION | 6095619000 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON NOVEMBER 15, 1999, A FIRE OCCURRED AT 202 E. GREENFIELD AVE AS A RESULT OF A GAS LEAK ON THE CUSTOMERS HOUSE PIPING. ON THAT DAY, A SOUTH JERSEY GAS SERVICEMAN WAS COMPLETING AN APPLIANCE SERVICE CALL AT THIS ADDRESS WHEN THE CUSTOMER TOLD HIM SHE SMELLED GAS OUTSIDE OF HER HOME. THE SERVICEMAN WAS SEARCHING FOR THE LEAK OUTSIDE THE BUILDING WHEN A FIRE STARTED INSIDE THE HOUSE. THE FIRE DEPARTMENT WAS CALLED AND RESPONDED IMMEDIATELY AND THE FIRE WAS PUT OUT. THE HOUSE WAS COMPLETELY GUTTED. THE SERVICEMAN ON THE SCENE EVACUATED THE HOMEOWER AND SHUT OFF THE GAS AT THE OUTSIDE METER AT THE TIME THE FIRE WAS DETECTED. THE GAS SERVICE TO THIS BUILDING WAS INSTALLED IN 1930 AND WAS 1 1/4" BARE STEEL. IT WAS PRESSURE TESTED AFTER THE INCIDENT AT ITS OPERATING PRESSURE (8" W.C.) AND HELD THE TEST. THE CUSTOMERS HOUSE PIPING WAS ALSO PRESSURE TESTED AT 8" W.C. AND IT DID NOT HOLD, INDICATING A HOUSE LINE FAILURE. THE POINT OF IGNITION IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 19990193 | 1999-12-06 | 2748 | CONSUMERS POWER CO | 2740 EAST LANSING | EAST LANSING | INGHAM | MI | 48825- | 3 | NO | 1405 | 1999-11-02 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 48 | 504513 | 19991102 | 53 | 60 | BY TEST | 110 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.13 | 0.101 | ASTM D2513 | PHILLIPS | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | JERRY F HOLERDA, PRINCIPAL ENGINEER | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-10-14 | YES | 2 |  | YES | NO DATA |  | LOCAL ELECTRIC COMPANY CREW, INSTALLING SHRINK SLEEVE ON ELECTRIC CABLE IN CLOSE PROXIMITY OF PLASTIC GAS SERVICE, MELTED GAS SERVICE, CAUSED FIRE, RESULTING IN BURNS TO TWO CREW MEMBERS.
2025-01-31 10:21 | YES | YES | 19990194 | 1999-12-06 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 2041 S 41ST STREET | LOUISVILLE | JEFFERSON | KY | 4 0211 | 3 | Null | 1900 | 1999-11-04 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 30 | 504770 | 19991104 |  |  |  | 100 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | GAS STOVE PIPING | OTHER | NO FAILURE | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | ABOVE GROUND |  | JOSEPH R RYAN | 5026272433 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990198 | 1999-12-07 | 20010 | U G I CORP | INTERSECTION CLAIRMONT & MORNINGSIDE DR | PALMER TOWNSHIP | NORTHAMPTON | PA | 18045- | 3 | NO | 1100 | 1999-11-05 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 30 | 504836 | 19991105 | 55 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE2406 | PLEXCO | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | TAYLOR C BET, DISTRIBUTION ENGINEER | 6108073140 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION
2025-01-31 10:21 | YES | NO | 19990199 | 1999-12-13 | 2596 | COLUMBIA GAS OF OHIO INC | 347 349 351 & 353 SYCAMORE RIDGE WAY | GAHANNA | FRANKLIN | OH | 43230- | 4 | NO | 1150 | 1999-11-16 | 0 | 0 | 750000 | 517387.0334 | 1249214.1454 | NO | 3 | 0 | 505948 | 19991116 | 44 | 60 | BY TEST | 118 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER SERVICE LINE | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | MD-2406 | UPONOR | 1999 | 1999 | OTHER | UNDER CONCRETE PATIO | A STEINMETZ, DIRECTOR OF OPERATIONS | 6144606312 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 19990202 | 1999-12-10 | 2748 | CONSUMERS POWER CO | 1801 E ATHERTON RD | FLINT | GENESEE | MI | 4 8529 | 3 | Null | 2042 | 1999-11-10 | 5 | 0 | 0 | 0 | 0 | NO | 1 | 21 | 505375 | 19991110 | 52 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | JERRY F HOLWERDA | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 19990204 | 1999-12-27 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 141 STIRLING RD | WATCHUNG | SOMERSET | NJ | 07080- | 3 | NO | 1320 | 1999-11-29 | 0 | 0 | 300000 | 206954.8134 | 499685.6582 | NO | 1 | 35 | 507160 | 19991129 | 35 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | WILLARD S CAREY | 9734307833 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20000001 | 2000-01-03 | 2416 | CITIZENS UTILITY CO | DRY CREEK & KACHINA DR | SEDONA | YAVAPAI | AZ | 8 6336 | 3 | Null | 1034 | 1999-11-24 | 0 | 0 | 1500000 | 1034774.0668 | 2498428.2908 | NO | 2 | 30 | 506809 | 19991124 | 215 | 220 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 2 | 0.154 |  |  | 1965 | 1965 | UNDER PAVEMENT |  | RICHARD CASTRO | 5206345555 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-11-05 | YES | 3 | 1999-11-05 | YES | NO DATA |  | 2" HIGH PRESSURE GAS LINE WAS HIT BY VERMEER TRENCHER WHILE TRENCHING TO INSTALL NEW SEWER LINE IN DRY CREEK RD. DOT REPORT 506809 ALAN GRNEAU, ACC REPORT 990604
2025-01-31 10:21 | YES | YES | 20000003 | 2000-01-04 | 18112 | SAN DIEGO GAS & ELECTRIC CO | 353 W PARK AVENUE | EL CAJON | SAN DIEGO | CA |  | 3 | Null | 1335 | 1999-12-18 | 0 | 1 | 50000 | 34492.4689 | 83280.943 | NO | 0 | 38 | 509425 | 19991218 | 0.25 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FACILITIES | OTHER | N/A | OTHER | N/A |  |  |  |  | 0 | 0 | ABOVE GROUND |  | ROGER W SPRENGER, SENIOR ENGINEER | 8585472023 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THE DAY OF THE INCIDENT, THE CUSTOMER WAS PAINTING HIS APARTMENT KITCHEN. SO THAT HE COULD PAINT BEHIND THE GAS RANGE, HE CLOSED THE SHUT OFF VALVE AT THE METER SET AND REMOVED THE GAS RANGE. AFTER COMPLETING HIS PAINTING, THE CUSTOMER REOPENED THE SHUTOFF VALVE AT THE METER SET. HE DID NOT RECONNECT THE GAS RANGE. GAS ESCAPED INTO THE APARTMENT BY THE OPEN GAS RANGE APPLIANCE VALVE. THE CUSTOMER LIT A CIGARETTE IGNITING THE GAS AND CAUSING AN EXPLOSION. THE CUSTOMER RECEIVED 2ND AND 3RD DEGREE BURNS AND THE APARTMENT BUILDING SUFFERED >$50,00 OF DAMAGES.
2025-01-31 10:21 | YES | NO | 20000005 | 2000-01-10 | 15518 | PIEDMONT NATURAL GAS CO INC | 8420 UNIVERSITY CITY BLVD | CHARLOTTE | MECKLENBURG | NC | 28213- | 3 | NO | 1734 | 1999-12-09 | 0 | 0 | 75000 | 51738.7033 | 124921.4145 | NO | 0 | 23 | 508515 | 19991209 | 60 | 75 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 | NIPPLE | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RONALD W COBB | 7043643120 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | NO |  | NO | 0 |  | YES | NO DATA |  | FAILURE OF THREADED PIPE IN THE METER SET ASSEMBLY.
2025-01-31 10:21 | NO | NO | 20000008 | 2000-01-13 | 1640 | BOSTON GAS CO | 25 LIBBY ROAD | MILTON | NORFOLK | MA | 2186 | 3 | Null | 1900 | 1999-12-14 | 0 | 0 | 30000 | 20695.4813 | 49968.5658 | NO | 1 | 15 | 509204 | 19991215 | 0 | 0 | BY CFR 192.619(A)(3) | 0 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.5 |  |  | 0 | 1927 | UNDER PAVEMENT |  | JOHN C HIGGINS | 7817943501 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: SUBSIDENCE |  | YES | 1999-09-02 | YES | 3 | PAINT | YES | NO DATA |  | A 6" IRON MAIN, OPERATING AT AN MAOP OF 14" WATER COLUMN, WAS INSTALLED ON LIBBY ROAD IN 1927. IN 1969, A WATER MAIN WAS INSTALLED ABOVE THE CAST IRON GAS MAIN. WOOD BLOCKING WAS USED TO SUPPORT THE WATER MAIN ON TOP OF THE GAS MAIN. IN OCTOBER THROUGH DECEMBER OF 1999, A 16" SEWER MAIN WAS INSTALLED ADJACENT TO THE WATER GAS MAINS, UNDERMINING BOTH. ON DECEMBER 14, 1999, THE GAS MAIN BROKE IN THE AREA WHERE THE WOOD BLOCKING WAS USED TO SUPPORT THE WATER MAIN. UPON EXCAVATION AND FURTHER GEO-TECHNICAL EXAMINATION, IT WAS FOUND THAT THE COMPACTION IN THE AREA ADJACENT TO THE BREAK WAS INSUFFICIENT, THEREBY CAUSING THE BREAK.
2025-01-31 10:21 | YES | NO | 20000009 | 2000-01-19 | 4483 | ENSTAR NATURAL GAS CO | LOT 6, BLK 4 WINDRIDGE ESTATES PART II | KENAI |  | AK | 9 9611 | 2 | Null | 730 | 2000-01-10 | 0 | 0 | 75000 | 50683.2179 | 122372.9792 | NO | 0 | 30 | 516591 | 20000110 | 550 | 600 |  | 1000 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPE | 1994 | 1994 | ABOVE GROUND |  | DAVID W BREDIN, MGR | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON MONDAY MORNING, JANUARY 10, 2000, AT APPROXIMATELY 7:30 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A FIRE AT LOT 6, BLOCK 4 WINDRIDGE ESTATE II SUBDIVISION, KENAI, ALASKA. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A SINGLE FAMILY HOME ON FIRE. HEAT FROM THE FIRE MELTED THE 5/8" POLYETHYLENE SERVICE LINE INSIDE THE STEEL RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED AT 8:00 AM AST. THE CAUSE OF THE FIRE IS UNKNOWN HOWEVER, NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20000010 | 2000-01-18 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) | EAST VALLEY & EVANS ROAD | EL JEBEL | PITKIN | CO |  | 3 | Null | 1025 | 1999-12-20 | 0 | 1 | 0 | 0 | 0 | NO | 3 | 0 |  | 19991220 | 350 | 400 |  | 0 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 40 | 0.395 | ASTM D2513 | PLEXCO PE 3408 | 0 | 1996 | UNDER GROUND OR UNDER WATER |  | DENNIS W JOHNSON | 3039147754 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1999-12-16 | NO | 0 |  | YES | NO DATA |  | PIPELINE WAS NOT PROPERLY MARKED
2025-01-31 10:21 | YES | YES | 20000014 | 2000-01-21 | 15259 | PENNSYLVANIA GAS & WATER CO | 112 LATHROP STREET | KINGSTON | LUZERNE | PA | 1 8704 | 3 | Null | 1343 | 1999-12-25 | 0 | 2 | 350000 | 241447.2823 | 582966.6012 | NO | 0 | 23 | 515423 | 19991225 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | OTHER | POSILOCK ADAPTER | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | F-2000 | INNER-TITE | 1976 | 1977 | UNDER GROUND OR UNDER WATER |  | JAMES M GREGER, SPECIAL PROGRAMS | 5708298866 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | FAILURE OF THE POSILOCK ADAPTER.
2025-01-31 10:21 | YES | YES | 20000015 | 2000-01-28 | 31348 | TXU GAS DISTRIBUTION | 309 N MAIN STREET | BLUE RIDGE | COLLIN | TX | 7 5215 | 3 | Null | 601 | 1999-12-12 | 1 | 0 | 100000 | 68984.9378 | 166561.8861 | NO | 14 | 29 | 508749 | 19991212 | 12 | 22 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | POLYETHYLENE PLASTIC |  | 0.75 |  | 2306 | NIPAK | 1971 | 1971 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER, SYSTEM MONITORING MGR | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A CONTRACTOR WHO WAS REPLACING A SEWER MAIN FOR THE CITY OF BLUE RIDGE PULLED A 3/4 INCH POLY SERVICE OUT OF A DRESSER COUPLING CAUSING LEAKAGE.
2025-01-31 10:21 | YES | NO | 20000016 | 2000-01-31 | 15233 | PFG GAS, INC | 825 MAIN STREET | STROUDSBURG |  | PA | 18360- | 3 | NO | 1700 | 2000-01-23 | 0 | 0 | 500000 | 337888.1191 | 815819.8614 | NO | 6 | 30 | 517634 | 20000123 | 0.25 | 2 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | JOINT |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1950 | WITHIN/UNDER BUILDING |  | ROBERT F BEARD, MGR ENGINEERING | 6109326544 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON JANUARY 23, 2000, AT APPROXIMATELY 5PM THERE WAS AN EXPLOSION OF 825 MAIN STREET, STROUDSBURG, PA. UPON INVESTIGATION BY PFG GAS INC PERSONNEL, IT WAS DETERMINED THAT AT 2" BARE STEEL NATURAL GAS MAIN LOCATED ON MAIN STREET HAD FAILED. THE APPARENT CAUSE OF THIS FAILURE IS EXCESSIVE OUTSIDE FORCE ON THE MAIN CAUSED BY SUBSIDENCE OF THE GROUND THE SUBJECT MAIN, AND AN INORDINATE AMOUNT OF PAVING MATERIAL OVER THE MAIN. UNAVAILABLE INFORMATION: SPECIFIC INFORMATION OF THE STEEL MAIN INVOLVED IS NOT AVAILABLE. SPECIFICATION, MANUFACTURER, YEAR MANUFACTURED AND YEAR INSTALLED ARE NOT AVAILABLE. HOWEVER RECORDS INDICATE THAT THIS MAIN WAS IN SERVICE PRIOR TO 1950 . ACTUAL MEASUREMENTS INDICATE THAT WALL THICKNESS IS APPROXIMATELY .154.
2025-01-31 10:21 | YES | NO | 20000017 | 2000-02-01 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 2801 LOOP 323 SSW | TYLER | SMITH | TX | 75711- | 2 | NO | 135 | 1999-11-23 | 0 | 0 | 100000 | 68984.9378 | 166561.8861 | NO | 0 | 35 |  | 19991123 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | FITTING |  | OTHER | INSULATING BUSHING | 1 |  | cboSpec |  | 0 | 0 | ABOVE GROUND |  | ERNEST DAVLIN | 9035347008 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | LIGHTENING STRUCK ELECTRICAL SERVICE, CAUSING FIRE TO GAS METER AND BUILDING.
2025-01-31 10:21 | NO | NO | 20000018 | 2000-02-01 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 609 COWAN (SOUTH DIST) | PASADENA | HARRIS | TX | 7 7506 | 3 | NO | 503 | 1999-12-23 | 0 | 0 | 50000 | 34492.4689 | 83280.943 | YES | 5 | 57 | 515309 | 19991223 | 39 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 |  |  |  | 0 | 1944 | UNDER GROUND OR UNDER WATER |  | JEFFREY A BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | NATURAL GAS FROM A 2" IP STEEL MAIN ACCUMALATED IN A HOUSE WHERE AN EXPLOSION & FIRE OCCURRED.
2025-01-31 10:21 | YES | YES | 20000020 | 2000-02-03 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 163 RIDGE STREET | CORRY | ERIE | PA | 16407- | 3 | NO | 1253 | 1999-11-21 | 0 | 1 | 200000 | 137969.8756 | 333123.7721 | NO | 4 | 50 | 506484 | 19991121 | 38 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | ASTM D2513 | DUPONT ALDYL A | 1977 | 1977 | UNDER GROUND OR UNDER WATER |  | CONRAD L DONELSON, SUPERINTENDENT | 8148718341 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION
2025-01-31 10:21 | YES | YES | 20000024 | 2000-02-04 | 18532 | SOUTHERN UNION GAS CO | 3020 WEST WALKER | BRECKENRIDGE | STEPHENS | TX | 7 6424 | 3 | Null | 1617 | 1999-12-30 | 1 | 0 | 0 | 0 | 0 | YES | 0 | 48 | 515824 | 19991230 | 15 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | 5L A25 | UNKNOWN | 0 | 1976 | ABOVE GROUND |  | PAUL JOHNSON | 9403257164 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | ACCORDING TO THE ACCIDENT REPORT, A COLLISON BETWEEN SMALL CAR AND MINIVAN OCCURRED WHEN THE SMALL CAR MADE A LEFT TURN IN FRONT OF ONCOMING TRAFFIC. THE COLLISON RESULTED IN THE SMALL CAR LEAVING THE PAVED ROADWAY AND STRIKING A GAS METER SET. THE GAS RISER TO THE METER SET WAS DAMAGED WHERE THE VALVE WAS THREADED ONTO THE RISER RESULTING IN LEAKAGE WHICH IGNITED. THE ACCIDENT RESULTED IN FATAL INJURIES TO THE DRIVER OF THE SMALL CAR.
2025-01-31 10:21 | NO | NO | 20000025 | 2000-02-10 | 12390 | METROPOLITAN UTILITIES DISTRICT | 7055 CROWN POINT | OMAHA | DOUGLAS | NE |  | 3 | Null | 1500 | 2000-01-27 | 0 | 0 | 2500 | 1689.4406 | 4079.0993 | NO | 0 | 15 |  |  | 15 |  |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.242 | ASTM D1248 | PLEXCO | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | JAMES M MCLAUGHLIN | 4024498211 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-01-25 | YES | 3 | 2000-01-25 | YES | NO DATA |  | LOCATING GAS SERVICE ERROR BY METROPOLITAN UTLITIES DISTRICT.
2025-01-31 10:21 | YES | YES | 20000026 | 2000-02-12 | 2309 | CHESAPEAKE UTILITY CORP | INGLESIDE DRIVE | MIDDLETOWN | NEW CASTLE | DE | 1 9709 | 1 | Null | 1115 | 2000-01-03 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 29 | 516045 | 20000103 | 40 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE 2406 | DRISCO | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | MARK FORESMAN | 3027346797 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20000027 | 2000-02-12 | 1088 | BALTIMORE GAS & ELECTRIC CO | 3122 BAKER STREET | BALTIMORE |  | MD | 2 1216 | 3 | Null | 1720 | 2000-01-13 | 0 | 2 | 150000 | 101366.4357 | 244745.9584 | NO | 0 | 25 | 516939 | 20000113 |  |  | BY TEST | 20 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | NO DATA |  | STEEL |  | 1.5 | 0.145 | NONE | UNKNOWN | 1909 | 1910 | WITHIN/UNDER BUILDING |  | DONALD L SHRADER | 4102915130 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | ON 1/13/00, AT 1720 AN EXPLOSION OCCURRED AT 3122 BAKER ST. IN AN ATTEMPT TO RESOLVE A POOR GAS SUPPLY TO THIS RESIDENT THE 1 1/2" GAS SERVICE WAS IN THE PROCESS OF BEING CLEARED OF RUST. NATURAL GAS WAS RELEASED INTO THE BASEMENT AND APPARENTLY IGNITED FROM THE WATER HEATER. THIS CAUSED AN EXPLOSION AND FIRE.
2025-01-31 10:21 | NO | NO | 20000028 | 2000-02-12 | 19471 | TIPTON COUNTY, FIRST UTIL DIST OF | 5442 HOLLY GROVE RD | BRIGHTON | TIPTON | TN | 38011- | 3 | NO | 815 | 2000-01-24 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 45 | 517708 | 20000124 | 50 | 80 | BY TEST | 125 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | ELTON H CLARK | 9014769525 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20000029 | 2000-02-04 | 15007 | PACIFIC GAS & ELECTRIC CO | 1452 - 19TH AVENUE | SAN FRANCISCO |  | CA | 9 4122 | 3 | Null | 2010 | 1998-05-16 | 0 | 2 | 500000 | 349224.2408 | 843190.5583 | NO | 0 | 20 | 437219 | 19980516 | 0.25 | 0.36 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | NO DATA |  | DONALD W ANDERSON | 4159730105 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AN EXPLOSION OCCURRED AT 2010 HOURS ON SATURDAY MAY 16, 1998. THE ENSUING FIRE DESTOYED A THREE STORY BUILDING AND DAMAGED ADJACENT BUILDINGS. THE CAUSE OF THE INCIDENT WAS IDENTIFIED AS IGNITION OF FIREWORKS INSIDE THE BUILDING.
2025-01-31 10:21 | NO | NO | 20000031 | 2000-02-17 | 2748 | CONSUMERS POWER CO | 1515 ELLIOTT AVENUE | MADISON HEIGHTS | OAKLAND | MI | 48071- | 3 | Null | 1121 | 2000-01-13 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 18 | 516894 | 20000113 | 52 | 60 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | INTERNAL | METER SET ASSEMBLY |  | REGULATOR/METER |  | CAST IRON |  | 0.75 |  | ASME B31.8 | AMERICAN METER | 0 | 1957 | WITHIN/UNDER BUILDING |  | JERRY F HOLWERDA, PRINCIPAL ENGINEER | 5177881835 | INTERNALLY | GENERAL CORROSION |  | OTHER | GENERAL CORROSION | NO DATA | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | PRELIMINARY INDICATIONS ARE THE SERVICE REGULATOR MAY HAVE FAILED TO FUNCTION PROPERLY, COUPLED WITH DOWNSTREAM FAILURE OF CUSTOMER EQUIPMENT. GAS ESCAPED FROM CUSTOMER EQUIPMENT AND WAS IGNITED BY UNKNOWN SOURCE. THIS ANALYSIS TO FURTHER INVESTIGATION OF CUSTOMER EQUIPMENT.
2025-01-31 10:21 | YES | YES | 20000032 | 2000-02-17 | 1088 | BALTIMORE GAS & ELECTRIC CO | 822 N LINWOOD AVE | BALTIMORE |  | MD | 2 1205 | 3 | NO | 1650 | 2000-01-26 | 0 | 1 | 100 | 67.5776 | 163.164 | NO | 3 | 10 | 517905 | 20000126 |  |  | BY TEST |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.43 | CI | UNKNOWN | 0 | 1916 | WITHIN/UNDER BUILDING |  | DENNIS C BLESSING | 4102914889 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | WE RECEIVED A GAS LEAK CALL AT 826 N LINWOOD AVE. WE FOUND A PROBLEM WITH THE GAS FURNACE AT THIS HOUSE AND PLACED A DEFECTIVE APPLIANCE TAG ON THE EQUIPMENT. THE MECHANIC PERFORMED A FRONT WALL INSPECTION AND PICKED UP A READING ON HIS METER. HE PROCEEDED TO CHECK OTHER HOMES IN THE BLOCK AND FOUND A READING OF GAS AT THE FRONT WALL OF 822 N LINWOOD AVE. HE HAD NO READINGS IN THE ATMOSPHERE OF THE DWELLING. HE TURNED ON A LIGHT IN THE CEILING OF THE BASEMENT SO AS TO SEE BETTER. AFTER FINISHING HIS CHECKS THE OWNER TURNED OFF THE LIGHT SWITCH AND A MINOR EXPLOSION OCCURRED. THE CUSTOMERS HAIR WAS SET FIRE AND SHE RECEIVED MINOR BURNS.THE MECHANIC WAS ABLE TO PUT OUT THE FIRE AND CALLED 911 FOR EMERGENCY PERSONNEL. WE LOCATED THE LEAK AND MADE REPAIRS TO THE 4" GAS MAIN. AFTER THE MAIN WAS REPAIRED THE FRONT WALL READINGS DISAPPEARED. WE FEEL A POCKET OF GAS HAD BUILT UP IN THE CONFINED CEILING AREA. AFTER THE MINOR EXPLOSION WE REMOVED SOME PANELING AND FOUND WALL WAS EXTREMELY WELL INSULATED AND THIS ALLOWED THE GAS TO POCKET ABOVE THE CEILING.
2025-01-31 10:21 | YES | NO | 20000033 | 2000-02-22 | 4483 | ENSTAR NATURAL GAS CO | ARTIC BLVD & TUDOR RD | ANCHORAGE |  | AK | 9 9618 | 3 | Null | 1515 | 2000-01-26 | 0 | 0 | 75000 | 50683.2179 | 122372.9792 | NO | 14 | 48 | 518074 | 20000128 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.188 | GRADE B STEEL, |  | 1962 | 1963 | UNDER PAVEMENT |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-01-19 | YES | 3 |  | YES | NO DATA |  | ON WEDNESDAY, JANUARY 26, 2000, AT APPROXIMATELY 3:15 PM AST, ENSTAR RECEIVED NOTICE THAT A GAS MAIN AT THE INTERSECTION OF TUDOR ROAD AND ARTIC BLVD. IN ANCHORAGE, ALASKA, HAD BEEN DAMAGED AND LEAKING NATURAL GAS. UPON ARRIVAL, ENSTAR CREWS FOUND AN AUGER DRILLED INTO AN 8" STEEL MAIN OPERATING AT 60 PSIG. NATURAL GAS WAS BLOWING THROUGH THE CORE OF THE AUGER. A SECOND AUGER WAS DRILLED CLOSE TO THE GAS MAIN 10 TO THE SOUTH AND A THIRD AUGER HOLE WAS LOCATED 2 NORTH OF THE DAMAGE. AN ENVIRONMENTAL ENGINEERING FIRM TAKING SOIL SAMPLES DRILLED THE HOLES. ENSTAR CREWS CLOSED PORTIONS OF THE INTERSECTION AND WORKED ALL NIGHT TO EXPOSE THE DAMAGED MAIN. THE MAIN WAS 7 1/2 DEEP. THE GROUND WAS FROZEN 8 DEEP. AT 6:03 AM AST, THURSDAY, JANUARY 27, A STEEL REPAIR FITTING WAS BOLTED OVER THE LEAK TO STOP THE BLOWING GAST. THE AUGER HAD DRILLED INTO THE MAIN, CAUSING HAIRLINE CRACKS TO FORM ON THE TOP OF THE MAIN. THE SECOND AUGER WAS UNCOVERED AND FOUND TO HAVE ALSO DAMAGED THE 8" MAIN. IT HAD GLANCED OFF THE SIDE OF THE 8" MAIN, SCRAPING THE SIDE OF THE PIPE, REMOVING APPROXIMATELY 50% OF THE PIPE WALL THICKNESS. THE THIRD AUGER HOLE WAS UNCOVERED AND FOUND THAT THE AUGER HAD STRUCK THE 8" MAIN "DEAD CENTER" REMOVING APPROXIMATELY 50% OF THE PIPE WALL THICKNESS. THE DRILLER INDICATED HE HAD CEASED DRILLING IN THIS HOLE BECAUSE HE RAN INTO SOMETHING HARD AND WHEN HE PULLED UP HIS BIT HE HAD METAL SHAVINGS ON IT. TO MAKE PERMANENT REPAIRS, A PRESSURE CONTOL FITTING WAS WELDED ON THE 8" MAIN AND NEARBY VALVE WAS CLOSEDD TO ISOLATE THE DAMAGED SECTION OF MAIN. A 12 SECTION OF PIPE CONTAINING ALL THREE DAMAGES WAS REMOVED AND A PIECE OF PRETESTED PIPE WAS WELDED IN ITS PLACE. THE CONTRACTOR HAD REQUESTED LOCATES AND ENSTAR HAD LOCATED THE PIPE PRIOR TO DRILLING. ENSTARS LOCATE MARKS WERE SEVERAL INCHES OUTSIDE THE 2 ACCURACY LIMITS PLACED ON IT BY LOCAL ORDIANCE. HOWEVER, LOCAL ORDINANCE REQUIRES ALL LOCATED UTILITIES TO BE EXPOSED PRIOR TO EXCAVATING AND TO REPORT ANY DAMAGE IMMEDIATELY UPON KNOWLEDGE OF SUCH DAMAGE. ENSTAR BELIEVES IT WAS UNREASONABLE FOR THE HOLES TO BE DRILLED WITHIN 5 OF ITS LINE WITHOUT PHYSICALLY EXPOSING THE PIPE. ENSTAR ALSO BELIEVES IT SHOULD HAVE BEEN IMMEDIATELY NOTIFIED WHEN METAL SHAVINGS WERE FOUND ON THE DRILL BIT. ENSTAR IS ACTIVELY PURSUING COLLECTION OF THIS CLAIM.
2025-01-31 10:21 | NO | NO | 20000034 | 2000-02-24 | 19040 | TALLAPOOSA GAS DEPT, CITY OF | 91 MAYS STREET | TALLAPOOSA | HARALSON | GA | 3 0176 | 3 | Null | 1000 | 2000-01-25 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 45 |  | 20000125 | 25 | 25 | BY CFR 192.619(A)(3) |  | NO DATA | ALL OTHER CAUSES | UNKNOWN | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.25 | UNKNOWN | UNKNOWN | 0 | 1949 | UNDER PAVEMENT |  | PHILIP EIDSON, CITY MANAGER | 7705742345 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | NATURAL GAS MIGRATED INTO MANHOLE AND SEWER LINE. NATURAL GAS ENTERED DWELLING THROUGH IMPROPER INSTALLED SEWER CONNECTION. SOURCE OF IGNITION UNKNOWN.
2025-01-31 10:21 | YES | YES | 20000035 | 2000-02-24 | 13360 | NEW ORLEANS PUBLIC SERVICE INC | 709-11 N SALCEDO | NEW ORLEANS |  | LA | 70119- | 3 | NO | 2355 | 2000-01-27 | 1 | 0 | 0 | 0 | 0 | NO | 1 | 20 |  | 20000128 | 0.25 | 0.54 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | SCHEDULE 40 | UKNOWN | 1925 | 1925 | WITHIN/UNDER BUILDING |  | WALTER H ROSS JR | 5045933462 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 12:40 A.M. ON 1/28/00, THE NEW ORLEANS FIRE DEPARTMENT NOTIFIED THE ENTERGY OIC THAT GAS WAS INVOLVED IN A FIRE. THE GAS SERVICE MAN ON DUTY WAS NOTIFIED BY THE OIC. AT APPROXIMATELY 1:20 A.M., THE GAS SERVICE MAN ARRIVED ON THE SCENE, BUT COULD NOT APPROACH THE GAS METER INSTALLATION BECAUSE OF THE FIRE. AT APPROXIMATELY 1:40 A.M. THE DUTY GAS REPAIR TRUCK WAS NOTIFIED OF THE OF LEAK. AT APPROXIMATELY 2:00 A.M. THE GAS REPAIR TRUCK ARRIVED ON THE SCENE. AT APPROXIMATELY 2:30 A.M. THE LOW PRESSURE (1/4 PSIG) GAS SERVICE WAS CUT OFF IN THE STREET TO STOP THE GAS SUPPLY AND THE FIRE EXTINGUISHED. THE RESIDENT, MISS MAE, WAS PRONOUNCE DEAD ON THE SCENE AS A RESULT OF INJURIES SUSTAINED IN THE FIRE. THE ENTERGY GAS NETWORK MANAGER ARRIVED ON THE SCENE AT APPROXIMATELY 2:45 A.M. AND PROCEEDED TO REVIEW AND VIDEO THE SCENE. THE ENTERGY GAS REPAIR CREW PERFORMED A LEAK INVESTIGATION IN FRONT OF THE ADDRESS AND ALONG THE BLOCK USING A COMBUSTIBLE GAS INDICATOR CHECKING AVAILABLE OPENINGS IN THE GROUND IN THE GROUND AND STREET. TELEPHONIC NOTIFICATION OF THE INCIDENT WAS MADE TO MR. WALTER BLOCKER AT APPROXIMATELY 3:00 A.M. INVESTIGATION REVEALED THA THE GAS SERVICE RISER COCKS FOR BOTH 709 AND 711 N SALCEDO WERE TURNED OFF, SHACKLED, AND LOCKED PRIOR TO, AND DURING THE FIRE. (NOTE THAT 711 IS BRANCH OFF THE 709 SERVICE). INVESTIGATION REVEALED THAT GAS SERVICE TO THE HOUSE HAD BEEN TURNED OFF PRIOR TO THE INCIDENT ON ACCOUNT OF NON-PAYMENT. COMPANY RECORDS INDICATE THAT THE GAS SERVICE TO 709 N SALCEDO WAS TURNED OFF ON 5/15/99 AND THE GAS SERVICE TO 711 N SALCEDO WAS TURNED OFF ON 7/21/99. ODOROMETER TESTS WERE PERFORMED ON 1/28/00 AT A VACANT HOUSE ACROSS THE STREET AND INDICATED ADEQUATE LEVELS OF ODORANT. A COPY OF THE ODORMETER TEST RESULTS IS ATTACHED. A LEAK SURVEY WAS PERFORMED ON 1/31/00 USING FLAME IONIZATION EQUIPMENT ON THE ENTIRE BLOCK INCLUDING AND SURROUNDING THE SUBJECT ADDRESS. NO INDICATIONS OF LEAKS WERE FOUND. THE NEW ORLEANS FIRE DEPARTMENTS FIRE INCIDENT REPORT STATED THAT THE AREA OF ORIGIN WAS IN THE BEDROOM.
2025-01-31 10:21 | YES | YES | 20000036 | 2000-02-23 | 4350 | ELIZABETHTOWN GAS CO | 32 CHRUCH STREET | FLEMINGTON | HUNTERDON | NJ |  | 4 | Null | 1443 | 2000-01-22 | 0 | 2 | 200000 | 135155.2476 | 326327.9446 | NO | 1 | 32 | 517573 | 20000122 | 55 | 60 | BY CFR 192.619(A)(3) | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  |  |  | PosiLock Adapter | INNER-TITE | 0 | 1971 | UNDER PAVEMENT |  | PHIL SALVATORE | 9086628306 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A mechanical compression fitting the polyethylene gas service line to the gas main was improperly installed. The connection separated allowing natural gas to migrate into the basement of the premises
2025-01-31 10:21 | YES | NO | 20000040 | 2000-02-29 | 792 | ATLANTA GAS LIGHT CO | 1959 CORNERS CIRCLE | LITHONIA | DEKALB | GA | 3 0038 | 3 | Null | 2213 | 2000-01-29 | 0 | 0 | 150000 | 101366.4357 | 244745.9584 | NO | 0 | 29 | 518191 | 20000130 | 12 | 0.75 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM |  |  |  | AMERICAN METER | 0 | 0 | WITHIN/UNDER BUILDING |  | TOMMY E GRAHAM | 7706024100 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | DUE TO OUTSIDE WEATHER CONDITIONS REGULATOR HAD FROZEN (ICE IN VENT) IN THE OPEN POSITION. THIS CONDITION ALLOWED 12 POUNDS OF PRESSURE TO BE PUT ON CUSTOMERS FUEL LINE. THIS RESULTED IN A FIRE AT THE WATER HEATER IN THE GARAGE AREA OF THE RESIDENCE.
2025-01-31 10:21 | YES | YES | 20000041 | 2000-02-29 | 13041 | NASHVILLE GAS CO | 1555 OLD HICKORY BLVD | BRENTWOOD | WILLIAMSON | TN | 3 7027 | 2 | Null | 913 | 2000-01-27 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 0 |  | 20000127 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | JOHN L CLARK JR. (VP TENNESSEE OPERATIONS) | 6157341709 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE FIRE MOST LIKELY RESULTED FROM NATURAL GAS LEAKING FROM THE CUSTOMER OWNED UNDERGROUND FUEL LINE TO A POOL HEATER. NASHVILLE GAS FACILITIES SERVING THIS ADDRESS DID NOT HAVE ANY LEAKAGE AND DID NOT CONTRIBUTE TO THIS HOUSE FIRE.
2025-01-31 10:21 | YES | YES | 20000042 | 2000-02-18 | 31348 | TXU GAS DISTRIBUTION | 1302 ALAMO LANE | GARLAND | DALLAS | TX | 7 5040 | 3 | Null | 313 | 2000-01-14 | 3 | 0 | 150000 | 101366.4357 | 244745.9584 | YES | 2 | 16 |  | 20000114 | 19 | 55 |  | 90 | NO DATA | ALL OTHER CAUSES | UNKNOWN | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 4 | 0.41 | PE 2406 | PLEXCO | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A LEAK OCCURRED ON THE MAIN AT A FUSION POINT. GAS MIGRATED UNDER THE STRUCTURE AND THE GAS IGNITED. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED ONCE AN ENGINEERING LABORATORY ANALYSIS OF THE PIPE IS COMPLETED.
2025-01-31 10:21 | YES | YES | 20000043 | 2000-02-29 | 31348 | TXU GAS DISTRIBUTION | 8101 ROYAL RIDGE PKWY | IRVING |  | TX | 7 5063 | 2 | NO | 1040 | 2000-01-19 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 29 |  | 20000119 | 21 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | RISER | VALVE |  | CAST IRON | [5 empty] | 0 | 0 | ABOVE GROUND |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 |  | YES | NO DATA |  | A VEHICLE BACKED INTO A VACANT RISER KNOCKING THE STOPCOCK OFF. A BUILDING WAS EVACUATED AND TXU GAS DISTRIBUTION HAS UNCONFIRMED INFORMATION THAT AN EVACUEE WAS HOSPITALIZED.
2025-01-31 10:21 | YES | NO | 20000047 | 2000-03-08 | 22182 | WASHINGTON GAS LIGHT CO | 5101 CONNECTICUT AVE NW | WASHINGTON |  | DC |  | 1 | NO | 2225 | 2000-02-04 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 1 | 35 |  | 20000204 |  |  | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | ROMELIA L KEMP | 7037505564 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE FIRE IN PROGRESS, CAUSE UNDETERMINED BY FIRE DEPT. METER AND PIPING EXPOSED TO FIRE. SERVICE WAS UNCOVERED IN SIDEWALK THEN CUT AND PLUGGED.
2025-01-31 10:21 | YES | NO | 20000048 | 2000-03-08 | 22182 | WASHINGTON GAS LIGHT CO | 20870 ISHERWOOD TERRACE | ASHBURN | LOUDOUN | VA |  | 2 | NO | 1556 | 2000-02-02 | 0 | 0 | 750000 | 506832.1786 | 1223729.7921 | NO | 0 | 40 | 518564 | 20000202 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTMD2513 | PHILLIPS | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | ROMELIA L KEMP | 7037505564 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO | 1999-12-30 | NO | 0 |  | YES | NO DATA |  | A PLUMBER FROM COMMONWEALTH PLUMBING RESTED THE PIPE HE WAS SOLDERING DIRECTLY ON OUR 3/4" HIGH PRESSURE PLASTIC SERVICE. PENETRATION TO THE SERVICE OCCURRED CAUSING A FIRE AND SIGNIFICANT PROPERTY DAMAGE.
2025-01-31 10:21 | YES | YES | 20000049 | 2000-03-13 | 6030 | GAINESVILLE REGIONAL UTIL GAS DEPT | 5515 NW 45TH DRIVE | GAINESVILLE | ALACHUA | FL | 3 2606 | 4 | NO | 1407 | 2000-03-06 | 0 | 1 | 3500 | 2365.2168 | 5710.739 | NO | 0 | 38 |  | 20000306 | 60 | 60 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 |  | PLEXCO | 0 | 1995 | UNDER GROUND OR UNDER WATER |  | THOMAS L BRAZEAL | 3523343600 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A BELL SOUTH EMPLOYEE WAS WORKING IN A BELLHOLE WITH A TORCH AND APPARENTLY BURNED A HOLE IN A 5/8" GAS SERVICE LINE. THE ESCAPING GAS WAS IGNITED BY THE TORCH.
2025-01-31 10:21 | NO | NO | 20000050 | 2000-03-14 | 2778 | COPPER MARKET INC |  | BAGDAD | YAVAPAI | AZ | 8 6321 | 2 | NO | 630 | 2000-02-23 | 0 | 0 | 11608 | 7844.4106 | 18940.0739 | YES | 0 | 32 |  | 20000223 |  | 30 |  |  | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | REGULATING STATION | REGULATOR/METER |  | NO DATA |  |  |  |  | FISHER | 1994 | 1995 | ABOVE GROUND |  | JACK MCBRIDE | 5206333262 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | OTHER | PILOT ACCURATED FAILURE & OPERATOR | PILOT ACCURATOR FAILURE ON MONITORING REGULATOR. MAINTENANCE PERSONS FAILURE TO REARM VERBATIM ALARM SYSTEM.
2025-01-31 10:21 | YES | YES | 20000051 | 2000-03-13 | 11032 | LACLEDE GAS CO | 1904 BIRCHWOOD DR | BARNHART | JEFFERSON | MO | 6 3012 | 3 | NO | 1501 | 2000-02-07 | 1 | 0 | 150000 | 101366.4357 | 244745.9584 | NO | 1 | 50 |  | 20000207 | 27 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | D2513 | PHILLIPS | 1996 | 1997 | UNDER GROUND OR UNDER WATER |  | PAUL HUNKER | 3143420528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-01-26 | YES | 3 | 2000-01-26 | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20000052 | 2000-03-15 | 22725 | WINFIELD GAS DEPT, CITY OF | 22234 C ST | STROTHER FIELD | COWLEY | KS | 6 7156 | 3 | NO | 1300 | 2000-03-01 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 30 |  | 20000302 |  | 40 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | GEORGE BRONSON |  | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | APPEARS THAT IGNITER ON GAS DRYER OF PRINTING PRESS FAILED TO ARC. GAS ACCUMULATION CAUSED EXPLOSION. NO FIRE
2025-01-31 10:21 | YES | YES | 20000053 | 2000-03-15 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | FOREST & ISLA INTERSECTION | BEAUMONT | JEFEFRSON | TX | 7 7708 | 3 | NO | 1234 | 2000-02-13 | 0 | 3 | 0 | 0 | 0 | NO | 0 | 46 |  | 20000213 | 25 | 50 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | SOUTHWESTERN BELL MANHOLE | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | OTHER | SOUTHWESTERN BELL MANHOLE | JAY JOHNSTON | 4098603400 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | FLASH FIRE AT SOUTHWESTERN BELL MOBILE
2025-01-31 10:21 | YES | NO | 20000054 | 2000-03-13 | 12018 | MADISON GAS & ELECTRIC CO | 1110 ERIN ST | MADISON | DANE | WI | 5 3715 | 3 | NO | 1032 | 2000-02-25 | 0 | 0 | 200000 | 135155.2476 | 326327.9446 | NO | 0 | 33 |  | 20000225 | 18 | 20 |  | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | PLEXCO | 1982 | 1982 | UNDER GROUND OR UNDER WATER |  | PHILIP NELSON | 6082577277 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-02-02 | YES | 2 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 20000059 | 2000-03-21 | 12582 | MISSISSIPPI VALLEY GAS | INTERSECTION OF 4TH ST AND 7TH AVE S | COLUMBUS | LOWNDES | MS | 3 9703 | 3 | NO | 1935 | 2000-02-23 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 15 | 520907 | 20000223 | 0.25 | 0.5 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER |  | CAST IRON |  | 4 | 0.5 |  |  | 0 | 1930 | UNDER PAVEMENT |  | DAN OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20000060 | 2000-03-20 | 11824 | LOUISVILLE GAS & ELECTRIC CO | 903 ELM ST | WEST POINT | HARDIN | KY | 4 0177 | 3 | NO | 505 | 2000-02-20 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 40 | 520532 | 20000220 | 15 | 15 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HOUS PIPING | BODY OF PIPE |  | STEEL |  | 1 |  | cboSpec | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | JOSEPH RYAN | 5026272433 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 5:05 AM ON SUNDAY FEB.20,2000 THE LG&E ELECTRIC SERVICE BOARD RECEIVED A CALL FROM THE WEST POINT FIRE DEPARTMENT STATING THAT THERE HAD BEEN AN EXPLOSION INSIDE THE RESIDENTIAL DWELLING AT 903 ELM ST CAUSING NATURAL GAS TO BE DISCHARGE TO THE ATMOSPHERE AND RESULTING IN A FIRE. A LG&E GAS SERVICEMAN WAS IMMEDIATELY DISPATCHED AT 5:05 AM. THE GAS ELECTRIC TO 903 ELM ST WERE TURNED OFF AT 5:45 AM. THE EXPLOSION OCCURED INSIDE A ONE STORY WOOD FRAME RESIDENTIAL HOME. THE EXPLOSION OCCURED UNDER THE HOUSE IN THE HOUSE IN CRAWL SPACE. THE BLOCK FOUNDATION HAD BEEN BLOWN OUTWARD ON ALL SIDES OF THE HOUSE. THE FIRE WAS LOCATED MAINLY OUTSIDE THE REAR WALL AROUND THE FLUE AREA AND THE FLOOR OF THE KITCHEN. THE HOMEOWNER WAS MR. LOUIS RUSSELL CURL RESIDING AT 903 ELM ST WEST POINT KENTUCKY. TANYA COOK OF 808 MAIN ST REPORTED THE INCIDENT. THIS ADDRESS IS LOCATED DIRECTLY BEHIND 903 ELM ST. SHE SAID THAT SHE HAD HEARD AN EXPLOSION AND LOOKED OUT AND SAW FIRE COMING FROM THE CEILING FELL ON HIM WHILKE HE WAS IN THE BED. HE STATED THAT HE THEN GOT UP AND PUT HIS CLOTHES ON AND THEN WENT INTO THE KITCHEN AREA. WHEN HE RCHED THE KITCHEN HE SAW SMOKE COMING FROM AROUND THE BOTTOM OF A HEATING STOVE WHICH WAS UP AGINST THE SOUTH WALL OF THE HOUSE. THE FLEW IS LOCATED DIRECTLY BEHIND THE STOVE AND AGINST THE SAME WALL LYING ON THE FLOOR. ACCORDING TO MR. CURL BOTH HEATING AND COOKING STOVES HAD BEEN IN THE HOME FOR OVER TWENTY YERS. MR. CURL STATED THAT HE TURNED THE GAS VALVE OFF TO THE HEATING STOVE BEFORE VACATING THE HOUSE. MR. LOUIS CURL RECEIVED NO INJURIES FROM THE FIRE. THE LG&E GAS ERVICE TO 903 ELM ST WAS A ONE INCH SERVICE CONSISITNG OF 1 INCH BARE STEEL PIPE APPROXIMATELY 4 FEET IN LENGTH FROM THE 10 INCH LG&E DISTRIBUTION MAIN TO THE GAS SERVICE STOP BOX. THE CUSTOMER SERVICE PIPING WAS 1 INCH BARE STEEL PIPE APPROXIMATELY 100 FEET IN LENGTH. THE SERVICE WAS INSTALLED IN 1942. THE COPMANY SERVICE PIPING WAS SUBSEQUENTLY REPLACED WITH 3/4 INCH STEEL PIPE WITH A THIN MILL COATING FROM A NEW 2 INCH LG&E DISTRIBUTION MAIN OPERATING AT 15 PSIG ON JULY 22, 1974. THE MOST RECENT LEAK SURVEY ON THE GAS SERVICE AT 903 ELM ELM ST WAS CONDUCTED DURING JUNE OF 1999. NO LEAKS WERE FOUND ON EITHER THE COMPANY OWNED OR CUSTOMER OWNED PIPING. THE MOST RECENT STOPBOX INSPECTION WAS CONDUCTED ON OCT19,1995. THE MOST RECENT SERVICE CALL TO 903 ELM ST WAS MADE ON FEB. 25, 1985 WHEN THE GAS METER WAS CHANGED. THERE WERENO CALLS TO LG&E PRIOR TO THE INCIDENT ABOUT ANY NATURAL GAS LEAKS OR ODORS FROM THE MR.CURL OR ANY OF THE NEIGHBORS. A PRESSURE TEST WAS CONDUCTED ON THE LG&E GA SDISTRIBUTION DEPARTMENT PERFORMED THE TEST. THE CUSTOMERS WAS PNEUMATICALLY TESTED FOR 15 MINUTES AT 35 PSIG. THE LG&E SERVICE WA TESTED FRPM THE STOPBOX TO THE GAS DISTRIBUTION MAIN FOR 15 MINUTES AT 100 PSIG. NO LEAKS WERE DETECTED ON EITHER THE LG&E SERVICE OR THE CUSTOMER SERVICE. THE CUSTOMER HOUSE PIPING WAS TESTED AT 6OZ. THE PRESSURE DROPPED TO ZERO IN 30 SECONDS THUS FAILING THE PRESSURE TEST. GAS ODORANT LEVELS WERE CHECKED ON FEB. 17,2000 AT 602 ELM ST AND ON THE DAY OF THE INCIDENT AT MULBERRY ST WHICH IS LOCATED BEHIND 903 ELM ST. THE ODORANT LEVELS WERE SATISFACTORY. THE EXPLOSION WASINVESTIGATED BY DEPUTY SHERIFF OFFICE AND MR KEITH MCBRIDE FIRE AND SECURITY INVESTIGATOR LOUISVILLE GAS AND ELECTRIC COMPANY.THE INVESTIGATION OF THE INCIDENT CONCLUDED THAT GAS HAD BUILT UPUNDER THE FLOOR IN THE CRAWL SPACE. ONCE THERE WAS ENOUGH GAS TO REACH AN IGNITION SOURCE MOST PROBABLY THE HEATING STOVE THE GAS IGNITED. THE BIULK OF THE GAS WAS IN THE CRAWL SPACE THUS THE BLOWING OF THE BRICK OUT ON ALL FOUR SIDES. THE HOUSE PIPING WAS IN THE SAME AREA AS THE POINT OF THE ORIGINOF THE FIRES WHICH WAS ALONG THE SOUTH WALL. THE GAS MOST LIKELY RESULTED FROM LEAKS IN THE HOUSE PIPING AND CAME FROM UNDER THE FLOOR AND WENT UP IN TO THE REAR WALL SPACE AND CAME OUT AT THE LOCATION WHERE THE STOVE WAS LOCATED. THE INCIDENT MEETS THE CRITERIA MEETS THE C
2025-01-31 10:21 | YES | YES | 20000061 | 2000-03-20 | 14210 | OKLAHOMA NATURAL GAS CO | 116 1/2 PANEL RD | ELK CITY | BECKHAM | OK | 7 3644 | 3 | Null | 730 | 2000-02-17 | 0 | 1 | 12000 | 8109.3149 | 19579.6767 | NO | 2 | 30 | 520255 | 20000217 | 32 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | PE2306 |  | 0 | 1982 | UNDER PAVEMENT |  | JAMES KUNKEL | 4055566401 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | GAS MIGRATED UNDER PAVEMENT FROM COLD FUSED POLYTHYLENE PIPE JOINT THROUGH A SEWER CONNECTION TO A PORTABLE BUILDING BEING USED AS A FIELD OFFICE. THE GAS IGNITED WHEN AN ELECTRICAL SWITCH WAS TURNED ON BY AN EMPLOYEE. THE EMPLOYEE WAS INJURED AND HOSPITALIZED.
2025-01-31 10:21 | YES | YES | 20000064 | 2000-03-24 | 18484 | SOUTHERN CALIFORNIA GAS CO | 24468 PARK ST | TORRANCE | LOS ANGELES | CA |  | 3 | NO | 1427 | 2000-02-23 | 0 | 1 | 100000 | 67577.6238 | 163163.9723 | NO | 4 | 3 | 520908 | 20000223 | 35 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 5 |  |  |  | 1983 | 1983 | UNDER PAVEMENT |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EXPLOSION OCCURRED WHEN CUSTOMER ATTEMPTED TO LIGHT A WALL FURNANCE. FURTHER INVESTIGATION FOUND A LEAKING 1/2 PLASTIC SERVICE AT ADJACENT PROPERTY. CAUSE OF LEAK UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 20000065 | 2000-03-29 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1005 E 3RD STREET | CALEXICO | IMPERIAL | CA |  | 3 | NO | 1138 | 2000-02-29 | 0 | 0 | 60000 | 40546.5743 | 97898.3834 | NO | 0 | 30 | 521504 | 20000229 | 35 | 60 | BY TEST |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.5 |  | PE |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | BACKHOE OPERATOR PULLED BRANCH SERVICE. LEAKING GAS WAS IGNITED BY WATER HEATER.
2025-01-31 10:21 | YES | YES | 20000066 | 2000-03-29 | 4475 | PENSACOLA, ENERGY SERVICES OF | 2132 JARROD DRIVE | CANTONMENT | ESCAMBIA | FL | 3 2514 | 2 | NO | 1150 | 2000-03-07 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 0 | 522212 | 20000308 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.18 | 2406 SDR | PLEXCO | 0 | 1997 | UNDER GROUND OR UNDER WATER |  | DON J SUAREZ | 8504745316 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-03-07 | YES | 3 | 2000-03-07 | YES | NO DATA |  | TIME WARNER CABLE COMPANY EMPLOYEE DAMAGED 5/8" P.E. SERVICE LINE BY USING PROPANE TORCH TO APPLY SHRINK WRAP COATING TO CABLE REPAIR. TORCH HEAD WEAKENED OR MELTED SERVICE LINE AND LEAKING GAS IGNITED, BURNING TIME WARNER EMPLOYEE ON FACE AND UPPER TORSO.
2025-01-31 10:21 | NO | NO | 20000067 | 2000-03-29 | 31202 | RELIANT ENERGY FIELD SERVICES CORP | SW 67TH STREET | LAWTON | COMMANCHE | OK | 73501- | 3 | NO | 1100 | 2000-03-13 | 0 | 0 | 15400 | 10406.9541 | 25127.2517 | NO | 1 | 0 |  | 20000313 | 90 | 125 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REG STATION | REGULATOR/METER |  | STEEL |  | 2 |  | 243 RPC | ROCKWELL | 0 | 1996 | NO DATA |  | R L MYERS | 5802505400 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | NO | 0 |  | NO | NO DATA
2025-01-31 10:21 | NO | NO | 20000068 | 2000-03-30 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 12TH AND MAIN STREET | RICHMOND |  | VA | 23219- | 4 | NO | 800 | 2000-02-22 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 30 | 520735 | 20000222 | 0.22 | 0.29 | BY TEST | 85 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0.09 | SDR11 | DRISCO PIPE | 0 | 1985 | UNDER PAVEMENT |  | ROBERT HOWARD | 8046468330 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-02-03 | YES | 3 | PAINT | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20000070 | 2000-04-04 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | WHIPPORWILL ROAD | IRONDALE | JEFFERSON | AL | 35210- | 2 | NO | 952 | 2000-03-17 | 0 | 0 | 400000 | 270310.4953 | 652655.8891 | NO | 3 | 15 | 661505 | 20000317 | 250 | 275 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LEE PETERS | 2053268186 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-03-14 | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20000073 | 2000-04-17 | 18536 | SOUTHWEST GAS CORPORATION | SOUTH FRONTAGE ROAD AT AVENUE 12E | YUMA | YUMA | AZ | 85367 | 3 | NO | 310 | 2000-03-20 | 0 | 0 | 129322 | 87392.7347 | 211006.9122 | YES | 2 | 52 | 523807 | 20000320 | 182 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  |  |  | 2" SINGLE PORT | MOONEY | 1993 | 1994 | ABOVE GROUND |  | JIM LANTTO, ADMINISTRATOR/COMPLIANCE | 5207946034 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null |  |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20000077 | 2000-04-18 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | GREEN AVE & GARFIELD AVE | MADISON | MORRIS | NJ |  | 3 | NO | 1330 | 2000-03-23 | 0 | 2 | 0 | 0 | 0 | NO | 3 | 0 | 524048 | 20000324 | 0.25 | 0.25 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 |  |  |  | 0 | 0 | UNDER PAVEMENT |  | PETER A CISTARO | 9734305100 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20000078 | 2000-04-20 | 12582 | MISSISSIPPI VALLEY GAS | 506/507 PORTER DRIVE | INDIANOLA | SUNFLOWER | MS | 38751- | 3 | NO | 245 | 2000-03-19 | 0 | 0 | 0 | 0 | 0 | NO | 1 | 30 | 523520 | 20000319 | 16 | 30 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1970 | UNDER GROUND OR UNDER WATER |  | DAN OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR PULLED 3/4 SERVICE LINE OUT OF 3/4" DRESSER ELL AT SERVICE TIE-IN TO 2" STEEL MAIN. GAS MIGRATED TO SANITARY SEWER AND INTO HOUSES FROM LEAKS IN SEWER PIPES IN HOMES. GAS IGNITED FROM WATER HEATER.
2025-01-31 10:21 | YES | YES | 20000079 | 2000-04-20 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 2101 W 35TH AVE | GARY | LAKE | IN | 46408- | 3 | NO | 20 | 2000-03-15 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 522959 | 20000315 | 28 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | A53 |  | 1996 | 1996 | ABOVE GROUND |  | DON J TOKOLV | 2196474770 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE LOCATION OF THE GAS INCIDENT IS NEAR A LIQUEFIED NATURAL GAS (LNG) REFUELING STATION, OWNED AND OPERATED BY THE CITY OF GARY TRANSPORTATION CENTER. BOIL-OFF FROM THE LNG TANK IS COLLECTED, METERED AND INJECTED INTO NIPSCOS GAS DISTRIBUTION SYSTEM IN THE VICINITY OF THE REFUELING STATION. A VEHICLE ASSOCIATED WITH THE TRANSPORTATION CENTER DROVE AROUND THE BARRIERS ONTO A GRASSY ARE NOT INTENDED FOR VECHICLE TRAFFIC. IN THE PROCESS, IT STRUCK THE ABOVE GROUND VENT OF THE UNDERGROUND LINE THAT RETURNS BOIL-OFF GAS TO THE NIPSCO DISTRIBUTION SYSTEM. THE FORCE OF THE VEHICLES IMPACT CREATED A LEAK IN THE UNDERGROUND LINE. NATURAL GAS MIGRATED FROM THE LINE TO A NEARBY GUARD HOUSE. WHEN THE ATTENDANT RETURNED TO THE GUARD HOUSE AND ATTEMPTED TO LIGHT A CIGARETTE, IT IGNITED THE NATURAL GAS. THE ATTENDANT SUFFERED BURNS TO HIS HANDS AND FACE. HE HAS SINCE BEEN RELEASED FROM THE HOSPITAL. THE GAS LINE WAS REPAIRED.
2025-01-31 10:21 | YES | NO | 20000084 | 2000-04-26 | 2364 | CINCINNATI GAS & ELECTRIC CO | 3781 BELFAST AVENUE | CINCINNATI | HAMILTON | OH | 4 5236 | 4 | Null | 2017 | 2000-02-12 | 0 | 0 | 180000 | 121639.7229 | 293695.1501 | NO | 1 | 43 | 519674 | 20000212 | 10 | 25 | BY TEST | 25 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.35 |  |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | SUSAN M. GILB | 5132872752 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A CRACK IN A 4" CAST IRON MAIN
2025-01-31 10:21 | YES | YES | 20000085 | 2000-04-27 | 15350 | PEOPLES NATURAL GAS CO | 38 & 40 PATRICIA DRIVE | GREENSBURG | WESTMORELAND | PA |  | 3 | Null | 1230 | 2000-03-22 | 0 | 3 | 300000 | 202732.8714 | 489491.9169 | NO | 3 | 0 | 523811 | 20000322 | 68 | 80 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 12 | 0.286 |  |  | 1940 | 1941 | UNDER GROUND OR UNDER WATER |  | JOYCE C. DAILEY, ESQUIRE | 4124975668 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-03-08 | YES | 3 | TEMPORARY PAINT | YES | NO DATA |  | THIRD PARTY CONTRACTOR BORED THROUGH 12 INCH NATURAL GAS DISTRIBUTION LINE.
2025-01-31 10:21 | YES | NO | 20000086 | 2000-04-27 | 15350 | PEOPLES NATURAL GAS CO | 1304 RT. 68/MIDLAND BEAVER RD.) | INDUSTRY | BEAVER | PA | 1 5052 |  | Null | 300 | 2000-03-22 | 0 | 0 | 150000 | 101366.4357 | 244745.9584 | NO | 0 | 30 | 523841 | 20000322 | 24 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 6 | 0.576 |  | PLEXCO | 0 | 1991 | UNDER GROUND OR UNDER WATER |  | JOYCE C. DAILEY | 4124975668 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-03-15 | NO | 0 |  | YES | NO DATA |  | THIRD PARTY CONTRACTOR DAMAGED MAINLINE WHILE INSTALLING TELEPHONE POLES.
2025-01-31 10:21 | NO | NO | 20000087 | 2000-04-27 | 22182 | WASHINGTON GAS LIGHT CO | GEORGIA AVE S OF EMORY LANE | OLNEY | MONTGOMERY | MD |  | 3 | NO | 1500 | 2000-03-30 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 |  | 20000331 | 18 | 26 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | STEEL |  | 12 | 0.25 | API5LX42 | LTV | 1994 | 1994 | OTHER |  | JAMES O BIELASKI | 2026246059 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20000089 | 2000-05-03 | 2364 | CINCINNATI GAS & ELECTRIC CO | 1278 MCGUFFEY LANE | BATAVIA | CLERMONT | OH | 4 5238 |  | Null | 511 | 2000-04-01 | 0 | 0 | 250000 | 168944.0595 | 407909.9307 | NO | 3 | 54 | 525231 | 20000406 | 50 | 60 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | RANDALL L SUTTLES | 5132873921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EXPLOSION STILL UNDER INVESTIGATION. INCIDENT STILL UNDER INVESTIGATION. VARIOUS FACTOS POSSIBLY CONTRIBUTED TO THE CAUSE OF THE RISER FAILURE AND INSPECTION TESTING AND REVIEW OF RECORDS AVAILABLE TO CG&E TO DATE FAIL TO DETERMINE THE SPECFIC CONTRIBUTING FACTOR(S)
2025-01-31 10:21 | NO | NO | 20000091 | 2000-05-05 | 11032 | LACLEDE GAS CO | 416 BOYCE STREET | FARMINGTON | ST FRANCOIS | MO | 6 3640 | 3 | NO | 1515 | 2000-03-25 | 0 | 0 | 20000 | 13515.5248 | 32632.7945 | NO | 2 | 55 |  | 20000327 | 24 | 30 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL B HUNKER JR | 3143420528 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | COATED | YES | 1971 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20000092 | 2000-05-08 | 22182 | WASHINGTON GAS LIGHT CO | 22007-22015 STONE PIER LANE | CLARKSBURG | MONTGOMERY | MD |  | 1 | Null | 1017 | 2000-04-08 | 0 | 0 | 370000 | 250037.2081 | 603706.6975 | NO | 0 | 19 | 525454 | 20000408 | 55 | 60 | BY CFR 192.619(A)(3) | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.095 | ASTM 2406 | PLEXCO | 0 | 2000 | UNDER GROUND OR UNDER WATER |  | ROMELIA L KEMP | 7037505564 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | MULTIPLE FACILITIES (METER, RISERS) EXPOSED IN CONSECUTIVE HOUSE FIRES. SERVICES WERE ABANDONED AT THE MAIN. CAUSE UNDETERMINED BY FIRE DEPARTMENT. GAS SECONDARY, PRIMARY CAUSE STILL UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 20000093 | 2000-05-09 | 18536 | SOUTHWEST GAS CORP | 15TH AVENUE AND FILLMORE | PHOENIX | MARICOPA | AZ | 8 5009 | 3 | Null | 1545 | 2000-03-04 | 0 | 0 | 0 | 0 | 0 | NO | 2 | 45 |  | 20000306 | 30 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 |  |  | 1948 | 1948 | UNDER PAVEMENT |  | PHILLIP S ANDREW | 6024845218 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-01-07 | YES | 3 | PAINT | YES | NO DATA |  | A CONTRACTOR WAS BORING ALONG 15TH AVENUE AND STRUCK A 6" STEEL DISTRIBUTION MAIN. THE MAIN WAS PROPERLY MARKED AND HAD BEEN POT HOLED BY THE BORING CONTRACTOR. THE DAMAGED CAUSED AN OUTAGE OF 1,250 ACCOUNTS. THIS OUTAGE CAUSED THE LOSS TO EXCEED $50,000, MAKING THE INCIDENT DOT REPORTABLE. THE NOTOFICATION TO DOT WAS MADE AS SOON AS INITIAL COST ESTIMATES WERE EXPECTED TO EXCEED $50,000.
2025-01-31 10:21 | YES | YES | 20000095 | 2000-05-22 | 31358 | TECO PEOPLES GAS LP OPERATIONS | WILEY DRIVE | ORLANDO | ORANGE | FL | 32827- | 1 | NO | 1157 | 2000-05-09 | 1 | 1 | 11711 | 7914.0155 | 19108.1328 | NO | 0 | 38 | 528600 | 20000510 | 125 | 125 | BY TEST | 200 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | API 5L |  | 1990 | 1990 | UNDER GROUND OR UNDER WATER |  | TIMOTHY J KASPRZYK | 8132284831 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-04-24 | NO | 0 |  | YES | NO DATA |  | 4 INCH MAIN CUT BY MIXER ON NEW ROAD PROJECT.
2025-01-31 10:21 | NO | NO | 20000096 | 2000-05-22 | 4483 | ENSTAR NATURAL GAS CO | NHN WYOMING DRIVE | WASILLA |  | AK | 99611- | 2 | NO | 1243 | 2000-05-13 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 1 | 37 | 528910 | 20000513 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1998 | 1998 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY AFTERNOON, MAY 13, 2000, AT APPROXIMATELY 12:43 PM AST, ENSTAR NATURAL GAS CO WAS NOTIFIED OF A FIRE AT TAX PARCEL C9, SECTION 26, ON WYOMING DRIVE ( NO HOUSE NUMBER) IN THE MATANUSKA SUSITNA BOROUGH. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A MOBILE HOME ON FIRE. HEAT FROM THE FIRE MELTED THE REGULATOR AND METER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED AT 2:20 PM AST THE CAUSE OF THE FIRE IS UNKNOWN HOWEVER, NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20000097 | 2000-05-08 | 2596 | COLUMBIA GAS OF OHIO INC | A1, A2, A3 & A4 COVENTRY DRIVE | CAMBRIDGE | GUERNSEY | OH | 43725- | 3 | NO | 1035 | 2000-04-13 | 0 | 1 | 200000 | 135155.2476 | 326327.9446 | NO | 1 | 15 |  | 20000413 | 40 | 60 | BY TEST | 106 | CORROSION | CORROSION | EXTERNAL | OTHER | CUSTOMER SERVICE LINE | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | API5L | UNKNOWN | 0 | 1970 | UNDER PAVEMENT |  | DAVID A MONTE | 6147669631 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20000098 | 2000-05-15 | 18484 | SOUTHERN CALIFORNIA GAS CO | MARQUARDT/ALONDRA | CERRITOS | ORANGE | CA |  | 3 | NO | 838 | 2000-04-14 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 8 | 27 | 526305 | 20000414 | 193 | 240 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 6 |  |  |  | 0 | 1948 | NO DATA |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | HIGH PRESSURE GAS MAIN HIT BY BORING MACHINE. STREET AND RAILROAD CLOSURE BY FIRE DEPARTMENT. CONTRACTOR DID NOT POT HOLE BEFORE BORING.
2025-01-31 10:21 | YES | YES | 20000099 | 2000-05-11 | 13710 | NORTHERN ILLINOIS GAS CO | 8220 SOUTH 83RD COURT | JUSTICE | COOK | IL |  | 3 | Null | 430 | 2000-04-21 | 0 | 2 | 150000 | 101366.4357 | 244745.9584 | NO | 0 | 0 | 526764 | 20000421 |  |  |  |  | NO DATA | ALL OTHER CAUSES | UNKNOWN | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | NO DATA |  | GEORGE WALDVOGEL | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20000100 | 2000-05-19 | 15359 | PEOPLES NATURAL GAS | 20214 VETERANS DR | ELK HORN | SARPY | NE | 68022- | 3 | NO | 1102 | 2000-04-12 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 34 |  | 20000412 | 25 | 25 | BY TEST | 25 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.102 |  | PLEXCO | 1995 | 1995 | UNDER PAVEMENT |  | KEVIN JAROSZ | 4025962174 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEWER CONTRACTOR WAS BLIND BORING AND HIT OUR GAS LINE. HE ALSO HIT THE SEWER LINE TO THE SAME ADDRESS.
2025-01-31 10:21 | NO | NO | 20000102 | 2000-05-30 | 12180 | MARSHALL COUNTY GAS DISTRICT | HWY 79 & DARRYL DRIVE | SCOTTSBORO | JACKSON | AL | 3 5768 | 3 | Null | 1528 | 2000-05-09 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 40 | 528603 | 20000510 | 70 | 100 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | OTHER | ALUMINUM | 8 | 0.75 |  | AMERICAN | 1974 | 1974 | ABOVE GROUND |  | RICHARD T LAWSON | 2565820324 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20000103 | 2000-05-31 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 4701 BEECHNUT | HOUSTON | HARRIS | TX | 7 7096 | 3 | Null | 1348 | 2000-04-28 | 0 | 0 | 40000 | 27031.0495 | 65265.5889 | NO | 6 | 52 |  | 20000428 | 40 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 8 | 0.188 | API5L | UNKNOWN | 0 | 1963 | UNDER GROUND OR UNDER WATER |  | JEFFERY A BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-04-20 | YES | 3 | 2000-04-20 | YES | NO DATA |  | THIRD PARTY USING A DRILLING AUGER DAMAGED A 8 I.P. STL. MAIN
2025-01-31 10:21 | YES | NO | 20000104 | 2000-06-02 | 15896 | PROVIDENCE GAS CO | 56 PEMBROKE LANE | COVENTRY | KENT | RI | 2816 | 3 | NO | 931 | 2000-05-18 | 0 | 0 | 250000 | 168944.0595 | 407909.9307 | NO | 0 | 30 | 529323 | 20000518 | 0 | 0 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | OUTLET PIPING | NO DATA |  | STEEL |  |  |  | UNKNOWN | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | MARIO CARLINO | 4012725040 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20000105 | 2000-06-05 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 3012 WOODROW AVE | RICHMOND |  | VA |  | 1 | NO | 1619 | 2000-05-08 | 0 | 1 | 200000 | 135155.2476 | 326327.9446 | NO | 2 | 41 | 528376 | 20000508 | 0.25 | 10 | BY TEST | 50 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE | JOINT |  | STEEL |  | 0.625 |  | BLACK IRON |  | 0 | 1982 | WITHIN/UNDER BUILDING |  | J C STAFFORD | 8046468350 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | LEAK SITE ON GAS SERVICE PIPE INSIDE HOUSE, DOWNSTREAM OF METER. BEYOND THE CONTROL OF THE GAS COMPANY
2025-01-31 10:21 | YES | NO | 20000108 | 2000-06-06 | 4547 | ESSEX COUNTY GAS CO | 81 HERRICK ROAD | BOXFORD | ESSEX | MA | 1921 | 2 | Null | 1205 | 2000-05-12 | 0 | 0 | 500000 | 337888.1191 | 815819.8614 | NO | 0 | 40 | 528835 | 20000512 | 90 | 100 | BY CFR 192.619(A)(3) | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 |  |  | AMERICAN | 0 | 1971 | WITHIN/UNDER BUILDING |  | MICHAEL SULLIVAN | 9789270846 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | YES | NO DATA |  | SEE PART D- OTHER BRIEF DESCRIPTION: (ON REVERSE SIDE)
2025-01-31 10:21 | YES | NO | 20000109 | 2000-06-06 | 4483 | ENSTAR NATURAL GAS CO | 7016 WEIMER ROAD | ANCHORAGE |  | AK | 9 9502 | 3 | Null | 1725 | 2000-06-06 | 0 | 0 | 1000000 | 675776.2381 | 1631639.7229 | NO | 1 | 3 | 531277 | 20000606 | 55 |  | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | M-8000 | DRISCOPIPE | 1993 | 1993 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20000110 | 2000-06-13 | 11720 | KEYSPAN ENERGY CORP | 27 PARKWAY DRIVE | ROSLYN HEIGHTS | NASSAU | NY | 1 1577 | 4 | Null | 1105 | 2000-05-07 | 6 | 0 | 0 | 0 | 0 | NO | 0 | 25 |  | 20000507 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | GAS APPLIANCE | OTHER | GAS APPLIANCES | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | DEBORAH PIELOCH | 5165452319 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D ON BACK OF THIS REPORT. ALSO SUPPLEMENTAL A & B*
2025-01-31 10:21 | YES | NO | 20000114 | 2000-06-14 | 1640 | BOSTON GAS CO | 503 POND STREET | BRAINTREE | NORFOLK | MA | 2184 | 2 | Null | 10 | 2000-05-15 | 0 | 0 | 250000 | 168944.0595 | 407909.9307 | NO | 0 | 45 | 529014 | 20000515 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1923 | UNDER GROUND OR UNDER WATER |  | JOHN C HIGGINS | 7817943501 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR STRUCK SERVICE TO HOME WITH A LARGE EXCAVATOR. SERVICE WAS PULLED AT POINT OF CONTACT, BUT NOT BROKEN. SERVICE BROKE INSIDE OF STRUCTURE, CAUSING STRUCTURE TO FILL WITH GAS. THIRD PART DID NOT NOTIFY DIG SAFE AS REQUIRED BY COMMONWEALTH OF MASSACHUSETTS REGULATION.
2025-01-31 10:21 | YES | NO | 20000115 | 2000-06-20 | 11720 | KEYSPAN ENERGY CORP | 25 BROADLAWN AVENUE | KINGS POINT | NASSAU | NY | 1 1024 | 4 | Null | 1334 | 2000-05-19 | 0 | 0 | 400000 | 270310.4953 | 652655.8891 | NO | 0 | 39 |  | 20000519 |  |  |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  |  |  |  | NO DATA | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DEBORAH PIELOCH | 5165452319 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | S.I. INDUSTRIES HIT 3/4 H.P. STEEL SERIVCE. THIS CAUSED HOUSE TO FILL UP WITH GAS AND EXPLODE. THEY WERE DIGGING TO MAKE AN EXTENSION FOR THE HOUSE. IT WAS MARKED OUT CORRECTLY CASE #1360017. ONE PERSON INJURIED BY FLYING DEBRIS AND TAKEN TO THE NORTH SHORE HOSP FOR MINOR INJURIES. GCM&S SHUT ONE VALVE TO MAKE SAFE CAUSING 5 HOUSES TO BE SHUT DOWN. REPAIR & RELITE COMPLETED BY 15:20.
2025-01-31 10:21 | NO | NO | 20000116 | 2000-06-26 | 18104 | SAN ANTONIO, CITY PUBLIC SERVICE BOARD OF | FM 1604 & BLANCO (FM 2696) | SAN ANTONIO | BEXAR | TX | 7 8258 | 3 | Null | 1316 | 2000-03-20 | 0 | 0 | 72183 | 48779.5562 | 117776.6501 | NO | 0 | 10 |  | 20000320 | 125 | 274 | BY TEST | 1080 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.25 | API 5L |  | 1997 | 1998 | UNDER GROUND OR UNDER WATER |  | ENEDELIA E STRAUGHAN | 2103534479 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | CONTRACTOR HIT SUPPLY LINE WITH ROCK SAW.
2025-01-31 10:21 | NO | NO | 20000119 | 2000-07-05 | 18484 | SOUTHERN CALIFORNIA GAS CO | 22 CORPORATE PLAZA DR | NEWPORT BEACH | ORANGE | CA |  | 3 | Null | 900 | 2000-05-17 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 58 | 529269 | 20000517 | 35 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 |  |  |  | 0 | 0 | NO DATA |  | JEFF KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-05-16 | NO | 0 |  | YES | NO DATA |  | PLUMBER WAS USING TORCH TO WORK ON WATER LINE AND CONTACTED EXPOSED PLASTIC MAIN, CAUSING LEAKAGE AND IGNITION. PLUMBER RECEIVED 1ST AND 2ND DEGREE BURNS.
2025-01-31 10:21 | NO | NO | 20000120 | 2000-07-05 | 22182 | WASHINGTON GAS LIGHT CO | 18TH STREET@FRANKLIN STREET NE | WASHINGTON |  | DC |  | 3 | NO | 848 | 2000-06-02 | 0 | 0 | 61600 | 41627.8163 | 100509.0069 | NO | 0 | 17 |  | 20000602 | 20 | 25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 20 | 0.68 | CLASS 150 |  | 1938 | 1938 | UNDER PAVEMENT |  | MARK |  | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-05-30 | YES | 3 | PAINT | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20000121 | 2000-07-06 | 21349 | VIRGINIA NATURAL GAS | 1820 DUKE OF YORK QUAY | VIRGINIA BEACH |  | VA | 2 3454 | 3 | Null | 1531 | 2000-05-30 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 4 | 530614 | 20000531 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.09 | PE2406 | PLEXCO | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | DONALD L WHITE | 7574665445 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | AN EMPLOYEE OF ANOTHER UTILITY COMPANY COX COMMUNICATIONS WAS PERFORMING WORK IN AN OPEN EXCAVATION WHERE THE GAS LINE WAS EXPOSED. THE WORKER WAS USING A PROPANE TORCH TO HEAT A CABLE REPAIR DEVICE AND ACCIDENTLY MELTED THE PLASTIC GAS SERVICE LINE, RUPTURING THE LINE AND IGNITING THE GAS. THE WORKER SUFFERED FIRST DEGREE BURNS.
2025-01-31 10:21 | NO | NO | 20000122 | 2000-07-07 | 18484 | SOUTHERN CALIFORNIA GAS CO | 300 N MISSION STREET | LOS ANGELES | LOS ANGELES | CA |  | 3 | Null | 1000 | 2000-06-07 | 0 | 0 | 0 | 0 | 0 | NO | 1 | 0 |  | 20000607 | 35 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JEFF KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | GAS COMPANY EMPLOYEE OVERCOME WHILE ATTEMPTING TO PUT CLAMP ON DAMAGED 3" PE MAIN. HOSPITALIZED FOR 3 DAYS. CURRENTLY RECOVERING AT HOME.
2025-01-31 10:21 | YES | YES | 20000123 | 2000-07-10 | 4475 | PENSACOLA, ENERGY SERVICES OF | 131 VALDOSTA AVE | PENSACOLA | ESCAMBIA | FL | 3 2507 | 4 | Null | 1130 | 2000-06-12 | 0 | 1 | 4000 | 2703.105 | 6526.5589 | NO | 0 | 45 | 531965 | 20000613 | 60 | 60 | BY TEST | 10 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | WELD | FUSION | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | 2406 SDR 10 | PLEXCO | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | DON J SUAREZ | 8504745316 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | THE OPERATOR WAS ATTEMPTING TO INSTALL A 5/8" SERVICE ONTO AN 1 1/4 MAIN. IT APPEARS THAT THE OPERATOR OVERHEATED THE FUSION ON THE SADDLE TO THE MAIN. THIS ACTION CAUSED THE FUSION TO FAIL, RELEASING NATURAL GAS IN THE ATMOSPHERE. STATIC ELECTRICITY THEN IGNITED THE ESCAPING NATURAL GAS.
2025-01-31 10:21 | NO | NO | 20000125 | 2000-07-17 | 22175 | DYNEGY MIDSTREAM SERVICES, L.P. | WEST CAMERON 72 |  |  | LA |  | 1 | NO | 1200 | 2000-06-16 | 0 | 0 | 0 | 0 | 0 | NO | 1 | 35 | 532354 | 20000616 | 1000 | 1235 | BY TEST | 1875 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | PURGE VALVE ASSEMBLY | NO DATA |  | STEEL |  | 2 | 0.218 | ANSI 900 | HACKNEY | 1996 | 1997 | UNDER GROUND OR UNDER WATER |  | ROB WALLER | 3377742995 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | UNKNOWN OUTSIDE FORCE
2025-01-31 10:21 | YES | NO | 20000133 | 2000-08-01 | 15007 | PACIFIC GAS & ELECTRIC CO | 2402 HURON DRIVE | SAN JOSE | SANTA CLARA | CA |  | 3 | Null | 1545 | 2000-07-04 | 0 | 0 | 76500 | 51696.8822 | 124820.4388 | NO | 2 | 35 |  | 20000710 | 55 | 60 |  | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1982 | ABOVE GROUND |  | SAHN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE STRUCK GAS METER SET LOCATED IN A METER CABINET RECESSED IN THE FRONT WALL OF THE BUILDING. LEAKING GAS CAUGHT FIRE. EXTENSIVE DAMAGE TO RESIDENCE, DUE TO FIRE.
2025-01-31 10:21 | NO | NO | 20000135 | 2000-08-04 | 7695 | HUTCHINSON UTILITIES COMMISSION | INTERSECTION DALE ST & SOUTH GRADE RD | HUTCHINSON | MCLEOD | MN | 5 5350 | 3 | NO | 1730 | 2000-07-14 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 15 |  | 20000714 | 25 | 25 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | STEEL |  | 4 | 0.237 | UNKNOWN | NORDSTROM | 1979 | 1979 | UNDER GROUND OR UNDER WATER |  | STEVE STURGES | 3205874746 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20000138 | 2000-08-11 | 13480 | NIAGARA MOHAWK POWER CORP | 1060 WTRY ROAD | NISKAYUNA | SCHENECTADY | NY |  | 3 | Null | 810 | 2000-06-12 | 0 | 0 | 450000 | 304099.3072 | 734237.8753 | NO | 3 | 35 |  | 20000612 | 22 | 22 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.09 | P3408 | PHILLIPS | 1980 | 1981 | OTHER | PAVEMENT SHOULDER | LAURIE T. BROWN | 3154604127 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-06-07 | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20000139 | 2000-08-16 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 336 W. CR 550 S. | BOONE GROVE | PORTER | IN | 4 6302 | 3 | Null | 1720 | 2000-07-07 | 0 | 0 | 60000 | 40546.5743 | 97898.3834 | NO | 2 | 40 | 534707 | 20000707 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | MAIN WAS HIT | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | DUPONT | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | DON J TOKOLY | 2196474770 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-06-16 | YES | 2 |  | NO | NO DATA |  | SEE ATTACHED
2025-01-31 10:21 | YES | YES | 20000141 | 2000-08-16 | 14210 | OKLAHOMA NATURAL GAS CO | 905 SENNYBRIDGE DRIVE | OKLAHOMA CITY | CANADIAN | OK |  | 3 | Null | 1615 | 2000-07-17 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 5 | 535699 | 20000717 | 50 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.409 | PE2306 |  | 0 | 1984 | UNDER GROUND OR UNDER WATER |  | JAMES R KUNKEL | 4055516810 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EMPLOYEE RECEIVED 2ND DEGREE BURNS WHEN GAS WAS IGNITED BY STATIC ELECTRICITY DURING PURGING OF PLASTIC PIPE FOLLOWING REPAIR OF A CUT LINE.
2025-01-31 10:21 | NO | NO | 20000142 | 2000-08-17 | 30769 | MISSOURI GAS ENERGY | 150 HIGHWAY EAST OF 291 HIGHWAY | LEE'S SUMMIT | JACKSON | MO | 6 4082 | 2 | Null | 1150 | 2000-07-03 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 4 | 5 | 534294 | 20000704 | 25 | 25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | UNKNOWN | CBOMANU | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | JIM GORMAN | 8164723431 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | PAINT | YES | NO DATA |  | RILEY CONSTRUCTION COMPANY WAS WORKING WITH A TRACK HOE LOWERING AN EXISTING FIBER OPTIC CABLE. THEY WERE EXCAVATING IN CLOSE PROXIMITY TO TWO OF OUR GAS LINES (8 INCH STEEL 55 POUND SYSTEM AND 4 INCH PLASTIC 25 POUND SYSTEM). THEY HAD LOCATES AND THE LOCATES WERE ACCURATE. OUR PIPELINES WERE TWELVE FEET DEEP AT THE POINT OF IMPACT. OUR INITIAL RESPONDERS THOUGHT THE 8 INCH STEEL LINE WAS HIT AND BLOWING BASED ON OBSERVATION AT THE JOB SITE. ACTIONS WERE TAKEN TO LOWER THE PRESSURE ON THE PIPELINE. THE CONTRACTOR WAS RELOCATING HIS TRACK HOE AND WHEN HE WENT TO PARK IT HE SWUNG HIS BOOM AROUND KNOCKING A POWER CABLE OFF AND ADJACENT POWER POLE CAUSING A SPARK THAT IGNITED THE GAS. THE FIRE EVENTUALLY BURNED THE CAB OF A TRACK HOE AND THE FIBER OPTIC CABLE THAT RILEY CONSTRUCTION COMPANY HAD BEEN HIRED TO LOWER. WE LOWERED THE PRESSURE ON THE 8 INCH MAIN TO ENABLE US TO EXTINGUISH THE FIRE AND MAKE REPAIRS. THE LOWERING THE PRESSURE WE REALIZED THE FIRE WAS NOT GETTING SMALLER AND TOOK CORRECTIVE ACTION ON THE 4 INCH PLASTIC LINE TO HELP LOWER THE PRESSURE TO EXTINGUISH THE FIRE. WE BUILT A BY PASS AROUND THE DAMAGED AREA TO KEEP GAS IN OUR SYSTEM AND ISOLATED THE DAMAGED LINE FOR THE EVENING.
2025-01-31 10:21 | YES | NO | 20000143 | 2000-08-14 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | 621 WRIGHT AVENUE | HUEYTOWN | JEFFERSON | AL | 3 5023 | 3 | Null | 410 | 2000-08-03 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 4 | 20 | 537577 | 20000803 | 30 | 50 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | LEE PETERS | 2053268186 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE CAUSE OF THE INCIDENT HAS NOT BEEN DETERMINED. A POST-INCIDENT INVESTIGATION REVEALED A LEAK IN THE 2 1/4 CAST IRON MAIN LOCATED 45 FEET FROM THE HOUSE. THE WALL THICKNESS OF THE UNDERGROUND MAIN IS .25 INCHES. ALABAMA GAS CORPORATION HOPES TO DETERMINE WITH FURTHER INVESTIGATION WHETHER THE LEAK IN THE MAIN LEAD TO GAS ESCAPING AND MIGRATING INTO THE HOUSE TO CAUSE THE EXPLOSION, OR WHETHER THE EXPLOSION, CAUSED BY ANOTHER SOURCE, CREATED THE LEAK IN THE MAIN.
2025-01-31 10:21 | NO | NO | 20000147 | 2000-08-19 | 4483 | ENSTAR NATURAL GAS CO | 54 BARRA LOOP | WASILLA |  | AK | 9 9654 | 2 | Null | 216 | 2000-08-15 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 55 | 538623 | 20000814 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | m-8000 | DRISCOPIPE | 1991 | 1991 | ABOVE GROUND |  | DAVID W BREDIN |  | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE ATTACHED SHEET
2025-01-31 10:21 | NO | NO | 20000148 | 2000-08-22 | 11320 | LAWRENCEVILLE, CITY OF | 1573 NEW HOPE ROAD | LAWRENCEVILLE | GWINNETT | GA | 3 0046 | 2 | Null | 1520 | 2000-07-27 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 1 | 0 | 536814 | 20000727 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.11 | PE2406 | DRISCOPIPE | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | AL HARTLEY | 7709633332 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-07-12 | YES | 0 |  | YES | NO DATA |  | DEVELOPER WAS CUTTING A ROAD INTO A SMALL SUBDIVISION. THE ROAD WAS FOLLOWING AN EXISTING DRIVEWAY WHICH HAD A 2" PE GAS SERVICE RUNNING ALONG THE EDGE. THE LINE HAD BEEN LOCATED AND SPOTTED BY POT HOLES. THE MOTOR GRADER OPERATOR GOT TO CLOSE THE LINE. GAS IGNITED UNDER THE MOTOR GRADER. THE UNIT BURNT, IT WAS A COMPLETE LOSS.
2025-01-31 10:21 | YES | NO | 20000149 | 2000-08-22 | 2596 | COLUMBIA GAS OF OHIO INC | COLUMBIA GAS POD MS #709587 RS#200 | CARROLLTON | CARROLL | OH | 44615- | 4 | Null | 217 | 2000-07-30 | 0 | 0 | 150000 | 101366.4357 | 244745.9584 | NO | 1 | 27 | 537032 | 20000730 | 37 | 47 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | TOWN BORDER STATION | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API5L |  | 0 | 1962 | WITHIN/UNDER BUILDING |  | J.M. YOUNG | 4408912452 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | AT APPROXIMATELY 0217 SUNDAY JULY 30, 2000 DAVE L. WORKMAN, AGE 33, 2143 ARROW RAOD, CARROLLTON, OH 44615 WAS SOUTHBOUND ON SR 43 AT THE SOUTH CARROLLTON VILLAGE CORPORATION LIMIT IN A 1989 FORD AREOSTAR. THE DRIVER LOST CONTROL ON A CURVE TO THE LEFT GOING OFF THE RIGHT SIDE OF THE ROADWAY STRIKING A NATURAL GAS METERING STATION.
2025-01-31 10:21 | YES | YES | 20000150 | 2000-08-24 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 1900 REDD STREET | RICHMOND |  | VA |  | 1 | Null | 1730 | 2000-07-21 | 0 | 1 | 0 | 0 | 0 | NO | 119 | 30 | 536180 | 20000721 | 20 | 120 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | JOINT |  | CAST IRON |  | 8 |  | C.I. HUB | CBOMANU | 0 | 1947 | UNDER GROUND OR UNDER WATER |  | J.C. STAFFORD | 8046468350 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | OLD 6" CAST IRON JOINT LEAKED OVER TIME FROM AGAING AND SOIL SUBSIDENCE.
2025-01-31 10:21 | NO | NO | 20000153 | 2000-08-28 | 30750 | MIDAMERICAN ENERGY COMPANY |  | WINTERSET | MADISON | IA | 5 0273 | 1 | Null | 2445 | 2000-08-02 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 0 | 537334 | 20000802 | 200 | 200 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | ROGER LORENZEN | 7122777678 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20000154 | 2000-09-01 | 30769 | MISSOURI GAS ENERGY | 205 E. OAK | WARRENSBURG | JOHNSON | MO | 6 4093 | 3 | NO | 1430 | 2000-07-24 | 0 | 1 | 40000 | 27031.0495 | 65265.5889 | NO | 1 | 30 |  | 20000724 | 17 | 17 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | 3408 | DRISCO | 1992 | 1992 | UNDER PAVEMENT |  | JIM GORMAN | 8164723431 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-07-12 | NO | 0 |  | YES | NO DATA |  | CONSTRUCTION COMPANY DID BORING WORK PRIOR TO LINES BEING LOCATED. THEY HIT OUR GAS LINE AND A SEWER LINE ALLOWING GAS TO ENTER HOME THRU SEWER PIPE.
2025-01-31 10:21 | YES | NO | 20000155 | 2000-09-01 | 6720 | GREELEY GAS CO | 100 E PARK ST. | OLATHE | JOHNSON | KS | 6 6061 | 3 | NO | 1039 | 2000-08-01 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 0 | 21 | 537342 | 20000802 | 55 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REGULATOR | REGULATOR/METER |  | OTHER | ALUMINUM | 2 |  |  | FISHER | 1984 | 1986 | ABOVE GROUND |  | GARY W GREGORY | 3038315680 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | UNKNOWN VEHICLE STRUCK REGULATOR. CAUSING RELEASE OF HIGH PRESSURE GAS INTO BUILDING. THE GAS IGNITED AND CAUSED A SMALL FIRE. MOST DAMAGED WAS CAUSED BY FIRE DEPT. AND SPRINKLER SYSTEM.
2025-01-31 10:21 | YES | YES | 20000156 | 2000-09-07 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 5720 WEDGEWOOD | CANTON | WAYNE | MI | 4 8187 | 3 | NO | 715 | 2000-08-07 | 0 | 2 | 300000 | 202732.8714 | 489491.9169 | NO | 0 | 0 | 537863 | 20000807 | 0.25 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | OTHER | UNKNOWN | STEEL |  | 0.5 |  |  | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS P FUNTSCH | 3135777026 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | DUE TO HOSPITALIZATION OF 2 PERSONS AND EXTENSIVE NEWS COVERAGE, THE INCIDENT WAS TELEPHONICALLY REPORTED.
2025-01-31 10:21 | YES | YES | 20000157 | 2000-09-07 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 17711 SUMNER | REDFORD | WAYNE | MI | 4 8240 | 3 | NO | 716 | 2000-08-08 | 2 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 0 | 41 | 537999 | 20000808 | 0.25 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINE | OTHER | FLEX CONNECTOR | OTHER | FUEL LINE |  |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LARRY K CROWDER | 3135777024 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | DUE TO TWO FATALITIES AND EXTENSIVE MEDIA COVERAGE, THE INCIDENT WAS TELEPHONICALLY REPORTED.
2025-01-31 10:21 | YES | YES | 20000158 | 2000-09-14 | 30769 | MISSOURI GAS ENERGY | 1426 W 50 TERRACE | KANSAS CITY | JACKSON | MO | 64112- | 3 | NO | 1625 | 2000-08-08 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 30 | 538078 | 20000808 | 1 | 2 | BY CFR 192.619(A)(3) |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.14 | API 5L | UNKNOWN | 0 | 1959 | OTHER | OPEN EXCAVATION | JIM GORMAN, SUPERINTENDENT | 8164723431 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | WHILE IN THE PROCESS OF CONDUCTING A SERVICE REPLACEMENT, CONTRACTOR WAS PREPARING ACTIVE SERVICE FOR RETIREMENT WHEN A SUDDEN RELEASE OF GAS OCCURRED RESULTING IN IMMEDIATE IGNITION WHICH CAUSED INJURIES TO TWO CONTRACT EMPLOYEES.
2025-01-31 10:21 | YES | NO | 20000159 | 2000-09-15 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | GLENBURY & TRANSPORT STREETS | PITTSBURGH | ALLEGHENY | PA | 1 5234 | 3 | NO | 1045 | 2000-07-06 | 0 | 0 | 96000 | 64874.5189 | 156637.4134 | NO | 1 | 50 | 540204 | 20000828 | 65 | 80 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.25 |  |  | 0 | 1955 | UNDER GROUND OR UNDER WATER |  | ROBERT P JOHNSON | 4125724450 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-04-17 | YES | 3 | 2000-04-17 | YES | NO DATA |  | THE RELEASE OF GAS WAS CAUSED BY A THIRD PARTY CONTRACTOR, ELLES BROTHERS, OPERATING A DRILLING RIG, WHILE CONSTRUCTING A RETAINING WALL NEAR COLUMBIA FACILITIES AT THE INTERSECTION OF TRANSPORT AND GLENBURY STREETS, PITTSBURGH, PENNSYLVANIA.
2025-01-31 10:21 | YES | YES | 20000163 | 2000-09-11 | 2304 | CHILDERSBURG GAS BOARD | 35601 US HIGHWAY 280 | SYLACAUGA | TALLADEGA | AL | 35150- | 2 | NO | 930 | 2000-08-16 | 1 | 0 | 500 | 337.8881 | 815.8199 | NO | 1 | 0 |  | 20000817 | 18 | 25 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | MICHAEL S MADDOX | 2563786064 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A 4 INCH DIAMETER CAST IRON GAS MAIN WAS IGNITED BY TWO INDIVIDUALS ON THE RIGHT OF WAY OF US HWY 280. A DETAILED REPORT IS ATTACHED.
2025-01-31 10:21 | NO | NO | 20000164 | 2000-09-14 | 12878 | MOUNTAINEER GAS CO | 205 PENDLETON STREET | BETHANY | OHIO | WV | 26032- | 3 | NO | 1302 | 2000-08-11 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 1 | 18 | 558427 | 20000811 | 40 | 40 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1.25 | 0.136 |  |  | 0 | 0 | UNDER PAVEMENT |  | MARY ANN RAPPOLD, ADMIN ASST | 3043470564 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20000167 | 2000-09-18 | 11800 | LOUISIANA GAS SERVICE CO | 4501 TAFT PARK | METAIRIE | JEFFERSON | LA | 70005- | 4 | NO | 1912 | 2000-09-01 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 0 | 19 | 540786 | 20000901 |  | 100 | BY TEST | 125 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | OTHER |  | STEEL |  | 1 | 0.113 | SCHEDULE 40 |  | 0 | 1971 | WITHIN/UNDER BUILDING |  | ANTHONY BROWN | 5048494363 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | MOST PROBABLE SCENARIO FOR EXPLOSION EVENT- INTERIOR HOUSE PIPING CONNECTION WAS UNCAPPED LEADING TO AN UNDETERMINED AMOUNT OF NATURAL GAS WITHIN AN UNATTACHED POOL CABANA BUILDING NEXT TO THE MAIN PROPERTY. THE ESCAPING NATURAL GAS ON THE INTERIOR OF THE POOL CABANA BUILDING ENCOUNTERED AN UNDETERMINED IGNITION SOURCE, WHICH TOUCHED OFF THE EXPLOSION. GAS HAD BEEN TURNED ON APPROXIMATELY 4 HOURS PRIOR TO THE EXPLOSION.
2025-01-31 10:21 | YES | YES | 20000168 | 2000-09-21 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 5811 LYNDHURST | HOUSTON | HARRIS | TX | 77033- | 3 | NO | 840 | 2000-08-01 | 0 | 2 | 0 | 0 | 0 | NO | 2 | 27 | 537310 | 20000801 | 42 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 1 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JEFFREY A BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT THIS TIME IT IS BELIEVED THAT GAS FROM BELOW GROUND RISER LEAK ENTERED THE RESIDENCE @ 5811 LYDNHURST & WAS IGNITED BY SPARK CAUSING EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | YES | 20000169 | 2000-09-21 | 31348 | TXU GAS DISTRIBUTION | 1610 CHALK HILL | DALLAS | DALLAS | TX | 75212- | 3 | NO | 1000 | 2000-08-02 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 12 | 537379 | 20000802 | 315 | 364 | BY TEST | 546 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CAST ALUMINUM |  |  |  |  | 0 | 0 | ABOVE GROUND |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | OTHER | OPERATING ERROR | A METER WAS OVER PRESSURED WHILE BEING PLACED BACK IN SERVICE. THE METER CAME APART AND A PARK OF THE METER STRUCK THE TECHNICIAN IN THE SIDE.
2025-01-31 10:21 | YES | NO | 20000170 | 2000-09-21 | 15007 | PACIFIC GAS & ELECTRIC CO | 5140 BUENA VISTA AVE | FAIR OAKS | SACRAMENTO | CA | 9 5628 | 3 | NO | 1236 | 2000-08-11 | 0 | 0 | 205000 | 138534.1288 | 334486.1432 | NO | 1 | 10 | 538413 | 20000811 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | UPNOR | 2000 | 2000 | UNDER GROUND OR UNDER WATER |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20000174 | 2000-09-25 | 7040 | HAMILTON GAS DEPT, CITY OF | 626 CLEVELAND AVE | HAMILTON | BUTLER | OH | 4 5013 | 1 | NO | 2324 | 2000-08-17 | 0 | 0 | 60000 | 40546.5743 | 97898.3834 | NO | 0 | 40 |  | 20000818 | 469 | 1 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | METER CONNECTIONS | NO DATA |  | 1 |  |  | CENTRAL (UNCONFIRMED) | 1994 | 1994 | WITHIN/UNDER BUILDING |  | CHARLES H GAYNOR | 5138685901 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SUSPICIOUS ORIGIN NOT RELATED TO CIVIL DISTURBANCE (IGNITION FACTOR 21). CIRCUMSTANCES OF EXPLOSION UNDER INVESTIGATION BY FIRE INVESTIGATOR. METER TAKEN FOR EVIDENCE.
2025-01-31 10:21 | NO | NO | 20000175 | 2000-09-06 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | KINDER AVE REGULATOR STATION #3438 | FALLOWFIELD | WASHINGTON | PA |  | 4 | NO | 1945 | 2000-08-16 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 3 | 42 | 539004 | 20000817 | 55 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 12 | 0.375 |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | ROBERT P JOHNSON, MANAGER QUALITY ASSURANCE | 4125724450 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-08-02 | YES | 3 | 2000-08-02 | YES | NO DATA |  | THE RELEASE OF NATURAL GAS APPEARS TO HAVE BEEN CAUSED BY ADDITIONAL EXTERNAL LOADING OVER A BURIED 12" STEEL GAS PIPELINE LOCATED WITHIN COLUMBIAS RIGHT OF WAY. COLUMBIA BELIEVES THIS LOADING CAUSED THE PIPELINE COUPLING FAILURE AND RELEASE OF GAS. REFER TO THE ATTACHED LETTER.
2025-01-31 10:21 | YES | NO | 20000176 | 2000-09-29 | 22182 | WASHINGTON GAS LIGHT CO | 20888 COSWORTH TERRACE & 46185 WALPOLE T | STERLING | LOUDOUN | VA | 2 0184 | 2 | NO | 140 | 2000-08-25 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 1 | 30 | 539903 | 20000825 | 19 | 25 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | NO DATA |  | STEEL | [5 empty] | 0 | 2000 | ABOVE GROUND |  | JERRY F KIDWELL | 7037507687 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THESE TWO BUILDINGS WERE UNDER CONSTRUCTION AT THE TIME OF THE FIRE. THE GAS METERS HAD NOT YET BEEN INSTALLED. DURING THE FIRE, DEBRIS FROM THE BURNING BUILDINGS FELL ON TOP OF ONE OF THE RISERS, DAMAGING THE STOPCOCK ON THE RISER AND ALLOWING SOME GAS TO ESCAPE.
2025-01-31 10:21 | YES | NO | 20000177 | 2000-10-03 | 18536 | SOUTHWEST GAS CORP | HEATHER AVE & RECKER ROAD | GILBERT | MARICOPA | AZ | 85234- | 3 | NO | 1346 | 2000-09-05 | 0 | 0 | 105498 | 71293.0416 | 172134.7275 | NO | 1 | 4 | 541136 | 20000905 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTM D2513 | PHILLIPS | 1995 | 1995 | UNDER PAVEMENT |  | PHILLIP S ANDREW | 6024845218 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-08-24 | YES | 0 |  | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20000179 | 2000-10-10 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 61 S EUCLID AVE | PITTSBURGH | ALLEGHENY | PA |  | 4 | NO | 1730 | 2000-09-16 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 1 | 542438 | 20000918 |  |  | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC | [5 empty] | 0 | 0 | OTHER | IN EXCAVATION | ROBERT P JOHNSON, MANAGER QUALITY ASSURANCE | 4125724450 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE EMPLOYEE ENTERED THE EXCAVATION WITH A SHOVEL TO CLEAR ADDITIONAL MATERIAL FROM THE EXCAVATION. NO INDICATION/ODOR OF GAS AT THAT TIME, HOWEVER, UPON ENTRY, A FLASH FIRE OCCURRED, AND THE EMPLOYEE IMMEDIATELY EXITED THE EXCAVATION, WHILE ANOTHER EMPLOYEE EXTINGUISHED THE FIRE. IN ADDITION TO AN OXYGEN MONITOR, THE EMPLOYEE WAS EQUIPPED WITH TWO WIRELESS PHONES. IT IS UNDETERMINED WHAT CAUSED THE ACCIDENTAL IGNITION.
2025-01-31 10:21 | YES | YES | 20000182 | 2000-10-19 | 12816 | MOSS POINT MUNICIPAL GAS SYSTEM, CITY OF | 4125 LEROY STREET | MOSS POINT | JACKSON | MS | 39563- | 2 | NO | 2119 | 2000-08-24 | 1 | 5 | 90000 | 60819.8614 | 146847.5751 | NO | 0 | 10 | 539882 | 20000825 | 13 | 38 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION |  |  |  |  | 0 | 0 | OTHER | UNDER INVESTIGATION | DAVID CHERAMIE, ASSISTANT SUPT | 2284751151 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | UNDETERMINED AT THIS TIME STILL UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 20000183 | 2000-10-20 | 18532 | SOUTHERN UNION GAS CO | 4690 BOCA CHICA BLVD | BROWNSVILLE | CAMERON | TX | 7 8521 | 3 | NO | 130 | 2000-09-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 40 | 542299 | 20000916 | 40 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | GRADE B A106 | UNKNOWN | 0 | 1984 | ABOVE GROUND |  | JESSE C WALLIS | 5123708212 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | A CAR, TRAVELING AT A HIGH RATE OF SPEED, STRUCK A VAN CAUSING THE DRIVER OF THE CAR TO LOSE CONTROL RESULTING IN CAR LEAVING THE ROADWAY. THE CAR THEN STRUCK NUMEROUS OBSTICLES INCLUDING A RESIDENTIAL GAS METER SET. THE GAS RISER TO THE METER SET WAS DAMAGED RESULTING IN LEAKAGE WHICH IGNITED. THE DRIVER OF THE CAR DIED OF INJURIES SUFFERED IN THE ACCIDENT.
2025-01-31 10:21 | NO | NO | 20000185 | 2000-10-24 | 4483 | ENSTAR NATURAL GAS CO | 3751 W 74TH AVE | ANCHORAGE |  | AK | 99502- | 3 | NO | 320 | 2000-10-14 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 2 | 15 | 545159 | 20001014 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1979 | 1979 | ABOVE GROUND |  | DAVID W BREDIN, DIRECTOR OF OPERATIONS | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SUNDAY MORNING, OCTOBER 14, 2000, AT APPROXIMATELY 3:20 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A MOBILE HOME FIRE AT 3751 W 74TH AVE ANCHORAGE, AK. AN ENSTAR SERVICEMAN AND DISTRIBUTION CREW WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A MOBILE HOME ON FIRE. HEAT FROM THE FIRE MELTED THE REGULATOR, METER AND HDPE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED AT 5:35 AM AST. THE CAUSE OF THE FIRE IS OF SUSPICIOUS ORIGIN AND IS BEING INVESTIGATED BY THE ANCHORAGE FIRE DEPARTMENT. HOWEVER, NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20000186 | 2000-10-24 | 12180 | MARSHALL COUNTY GAS DISTRICT | INTERSECTION OF ALABAMA HWY 205 & JEFFRE | ALBERTVILLE | MARSHALL | AL | 3 5950 | 3 | NO | 1745 | 2000-09-28 | 1 | 0 | 0 | 0 | 0 | NO | 0 | 0 | 543673 | 20000929 | 18 | 22 | BY TEST | 33 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 |  |  | 1973 | 1973 | UNDER GROUND OR UNDER WATER |  | RICHARD T LAWSON | 2565820324 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20000187 | 2000-10-18 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | TIERCE PATTON ROAD |  | TUSCALOOSA | AL | 3 5475 | 3 | NO | 900 | 2000-10-02 | 0 | 1 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 35 | 543939 | 20001002 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | PE 2406 | PHILLIPS DRISCO PIPE | 1993 | 1993 | UNDER GROUND OR UNDER WATER |  | TOM JOHNSTONE | 2053262990 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES | NO DATA |  | D&L CONSTRUCTION COMPANY, INCS BACKHOE OPERATOR EXCAVATED INTO ALABAMA GAS CORPS 4" PLASTIC MAIN WHILE WORKING TO INSTALL TELECOMMUNICATIONS CABLE. PIPELINE HAD BEEN ACCURATELY LOCATED AND MARKED BY AGCS THIRD PARTY LOCATING COMPANY
2025-01-31 10:21 | NO | NO | 20000188 | 2000-10-23 | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8890 LA CARTERA | SAN DIEGO |  | CA | 9 2129 | 3 | NO | 1505 | 2000-09-13 | 0 | 0 | 51500 | 34802.4763 | 84029.4457 | NO | 1 | 20 | 542057 | 20000913 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | ASTM A53 | UNKNOWN | 1986 | 1986 | ABOVE GROUND |  | ROGER W SPRENGER | 8585472023 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | TRUCK (WITHOUT DRIVER) ROLLED DOWN THE STREET INTO AN ATTACHED GARAGE AND CONNECTED GAS METER SET ASSEMBLY. THE GAS SERVICE LINE WAS BROKEN AT THE NIPPLE BETWEEN THE SHUT OFF VALVE AND THE REGULATOR. A FIRE OCCURRED RESULTING IN DAMAGE TO THE TRUCK AND THE STRUCTURE.
2025-01-31 10:21 | NO | NO | 20000189 | 2000-10-27 | 30750 | MIDAMERICAN ENERGY COMPANY | 525 W CHARISH | TEA | LINCOLN | SD | 57064- | 4 | NO | 1120 | 2000-10-04 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 55 | 544178 | 20001004 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | PLEXCO | 1992 | 1992 | UNDER GROUND OR UNDER WATER |  | ROGER LORENZEN, GAS STANDARDS | 7122777678 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-09-28 | YES | 2 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20000190 | 2000-10-27 | 4060 | EAST OHIO GAS CO | 525 BRISTOL LANE | AURORA | PORTAGE | OH |  | 3 | NO | 1040 | 2000-09-29 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 40 | 543702 | 20000929 | 50 | 60 | BY TEST |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | OTHER | PIPE CUT BY PLUMBER | POLYETHYLENE PLASTIC |  | 1.125 | 0.121 | PE3408 | PHILLIPS DRISCO PIPE | 1997 | 1999 | OTHER | IN SERVICE LINE DITCH | CLARENCE W MOORE, MANAGER | 2167366835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | OTHER | PLUMBER CUT THROUGH LIVE SERVICE LINE | METER MANIFOLD WAS RELOCATED BECAUSE OF CONSTRUCTION MODIFICATION TO FRONT OF HOUSE. SERVICE LINE HAD GAS IN IT AND WAS STUBBED OFF WITH PERMASET FITTING. PLUMBER THEN CUT THROUGH SERVICE LINE WITHOUT CHECKING FOR GAS. GAS LEAKED OUT AND WAS IGNITED BY SPARK CAUSING A FIRE WHICH ENGULFED HOUSE. PLUMBER GOT OUT OF DITCH WITHOUT INJURY.
2025-01-31 10:21 | YES | YES | 20000193 | 2000-10-30 | 13170 | NAVASOTA, CITY OF | SW CORNER OF FM 379 & INTERSTATE DR | NAVASOTA | GRIMES | TX | 7 7868 | 3 | NO | 1730 | 2000-08-16 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 10 |  | 20000817 | 53 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | JOINT |  | STEEL |  | 0.002 | 0.216 | PE 2406 | UPONOR | 1999 | 2000 | UNDER GROUND OR UNDER WATER |  | BILL ZDUNKAWICZ | 9368256450 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | ON OR ABOUT 17:30 HOURS ON AUGUST 16, 2000, AN INCIDENT INVOLVING THE RELEASE AND SUBSEQUENT IGNITION OF NATURAL GAS OCCURRED AT THE SOUTHWEST CORNER OF INTERSTATE DRIVE AND STATE HIGHWAY 379 WHICH IS IMMEDIATELY SOUTH OF NAVASOTA, TEXAS. TWO CONTRACT WORKERS HAD COMPLETED THE JOINING OF A 2" SECTION OF POLYETHYLENE PIPE (PE 2406, UPONOR) WITH A 2" COATED STEEL MAIN USING A 2" STYLE 90 DRESSER COUPLING AND FITTINGS. THE POLYETHYLENE PIPE HAD BEEN INSERTED WITH AN INTERNAL STEEL STIFFENER. THE JOINT HAD BEEN PRESSURE TESTED AND CONTRACT EMPLOYEES, MR. BOBBY ENGLEDOW OF TEX-CON AND MR. MARIO ESTRADA OF ELLIOTT CONSTRUCTION, WERE RE-COATING THE REPRESSURIZED STEEL PIPE WHEN THE STEEL LINE SEPARATED FROM THE COUPLING. UPON RELEASE OF NATURAL GAS, BOTH INDIVDUALS ESCAPED THE AREA WITHOUT INJURY. MR. GREER WAS STANDING OVER THE EXCAVATION AND RECEIVED BURNS TO THE FACE AND HANDS UPON IGNITION OF NATURAL GAS. FIELD PERSONNEL EXTINGUISHED THE FIRE AFTER APPROXIMATELY ONE MINUTE BY CLOSING APPROPRIATE VALVES AT THE SITE. MR. GREER WAS TRANSPORTED TO GRIMES COUNTY ST JOSEPHS HOSPITAL WHERE HE WAS ADMITTED AND TREATED FOR SEVERAL DAYS AND SUBSEQUENTLY RELEASED FOR OUT-PATIENT CARE. THE SCENE WAS MADE SAFE AND SECURED PENDING THE ARRIVAL OF THE TEXAS RAILROAD COMMISSION. THE AGENCIES WERE NOTIFIED AND A PROBABLE CAUSE INVESTIGATION WAS CONDUCTED. THE PROBABLE CAUSE FINDINGS INDICATE THAT THERE WAS INADEQUATE ANCHORING OF THE STEEL PIPE BY THE DRESSER COUPLING UNDER THE CONDITIONS THAT EXISTED AT THE TIME OF THE INCIDENT. THE SEPARATION OF THE STEEL PIPE FROM THE COUPLING RESULTED IN THE RELEASE OF NATURAL GAS.
2025-01-31 10:21 | YES | YES | 20000194 | 2000-10-30 | 18104 | SAN ANTONIO, CITY PUBLIC SERVICE BOARD OF | 7506 MONTE CRISTO | SAN ANTONIO | BEXAR | TX | 7 8239 | 3 | NO | 215 | 2000-09-11 | 0 | 1 | 0 | 0 | 0 | NO | 7 | 15 |  | 20000912 | 9 | 33 | BY TEST | 50 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | WELD |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | DRISCOPIPE 8100 | PHILLIPS | 0 | 1979 | UNDER GROUND OR UNDER WATER |  | ENEDELIA E STRAUGHAN | 2103534479 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | OTHER |  | WHILE CPS PERSONNEL WERE MAKING REPAIRS TO A 2" PLASTIC SERVICE, EMPLOYEE APPARENTLY STRUCK FLINT ROCK WITH A SHOVEL, RESULTING IN AN IGNITION. THE CPS EMPLOYEE RECEIVED 2ND DEGREE BURNS TO HIS FOREARM AND WAS TRANSPORTED TO UNIVERSITY HOSPITAL.
2025-01-31 10:21 | YES | YES | 20000195 | 2000-10-30 | 15007 | PACIFIC GAS & ELECTRIC CO | NORTH PALM ST & FOURTH (OLD NAME GADDY) | DELHI | MERCED | CA | 95315 | 2 | NO | 1145 | 2000-09-25 | 0 | 1 | 45000 | 30409.9307 | 73423.7875 | NO | 3 | 10 | 543247 | 20000925 | 48 | 60 | BY TEST | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | UPONOR | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-09-08 | YES | 3 | 2000-09-08 | YES | NO DATA |  | CONTRACTOR, HENNING BROTHERS, WAS DRILLING FOR A STREETLIGHT POLE BASE AND STRUCK A 2-IN PLASTIC GAS MAIN. GAS ESCAPED IGNITED, CAUSING FIRST AND SECOND DEGREE BURNS TO THE EQUIPMENT OPERATOR, AND SERIOUSLY DAMAGING THE DRILLING RIG. THE INJURED OPERATOR WAS ADMITTED TO A LOCAL HOSPITAL AND LATER TRANSFERRED TO THE UC DAVIS BURN UNIT AS A PRECAUTION (FULL RECOVERY EXPECTED). FIRE DEPARTMENT, SHERIFF, COUNTY HEALTH, AMBULANCE WAS ON SCENE, AREA BLOCKED OFF, AND TRAFFIC REROUTED. TWO CUSTOMERS IMPACTED. MAIN SHUTDOWN AT 1455 HOURS, AND REPAIRS COMPLETED AT 2130 HOURS.
2025-01-31 10:21 | NO | NO | 20000196 | 2000-11-06 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 1260 E 36TH STREET | ERIE | ERIE | PA | 16504- | 3 | NO | 2046 | 2000-10-09 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 12 | 544671 | 20001009 | 0.25 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER HOUSELINE | OTHER | OPEN GAS LINE TO DRYER | OTHER | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | CONRAD L DONELSON, SUPERINTENDENT | 8148718341 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THIS WAS A NON-REPORTABLE INCIDENT. FAILURE WAS ON CUSTOMER HOUSELINE.
2025-01-31 10:21 | YES | NO | 20000197 | 2000-11-03 | 20110 | UNION LIGHT HEAT & POWER CO | R/W OFF 1800 BLK MONMOUTH-SHOPPING CENTE | NEWPORT | CAMPBELL | KY | 41071- | 4 | NO | 237 | 2000-10-06 | 0 | 0 | 5000000 | 3378881.1907 | 8158198.6143 | NO | 0 | 0 | 544275 | 20001006 | 0.25 | 1 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | NO DATA |  | 8 | 0.277 |  | NATIONAL TUBE | 1955 | 1955 | UNDER PAVEMENT |  | SUSAN M GILB | 5132872752 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | WATER ENTERED A 8" COATED STEEL GAS MAIN AND TRAVELED THROUGHOUT THE GAS SYSTEM.
2025-01-31 10:21 | YES | NO | 20000198 | 2000-11-07 | 8070 | INDIANA GAS CO INC | 2520 LINCOLN DRIVE | CLARKSVILLE | CLARK | IN | 47130- | 3 | NO | 645 | 2000-10-12 | 0 | 0 | 161700 | 109273.0177 | 263836.1432 | NO | 1 | 35 |  | 20001012 | 335 | 425 | BY TEST | 650 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | OTHER | INSULATOR | STEEL |  | 6 | 0.28 | SCHEDULE 40 | KEROTEST | 1981 | 1981 | ABOVE GROUND |  | RICK SLAGLE, MANAGER SYSTEM STANDARDS | 3173210518 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CAUSE OF INCIDENT APPEARS TO BE A GROUND FAULT PROBLEM WITH ELECTRIC WIRES OVERHEAD. THIS APPARENTLY CAUSED AN ELECTRIC SURGE TO GROUND TO THE PIPELINE WHICH IN TURN CAUSED FAILURE OF AN INSULATOR ALLOWING 335 PSIG TO ESCAPE TO ATMOSPHERE. IGNITION SOURCE BELIEVED TO BE ELECTRICAL.
2025-01-31 10:21 | NO | NO | 20000199 | 2000-11-09 | 7485 | LAS VEGAS, CITY OF, HOUSING AUTH OF | 2002 HOT SPRINGS | LAS VEGAS |  | NM | 87701- |  | Null | 0 | 2000-09-06 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 0 | [6 empty] | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER PLASTIC |  | 1 |  |  |  | 0 | 0 | OTHER | IN EXCAVATED TRENCH | RICHARD TRUJILLO | 5054540265 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | 1" PVC SERVICE LINE MELTED AND RUPTURED, CAUSED BY STREET PERSONNEL USING A CUTTING TORCH TOO CLOSE TO THE SERVICE LINE.
2025-01-31 10:21 | YES | NO | 20000200 | 2000-11-13 | 31348 | TXU GAS DISTRIBUTION | BRAIR RIDGE @ SHOAL FOREST | PLANO | COLLIN | TX | 75024- | 3 | NO | 1127 | 2000-10-05 | 0 | 0 | 300000 | 202732.8714 | 489491.9169 | NO | 1 | 11 |  | 20001005 | 21 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 |  | PE 2406 | PLEXCO | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A TRENCHER CUT A 3 INCH POLY MAIN. GAS IGNITED AND THE TRENCHER BURNED.
2025-01-31 10:21 | NO | NO | 20000201 | 2000-11-13 | 2332 | CHEYENNE LIGHT FUEL & POWER | ROUNDTOP & HAPPY JACK RD | CHEYENNE | LARAMIE | WY | 82009- | 3 | NO | 1215 | 2000-10-24 | 0 | 0 | 0 | 0 | 0 | NO | 1 | 0 | 546156 | 20001024 | 30 | 60 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM | DRISCO | 1988 | 1989 | UNDER GROUND OR UNDER WATER |  | DAVID MCCLINTOCK, MANAGER | 3077782168 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-10-11 | YES | 3 | FLAGS AND PAINT | YES | NO DATA |  | CONTRACTOR DAMAGED MAIN IN THE PROCESS OF INSTALLING FIBER OPTIC CABLE.
2025-01-31 10:21 | YES | YES | 20000203 | 2000-11-14 | 10037 | WESTERN RESOURCES INC (AKA KPL CO. OR GAS SERVICE) | 1120 1/2 S DEWEY | BARTLESVILLE | WASHINGTON | OK | 7 4003 | 3 | NO | 500 | 2000-10-15 | 0 | 2 | 35000 | 23652.1683 | 57107.3903 | NO | 1 | 30 | 545258 | 20001015 | 0.875 | 0.875 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MATT FULGHUM, MANAGER III | 9183361740 | EXTERNALLY | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | RECORDS ACQUIRED FROM FORMER OPERATORS DID NOT SHOW EXISTENCE OF THIS SHORT SECTION (40 FEET) OF 2-INCH BARE STEEL PIPE.
2025-01-31 10:21 | YES | YES | 20000205 | 2000-11-17 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | PROGRESS STREET |  | JEFFERSON | AL |  | 2 | NO | 1355 | 2000-11-01 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 45 | 546988 | 20001101 | 250 | 300 | BY TEST | 450 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | NO DATA |  |  |  | 4" GATE VALVE | KEROTEST | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LEE PETERS, DISTRIBUTION ENGINEER | 2053268186 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20000206 | 2000-11-17 | 15462 | PECO ENERGY CO | 2050 BUTLER PIKE | PLYMOUTH MEETING | MONTGOMERY | PA | 19462- | 3 | NO | 440 | 2000-10-21 | 0 | 0 | 300000 | 202732.8714 | 489491.9169 | NO | 4 | 35 | 545852 | 20001021 | 17 | 25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.41 |  |  | 0 | 1958 | UNDER PAVEMENT |  | T MARK ANDRAKA, ENGINEER | 6109411641 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-07-10 | YES | 0 |  | YES | NO DATA |  | SEE PART D - OTHER
2025-01-31 10:21 | YES | NO | 20000207 | 2000-11-24 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #596 | SADDLEBROOKE | PIMA | AZ | 85739 | 3 | NO | 1501 | 2000-11-06 | 0 | 0 | 120000 | 81093.1486 | 195796.7667 | YES | 2 | 29 | 547944 | 20001106 | 150 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | REGULATOR/METER |  | STEEL |  |  |  | 2" SINGLE PORT | MOONEY | 1994 |  | ABOVE GROUND |  | JAMES LANTTO | 5207946034 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20000208 | 2000-11-22 | 18536 | SOUTHWEST GAS CORP | 370 ANDRIA DRIVE | STATELINE | DOUGLAS | NV | 8 9449 | 3 | NO | 1405 | 2000-10-26 | 0 | 1 | 451884 | 305372.4696 | 737311.8845 | NO | 1 | 10 | 546449 | 20001026 | 40 | 43 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | OTHER | PVC | 0.5 | 0.06 | ASTM D-2513 | KRALOY | 0 | 1964 | UNDER GROUND OR UNDER WATER |  | JEFFERY L MAPLES | 7758872805 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20000209 | 2000-11-22 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1320 CENTRAL PARK BLVD | FREDERICKSBURG | SPOTSYLVANIA | VA | 22401- | 3 | NO | 1305 | 2000-10-23 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 0 | 56 | 546029 | 20001023 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR 11 | PLEXCO | 1997 | 1998 | UNDER GROUND OR UNDER WATER |  | NORMAN G DUREN | 8043235312 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A PLUMBING CONTRACTOR (CAPITAL PLUMBING AND AIR) FAILED TO NOTIFY THE ONE CALL NOTIFICATION CENTER (MISS UTILITY) OF THE INTENT TO EXCAVATE AND SUBSEQUENTLY STRUCK AND UNMARKED 2" MEDIUM PRESSURE PLASTIC MAIN.
2025-01-31 10:21 | YES | YES | 20000210 | 2000-08-10 | 1800 | KEYSPAN ENERGY-WEST | 420 STATE STREET | BROOKLYN | KINGS | NY |  | 4 | NO | 1950 | 2000-07-11 | 3 | 0 | 0 | 0 | 0 | NO | 1 | 5 | 535097 | 20000712 | 0.25 | 0.4 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | N/A | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN P KELLY, GENERAL FOREPERSON | 7184032908 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20000212 | 2000-12-04 | 18484 | SOUTHERN CALIFORNIA GAS CO | SANTA MONICA & LA JOLLA AVE | WEST HOLLYWOOD | LOS ANGELES | CA |  | 3 | NO | 955 | 2000-10-31 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 3 | 20 | 546899 | 20001031 | 35 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 |  |  |  | 0 | 0 | NO DATA |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | PAINT ON PAVING THAT WAS SUBSEQUENTLY REMOVED | YES | NO DATA |  | CONTRACTOR PULLED SERVICE OFF OF 6" STEEL MAIN. FACILITY HAD BEEN PROPERLY LOCATED. REPORTED DUE TO LOSS OVER $50,000. LOSS DUE TO BUSINESS OUT OF GAS AND REPAIRS.
2025-01-31 10:21 | YES | NO | 20000213 | 2000-11-27 | 18536 | SOUTHWEST GAS CORP | 2546 N 11TH STREET | PHOENIX | MARICOPA | AZ | 85006 | 3 | NO | 2154 | 2000-10-31 | 0 | 0 | 95000 | 64198.7426 | 155005.7737 | NO | 1 | 45 | 546933 | 20001031 | 30 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.151 | ASTM D2513 | PHILLIPS | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | SHAWN BRINK; ADMINISTRATOR/DIVISION COMPLIANCE | 6024845489 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | TREE ROOT GROWTH AND SOIL PRESSURE | Null |  | Null | 0 |  | Null |  |  | THE CAUSE OF THE LEAK IS UNDER INVESTIGATION BY A THIRD PARTY LABORATORY. A SUPPLEMENTAL REPORT WILL BE SUBMITTED BASED ON THE RESULTS OF THE LABORATORY TESTS. SUPPLEMENTAL REPORT: THE CAUSE OF THE LEAK STRESS-RUPTURE DUE TO EXCESSIVE COMPRESSION LOADING OF THE PIPE BY A LARGE TREE ROOT.
2025-01-31 10:21 | YES | YES | 20000214 | 2000-12-04 | 13480 | NIAGARA MOHAWK POWER CORP | 219 PRIMROSE STREET | SYRACUSE | ONONDAGA | NY | 1 3202 | 3 | NO | 1243 | 2000-10-26 | 0 | 1 | 0 | 0 | 0 | YES | 0 | 9 | 546391 | 20001026 | 8.9 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | MILES ROSS | 3154604127 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT 12:45PM ON OCTOBER 26, 2000 NIAGARA MOHAWK SYSTEM OPERATIONAL DISPATCH RECEIVED A CALL FROM THE ONONDAGA COUNTY 911 CENTER REQUESTING RESPONSE TO AN EXPLOSION AT 219 PRIMROSE AVENUE. THE FOLLOWING IS A SUMMARY OF THE RESPONSE TO THIS INCIDENT:12:46 SYSTEM OPERATIONAL DISPATCH DISPATCHES SERVICE REPRESENTATIVE MARTIN TO THE SCENE. UPON HIS ARRIVAL, SERVICE REP MARTIN FINDS THAT THE SYRACUSE FIRE DEPARTMENT HAS SHUT OFF THE GAS AT THE SHUT OFF IN THE HOUSE. 12:50 GAS DISPATCH IS ALERTED. MARK RYBINSKI, MANAGER OF GAS AND ELECTRIC CONSTRUCTION AND MAINTENANCE IS INFORMED OF THE INCIDENT AND ACTIVATES THE DIVISIONAL GAS EMERGENCY ORGANIZATION AT THE DISPATCH OFFICE ON E-1,300 ERIE BLVD. SYRACUSE. ANETTE BRATEK, GAS SUPERVISOR IS ALERTED OF THE INCIDENT. 12:59 CHIEF GAS MECHANIC, ROBERT POWERS IS DISPATCHED TO MOVE HIS CREW TO THE SCENE.13:05 GAS CREW ARRIVES AT THE SCENE AND BEGINS AN OUTSIDE, UNDERGROUND INVESTIGATION. THIS INVESTIGATION INCLUDES TAKING BAR HOLE READINGS WITH A COMBUSTIBLE GAS INDICATOR AT THE APPROPRIATE LOCATIONS ALONG THE GAS SERVICE AND GAS MAIN LINES. ALL BAR HOLE READINGS SHOW NO GAS PRESENT IN THE GROUND. AFTER CONDUCTING THE PRELIMINARY INVESTIGATION, THE GAS CREW EXCAVATES THE SERVICE AND PERFORMS A PRESSURE CHECK BETWEEN THE MAIN AND THE INSIDE SHUT OFF AT 90PSI FOR 15 MINUTES. THIS TEST SHOWED NO LOSS OF PRESSURE IN THE FACILITY. DURING THE SAME TIME PERIOD, THE GAS DEPARTMENT CONDUCTED A MOBILE LEAK INVESTIGATION WITH A FLAME IONIZATION UNIT AND PERFORMED ODORIZATION CHECKS. THE F.I. SURVEY SHOWED NO INDICATION OF A LEAK IN THE STREET AND THE ODORZATION TESTS INDICATED THE APPROPRIATE LEVELS OF ODORANT IN THE GAS. 13:35 SERVICE DEPARTMENT SUPERVISOR PAUL HART ARRIVES AND DIRECTS SERVICE PERSONNEL IN PERFORMING WALL CHECKS AT NUMBERS 214,218,220,221,223,224,229,230 AND 231 PRIMROSE AVE. ALL CHECKS SHOW NO GAS IN THE ATMOSPHERE IN THESE RESIDENCES. AT THE SAME TIME, SERVICE DEPARTMENT PERSONNEL, WITH INVESTIGATORS FROM SYRACUSE FIRE DEPARTMENT, CONDUCTED AN INSIDE INVESTIGATION OF THE CUSTOMERS GAS LINES. THE GAS WAS TURNED ON AND A PRESSURE CHECK WAS DONE AT THE METER. A TEN-MINUTE TEST AT 8.9 IN. W.C. SHOWED NO MOVEMENT OF THE HALF FOOT DIAL ON THE METER. AN ADDITIONAL OPERATIONAL CHECK OF THE APPLIANCES WAS DONE. ALL WERE FOUND TO BE IN GOOD WORKING ORDER AND WERE VENTED PROPERLY. A 3/4 INCH LINE THAT TERMINATED WITH AN UNPLUGGED VALVE IN THE CLOSED POSITION WAS FOUND IN THE VICINITY OF THE ELECTRIC DRYER. THIS WAS ALSO THE APPARENT AREA OF ORIGIN OF THE FIRE/EXPLOSION. IT COULD BE DETERMINED IF EITHER NIMO OR FIRE DEPARTMENT PERSONNEL HAD CLOSED THIS VALVE. AFTER ALL TESTING WAS COMPLETED, THE UNDERGROUND SERVICE TO THIS ADDRESS WAS RENEWED USING 1" PLASTIC PIPE. THE SERVICE WAS LEFT LOCKED IN THE OFF POSITION. ALL TESTING WAS CONDUCTED IN THE PRESENCE OF KEVIN SPEICHER OF THE NEW YORK STATE PUBLIC SERVICE COMMISSION WHO DETERMINED THAT THE INCIDENT WAS NOT A RESULT OF ANY FAILURE ON THE PART OF NIAGARA MOHAWK OR OF NIAGARA MOHAWKS GAS DISTRIBUTION SYSTEM. IN ADDITION TO THE REQUIRED LOCAL AND STATE AGENCY NOTIFICATIONS, A PRECAUTIONARY NOTIFICATION TO THE FEDERAL DEPARTMENT OF TRANSPORTATION WAS MADE IT BECAME APPARENT THAT A RESIDENT OF THE HOUSE WAS TRANSPORTED TO A LOCAL HOSPITAL.
2025-01-31 10:21 | NO | NO | 20000215 | 2000-12-04 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | SOUTH ST & WHITEHALL ST | NEW YORK CITY |  | NY | 10004- | 4 | NO | 1116 | 2000-11-03 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 41 | 547171 | 20001103 | 0.184 | 0.433 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | D-2513 | DRISCOPIPE | 1996 | 2000 | UNDER PAVEMENT |  | FRANK J CIMINIELLO | 7183192316 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | PRELIMINARY ANALYSIS INDICATED AN ELECTRIC BURNOUT SUBSEQUENTLY MELTED AND IGNITED 4" LOW-PRESSURE PLASTIC GAS MAIN EXPOSED IN AN OPEN CONTRACTORS EXCAVATION. CONTRACTOR ACTIVITY IN THE AREA PRIOR TO INCIDENT. THE NEW YORK CITY FIRE DEPARTMENT EVACUATED AN UNKNOWN NUMBER OF PEOPLE FROM THE FERRY TERMINAL. THE OFFICE OF EMERGENCY MANAGEMENT, NEWS MEDIA AND UNITED STATES COAST GUARD REPRESENTATIVES WERE ON LOCATION. THE SECTION OF MAIN WAS REPLACED AND SERVICE RESTORED TO THE COAST GUARD ADMINISTRATION BUILDING, WHICH WAS THE ONLY SERVICE SUPPLIED BY THE AFFECTED SECTION OF MAIN.
2025-01-31 10:21 | YES | NO | 20000216 | 2000-12-11 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 461 GROVE AVENUE | VALPARAISO | PORTER | IN | 4 6383 | 3 | NO | 1915 | 2000-11-03 | 0 | 0 | 300000 | 202732.8714 | 489491.9169 | NO | 0 | 45 | 547271 | 20001104 | 50 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | TBD | OTHER | TBD | OTHER | TBD |  |  |  |  | 0 | 0 | OTHER | TBD | DON J TOKOLY | 2196474770 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON FRIDAY, NOVEMBER 3, 2000, AT APPROXIMATELY 7:15PM CST, A COMBUSTIBLE GAS MIXTURE BUILT UP AND IGNITED IN A HOUSE LOCATED AT 461 GROVE AVENUE IN VALPARAISO, INDIANA. THERE WERE NO OCCUPANTS IN THE HOUSE AT THE TIME OF THE EXPLOSION AND NO INJURIES RESULTED. THE HOUSE AT 461 GROVE AVENUE WAS A TOTAL LOSS. DAMAGE WAS SUSTAINED TO HOUSES IMMEDIATELY ADJACENT TO 461 GROVE AVE. TOTAL DAMAGE WAS ESTIMATED IN THE RANGE OF $200,000 TO $300,00. NORTHERN INDIANA PUBLIC SERVICE COMPANYS PRELIMINARY INVESTIGATION REVEALED TWO POSSIBLE SOURCES OF NATURAL GAS ACCUMULATION IN THE HOME:1)A COMPANY MAINTENANCE CREW INADVERTENTLY DAMAGED THE UNDERGROUND SERVICE LINE WHEN THEY STOPPED THE FLOW OF NATURAL GAS TO BEGIN REPAIRS TO THE SERVICE LINE AT 461 GROVE AVENUE EARLIER THAT AFTERNOON. THE PLASTIC SERVICE LINE WAS DAMAGED WHEN THE CREW OPERATED A STEEL VALVE WHICH CONTAINED 5/8" INSERTED PLASTIC LINE. THE CREW WAS UNAWARE OF THE DAMAGE, WHICH RESULTED IN THE MIGRATION OF NATURAL GAS THROUGH THE SOIL NEAR THE CUSTOMERS HOME. 2)LATER THAT SAME AFTERNOON, THE CUSTOMER TOOK FURTHER ACTION TO CHANGE HIS NATURAL GAS PIPE SYSTEM AT A POINT DOWNSTREAM FROM THE METER AND THROUGH THE FOUNDATION OF THE HOUSE. A PIPE UNION INVOLVED IN THE WORK PERFORMED BY THE CUSTOMER WAS FOUND TO BE APPROXIMATELY 1-1/2 TURNS LOOSE. THE EXTENT TO WHICH EITHER OF THESE TWO POTENTIAL SOURCES CONTRIBUTED TO THE ACCUMULATION OF NATURAL GAS WITHIN THE HOME HAS NOT YET BEEN DETERMINED. FURTHER, THE EXACT SOURCE OF IGNITION IS STILL UNKNOWN.
2025-01-31 10:21 | NO | NO | 20000217 | 2000-12-11 | 12378 | MESA MUNICIPAL SYSTEM, CITY OF | 1811 E UNIVERSITY DRIVE | MESA | MARICOPA | AZ | 8 5203 | 4 | NO | 900 | 2000-11-18 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 25 | 548592 | 20001118 | 149.25 | 157 |  |  | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL | [5 empty] | 0 | 1966 | OTHER | EXCAVATION | MICHAEL R COMSTOCK | 4806442490 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-11-17 | YES | 3 | 2000-11-17 | YES | NO DATA |  | ABOUT 9:00 AM ON NOVEMBER 18, 2000, WHILE EXCAVATING FOR A DEVELOPMENT SERVICES PROJECT FOR THE CITY OF MESA, ARIZONA, ARCHON, INC., A GENERAL CONTRACTOR, DUG-IN TO AND SEVERED A FOUR (4") INCH HIGH PRESSURE (HP) NATURAL GAS MAIN. THE MAIN WAS OPERATING AT 149.25 PSIG AT THE TIME OF THE DIG-IN. WITHIN ONE MINUTE OF THE HIT LINE, THE OPERATOR OF THE 1994 KOMATSU,MODEL NUMBER PC400LC, HAD REMOVED HIMSELF FROM THE OPERATORS CAB OF THE TRAC-HOE AND BEGAN TO BLOCK TRAFFIC. A CITY OF MESA POLICE OFFICER WHO WAS DRIVING BY EXCAVATION SITE AT THE TIME OF THE DIG-IN, HAD STOPPED TO AID THE OPERATOR WHEN THE VENTING NATURAL GAS IGNITED. THE RESULTING FIRE FROM THE NATURAL GAS LINE IGNITING, CAUSED EXTENSIVE DAMAGE TO THE TRACHOE, SEVERAL OVERHEAD UTILITY LINES (ELECTRIC, CABLE TV, TELEPHONE), ONE POWER POLE, AN ADVERTISING SIGN TO A LOCAL BUSINESS OFFICE COMPLEX, AND ONE LARGE PALM TREE. THERE WERE NO INJURIES, MEDICAL EMERGENCIES, OR DEATHS AS A RESULT OF THE DIG-IN. TWO GAS VALVES WERE CLOSED AND THE DIG-IN IS ESTIMATED TO BE $13,563.08 OR 2,811 DKTH, BASED ON THE COST OF GAS AT THE TIME OF THE INCIDENT. DAMAGE ASSESSMENTS ESTIMATED TO PROPERTY LOSSES HAVE YET TO BE DETERMINED, HOWEVER IT IS SAFE TO ASSUME THE LOSS WILL EXCEED THE REPORTING LIMITS REQUIRED BY FEDERAL AND STATE REGULATIONS. THE PROBABLE CAUSE OF THE INCIDENT POINTS TO TWO FACTORS. FIRST THE CITY OF MESAS UTILITY LOCATE OR "BLUE STAKE MARK" WAS FOUND TO BE FIVE (5) FEET EAST OF THE ACTUAL LOCATION OF THE FOUR (4") HP NATURAL GAS MAIN. THE SECOND WAS THE CONTRACTOR, ARCHON,INC. FAILED TO "POTHOLE" AND LOCATE THE HP GAS NATURAL GAS MAIN PRIOR TO THE BEGINNING OF EXCAVATION ACTIVITY FOR THE INSTALLATION OF A SEWER MANHOLE. THE MAJOR SAFETY ISSUES IDENTIFIED IN THIS REPORT ARE THE ADEQUACY OF THE UTILITY LOCATE MARKS BY THE CITY OF MESA AND THE REQUIREMENTS OF AN EXCAVATION ACTIVITY FOR THE INSTALLATION OF A SEWER MANHOLE. THE MAJOR SAFETY ISSUES IDENTIFIED IN THIS REPORT ARE THE ADEQUACY OF THE UTILITY LOCATE MARKS BY THE CITY OF MESA AND THE REQUIREMENTS OF AN EXCAVATOR TO: "NOTIFY EITHER THE OWNER OF AN UNDERGROUND FACILITY OR AN ORGANIZATION DESIGNATED BY THE OWNER IF THE EXCAVATOR ENCOUNTERS AN UNDERGROUD FACILITY THAT HAS NOT BEEN MARKED OR HAS BEEN MARKED IN THE WRONG LOCATION"(ARIZONA REVISED STATUE, (ARS)40-360-23). AS A RESULT OF THE INVESTIGATION, SUBSEQUENT AFTER ACTION REVIEWS, AND INTERVIEWS WITH RESPONSIBLE PARTIES FOR EACH ORGANIZATION INVOLVED, CORRECTIVE ACTION FOR EACH OF THE MAJOR SAFETY ISSUES HAS BEEN RECOMMENDED AND IMPLEMENTED. THE EMERGENCY RESPONSE PLAN AND COORDINATION BETWEEN EMERGENCY RESPONSE AGENCIES, (CITY OF MESA FIRE DEPARTMENT, CITY OF MESA POLICE DEPARTMENT, CITY OF MESA UTILITIES DEPARTMENT)WAS PUT INTO ACTION AS TRAINED TO AND FOUND TO BE ADEQUATE IN FORMAT AND APPLICATION UNDER FIELD CONDITIONS.
2025-01-31 10:21 | YES | NO | 20000218 | 2000-12-12 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 16500 BLK. BATTLECREEK DR. (WEST DIST) | HOUSTON | HARRIS | TX | 7 7095 | 3 | NO | 858 | 2000-11-02 | 0 | 0 | 200000 | 135155.2476 | 326327.9446 | YES | 5 | 13 | 547085 | 20001102 | 43 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2406 | NO DATA | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | JEFFREY A BISH MGR GAS OPERATIONS & MEASURE | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-12-19 | NO | 0 |  | YES | NO DATA |  | THIRD PARTY DAMAGED A 2" I.P. PLA. MAIN WITH A BORING TOOL. ESCAPING GAS ENTERED DAMAGED SEWER MAIN AND SUBSEQUENTLY ENTERED HOME WHERE AN EXPLOSION AND FIRE OCCURRED.
2025-01-31 10:21 | YES | NO | 20000219 | 2000-12-12 | 31348 | TXU GAS DISTRIBUTION | 201 E PARK STREET | LITTLE ELM | DENTON | TX | 7 5068 | 3 | NO | 1835 | 2000-10-29 | 0 | 0 | 80000 | 54062.0991 | 130531.1778 | NO | 9 | 55 | 546732 | 20001029 | 21 | 60 | BY TEST | 90 | NO DATA | ALL OTHER CAUSES | UNKNOWN | OTHER | SERVICE SADDLE | OTHER | SERVICE SADDLE | POLYETHYLENE PLASTIC |  | 0.75 | 0.16 |  |  | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER SYSTEM MONTORING MGR | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A LEAK OCCURRED AT A SERVICE SADDLE. GAS MIGRATED UNDER THE STRUCTURE AND THE GAS IGNITED. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED ONCE AN ENGINEERING LABORATORY ANALYSIS OF THE PIPE IS COMPLETED.
2025-01-31 10:21 | YES | YES | 20000220 | 2000-12-14 | 13782 | NORTHERN STATES POWER CO | 1415 BERKELEY AVENUE | ST PAUL | RAMSEY | MN | 5 5105 | 3 | NO | 1631 | 2000-11-16 | 0 | 1 | 130000 | 87850.911 | 212113.164 | NO | 1 | 31 | 548453 | 20001116 | 54 | 66 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D2513 | PLEXCO | 0 | 1997 | UNDER PAVEMENT |  | NICK J BOOSALIS, SPECIALTY | 6512292317 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | POLYETHYLENE PLASTIC GAS MAIN WAS DAMAGED DURING THE CLEANING OF THE SANITARY SEWER SERVICE BY A THIRD PARTY FROM WITHIN THE HOUSE AT 1415 BERKELEY AVENUE. GAS ESCAPED INTO THE HOUSE, PRESUMABLY THROUGH THE SANITARY SEWER SERVICE, AND WAS IGNITED BY AN UNDETERMINED SOURCE OF IGNITION. THE PERSON CLEANING THE SANITARY SEWER SERVICE WAS BURNED WHEN RETURNING TO THE WORK AREA AFTER MAKING A PHONE CALL.
2025-01-31 10:21 | NO | NO | 20000222 | 2000-12-19 | 4483 | ENSTAR NATURAL GAS CO | 7745 PALMER WASILL HIGHWAY | WASILLA |  | AK | 9 9654 | 2 | NO | 2344 | 2000-12-07 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 0 | 30 | 550305 | 20001208 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | M-8000 | DRISCOPIPE | 1998 | 1998 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THRUSDAY EVENING, DECEMBER 7,2000, AT APPROXIMATELY 11:44 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 7745 PALMER WASILLA HIGHWAY, WASILLA, AK. AN ENSTAR SERVICEMAN AND DISTRIBUTION PERSON WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A COMMERCIAL BUILDING ON FIRE. HEAT FROM THE FIRE MELTED THE 7/8" OD HDPE SERVICE LINE INSIDE THE SERVICE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS PINCHED OFF A 12:14 AM AST AND CAPPED AT 1:35 AM AST. THE CAUSE OF THE FIRE IS UNKNOWN. HOWEVER, NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20000229 | 2000-12-26 | 15007 | PACIFIC GAS & ELECTRIC CO | 1045 MCKINSTRY ST | NAPA | NAPA | CA | 94559-2615 | 3 | NO | 1730 | 2000-11-16 | 0 | 0 | 252000 | 170295.612 | 411173.2102 | NO | 4 | 36 | 548476 | 20001116 | 25 | 30 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 3 | 0.304 | D2513 | DRISCOPIPE | 1980 | 1980 | UNDER GROUND OR UNDER WATER |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ESCAPING GAS FROM A LEAK AT A BUTT FUSION FAILURE MIGRATED INTO LOWER UNIT OF TWO-STORY DUPLEX. GAS WAS IGNITED AND EXPLOSION AND HOUSE FIRE RESULTED. NO REPORTS OF GAS ODOR WERE MADE PRIOR TO INCIDENT. HOWEVER, FIRE DEPARTMENT REPORTED STRONG GAS ODOR AFTER ARRIVAL ON SCENE. GAS MAY HAVE MIGRATED IN UTILITY TRENCH THEN THROUGH WATER OR SEWER SERVICE TRENCH TO ACCUMULATE IN HOUSE. GASOLINE VAPOR ALSO DETECTED IN SOIL. PIPE DEPTH WAS 30 INCHES. ADD 6/19/2001: MAIN LOCATED IN UNPAVED DRIVEWAY OF CONSTRUCTION YARD, AND SUBJECTED TO HEAVY EQUIPMENT WHELL LOADING. MODERATE EARTHQUAKE OCCURRED IN VICINITY OF 9/9/00. VISUAL EXAMINATION OF THE BUTT FUSION SHOWED INCOMPLETE ROLL BACK OF THE BEAD.
2025-01-31 10:21 | NO | NO | 20000230 | 2000-12-26 | 13707 | NORTHERN MINNESOTA UTILITIES | INTERSECTION OF COUNTY RD 28 AND MN STAT | AITKIN | AITKIN | MN | 5 6431 | 1 | NO | 930 | 2000-11-27 | 0 | 0 | 0 | 0 | 0 | NO | 2 | 0 | 549288 | 20001127 | 150 | 175 | BY TEST | 275 | ACCIDENTALLY CAUSED BY OPERATOR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.156 | API 5L GRADE B |  | 0 | 1991 | UNDER GROUND OR UNDER WATER |  | RON CARLBERG | 2188782245 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES | 2000-11-24 | YES | 0 |  | YES | PHYSICAL DAMAGE DURING CONSTRUCTION |  | NORTHERN PIPELINE CONSTRUCTION CO.(NPL), AN INDEPENDENT CONTRACTOR WORKING FOR NORTHERN MINNESOTA UTILITIES (NMU), DAMAGED 4" STEEL LINE THAT SERVES THE COMMUNITY OF AITKIN. THIS DAMAGE RESULTED IN LOSS OF SERVICE TO THE ENTIRE COMMUNITY OF 756 CUSTOMERS.
2025-01-31 10:21 | NO | NO | 20000231 | 2000-12-22 | 15896 | PROVIDENCE GAS CO | 833 835 JEFFERSON BLVD | WARWICK |  | RI |  | 4 | NO | 1423 | 2000-11-03 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 0 | 547205 | 20001103 |  |  | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | OTHER |  | MARIO CARLINO | 4012725040 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | PROVIDENCE GAS COMPANY IS FILING THIS FORM AT THE REQUEST OF MR. DON LEDVERSIS OF THE RHODE ISLAND DIVISION OF PUBLIC UTILITIES EVEN THOUGH IT BELIEVES THAT IT IS NOT NECESSARY OR APPROPRIATE FOR IT TO DO SO. ON FRIDAY, NOVEMBER 3, 2000 AT APPROXIMATELY 14:23 EST, PROVIDENCE GAS COMPANY MADE A TELEPHONIC REPORT TO THE U.S. DEPARTMENT OF TRANSPORTATION, OFFICE OF PIPELINE SAFETY, REGARDING AN EVENT WHICH OCCURRED THAT SAME DAY AT 833-835 JEFFERSON BLVD., WARWICK, RHODE ISLAND. THIS EVENT WAS REPORTED AS A FIRE AND EXPLOSION WHICH RESULTED IN PROPERTY DAMAGE OF MORE THAN $50,000.00. AT THE TIME OF THIS REPORT, IT WAS SUSPECTED THAT NATURAL GAS WAS INVOLVED. MORE CAREFUL INVESTIGATION DONE SINCE THE EVENT INDICATES THAT THE EVENT WAS NOT CAUSED BY A RELEASE OF NATURAL GAS. THE COMPANY HAS LEARNED THAT:(A) THE FURNACE AT THE SUBJECT ADDRESS WAS FUELED BY OIL AND NOT BY GAS; (B) THE LOCAL FIRE DEPARTMENT RESPONDED TO A FIRE CALL EARLIER ON NOVEMBER 3 WHILE AN OIL TECHNICIAN WAS PRESENT WORKING ON THE OIL FIRED FURNACE; (C)WITNESSES HAVE REPORTED THAT THERE WAS A "HEAVY OIL SMELL" IN THE BUILDING; (D) NO ONE REPORTED SMELLING GAS;AND (E) BAR HOLE TESTING SHOWED THAT NATURAL GAS WAS NOT MIGRATING TO THE BUILDING. PENDING FURTHER INVESTIGATION, THE CONSULTING ENGINEER RETAINED BY OUR ATTORNEYS ADVISES US THAT THE EVENT WAS MOST LIKELY A SMOKE EXPLOSION CAUSED BY A MALFUNCTION OF THE OIL FIRED HEATING SYSTEM IN THE SUBJECT DWELLING. FOR THE FOREGOING REASONS, WE BELIEVE THAT THE EVENT IS NOT AN "INCIDENT" WITHIN THE MEANING OF 49 CFR $ 191.3.
2025-01-31 10:21 | YES | NO | 20000232 | 2000-12-26 | 13840 | NORTHWEST NATURAL GAS CO | 6921 NE KILLINGSWORTH STREET | PORTLAND | MULTNOMAH | OR | 9 7128 | 3 | NO | 2145 | 2000-11-22 | 0 | 0 | 125000 | 84472.0298 | 203954.9654 | NO | 0 | 40 |  | 20001122 | 35 | 57 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | NO FAILURE | NO DATA |  | 0.75 |  |  |  | 0 | 0 | ABOVE GROUND |  | BRUCE L. PASKETT | 5032264211 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | AN INDIVIDUAL LOST CONTROL OF A VEHICLE, DRIVING INTO THE SIDE OF A BUILDING AND DAMAGING THE RISER. RELEASED GAS WAS IGNITED BY DOWN POWER LINES. BUILDING WAS ASSESSED AS A COMPLETE LOSS, DUE TO THE FIRE.
2025-01-31 10:21 | NO | NO | 20000233 | 2000-12-19 | 18104 | SAN ANTONIO, CITY PUBLIC SERVICE BOARD OF | SE CORNER OF DALLAS AND NAVARRO | SAN ANTONIO | BEXAR | TX | 7 8205 | 1 | NO | 2219 | 2000-11-11 | 0 | 0 | 53380 | 36072.9356 | 87096.9284 | NO | 0 | 56 |  | 20001111 | 9 | 33 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.25 | GRADE B |  | 0 | 1959 | UNDER PAVEMENT |  | ARMANDO CARMONA | 2103532648 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-11-02 | YES | 0 |  | YES | NO DATA |  | 12-INCH STEEL MAIN WAS HIT BY ADB UTILITY (CONTRACTOR) BORING FOR FIBER OPTIC CABLE.
2025-01-31 10:21 | YES | NO | 20000234 | 2000-12-21 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 4 CEDAR BROOK DRIVE | CRANBURY | MIDDLESEX | NJ | 8512 | 2 | NO | 1320 | 2000-11-28 | 0 | 0 | 300000 | 202732.8714 | 489491.9169 | NO | 2 | 15 | 549410 | 20001128 | 54 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.491 | D-2513 | PLEXCO | 1998 | 1999 | UNDER GROUND OR UNDER WATER |  | WILLARD S. CAREY | 9734307833 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | YES | NO DATA |  | ON THE DAY IN QUESTION THE COMPANY RECEIVED A CALL FROM THE SOUTH BRUNSWICK POLICE DEPARTMENT REPORTING THAT WHILE CARUSO CONTRACTING CO., OF PO BOX 2043, OCEAN, NJ 07712 WAS EXCAVATING TO INSTALL WATER AND SEWER MAINS THEY STRUCK AND DAMAGED A 6" DIAMETER, PLASTIC, 60 PSIG DESIGN MAIN IN FRONT OF #4 CEDAR BROOK DRIVE, CRANBURY, NJ. THE DAMAGE RESULTED IN THE RELEASE OF GAS WHICH IGNITED AND DESTROYED THE BACKHOE THAT WAS PERFORMING THE EXCAVATION. POLICE AND/OR FIRE DEPARTMENT PERSONNEL EVACUATED APPROXIMATELY 60 PEOPLE FROM #4 CEDAR BROOK DRIVE AS A PRECAUTION. COMPANY PERSONNEL ARRIVED AT THE LOCATION AT 1:35 PM AND SHUT DOWN THE MAIN TO MAKE SAFE.PERMANENT REPAIRS WERE MADE BY REPLACING THE DAMAGED SEGMENT OF MAIN. INVESTIGATION BY THE COMPANY DISCLOSED THAT THE CONTRACTOR HAD CALLED FOR A MARK-OUT AND THAT THE COMPANY DID MARK-OUT THE FACILITIES IN THE AREA, HOWEVER THE MARKOUT REQUEST WAS NOT VALID IN THAT THE CONTRACTOR WAS EXCAVATING IN AN AREA BEYOND THAT SPECIFIED IN THE MARK-OUT REQUEST. THE OPERATOR OF THE BACKHOE WAS TRANSPORTED TO THE ROBERT WOOD JOHNSON HOSPITAL IN NEW BRUNSWICK, NJ WHERE HE WAS TREATED FOR MINOR INJURIES AND RELEASED. DAMAGE WAS LIMITED TO THE BACKHOE THAT CAUSED THE DAMAGE. THE MACHINE, ESTIMATED TO HAVE A VALUE OF $300,000, WAS DESTROYED BY THE FIRE.
2025-01-31 10:21 | NO | NO | 20000235 | 2000-12-27 | 5060 | FALL RIVER GAS CO | CENTRAL STREET | FALL RIVER | BRISTOL | MA | 02721- | 3 | Null | 0 | 2000-01-18 | 0 | 0 | 41948 | 28347.4616 | 68444.0231 | NO | 11 | 0 | 517203 | 20000118 | 50 | 100 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | WELD |  | STEEL |  | 8 | 0.3 | SCHEDULE 40 |  | 0 | 1947 | OTHER | BRIDGE | CHRISTOPHER J MATTE | 5086891170 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20010002 | 2001-01-02 | 31459 | KEYSPAN ENERGY DELIVERY | 11 HIGHLAND AVENUE | MALDEN | MIDDLESEX | MA | 02148- |  | NO | 739 | 2000-11-29 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 30 |  | 20001129 | 16 | 25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.5 | API5L |  | 0 | 1968 | UNDER PAVEMENT |  | MICHAEL E SULLIVAN | 6177235512 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | ON NOVEMBER 29, 2000 AT APPROXIMATELY 7:39 A.M., A PAVEMENT GRINDER OPERATED BY NOCELLA CONSTRUCTION AND OWNED BY FITZGERALD GRADING, INC., STRUCK A 16" INTERMEDIATE PRESSURE STEEL GAS LINE. THE MALDEN FIRE DEPARTMENT AND KEYSPAN EMPLOYEES RESPONDED IMMEDIATELY. SEVERAL BUILDINGS IN THE VICINITY OF THE BREAK WERE EVACUATED BY THE FIRE DEPARTMENT AND TRAFFIC WAS DIVERTED. SERVICE ON COMMUTER TRAIN WAS CURTAILED FOR APPROXIMATELY THIRTY (30) MINUTES. THE LINE WAS OPERATING AT APPROXIMATELY 16 PSI.
2025-01-31 10:21 | YES | NO | 20010003 | 2001-01-04 | 2364 | CINCINNATI GAS & ELECTRIC CO | 2728 RIVER ROAD | RIVERSIDE | HAMILTON | OH | 4 5204 | 4 | NO | 602 | 2000-11-24 | 0 | 0 | 85000 | 57440.9802 | 138689.3764 | NO | 0 | 0 | 549354 | 20001128 | 0 | 0 |  |  | NO DATA | ALL OTHER CAUSES | UNKNOWN | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | NO DATA |  | RANDALL L. SUTTLES | 5132873921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A CRACK WAS FOUND IN A 4" CAST IRON MAIN RUNNING ADJACENT TO THE PROPERTY.
2025-01-31 10:21 | NO | NO | 20010004 | 2001-01-08 | 4483 | ENSTAR NATURAL GAS CO | 15825 E. SHAWN DR. | MATANUSKA | SUSITNA | AK | 9 9654 | 3 | NO | 654 | 2000-12-25 | 0 | 0 | 50000 | 33788.8119 | 81581.9861 | NO | 1 | 48 | 551870 | 20001225 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1997 | 1997 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON CHRISTMAS DAY, MONDAY, DECEMBER 25, 2000, AT APPROXIMATELY 6:54 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 15825 E. SHAWN DR., IN THE MATANUSKA SUSITNA BOROUGH (NEAR PALMER, AK). AN ENSTAR SERVICEMAN AND DISTRIBUTION PERSON WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THEY FOUND A MOBILE HOME ON FIRE. HEAT FROM THE FIRE MELTED THE 5/8" OD HDPE SERVICE LINE INSIDE THE SERVICE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS PINCHED OFF AT 8:42 AM AST AND CAPPED. THE CAUSE OF THE FIRE IS UNKNOWN BUT IS BELIEVED TO HAVE BEEN CAUSED BY ARSON. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20010005 | 2000-11-20 | 31348 | TXU GAS DISTRIBUTION | BRIARWICK AND AMBER GLENN | AUSTIN | WILLIAMSON | TX | 7 8729 | 3 | NO | 1647 | 2000-10-18 | 0 | 0 | 160000 | 108124.1981 | 261062.3557 | YES | 5 | 46 |  | 20001018 | 21 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC | [5 empty] | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | YES | NO DATA |  | A THIRD PARTY CONTRACTOR CUT A SIX INCH POLY MAIN. GAS IGNITED WHEN A TXU GAS DISTRIBUTION TRUCK BACKFIRED NEAR THE BLOWING GAS LEAK. THE TRUCK WAS ALSO DESTROYED IN THE FIRE.
2025-01-31 10:21 | NO | NO | 20010010 | 2001-01-09 | 12690 | MONTANA POWER CO | 1255 FRONTAGE ROAD | COLUMBIA FALLS | FLATHEAD | MT | 5 9912 | 3 | NO | 946 | 2000-12-11 | 0 | 0 | 60000 | 40546.5743 | 97898.3834 | NO | 0 | 45 | 550607 | 20001211 | 30 | 32 | BY CFR 192.619(A)(3) | 32 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.188 | API 5L, GR B |  | 1966 | 1967 | UNDER GROUND OR UNDER WATER |  | JOHN P KOVACICH | 4067512204 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | PIPELINE EXPERIENCED A RAPID SEPARATION RESULTING FROM TENSILE STRESS FROM THERMAL CONTRACTION AT A STRESS RISER CAUSED BY PAST EXCAVATION (A SEWER LINE CROSSES DIRECTLY BELOW THE GAS LINE AT THE POINT OF FAILURE).
2025-01-31 10:21 | YES | NO | 20010011 | 2001-01-10 | 8280 | I E S UTILITIES, INC. | 212 & 214 MAPLE STREET | HUBBARD | HARDIN | IA | 5 0122 | 3 | NO | 1120 | 2000-12-07 | 0 | 0 | 1000000 | 675776.2381 | 1631639.7229 | NO | 0 | 21 | 550248 | 20001207 | 17 | 18 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | API 5L | REPUBLIC, OR JONES & LAUGHLIN | 1961 | 1961 | OTHER | HARD PACKED GRAVEL | ROSANNE ROGERS LATSCH | 6082525540 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | 2-INCH STEEL MAIN FAILURE APPEARS TO BE DUE TO STRESS CRACKING. THE MAIN WAS LOCATED IN A GRAVEL ALLEY WAY THAT WAS USED BY SEMITRAILERS. THE PIPE APPEARED TO BE BENT DOWNWARD, WAS IN A SAND BACKFILL AREA,, WAS WRAPPED AND CATHODICALLY PROTECTED. AT THE TIME OF THE INCIDENT THERE WAS 18 TO 24 INCHES OF FROST. EMPLOYEES WERE INVESTIGATING A GAS LEAK CALL AT THE TIME OF THE INCIDENT TIME.
2025-01-31 10:21 | YES | YES | 20010012 | 2001-01-16 | 2596 | COLUMBIA GAS OF OHIO INC | 1469 WILBUR ROAD | MEDINA | MEDINA | OH | 4 4256 | 4 | NO | 2114 | 2000-12-16 | 1 | 1 | 400000 | 270310.4953 | 652655.8891 | NO | 0 | 46 | 551180 |  | 50 | 60 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION | NO DATA |  |  |  |  | CBOMANU | 0 | 0 | OTHER | UNDER INVESTIGATION | J.M. YOUNG | 4408912452 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CAUSE NOT YET DETERMINED. OBSERVED LEAKAGE AT THE RISER PORTION OF THE CUSTOMER OWNED SERVICE LINE AT THE SITE. THE CONDITION OF THE RISER WILL BE INVESTIGATED BY FURTHER EXAMINATION AND TESTING IN A LABORATORY SETTING.
2025-01-31 10:21 | YES | NO | 20010013 | 2001-01-16 | 12018 | MADISON GAS & ELECTRIC CO | 925 SOUTH WHITNEY WAY | MADISON | DANE | WI | 53711- | 3 | NO | 1930 | 2000-12-16 | 0 | 0 | 100000 | 67577.6238 | 163163.9723 | NO | 1 | 0 | 551399 | 20001219 | 1 | 0.5 |  |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  |  |  | S-102 REGULATOR | FISHER | 1972 | 1972 | WITHIN/UNDER BUILDING |  | PHILIP W NELSON | 6082527277 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA |  | A FIRE OCCURRED INSIDE ON UNIT OF AN EIGHT-UNIT APARTMENT BUILDING. THE OUTSIDE GAS METER AND REGULATOR WERE COVERED WITH AN EXCESSIVE LAYER OF ICE. THE ICE FORMED AS A RESULT OF WATER THAT DRIPPED OFF THE BUILDING EAVES OVERHEAD. THE BUILDUP OF ICE OVER THE VENT ON THE REGULATOR PREVENTED THE REGULATOR FROM OPERATING PROPERLY AND ALLOWED A HIGHER THAN NORMAL GAS PRESSURE INSIDE THE APARTMENT BUILDING. THE FIRE STARTED AS A RESULT OF A HIGH PILOT LIGHT ON A GAS FIREPLACE. THE FIREPLACE OVERHEATED AND CAUSED COMBUSTIBLE MATERIALS NEAR THE FIREPLACE TO IGNITE. THE METER AND REGULATOR WERE TESTED AFTER REMOVING THE ICE. THE METER AND REGULATOR WERE FOUND TO BE IN PROPER OPERATING CONDITION.
2025-01-31 10:21 | NO | NO | 20010014 | 2001-01-16 | 12684 | MONTANA - DAKOTA UTILITIES CO | MIDWAY BETWEEN 506 & 955 HWY 14 | POWELL |  | WY | 8 2435 | 2 | NO | 1135 | 2000-12-20 | 0 | 0 | 25000 | 16894.406 | 40790.9931 | YES | 0 | 40 | 551547 | 20001220 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | OUTSIDE FORCE 3RD PARTY | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR11 | PLEXCO | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | LADONNA EMINETH | 7012227924 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 2 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20010015 | 2001-01-22 | 15469 | PHILADELPHIA GAS WORKS | 3100 PASSYUNK AVE | PHILADELPHIA |  | PA | 1 9145 |  | NO | 2211 | 2000-12-22 | 0 | 0 | 1200000 | 810931.4858 | 1957967.6674 | NO | 2 | 30 | 551758 | 20001223 | 112 | 140 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 20 | 0.375 | API 5L GRADE B |  | 0 | 1965 | ABOVE GROUND |  | ABDOL R NAYAK | 2156846316 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20010017 | 2001-01-23 | 792 | ATLANTA GAS LIGHT CO | 1989 KIMBERLY VILLAGE LN APTS B & F | MARIETTA | COBB | GA | 3 0066 | 3 | NO | 2116 | 2000-12-19 | 0 | 0 | 48500 | 32775.1475 | 79134.5266 | YES | 0 | 13 | 551481 | 20001220 | 10 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  |  |  | 1813B | AMERICAN | 0 | 0 | ABOVE GROUND |  | EVAN STOUT | 7704235734 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | YES | NO DATA |  | WATER DRAINING FROM A ROOF FROZE ONTO THE SERVICE REGULATOR, CAUSING AN ICICLE TO FORM OVER THE VENT TO THE INTERNAL RELIEF OF THE REGULATOR. THE VACUUM CREATED BY THE STOPPED VENT CAUSED THE REGULATOR TO LOCK OPEN, EMITTING EXCESS GAS INTO THE RESIDENCE. THE ESCAPING GAS IGNITED CAUSING THE SPRINKLER SYSTEM TO REACT.
2025-01-31 10:21 | NO | NO | 20010018 | 2001-01-23 | 15007 | PACIFIC GAS & ELECTRIC CO | 26207 CASCADE DRIVE | HAYWARD | ALAMEDA | CA | 9 4544 | 3 | NO | 330 | 2000-12-25 | 0 | 0 | 52500 | 35478.2525 | 85661.0855 | NO | 1 | 23 | 551860 | 20001225 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 |  |  |  | 0 | 0 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE STRUCK GAS METER SET CAUSING STRUCTURE FIRE.
2025-01-31 10:21 | YES | YES | 20010019 | 2001-01-30 | 12582 | MISSISSIPPI VALLEY GAS | 145 MULLENS-WILLIAMS RD | LYON | COAHOMA | MS |  | 1 | NO | 1230 | 2001-01-06 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 552512 | 20010106 | 5 | 5 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 |  |  |  | 0 | 1946 | UNDER GROUND OR UNDER WATER |  | DAN W OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | 2" CAST IRON MAIN BROKE AT JOINT FITTING APPROXIMATELY 20 FEET IN FRONT OF HOUSE. MAIN BROKE AS RESULT OF EXTERNAL LOADING CAUSING BY SOIL SHIFTING. GAS APPEARED TO MIGRATE INTO CINDER BLOCK WALLS OF HOUSE ALONG FRACTURE IN SOIL OR SERVICE LINE UNDER FROZEN TOP SOIL.
2025-01-31 10:21 | NO | NO | 20010020 | 2001-01-22 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 4600 PINE | BELLAIRE | HARRIS | TX | 7 7401 | 3 | NO | 1316 | 2000-12-21 | 0 | 0 | 8000 | 5406.2099 | 13053.1178 | NO | 13 | 54 |  | 20001221 | 45 | 60 | BY CFR 192.619(A)(3) | 115 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | API 5L A |  | 0 | 1963 | UNDER PAVEMENT |  | JEFFREY A BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | PIPE CRACKED FROM THIRD PARTY DAMAGE WHICH OCCURRED AT SOME UNKNOWN RIOR TIME.
2025-01-31 10:21 | NO | NO | 20010021 | 2001-01-26 | 31202 | RELIANT ENERGY FIELD SERVICES CORP | APT 503 WOODRIDGE | KARNACK | HARRISON | TX |  | 2 | NO | 1850 | 2001-01-05 | 0 | 0 | 40000 | 26391.081 | 63720.4059 | YES | 2 | 0 |  | 20010105 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL | [5 empty] | 0 | 0 | ABOVE GROUND |  | TERRY SHARP | 9035720551 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | TRUCK HIT APARTMENT BUILDING AND METER LOOP.
2025-01-31 10:21 | NO | NO | 20010022 | 2001-01-29 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 10450 NEVINS ROAD | SIX LAKES | MONTCALM | MI | 4 8886 | 1 | NO | 1810 | 2001-01-06 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 0 | 552803 | 20010106 | 400 | 850 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | LOOP | FITTING |  | STEEL |  | 6 | 0.432 |  | TAYLOR MANUFACTURING | 2000 | 2000 | OTHER | INSIDE HEATER VESSEL | THOMAS P FUNTSCH | 3135777026 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | NATURAL GAS BEING DRIED IN A DEHYDRATION LOOP WAS OVERHEATED. A 180 DEGREE STEEL FITTING FAILED AND THE THEN LEAKING FROM THE BURNER PILOT CAUSING DAMAGE.
2025-01-31 10:21 | YES | NO | 20010026 | 2001-01-30 | 31467 | PPL GAS UTILITIES CORP | 43 SLOCUM AVENUE | EXETER | LUZERNE | PA | 1 8643 | 3 | NO | 1410 | 2000-12-17 | 0 | 0 | 250000 | 168944.0595 | 407909.9307 | NO | 0 | 15 |  | 20001217 | 30 | 60 | BY TEST |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2.375 | 0.154 | SCH 40 | UNKNOWN | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | ROBERT F BEARD | 7175602750 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | APPARENT CAUSE OF ACCIDENT WAS THIRD PARTY DAMAGE. INVESTIGATION IS ONGOING.
2025-01-31 10:21 | YES | YES | 20010027 | 2001-02-05 | 603 | ARKLA, A NORAM ENERGY COMPANY | 223 ELBERTA | LAMAR | JOHNSON | AR |  | 3 | NO | 300 | 2000-11-06 | 1 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 548119 | 20001113 | 48 | 60 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.09 | D-2513 | UNKNOWN | 1973 | 0 | UNDER GROUND OR UNDER WATER |  | ULYS R REID | 5013774554 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE HOME AT 223 ELBERTA APPEARS TO HAVE HAD AN ADDITION BUILT ON TO THE SIDE OF THE HOUSE. THE ORIGINAL, 1-INCH STEEL SERVICE LINE WOULD HAVE BEEN LOCATED UNDER THE NEW ADDITION. A 1.25-INCH PE 3406 PLASTIC SERVICE LINE WAS INSTALLED TO REROUTE THE SERVICE AROUND THE ADDITION BY AN AS-YET UNIDENTIFIED THIRD PARTY. A 1-INCH LONGITUDINAL CRACK WAS DISCOVERED IN THIS PLASTIC LINE, APPROXIMATELY 13-FEET FROM THE HOME ON THE 1.25-INCH SERVICE LINE ON THE STREET SIDE OF THE HOME. THE AREA WAS BAR-TESTED AND INDICATED SIGNIFICANT CONCENTRATIONS OF NATURAL GAS AROUND THE SLAB OF THE NEW ADDITION. AS STATED ABOVE, BASED ON THE PRELIMINARY INVESTIGATION, IT APPEARS THAT A THIRD PARTY INSTALLED THE PLASTIC GAS SERVICE LINE AROUND THE NEW ADDITION.
2025-01-31 10:21 | YES | YES | 20010028 | 2001-02-06 | 13710 | NORTHERN ILLINOIS GAS CO | 1604 43RD AVE | STONE PARK | COOK | IL |  | 3 | NO | 2030 | 2001-01-14 | 0 | 1 | 5000 | 3298.8851 | 7965.0507 | NO | 0 | 30 | 553576 | 20010115 | 60 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | FITTING |  | STEEL | [5 empty] | 0 | 0 | ABOVE GROUND |  | GEORGE WALDVOGEL | 8159838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | OUTSIDE METER SET WAS DAMAGED FROM FALLING ICE. CUSTOMER WAS INVESTIGATING THE DAMAGES WHEN THE GAS IGNITED. (CAUSE UNKNOWN) CUSTOMER RECEIVED BURNS TO THE FACE AND HANDS TAKEN TO HOSPITAL.
2025-01-31 10:21 | YES | YES | 20010029 | 2001-02-05 | 31348 | TXU GAS DISTRIBUTION | 3500 S GROVE | FORT WORTH | TARRANT | TX | 7 6106 | 3 | NO | 1929 | 2000-11-25 | 0 | 1 | 40000 | 27031.0495 | 65265.5889 | NO | 13 | 16 |  | 20001125 | 28 | 30 | BY TEST | 90 | NO DATA | ALL OTHER CAUSES | UNKNOWN | MAIN |  | JOINT |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE2306 | NIPAK | 1981 | 1981 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A LEAK OCCURRED AT A REDUCER. GAS MIGRATED UNDER THE STRUCTURE AND IGNITED. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED ONCE AN ENGINEERING ANALYSIS IS COMPLETED.
2025-01-31 10:21 | YES | NO | 20010030 | 2001-02-08 | 603 | ARKLA, A NORAM ENERGY COMPANY | 607 CHICKADEE DR | LITTLE ROCK | PULASKI | AR | 7 2205 | 3 | NO | 1320 | 2001-01-03 | 0 | 0 | 350000 | 230921.9592 | 557553.5513 | NO | 0 | 25 | 552575 | 20010104 | 28 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.179 |  | UNKNOWN | 1965 | 1965 | UNDER GROUND OR UNDER WATER |  | SCOTT E DOYLE | 5013774554 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 1997-07-28 | YES | 3 | 1997-07-28 | YES | NO DATA |  | 2 INCH STEEL PIPE DEVELOPED AN APPROXIMATE 60% PLUS TRANSVERSE CRACK FROM AN OUTSIDE FORCE. METALURGICAL EXAMINATION IS BEING PERFORMED THROUGH THE APSC TO DETERMINE FAILURE MODE.
2025-01-31 10:21 | NO | NO | 20010033 | 2001-02-09 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 8800 RIO GRANDE | ALBUQUERQUE | BERNALILLO | NM | 8 7102 | 3 | NO | 1338 | 2001-01-16 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 553767 | 20010116 | 175 | 175 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.375 | API 5L | UNKNOWN | 1958 | 1958 | UNDER PAVEMENT |  | TOM BULLARD | 5052414510 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-01-11 | YES | 3 | 2001-01-11 | YES | NO DATA |  | CABLE CONTRACTOR BORED INTO HIGH PRESSURE 16-INCH DISTRIBUTION LINE.
2025-01-31 10:21 | YES | NO | 20010034 | 2001-02-09 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 926 ISLETA SW | ALBUQUERQUE | BERNALILLO | NM | 8 7102 | 3 | NO | 506 | 2001-01-14 | 0 | 0 | 80000 | 52782.1621 | 127440.8117 | NO | 1 | 49 | 553502 | 20010114 | 60 | 60 | BY TEST | 40 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL | [5 empty] | 0 | 0 | ABOVE GROUND |  | TOM BULLARD | 5052414510 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | VEHICLE CRASHED INTO BUILDING AND METER SET, BREAKING METER SET AT RISER.
2025-01-31 10:21 | YES | NO | 20010035 | 2001-02-02 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | 17TH STREET & ST CHARLES AVE | BIRMINGHAM | JEFFERSON | AL | 3 5208 | 3 | NO | 1145 | 2001-01-09 | 0 | 0 | 83000 | 54761.4932 | 132219.8422 | NO | 15 | 15 |  | 20010119 | 0.2 | 0.25 |  |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 |  |  |  | 0 | 0 | UNDER PAVEMENT |  | LEE PETERS | 2053268186 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | WHILE INSTALLING A MAIN BY DIRECTIONALLY BORING, A CONTRACTOR DAMAGED TWO WATER LINES AND A LOW PRESSURE CAST IRON GAS MAIN. WATER FILLED PORTIONS OF THE DISTRIBUTION SYSTEM THUS CAUSING THE LOSS OF SERVICE TO 209 HOUSES.
2025-01-31 10:21 | NO | NO | 20010041 | 2001-02-16 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1711 VIKING DR. | HOUSTON | HARRIS | TX | 7 7018 | 3 | NO | 1633 | 2001-01-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 51 | 553778 | 20010116 | 42 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | VARIOUS |  |  | VARIOUS | VARIOUS | 0 | 1997 | ABOVE GROUND |  | JEFFREY A. BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | A STRUCRTURE FIRE CAUSED THE METER SET ASSEMBLY TO MELT THAT CAUSED GAS TO ESCAPE AND IGNITE.
2025-01-31 10:21 | NO | NO | 20010042 | 2001-02-21 | 11032 | LACLEDE GAS CO | 902 W LIBERTY | FARMINGTON | ST FRANCOIS | MO | 6 3640 | 3 | NO | 1215 | 2001-01-12 | 0 | 0 | 75000 | 49483.277 | 119475.761 | NO | 2 | 9 |  | 20010112 | 23.9 | 30 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 |  |  | 0 | 1951 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER, JR | 3143420528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-10-09 | YES | 3 | 2000-10-09 | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20010043 | 2001-02-26 | 18484 | SOUTHERN CALIFORNIA GAS CO | 2-1/2 MILES S OF HWY 166 & 1/2 MI HWY 33 | CUYAMA | SANTA BARBARA | CA |  | 1 | NO | 1120 | 2001-02-02 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 3 | 28 | 555595 | 20010202 | 292 | 675 | BY TEST | 1170 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 20 | 0.25 | X-52 | NO DATA | 0 | 0 | UNDER GROUND OR UNDER WATER |  | GREG RODDICK | 2132445730 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES | NO DATA |  | FARMER STRUCK TRANSMISSION LINE #8109 WHILE RIPPING FIELDS WITH BULLDOZER.
2025-01-31 10:21 | YES | YES | 20010044 | 2001-02-22 | 7348 | HOPE GAS INC | KEEVER STREET | PARKERSBURG | WOOD | WV | 2 6101 | 2 | NO | 1215 | 2001-01-29 | 0 | 1 | 0 | 0 | 0 | NO | 2 | 0 | 555102 | 20010129 | 47 | 60 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 |  |  |  | 0 | 1958 | UNDER PAVEMENT |  | ROGER D. BROWN | 3046273615 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A WATER BOARD EMPLOYEE ENTERED AN UNDERGROUND VAULT BELONGING TO THE PARKERSBURG WATER BOARD WITH THE INTENTION OF INSTALLING A DEHUMIDIFIER. THE EMPLOYEE PLUGGED THE DEHUMIDIFIER INTO AN ELECTRICAL OUTLET. AS THE SWITCH ON THE DEHUMIDIFIER WAS TURNED ON A FLASH FIRE ERUPTED CREATING BURNS ON HIS HANDS, NECK AND FACE. WATER BOARD OFFICIALS INDICATED THAT THE EMPLOYEE DID NOT FOLLOW PROCEDURES ESTABLISHED BY THE WATER BOARD BEFORE ENTERING THE VAULT. AFTER THE FLASH FIRE, TWO (2) GAS PIPELINE LEAKS WERE REPAIRED, ONE LEAK LOCATED APPROXIMATELY 50 FEET FROM THE VAULT AND THE SECOND LEAK LOCATED APPROXIMATELY 100 FEET FROM THE VAULT. AN ODOR LEVEL SURVEY TAKEN AFTER THE INCIDENT OCCURRED REVEALED THAT THE GAS WAS PROPERLY ODORIZED. THE INCIDENT IS STILL BEING INVESTIGATED.
2025-01-31 10:21 | YES | NO | 20010045 | 2001-02-27 | 15931 | PUBLIC SERVICE CO OF COLORADO | 2537 PEARL ST | BOULDER | BOULDER | CO | 8 0302 | 3 | NO | 1159 | 2001-01-31 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 2 | 31 | 555332 | 20010131 | 7 | 15 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | NO DATA |  | 1 | 0.133 | ANSI B16.3 | DRESSER | 0 | 1953 | UNDER GROUND OR UNDER WATER |  | TULIA WEST | 3039382314 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-02-08 | YES | 3 | PAINT | YES | NO DATA |  | CONTRACTORS EQUIPMENT SHAGGED 1" MW SERVICE PULLING PIPE OUT OF COMPRESSION COUPLING & CRACKING ELL.
2025-01-31 10:21 | YES | YES | 20010047 | 2001-03-02 | 22763 | WISCONSIN GAS CO | NORTH 3655 ELM STREET | ELLINGTON | OUTAGAMIE | WI | 5 4944 | 3 | NO | 1101 | 2001-02-03 | 1 | 1 | 185000 | 122058.7498 | 294706.8771 | NO | 4 | 24 | 555703 | 20010204 | 50 | 60 | BY TEST | 105 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ANSI B16.4 | PLEXCO | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | STEVEN D. PETTIT | 4142916486 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20010048 | 2001-03-02 | 12582 | MISSISSIPPI VALLEY GAS | 1212 WOOD STREET | JACKSON | HINDS | MS | 3 9213 | 3 | NO | 1515 | 2001-02-18 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 15 | 557117 | 20010218 | 24 | 37 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | UNSPECIFIED CORROSION | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 |  |  | 0 | 1950 | ABOVE GROUND |  | DAN W. OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ABOVE GROUND CORROSION LEAK ON 1" SERVICE RISER IN VACANT LOT NEXT TO 1212 WOOD STREET.A 1" STEEL SERVICE LINE TO A VACANT LOT HAD A CORROSION LEAK ON A PORTION OF PIPE EXTENDING ABOVE GROUND LEVEL. AN EMERGENCY MEDICAL UNIT RESPONDED ON FEBRUARY 18, 2001 TO THE LOCATION AND ADMINISTERED CARE TO AN UNKNOWN INDIVIDUAL. ORIGINAL REPORTS INDICATED AN INDIVIDUAL SMELLED NATURAL GAS AND AS A RESULT, THE INDIVIDUAL WAS TRANSPORTED TO A HOSPITAL FOR MEDICAL CARE. HOWEVER, THE MEDICAL RESPONSE COMPANY LATER CONFIRMED THAT THE INDIVIDUAL WAS NOT TRANSPORTED TO A HOSPITAL AND DID NOT REQUIRE FURTHER MEDICAL CARE. THEREFORE, THIS INCIDENT BECAME A NONREPORTABLE INCIDENT. MISSISSIPPI VALLEY GAS INSTALLED A 1" PIPE SAVER CLAMP ON THE LEAKING PIPE TO STOP THE GAS LEAKAGE ON FEBRUARY 18, 2001. THE FOLLOWING DAY, FEBRUARY 19, 2001, THE SERVICE LINE WAS DISCONNECTED FROM THE MAIN AND WAS RETIRED FROM SERVICE.
2025-01-31 10:21 | YES | NO | 20010050 | 2001-03-05 | 30769 | MISSOURI GAS ENERGY | 21ST AND HOLMES | KANSAS CITY | JACKSON | MO | 6 4108 | 3 | NO | 1838 | 2001-01-18 | 0 | 0 | 600000 | 395866.2157 | 955806.0879 | NO | 1 | 11 | 554050 | 20010118 | 90 | 100 | BY TEST | 188 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | FITTING |  | STEEL |  | 12 | 0.219 | API 5L B | UNKNOWN | 0 | 1987 | ABOVE GROUND |  | JIM GORMAN | 8169692275 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOMELESS PERSONS HAD BUILT A FIRE UNDER THE EXPOSED 12" PIPELINE NEAR A FLANGE UP UNDER A BRIDGE FOR HEAT DURING SEVERE COLD WEATHER.
2025-01-31 10:21 | YES | YES | 20010051 | 2001-03-01 | 13210 | NEODESHA GAS DEPT, CITY OF | 1103 N 6TH | NEODESHA | WILSON | KS | 6 6757 |  | NO | 359 | 2001-02-06 | 0 | 1 | 1200 | 791.7324 | 1911.6122 | NO | 4 | 0 | 555970 | 20010207 | 0 | 0 |  |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | NO DATA |  | CAST IRON | [5 empty] | 0 | 1951 | UNDER PAVEMENT |  | GLEN FULLER | 3163222831 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON TUESDAY, FEBRUARY 6, 2001 AT 3:50 P.M., JERRY LOUR CALLED ON THE RADIO THAT THERE HAD BEEN AN EXPLOSION AT 1103 N. 6TH. DARRELL CLARK, BRENT WHEELER AND LEON REEDY ARRIVED ON SITE AT 4:00 P.M. LEON SHUT OFF THE GAS METER. DARRELL AND BRENT WENT INSIDE THE BUILDING WITH CGI TO MAKE SURE IT WAS SAFE. THEY WENT TO THE WEST SIDE OF BUILDING ON THE YARD LINE ENTRANCE BARHOLE AND CHECKED WITH CGI OK. STARTED BARHOLING ALONG SOUTH SIDE OF BUILDING STARTED PICKING UP READINGS OF 20%, 40%, 60% ALONG IN FRONT OF THE BUILDING. DARRELL SENT LEON TO FLAME PACK 3" POLY LINE GAS LINE IN ALLEY WEST OF BUILDING FROM TANK STREET TO WALNUT 1 BLOCK NORTH NO LEAK FOUND. LEON STARTED EAST FROM ALLEY ON TANK STARTED PICKING UP READINGS ABOUT 50 FT. EAST OF ALLEY OR TO THE TREE BY STREET. DARRELL AND BRENT WERE BARHOLING AROUND SIDEWALK TO BUILDING AND 6TH STREETSIDE AND STARTED BY CURB ON TANK STREET WHERE FOUND READING 60% TO 100% READINGS. DARRELL CALLED GLEN FULLER ABOUT 4:20 P.M. WHEN I ARRIVED I ASKED DARRELL WHERE HE HAD CHECKED AND WHERE HIGHEST READINGS WE RECHECKED BY STREET. I SENT BRENT AFTER COMPRESSOR TO DRILL STREET. DARRELL AND I LOCATED WATER AND GAS LINES IN STREET THEN WE DRILLED HOLES OVER GAS MAIN THEN WE USED CGI TO TRY TO PIN POINT LEAK. I SENT DARRELL AND BRENT AND LEON TO SHUT DOWN 5 GAS GATES. I WENT TO SHOP AT 5:45 P.M. TO CALL JOHN ASHLOCK WITH KCC ON INCIDENT. THEN WENT BACK TO THE LEAK AND STARTED DIGGING OUT FOUND LEAK CLEANED CAST IRON INSTALLED FULL CIRCLE GAS CLAMP AND TOOK COUPON OF CAST IRON TURNED GAS BACK ON AND SOAPED REPAIR CLAMP NO LEAKS. WE PURGED GAS LINE FROM GAS SERVICE 518 TANK THE ONLY HOUSE AFFECTED. WE RECHECKED AREA. FINISHED AT 8:00 P.M., FEBRUARY 6, 2001. COUPON WAS SENT OFF TO KANSAS GAS SERVICE FEBRUARY 8, 2001. WEDNESDAY, FEBRUARY 7, 2001. TOM DEBAUN AND JOHN ASHLOCK WITH THE K.C.C. WERE IN TOWN FOR INCIDENT. JOHN HAD GREELEY GAS CO. TO TAKE CAPTAN READINGS. READING TAKEN BY GLEN FULLER AND DARRELL CLARK FROM THE CITY OF NEODESHA, JOHN ASHLOCK FROM K.C.C., AND LES FROM GREELEY GAS CO. CAPTAN READINGS WERE VERY STRONG. WE PLUGGED ALL APPLIANCE LINES, HEATERS, STOVES AND HOT WATER TANK AND PRESSURE TESTED YARD LINE AND BUILDING TOGETHER WE LOST PRESSURE. CUT OFF YARD LINE FROM BUILDING AND PLUGGED AND PRESSURE TESTED YARD LINE FROM BUILDING AND PLUGGED AND PRESSURE TESTED YARD LINE. WE LOST PRESSURE SO WE PRESSURE TESTED LINES IN BUILDING AND IT DID NOT HOLD. WENT TO SHOP WENT OVER FLAME PACK SURVEY OF AREA AND LOOKED AT PRESSURE RECORDING CHARTS FROM N. 11TH AND WEST MAIN AND S. 4TH GAS STATIONS FOR FEBRUARY 6, 2001, AND CHECKED COUPON FROM CAST IRON AT LEAK.
2025-01-31 10:21 | NO | NO | 20010052 | 2001-03-09 | 18484 | SOUTHERN CALIFORNIA GAS CO | TEMESCAL CYN/LANDFILL RD | CORONA | RIVERSIDE | CA |  | 2 | NO | 1240 | 2001-02-01 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 23 | 22 | 555495 | 20010202 | 385 | 400 | BY TEST |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 2 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | W.J. KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES | NO DATA |  | KENKO INC. STRUCK A 2" STEEL SERVICE LINE WHILE INSTALLING A SEWER LINE.
2025-01-31 10:21 | NO | NO | 20010053 | 2001-03-09 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | HAGGERTY AND ECORSE ROADS | VAN BUREN | WAYNE | MI | 4 8111 | 3 | NO | 2026 | 2001-01-10 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 0 | 553380 | 20010112 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.25 |  |  | 0 | 1920 | UNDER PAVEMENT |  | THOMAS P. FUNTSCH | 3135777026 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | BORING CONTRACTOR STRUCK GAS MAIN UNDER INTERSECTION. EXTENSIVE WORK REQUIRED TO CONTROL GAS LEAK AND REPAIR THE PIPELINE.
2025-01-31 10:21 | YES | NO | 20010054 | 2001-03-07 | 15462 | PECO ENERGY CO | NORRISTOWN RD N/O WELSH RD | HORSHAM | MONTGOMERY | PA | 1 9044 | 3 | NO | 1110 | 2001-02-13 | 0 | 0 | 200000 | 131955.4052 | 318602.0293 | NO | 6 | 50 |  | 20010221 | 68 | 99 | BY TEST | 150 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.41 | SDR11 | PLEXCO | 0 | 1995 | UNDER GROUND OR UNDER WATER |  | JOHN H. FRANTZ | 6109411637 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-02-08 | YES | 3 | 2001-02-08 | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20010055 | 2001-03-13 | 15931 | PUBLIC SERVICE CO OF COLORADO | 7991 & 7993 S. KALISPELL WAY |  | ARAPAHOE | CO | 8 0112 | 3 | NO | 1350 | 2001-02-19 | 0 | 0 | 360000 | 237519.7294 | 573483.6528 | NO | 1 | 8 | 557187 | 20010219 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | PE 2406 | UPONOR | 0 | 2000 | UNDER GROUND OR UNDER WATER |  | DENNIS SKUBAL | 3035717721 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-02-12 | YES | 3 | 2001-02-12 | YES | NO DATA |  | THIRD PARTY EXCAVATING CONTRACTOR DIGGING WITH BACKHOE REMOVING FROST FOR DRIVEWAY CONCRETE POUR PUNCTURED 1.25" P.E. GAS MAIN. BLOWING GAS ENTERED STRUCTURE. GAS IGNITED FROM UNKNOWN SOURCE DAMAGING STRUCTURE.
2025-01-31 10:21 | NO | NO | 20010056 | 2001-03-19 | 13850 | NORTHWESTERN PUBLIC SERVICE CO | 1712 DAKOTA AVE SOUTH | HURON | BEADLE | SD | 5 7350 | 3 | Null | 850 | 2001-02-26 | 0 | 0 | 55000 | 36287.7364 | 87615.5581 | NO | 0 | 10 | 557887 | 20010226 | 25 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 |  | REGULATOR | UNIVERSAL CONTROLS | 0 | 1961 | ABOVE GROUND |  | JAMES MANN | 6053537522 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 |  | Null | NO DATA |  | A SNOW REMOVAL CONTRACTOR WAS REMOVING SNOW BEHIND THE BUILDING AT THE HURON VISION CENTER LOCATED AT THE ABOVE REFERENCED LOCATION. THE SNOW REMOVAL TOOK PLACE BETWEEN 10:00 & 10:30 PM ON THE EVENING OF FEBRUARY 25, 2001. AN EMPLOYEE OF THE CLINIC ARRIVED BETWEEN 8:30 AND 9:00 AM ON THE MORNING OF FEBRUARY 26 TO OPEN THE BUSINESS. THE EMPLOYEE SMELLED SMOKE AND WHAT SHE THOUGHT WAS PROPANE. NORTHWESTERN PUBLIC SERVICE AND THE HURON FIRE DEPARTMENT WERE THEN NOTIFIED. INVESTIGATION REVEALED THAT A FIRE HAD IGNITED IN THE BASEMENT OF THE BUILDING AT THE NATURAL GAS WATER HEATER. THE FIRE WAS EXTINGUISHED BY THE HURON FIRE DEPARTMENT. INVESTIGATION ALSO REVEALED THAT THE SNOW REMOVAL CONTRACTOR HAD DAMAGED THE GAS SERVICE REGULATOR AT THE METER ASSEMBLY. NATURAL GAS WAS BLOWING INTO THE OUTSIDE ATMOSPHERE FROM THE DAMAGED REGULATOR. IT IS SUSPECTED THAT THE DAMAGED SERVICE REGULATOR COULD HAVE ALLOWED A PRESSURE HIGHER THAN THE STANDARD DELIVERY PRESSURE OF 0.25 PSIG INTO THE CUSTOMER PIPING AND POSSIBLY CAUSED THE WATER HEATER TO MALFUNCTION. THE BLOWING GAS AT THE REGULATOR DID NOT CONTRIBUTE TO THE FIRE. NORTHWESTERN PUBLIC SERVICE RECEIVED NOTICE OF THIS INCIDENT AT 8:50 AM ON THE MORNING OF FEBRUARY 26. OUR CREWS RESPONDED AND HAD THE GAS SHUT OFF BY 8:55 AM. THE GAS WAS SHUT OFF AT THE SERVICE RISER. THE BUILDING SUFFERED VERY LITTLE DAMAGE DUE TO THE FLAMES BUT A SIGNIFICANT AMOUNT OF SMOKE DAMAGE. REPAIR AND CLEAN-UP COSTS ARE CURRENTLY ESTIMATED AT $55,000. THERE WERE NO INJURIES RELATED TO THE INCIDENT. THE INCIDENT WAS REPORTED TELEPHONICALLY AS REQUIRED BY 49 CFR PART 191.5. THE TELEPHONE REPORT WAS MADE AT 10:40 AM ON THE MORNING OF FEBRUARY 26. OUR CREWS RESPONDED AND HAD THE GAS SHUT OFF BY 8:55 AM. THE GAS WAS SHUT OFF AT THE SERVICE RISER. THE BUILDING SUFFERED VERY LITTLE DAMAGE DUE TO THE FLAMES BUT A SIGNIFICANT AMOUNT OF SMOKE DAMAGE. REPAIR AND CLEAN-UP COSTS ARE CURRENTLY ESTIMATED AT $55,000. THERE WERE NO INJURIES RELATED TO THE INCIDENT. THE INCIDENT WAS REPORTED TELEPHONICALLY AS REQUIRED BY 49 CFR PART 191.5. THE TELEPHONE REPORT WAS MADE AT 10:40 AM ON THE MORNING OF FEBRUARY 26. THE TELEPHONE OPERATOR WAS JONES THE REPORT WAS ASSIGNED THE NUMBER 557887. MR. MARTIN BETTMANN, THE PIPELINE SAFETY MANAGER FOR THE STATE OF SOUTH DAKOTA, INVESTIGATED THIS INCIDENT ON MARCH 14. ALL TIMES LISTED IN THIS REPORT ARE CENTRAL STANDARD TIME.
2025-01-31 10:21 | NO | NO | 20010057 | 2001-03-20 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 6815 SHAVELSON (EAST DIST) | HOUSTON | HARRIS | TX | 7 7024 | 3 | NO | 1127 | 2001-02-20 | 0 | 0 | 35000 | 23092.1959 | 55755.3551 | NO | 0 | 15 | 557290 | 20010220 | 5 |  |  |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | INCORRECT OPERATION | METER SET ASSEMBLY |  | NO DATA |  | OTHER | VARIOUS |  |  |  |  | 0 | 0 | ABOVE GROUND |  | JEFFREY A. BISH | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | DURING A CUSTOMER METER INSPECTION AN EMPLOYEE CAUSED AN ACCIDENTIAL OVER PRESSURE OF A CUSTOMER HOUSELINE RESULTING IN A FIRE.
2025-01-31 10:21 | YES | YES | 20010058 | 2001-03-15 | 12582 | MISSISSIPPI VALLEY GAS | 1010 NORTH YALE STREET | CLEVELAND | BOLIVAR | MS | 38732- | 3 | NO | 1600 | 2001-02-13 | 1 | 1 | 90000 | 59379.9324 | 143370.9132 | NO | 2 | 33 | 556649 | 20010213 | 20 | 21 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAN W. OGLESBEE | 6019616881 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | BROKEN 2" C.I. LINE NEXT DOOR (1008 NORTH YALE STREET) ALLOWED GAS TO MIGRATE INTO THE SEWER & RESIDENCE.
2025-01-31 10:21 | YES | NO | 20010063 | 2001-02-13 | 15007 | PACIFIC GAS & ELECTRIC CO | 8311 NO. EL DORADO | STOCKTON | SAN JOAQUIN | CA | 9 5210 | 3 | NO | 140 | 2001-01-26 | 0 | 0 | 102000 | 67297.2567 | 162487.0349 | NO | 3 | 25 | 554378 | 20010126 | 50 | 60 | BY TEST | 102 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.156 | SMLS | UNKNOWN | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2000-09-20 | YES | 0 |  | YES | NO DATA |  | A LARGE DIAMETER SEWER LINE WAS INSTALLED PARALLEL AND TEN FEET AWAY FROM A 4-INCH GAS MAIN. IT IS LIKELY THAT THE CONTRACTOR STRUCK THE CROSSING 3/4 INCH GAS SERVICE. A LEAK DID NOT OCCUR IN THE SEWER TRENCH LINE. FORCES EXERTED ON THE GAS SERVICE LINE CAUSED FAILURES AT THE BASE OF THE WELDS WHERE THE SERVICE TEE WAS CONNECTED TO THE SERVICE LINE AND MAIN. IT IS UNKNOWN WHETHER PIPELINE FAILURE WAS IMMEDIATE OR DELAYED. PACIFIC GAS AND ELECTRIC COMPANY WAS NOT CONTACTED AT THE TIME OF THE DAMAGE. AT 0051 HOURS ON JANUARY 26, 2001, THE FIRE DEPARTMENT NOTIFIED THE COMPANY OF A GAS LEAK. THE FIRE AND POLICE DEPARTMENTS WERE ON SCENE AND HAD ALREADY EVACUATED THE ADJACENT HOUSE, WHICH ULTIMATELY IGNITED. UPON ARRIVING AT 0120 HOURS, THE GAS FIELD SERVICE REPRESENTATIVE OBSERVED NATURAL GAS BUBBLING THROUGH STANDING WATER IN THE PLANTER STRIP BETWEEN THE STREET AND SIDEWALK. IMMEDIATELY AFTER CALLING FOR A GAS CREW TO MAKE AN UNDERGROUND REPAIR, THE ADJACENT HOUSE IGNITED AT 0140 HOURS. PRESSURE CONTROL FITTINGS WERE INSTALLED AND OPERATED AND GAS FLOW TO THE LEAKING SECTION WAS STOPPED AT 0445 HOURS. THE DAMAGED SECTIONS OF MAIN AND SERVICE WERE REPLACED WITH NEW STEEL PIPE. THE CALIFORNIA PUBLIC UTILITIES COMMISSION CAME TO THE SITE AND WITNESSED FINAL REPAIR WORK.
2025-01-31 10:21 | YES | NO | 20010064 | 2001-03-21 | 31348 | TXU GAS DISTRIBUTION | 100 BLOCK OF CHARLES STREET | WHITESBORO | GRAYSON | TX | 7 6273 | 3 | NO | 1327 | 2001-02-26 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 2 | 33 |  | 20010226 | 0 | 36 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 |  | 3306 |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | OTHER | OPERATING ERROR, NO PROCEDURE VIOLATION | A CONTRACTOR WORKING FOR TXU REPLACING A GAS MAIN BORED INTO THE GAS MAIN AS WELL AS A WATER MAIN. WATER ENTERED THE LOW PRESSURE GAS SYSTEM FILLING THE GAS MAINS AND SERVICE WITH WATER.
2025-01-31 10:21 | YES | YES | 20010065 | 2001-03-29 | 15359 | PEOPLES NATURAL GAS | 1645 OAKBROOKE DIVE | EAGAN | DAKOTA | MN | 5 5122 | 3 | NO | 805 | 2000-10-23 | 0 | 1 | 1000000 | 675776.2381 | 1631639.7229 | NO | 3 | 0 |  | 20001023 | 25 | 66 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | 2406 PE | PLEXCO | 1999 | 1999 | UNDER GROUND OR UNDER WATER |  | WILLIAM DEKKER | 6514238930 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | GAS LEAKED FROM AN INCOMPLETE PIPE FUSION INTO THE HOUSE AT 1645 OAKBROOKE DRIVE. AN UNKNOWN SOURCE OF IGNITION, INSIDE THE HOUSE, CAUSED AN EXPLOSION INJURYING ONE PERSON AND DAMAGING THIS HOUSE AND TWO ADJACENT HOUSES.
2025-01-31 10:21 | YES | YES | 20010066 | 2001-04-09 | 4473 | ENERGAS CO | 804 N BELL | BIG SPRING | HOWARD | TX | 7 9720 | 3 | NO | 1215 | 2001-03-08 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 5 |  | 20010308 | 10 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL | [5 empty] | 0 | 0 | UNDER GROUND OR UNDER WATER |  | GARY C. AXTON | 8067984474 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | THIRD PARTY HIT GAS LINE AND PULLED THE LINE APART AT A COUPLING 80 FT AWAY. SUBSEQUENTLY TO STOPPING GAS FLOW, A FLASH OCCURED IN THE BUILDING AT 804 N BELL.
2025-01-31 10:21 | YES | NO | 20010067 | 2001-03-27 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 34 GAIL PLACE | SECAUCUS | HUDSON | NJ | 7094 | 2 | NO | 1015 | 2001-02-23 | 0 | 0 | 300000 | 197933.1079 | 477903.044 | NO | 1 | 45 | 557630 | 20010223 | 15 | 15 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | COMPRESSION TEE | STEEL |  | 0.75 | 0.154 |  |  | 0 | 1963 | WITHIN/UNDER BUILDING |  | WILLARD S. CAREY | 9734307833 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-02-23 | YES | 0 |  | YES | NO DATA |  | ON FRIDAY, FEBRUARY 23, 2001, AT APPROXIMATELY 9:30 AM AN EMPLOYEE WAS DISPATCHED TO GAIL PLACE, SECAUCUS, TO PERFORM AN EMERGENCY MARKOUT FOR THE UNITED WATER COMPANY. THE EMPLOYEE OBTAINED FROM THE DISTRICT HEADQUARTERS THE INFORMATION AS TO THE SERVICE LOCATION FOR 33 GAIL PLACE AND PROCEEDED TO MARKOUT THE SERVICE. THE WATER COMPANY HAD ALREADY STARTED TO EXCAVATE IN THE ROADWAY SO THE EMPLOYEE MARKED THE ADJACENT SIDEWALK AREA AND HE PLACED TWO "G" MARKS IN THE ROADWAY, NORTH AND SOUTH OF THE EXCAVATION. THE MARKOUT WAS PERFORMED AT 10:00 AM. AT APPROXIMATELY 10:10 AM THE WATER COMPANY PULLED THE GAS SERVICE TO 33 GAIL PLACE. THEY INFORMED THE COMPANY EMPLOYEE OF THE DAMAGE AT 10:16 AM AND HE IMMEDIATELY BEGAN TO CHECK THE ADJACENT BUILDINGS. HOUSE NUMBER 33 GAIL PLACE HAD A 0 GAS READING AND IT WAS NOTED THAT THE CUSTOMER HAD GAS TO THE APPLIANCES. HE WAS UNABLE TO GAIN ACCESS TO 34 GAIL PLACE AND UPON CHECKING THE KEYHOLE AND DOORWAYS FOR READINGS HE OBTAINED A 0% GAS READING. IN HOUSE NUMBER 32 GAIL PLACE HE OBTAINED A 1% GAS READING IN THE BASEMENT AT APPROXIMATELY 10:25 AM AND REQUESTED THE CUSTOMER TO VACATE THE BUILDING. UNFORTUNATELY THE CUSTOMER DID NOT UNDERSTAND ENGLISH. THE COMPANY EMPLOYEE CONTACTED THE DISTRICT HEADQUARTERS, INFORMED THEM OF HIS FINDINGS AND REQUESTED VALVE INFORMATION AND ASSISTANCE. AT 10:51 THE COMPANY EMPLOYEE SPOKE TO THE SON-IN-LAW OF THE RESIDENT AT 32 GAIL PLACE AND WAS ABLE TO HAVE THE WOMAN LEAVE THE BUILDING. AT 10:56 AM ADDITIONAL SERVICE TECHNICIANS ARRIVED AT THE SCENE AND OBTAINED A 40% READING IN THE BASEMENT CEILING OF 32 GAIL PLACE. AT 11:10 AM A READING OF 15% GAS WAS OBTAINED AT A WINDOW AT 34 GAIL PLACE. UPON OBTAINING THIS READING THE COMPANY, AT 11:15 AM, REQUESTED THAT THE UNITED WATER COMPANY ASSIST IN DIGGING A VENT HOLE IN FRONT OF 34 GAIL PLACE. AT 11:30 AM AN EXPLOSION OCCURRED AT 34 GAIL PLACE. SECAUCUS POLICE AND FIRE DEPARTMENTS WERE IMMEDIATELY NOTIFIED AND ARRIVED ON THE SCENE AT 11:40 AM. AT 11:45 AM A 200 FOOT SECTION OF THE 2" STEEL GAS MAIN ON GAIL PLACE WAS ISOLATED AND SHUT DOWN. POST ACCIDENT INVESTIGATION BY THE COMPANY DISCLOSED THAT THE MARKOUT FOR THE SERVICE TO 33 GAIL PLACE WAS OFF BY 2 FEET. IT WAS ALSO NOTED THAT THE UNITED WATER COMPANY HAD USED A BACK HOE TO WIDEN THE EXCAVATION RATHER THAN HAND DIGGING WITHIN TWO FEET OF THE MARKOUT. AN INSPECTION OF THE DAMAGED SERVICE TO 33 GAIL PLACE DISCLOSED THAT THE 3/4" SERVICE CONNECTION HAD BEEN PULLED OUT OF THE MAIN RESULTING IN THE NATURAL GAS LEAK. PROPERTY DAMAGE CONSISTED OF PARTIAL DAMAGE TO NUMBER 32 GAIL PLACE AND A TOTAL LOSS FOR NUMBER 34 GAIL PLACE.
2025-01-31 10:21 | NO | NO | 20010068 | 2001-04-06 | 13580 | NORTH CAROLINA NATURAL GAS CORP | 107 COVINGTON PLACE | DUNN | HARNETT | NC | 2 8334 | 3 | NO | 145 | 2001-03-01 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 1 | 0 |  | 20010302 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | OTHER | ANODELESS RISER | 0.75 | 0.095 | ASTM 2406 | PERFECTION | 1992 | 1994 | UNDER GROUND OR UNDER WATER |  | THEODORE R. HODGES | 9195466369 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE FIRE.
2025-01-31 10:21 | NO | NO | 20010069 | 2001-04-18 | 30750 | MIDAMERICAN ENERGY COMPANY | 35TH & ASHWORTH | DES MOINES | POLK | IA | 5 0265 | 3 | NO | 1704 | 2001-03-15 | 0 | 0 | 52000 | 34308.4054 | 82836.5276 | NO | 3 | 0 | 559799 | 20010316 | 105 | 125 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.219 | API 5L |  | 0 | 1970 | UNDER PAVEMENT |  | ROGER LORENZEN | 7122777678 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-02-22 | YES | 2 |  | YES | NO DATA |  | CONTRACTOR INSTALLING COMMUNICATIONS CONDUIT MADE A DIRECTIONAL BORE. CONTRACTOR HAD REQUESTED AND RECEIVED LOCATES FOR THE GAS FACILITIES AND DRILLED A "LOCATE" HOLE TO FIND THE TOP OF THE 16" GAS LINE. CONTRACTOR INDICATED THEY HAD SUCCESSFULLY MADE THE ORIGINAL BORE PERPENDICULAR TO THE GAS MAIN, BUT AS THEY WERE BACK REAMING AND PULLING IN THE CONDUIT, THE BACK REAMER STRUCK AND DAMAGED OUR GAS MAIN. THE DAMAGED AREA ON THE PIPE WAS APPROXIMATELY 2" IN DIAMETER AND THE HOLE IN THE MAIN WAS APPROXIMELY 1/4 TO 1/2".
2025-01-31 10:21 | YES | YES | 20010078 | 2001-04-17 | 14210 | OKLAHOMA NATURAL GAS CO | 3301 CHISHOLM TRAIL | OKLAHOMA |  | OK | 73107- | 3 | NO | 1330 | 2001-03-20 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 15 | 560232 | 20010321 | 50 | 60 | BY TEST | 95 | ACCIDENTALLY CAUSED BY OPERATOR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE-2406 | PLEXCO | 0 | 1992 | UNDER GROUND OR UNDER WATER |  | WAYNE C. WILLIAMS | 4055566409 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION
2025-01-31 10:21 | YES | NO | 20010079 | 2001-04-30 | 11032 | LACLEDE GAS CO | 304 BRIDLE CREST DRIVE | FENTON | JEFFERSON | MO | 6 3026 | 3 | NO | 1825 | 2001-03-25 | 0 | 0 | 350000 | 230921.9592 | 557553.5513 | NO | 0 | 55 | 560698 | 20010325 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.99 | ASTM D2513 | PHILIPS | 2000 | 2000 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER JR. | 3143420528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | HOME OWNER PIERCED THE SERVICE WITH A FOREIGN OBJECT, POSSIBLY A 1/2 INCH BY 36 INCH PIECE OF STEEL REINFORCING BAR. THE NATURAL GAS MIGRATED INTO THE RESIDENCE AND WAS IGNITED BY AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 20010081 | 2001-05-01 | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 700 BLOCK OF TOWNSHIP RD 179 | BELLEFONTAINE | LOGAN | OH | 4 3311 | 3 | NO | 1150 | 2001-03-29 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 561110 | 20010329 | 47 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 3 | 0.307 | PE 2406 CEC | UPONOR | 1995 | 1995 | UNDER GROUND OR UNDER WATER |  | JOHN A. SPINKS | 9378326408 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | CONTRACTOR (FOUSS CONSTRUCTION) DUG-IN TO A MEDIUM PRESSURE PLASTIC DISTRIBUTION LINE RESULTING IN A FIRE, INJURING THE TRENCHER OPERATOR. THE LOCATING CONTRACTOR (RELIANT SERVICES) PERFORMED AN INCOMPLETE LOCATE OF ALL MAIN IN THE AREA.
2025-01-31 10:21 | YES | NO | 20010082 | 2001-05-01 | 6920 | GULF STATES UTILITIES CO | JEFFERSON HIGHWAY AT HOO SHOO TOO RD | NEW ORLEANS |  | LA | 70805- | 3 | Null | 1030 | 2001-04-06 | 0 | 0 | 150000 | 98966.5539 | 238951.522 | NO | 1 | 0 | 562065 | 20010406 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.09 | MEDIUM DENSITY | UPNOR | 2001 | 2001 | UNDER GROUND OR UNDER WATER |  | ROBERT F GUISE | 5045933449 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-04-05 | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20010088 | 2001-05-08 | 31348 | TXU GAS DISTRIBUTION | HARWOOD & BLUE QUAIL | BEDFORD | TARRANT | TX | 7 6021 | 3 | NO | 1410 | 2001-04-04 | 0 | 0 | 250000 | 164944.2565 | 398252.5366 | YES | 1 | 59 | 561805 | 20010404 | 30 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.395 | PE 2606 |  | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-02-16 | YES | 3 |  | YES | NO DATA |  | A THIRD PARTY CONTRACTOR USING AN AUGER TRUCK CUT A GAS MAIN. THE AUGER TRUCK CAUGHT FIRE.
2025-01-31 10:21 | YES | YES | 20010092 | 2001-05-18 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 851 CERRILLOS ROAD | SANTA FE | SANTA FE | NM | 8 7501 | 3 | NO | 1415 | 2001-04-25 | 0 | 2 | 180000 | 118759.8647 | 286741.8264 | NO | 3 | 45 | 564086 | 20010425 |  |  |  |  | CORROSION | CORROSION | EXTERNAL | MAIN |  | BODY OF PIPE |  | NO DATA |  | 8 | 0.188 |  | UNKNOWN | 0 | 0 | UNDER PAVEMENT |  | LARRY K. HUTCHINSON | 5052414578 | EXTERNALLY | GENERAL CORROSION |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 2:15 PM ON APRIL 25, 2001 THE NORTHERN INSURANCE COMPANY BUILDING LOCATED AT 851 CERRILLOS ROAD IN SANTA FE, NEW MEXICO EXPLODED. TWO WOMEN WERE INJURED IN THE INCIDENT AND WERE HOSPITALIZED. (A) ESTIMATED PRESSURE AT POINT AND TIME OF INCIDENT =60 PSIG (B) MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP)=*4.5 PSIG (REFER TO NOTE BELOW) (C) MAOP ESTABLISHED BY: **REFER TO NOTE BELOW. *NOTE: 7(B) SANTA FES AQUA/GALISTEO SYSTEM WAS IN STEP 4 (LAST PHASE) OF AN UPRATING PROCESS WHEN INCIDENT OCCURRED. SYSTEM WAS IN THE PROCESS OF BEING UPRATED FROM 4.5 PSIG TO 60 PSIG. **NOTE:7(C) THE AQUA FRIA/GALISTEO SYSTEM HAS AN MAOP OF 4.5 PSIG (BEFORE UPRATING PROCESS BEGAN). SINCE THE LINE WAS INSTALLED BEFORE JULY 1, 1965 ORIGINAL PRESSURE TESTS RECORDS WOULD NOT BE APPLICABLE. THERE ARE NO RECORDS AVAILABLE SUBSTANTIATING THE HIGHEST OPERATING PRESSURE THIS SEGMENT OF LINE WAS SUBJECTED TO DURING THE 5 YEARS PRECEDING JULY 1, 1970. THE FOLLOWING REASON FOR UPRATING THE SYSTEM WERE TO ESTABLISH AN MAOP, BE COMPATIBLE WITH SURROUND SYSTEMS AND HAVE SUFFICIENT PRESSURE TO HANDLE GROWTH IN THE AREA.
2025-01-31 10:21 | YES | YES | 20010093 | 2001-05-22 | 3280 | DEMING GAS SYSTEM | 514 E CEDAR STREET | DEMING | LUNA | NM | 8 8030 | 3 | NO | 2315 | 2001-05-04 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 35 | 565272 | 20010507 | 20 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM CASE METER | 1 | 0 | 175 | SPRAQUE | 1982 | 1982 | ABOVE GROUND |  | LOUIS JEN KINS | 5055468848 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE RAN OVER GAS METER, ESCAPING GAS IGNITED.
2025-01-31 10:21 | NO | NO | 20010094 | 2001-05-22 | 30881 | GASCO DISTRIBUTION SYSTEMS, INC. | 130 FRALEY STREET | KANE | MCKEAN | PA | 1 6735 | 3 | NO | 2119 | 2001-05-01 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 0 | 564986 | 20010504 |  |  |  |  | NO DATA | ALL OTHER CAUSES | UNKNOWN | OTHER | CUSTOMER OWNED PIPING AND EQUIPMENT | OTHER | HOT WATER HEATER | OTHER | FLEX CONNECTOR |  |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | KENNETH D. MAGYAR | 7404546198 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE FIRE MARSHALL SAID THAT A FAULTY HOT WATER HEATER OVERHEATED, WHICH WAS THE CAUSE OF THE FIRE. THE FIRE MARSHALL SAID THERE WAS A SMALL LEAK AT THE WATER HEATER, WHERE THE FLEX CONNECTOR SCREWED INTO THE WATER HEATER CONTROL VALVE. THE FIRE MARSHALL SAID THAT LEAK WAS NOT THE CAUSE OF THE FIRE, BUT COULD HAVE HELPED FUELED THE FIRE.
2025-01-31 10:21 | YES | NO | 20010095 | 2001-05-21 | 12350 | MINNEGASCO INC | 10111 CEDAR LAKE ROAD | MINNETONKA | HENNEPIN | MN | 5 5305 |  | NO | 1431 | 2001-01-01 | 0 | 0 | 1000000 | 659777.0262 | 1593010.1466 | NO | 2 | 12 | 552356 | 20010101 | 10 | 15 |  |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  |  |  | cboSpec | CBOMANU | 0 | 0 | ABOVE GROUND |  | DENNIS HOMOLKA | 6128618689 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20010098 | 2001-05-24 | 12378 | MESA MUNICIPAL SYSTEM, CITY OF | ATTAWAY AND JUDD ROAD | QUEEN CREEK | PINAL | AZ | 8 5242 | 1 | NO | 1840 | 2001-03-14 | 0 | 0 | 0 | 0 | 0 | NO | 2 | 0 |  |  | 150 | 175 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 4 | 0.1 |  |  | 0 | 1948 | OTHER | FIELD PLOWING | MICHAEL R. COMSTOCK | 4806442490 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO | NO DATA |  | FARMER HIT THE 4" GAS MAIN WHILE PLOWING HIS FIELD TO PLANT CROPS. CITY OF MESA LINE MARKERS WERE IN PLACE
2025-01-31 10:21 | YES | NO | 20010099 | 2001-05-23 | 13782 | NORTHERN STATES POWER CO | 605 CARTER DRIVE | NORTHFIELD | RICE | MN | 5 5057 | 3 | NO | 1647 | 2001-04-24 | 0 | 0 | 250000 | 164944.2565 | 398252.5366 | NO | 0 | 53 |  | 20010425 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER |  | OTHER | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | BEN SHERMAN | 6512292354 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE SUSPECTED SOURCE OF THE GAS THAT CAUSED THE EXPLOSION IS A LEAK ON THE CUSTOMER OWNED GAS PIPING INSIDE THE HOUSE AT 605 CARTER DRIVE. THE HOUSE FIRE THAT FOLLOWED THE EXPLOSION MELTED THE SERVICE REGULATOR AND THE GAS METER. THE FIRE ALSO DAMAGED THE ANODELESS RISER AND MELTED THE GREASE IN THE SERVICE VALVE. BAR HOLE TESTING WAS PERFORMED AND NO GAS WAS FOUND IN THE GROUND. THE SERVICE LINE WAS PRESSURE TESTED FOLLOWING THE EXPLOSION AND THE SERVICE DID NOT LEAK. THE EXPLOSION AND FIRE IS UNDER INVESTIGATION BY THE STATE FIRE MARSHAL.
2025-01-31 10:21 | NO | NO | 20010100 | 2001-05-24 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 209 PIPERWOOD DRIVE | CARY | WAKE | NC | 2 7511 | 3 | NO | 1245 | 2001-05-02 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 38 | 564762 | 20010502 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTM D 2513 | DRISCOPIPE | 1990 | 1991 | UNDER GROUND OR UNDER WATER |  | JIMMY JONES | 9198362419 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | THIRD PARTY, CABLEVISION, IN PROCESS OF REPAIRING CABLE EXPOSED 3/4" PLASTIC SERVICE LINE. CABLEVISION REPAIRMAN MELTED PLASTIC SERVICE WITH A TORCH WHILE INSTALLING HEAT SHRINK SLEEVE ON CABLE SPLICE. REPAIRMAN WAS BURNED WHEN GAS IGNITED & WAS TAKEN TO HOSPITAL FOR FIRST AID & WAS RELEASED THE SAME DAY.
2025-01-31 10:21 | YES | NO | 20010101 | 2001-05-30 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 549 E. GIBSON | JASPER | JASPER | TX | 7 5951 | 3 | NO | 915 | 2001-04-25 | 0 | 0 | 115000 | 75874.358 | 183196.1669 | YES | 0 | 57 |  | 20010425 | 22 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | VALVE |  | STEEL |  |  |  |  | CBOMANU | 0 | 0 | ABOVE GROUND |  | ARTHUR E. JOHNSON | 4098607111 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE STRUCK GAS METER. IGNITION OCCURRED.
2025-01-31 10:21 | NO | NO | 20010103 | 2001-05-30 | 2596 | COLUMBIA GAS OF OHIO INC | STATE ROUTE 37 @ WARRENSBURG RD | DELAWARE | DELAWARE | OH | 4 3015 | 3 | NO | 1545 | 2001-04-25 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 5 | 26 |  | 20010425 | 42 | 48 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.491 | PE2406 | UPONOR | 1993 | 1994 | UNDER GROUND OR UNDER WATER |  | DONNA L. YOUNG | 6148182101 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-04-23 | YES | 3 | FLAGS, PAINT & WARNING TAPE | YES | NO DATA |  | THIRD PARTY CONTRACTOR ERRONEOUSLY STRUCK AND INITIALLY DAMAGED A "6 PLASTIC MEDIUM DENSITY PIPELINE OPERATING AT APPROXIMATELY 42 PSIG. COLUMBIA GAS OF OHIO, INC EMPLOYEES WERE ATTEMPTING TO MAKE REPAIRS ON DAMAGED LINE, WHEN UNKNOWN IGNITION SOURCE IGNITED GAS.
2025-01-31 10:21 | YES | NO | 20010104 | 2001-05-25 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 20230 PRINCE CREEK DR (WEST DIST) | KATY | HARRIS | TX | 7 7450 | 3 | NO | 1417 | 2001-05-02 | 0 | 0 | 200000 | 131955.4052 | 318602.0293 | NO | 2 | 54 | 564773 | 20010502 | 44 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE2306 | UNK | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | TAL R. CENTERS, JR | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-04-30 | YES | 3 | YELLOW PAINT | YES | NO DATA |  | THIRD PARTY DAMAGED A .75 INCH IP PLA. SERVICE LINE WITH A BORING TOOL AND ESCAPING GAS WAS IGNITED.
2025-01-31 10:21 | YES | YES | 20010105 | 2001-06-04 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | LOGAN PASS & PAHLMIER DRIVE | NEW BRAUNFELS | COMAL | TX | 7 8130 | 3 | NO | 1211 | 2001-05-19 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 56 | 566674 | 20010519 | 30 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | SDR 11 | DUPONT | 2000 | 2000 | UNDER GROUND OR UNDER WATER |  | EDWARD HORN | 8306436922 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR DAMAGED A 2" POLYETHYLENE GAS MAIN WHILE TRENCHING.
2025-01-31 10:21 | NO | NO | 20010106 | 2001-06-04 | 18484 | SOUTHERN CALIFORNIA GAS CO | 26623 MAY WAY | SANTA CLARITA | LOS ANGELES | CA |  | 1 | NO | 1115 | 2001-05-09 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 565500 | 20010509 |  |  | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | STEEL | [5 empty] | 0 | 0 | ABOVE GROUND |  | W.J. KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | DURING PLANNED BLOWDOWN TO TRANSMISSION LINE, ODORANT WAS SMELLED AT JR HIGH SCHOOL APPOXIMATE 11/2 AWAY. SCHOOL WAS EVACUATED, 9 STUDENTS AND 1 ADULT WERE TRANSPORTED TO HOSPITAL WITH NAUSEA AND DIZZINESS. ALL TREATED AND RELEASED. SCHOOL RE-OPENED.
2025-01-31 10:21 | NO | NO | 20010109 | 2001-06-11 | 18532 | SOUTHERN UNION GAS CO | 4525 SOUTH 2ND STREET | AUSTIN | TRAVIS | TX | 7 8745 | 3 | NO | 1848 | 2001-05-19 | 0 | 0 | 75000 | 49483.277 | 119475.761 | NO | 0 | 15 | 566695 | 20010519 | 40 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | API 5L B |  | 0 | 0 | ABOVE GROUND |  | JESSE C. WALLIS | 5123708212 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | UNOCCUPIED VEHICLE ROLLED DOWN HILL, OVER A CURB AND THROUGH RESIDENTIAL CARPORT STRIKING A RESIDENTIAL GAS METER SET AT THE STRUCTURE CAUSING LEAKAGE WHICH RESULTED IN A RESPONSE BY THE LOCAL FIRE DEPARTMENT. WHILE FIREFIGHTERS WERE ATTEMPTING TO SHUT OFF METER AT VALVE ON RISER THE GAS IGNITED CAUSING MAJOR DAMAGE TO STRUCTURE AND VEHICLE. IGNITION DID NOT CAUSE ANY INJURIES. FIRE WAS IMMEDIATELY EXTINGUISHED AND VALVE WAS THEN SHUT OFF STOPPING THE FLOW OF GAS.
2025-01-31 10:21 | NO | NO | 20010112 | 2001-06-19 | 31099 | BAGLEY NATURAL GAS, CITY OF | NW CORNER OD SUNSET US HIGHWAY 2 | BAGLEY | CLEARWATER | MN | 5 6621 |  | NO | 1640 | 2001-06-04 | 0 | 0 | 3000 | 1979.3311 | 4779.0304 | NO | 0 | 40 |  | 20010604 | 50 | 60 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.25 | ASTM-D2513 | PLEXCO | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | EARL A. HOLMSTROM | 2186942300 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | 2" BRANCH OFF OF A 4" MAIN. THE 4" MAIN WAS LOCATED, BUT THE 2" MAIN WAS NOT.
2025-01-31 10:21 | YES | NO | 20010113 | 2001-06-14 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 2210 BROOKS | HOUSTON | HARRIS | TX | 7 7026 | 3 | NO | 1936 | 2001-05-19 | 0 | 0 | 1500000 | 989665.5393 | 2389515.2198 | NO | 2 | 46 |  | 20010519 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | RISER | DRIP/RISER |  | OTHER | VARIOUS | 1 | 0.075 | ASTM | UNK | 0 | 1986 | UNDER GROUND OR UNDER WATER |  | TAL R. CENTERS | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | AN EMPTY WAREHOUSE ON FIRE, WALL COLLAPSED ON VACANT RISER AND ESCAPING GAS WAS IGNITED.
2025-01-31 10:21 | YES | NO | 20010115 | 2001-06-25 | 14210 | OKLAHOMA NATURAL GAS CO | BETWEEN SW 4TH & SW 5TH MAY AVE | OKLAHOMA CITY | OKLAHOMA | OK | 73108- | 3 | NO | 1534 | 2001-05-25 | 0 | 0 | 125000 | 82472.1283 | 199126.2683 | NO | 6 | 48 | 567352 | 20010525 | 48 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.312 | SMIS GR B |  | 0 | 1956 | UNDER GROUND OR UNDER WATER |  | WAYNE WILLIAMS, ENGINEER III | 4055566409 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-05-21 | YES | 0 |  | YES | NO DATA |  | THIRD PARTY CONTRACTOR HIT A 12" MP MAIN IN THE NORTH CANADIAN RIVER.
2025-01-31 10:21 | NO | NO | 20010116 | 2001-06-25 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | BOX 307 FRONT STREET | FREDRICKTOWN | WASHINGTON | PA | 1 5333 | 1 | NO | 815 | 2001-06-04 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 20010608 | 34 | 38 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 2 |  |  |  | 0 | 0 | UNDER PAVEMENT |  | TRACEY L FAULK, COMPLIANCE SPECIALIST | 7245273960 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | Null | 0 |  | YES | NO DATA |  | CONTRACTOR WAS MAKING REPAIRS TO NEWLY INSTALLED SEWER SYSTEM WHEN THEY HIT A MEDIUM PRESSURE TAP ON A 2" STEEL MAIN. GAS ENTERED HOME AT BOX 307 FRONT STREET AND IS THOUGHT TO HAVE IGNITED AT A SPACE HEATER IN THE BASEMENT. ELDERLY RESIDENT WAS ASSISTED OUT OF THE RESIDENCE BY CREWS ON SITE AND FIRE WAS EXTINGUISHED BY COLUMBIA GS CREW ON SITE. RESIDENT WAS TAKEN TO A FAMILY MEMBERS HOME FROM THE SCENE. COLUMBIA GAS OUTREACH DEPARTMENT CONTACTED FAMILY MEMBER ON JUNE 5TH AND WAS INFORMED THAT CUSTOMER HAD BEEN TAKEN TO THE HOSPITAL BY FAMILY MEMBERS ON JUNE 4TH AND HAD BEEN ADMITTED. THE FAMILY MEMBER STATED THAT THE CUSTOMER HAS ON-GOING MEDICAL PROBLEMS.
2025-01-31 10:21 | YES | NO | 20010121 | 2001-06-27 | 4472 | KINDER MORGAN ENERGY PARTNERS, L.P. | STATE HIGHWAY 82 & BALTIC AVENUE | ASPEN | PITKIN | CO | 8 1611 | 3 | NO | 1436 | 2001-05-21 | 0 | 0 | 80000 | 52782.1621 | 127440.8117 | NO | 1 | 30 | 566862 | 20010521 | 266 | 550 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.156 | X-42 |  | 0 | 1960 | UNDER GROUND OR UNDER WATER |  | BERNADETTE M FRIEH | 3039147829 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | THE CONTRACTOR HAS BEEN WORKING FOR OVER A YEAR IN THE AREA., PARALLELING THE PIPELINE, CONSTRUCTING A NEW HIGHWAY. THE CONTRACTOR CALLED IN TO REQUEST A LOCATE, AND A LOCATE WAS PROVIDED. A POTHOLE, WHICH WAS NOT DUG DEEP ENOUGH BY THIS CONTRACTOR, DID NOT LOCATE THE LINE, AND THE LINE WAS HIT.
2025-01-31 10:21 | YES | YES | 20010122 | 2001-07-03 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 1034 HICKOX STREET | SANTA FE | SANTA FE | NM | 8 7501 | 3 | NO | 1400 | 2001-05-30 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 10 | 567778 | 20010530 | 0 | 0 |  |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | SPARKS OCCURED IN GASEOUS ATMOSPHERE | STEEL |  | 1.25 | 0.14 | UNKNOWN | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LARRY K. HUTCHINSON | 5052414578 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | OTHER | SEE ATTACHMENT | ON MAY 30, 2001 A CREW FROM J & D CONTRUCTION WAS RETIRING A SERVICE LINE LOCATED AT 1034 HICKOX STREET IN SANTA FE, NEW MEXICO. AT APPROXIMATELY 2:00 PM A PNM EMPLOYEE AND TWO CONTRACTOR EMPLOYEES FROM J & D CONTRUCTION WERE BURNED. THE SERVICE LINE THEY WERE WORKING ON WAS CUT BUT THE PIPE WAS IN A BIND AND WOULD NOT SEPARATE SO AN EXPANSION PLUG COULD BE INSTALLED. THE THREE EMPLOYEES WERE BURNED WHEN GAS IGNITED DURING THE ATTEMPT TO SEPARATE THE CUT SERVICE LINE. ALL THREE EMPLOYEES WERE TRANSFERRED TO THE HOSPITAL WHERE THE PNM EMPLOYEE AND A J & D EMPLOYEE WERE ADMITTED FOR BURN TREATMENTS. THE OTHER J & D EMPLOYEE WAS NOT ADMITTED TO THE HOSPITAL BUT WAS GIVEN FIRST AID TREATMENT FOR HIS BURNS AND RELEASED.
2025-01-31 10:21 | NO | NO | 20010123 | 2001-07-03 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 5902 N HOUSTON ROSSLYN (NORTH) | HOUSTON | HARRIS | TX | 7 7092 | 3 | NO | 801 | 2001-06-04 | 0 | 0 | 7500 | 4948.3277 | 11947.5761 | YES | 12 | 0 |  | 20010604 | 78 | 160 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 | API 5L A | UNK. | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | TAL R. CENTERS, JR. | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-05-03 | YES | 3 | 2001-05-03 | YES | NO DATA |  | THIRD PARTY DAMAGED A 1 1/4" H.P. STL. SERVICELINE WITH A TRACKHOE WHILE INSTALLING SANITARY SEWER LINES.
2025-01-31 10:21 | NO | NO | 20010124 | 2001-07-03 | 1344 | BERKSHIRE GAS CO | EAST STREET | PITTSFIELD | BERKSHIRE | MA | 01201- | 3 | NO | 1050 | 2001-06-03 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 | 568206 | 20010603 | 30 | 12 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR PIT | REGULATOR/METER |  | OTHER | NA | 0 | 0 | NA | FISHER | 1973 | 1973 | UNDER GROUND OR UNDER WATER |  | RICHARD E. NASMAN | 4134450303 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE FOLLOWING PRESENTS INFORMATION RELATED TO THE RECENT INCIDENT EXPERIENCE BY THE BERKSHIRE GAS COMPANY ("BERKSHIRE") WITH REGARDS TO THE OVER-PRESSURIZATION OF ITS PITTSFIELD LOW PRESSURE DISTRIBUTION SYSTEM ON SUNDAY, JUNE 3, 2001. BASED ON BERKSHIRES ANALYSIS, THE OVERPRESSURE OF THE PITTSFIELD LOW-PRESSURE SYSTEM WAS CAUSED BY FLOODING OF THE EAST STREET REGULATOR PIT CREATED WHEN A GENERAL CONTRACTORS SITE DRAINAGE CONTROL MEASURES IN THE AREA OF THE REGULATOR PIT PREVENTED PROPER DRAINAGE AND SUBSEQUENT LOW-PRESSURE SYSTEM. THE COMPANY, IN-CONJUNCTION WITH THE STREET RECONSTRUCTION PROJECT, IS PRESENTLY INSTALLING NEW REGULATOR PITS TO REPLACE THIS PIT. THE EAST STREET LOW-PRESSURE REGULATOR STATION CONSISTS OF TWO (2) FISHER 298 TEK REGULATORS CONFIGURED IN A WORKING MONITOR CONFIGURATION. THE PIT WAS ORIGINALLY EQUIPPED WITH TWO 8" VENT STACKS FOR VAULT VENTILATION. THREE (3) FISHER 61H PILOTS ARE USED IN THIS CONFIGURATION WITH THE OVERRIDE PILOT VENT LINE VENTED IN ONE OF THE 8" VENT STACKS. THE VENT LINES FOR THE PILOTS WERE RUN TO THE TOP OF THE REGULATOR VAULT AND "CANDY CANED" OVER. THE FIRST STAGE REGULATION REDUCES PRESSURES FROM 100 PSIG TO 10 PSIG. THE SECOND STAGE REGULATION REDUCES THE 10 PSIG TO 12" WC (WATER COLUMN). DUE TO MAJOR ROAD RECONSTRUCTION IN THE AREA OF THE REGULATOR PIT AND THE RELOCATION OF THE ROADWAY, THE REMOVAL OF THE EXISTING VENT STACK WAS NECESSARY TO ACCOMMODATE THIS CONSTRUCTION. BASED ON OUR EXPERIENCE OF WATER/DRAINAGE CONDITIONS IN THE AREA, THE COMPANY RE-VENTED THE EXISTING OVERRIDE PILOT INSIDE OF THE REGULATOR PIT BASED ON PREVIOUS KNOWLEDGE THAT THE PIT HAS NOT HAD WATER PROBLEMS AND THAT THIS VENTING MODIFICATION WAS ONLY A TEMPORARY CONDITION UNTIL THE NEW PIT WAS ACTIVATED. ON SUNDAY JUNE 3, THE PITTSFIELD AREA EXPERIENCED A RAINFALL EVENT IN WHICH RAINFALL IN THE AREA OF THE REGULATOR PIT WAS NOT ABLE TO DRAIN PROPERLY INTO THE CATCH BASINS DUE TO THE RESTRICTION CAUSED BY HAY BAILS SURROUNDING THE CATCH BASIN.THIS SITUATION CAUSED FLOODING IN THE AREA OF THIS REGULATOR PIT. THE FLOODING WAS SUCH THAT WATER ENTERED THE REGULATOR PIT AND ENTERED THE RELOCATED OVERRIDE PILOT VENT LINES AND CAUSED THE REGULATORS TO FAIL. THE ROAD CONSTRUCTION CONTRACTOR COINCIDENTALLY WAS ON-SITE TO RECTIFY THE DRAINAGE PROBLEM AND HAD BEEN CONTACTED BY LOCAL AUTHORITIES BECAUSE OF THE FLOODING THEY WERE CAUSING. THE CONTRACTOR REMOVED THE HAY BAILS AND THE DRAINAGE SYSTEM IMMEDIATELY REMOVED THE FLOODING CONDITION, WHICH ALLOWED BERKSHIRE GAS OPERATIONS STAFF TO GAIN ACCESS TO THE REGULATOR PIT AND REMOVE WATER IN THE PIT. WHEN THE WATER ENTERED THE VAULT. THE WATER PRESSURE FILLED THE PILOT VENT PIPING, AND CHANGED THE SETTINGS OF THE PILOT DUE TO THE WATER PRESSURE. WHEN THE VAULT WAS PUMPED THE SPRING PRESSURE OF THE PILOT PUSHED THE WATER OUT OF THE VENT LINES AND THE PIT RETURNED TO NORMAL OPERATION. AT NO TIME DID ANY WATER ACTUALLY GET INTO THE PILOTS OR REGULATORS. THE REGULATOR PIT WAS THEN RETURNED TO SERVICE AND IMMEDIATELY BROUGHT SYSTEM PRESSURES BACK TO NORMAL OPERATING PRESSURES. BASED ON THE TIMING OF EVENTS IT BELIEVED THE OVERPRESSURIZATION OCCURRED FOR APPROXIMATELY 1.5 HOURS. UPON IDENTIFICATION OF THE INCIDENT, THROUGH THE INITIATION OF SYSTEM ALARMS BEGINNING AT 10:50AM AND ASSESSMENT OF CONDITIONS, BERKSHIRE IMPLEMENTED ITS EMERGENCY RESPONSE PROCEDURES WHICH INCLUDED THE INVESTIGATION OF NUMEROUS LOCATIONS TO IDENTIFY WHETHER THE SITUATION HAD IMPACTS TO BERKSHIRE DISTRIBUTION SYSTEM OR CUSTOMER SERVICES. BASED ON THE EFFORTS CONDUCTED BY BERKSHIRE IMMEDIATELY FOLLOWING THE INCIDENT (WHICH INVOLVED INSPECTING OVER 2000 SERVICE LOCATIONS OVER APPROXIMATELY A 28 HOUR PERIOD) IT WAS DETERMINED THAT THE OVER-PRESSURIZATION EVENT DID NOT IMPACT THE DISTRIBUTION SYSTEM INTERGRITY OR CUSTOMER SERVICES. AS A RESULT OF THIS INCIDENT THE COMPANY ISOLATED THIS REGULATOR PIT FROM THE SYSTEM THE FOLLOWING DAY SO AS TO PREVENT ITS REOCCURRENCE. WHEN THE NEW REGULATOR PIT IS ACT
2025-01-31 10:21 | YES | NO | 20010125 | 2001-07-05 | 18536 | SOUTHWEST GAS CORP | ON RUSSELL ROAD WEST OF WARBONNET WAY | LAS VEGAS | CLARK | NV | 8 9147 | 3 | NO | 1048 | 2001-06-07 | 0 | 0 | 489169 | 322742.4681 | 779251.1804 | NO | 1 | 13 |  | 20010607 | 55 | 60 | BY TEST | 98 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.507 | 0.414 | DRISCOPE M8000 | CHEVRON PHILLIPS CHEMICAL CO | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | TOM CARDIN | 7023652008 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-05-22 | YES | 0 |  | YES | NO DATA |  | WHILE AN OPERATOR FOR R.P. WEDDELL & SONS WAS TRENCHING FOR SEWER IMPROVEMENTS, HE STRUCK AND DAMAGED A 4" P.E. GAS MAIN. THE CONTRACTOR HAD A CURRENT USA ONE-CALL TICKET, BUT THE LOCATE WAS INCORRECT. THE INCIDENT RESULTED IN 2,568 THERMS OF LOST GAS AND AN OUTAGE TO 518 CUSTOMERS. THERE WAS IGNITION OF GAS, WHICH DAMAGED THE TRENCHER. THERE WERE NO INJURIES AS A RESULT OF THE INCIDENT.
2025-01-31 10:21 | NO | NO | 20010126 | 2001-07-12 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 11031 HOUSTON DR. (BAYPORTE) | LAPORTE | HARRIS | TX | 7 7571 | 3 | NO | 230 | 2001-06-04 | 0 | 0 | 60000 | 39586.6216 | 95580.6088 | YES | 2 | 20 | 568215 | 20010604 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | VARIOUS |  |  |  |  | 0 | 0 | ABOVE GROUND |  | TAL R. CENTERS | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | A CARPORT STRUCTURE COLLAPSED DUE TO FIRE, DAMAGING METER SET ASSEMBLY AND ESCAPING GAS WAS IGNITED.
2025-01-31 10:21 | NO | NO | 20010127 | 2001-07-10 | 11032 | LACLEDE GAS CO | INTERSTATE 270 AND MANCHESTER ROAD | DES PERES | ST LOUIS | MO | 6 3131 | 3 | NO | 1100 | 2001-05-29 | 0 | 0 | 49000 | 32329.0743 | 78057.4972 | NO | 1 | 45 | 567619 | 20010529 | 157 | 300 | BY TEST | 475 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 16 | 0.249 | API 5LX X42 | KAISER STEEL CO. | 1962 | 1963 | UNDER GROUND OR UNDER WATER |  | PAUL B. HUNKER, JR. | 3143420528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 |  | YES | NO DATA |  | WHILE ATTEMPTING TO MOVE AND SCOOP EARTH FROM OVER THE STEEL GAS PIPELINE WHICH WAS MARKED FOR ANOTHER CONTRACTOR, THE DAMAGING CONTRACTOR STRUCK THE MAIN WITH A BUCKET TOOTH FROM A HI-LIFT DOZER (CAT963C). NO ATTEMPT WAS MADE BY THE CONTRACTOR TO EXPOSE THE PIPELINE AND DETERMINE ITS DEPTH OF COVER AT THE POINT OF DAMAGE PRIOR TO THE INCIDENT. THE CONTRACTOR DID NOT NOTIFY LACLEDE GAS COMPANY OR MISSOURI ONE-CALL OF ITS INTENT TO EXCAVATE AT THE POINT OF DAMAGE PRIOR TO THE INCIDENT.
2025-01-31 10:21 | YES | YES | 20010128 | 2001-07-06 | 5580 | FRANNIE - DEAVER UTILITIES | 166 RD 3 N | DEAVER | PARK | WY | 8 2421 | 1 | NO | 230 | 2001-06-25 | 2 | 1 | 40000 | 26391.081 | 63720.4059 | NO | 0 | 15 |  | 20010625 | 56 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 1985 | WITHIN/UNDER BUILDING |  | BRYAN LEE | 3076642221 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HIGH WINDS CAUSED A LIMB TO FALL SOME 20 TO 30 FEET AND STRUCK THE SPRING HOUSING OF THE GAS REGULATOR AND SHEARED IT OFF. THE REGULATOR FAILED IN THE OPEN POSITION AND GAS ENTERED THE HOUSE THROUGH THE GAS PIPING. THE PILOT LIGHT WAS SNUFFED OUT WHEN THE PRESSURE INCREASED FROM 4 OUNCES TO CLOSE TO THE LINE PRESSURE OF 56 PSI. THE GAS AIR MIXTURE WAS IGNITED AND THE HOUSE WAS DESTROYED.
2025-01-31 10:21 | NO | NO | 20010133 | 2001-07-16 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 5730 GRIGGS RD @LONG DR (SOUTH DIST) | HOUSTON | HARRIS | TX | 7 7021 | 3 | NO | 355 | 2001-06-15 | 0 | 0 | 58000 | 38267.0675 | 92394.5885 | YES | 5 | 30 | 571600 | 20010615 | 42 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | API 5L A | UNK | 0 | 1979 | ABOVE GROUND |  | TAL R. CENTERS, JR. | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | Null | NO DATA |  | THIRD PARTY DAMAGED A 4" I.P./ STEEL RELIEF VALVE STACK WITH HIS TRUCK.
2025-01-31 10:21 | NO | NO | 20010134 | 2001-07-17 | 3190 | DEFUNIAK SPRINGS NATURAL GAS SYSTEM, CITY OF | 54 MINNESOTA | DEFUNIAK SPRINGS | WALTON | FL | 3 2435 | 2 | NO | 1100 | 2001-06-21 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 1 | 570363 | 20010621 |  | 20 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 |  | UNK | UNK | 0 | 0 | UNDER PAVEMENT |  | JOHN V. RAUCH | 8508928503 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE INCIDENT OCCURRED DURING THE SECOND CUT TO REMOVE A ONE FOOT SECTION OF AN EXISTING 3/4" GALVANIZED GAS SERVICE LINE. THE BELL HOLE HAD BEEN EVACUATED AND THE GAS LINE TAP HAD BEEN CLOSED AND JUMPER CABLES HAD BEEN INSTALLED SPANNING THE AERA TO BE CUT. RONALD MCLENDON WAS IN THE BELL HOLE.HE WAS WEARING PROTECT GOGGLES, HIS WORK SHIRT, PANTS, BOOTS AND GLOVES. A FIRE EXTINGUISHER WAS PROPERLY SIGHTED AND MANNED. RONALD COMPLETE THE FIRST CUT USING A RECIPROCATING SAW WITHOUT INCIDENT. DURING THE SECOND CUT, APPROXIMATELY ONE FOOT CLOSER TO THE TAP THERE WAS A SHORT DURATION FLASH FIRE. RONALD WAS BURNED ON HIS ARMS AND HIS FACE. RONALD WENT TO THE TRUCK AND IMMEDIATELY FLUSHED THE AREA WITH COLD WATER. DUE TO THE NATURE OF THE BURNS HE WAS TRANSPORTED TO THE LOCAL EMERGENCY ROOM. DIAGNOSIS WAS FIRST-DEGREE BURNS ON HIS ARMS AND THE EXPOSED AREAS OF HIS FACE. HE WAS TREATED AND RELEASED. THE CREW ON SIGHT CONFIRMED THERE WAS NO RESIDUAL FIRE AND THAT THE COUPON ON THE TAP WAS FULLY CLOSED. THE CREW COMPLETED INSERTING THE LINES THAT HAD BEEN CUT AND CLOSED UP THE BELL HOLES AND THEN SWITCHED TO REPARING ASPHALT.
2025-01-31 10:21 | YES | YES | 20010135 | 2001-07-12 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 2101 1ST AVENUE | RICHMOND |  | VA | 2 3222 | 1 | NO | 1543 | 2001-06-18 | 1 | 1 | 0 | 0 | 0 | NO | 0 | 25 | 569959 | 20010618 | 8 | 8 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | OTHER | COPPER | 1.25 |  | STANDARD | CBOMANU | 0 | 0 | WITHIN/UNDER BUILDING |  | J.C. STAFFORD, SR | 8046468350 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | VACATED HOUSE (BOARDED UP) VANDALIZED BY REMOVING APPROXIMATELY 20 FEET OF 1 1/4" COPPER SERVICE LINE CAUSING GAS RELEASE IN CRAWL SPACE.
2025-01-31 10:21 | YES | NO | 20010136 | 2001-07-23 | 18536 | SOUTHWEST GAS CORP | 2938 E. PRESIDIO ROAD | TUCSON | PIMA | AZ | 8 5712 | 3 | NO | 2332 | 2001-07-04 | 0 | 0 | 85000 | 56081.0472 | 135405.8625 | NO | 1 | 59 | 571839 | 20010705 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTM 2513 | DUPONT | 1971 | 1971 | UNDER GROUND OR UNDER WATER |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | SOUTHWEST GAS WAS NOTIFIED OF A FIRE AT 2938 E. PRESIDIO ROAD AT 2332 HOURS ON JULY 4, 2001. ONCE THE FIRE WAS EXTINGUISHED, NATURAL GAS LEAKAGE WAS DETECTED. THE LEAKING GAS WAS SHUT DOWN AT 0131 HOURS ON JULY 5 BY SQUEEZING THE SERVICE AT THE PROPERTY LINE. FURTHER INVESTIGATION AND EXCAVATION DETERMINED THAT A TREE ROOT HAD DAMAGED A 3/4" DUPONT ALDYL A POLYETHYLENE SERVICE LINE. AS A RESULT OF THIS DAMAGE, NATURAL GAS MIGRATED INTO THE BUILDING AND IGNITED. APPROXIMATELY 40 PEOPLE WERE EVACUATED DURING THE FIRE. THERE WERE NO INJURIES OR FATALITIES. THE ESTIMATED PROPERTY DAMAGE IS $85,000.
2025-01-31 10:21 | NO | NO | 20010137 | 2001-07-20 | 8040 | ILLINOIS POWER CO | 1131 AND 1135 GRAND AVE. | GALESBURG | KNOX | IL | 6 1401 | 3 | NO | 1005 | 2001-06-22 | 0 | 0 | 65000 | 42885.5067 | 103545.6595 | NO | 0 | 37 | 570818 | 20010622 | 50 | 60 | BY CFR 192.619(A)(3) |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | OTHER | X-PANDER PLUG | STEEL |  | 0.75 | 0.154 | API 5L A |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | D.R. JOHNSON | 2174247001 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON JUNE 22, 2001, A TWO-MAN GAS CREW WAS REPLACING THE RISER AT 1135 GRAND AVENUE IN GALESBURG, ILLINOIS. THIS WORK WAS BEING DONE DUE TO A COMPRESSION FITTING FOUND BELOW GROUND AT THE RISER. THE SERVICE HAD BEEN EXPOSED BETWEEN 1131 AND 1135 GRAND AVENUE BECAUSE THIS WAS A SPLIT SERVICE (TWO SERVICES SERVED FROM A COMMON SERVICE LINE) COMING UP BETWEEN THE TWO HOUSES UNDER THE DRIVEWAY. THE SERVICE TAP WAS UNDER THE MIDDLE OF THE CONCRETE DRIVEWAY. AFTER A DISCUSSION OF THE JOB, CREW MEMBERS DECIDED TO CUT THE 3/4" STEEL SERVICE, THREAD AN ADAPTER ON, AND INSTALL A PLASTIC STUB AND RISER. THE 3/4" STEEL SERVICE WAS OPERATING AT ROUND 50 PSI. THE 3/4" STEEL SERVICE WAS CUT, AND AN X-PANDER PLUG WAS INSTALLED. THE LINE WAS THEN THREADED IN PREPARATION FOR THE INSTALLATION OF THE ADAPTER. THE X-PANDER PLUG HAD BEEN INSTALLED FOR ABOUT 20-30 MINUTES AT THIS TIME. AS THE CREW LEADER GOT INTO POSITION AND INSTALLED THE TOOL TO PULL THE X-PANDER PLUG, THE PLUG BLEW OUT OF THE 3/4" PIPE. IT IMMEDIATELY IGNITED FROM AN UNKNOWN SOURCE. IT IS SPECULATED THAT THE IGNITION WAS CAUSED BY STATIC ELECTRICITY.
2025-01-31 10:21 | YES | NO | 20010139 | 2001-07-27 | 792 | ATLANTA GAS LIGHT CO | 1000 WHITLOCK AVE #100 | MARIETTA | COBB | GA | 3 0060 | 3 | NO | 740 | 2001-06-27 | 0 | 0 | 200000 | 131955.4052 | 318602.0293 | NO | 0 | 46 | 571036 | 20010627 | 60 | 60 | BY TEST | 135 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL | [5 empty] | 0 | 1995 | ABOVE GROUND |  | PHYLLIS W STALLINGS | 7704235720 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | DRIVER OF A PASSENGER VEHICLE LOST CONTROL, JUMPED A CURB AND STRUCK GAS METER SET. THIS CAUSED THE 1 1/4" NIPPLE TO CRACK BELOW THE PRIMARY REGULATOR. THE ESCAPING GAS IGNITED CAUSING DAMAGE TO AUTOMOBILE AND THREE BUSINESSES. THE DRIVER OF THE VEHICLE WAS TAKEN TO THE HOSPITAL FOR TREATMENT AND RELEASED.
2025-01-31 10:21 | YES | NO | 20010140 | 2001-07-30 | 13660 | NORTH SHORE GAS CO | 5660 OAKWOOD | LONG GROVE | LAKE | IL |  | 3 | NO | 430 | 2001-07-07 | 0 | 0 | 500000 | 329888.5131 | 796505.0733 | NO | 1 | 30 |  | 20010707 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL | [5 empty] | 0 | 0 | ABOVE GROUND |  | JOHN KLECZYNSKI, MANAGER | 8472634611 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | LIGHTNING STREAK THE ROOF OF A HOME AND CAUSED A FIRE THAT DAMAGED NORTH SHORES METER SET.
2025-01-31 10:21 | NO | NO | 20010141 | 2001-08-03 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 4555 LUCERNE AVENUE | PITTSBURGH | ALLEGHENY | PA |  | 2 | Null | 1615 | 2001-07-09 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 15 |  | 20010709 | 0.25 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | PRIVATE WELL | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | TRACEY L. FAULK | 7245273960 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | INITIAL INVESTIGATION SHOWED METHANE ACCUMULATION IN A WATER WELL LOCATED IN THE BASEMENT. IGNITION OCCURED WHEN PUMP RELAY ENERGIZED CAUSING AN EXPLOSION.
2025-01-31 10:21 | NO | NO | 20010143 | 2001-08-13 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 4015 WILMER | HOUSTON | HARRIS | TX | 77003- | 3 | NO | 1518 | 2001-07-12 | 0 | 0 | 70000 | 46184.3918 | 111510.7103 | YES | 0 | 24 | 572771 | 20010712 | 38 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | VARIOUS |  |  |  |  | 0 | 1991 | ABOVE GROUND |  | TAL R CENTERS | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | GARAGE FIRE SPREAD TO HOUSE AND HEAT MELTED INSULATING BUSHING ON METER SET ASSEMBLY AND ESCAPING GAS WAS IGNITED.
2025-01-31 10:21 | YES | YES | 20010144 | 2001-08-17 | 621 | ARKANSAS OKLAHOMA GAS CORP | 3508 MAY BRANCH LANE | FORT SMITH | SEBASTIAN | AR | 7 1917 | 3 | NO | 1522 | 2001-07-30 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 38 | 574827 | 20010730 | 25 | 50 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 11 | ASTMD251 | DUPONT | 1974 | 1974 | UNDER GROUND OR UNDER WATER |  | DAN DEHART | 5017833181 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-07-18 | YES | 3 | 2001-07-18 | YES | NO DATA |  | OPERATORS 2" PLASTIC MAIN STRUCK BY TV CABLE CREW. MAIN HAD BEEN PROPERLY MARKED IN ADVANCE. GAS WAS IGNITED AT SITE OF BREAK BY UNKNOWN CAUSE RESULTING IN OVERNIGHT HOSPITALIZATION OF ONE OF OPERATORS EMPLOYEES
2025-01-31 10:21 | NO | NO | 20010145 | 2001-08-20 | 12690 | MONTANA POWER CO | 2 DAVIDISON STREET | ABSAROKEE | STILLWATER | MT | 59001- | 3 | NO | 900 | 2001-07-21 | 0 | 0 | 70000 | 46184.3918 | 111510.7103 | NO | 1 | 42 | 573817 | 20011211 | 20 | 22 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 |  | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | COREY HALVORSON | 4067512204 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-07-01 | YES | 3 | PAINT | YES | NO DATA |  | PIPELINE EXPERIENCED A SHEARING STRESS FROM EARTH MOVEMENT WHICH RESULTING FROM OUTSIDE CONTRACTOR EXCAVATION TAKING PLACE NEXT TO GAS MAIN.
2025-01-31 10:21 | YES | YES | 20010149 | 2001-08-21 | 630 | ARKANSAS WESTERN GAS CO | HWY 72 WEST @ EIGHTH STREET | GRAVETTE | BENTON | AR | 72736- | 3 | NO | 1100 | 2001-08-15 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 30 | 576640 | 20010815 | 37 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | D-2513 | UPONOR-ALDYL | 1983 | 1983 | UNDER GROUND OR UNDER WATER |  | MICHAEL Z HAYS | 5015828260 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-08-09 | YES | 3 | PAINT | YES | NO DATA |  | PRIVATE CONTRACTOR WAS EXPOSING 2" PLASTIC GAS MAIN WITH BACKHOE AND STRUCK TOP OF MAIN CAUSING A RELEASE OF GAS. COMPANY CREW RESPONSED TO MAKE REPAIRS ON MAIN (HAD TWO-WAY FEED). ONE SIDE WAS SQUEEZED OFF - SECOND SIDE IGNITED AT SQUEEZE OFF ATTEMPT BURNING ONE COMPANY EMPLOYEE REQUIRING OVERNIGHT STAY IN LOCAL HOSPITAL FOR OBSERVATION.
2025-01-31 10:21 | NO | NO | 20010152 | 2001-09-04 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 3205 DARLING | PASADENA | HARRIS | TX | 77503- | 3 | NO | 1035 | 2001-08-16 | 0 | 0 | 70000 | 46184.3918 | 111510.7103 | NO | 0 | 45 | 576736 | 20010816 | 40 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER |  |  |  |  | VARIOUS | 0 | 1997 | ABOVE GROUND |  | TAL R. CENTERS JR. | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A FIRE WHICH ORIGINATED INSIDE A GARAGE SPREAD TO AND DAMAGED A METER SET ASSEMBLY. THE ESCAPING GAS WAS IGNITED.
2025-01-31 10:21 | NO | NO | 20010153 | 2001-09-05 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | BRETON & HALL | EAST GRAND RAPIDS | KENT | MI | 4 9506 | 3 | NO | 1429 | 2001-07-24 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 2 | 574130 | 20010724 | 150 |  |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | PRESSURE TEST VALVE FITTING | NO DATA |  | STEEL |  | 0.75 | 0.154 |  |  | 0 | 0 | UNDER PAVEMENT |  | LARRY K. CROWDER | 3135777024 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-07-24 | NO | 0 |  | YES | NO DATA |  | EXCAVATING CONTRACTOR DAMAGED VAULT AND FALLING CONCRETE BROKE FITTING FOR PRESSURE TEST VALVE.
2025-01-31 10:21 | YES | NO | 20010156 | 2001-09-06 | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 13 FRYBURG ROAD | OIL CITY | VENANGO | PA | 16301- | 2 | NO | 1638 | 2001-08-02 | 0 | 0 | 160000 | 105564.3242 | 254881.6234 | NO | 1 | 47 | 575238 | 20010802 | 42 | 47 | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | UNSPECIFIED CORROSION | MAIN |  | BODY OF PIPE |  | STEEL |  | 10 |  |  |  | 0 | 1918 | UNDER GROUND OR UNDER WATER |  | CONRD L DONELSON | 8148718341 | NO DATA | LOCALIZED PITTING |  | GALVANIC |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | NATURAL GAS, LEAKING FROM A CORROSION PIT FAILURE IN A 10" GAS MAIN, MIGRATED INTO THE BASEMENT OF A RESIDENTIAL HOME. IGNITION OF THE SUBSEQUENT NATURAL GAS BUILDUP RESULTED IN A EXPLOSION AND FIRE.
2025-01-31 10:21 | YES | NO | 20010157 | 2001-09-13 | 12350 | MINNEGASCO INC | 7950 TIMBER LAKE DR | EDEN PRAIRE | HENNEPIN | MN | 55344- |  | NO | 1055 | 2001-08-18 | 0 | 0 | 400000 | 263910.8105 | 637204.0586 | NO | 3 | 0 | 577071 | 20010818 | 55 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC |  | 1.25 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DENNIS HOMOLKA | 6128618689 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CRACK IN 1 1/4" AA PLASTIC MAIN FOUND IN FRONT OF RESIDENCE. CAUSE OF EXPLOSION STILL UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 20010158 | 2001-09-13 | 603 | ARKLA, A NORAM ENERGY COMPANY | 5604 SUMMERHILL RD | TEXARKANA | BOWIE | TX | 7 5503 | 3 | NO | 130 | 2001-08-16 | 0 | 0 | 300 | 197.9331 | 477.903 | YES | 0 | 15 |  | 20010816 | 10 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | STEEL |  | 0.75 | 0.113 | ASTMD2513 | UPONOR | 1999 | 1999 | ABOVE GROUND |  | SCOTT E DOYLE | 5013774554 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | BRICK WALL OF COMMERICAL BUILDING FELL ON METER SET ASSEMBLY BREAKING RISER AT GROUND IGNITING GAS. ORIGIN OF FIRE UNRELATED TO NATURAL GAS.
2025-01-31 10:21 | NO | NO | 20010159 | 2001-09-13 | 4483 | ENSTAR NATURAL GAS CO | E STREET AND ALLEY BETWEEN 10TH AND 11TH | ANCHORAGE |  | AK | 9 9502 | 3 | NO | 2100 | 2001-08-20 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 2 | 26 | 577181 | 20010820 | 55 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT |  | STEEL |  | 6.625 | 0.188 |  |  | 1960 | 1961 | UNDER GROUND OR UNDER WATER |  | DAVID W. BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-08-13 | YES | 3 | 2001-08-13 | YES | NO DATA |  | ON MONDAY EVENING, AUGUST 20, 2001, AT 9:00 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY A CUSTOMER OF A GAS MAIN BLOWING AT THE CORNER OF E STREET AND THE ALLEY BETWEEN 10TH AND 11TH STREETS, IN ANCHORAGE, ALASKA. AN ENSTAR SERVICE TECHNICIAN WAS DISPATCHED TO THE SCENE. THE ANCHORAGE FIRE DEPARTMENT WAS ALSO NOTIFIED. THE ON-CALL SUPERVISOR AND DISTRIBUTION PERSONNEL WERE CALLED IN TO RESPOND. UPON ARRIVAL AT THE LOCATION OF THE GAS LEAK, THE SERVICE TECHNICIAN REPORTED FINDING A 6" STEEL MAIN PULLED OUT OF A DRESSER COUPLING AND GAS BLOWING AT 60 PSIG FROM BOTH ENDS OF THE MAINS. ADDITIONAL EMPLOYEES WERE CALLED IN INCLUDING THE VP OF OPERATIONS VP OF ENGINEERING AND THE DISTRIBUTION SUPERVISOR ALONG WITH ADDITIONAL DISTRIBUTION AND SERVICE EMPLOYEES. AT APPROXIMATELY 9:30 PM ENSTARS VP OF OPERATIONS ARRIVED AT THE LOCATION OF THE LEAK AND SET UP A COMMAND SITE WITH ENSTARS ON-CALL SUPERVISOR AND THE ANCHORAGE FIRE DEPARTMENT (AFD). AFD WAS IN THE PROCESS OF EVACUATING HOMES WITHIN A ONE-BLOCK RADIUS OF THE BLOWING GAS. TWO VALVES ON THE 6" MAIN NEEDED TO BE CLOSED AND A 4" HDPE MAIN NEEDED TO BE SQUEEZED OFF TO ISOLATE THE BLOWING GAS. AT 9:45 PM, AN ENSTAR CREW CLOSED ONE 6" VALVE TO ISOLATE THE BLOWING GAS FROM THE WEST SIDE OF THE BREAK. THE CREW THEN WENT TO THE 6" VALVE SEVERAL BLOCKS TO THE EAST. THEY OBTAINED UTILITY LOCATES ON THE BURIED VALVE. THE VALVE WAS EXCAVATED AND SHUT DOWN AT 11:08 PM. SIMULTANEOUSLY A SECOND CREW WORKED ON GETTING UTILITY LOCATES AND EXPOSING THE 4" HDPE MAIN. THE 4" MAIN WAS PINCHED OFF AT 11:26 PM TO STOP ALL BLOWING GAS. APPROXIMATELY 175 CUSTOMERS WERE LEFT WITHOUT NATURAL GAS SERVICE UNTIL REPAIRS WERE MADE. CREWS WORKED THROUGH THE NIGHT TO REPAIR THE 6" MAIN. THE MAIN WAS PUT BACK IN SERVICE AT APPROXIMATELY 7:00 AM, TUESDAY, AUGUST 21, 2001. GAS SERVICE TO THE AFFECTED CUSTOMERS WAS TURNED ON THROUGHOUT THAT DAY. UPON INVESTIGATION, IT WAS DISCOVERED THAT A CONTRACTOR, WHILE INSTALLING A CONCRETE ELECTRICAL DUCT BANK SYSTEM, HAD PARTIALLY AND/OR ENTIRELY EXPOSED ENSTARS 6" STEEL MAIN FOR APPROXIMATELY 150. THE 6" GAS MAIN WAS LEFT EXPOSED AND UNSUPPORTED IN THE SIDE BANK OF THE OPEN DITCH EXCAVATION. ENSTAR SUSPECTS VIBRATIONS FROM CONSTRUCTION EQUIPMENT AND COMPACTION EQUIPMENT CAUSED THE SIDES OF THE OPEN EXCAVATION TO SLOUGH AND MOVE THE GAS MAIN, CAUSING THE 6" GAS MAIN TO PULL OUT OF A 6" DRESSER COMPRESSION COUPLING LOCATED AT A 90 DEGREE ELL. ENSTAR HAD RECEIVED NO PRIOR NOTIFICATION FROM THE CONTRACTOR THAT THE MAIN WOULD BE EXPOSED OR A REQUEST FOR ASSISTANCE IN SUPPORTING THE 6" MAIN. THE CONTRACTOR DID NOT SUPPORT OR RESTRAIN THE 6" GAS MAIN. ENSTAR IS AGGRESSIVELY PURSUING REIMBURSEMENT FROM THE CONTRACTOR FOR ALL COSTS ASSOCIATED WITH REPAIRS.
2025-01-31 10:21 | NO | NO | 20010163 | 2001-09-19 | 4483 | ENSTAR NATURAL GAS CO | 3830 N GREENTREE ST | MATANUSKA | SUSITNA | AK | 99654- | 2 | NO | 215 | 2001-09-10 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 56 | 579337 | 20010910 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1989 | 1989 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON MONDAY MORNING, SEPTEMBER 13, 2001, AT APPROXIMATELY 2:15 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE MATANUSKA VALLEY FIRE DEPARTMENT OF A FIRE AT 3830 N GREENTREE ST NORTHEAST OF WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENCE. UPON ARRIVAL THE SERVICEMAN FOUND A SINGLE FAMILY HOME ON FIRE. HEART FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AT 3:11 AM AST. THE CAUSE OF THE FIRE IS UNDER INVESTIGATION BUT ACCORDING TO FIRE CHIEF KRILL, NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20010164 | 2001-08-30 | 18536 | SOUTHWEST GAS CORP | 521 - 523 1/2 S ORANGE AVENUE | YUMA | YUMA | AZ | 85364- | 3 | NO | 1157 | 2001-08-30 | 0 | 0 | 269000 | 177480.02 | 428519.7294 | NO | 1 | 41 | 578342 | 20010830 | 29 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.235 | ASTM A-105 | MUELLER | 1984 | 1984 | UNDER GROUND OR UNDER WATER |  | RANDY J SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES | 2001-08-06 | YES | 3 | PAINT | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20010168 | 2001-08-30 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 7501 LINNETT ROAD | WENDELL | WAKE | NC | 27591- | 3 | NO | 1058 | 2001-08-25 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 0 | 32 | 577872 | 20010827 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | 3/4" X 6" BLACK STEEL NIPPLE | STEEL |  | 0.75 | 0.113 | ASTM-A-53 |  | 0 | 1998 | ABOVE GROUND |  | GLENN FLOWERS | 9198362416 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | HOME OWNER HIT GAS METER WITH RIDING MOWER.
2025-01-31 10:21 | NO | NO | 20010172 | 2001-09-27 | 31202 | RELIANT ENERGY FIELD SERVICES CORP | BOX 91, COLLINS ST | NAPLES | MORRIS | TX | 7 5568 | 1 | NO | 1356 | 2001-08-17 | 0 | 0 | 500 | 329.8885 | 796.5051 | NO | 0 | 40 |  | 20010817 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 |  | D2513 |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | TY SCHLOSSER | 9035720551 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | LIGHTNING STRUCK TREE AND TRAVELED THROUGH ROOTS TO BURN HOLE IN GAS SERVICE LINE.
2025-01-31 10:21 | YES | YES | 20010173 | 2001-10-02 | 13710 | NORTHERN ILLINOIS GAS CO | WHEELER ROAD, 400' N. OF RTE 75 | DURAND | WINNEBAGO | IL | 6 1024 | 1 | NO | 1130 | 2001-08-29 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 578348 | 20010829 | 230 | 230 | BY TEST | 345 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | ABOVE GROUND |  | LETICIA QUEZADA | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | LAWN MOWER HIT FARM TAP (1ST STAGE REGULATOR). 1" HIGH-PRESSURE VALVE WAS BROKEN OFF THE RISER. NATURAL GAS IGNITED AND COUNTY WORKER WAS BURNED OVER 20% OF BODY.
2025-01-31 10:21 | YES | NO | 20010175 | 2001-10-15 | 11720 | KEYSPAN ENERGY CORP | SHORE ROAD | GLENWOOD LANDING |  | NY | 11547 |  | NO | 1416 | 2001-09-06 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 0 | 17 | 579029 | 20010906 | 60 |  |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | NO DATA |  | R. VERDERAME | 5165454047 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20010176 | 2001-10-10 | 22182 | WASHINGTON GAS LIGHT CO | 9432 WHITECEDAR COURT | VIENNA | FAIRFAX | VA | 2 2181 | 3 | NO | 2206 | 2001-09-08 | 0 | 0 | 200000 | 131955.4052 | 318602.0293 | NO | 0 | 29 | 579263 | 20010909 | 19.9 | 35 | BY TEST |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INTERIOR OF HOUSE | REGULATOR/METER |  | OTHER | REGULATOR, ALUMINUM CASED |  |  |  | AMERICAN METER | 1989 | 1994 | WITHIN/UNDER BUILDING |  | JERRY F. KIDWELL | 7037507687 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | WG METER AND REGULATOR ASSEMBLY WERE DAMAGED AND NATURAL GAS WAS RELEASED FOLLOWING AN EXPLOSION AND FIRE IN THIS HOUSE. SOURCE OF FIRE IS BELIEVED TO BE THE WATER HEATER.
2025-01-31 10:21 | YES | YES | 20010180 | 2001-10-22 | 792 | ATLANTA GAS LIGHT CO | 786 COVENTRY TOWNSHIP PLACE | MARIETTA | COBB | GA |  | 3 | NO | 1232 | 2001-09-30 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 17 | 581387 | 20010930 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ASTM PE 2406 | UNKNOWN | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | PHYLLIS W. STALLINGS | 7704235720 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | MARIETTA POWER TECHNICIAN WAS INSTALLING A SHRINK SLEEVE TO POWER CABLE LOCATED UNDERNEATH 5/8" PLASTIC GAS SERVICE LINE. APPARENTLY, THE HEAT FROM THE TORCH BEING USED BY THE TECHNICIAN TO INSTALL THE SLEEVE MELTED THE 5/8" PLASTIC GAS LINE, RESULTING IN GAS ESCAPING AND IGNITING, CAUSING BURNS TO ARM AND FACE OF TECHNICIAN.
2025-01-31 10:21 | NO | NO | 20010181 | 2001-10-22 | 31348 | TXU GAS DISTRIBUTION | JEFFERSON AND SEVENTH STREET | KAUFMAN | KAUFMAN | TX | 75142- | 3 | NO | 1715 | 2001-09-06 | 0 | 0 | 10000 | 6597.7703 | 15930.1015 | NO | 2 | 45 |  | 20010906 | 10 | 45 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.307 |  |  | 0 | 1985 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES | NO DATA |  | A THIRD PARTY BORING CONTRACTOR BORED IN TO A GAS MAIN AS WELL AS A SEWER MAIN. THE HIGHER PRESSURE GAS ENTERED THE SEWER MAIN CAUSING DAMAGE WITHIN A HOUSE.
2025-01-31 10:21 | YES | YES | 20010183 | 2001-10-23 | 2568 | COLORADO SPRINGS, CITY OF | 6960 ABILENE RIDGE TRAIL | COLORADO SPRINGS | EL PASO | CO | 8 0922 | 1 | NO | 1330 | 2001-09-25 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 30 | 581048 | 20010926 | 60 | 63 | BY TEST | 110 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D 2513 | UPONOR | 2001 | 2001 | ABOVE GROUND |  | DANIEL J. HIGGINS | 7196683581 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CONTRACTOR EMPLOYEES WERE PERFORMING A PURGE ON A NEW TWO-INCH POLYETHYLENE GAS MAIN. THE EMPLOYEES PLACED A SQUEEZE TOOL ON THE LINE TO CONTROL THE FLOW OF PURGE GAS, BELIEVING THAT THE SQUEEZE TOOL SUFFICIENTLY COMPRESSED THE PIPE TO PREVENT ANY GAS FLOW. NEXT, THE EMPLOYEES WERE TO CUT THE PIPE CAP OFF AND INSTALL A GROUNDING STRAP, PRIOR TO OPENING THE SQUEEZE TOOL AND INITIATING THE PURGE. WHEN THE EMPLOYEES CUT THE PIPE CAP, GAS BEGAN TO ESCAPE BECAUSE THE SQUEEZE TOOL HAD NOT BEEN COMPRESSED FAR ENOUGH. THE GROUNDING STRAP HAD NOT BEEN INSTALLED AND THE ESCAPING GAS WAS IGNITED BY STATIC ELECTRICITY.
2025-01-31 10:21 | YES | YES | 20010184 | 2001-10-30 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 2730,2733,2734 MAGNOLIA STREET | RICHMOND |  | VA | 23223- | 4 | NO | 2145 | 2001-10-21 | 0 | 10 | 100000 | 65977.7026 | 159301.0147 | NO | 0 | 20 | 583587 | 20011021 | 21.5 | 25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.48 |  | UNKNOWN | 0 | 1958 | UNDER PAVEMENT |  | J C STAFFORD | 8046468350 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA |  | UNKNOWN AT THIS TIME/INVESTIGATION CONTINUES
2025-01-31 10:21 | NO | NO | 20010185 | 2001-11-02 | 15469 | PHILADELPHIA GAS WORKS | 122 W. HIGHLAND AVE. | PHILADELPHIA | PHILADELPHIA | PA | 1 9118 | 3 | NO | 1212 | 2001-10-02 | 0 | 0 | 75000 | 49483.277 | 119475.761 | NO | 0 | 27 |  | 20011002 | 0.25 | 0.5 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | VALVE ON METER BAR | STEEL |  | 0.75 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | PAUL A. MONDIMORE | 2156846372 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE PHILADELPHIA FIRE DEPARTMENT AND PHILADELPHIA GAS WORKS HAVE INVESTIGATED THIS INCIDENT. TO DATE THE FIRE MARSHALLS OFFICE HAS NOT RELEASED ITS FINDINGS. PGW HAS CONCLUDED ITS INVESTIGATION AND HAS DETERMINED THAT NATURAL GAS WAS A FUEL IN THIS FIRE AND EXPLOSION AT 122 W. HIGHLAND AVE. PGW HAS ALSO DETERMINED THAT THE SOURCE OF THE NATURAL GAS ORIGINATED FROM WITHIN THE BASEMENT OF 122 W. HIGHLAND AVE. BASED ON PGWS TESTING OF ITS FACILITIES INCLUDING THE METER AND METER ASSEMBLY, THE ONLY LEAK DISCOVERED WAS A SMALL FUZZ LEAK ON THE 3/4" METER BAR SHUTOFF COCK. THIS LEAK COULD BE ATTRIBUTED TO THE FIRE MELTING THE PLUG VALVE LUBRICATION (GREASE) AND NOT BE THE CAUSE OF THE FIRE. THE PFD WAS LEAD INVESTIGATOR ON THIS INCIDENT AND PGW DID NOT HAVE ACCESS TO THE CUSTOMERS FUEL LINES OR NATURAL GAS EQUIPMENT TO DETERMINE IF OTHER LEAKS WERE PRESENT IN THE BASEMENT. PGW IS WAITING FOR THE PFDS DETERMINATION AS TO THE SOURCE AND CAUSE OF THE FIRE.
2025-01-31 10:21 | NO | NO | 20010186 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #575 RANCHO V | ORO VALLEY | PIMA | AZ | 8 5737 | 3 | NO | 2326 | 2001-10-05 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | YES | 1 | 4 | 582132 | 20011006 | 101 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | VALVE |  | STEEL |  |  |  | ANSI B16.10 | NORDSTROM | 1992 | 1992 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 5, 2001 AT 2324 HOURS AN ALARM WAS RECEIVED FROM A REMOTE PRESSURE MONITORING DEVICE, INDICATING AN OVERPRESSURE CONDITION ON THE DISTRIBUTION SYSTEM FED FROM REGULATOR STATION #575. UPON VERIFICATION OF THE ALARM AT 2326 HOURS, FIELD PERSONNEL WERE DISPATCHED TO THE LOCATION. UPON ARRIVAL AT THE REGULATOR STATION ON OCTOBER 6,2001 AT 0030 HOURS, A GAUGE READING ON THE OUTLET OF THE STATION SHOWED 101 PSIG. THE LOCK FOR THE ABOVE GROUND BYPASS VALVE HAD BEEN REMOVED AND THE VALVE HAD BEEN PARTIALLY OPENED. THE DISTRIBUTION SYSTEM WAS RESTORED TO NORMAL OPERATING PRESSURES BELOW 60 PSIG BY TURNING OFF THE BYPASS VALVE. THE AREA OF THE SYSTEM AFFECTED BY THE OVERPRESSURE WAS DETERMINED AND A LEAK SURVEY CONDUCTED. ANY LEAKAGE FOUND HAS BEEN OR WILL BE REPAIRED AND ANOTHER LEAK SURVEY WILL BE PERFORMED IN 30 DAYS TO ENSURE THAT THERE IS NO ADDITIONAL LEAKAGE. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010187 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #545 SPEEDWAY | TUCSON | PIMA | AZ | 8 5748 | 3 | NO | 831 | 2001-10-06 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | YES | 0 | 0 |  | 20011006 | 0 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | REGULATOR/METER |  | STEEL |  |  |  | ANSI/ISA S75.01/02 | AMERICAN METER | 1988 | 1989 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 6, 2001 AT 0831 HOURS WE BEGAN RECEIVING TELEPHONE CALLS FROM CUSTOMER REPORTING INOPERABLE APPLIANCES. AT 1005 HOURS IT WAS DETERMINED THAT THE REGULATOR STATION SERVING THE DISTRIBUTION SYSTEM IN THE VICINITY OF SPEEDWAY BLVD. AND HOUGHTON RD. HAD BEEN VANDALIZED. THE LOCK SECURING THE FENCED ENCLOSURE FOR THE REGULATOR STATION HAD BEEN REMOVED AND THE ADJUSTMENT SCREWS FOR THE WORKER AND MONITOR REGULATORS HAD BEEN TAMPERED WITH, SHUTTING OFF THE FLOW OF GAS. THIS RESULTED IN AN OUTAGE OF 819 CUSTOMERS. THE SYSTEM WAS PURGED AND RESTORED TO NORMAL OPERATION, WITH CUSTOMER RELIGHTS COMPLETED ON 10/07/01. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010188 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #566 1501 E. | TUCSON | PIMA | AZ | 8 5718 | 3 | NO | 1650 | 2001-10-06 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | YES | 0 | 5 |  | 20011006 | 72 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | VALVE |  | STEEL |  |  |  | ANSI B16.10 | NORDSTROM | 1990 | 1991 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 6, 2001 AT 1650 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED 72 PSIG ON THE OUTLET OF THE STATION. THE LOCK FOR THE ABOVE GROUD BYPASS VALVE HAD BEEN REMOVED AND THE VALVE HAD BEEN PARTIALLY OPENED, RESULTING IN AN OVERPRESSURE CONDITION. THE DISTRIBUTION SYSTEM WAS RESTORED TO NORMAL OPERATING PRESSURES BELOW 60 PSIG. THE AREA OF THE SYSTEM AFFECTED BY THE OVERPRESSURE WAS DETERMINED AND A LEAK SURVEY CONDUCTED. ANY LEAKAGE FOUND HAS BEEN OR WILL BE REPAIRED AND ANOTHER LEAK SURVEY WILL BE PERFORMED IN 30 DAYS TO ENSURE THAT THERE IS NO ADDITIONAL LEAKAGE. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010189 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #18 LA CHOLLA | TUCSON | PIMA | AZ | 8 5704 | 3 | NO | 1409 | 2001-10-07 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | YES | 0 | 41 |  | 20011007 | 70 | 45 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | REGULATOR/METER |  | STEEL |  |  |  | ASTM A-126 | FISHER | 1994 | 1994 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 7, 2001 AT 1409 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED 70 PSIG ON THE OUTLET OF THE STATION. THE ADJUSTMENT SCREWS FOR THE WORKER AND MONITOR REGULATORS HAD BEEN TAMPERED WITH, RESULTING IN AN OVERPRESSURE CONDITION. THE DISTRIBUTION SYSTEM WAS RESTORED TO NORMAL OPERATING PRESSURES BELOW 45 PSIG. THE AREA OF THE SYSTEM AFFECTED BY THE OVERPRESSURE WAS DETERMINED AND A LEAK SURVEY CONDUCTED. ANY LEAKAGE FOUND HAS BEEN OR WILL BE REPAIRED AND ANOTHER LEAK SURVEY WILL BE PERFORMED IN 30 DAYS TO ENSURE THAT THERE IS NO ADDITIONAL LEAKAGE. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010190 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #26 6993 N. O | TUCSON | PIMA | AZ | 8 5704 | 3 | NO | 1524 | 2001-10-07 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | YES | 0 | 0 |  | 20011009 | 58 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | REGULATOR/METER |  | STEEL |  |  |  | ANSI/ISA S75.01/02 | AMERICAN METER | 1971 | 1971 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 7, 2001 AT 1524 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED THAT THE REGULATOR STATION HAD BEEN TAMPERED WITH. THE LOCK SECURING THE GATE FOR THE FENCED ENCLOSURE HAD BEEN REMOVED AND THE ADJUSTMENT SCREWS FOR THE WORKER AND MONITOR REGULATORS HAD BEEN TAMPERED WITH. ALTHOUGH THIS REDUCED THE OUTLET PRESSURE, THERE WAS NOT AN OUTAGE ON THIS MULTIFED SYSTEM. THE STATION WAS RESTORED TO NORMAL OPERATION. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010191 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #22 LA CHOLLA | TUCSON | PIMA | AZ | 8 5704 | 3 | NO | 1025 | 2001-10-08 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | YES | 0 | 7 |  | 20011008 | 73 | 35 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | REGULATOR/METER |  | STEEL |  |  |  | ASTM A-126 | FISHER | 1990 | 1990 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 8, 2001 AT 1025 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED 73 PSIG ON THE OUTLET OF THE STATION. THE ADJUSTMENT SCREWS ON THE WORKER AND MONITOR REGULATORS HAD BEEN TAMPERED WITH RESULTING IN AN OVERPRESSURE CONDITION. THE DISTRIBUTION SYSTEM WAS RESTORED TO NORMAL OPERATING PRESSURES BELOW 35 PSIG. THE AREA OF THE SYSTEM AFFECTED BY THE OVERPRESSURE WAS DETERMINED AND A LEAK SURVEY CONDUCTED. ANY LEAKAGE FOUND HAS BEEN OR WILL BE REPAIRED AND ANOTHER LEAK SURVEY WILL BE PERFORMED IN 30 DAYS TO ENSURE THAT THERE IS NO ADDITIONAL LEAKAGE. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010192 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #MT259 ROCKCL | ORACLE | PINAL | AZ | 8 5623 | 2 | NO | 1400 | 2001-10-08 | 0 | 0 | 70000 | 46184.3918 | 111510.7103 | YES | 0 | 0 |  | 20011009 | 38 | 40 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STSTION | VALVE |  | STEEL |  |  |  | ANSI B16.10 | NORDSTROM | 1977 | 1977 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 8, 2001 AT 1400 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED THAT THE REGULATOR STATION HAD BEEN TAMPERED WITH. THE LOCK SECURING THE GATE FOR THE FENCED ENCLOSURE HAD BEEN REMOVED AND THE ABOVE GROUND INLET VALVE TURNED OFF. ALTHOUGH THIS SHUT OFF THE FLOW OF GAS, THERE WAS NOT AN OUTAGE ON THIS MULTIFED SYSTEM. THE STATION WAS RESTORED TO NORMAL OPERATION. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20010193 | 2001-11-02 | 18536 | SOUTHWEST GAS CORP | DISTRICT REGULATOR STATION #575 RANCHO V | TUCSON | PIMA | AZ | 8 5737 | 3 | NO | 1040 | 2001-10-12 | 0 | 0 | 8750 | 5773.049 | 13938.8388 | NO | 0 | 0 |  | 20011012 | 58 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | VALVE |  | STEEL |  |  |  | ANSI B16.10 | NORDSTROM | 1992 | 1992 | ABOVE GROUND |  | RANDY J. SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON OCTOBER 12, 2001 AT 1040 HOURS A SPECIAL REGULATOR STATION INSPECTION IDENTIFIED THAT THE REGULLATOR STATION HAD BEEN TAMPERED WITH. THE ABOVE GROUND INLET VALVE WAS TURNED OFF AND THE ADJUSTMENT SCREW ON THE MONITOR REGULATOR HAD BEEN TAMPERED WITH. ALTHOUGH THIS SHUT OFF THE FLOW OF GAS, THERE WAS NOT AN OUTAGE ON THIS MULTIFED SYSTEM. THE STATION WAS RESTORED TO NORMAL OPERATION. DUE TO THE CAUSE OF THE INCIDENT BEING VANDALISM, A CONTINUING INVESTIGATION PROCESS IS UNDER WAY, WHICH INCLUDES COORDINATION WITH THE FBI.
2025-01-31 10:21 | NO | NO | 20020001 | 2002-01-04 | 5700 | FULTONDALE GAS BOARD | COALBURG ROAD | BIRMINGHAM | JEFFERSON | AL |  | 2 | Null | 130 | 2001-10-30 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 10 | 584811 |  | 158 | 215 | BY TEST |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 |  |  | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | LESLIE D SHIPP | 2058416456 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | YES | NO DATA |  | ON OCTOBER 30, 2001, SOUTHEASTERN CONSTRUCTION (PHONE NUMBER 865-470-7777), ADDRESS: 8605 AMBLECOTE ROAD, KNOXVILLE, TENNESSEE 37923) WAS CLEARING RIGHT-OF-WAY FOR ALABAMA POWER ON COALBURG ROAD, JEFFERSON COUNTY, ALABAMA. THEY WERE CLEARING RIGHT-OF-WAY AND IN THE PROCESS OF GRATING FOR AN ACCESS ROAD TO COALBURG ROAD THE CONTRACTORS, SOUTHEASTERN CONSTRUCTION DAMAGED A 6" STEEL DISTRIBUTION LINE OWNED BY THE CITY OF FULTONDALE GAS BOARD. ESTIMATED TIME OF THIS INCIDENT 1:35 P.M. OCTOBER 30, 2001. A SECTION OF DISTRIBUTION LINE ON COALBURG ROAD HAD TO BE ISOLATED. AN ESTIMATED SEVENTY-ONE (71) FULTONDALE GAS CUSTOMERS HAD SERVICE INTERRUPTED. DAMAGE INCLUDED WAS A 5 6" SECTION OF THE 6" STEEL DISTRIBUTION LINE AND WAS WELDED BACK IN PLACE. ALSO, IN THE DAMAGE WAS ONE (1) ROTARY METER DAMAGED BECAUSE OF THE EXTRA AMOUNT OF LOAD PUT ON THE SYSTEM. CONTRACTORS, SOUTHEASTERN CONSTRUCTION, DID NOT ABIDE BY ACT 94-47 WHICH IS THE ALABAMA 1 CALL NOTIFICATION PROVISION. THERE WAS NO CALL IN FOR THE LOCATE. THIS APPEARS TO BE WHAT CONTRIBUTED TO THIS INCIDENT.
2025-01-31 10:21 | YES | NO | 20020002 | 2002-01-04 | 18536 | SOUTHWEST GAS CORP | 1229 E ENCANTADA PL | PHOENIX | MARICOPA | AZ | 8 5014 | 3 | NO | 1822 | 2001-11-03 | 0 | 0 | 150000 | 98966.5539 | 238951.522 | YES | 2 | 38 | 585073 | 20011103 | 30 | 30 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC |  | 1.25 | 0.18 | SCHEDULE 40 |  | 1972 | 1972 | UNDER PAVEMENT |  | BERNIE GALLENBECK | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-11-03 | YES | 3 | 2001-11-03 | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20020003 | 2002-01-08 | 2700 | CONNECTICUT NATURAL GAS CORP | 25 CLEMENS COURT | ROCKY HILL |  | CT | 6067 |  | NO | 400 | 2001-11-20 | 0 | 0 | 750000 | 494832.7696 | 1194757.6099 | NO | 0 | 30 | 586594 | 20011121 | 40 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA | [5 empty] | 0 | 0 | ABOVE GROUND |  | VIC FRYXELL | 8607273003 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE CAUGHT ON FIRE IN GARAGE, SET OTHER VEHICLES ON FIRE, SPREAD TO GARAGE STRUCTURE AND ADJACENT CONDOMINUMS AND GARAGE.
2025-01-31 10:21 | NO | NO | 20020008 | 2002-01-15 | 2596 | COLUMBIA GAS OF OHIO INC | 2872 HOWEY RD (A, B, C & D) | COLUMBUS | FRANKLIN | OH | 4 3224 | 3 | NO | 1702 | 2001-12-16 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 1 | 13 | 588859 | 20011216 |  |  | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | METER SET ASSEMBLY | STEEL |  | 1.25 |  |  |  | 0 | 0 | ABOVE GROUND |  | MICHAEL F SUCHARSKI | 6144502064 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20020009 | 2002-01-15 | 4483 | ENSTAR NATURAL GAS CO | 101 E. WHITNEY RD. | ANCHORAGE |  | AK | 99502- | 3 | NO | 1900 | 2001-12-26 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 0 | 30 | 589292 | 20011226 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1981 | 1981 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON FRIDAY EVENING, DECEMBER 21, 2001 AT APPROXIMATELY 7:00 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 101 E. WHITNEY ROAD, ANCHORAGE, ALASKA. AN ENSTAR SERVICE WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A COMMERCIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AT 7:30 PM AST. THE FIRE IS BELIEVED TO HAVE BEEN STARTED FROM WELDING OR GRINDING SPARKS. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20020010 | 2002-01-15 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 2740 PIPER RD. | PEARLAND | BRAZORIA | TX | 77581- | 3 | NO | 1604 | 2001-11-20 | 0 | 1 | 0 | 0 | 0 | YES | 2 | 2 | 586570 | 20011120 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | ASTM D2513 | UPONOR | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | TAL R. CENTERS, JR. | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-10-31 | YES | 2 |  | YES | NO DATA |  | THIRD PARTY DAMAGED A .75 INCH I.P. SERVICE LINE WITH A TORCH WHILE REPAIRING A TELEPHONE CABLE. THE ESCAPING GAS WAS IGNITED AND THIRD PARTY EMPLOYEE WENT TO HOSPITAL WITH SECOND DEGREE BURNS TO HANDS AND FACE.
2025-01-31 10:21 | YES | YES | 20020011 | 2002-01-15 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | FRANKLIN STREET AND ESTES DRIVE | CHAPEL HILL | ORANGE | NC | 2 7312 | 3 | NO | 2100 | 2001-10-16 | 0 | 1 | 20000 | 13195.5405 | 31860.2029 | NO | 1 | 55 | 583395 | 20011016 | 60 | 60 | BY TEST | 103 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTM 2513 | PLEXCO | 1995 | 1995 | UNDER PAVEMENT |  | KENNETH G. GRIFFIN | 9195987413 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-10-11 | YES | 3 | 2001-10-11 | YES | NO DATA |  | 9:03 PM A PSNC ENERGY SERVICE EMPLOYEE IS MONITORING A POLICE SCANNER AND IS MADE AWARE OF A GAS LEAK ON FRANKLIN STREET, CHAPEL HILL, NC. HE DECIDES TO DRIVE TO THE LOCATION TO SEE IF IT IS A NATURAL GAS LEAK. 9:10 PM THE CUSTOMER CARE CENTER (CCC) RECEIVES A CALL FROM THE ORANGE COUNTY 911 STATING A GAS LINE HAS BEEN BROKEN AND A FIRE IS CONSUMING CONSTRUCTION EQUIPMENT AND A POWER POLE. THEY PAGE THE SERVICE EMPLOYEE ALREADY RESPONDING TO THE GAS LEAK. 9:12 PM THE SUPERVISOR ON-CALL IS NOTIFIED OF SITUATION BY CCC. 9:15 PM SERVICE DEPARTMENT EMPLOYEE ARRIVES AT THE SCENE AND CALLS THE CONSTRUCTION DEPARTMENT CREWS RESPONDING TO ANOTHER INCIDENT TO RESPOND TO CHAPEL HILL. 9:35 PM TWO CONSTRUCTION DEPARTMENT CREWS AND THEIR SUPERVISOR ARRIVE AT THE CHAPEL HILL SITE AND BEGIN TO COORDINATE THEIR EFFORTS WITH THE FIRE DEPARTMENT. 10:55 PM AFTER DIGGING TWO BELL-HOLES AND SQUEEZING OFF FOUR-INCH MAINS, AND TURNING ONE VALVE, THE FIRE IS EXTINGUISHED. WEDNESDAY, OCTOBER 17, 2001. 2:00 AM GDS PERSONNEL ARE ALLOWED TO BEGIN THEIR RESTORATION WORK AFTER THE DUKE ENERGY (POWER) HAS MADE TEMPORARY REPAIRS AND THE CONTRACTOR EQUIPMENT IS REMOVED. 9:00 AM REPAIRS ARE COMPLETED BY THE GDS PERSONNEL AND GAS IS RESTORED TO FOUR COMMERCIAL CUSTOMERS.
2025-01-31 10:21 | YES | YES | 20020014 | 2002-01-18 | 18536 | SOUTHWEST GAS CORP | 300 E. TROPICANA AVE. SPACE 11 | LAS VEGAS | CLARK | NV | 8 9109 | 3 | NO | 948 | 2001-12-20 | 0 | 1 | 21598 | 14249.8642 | 34405.8331 | NO | 0 | 42 | 589531 | 20011226 | 26 | 33 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | OTHER PLASTIC |  | 0.5 | 0.057 | UNKNOWN | KRALOY | 0 | 1963 | UNDER GROUND OR UNDER WATER |  | TOM CARDIN | 7023652008 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | WHILE IN THE PROCESS OF REPLACING A TILTING SERVICE RISER AT 300 E. TROPICANA AVE. SPACE 11, A GAS LEAK IGNITED CAUSING A SWG CREWMEMBER TO RAPIDLY EXIT THE AREA, INJURING HIS LEG. IT WAS LATER DETERMINED THAT AN EXCAVATION FOR A WATER LEAK HAD CAUSED THE METER SET TO SUBSIDE INTO THE EXCAVATED AREA AND THE UNDERGROUND RISER CONNECTION TO CRACK. THE CAUSE OF THE GAS IGNITION WAS SUSPECTED TO BE A CUSTOMERS UNDERGROUND FAULTY ELECTRICAL FACILITIES. THE INJURED EMPLOYEE WAS TREATED AND RELEASED ON 12/20/01. BASED ON SUBSEQUENT DOCTORS MEDICAL EVALUATION, THE EMPLOYEE WAS HOSPITALIZED ON 12/24/01 FOR CORRECTIVE KNEE SURGERY AND WAS RELEASED FROM THE HOSPITAL ON 12/26/01.
2025-01-31 10:21 | YES | NO | 20020015 | 2002-01-18 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | NC HWY 147 & ALSTON AVENUE | DURHAM | DURHAM | NC | 2 7707 | 3 | NO | 1830 | 2001-10-15 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 0 | 30 | 583250 | 20011015 | 60 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 | API | UNKNOWN | 0 | 1969 | ABOVE GROUND |  | KENNETH G. GRIFFIN | 9195987413 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | 6:28 PM PSNC ENERGY CCC RECEIVES A CALL FROM DURHAM COUNTY 911 STATING THERE HAS BEEN AN ACCIDENT ON HIGHWAY 147 AND A GAS MAIN HAS BEEN RUPTURED AND IS BLOWING. POLICE ARE ON SITE AND BLOCKING TRAFFIC, AND FIRE IS IN ROUTE. 6:35 PM CCC PAGES THE SERVICEMAN AND CONSTRUCTION LEADER ON CALL. 6:40 PM CCC NOTIFIES THE SERVICEMAN AND CONSTRUCTION LEADER VIA PHONE. 6:50 PM THE SERVICEMAN ARRIVES ON SCENE, CALLS THE SUPERVISOR ON-CALL, AND BEGINS COORDINATING WITH THE EMERGENCY SERVICE PERSONNEL. 7:15 PM CONSTRUCTION DEPARTMENT CREW ARRIVES A THE SCENE AND BEGINS TO ASSESS THE SITUATION. CREW MEMBERS ARE SENT TO THE DURHAM OPERATIONS CENTER TO OBTAIN MATERIALS AND TAPPING EQUIPMENT. 9:00 PM AFTER STOPPING IN THE DURHAM OFFICE TO CHECK ENGINEERING RECORDS OF THE GAS MAIN (GEOHAWK SOFTWARE), THE ON CALL SUPERVISOR ARRIVES AT THE SCENE. 10:00 PM AFTER SEARCHING FOR VALVES AND DETERMINING WHERE THE MAINS ARE LOCATED, THE CONSTRUCTION DEPARTMENT BEGINS TO SAW-CUT ALSTON AVENUE IN TWO LOCATIONS AND DIGS BELL-HOLES IN SEARCH OF THE 8-INCH DISTRIBUTION MAIN. 12:30 AM GDS PERSONNEL FIND A RETIRED 8-INCH MAIN ON THE NORTH SIDE OF HWY 147. THE DECISION IS MADE TO WAIT UNTIL A SHORING BOX IS LOCATED BEFORE DIGGING FURTHER AT THE LOCATION. 6:00 AM AFTER WELDING ON AN 8-INCH PRESSURE CONTROL FITTING, TAPPING IS STARTED ON THE SOUTH SIDE OF HWY 147. AFTER TAPPING, THE MAIN IS STOPPED-OFF. 7:30 AM A CAVE-IN ON THE NORTH SIDE OF HWY 147 CAUSES THE CONSTRUCTION DEPARTMENT TO MOVE FURTHER NORTH AND TRY TO LOCATE THE 8-INCH MAIN. 9:00 AM AFTER LOCATING THE MAIN ON THE NORTH SIDE, AN 8-INCH SQUEEZE-OFF TOOL IS USED TO UNSUCCESSFULLY STOP THE FLOW OF GAS. UPON BACKING OFF THE TOOL, IT IS FOUND THE MAIN IS SPILT AND THE SQUEEZE-OFF MUST REMAIN ON THE PIPE. ABOUT THIS TIME, THE 8-INCH IS FOUND AT THE ORIGINAL NORTH BELL-HOLE. 11:20 AM A SECOND SQUEEZE-OFF UNDER THE BRIDGE IS UNSUCCESSFUL AT STOPPING THE FLOW OF GAS. 2:00 PM AFTER WELDING ON THE SECOND PRESSURE-CONTROL FITTING AND TAPPING THE MAIN, THE FLOW OF GAS IS STOPPED.
2025-01-31 10:21 | YES | NO | 20020016 | 2002-01-23 | 2364 | CINCINNATI GAS & ELECTRIC CO | 3149 TIMBERVIEW DRIVE | CINCINNATI | HAMILTON | OH | 4 5211 | 4 | NO | 1000 | 2001-12-23 | 0 | 0 | 170000 | 112162.0945 | 270811.7249 | NO | 0 | 4 | 589364 | 20011223 | 11 | 35 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | NO DATA |  | CAST IRON | [5 empty] | 0 | 0 | OTHER | BREAK IN GAS MAIN WAS UNDERGROUND WHILE EXPLOSION | RANDALL L. SUTTLES, REGULATORY COMPLIANCE SPECIALIST | 5132873921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EXPLOSION STILL UNDER INVESTIGATION. 4-16-04 NATURAL GAS FROM A BREAK IN THE GAS MAIN MIGRATED TO THE RESIDENCE LOCATED AT 3149 TIMBERVIEW DRIVE AND WAS IGNITED.
2025-01-31 10:21 | YES | NO | 20020017 | 2002-01-18 | 18484 | SOUTHERN CALIFORNIA GAS CO | 16468 LAKESHORE DR. | ELSINORE | RIVERSIDE | CA |  | 2 | NO | 130 | 2001-12-21 | 0 | 0 | 1000000 | 659777.0262 | 1593010.1466 | NO | 17 | 0 | 589269 | 20011221 | 40 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 4 |  | ALDYL A | DUPONT | 1980 | 1980 | NO DATA |  | W.J. KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | STRESS CHECK ON 3" PE FITTINGS CAUSED LEAK THAT MIGRATED TO TELEPHONE SWITCHING FACILITY, RESULTING IN EXPLOSION.
2025-01-31 10:21 | NO | NO | 20020018 | 2002-01-23 | 14210 | OKLAHOMA NATURAL GAS CO | CITYWIDE SWATH RUNNING SW TO NE | CORDELL | WASHITA | OK | 7 3632 | 3 | NO | 1800 | 2001-10-09 | 0 | 0 | 75000 | 49483.277 | 119475.761 | NO | 2 | 30 | 582495 | 20011009 | 40 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC | [5 empty] | 0 | 0 | UNDER GROUND OR UNDER WATER |  | BOBBY JOHNSTON | 4055516907 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA |  | APPROXIMATELY 125 DOMESTIC GAS METER SETTINGS AND SOME ASSOCIATED PIPELINE AND REGULATOR SETTINGS WERE DESTROYED OR DAMAGED BY A TORNADO THAT STRUCK CORDELL, OK.
2025-01-31 10:21 | YES | YES | 20020022 | 2002-01-25 | 10270 | KINGS MOUNTAIN NATURAL GAS SYSTEM | 146 PERSIMMON CREEK RD. | KINGS MOUNTAIN | CLEVELAND | NC | 2 8086 | 3 | NO | 1715 | 2001-11-29 | 0 | 1 | 12865 | 8488.0314 | 20494.0755 | NO | 1 | 15 | 587316 | 20011129 | 30 | 90 | BY TEST | 135 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | SERVICE TEE | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 |  | D2513 | DRISCO PIPE | 1989 | 1989 | UNDER GROUND OR UNDER WATER |  | MIKE NICHOLSON | 7047344521 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES | 2001-11-26 | YES | 3 | 2001-11-26 | YES | NO DATA |  | ON NOVEMBER 29, 2001 TWO CITY EMPLOYEES WERE ASSIGNED TO INSTALL A 3/4 INCH SERVICE LINE AT A LOCATION ACROSS THE STREET FROM 146 PERSIMMON CREEK ROAD. AFTER COMPLETING THE EXCAVATION AND ROAD BORE THE EMPLOYEE ENTERED THE BELL HOLE TO INSTALL THE SERVICE TEE. THE EMPLOYEES FAILED TO PROPERLY GROUND (BOND) THE MAIN PRIOR TO ELECTRO-FUSING THE SERVICE TEE. AFTER INSTALLING THE SERVICE TEE, THE EMPLOYEES FOUND THE SERVICE TEE TO BE DEFECTIVE. THE SERVICE TEE WAS NOT PROPERLY INSPECTED PRIOR TO INSTALLATION. THE EMPLOYEES ATTEMPTED TO REPAIR THE SERVICE TEE INSTEAD OF ABANDONING THE SERVICE TEE AND INSTALLING A NEW SERVICE TEE AS INDICATED IN THE CITY OF KINGS MOUNTAINS O&M MANUAL. DURING THIS ATTEMPT TO REPAIR THE SERVICE TEE, AN IGNITION SOURCE OF UNKNOWN ORIGIN IGNITED ESCAPING GAS, RESULTING IN ONE EMPLOYEE BEING BURNED, AND ANOTHER RECEIVING MINOR BURNS.
2025-01-31 10:21 | NO | NO | 20020023 | 2002-01-24 | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | VESEY ST BETWEEN WEST BROADWAY & CHU | NEW YORK CITY | MANHATTAN | NY | 1 0048 | 4 | NO | 448 | 2001-09-13 | 0 | 0 | 0 | 0 | 0 | NO | 4 | 0 | 579610 | 20010913 | 0.238 | 0.433 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  |  | UNKNOWN | 0 | 1895 | UNDER PAVEMENT |  | HANK MEYER O.G.S. | 7183192310 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A TERRORIST ATTACK TO THE WTC ON 9/11/01 CAUSED DAMAGE TO THE GAS DISTRIBUTION SYSTEM SUPPLYING LOWER MANHATTAN. A STRONG GAS ODOR WAS REPORTED AT THE ABOVE LOCATION AND WE FOUND ON OUR ARRIVAL THAT THE GAS HAD IGNITED. COMPANY CREWS SHUT ONE MAIN VALVE AND CUT AND CAPPED THE MAIN AT A SECOND LOCATION. THE FIRE WAS EXTINGUISHED AFTER 4 HOURS. A RESTORATION PLAN FOR THE AFFECTED AREA HAS BEEN ESTABLISHED. TO DATE THE GAS SUPPLYING THIS AREA IS STILL OFF. THERE ARE FIVE SERVICES FED FROM THIS SECTION OF MAIN. THEY REMAIN OFF DUE TO EXTENSIVE DAMAGE TO ALL THE BUILDINGS AND THE SURROUNDING AREA. THERE WERE NO INJURIES OR MEDIA ON LOCATION.As per our conversation on 3/5/02. DOT report # 579610 pertaining to a Con Edison of NY incident @ Vesey Street between West Broadway & Church Street in Manhattan on 9/13/01. There was a gas fire in the street due to the damage done from the attack at the WTC. There was no property damage due to the fire, all damage was due to the attack. If any additional information is needed contact me at 718-319-2310 Hank Meyer
2025-01-31 10:21 | NO | NO | 20020026 | 2002-02-06 | 4483 | ENSTAR NATURAL GAS CO | 8133 PARKRIDGE CIRCLE | ANCHORAGE |  | AK | 9 9507 | 3 | NO | 2055 | 2001-12-29 | 0 | 0 | 50000 | 32988.8513 | 79650.5073 | NO | 2 | 45 | 589777 | 20011230 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M-8000 | DRISCOPIPE | 1986 | 1986 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY EVENING, DECEMBER 29, 2001 AT APPROXIMATELY 8:55 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 8133 PARKRIDGE CIRCLE, ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. AT APPROXIMATELY 10:25 PM IT WAS DETERMINED THAT HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION REPAIR CREW WAS CALLED IN TO DIG UP AND PINCH OFF THE SERVICE LINE. EXPLODING PROPANE TANKS, INACCESSIBILITY DUE TO FIRE FIGHTING EQUIPMENT AND FROZEN GROUND DELAYED ENSTAR IN SHUTTING DOWN THE SERVICE LINE. THE SERVICE LINE WAS DUG UP AND PINCHED OFF AT 1:10 AM AST ON DECEMBER 30. THE FIRE IS BELIEVED TO HAVE STARTED FROM MALFUNCTIONING TEMPORARY PROPANE HEATERS. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20020027 | 2002-02-05 | 15329 | PEOPLES GAS LIGHT & COKE CO | 1116 N. LECLAIRE | CHICAGO | COOK | IL |  | 3 | NO | 1118 | 2001-10-09 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 20 | 582346 | 20011009 | 0.25 | 12 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 1.5 |  | UNKNOWN | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWIN C. PROCTOR | 7737946851 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | BUILDING CAUGHT ON FIRE DUE TO THE IGNITION OF LEAKING NATURAL GAS IN THE BASEMENT. GAS LEAK WAS CAUSED BY PERSONS TAMPERING WITH OUR FACILITIES (GAS METERS) WITH THE INTENT TO STEAL GAS. GAS METERS HAD PREVIOUSLY BEEN TURNED OFF AND LOCKED FOR NON-PAYMENT.
2025-01-31 10:21 | YES | NO | 20020028 | 2002-02-05 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | NO. 40 MAESTAS RD. | TALPA | TAOS | NM | 8 7557 | 3 | NO | 1455 | 2001-12-07 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 0 | 21 | 588077 | 20011207 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT |  | OTHER | ANODELESS RISER | 1 |  | UNKNOWN | UNKNOWN | 0 | 0 | ABOVE GROUND |  | LAVANDA JONES | 5057584223 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | 13 YEAR OLD DRIVING CHEVY TAHOE HIT GAS METER AND HOUSE WHICH IGNITED; FLAMES DESTROYED BOTH THE VEHICLE AND HOUSE.
2025-01-31 10:21 | YES | NO | 20020029 | 2002-02-15 | 4483 | ENSTAR NATURAL GAS CO | 3711 FAUS | ANCHORAGE |  | AK | 9 9508 | 3 | YES | 125 | 2002-01-17 | 0 | 0 | 100000 | 64952.5219 | 156825.7492 | NO | 3 | 5 | 591420 | 20020117 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | PLEXCO | YELLOWSTRIPE HDPE | 2001 | 2001 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THURSDAY MORNING, JANUARY 17, 2002 AT APPROXIMATELY 1:25 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ELMENDORF AIR FORCE BASE FIRE DEPARTMENT OF A FIRE AT 3711 FAUST CT, ELMENDORF AIR FORCE BASE, ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A 4-UNIT APARTMENT COMPLEX THAT WAS UNDER CONSTRUCTION ON FIRE. THE FIRE DID NOT IMPACT THE SERVICE LINE TO UNITS A & B. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER TO C & D UNITS, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION REPAIR CREW WAS CALLED IN TO DIG UP AND PINCH OFF THE SERVICE LINE. THE SERVICE LINE WAS DUG UP AND PINCHED OFF AT 4:20 AM ADT. THE FIRE IS BELIEVED TO HAVE STARTED FROM TEMPORARY HEATERS INSIDE THE BUILDING. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20020030 | 2002-02-19 | 2748 | CONSUMERS POWER CO | 4256 MONROE AVE | WATERFORD | OAKLAND | MI | 4 8329 | 3 | NO | 357 | 2001-12-18 | 0 | 1 | 200000 | 131955.4052 | 318602.0293 | NO | 3 | 3 | 588978 | 20011218 | 53.7 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | UNKNOWN | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | JOAQUIN J. AFFONSO | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE EXPLOSION DUE TO GAS LEADAGE INSIDE THE RESIDENCE. UNKNOWN REASON FOR INCIDENT. NO GAS WAS FOUND IN THE GROUND ADJACENT TO THE HOUSE AND THE SERVICE LINE WAS PRESSURE TESTED WITH NO LEAKAGE FOUND. ON-GOING INVESTIVATION OF THE METER AND REGULATOR MAY DETERMINE CAUSE OF THE INCIDENT. CURRENTLY, FAILURE OF THE CUSTOMER EQUIPMNET IS SUSPECTED.
2025-01-31 10:21 | YES | YES | 20020031 | 2002-02-13 | 2596 | COLUMBIA GAS OF OHIO INC | WESTBROOK AND FIR | TOLEDO | LUCAS | OH |  | 2 | NO | 1406 | 2001-10-11 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 4 |  | 20011011 | 0.5 |  | BY CFR 192.619(A)(3) |  | CORROSION | CORROSION | UNSPECIFIED CORROSION | MAIN |  | BODY OF PIPE |  | STEEL |  | 3 |  |  |  | 0 | 0 | OTHER | MANHOLE | CHRISTINE MAYNARD | 6144602240 | NO DATA | LOCALIZED PITTING |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | DURING RECONSTRUCTION OF THE WATER MAIN IN THIS AREA, A CONSTRUCTION WORKER ENTERED A MANHOLE TO PURGE THE NEW WATER LINE. DURING THIS PROCESS, THERE WAS AN ACCIDENTAL IGNITION INSIDE THE MANHOLE. SUBSEQUENT INVESTIGATION REVEALED THAT BOTH THE CONTRACTOR AND THE WORKER HAD FAILED TO CHECK ATMOSPHERIC CONDITIONS BEFORE THE WORKER ENTERED THE WORKSPACE TO PURGE THE NEW WATER LINE. THE INVESTIGATION ALSO REVEALED A CIGARETTE LIGHTER AND A PARTIALLY BURNED CIGARETTE WERE FOUND IN THE SAME WORKSPACE. THE WORKER RECEIVED 1ST AND 2ND DEGREE BURNS TO HIS HANDS, FACE AND NECK.
2025-01-31 10:21 | NO | NO | 20020032 | 2002-02-12 | 30769 | MISSOURI GAS ENERGY | 32ND AND BUCHANAN | NORTH KANSAS CITY | CLAY | MO | 64116- | 3 | NO | 806 | 2001-12-10 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 9 | 588231 | 20011210 | 125 | 150 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER |  | STEEL |  | 30 |  | UNKNOWN | UNKNOWN | 0 | 1961 | UNDER GROUND OR UNDER WATER |  | JIM GORMAN | 8163605893 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | OCCURRENCE UNDER INVESTIGATION. MINUTE PRESENCE OF NATURAL GAS DOES NOT SUPPORT THE POWERFUL FLASH THAT REPORTABLY OCCURRED.
2025-01-31 10:21 | NO | NO | 20020033 | 2002-02-12 | 31097 | ISLAND ENERGY | BUILDING 720 BERTH 20 | MARE ISLAND | SOLANO | CA | 9 4592 | 3 | YES | 900 | 2002-01-10 | 0 | 0 | 3022 | 1962.8652 | 4739.2741 | NO | 0 | 15 |  | 20020201 | 27 |  | BY TEST | 30 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 2 | 0.25 | ASTM A53A | SHINHO STEEL | 1995 | 1998 | ABOVE GROUND |  | WILLIAM PLUMMER | 7075625000 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | NO | NO DATA |  | WORK FORCE FOR XKT ENGINEERING WAS LIFTING BOOM FOR CRANE, SHIFTED BOOM TOWARD METER SET ASSY AND DESTROYED METER AND COMPENSATOR METER IS A 3175CDB3 05521-0212 INST DRIVE ROOTS GAS ROTERY METER ME-6000 EDFCV METRETEK FLOW COMPUTER, TEMP & PRESS CORRECTOR.
2025-01-31 10:21 | NO | NO | 20020034 | 2002-02-11 | 13660 | NORTH SHORE GAS CO | 813 HELMHOLZ | WAUKEGAN | LAKE | IL | 6 0085 | 3 | NO | 248 | 2001-12-15 | 0 | 0 | 75000 | 49483.277 | 119475.761 | NO | 1 | 54 | 588751 | 20011215 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | PIPE NIPPLE | STEEL |  | 0.75 |  | UNKN | UNKN | 0 | 1972 | ABOVE GROUND |  | JOHN J. JUST | 8472634679 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | A MOTOR VEHICLE LEFT THE ROADWAY, CROSSED THE CUSTOMERS LAWN AND STRUCK THE METER SET ASSEMBLY INSTALLED OUTSIDE OF THE PREMISE. THE IMPACT SEVERED A PIPE NIPPLE OF THE METER SET ASSEMBLY. THE VEHICLE CAME TO REST ON THE METER SET ASSEMBLY WITH THE ENGINE STILL RUNNING. NORTH SHORE GAS PERSONNEL ARRIVED AT THE SCENE 46 MINUTES AFTER NOTIFICATION BUT WERE UNABLE TO SHUT OFF THE GAS UNIT UNTIL THE FIRE AROUND THE METER SET ASSEMBLY WAS BROUGHT UNDER CONTROL BY THE FIRE DEPARTMENT.
2025-01-31 10:21 | NO | NO | 20020035 | 2002-02-19 | 6920 | GULF STATES UTILITIES CO | 2359 GEORGIA STREET | BATON ROUGE |  | LA | 7 0802 | 3 | NO | 1327 | 2002-01-18 | 0 | 0 | 15000 | 9742.8783 | 23523.8624 | NO | 0 | 5 | 591596 | 20020118 | 7 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | INSIDE RESIDENCE | NO DATA |  | NO DATA |  | 0.5 | 0 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ROBERT F. GUISE | 5045933449 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20020036 | 2002-02-19 | 13041 | NASHVILLE GAS CO | 513 WEST COLLEGE STREET | GREENBRIER | ROBERTSON | TN | 3 7073 | 2 | NO | 2145 | 2001-12-28 | 0 | 2 | 0 | 0 | 0 | NO | 1 | 45 | 589732 | 20011228 | 37 | 40 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | STEEL |  | 34 | 0.113 |  |  | 0 | 0 | UNDER PAVEMENT |  | JOHN L. CLARK, JR. | 6157341709 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | OUTSIDE PARTY DAMAGED RESIDENTIAL NATURAL GAS SERVICE LINE WHILE EXCAVATING TO REPAIR BROKEN WATER LINE. LEAKING NATURAL GAS MIGRATED THROUGH SEWER DITCH LINE TO SMALL HOUSE. IGNITION OCCURRED WHICH RESULTED IN DAMAGE TO THE HOUSE AND INJURIES TO THOSE PEOPLE INSIDE THE HOME.
2025-01-31 10:21 | NO | NO | 20020038 | 2002-03-01 | 18536 | SOUTHWEST GAS CORP | 16TH STREET & PALM LN. | PHOENIX | MARICOPA | AZ | 8 5020 | 3 | NO | 1225 | 2002-01-29 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 4 | 36 | 592540 | 20020129 | 30 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.146 |  |  | 1945 | 1945 | UNDER PAVEMENT |  | BERNIE GALLENBECK | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | ARIZONA CORPORATION COMMISSION INCIDENT: PL NUMBER 2002-0089 THE 2" STEEL PIPE APPEARS TO HAVE BEEN DAMAGED BY AN UNKNOWN 3RD PARTY, WHICH CAUSED THE EVENTUAL PIPELINE LEAK. SOUTHWEST IS INVESTIGATING TO DETERMINE WHO CAUSED THE ORIGINAL DAMAGE AND WHEN IT OCCURRED; AS A RESULT, THERE IS NO LOCATING INFORMATION AVAILABLE AT THIS TIME. IN ADDITION, SOUTHWEST IS PERFORMING A MATERIAL INVESTIGATION TO EVALUATE THE CAUSE OF DAMAGE TO THE FACILITY. THERE WERE NO INJURIES OR PROPERTY DAMAGE AS A RESULT OF THIS INCIDENT; HOWEVER, THE RESULTING EMERGENCY RESPONSE, PIPELINE REPAIRS, 1,350 CUSTOMER OUTAGE AND THE ASSOCIATED RELIGHT COSTS CAUSED THE ESTIMATED PROPERTY DAMAGE TO EXCEED $50,000.
2025-01-31 10:21 | YES | YES | 20020039 | 2002-03-01 | 2748 | CONSUMERS POWER CO | 13245 PEARSON HIGHWAY | BROOKLYN | LENAWEE | MI |  | 3 | NO | 1353 | 2002-01-22 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 14 | 591900 | 20020122 | 50 | 60 | BY TEST |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE-24 | DRISCOPIPE 6500 | 1997 | 1997 | UNDER GROUND OR UNDER WATER |  | JOAQUIN J. AFFONSO | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-01-14 | YES | 0 |  | YES | NO DATA |  | A CONSTRUCTION COMPANY DAMAGED A 2" PLASTIC PIPELINE WHILE INSTALLING COMMUNICATIONS CABLE UTILIZING DIRECTIONAL BORING PROCEDURES. THE DAMAGE RESULTED IN A SUBSURFACE LEAK WITH GAS FILTERING THROUGH THE GROUND AROUND THE DAMAGED AREA. A DISTRIBUTION CREW WAS IN THE PROCESS OF INSTALLING A BYPASS AROUND THE DAMAGED AREA WHEN THE GAS IGNITED RESULTING IN AN INJURY TO A GAS LINES WORKER.
2025-01-31 10:21 | YES | NO | 20020040 | 2002-03-08 | 12876 | QUESTAR GAS COMPANY | 900 EAST 100 NORTH | PAYSON | UTAH | UT | 8 4651 | 3 | NO | 1629 | 2002-02-09 | 0 | 0 | 550000 | 357238.8704 | 862541.6204 | NO | 5 | 16 | 593578 | 20020209 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL | [5 empty] | 0 | 1960 | ABOVE GROUND |  | JEFFREY D. HANSEN | 8013243645 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | A CAR WAS PARKED ACROSS THE STREET AND LEFT UNATTENDED (WHILE RUNNING) WHEN IT ROLLED OUT OF THE PARKING LOT, WENT ACROSS THE STREET, OVER THE CURB AND STRUCK THE NATURAL GAS METER (THE GAS METER LOCATED APPROXIMATELY 20 FEET OFF THE CURB). THE IMPACT OF THE CAR BROKE THE PIPING (3/4" X 5" NIPPLE) RIGHT ABOVE THE SERVICE VALVE. THE ESCAPING NATURAL GAS WAS IGNITED AND CAUGHT THE BUILDING ON FIRE. THE BUILDING DESTROYED IN THE FIRE.
2025-01-31 10:21 | NO | NO | 20020041 | 2002-03-07 | 31348 | TXU GAS DISTRIBUTION | 3213 SANDERS | GARLAND | DALLAS | TX | 75042- | 3 | NO | 500 | 2002-01-25 | 0 | 0 | 75000 | 48714.3914 | 117619.3119 | NO | 11 | 30 | 592160 | 20020125 | 23 | 55 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 |  |  |  | 0 | 1959 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | 0 | Null |  | Null | 0 |  | Null | NO DATA |  | A LEAK OCCURRED BELOW GROUND NEAR THE INLET RISER SERVING 3209 SANDERS. GAS MIGRATED UNDER THE SLAB AT 3213 SANDERS AND WAS IGNITED BY AN UNDETERMINED SOURCE.
2025-01-31 10:21 | YES | YES | 20020043 | 2002-03-13 | 603 | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | 800 SPRING STREET | HOT SPRINGS | GARLAND | AR | 71901- | 3 | NO | 2337 | 2002-02-19 | 0 | 1 | 0 | 0 | 0 | NO | 2 | 0 | 594472 | 20020220 | 22 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | REG STA | BODY OF PIPE |  | STEEL |  | 4 | 0.188 |  |  | 1963 | 1963 | ABOVE GROUND |  | SCOTT DOYLE | 5013774554 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A REGULATOR STATION SERVING APPROXIMATELY 120 CUSTOMERS WAS RUN OVER BY AN ALLEGED DRUNK DRIVER. THE DRIVER WAS TAKEN TO THE HOSPITAL AND TREATED FOR INJURIES ASSOCIATED WITH THE VEHICLE ACCIDENT.
2025-01-31 10:21 | YES | NO | 20020044 | 2002-03-14 | 18308 | SIERRA PACIFIC POWER CO | 1170 GENTRY WAY SPACE #'S 17 AND 19 | RENO | WASHOE | NV | 8 9502 | 3 | NO | 1447 | 2002-02-07 | 0 | 0 | 84000 | 54560.1184 | 131733.6293 | NO | 1 | 10 | 593379 | 20020207 | 37 | 40 | BY TEST | 50 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | METER SET ASSEMBLY & SERVICE LINE | OTHER | REGULATOR AND METER | STEEL |  | 0.75 | 0.113 | API 5L A25 |  | 1965 | 1966 | ABOVE GROUND |  | TOM CLIFTON | 7758343265 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | MOBILE HOME FIRE CAUSED SUBSEQUENT DAMAGE TO TWO METER MANIFOLD AND REGULATOR. DAMAGE TO METERS AND REGULATOR RESULTED IN A RELEASE OF GAS WHICH IGNITED CAUSING FURTHER DAMAGE TO METERS AND REGULATOR.
2025-01-31 10:21 | NO | NO | 20020045 | 2002-03-15 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 8933 GARDT STREET | FORT WAYNE | ALLEN | IN | 46818- | 3 | NO | 1208 | 2002-02-05 | 0 | 0 | 75000 | 48714.3914 | 117619.3119 | NO | 0 | 30 | 593125 | 20020205 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ASTM D2513 | UPONOR | 1982 | 1982 | UNDER GROUND OR UNDER WATER |  | DON J. TOKOLY | 2196474770 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | THIRD PARTY CONTRACTOR EXCAVATING ALONG OUTSIDE PERIMETER OF HOUSE STRUCK PLASTIC GAS SERVICE LINE CAUSING IT TO LEAK. GAS IGNITED AND BURNED PORTION OF THE STRUCTURE. NO INJURIES RESULTED. LOCATES WERE NOT REQUESTED PRIOR TO INCIDENT.
2025-01-31 10:21 | YES | YES | 20020047 | 2002-03-18 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 3017 WARBORO ROAD | MIDLOTHIAN | CHESTERFIELD | VA | 2 3112 | 3 | NO | 1549 | 2002-02-19 | 0 | 1 | 120000 | 77943.0263 | 188190.899 | NO | 1 | 22 | 594446 | 20020219 | 54 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | HIGH VOLUME TAPPING TEE | FITTING |  | POLYETHYLENE PLASTIC |  | 2 |  | ASTM D3261 | CENTRAL PLASTICS | 2001 | 2002 | OTHER | EXCAVATED MAIN | NORMAN G DUREN | 8043235312 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AN UNINTENTIONAL RELEASE OF NATURAL GAS AND SUBSEQUENT IGNITION CONSUMED A PLASTIC PIPELINE FACILITY AND APPURTENANCES PRESENT DURING TIE-IN AND BYPASS OPERATIONS ASSOCIATED TO THE RELOCATION OF AN EXISTING 6" PLASTIC MAIN. THE RELEASE OF GAS OCCURRED AFTER THE NEW PLASTIC MAIN HAD BEEN TIED IN TO THE EXISTING MAIN AND ONE OF TWO - 2" PLASTIC BYPASSES REMAINED TO BE ABANDONED. EACH PLASTIC BYPASS UTILIZED TWO - 2" HIGH VOLUME TAPPING TEES AND A SHORT SECTION OF 2" PLASTIC PIPE BETWEEN EACH TEE. ALTHOUGH THE CAUSE OF THE RELEASE OF GAS IS NOT KNOWN FOR CERTAIN, THE RELEASE OF GAS MAY HAVE OCCURRED DUE TO THE ABSENCE OF, OR DAMAGE TO A NEOPRENE O-RING BETWEEN THE TAPPING WRENCH AND THE HIGH VOLUME TAPPING TEE, WHICH PERMITTED GAS TO ESCAPE. DURING NORMAL TAPPING OPERATIONS, GAS IS CONTAINED WITHIN THE HIGH VOLUME TAPPING TEE AND TAPPING TEE WRENCH CONFIGURATION. THE SOURCE OF IGNITION IS BELIEVED TO HAVE BEEN STATIC ELECTRICITY GENERATED AS A RESULT OF SEATING THE TAPPING TEE CUTTER IN PREPARATION FOR ABANDONMENT OF THE SECOND 2" BYPASS.
2025-01-31 10:21 | NO | NO | 20020048 | 2002-03-20 | 4483 | ENSTAR NATURAL GAS CO | 271 E PARK AVE | WASILLA |  | AK | 99654- | 2 | NO | 207 | 2002-03-08 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 2 | 3 | 596003 | 20020308 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | DRISCOPIPE | M 8000 HDPE | 1984 | 1984 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON FRIDAY MORNING, MARCH 8, 2002, AT APPROXIMATELY 2:07 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIEDBY THE WASILLA FIRE DEPARTMENT OF A FIRE AT 271 E PARK AVE, WASILLA, AK. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A SMALL COMMERICAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER. CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AT 4:10 AM ADT. THE ORIGIN OF FIRE HAS NOT BEEN DETERMINED. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20020049 | 2002-03-22 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1317 PALISADES BEACH RD | SANTA MONICA | LOS ANGELES | CA |  | 3 | NO | 1013 | 2002-03-01 | 0 | 0 | 1000000 | 649525.2189 | 1568257.4917 | NO | 1 | 25 | 595360 | 20020301 | 43 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 |  |  |  | 0 | 1963 | UNDER PAVEMENT |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-12-04 | YES | 3 | PAINT | YES | NO DATA |  | CONTRACTOR STRUCK STEEL SERVICE WHILE CUTTING CONCRETE, WHICH IGNITED, DAMAGING BUILDING AND CONTENTS.
2025-01-31 10:21 | YES | NO | 20020050 | 2002-03-28 | 20010 | U G I CORP | 2802 NORTHAMPTON ST | PALMER | NORTHAMPTON | PA | 1 8045 | 3 | NO | 28 | 2002-01-11 | 0 | 0 | 150000 | 97428.7828 | 235238.6238 | NO | 1 | 34 | 590816 | 20020111 | 58 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.28 | UNKNOWN | UNKNOWN | 0 | 1931 | UNDER PAVEMENT |  | DAVID R HANNUM | 6107963507 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | NATURAL GAS LEAKING FROM A CRACKED FOUR-INCH (4") BARE STEEL MAIN APPARENTLY FOLLOWED THE SANITARY SEWER TRENCH AND MIGRATED INTO HOUSE 2802 NORTHAMPTON STREET. PALMER TOWNSHIP. UNKNOWN IGNITION SOURCE CAUSED AND EXPLOSION. THE CAUSE OF THE CRACK REMAINS UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 20020051 | 2002-03-28 | 15462 | PECO ENERGY CO | 28-30, 34 WEST STATE STREET | DOYLESTOWN | BUCKS | PA | 1 8907 | 3 | NO | 300 | 2002-03-03 | 0 | 0 | 150000 | 97428.7828 | 235238.6238 | NO | 1 | 0 | 595485 | 20020303 | 0.2 | 66.7 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 | ASTM D2513 | PLEXCO | 0 | 1998 | UNDER PAVEMENT |  | T MARK ANDRAKA | 6109411641 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20020052 | 2002-03-28 | 15462 | PECO ENERGY CO | 831 CHAPEL RD | ROYERSFORD | MONTGOMERY | PA | 1 9468 | 2 | NO | 1343 | 2002-03-09 | 0 | 0 | 200000 | 129905.0438 | 313651.4983 | NO | 1 | 20 | 596213 | 20020311 | 15 | 66.7 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.9 | ASTM D2513 | PLEXCO | 0 | 1981 | UNDER GROUND OR UNDER WATER |  | T MARK ANDRAKA | 6109411641 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA
2025-01-31 10:21 | YES | NO | 20020053 | 2002-04-01 | 31348 | TXU GAS DISTRIBUTION | 400 VILLAGE COMMONS | GEORGETOWN | WILLIAMSON | TX | 7 8628 | 3 | NO | 1656 | 2002-02-20 | 0 | 0 | 250000 | 162381.3047 | 392064.3729 | NO | 2 | 15 |  | 20020220 | 18 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A NON-ONCOR EXCAVATOR DAMAGED A GAS MAIN. THE ESCAPING GAS IGNITED AND THE BULLDOZER BURNED.
2025-01-31 10:21 | YES | NO | 20020054 | 2002-04-09 | 15329 | PEOPLES GAS LIGHT & COKE CO | 107TH STREET &TROY ST. | CHICAGO | COOK | IL |  | 3 | YES | 1335 | 2002-02-26 | 0 | 0 | 200000 | 129905.0438 | 313651.4983 | NO | 2 | 50 |  | 20020226 | 20 | 24.9 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  |  |  | 0 | 1940 | UNDER GROUND OR UNDER WATER |  | THOMAS C. ZIEGENFUSS | 3122404682 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-02-20 | YES | 3 | 2002-02-20 | YES | NO DATA |  | ON FEBRUARY 26, 2002, EMPLOYEES OF THE CITY OF CHICAGOS SEWER DEPARTMENT WERE PERFORMING WORK IN THE PARKWAY IN FRONT OF 3140 W. 107TH STREET. IN THE COURSE OF THEIR WORK, THE SEWER DEPARTMENT CREW DUG AN EXCAVATION IN THE PARKWAY AND EXPOSED A 6-INCH CAST IRON MEDIUM PRESSURE NATURAL GAS MAIN AND A 20-INCH CAST IRON MEDIUM PRESSURE NATURAL GAS MAIN, BOTH OWNED BY PEOPLES GAS. SOMEHOW DURING THEIR WORK, THE SEWER DEPARTMENT EMPLOYEES SEVERED THE 6-INCH MAIN, THEREBY CAUSING A GAS LEAK. THE ESCAPING GAS WAS IGNITED. WE BELIEVE THAT THE SOURCE OF IGNITION WAS A PROPANE HEATER BEING USED BY THE SEWER DEPARTMENT CREW NEAR THE EDGE OF EXCAVATION. THE FIRE DAMAGED TWO HOMES, ONE BACKHOE AND TWO TREES. IT WAS REPORTED THAT TWO SEWER DEPARTMENT EMPLOYEES SUSTAINED MINOR BURNS.PEOPLES GAS SHUT DOWN BOTH THE 6-INCH AND THE 20-INCH MAINS TO ELIMINATE THE SOURCE OF GAS AND TO PROTECT PUBLIC SAFETY. APPROXIMATELY 4,500 CUSTOMERS LOST GAS SERVICE WHEN PEOPLES GAS SHUT DOWN THE TWO MAINS.
2025-01-31 10:21 | YES | NO | 20020055 | 2002-04-11 | 4060 | DOMINION EAST OHIO | INTERSECTION OF LEE RD & LIBBY RD | MAPLE HEIGHTS | CUYAHOGA | OH | 4 4137 | 3 | NO | 1453 | 2002-03-11 | 0 | 0 | 1000000 | 649525.2189 | 1568257.4917 | NO | 1 | 0 |  | 20020311 | 87 | 95 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT |  | STEEL |  | 20 | 0.25 |  |  | 1941 | 1941 | UNDER GROUND OR UNDER WATER |  | BRIAN D. WITTE | 2167366845 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | THE CAUSE OF THE INCIDENT WAS A CONTRACTOR WORKING ON THE INSTALLATION OF A SEWER LINE AT THE INTERSECTION OF LEE AND LIBBY ROADS IN MAPLE HEIGHTS, OHIO. DURING THE CONSTRUCTION PHASE OF EXCAVATION A 6 INCH VALVE AND FLANGE ATTACHED TO A 24 INCH 90 PSIG WATER MAIN WAS DISTURBED WITH THE RESULT BEING A SIGNIFICANT WATER RELEASE INTO THE DITCH. THE WATER MAIN BREAK OCCURRED AROUND 11:00 AM AND WATER BEING RELEASED INTO THE DITCH STARTED TO ERODE AND UNDERMINE THE GROUND UNDER OUR DISTRIBUTION 20" INTERMEDIATE PRESSURE PIPELINE. AROUND 2:53 PM WITH THE WATER STILL BEING RELEASED FROM THE WATER MAIN BREAK THE GROUND HAD BECOME SO UNDERMINED THAT OUR PIPELINE NO LONGER HAD UNDERGROUND SUPPORT AND IT COLLAPSED AND SEPARATED AT A DRESSER COUPLING WHICH JOINED THE PIPELINE TOGETHER AND GAS BEGAN TO FILL THE INTERSECTION AND SURROUNDING AREA. GAS CONTROL RECOGNIZED THERE WAS AN ABNORMAL SITUATION OCCURRING AND IMMEDIATELY CALLED THE CLEVELAND EASTERN SHOP SUPERVISOR TO ALERT HIM AND TO DISPATCH A CREW TO INVESTIGATE. AT 3:20 PM DOMINION EAST OHIO PERSONNEL WERE ON SITE AND RECOGNIZED GAS WAS BLOWING FROM AN APPARENT CONTRACTOR DIG IN. THEY ASSESSED THE SITUATION AND MADE THE IMMEDIATE DECISION TO CLOSE THREE GATE VALVES THAT WOULD ISOLATE THE PIPELINE. AT 3:32 PM THE DOMINION EAST OHIO SUPERVISOR ON SITE CALLED GAS CONTROL TO INFORM THEM THAT THE GAS HAD CAUGHT FIRE AND PROPERTY AND AUTOMOBILES WERE BEING DAMAGED BUT NO INJURIES TO ANY HUMANS HAD OCCURRED. LOCAL FIRE, RESCUE AND POLICE DEPARTMENTS HAD ALL ARRIVED AT THE SITE AND WERE WORKING IN CONJUNCTION WITH ALL INVOLVED TO HELP PUT OUT THE FIRE AND PROTECT THE PEOPLE IN THE AREA. THE FIRE WAS EXTINGUISHED AROUND 3:50 PM WITH SIGNIFICANT FIRE DAMAGED TO LOCAL ESTABLISHMENTS, INFRASTRUCTURE AND AUTOMOBILES IN THE VICINTY. THE DAMAGED PORTION OF THE 20" PIPELINE WAS REPLACED WITH NEW 20" PIPE WHICH WAS JOINED BY WELDED JOINTS AND RECONNECTED AT THE ENDS BY DRESSER COUPLINGS AND REINFORCED WITH LUGS TO ADD EXTRA SUPPORT TO THE PIPELINE. TO MINIMIZE THE POSSIBILITY OF A RECURRENCE OF THIS SITUATION DOMINION EAST OHIO WILL WORK WITH THE CONTRACTOR PERFORMING THE SEWER PROJECT TO LUG ANY EXPOSED DRESSER COUPLED PIPE IT EXPOSES IN THE FUTURE OF THIS PROJECT IN MAPLE HEIGHTS. THE CONTRACTOR WILL BE ENCOURAGED TO CONTINUE TO USE AND SUPPORT THE OHIO UTILITIES PROTECTION SYSTEM. ADDITIONALLY, EACH DOMINION EAST OHIO DIVISION MANAGER WILL BE INFORMED OF THE DETAILS OF THIS INCIDENT SO THAT IT CAN BE REVIEWED WITH THE APPROPRIATE PERSONNEL IN THEIR DIVISION.
2025-01-31 10:21 | YES | NO | 20020056 | 2002-04-29 | 4483 | ENSTAR NATURAL GAS CO | 101 E 9TH AVE | ANCHORAGE |  | AK | 9 9501 | 3 | NO | 320 | 2002-04-09 | 0 | 0 | 4000000 | 2598100.8756 | 6273029.9667 | NO | 4 | 55 | 598955 | 20020409 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.188 | DRISCOPIPE | 8000 HDPE | 1980 | 1980 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON TUESDAY MORNING, APRIL 9, 2002 AT APPROXIMATELY 3:20 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 108 E 8TH STREET, ANCHORAGE, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND THE 4-STORY ASPEN HOTEL (STILL UNDER CONSTRUCTION) ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER TO AN ADJACENT COMMERCIAL BUILDING APPROXIMATELY 25 ACROSS THE ALLEY AT 101 E 9TH AVENUE, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION REPAIR CREW WAS CALLED IN TO DIG UP AND SHUT OFF THE GAS. THE HEAT FROM THE FIRE AND FALLING DEBRIS PREVENTED DIGGING UP AND SHUTTING DOWN THE SERVICE LINE. THE MAIN WAS DUG UP APPROXIMATELY 200 AWAY AND SQUEEZED OFF AT 8:25 AM AST. THE FIRE IS UNDER INVESTIGATION BY THE ANCHORAGE FIRE DEPARTMENT AND BUREAU OF ALCOHOL, TOBACCO AND FIREARMS. NATURAL GAS FROM ENSTARS FACILITIES IS NOT SUSPECTED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20020057 | 2002-04-23 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | 831 HARRISON CITY ROAD | LEVEL GREEN | WESTMORELAND | PA |  | 3 | NO | 2045 | 2001-01-04 | 0 | 0 | 95104 | 62747.4343 | 151501.637 | NO | 7 | 0 | 599079 | 20010104 | 15 | 30 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.249 |  |  | 0 | 1959 | WITHIN/UNDER BUILDING |  | WESLEY A SOYSTER | 4123953381 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | ON THURSDAY, JANUARY 4, 2001, AN EXPLOSION OCCURRED AT A CAR WASH AT 831 HARRISON CITY ROAD, LEVEL GREEN, WESTMORELAND COUNTY, PA AT 8:45 PM. INITIALLY, THE EXPLOSION WAS REPORTED TO THE PENNSYLVANIA PUBLIC UTILITY COMMISSION GAS SAFETY DIVISION VIA A "COURESTY CALL". A FORMAL REPORT WAS NOT REQUIRED AS DAMAGE ESTIMATES WERE APPROXIMATELY $20,000. A CRACK IN EQUITABLES 4-INCH DISTRIBUTION MAIN WAS REPAIRED LATER THAT EVENING AND SERVICE RESTORED 1/5/01. ON APRIL 8, 2002, EQUITABLE RECEIVED A CALL FROM MR. STEVE HURBANEK OF THE PENNSYLVANIA PUBLIC UTILITY COMMISSION GAS SAFETY DIVISION. MR. HURBANEK SAID THAT ACTUAL DAMAGES RESULTING FROM BUILDING AND EQUIPMENT PERSONAL PROPERTY, AND BUSINESS LOSS NOW TOTALED $95, 104.19. THIS INFORMATION WAS OBTAINED FROM A "STATEMENT OF ACTUAL CASH VALUE". MR. HURBANEK ADVISED EQUITABLE TO MAKE TELEPHONIC AND WRITTEN REPORTS AS OUTLINED IN 191.5 AND 191.9. THUS, EQUITABLE MAKES THIS REPORT BECAUSE OF THE CHANGE IN DAMAGES NOTED ABOVE. EQUITABLE ALSO MADE TELEPHONIC REPORT APRIL 10, 2002 AT 8:25 AM. THE TELEPHONIC REPORT NUMBER IS 599079.
2025-01-31 10:21 | NO | NO | 20020058 | 2002-04-23 | 15462 | PECO ENERGY CO | BALTIMORE PIKE @ UNION AVENUE | LANSDOWNE | DELAWARE | PA | 1 9050 | 3 | NO | 1115 | 2002-03-21 | 0 | 0 | 5000 | 3247.6261 | 7841.2875 | YES | 1 | 8 | 597236 | 20020321 | 20 | 33 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.316 | ASTM D2513 | DU PONT | 0 | 1988 | UNDER PAVEMENT |  | MARK C CONNORS | 6109411583 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-03-19 | NO | 0 |  | YES | NO DATA |  | CONTRACTOR CALLED FOR A PRIVATE PROPERTY, LOCATE IN NOVEMBER OF 2001. CONTRACTOR HAD CALLED FOR ANOTHER LOCATE (FOR EXCAVATION IN PAVING) ON 3/19/02 AND WAS NOT TO BEGIN EXCAVATING UNTIL 3/22/02 AFTER 1:30PM (72 HOURS AFTER THE CALL). THE DAMAGE OCCURRED AT 11:15AM ON 3/21/02 AS THE CONTRACTOR WAS USING MARKS FROM NOVEMBER 2001.
2025-01-31 10:21 | NO | NO | 20020059 | 2002-04-19 | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 1105 CAPITAL HILL DRIVE | JEFFERSONVILLE | CLARK | IN | 4 7130 | 3 | NO | 1632 | 2002-03-20 | 0 | 0 | 60000 | 38971.5131 | 94095.4495 | NO | 2 | 8 | 597180 | 20020320 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0.75 |  | SCH 80 A53A | RW LYALL | 1998 | 1998 | ABOVE GROUND |  | RICK L SLAGLE | 8124914611 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20020060 | 2002-04-15 | 15259 | PENNSYLVANIA GAS & WATER CO | 403 CHURCH STREET | HONESDALE | WAYNE | PA | 18431- | 3 | NO | 128 | 2002-04-03 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 0 | 23 | 598373 | 20020403 | 0.25 | 55 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | GAS METER | OTHER | GAS METER | 1 | 0.9 | 275 | EQUIMETER | 1999 | 1999 | ABOVE GROUND |  | ANTHONY M DECESARIS | 5708298870 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AN INDIVIDUAL DRIVING A TOYOTA PICKUP TRUCK, WHILE UNDER THE INFLUENCE OF ALCOHOL, LEFT THE ROAD AND HIT A MULTIPLE FAMILY DWELLING INCLUDING A MULTIPLE METER SET DESTORYING BOTH METERS AND ASSOCIATED PIPING (AFTER THE REGULATOR) CAUSING THE RELEASE OF GAS AND SUBSEQUENT FIRE.
2025-01-31 10:21 | NO | NO | 20020061 | 2002-04-16 | 3600 | DUMAS, CITY OF | 223 SPRUCE | DUMAS | MOORE | TX | 7 9029 | 3 | NO | 0 | 2002-03-20 | 0 | 0 | 55000 | 35723.887 | 86254.162 | NO | 0 | 0 |  |  | 25 | 60 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NOTHING FAILED | CAST IRON | [5 empty] | 0 | 0 | ABOVE GROUND |  | PATTY STAHL | 8069354707 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | FRONTEND LOADER PICKING UP DEBRIS AND TRASH IN THE ALLEY, HIT REGULATOR AND KNOCKED OFF METER SET.
2025-01-31 10:21 | YES | NO | 20020062 | 2002-05-07 | 2596 | COLUMBIA GAS OF OHIO INC | 29150 GLENWOOD ROAD | PERRYSBURG | WOOD | OH | 4 3551 | 2 | NO | 1358 | 2002-04-04 | 0 | 0 | 500000 | 324762.6094 | 784128.7458 | NO | 0 | 27 |  | 20020404 | 50 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | OTHER | ALUMINUM METER/ABOVE GROUND | 1.25 | 0.14 | API-5L | UNKNOWN | 0 | 1999 | ABOVE GROUND |  | CHRISTINE L MAYNARD | 6144602240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A PERSON WITH A HISTORY OF SEIZURES LOST CONTROL OF HIS VEHICLE, TRAVELED OFF THE MAIN ROAD, TRAVELED ACROSS A FIELD, AND HIT THE FENCED METER SETTING LOCATED AT 29150 GLENWOOD ROAD IN PERRYSBURG, OH, WHICH RESULTED IN GAS ESCAPING FROM THE DAMAGED METER SETTING. AFTER A PASSERBY REMOVED THE PERSON FROM THE WRECKED VEHICLE, THE GAS IGNITED AND THE BUILDING CAUGHT ON FIRE. THE FIRE DEPARTMENT WAS DISPATCHED TO THE SCENE AT 13:58; COH WAS NOTIFIED AT 14:02; COH SERVICE TECHNICIAN ARRIVED ON SITE AND IMMEDIATELY SHUT GAS OFF AT THE CURB VALVE AT 14:25. THE PERSON OPERATING THE VEHICLE WAS KILLED AS A RESULT OF INJURIES SUSTAINED FROM THE IMPACT OF THE ACCIDENT; THE FATALITY WAS NOT GAS RELATED.
2025-01-31 10:21 | YES | NO | 20020063 | 2002-03-21 | 15359 | PEOPLES NATURAL GAS | 325 55TH STREET NE LOT 89 | ROCHESTER | OLMSTED | MN | 5 5906 | 3 | NO | 1155 | 2002-02-13 | 0 | 0 | 140000 | 90933.5306 | 219556.0488 | NO | 0 | 15 |  | 20020213 | 50 | 66 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTM D-2513 | PLEXCO | 1990 | 1990 | UNDER PAVEMENT |  | MIKE MCLAUGHLIN | 2188782212 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA
2025-01-31 10:21 | NO | NO | 20020064 | 2002-05-03 | 2364 | CINCINNATI GAS & ELECTRIC CO | 802 15TH AVENUE | MIDDLETOWN | BUTLER | OH | 4 5044 | 4 | Null | 1211 | 2002-04-06 | 0 | 0 | 75000 | 48714.3914 | 117619.3119 | NO | 0 | 3 | 598701 | 20020406 |  |  |  |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | FITTING |  | STEEL | [5 empty] | 0 | 0 | NO DATA |  | RANDALL L SUTTLES | 5132873921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | EXPLOSION STILL UNDER INVESTIGATION. 5-31-02 GAS SERVICE FAILED INSIDE THE HOUSE DUE TO EXCESSIVE INTERNAL STRESS ON THE PIPE. THE FILL HAD NOT BEEN SUITABLY COMPACTED AND IT SETTLED UNDER THE LOAD OF THE OVERLYING FILL.
2025-01-31 10:21 | NO | NO | 20020065 | 2002-05-02 | 4483 | ENSTAR NATURAL GAS CO | W GODIN DR | BIG LAKE |  | AK | 9 9652 | 2 | NO | 2307 | 2002-04-13 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 1 | 38 | 599548 | 20020414 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.188 |  | DRISCOPIPE | 2000 | 2000 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY EVENING, APRIL 13, 2002, AT APPROXIMATELY 11:07 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE BIG LAKE FIRE DEPARTMENT OF A FIRE ON GODIN DRIVE, NEAR BEAVER LAKE (NE 1/4 SECTION 17, T17NRSW) ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A SMALL AIRCRAFT HANGAR ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AT 12:45 AM ADT, APRIL 14, 2002. THE FIRE IS BELIEVED TO HAVE FROM A WOODSTOVE. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20020066 | 2002-05-15 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 13217 ROBSON | DETROIT | WAYNE | MI |  | 3 | NO | 1438 | 2002-04-16 | 0 | 1 | 100000 | 64952.5219 | 156825.7492 | NO | 2 | 0 | 599945 | 20020417 | 0.25 | 0.25 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER FUEL LINE | NO DATA |  | STEEL | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | LARRY CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20020068 | 2002-06-03 | 4483 | ENSTAR NATURAL GAS CO | 8311 KIP COURT | ANCHORAGE |  | AK | 99507- | 2 | NO | 647 | 2002-05-18 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 0 | 53 | 604984 | 20020518 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | DRISCOPIPE | UNKNOWN | 1981 | 1981 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY MORNING, MAY 18, 2002 AT APPROXIMATELY 6:47 AM ADT, ENSTAR NATURAL GAS COMPANY WAS ASKED TO RESPOND TO A HOUSE FIRE AT 8311 KIP COURT, ANCHORAGE, AK. THE FIRE BURNED ENSTARS SERVICE LINE RISER. THE POLYETHYLENE GAS SERVICE LINE INSIDE THE STEEL RISER MELTED, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED BY ENSTAR PERSONNEL AT 7:40 AM ADT. FIRE DEPARTMENT OFFICALS BELIEVE A BARBEQUE GRILL ON THE DECK CAUSED THE FIRE. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20020069 | 2002-06-13 | 31635 | NSTAR ELECTRIC GAS | 9 BONITO DRIVE | FRAMINGHAM | MIDDLESEX | MA | 1701 | 4 | NO | 822 | 2002-05-24 | 0 | 0 | 150000 | 97428.7828 | 235238.6238 | NO | 0 | 25 | 606148 | 20020524 | 55 | 60 | BY CFR 192.619(A)(3) |  | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER | THREADS ON PIPE AT REGULATOR | STEEL |  | 1 | 0.125 |  |  | 0 | 1958 | WITHIN/UNDER BUILDING |  | DARRELL W HOBART | 5083056885 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 08:21 AM ON MAY 24, 2002 A BACKHOE OPERATOR EMPLOYED BY PIPELINE CONSTRUCTION, A CONTRACTOR FOR NSTAR GAS, INADVERTENTLY PULLED A 1" STEEL SERVICE TO 9 BONITO DRIVE, FRAMINGHAM. THE CONTRACT CREW WAS EXCAVATING TO PERFORM A SERVICE TIE-OVER FROM AN EXISTING 2" STEEL MAIN TO A NEW 4" PLASTIC MAIN. THE SERVICE PULLED THROUGH THE CELLAR WALL AND BROKE AT THE THREADS UNDER THE SERVICE REGULATOR. AN NSTAR EMPLOYEE WAS IN THE CELLAR ATTEMPTING TO SHUT OFF THE SERVICE LINE VALVE WHEN THE SERVICE WAS PULLED. THE NSTAR EMPLOYEE IMMEDIATELY ATTEMPTED TO EVACUATE THREE PERSONS FROM THE HOUSE. AN EXPLOSION OCCURRED IN THE HOUSE AT APPROX 08:22 A.M. TWO PERSONS WERE STILL IN THE HOUSE WHEN THE EXPLOSION OCCURRED BUT ESCAPED WITHOUT MAJOR INJURY. ONE PERSON REPORTED MINOR SCRAPES ON HER WRIST. THE FRAMINGHAM FIRE DEPARTMENT WAS IMMEDIATELY NOTIFIED BY NSTAR AND TWO GAS COMPANY CREWS WERE DISPATCHED TO THE SITE. THE SERVICE TEE WAS PINNED OFF AT 08:47 A.M. THE FIRE DEPARTMENT THEN EXTINGUISHED THE ENSUING FIRE. AN NSTAR EMPLOYEE HAD PREVIOUSLY PROPERLY MARKED THE MAIN AND SERVICE LINES ON BONITO DRIVE. DEPTHS OF THE MAIN AND SERVICES WERE UNKNOWN AT THE TIME THE EMPLOYEE MARKED THE LINES. THE SERVICE TO #9 BONITO WAS 4 2" DEEP AT THE SERVICE TEE, WHICH HAD BEEN EXCAVATED PRIOR TO THE INCIDENT. APPROXIMATELY 3 FROM THE EXISTING 2" STEEL MAIN, WHERE THE BACKHOE OPERATOR WAS EXCAVATING TO MAKE MORE ROOM FOR THE SERVICE TIE-OVER WHEN THE INCIDENT OCCURRED, THE SERVICE LINE CHANGED ELEVATION TO 2 8" DUE TO A DRAIN LINE. DURING THE INVESTIGATION IT WAS DISCOVERED THAT THE BACKHOE OPERATOR BELIEVED HE COULD EXCAVATE SAFELY WITH THE BUCKET TO DEPTH OF APPROXIMATELY 4 WHEN HE ACTUALLY PULLED THE SERVICE LINE AT 2 8".
2025-01-31 10:21 | YES | YES | 20020070 | 2002-06-14 | 31632 | NORTHWESTERN ENERGY LLC | 825 W GALENA | BUTTE | SILVER BOW | MT | 59701- | 3 | NO | 1842 | 2002-06-01 | 0 | 1 | 10000 | 6495.2522 | 15682.5749 | NO | 1 | 30 | 607961 | 20020601 | 15 | 17 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | NO DATA |  | 0.75 | 0.154 | BLACK IRON | UNKNOWN | 1930 | 1931 | UNDER PAVEMENT |  | LEONARD W LEVEAUX | 4064972345 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | YES | NO DATA |  | STRUCTURE DEMOLITION RECENTLY AT AN ADJACENT PROPERTY MAY HAVE CAUSED UNANTICIPATED LOADS ON THE CURB BOX. WEATHER CONDITIONS WERE ALSO VERY WET.
2025-01-31 10:21 | YES | NO | 20020071 | 2002-06-19 | 12876 | QUESTAR GAS COMPANY | 6538 EAST HWY 40 | FORT DUCHESNE | UINTA | UT | 84025- | 3 | NO | 2210 | 2002-05-22 | 0 | 0 | 92000 | 59756.3201 | 144279.6892 | NO | 1 | 50 | 605881 | 20020522 | 45 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | CLOTH REINFORCED | 0.75 |  | 61 | LANCASTER | 1988 | 1998 | ABOVE GROUND |  | TROY D SORENSON | 8013243452 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | AS A RESULT OF ARSON THE INTENSE HEAT FROM THE BUILDING FIRE CAUSED THE QUESTAR OWNED SERVICE REGULATOR TO FAIL AND RELEASE GAS. WITH THIS RELEASE OF GAS, THERE WAS A SECONDARY IGNITION AT THE REGULATOR.
2025-01-31 10:21 | YES | NO | 20020072 | 2002-06-14 | 4483 | ENSTAR NATURAL GAS CO | 2875 INTERNATIONAL RD | ANCHORAGE |  | AK | 99519- | 3 | NO | 407 | 2002-05-26 | 0 | 0 | 350000 | 227333.8266 | 548890.1221 | NO | 2 | 3 | 606759 | 20020526 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.626 | 0.09 | DRISCOPIPE |  | 1986 | 1986 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY MORNING, MARCH 26, 2002, AT APPROXIMATELY 4:07 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT OF A FIRE AT 2875 INTERNATIONAL AIRPORT RD, ANCHORAGE, AK. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A SIX-CAR GARAGE ON FIRE. AN EXPLOSION KNOCKED DOWN THE WALL AND THE SERVICE LINE WAS BROKEN OFF JUST BELOW THE SHUTOFF COCK. NATURAL GAS WAS BLOWING AWAY FROM THE FIRE AND DID NOT IGNITE. THE SERVICE LINE WAS DUG UP AND PINCHED OFF. THE ORIGIN OF THE FIRE HAS NOT BEEN DETERMINED, BUT NATURAL GAS FROM ENSTARS FACILITIES IS NOT SUSPECTED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE OR EXPLOSION.
2025-01-31 10:21 | YES | YES | 20020073 | 2002-06-25 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) | 2012 N MERIDIAN | COZAD | DAWSON | NE | 69130- | 3 | NO | 316 | 2002-05-20 | 0 | 1 | 60000 | 38971.5131 | 94095.4495 | NO | 0 | 30 | [6 empty] | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER'S HOUSE | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | JAMES PHILLIPS | 3039147753 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | INCIDENT IS BEING INVESTIGATED BY THE STATE FIRE MARSHALLS OFFICE. THE CUSTOMER ALLEGEDLY LOOSENED A NATURAL GAS FITTING INSIDE THE HOUSE AND SUPPLIED IGNITION FOR A GAS EXPLOSION. HOUSE WAS DESTOYED BY THE EXPLOSION AND THE CUSTOMER WAS TAKEN TO A HOSPITAL BURN CENTER IN CRITICAL CONDITION. ONE PERSON INJURED, 20 EVACUATED, APPROXIMATELY $60,000 IN PROPERTY DAMAGE.
2025-01-31 10:21 | NO | NO | 20020074 | 2002-06-25 | 2748 | CONSUMERS POWER CO | 1681 CHRISTINE TERRACE | MADISON HEIGHTS | OAKLAND | MI | 4 8071 | 3 | NO | 1618 | 2002-05-15 | 0 | 0 | 55000 | 35723.887 | 86254.162 | NO | 0 | 56 |  | 20020516 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.66 | 0.166 | ASTM D2513 | PHILLIPS | 1993 | 1993 | UNDER GROUND OR UNDER WATER |  | JOAQUIN J AFFONSO | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR HIT 1 1/4 INCH PLASTIC PIPELINE DURING DIRECTIONAL BORING OPERATIONS. ESCAPING GAS IGNITED AND DESTROYED A SINGLE WIDE TRAILER AND CONTENTS.
2025-01-31 10:21 | YES | YES | 20020075 | 2002-07-05 | 15518 | PIEDMONT NATURAL GAS CO INC | VERDICT RIDGE RD | DENVER | LINCOLN | NC | 28037- | 3 | NO | 1330 | 2002-06-07 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 5 | 609362 | 20020607 | 60 | 75 |  |  | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  |  |  | MDPE | PERFORMANCE | 2001 | 2002 | NO DATA |  | GEORGE WALLACE | 7043643120 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | GAS ESCAPED BACKFLOWING THROUGH BYPASS TAPPING TEE.
2025-01-31 10:21 | YES | YES | 20020076 | 2002-07-05 | 20110 | UNION LIGHT HEAT & POWER CO | 515 W 19TH STREET | COVINGTON | KENTON | KY | 41014 | 4 | NO | 730 | 2002-06-06 | 0 | 2 | 2000000 | 1299050.4378 | 3136514.9834 | NO | 0 | 30 | 608820 | 20020606 | 11 |  |  |  | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | METER SET ASSEMBLY |  | VALVE |  | STEEL |  | 2 | 0.154 | ANSI B16.33 |  | 0 | 1969 | WITHIN/UNDER BUILDING |  | RANDALL SUTTLES | 5132873921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | WHILE REPLACING A DEFECTIVE VALVE ON A METER SET, GAS IGNITED CAUSING AN EXPLOSION AND BURN INJURIES TO TWO (2) COMPANY EMPLOYEES.
2025-01-31 10:21 | YES | NO | 20020077 | 2002-07-05 | 4483 | ENSTAR NATURAL GAS CO | 1405 W 27TH | ANCHORAGE |  | AK | 9 9518 | 3 | NO | 1630 | 2002-06-04 | 0 | 0 | 250000 | 162381.3047 | 392064.3729 | NO | 0 | 40 | 608461 | 20020604 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | DRISCOPIPE | M 8000 HDPE | 1981 | 1981 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON TUESDAY AFTERNOON JUNE 4, 2002, A SMALL CAR RAN INTO AN AL 800 GAS METER SET ASSEMBLY SERVING A 30 UNIT CONDOMINUM COMPLEX AT 1405 W 27TH AVENUE, ANCHORAGE, AK 99519. THE REGULATOR BROKE OFF THE RISER CAUSING A RELEASE OF NATURAL GAS. THE DRIVER OF THE CAR LEFT THE SCENE WITHOUT REPORTING THE DAMAGE SHE WAS LATER IDENTIFIED AND TRACKED DOWN. THE NATURAL GAS CAUGHT FIRE FROM AN UNKNOWN IGNITION SOURCE. THE STRUCTURE SUFFERED EXTENSIVE DAMAGE. THE GAS VALVE ON THE RISER WAS CLOSED BY THE ANCHORAGE FIRE DEPARTMENT TO STOP MOST OF THE GAS RELEASE. THE FIRE CAUSED THE POLYETHYLENE SERVICE LINE RISER TO MELT AND RELEASE A SMALL AMOUNT OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED TO STOP THE FLOW OF GAS.
2025-01-31 10:21 | NO | NO | 20020078 | 2002-07-05 | 4483 | ENSTAR NATURAL GAS CO | 19026 KLONDIKE 40 BLM X19 | EAGLE RIVER |  | AK | 99577- |  | NO | 627 | 2002-06-19 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 0 | 40 | 612215 | 20020620 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | DRISCOPIPE |  | 1977 | 1977 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON WEDNESDAY EVENING, JUNE 19, 2002 A FIRE DAMAGED A SINGLE FAMILY RESIDENCE AT 19026 KLONDIKE, EAGLE RIVER, AK. ENSTAR WAS NOT NOTIFIED OF THE FIRE. ON THURSDAY, JUNE 20, 2002, ENSTAR WAS CALLED BY THE OWNER OF THE HOME REPORTING A GAS ODOR. ENSTAR RESPONDED WITH A SERVICE TECHINICAN AND REPAIR CREW. THE SERVICE LINE TO THE STRUCTURE WAS DUG UP AND TESTED. THE SERVICE LINE FAILED THE AIR TEST. FURTHER INVESTIGATION SHOWED THE POLYETHYLENE SERVICE LINE TUBING INSIDE THE STEEL RISER HAD BEEN DAMAGED FROM THE FIRE. THE CREW PINCHED OFF THE SERVICE LINE AND CAPPED IT. THE ORIGIN OF THE FIRE HAS NOT BEEN DETERMINED, BUT NATURAL GAS FROM ENSTARS FACILITIES IS NOT SUSPECTED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE.
2025-01-31 10:21 | NO | NO | 20020079 | 2002-07-05 | 4483 | ENSTAR NATURAL GAS CO | 909 HIGH BUSH BLM LOT 34 GR 7415 | KENAI |  | AK | 99611- | 3 | Null | 1730 | 2002-06-07 | 0 | 0 | 75000 | 48714.3914 | 117619.3119 | NO | 0 | 50 | 609448 | 20020607 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | DRISCOPIPE |  | 1995 | 1995 | NO DATA |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON 6/7/02, A STRUCTURE FIRE DESTROYED A HOME/SHOP AND BURNED UP THE METER SET. THE RISER MELTED AND RELEASED GAS FROM OUR FACILITY. A SERVICE CREW EXCAVATED THE SERVICE AND CUT AND CAPPED THE SERVICE. THERE HAS BEEN NO INDICATION OF GAS INVOLVEMENT AS A CAUSE OF THE FIRE.
2025-01-31 10:21 | NO | NO | 20020080 | 2002-07-19 | 13480 | NIAGARA MOHAWK POWER CORP | WILLIAM ST | SOUTH GLEN FALLS |  | NY | 1 2803 | 3 | NO | 1056 | 2002-06-18 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 55 | 611825 | 20020618 | 99 | 99 | BY TEST | 150 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | PRESSURE RELIEF PIPING | BODY OF PIPE |  | STEEL |  |  |  | API 5L |  | 0 | 1992 | ABOVE GROUND |  | SCOTT ACKERMANN | 5187615990 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA |  | FACILITIES EMPLOYEE DAMAGE 1" STEEL TEST POINT WHILE MOWING
2025-01-31 10:21 | YES | NO | 20020081 | 2002-07-18 | 15007 | PACIFIC GAS & ELECTRIC CO | 1812 CONCORD CT | CONCORD | CONTRA COSTA | CA |  | 3 | NO | 1515 | 2002-06-21 | 0 | 0 | 151000 | 98078.3081 | 236806.8812 | NO | 1 | 10 | 612486 | 20020621 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 0.75 |  |  |  | 0 | 0 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | FIRE DEPT SAID FIRE STARTED IN TRASHCAN ON SIDE OF HOUSE, WHICH MELTED THE GAS METER, CAUSING GAS TO ESCAPE. THE ESCAPING GAS PROVIDED MORE FUEL TO THE FIRE. AN ACETYLENE TANK INSIDE THE GARAGE ALSO ADDED FUEL TO THE FIRE. GAS DID NOT CAUSE THIS INCIDENT BUT CONTRIBUTED TO THE SCOPE. THE AMOUNT OF DAMAGE ATTRIBUTABLE TO ESCAPING GAS IS NOT KNOWN.
2025-01-31 10:21 | NO | NO | 20020082 | 2002-07-09 | 13707 | NORTHERN MINNESOTA UTILITIES | 401 SOUTH CONLEY AVE | THIEF RIVER FALLS | PENNINGTON | MN | 5 6701 | 3 | NO | 1157 | 2002-06-14 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 15 | 611131 | 20020614 | 42 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | JOINT |  | STEEL |  | 2 | 0.154 |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | MIKE LAUGHLIN | 2188782212 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | OUR INVESTIGATION SUGGESTS AN EXPLOSION WAS CAUSED BY A MECHANICAL FAILURE AT A INDUSTRIAL WATER HEATER WHICH CAUSED $300,000 IN DAMAGES TO THE TURKEY PLANT.
2025-01-31 10:21 | NO | NO | 20020083 | 2002-07-15 | 4483 | ENSTAR NATURAL GAS CO | 341 E 77TH | ANCHORAGE |  | AK | 9 9518 | 3 | NO | 1110 | 2002-07-07 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 0 | 5 | 615968 | 20020708 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.875 | 0.09 | DRISCOPIPE |  | 1982 | 1982 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SUNDAY MORNING, JULY 7, 2002, TWO TEENAGERS WERE RACING CARS AND LOST CONTROL OF THEIR VEHICLES. ONE OF THE CARS HIT A BLOCK BUILDING AT 341 E 77TH ANCHORAGE. THE SECOND CAR HIT THE GAS METER ATTACHED TO THE BLOCK BUILDING AND ALSO AN ELECTRIC TRANSFORMER AND TELEPHONE PEDESTAL. ENSTAR WAS CALLED TO RESPOND TO THE BLOWING GAS BUT THE ANCHORAGE FIRE DEPARTMENT SHUT OFF THE GAS BEFORE A SERVICE TECHINICAN ARRIVED. THE INITIAL CALL WAS MADE 7/8/02 AFTER IT WAS DETERMINED THAT THE DAMAGE WOULD PROBABLY EXCEED $50,000.
2025-01-31 10:21 | YES | YES | 20020084 | 2002-08-12 | 31635 | NSTAR ELECTRIC GAS | 65 MAIN STREET | HOPKINTON | MIDDLESEX | MA | 01748- | 4 | NO | 141 | 2002-07-24 | 2 | 0 | 400000 | 259810.0876 | 627302.9967 | NO | 3 | 25 |  | 20020724 | 58 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDER INVESTIGATION | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | DARRELL W HOBART | 5083056885 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT 01:49A.M. NSTAR GAS RECEIVED A CALL FROM THE HOPKINTON FIRE DEPARTMENT THAT THERE WAS A HOUSE EXPLOSION AND BUILDING COLLAPSE AT 65 MAIN ST., HOPKINTON AND FOUR PERSONS WERE INJURED. IT WAS ALSO REPORTED THAT ONE CHILD WAS STILL IN THE BUILDING. NSTAR IMMEDIATELY DISPATCHED PERSONNEL TO THE SCENE. THE FIRST NSTAR PERSON AT THE SCENE ATTEMPTED TO SHUT OFF THE SERVICE AT 2:12 A.M. BUT WERE UNABLE TO GET ACCESS TO THE CURB VALVE DUE TO THE STRUCTURE COLLAPSING OVER THE SERVICE LINE.DISTRIBUTION CREWS THEN BEGAN SIMULTANEOUSLY LOCATING VALVES AND EXCAVATING THE 3 PLASTIC MAIN ON BOTH SIDES OF THE BUILDING. NSTAR GAS PERSONNEL CONTINUALLY CHECKED ADJACENT STRUCTURES FOR GAS READINGS. THE MAIN WAS SQUEEZED OFF AT 05:06 A.M. FOR THE REMAINDER OF THE DAY NSTAR PERSONNEL ASSISTED THE HOPKINTON FIRE DEPARTMENT, THE STATE FIRE MARSHALLS OFFICE AND THE DEPARTMENT OF TELECOMMUNICATIONS AND ENERGY WITH THE INVESTIGATION. WHEN ENOUGH OF THE COLLAPSED STRUCTURE HAD BEEN CLEARED AWAY AND NSTAR PERSONNEL WERE ABLE TO GAIN ACCESS TO THE SERVICE LINE THEY EXCAVATED AT THE FOUNDATION AND CUT AND REMOVED THE SERVICE LINE AT THE FOUNDATION. THIS SECTION OF THE SERVICE LINE WAS TURNED OVER TO THE STATE FIRE MARSHALLS OFFICE. THE REMAINDER OF THE SERVICE LINE AND THE MAIN IN FRONT OF 65 MAIN ST. WERE CAPPED AND SUCCESSFULLY PRESSURE TESTED AT 58 PSIG FROM 10:15 P.M. TO 11:20 P.M. THE PRESSURE TEST WAS CONDUCTED USING A CALIBRATED GAUGE, A CALIBRATED RECORDING CHART, A CERTIFIED DEAD WEIGHT TESTER. AS OF THE WRITING OF THIS REPORT THERE HAS BEEN NO CONCLUSIVE EVIDENCE TO DETERMINE THE CAUSE OF THE EXPLOSION.
2025-01-31 10:21 | NO | NO | 20020085 | 2002-08-19 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 14006 SWISS HILL | HOUSTON | HARRIS | TX | 77077- | 3 | NO | 1604 | 2002-06-12 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 17 |  | 20020612 | 38 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | VARIOUS |  |  |  |  | 0 | 1977 | ABOVE GROUND |  | TAL R CENTERS JR | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | DUE TO A HOUSE FIRE METER SET ASSEMBLY WAS DAMAGED AND THE ESCAPING GAS IGNITED.
2025-01-31 10:21 | YES | YES | 20020087 | 2002-09-04 | 8040 | ILLINOIS POWER CO | 100 SOUTH 78TH STREET | BELLEVILLE | ST CLAIR | IL | 6 2223 | 3 | NO | 1000 | 2002-07-12 | 0 | 1 | 350000 | 227333.8266 | 548890.1221 | NO | 0 | 25 | 616423 | 20020712 | 36 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.242 | 2406 | PLEXCO | 2001 | 2000 | UNDER GROUND OR UNDER WATER |  | J B HOLLIBAUGH | 2174246945 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 20020088 | 2002-09-05 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1855 LINCOLN AVE | EL CENTRO | IMPERIAL | CA |  | 3 | NO | 1734 | 2002-08-03 | 1 | 0 | 0 | 0 | 0 | NO | 1 | 11 | 618827 | 20020803 | 35 | 60 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 2 |  |  |  | 0 | 1988 | ABOVE GROUND |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | DRIVER LOST CONTROL OF VEHICLE, TRAVELLED OUT OF ROADWAY, ACROSS SIDEWALK, THROUGH STEEL & CONCRETE POSTS ADD STRUCK MSA; IGNITING. DRIVER DIED FROM BURN INJURIES.
2025-01-31 10:21 | YES | YES | 20020089 | 2002-09-06 | 18496 | SOUTHERN CONNECTICUT GAS CO | 309 TERRACE AVE | WEST HAVEN | NEW HAVEN | CT | 06516 | 3 | NO | 350 | 2002-08-13 | 2 | 5 | 0 | 0 | 0 | NO | 1 | 15 | 619710 | 20020813 | 49 | 50 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN, BUT PROBABLY ON THE CUSTOMERS SIDE | OTHER | UNKNOWN | NO DATA | [5 empty] | 0 | 0 | OTHER | UNKNOWN | THOMAS P CHIZINSKI | 2037957868 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE SOUTHERN CONNECTICUT GAS COMPANY (SCG) WAS NOTIFIED OF A FIRE AND EXPLOSION AT THE ORCHARD HILL RESIDENTIAL CONDOMINIUM COMPLEX, 309 TERRACE AVENUE, WEST HAVEN, CONNECTICUT AT 3:50 AM ON AUGUST 13, 2002. THE CALL CAME TO THE SCG DISPATCH CENTER FROM THE WEST HAVEN FIRE DEPARTMENT. SCG PERSONNEL RESPONDED TO THE CALL IMMEDIATELY AND THE FIRST TECHNICIAN ARRIVED AT 3:58 A.M. WHEN THE TECHNICIAN ARRIVED, A FIRE WAS IN PROGRESS AND A FULL FIRE DEPARTMENT RESPONSE WAS UNDER WAY. THE GAS METERS AND REGULATORS FOR UNITS 6. 7 AND 8 HAD BEEN DAMAGED BY THE EVENT AND COULD NOT BE REACHED. AT THE REQUEST OF THE FIRE CHIEF, THE FIRST RESPONDING TECHNICIAN BEGAN SHUTTING OFF GAS SERVICE TO ALL OF THE OTHER BUILDINGS IN THE COMPLEX. SHORTLY AFTER THE FIRST TECHNICIAN ARRIVED, OTHERS CAME AS WELL. GAS TO THE ENTIRE COMPLEX WAS SHUT OFF BY CLOSING A VALVE ON THE LINE FEEDING THE COMPLEX AT 5:05 A.M. THE CONNECTICUT DEPARTMENT OF PUBLIC UTILITIES GAS PIPELINE SAFETY UNIT (GPSU) WAS NOTIFIED AND CAME TO THE SITE. A CALL TO THE NRC TO GIVE TELEPHONE NOTICE WAS PLACED AT 7:04 A.M. BECAUSE OF A CONFIRMED FATILITY. BETWEEN 5:55 PM AND 6:15 PM., SCG PERSONNEL ISOLATED AND TESTED SCGS UNDERGROUND PIPING IN THE COMPLEX AREA. THE UNDERGROUND PIPING HELD PRESSURE AND WAS LEAK FREE AT 60 PSIG, WHICH IS THE MAOP FOR THE SYSTEM. THIS TESTING WAS OBSERVED AND SUPERVISED BY GPSU AND THE CONNECTICUT FIRE MARSHAL. BAR HOLE TESTING WAS COMMENCED AT APPROXIMATELY 4:30 A.M. AND WAS DONE IN SEVERAL AREAS OF THE CONDOMINUM COMPLEX DURING THE DAY. THE BAR HOLE TESTING SHOWED THAT NATURAL GAS HAD NOT BEEN RELEASED INTO THE SOIL FROM SCG UNDERGROUND SYSTEM. SCG HAS CONCLUDED THAT THE EXPLOSION AND FIRE WERE NOT A RESULT OF ANY LEAKAGE ON ITS SYSTEM. AT THIS POINT, SCG DOES NOT KNOW WHAT FUEL WAS IGNITED FIRST, WHERE THE ORIGIN OF THE FIRE WAS, OR WHAT THE CAUSE OF THE EVENT WAS. THE EXPLOSION DAMAGED THE METERS AND REGULATORS THAT SERVED UNITS 6, 7 AND 8. SCG IS CONTINUING TO INVESTIGATE AND IS WORKING WITH THE FIRE MARSHAL AND LOCAL AUTHORITIES.
2025-01-31 10:21 | YES | NO | 20020090 | 2002-09-11 | 18484 | SOUTHERN CALIFORNIA GAS CO | 20914 TOMLEE | TORRANCE | LOS ANGELES | CA |  | 3 | NO | 555 | 2002-08-13 | 0 | 0 | 1000000 | 649525.2189 | 1568257.4917 | NO | 1 | 45 | 619731 | 20020813 | 30 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 |  |  |  | 0 | 1961 | ABOVE GROUND |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EXPLOSION RELATED TO ESCAPING NATURAL GAS COLLECTING UNDER FUMIGATION TENT AND IGNITING.
2025-01-31 10:21 | NO | NO | 20020091 | 2002-09-18 | 31402 | SANTAQUIN CITY | 343 N PEACH | SANTAQUIN | UTAH | UT | 8 4655 | 2 | NO | 1830 | 2002-09-12 | 0 | 0 | 500 | 324.7626 | 784.1287 | NO | 3 | 30 | 622842 | 20020913 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 |  |  |  | 0 | 2000 | ABOVE GROUND |  | WADE EVA | 8017543211 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | NO |  | NO | 0 |  | YES | NO DATA |  | RAIN STORM CAUSED A MUD SLIDE WHICH PUSHED A VEHICLE. THE VEHICLE PULLED M.S.A AWAY FROM STRUCTURE AND 1/2 SERVICE LINE.
2025-01-31 10:21 | YES | NO | 20020092 | 2002-09-24 | 24015 | YANKEE GAS SERVICES CO | 108 HOLLY HILL DRIVE | UNCASVILLE | NEW LONDON | CT | 6382 | 3 | NO | 1749 | 2002-08-22 | 0 | 0 | 100000 | 64952.5219 | 156825.7492 | NO | 1 | 41 | 621045 | 20020826 | 5 | 2 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1 | 0.13 |  | NO DATA | 0 | 1963 | WITHIN/UNDER BUILDING |  | MICHAEL R FORTIER | 8064374125 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | OCCUPANT WAS USING A FLAMMABLE LIQUID TO CLEAN THE BASEMENT FLOOR AND WALLS WHICH IGNITED. THE FIRE DAMAGED THE METER SET, MELTING THE INSULATED COUPLING AND THE METER INDEX. A SMALL AMOUNT OF NATURAL GAS WAS RELEASED INTO THE FIRE.
2025-01-31 10:21 | YES | YES | 20020093 | 2002-09-19 | 621 | ARKANSAS OKLAHOMA GAS CORP | 1612 BURNHAM RD | FORT SMITH | SEBASTIAN | AR | 7 2903 | 3 | NO | 457 | 2002-09-08 | 1 | 0 | 0 | 0 | 0 | NO | 0 | 11 | 622283 | 20020908 | 25 | 50 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 0.75 |  |  |  | 0 | 0 | ABOVE GROUND |  | DAN DEHART | 4797833181 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | AN AUTO RAN OFF BURNHAM ROAD, JUMPED THE DITCH, EJECTING A PASSENGER AND CAUSING HER DEATH. THE CAR CONTINUED ON, RUNNING THROUGH A FENCE, HITTING A GAS METER SET, SEVERING THE METER SET ABOVE THE SHUT-OFF VALVE, AND CAUSING A RELEASE OF NATURAL GAS. THE RELEASE OF NATURAL GAS WAS NOT A CONTRIBUTING FACTOR IN THE DEATH. HOWEVER, THIS REPORT IS BEING SUBMITTED SINCE THERE WAS A DEATH AS A RESULT OF THE AUTO ACCIDENT AND A RELEASE OF NATURAL GAS.
2025-01-31 10:21 | YES | YES | 20020094 | 2002-09-13 | 603 | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | 3006 POPLAR ST | PINE BLUFF | JEFFERSON | AR | 7 1611 | 3 | NO | 1500 | 2002-08-21 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 5 | 620761 | 20020821 | 5.3 | 1 | BY TEST | 1.5 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.14 |  |  | 0 | 1947 | UNDER GROUND OR UNDER WATER |  | KEITH KITTINGER | 5013774669 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA |  | ELECTRIC SAW WAS USED TO CUT PIPE WHILE GAS WAS IN LINE.
2025-01-31 10:21 | NO | NO | 20020095 | 2002-09-18 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | E PARIS & SWANK | KENTWOOD | KENT | MI | 4 9503 | 2 | NO | 1010 | 2002-08-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 0 | 621193 | 20020827 | 60 | 60 | BY TEST | 60 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | OTHER PLASTIC |  | 6 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LAWRENCE K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | YES | NO DATA |  | ALL CLEAR WAS GIVEN IN ERROR BY MICHCON STAKER
2025-01-31 10:21 | YES | YES | 20020096 | 2002-09-25 | 603 | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | 2400 RICHMOND RD | TEXARKANA | BOWIE | TX | 7 5501 | 3 | NO | 1033 | 2002-08-26 | 0 | 1 | 90000 | 58457.2697 | 141143.1743 | NO | 0 | 42 | 621060 | 20020826 | 15 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.156 |  |  | 1977 | 1978 | UNDER GROUND OR UNDER WATER |  | KEITH KITTINGER | 5013774669 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR DID NOT ATTEMPT TO NOTIFY UTILITIES FOR UNDERGROUND LOCATES BEFORE OPERATING ASPHALT RECLAIMER
2025-01-31 10:21 | YES | NO | 20020097 | 2002-09-25 | 22182 | WASHINGTON GAS LIGHT CO | 211 KETTERING DR | UPPER MARLBORO | PRINCE GEORGE | MD | 2 0774 | 3 | NO | 146 | 2002-08-27 | 0 | 0 | 250000 | 162381.3047 | 392064.3729 | NO | 0 | 33 | 621121 | 20020827 | 52.7 | 55 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM |  |  | CLASS 250 | AMERICAN | 1995 | 1995 | WITHIN/UNDER BUILDING |  | JOHN H FLUHARTY JR | 7034086568 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | FIRE AND EXPLOSION TO SINGLE FAMILY HOME, WHICH CAUSED FAILURE TO METER FACE PLATE AND REGULATOR DIAPHRAM. INCIDENT IS UNDER INVESTIGATION BY THE PRINCE GEORGES COUNTY FIRE DEPARTMENT.
2025-01-31 10:21 | NO | NO | 20020098 | 2002-09-25 | 22182 | WASHINGTON GAS LIGHT CO | 7710 HAYNES POINT WAY "D" | NEWINGTON | FAIRFAX | VA | 2 2315 | 4 | NO | 340 | 2002-08-23 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 0 | 30 | 620788 | 20020823 | 2 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | ASTM A-108 | QUANEX | 0 | 1997 | WITHIN/UNDER BUILDING |  | JOHN H FLUHARTY JR | 7034086568 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null | NO DATA |  | INCIDENT (GAS EXPLOSION W/FIRE) OCCURRED DUE TO GROUND SETTLEMENT ALONG BUILDING WALL, WHICH CAUSED STRESS ON PIPE THREADS (1 STEEL SCH 40) AND CAUSED A BREAK AT BEGINNING EDGE OF A 90 DEGREE ELBOW IN THE UTILITY CLOSET.
2025-01-31 10:21 | YES | YES | 20020099 | 2002-09-18 | 15476 | T W PHILLIPS GAS & OIL CO | NEAR TOWN OF PANIC | MCCALMONT | JEFFERSON | PA |  | 2 | NO | 1045 | 2002-09-16 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 15 | 623147 | 20020917 | 25 | 60 | BY CFR 192.619(A)(3) |  | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | NO MATHERIAL FAILED | STEEL | [5 empty] | 0 | 0 | OTHER | EXCAVATION | KEITH A SWANTON | 7242872751 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | OPERATING PROCEDURE INAPPROPRIATE |  | EMPLOYEE WERE EXECUTING A 2-INCH HOT TAP INTO 4-INCH STEEL PIPELINE. DURING THE TAPPING PROCEDURE, GAS WAS EXITING A PLASTIC TRANSITION FITTING AND IGNITED. INCIDENT UNDER INVESTIGATION, HOWEVER, STATIC ELECTRICITY WAS THE APPARENT IGNITION SOURCE. TWO EMPLOYEES, TED KOLSON AND JACOB ISHMAN, SUSTAINED SECOND AND THIRD-DEGREE BURNS TO THEIR HANDS AND ARMS.
2025-01-31 10:21 | NO | NO | 20020101 | 2002-09-26 | 12684 | MONTANA - DAKOTA UTILITIES CO |  | KAYCEE | JOHNSON | WY | 8 2639 | 3 | NO | 645 | 2002-08-27 | 0 | 0 | 15000 | 9742.8783 | 23523.8624 | YES | 3 | 0 | 621160 | 20020827 | 10 | 20 | BY TEST | 20 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | NO DATA |  | NO DATA |  | NO DATA |  |  |  | cboSpec | CBOMANU | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DOUGLAS M LEE | 7012227994 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | Null |  | Null | 0 |  | Null | NO DATA |  | FLASH FLOOD CAUSED BY 7 INCH RAINFALL WITHIN 1 HR PERIOD.
2025-01-31 10:21 | NO | NO | 20020102 | 2002-09-19 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | LIVERNOIS & W LAFEYETTE | DETROIT | WAYNE | MI | 4 8208 |  | NO | 923 | 2002-07-16 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 4 | 4 | 616962 | 20020717 | 2 | 2 | BY TEST | 2 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | OTHER | [5 empty] | 0 | 0 | UNDER PAVEMENT |  | LARRY K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20020103 | 2002-09-19 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | LYON & OTTAWA | GRAND RAPIDS | KENT | MI | 4 9503 | 2 | NO | 945 | 2002-06-28 | 0 | 0 | 0 | 0 | 0 | NO | 0 | 0 | 614288 |  | 10 | 10 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 6 |  |  |  | 0 | 0 | ABOVE GROUND |  | LARRY K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES | NO DATA |  | CONTRACTOR DAMAGED MICHCON FACILITIES.
2025-01-31 10:21 | YES | NO | 20020104 | 2002-09-19 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 22140 W GRAND RIVER | DETROIT | WAYNE | MI | 4 8234 | 3 | NO | 350 | 2001-11-30 | 0 | 0 | 100000 | 65977.7026 | 159301.0147 | NO | 3 | 59 | 587344 | 20011130 | 2 | 2 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 |  |  |  | 0 | 1926 | UNDER GROUND OR UNDER WATER |  | LARRY CROWDER | 3135777024 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | EXCAVATION BY CITY OF DETROIT WATER DEPARTMENT.
2025-01-31 10:21 | YES | NO | 20020106 | 2002-10-01 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 3967 BELMONT | HAMTRAMCK | WAYNE | MI | 4 8212 | 3 | Null | 1355 | 2002-09-08 | 0 | 0 | 100000 | 64952.5219 | 156825.7492 | NO | 0 | 30 | 622405 | 20020909 | 0.025 | 0.025 | BY TEST | 0.025 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | NO DATA |  | OTHER | COPPER |  |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LAWRENCE K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | RELEASE OF GAS CAUSED BY LEAK IN CUSTOMERS FUEL LINE. THIS RELEASE OF GAS WAS IGNITED BY TWO SEPARATE AND UNRELATED FIRES BURNING WITHIN THE DWELLING.
2025-01-31 10:21 | YES | NO | 20020107 | 2002-10-03 | 15462 | PECO ENERGY CO | 2505 WALTON ROAD | HUNTINGDON VALLEY | MONTGOMERY | PA | 19006- | 1 | NO | 1533 | 2002-09-12 | 0 | 0 | 200000 | 129905.0438 | 313651.4983 | NO | 1 | 1 | 622773 | 20020912 | 20 | 67 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | DSR7 | ALLIED | 0 | 1971 | ABOVE GROUND |  | MARK D BERNER | 6109411751 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20020108 | 2002-10-03 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 558 BECKS RUN ROAD | PITTSBURGH | ALLEGHENY | PA | 1 5210 | 1 | NO | 248 | 2002-09-20 | 1 | 0 | 75000 | 48714.3914 | 117619.3119 | NO | 0 | 43 | 623482 | 20020920 | 6.5 | 7 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  |  |  | AL250 | AMERICAN | 0 | 1982 | ABOVE GROUND |  | U GRANT YORK | 4125727784 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SINGLE VEHICLE ACCIDENT WHERE CAR LEFT ROADWAY AND CRASHED INTO RESIDENCE. THE GAS METER SERVICING THIS CUSTOMER (558 BECKS RUN ROAD) WAS DAMAGED THAT RESULTED IN BLOWING GAS (NO IGNITION) AND DEATH OF THE DRIVER.
2025-01-31 10:21 | YES | NO | 20020109 | 2002-10-16 | 18484 | SOUTHERN CALIFORNIA GAS CO | 66329 GRANADA AVE | DESERT HOT SPRINGS |  | CA |  | 3 | NO | 200 | 2002-09-29 | 0 | 0 | 100000 | 64952.5219 | 156825.7492 | NO | 4 | 34 | 624273 | 20020929 | 35 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 |  |  |  | 0 | 0 | ABOVE GROUND |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE STRUCK ANOTHER VEHICLE INSIDE GARAGE, PUSHING VEHICLE THROUGH REAR WALL OF GARAGE AND STRIKING METER SET, WHICH IGNITED.
2025-01-31 10:21 | NO | NO | 20020110 | 2002-11-05 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 316 EAST PRINCESS STREET | YORK | YORK | PA | 1 7404 | 1 | NO | 536 | 2002-10-11 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 51 | 625696 | 20021011 | 0.5 | 1 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | OTHER | DUPLEX APARTMENT | U GRANT YORK | 4125727784 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ELECTRICAL FIRE STARTED ON THE 2ND FLOOR OF 316 EAST PRINCESS STREET. NOTE!! INCIDENT WAS NOT CAUSED BY NATURAL GAS.
2025-01-31 10:21 | YES | YES | 20020111 | 2002-10-28 | 10037 | WESTERN RESOURCES INC (AKA KPL CO. OR GAS SERVICE) | 835 FAIRDALE COMPLEX C | SALINA | SALINE | KS | 6 7401 |  | Null | 650 | 2002-10-02 | 1 | 0 | 750000 | 487143.9142 | 1176193.1188 | NO | 1 | 55 | 624663 | 20021002 | 44 | 50 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | NO DATA |  | CHUCK RAPP | 7878223502 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20020112 | 2002-11-01 | 18536 | SOUTHWEST GAS CORP | 1301 W CHERYL DR | PHOENIX | MARICOPA | AZ | 8 5022 | 3 | NO | 1455 | 2002-10-14 | 0 | 0 | 120000 | 77943.0263 | 188190.899 | NO | 0 | 10 | 626397 | 20021016 | 0.25 |  |  |  | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM |  |  | ANSI B109.1 | AMERICAN AC250 | 2002 | 2002 | ABOVE GROUND |  | BERNIE GALLENBECK | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | NO |  | NO | 0 |  | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20020113 | 2002-11-05 | 2364 | CINCINNATI GAS & ELECTRIC CO | 6955 LAKOTA RIDGE DRIVE | LIBERTY | BUTLER | OH | 4 5011 | 4 | NO | 813 | 2002-10-06 | 0 | 0 | 300000 | 194857.5657 | 470477.2475 | NO | 0 | 0 | 625073 | 20021006 | 50 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | OTHER | THE FITTING WAS INSTALLED ABOVE GROUND WHILE THE D | RANDALL L SUTTLES | 5132873921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | VARIOUS FACTORS POSSIBLY CONTRIBUTED TO THE CAUSE OF THE INCIDENT. INSPECTION, TESTING, AND REVIEW OF RECORDS AVAILABLE TO CG&E TO DATE FAIL TO IDENTIFY THE SPECIFIC CONTRIBUTING FACTORS.
2025-01-31 10:21 | NO | NO | 20020114 | 2002-11-06 | 4483 | ENSTAR NATURAL GAS CO | 51819 RUT AVE | NIKISKI |  | AK | 99635- | 2 | NO | 343 | 2002-10-29 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 0 | 47 | 627574 | 20021029 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 |  | DRISCOPIPE M 8000 HDPE | 1998 | 1998 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON TUESDAY MORNING, OCTOBER 29, 2002, AT APPROXIMATELY 3:43 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ALASKA STATE TROOPERS OF A FIRE AT 51819 RUT AVE, NIKISKI, AK 99635. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL HE FOUND A SINGLE-FAMILY HOME ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE RISER, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE LINE WAS DUG UP, PINCHED OFF AND CAPPED AT 4:30 AM AST. THE CAUSE OF THE FIRE IS UNKNOWN HOWEVER, NATURAL GAS FROM ENSTARS FACILITIES IS NOT SUSPECTED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE.
2025-01-31 10:21 | NO | NO | 20020115 | 2002-11-12 | 31097 | ISLAND ENERGY | BUILDING 597 | MARE ISLAND | SOLANO | CA | 9 4592 | 1 | YES | 800 | 2002-10-23 | 0 | 0 | 3000 | 1948.5757 | 4704.7725 | YES | 0 | 0 | 626889 |  | 27 | 30 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.25 | 0.09 | ASTM D2513 | NIPAC | 1978 | 1978 | UNDER PAVEMENT |  | WILLIAM PLUMMER | 7075625000 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | CONTRACTOR DEMOLISHING BUILDING
2025-01-31 10:21 | YES | NO | 20020116 | 2002-11-14 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 649 ALABAMA DRIVE | HERNDON |  | VA | 2 0170 | 3 | NO | 1040 | 2002-10-17 | 0 | 0 | 273103 | 177387.2859 | 428295.8257 | NO | 3 | 30 | 626493 | 20021017 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.219 | API-5L |  | 1960 | 1960 | UNDER PAVEMENT |  | NORMAN G DUREN | 8043235312 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 20020117 | 2002-11-14 | 18584 | SPRINGFIELD, CITY UTILITIES OF | 1910 E BURNTWOOD | SPRINGFIELD | GREENE | MO | 6 5801 | 3 | NO | 1530 | 2002-09-25 | 0 | 1 | 24979 | 16224.4904 | 39173.5039 | NO | 0 | 45 | 623949 | 20020925 | 56 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.095 | PE2406 | UPONOR | 1992 | 1992 | UNDER GROUND OR UNDER WATER |  | GARY GIBSON | 4178318755 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES |  | YES | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 20020118 | 2002-11-21 | 2588 | COLUMBIA GAS OF MARYLAND INC | 88 WEST MECHANICS STREET | FROSTBURG | ALLEGANY | MD | 2 1532 | 1 | NO | 316 | 2002-10-21 | 0 | 1 | 80000 | 51962.0175 | 125460.5993 | YES | 1 | 34 | 626770 | 20021021 | 0.5 | 1 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | N/A | OTHER | N/A | OTHER | N/A |  |  |  |  | 0 | 0 | OTHER | APARTMENT | U GRANT YORK | 4125727784 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CONTROL ON CUSTOMERS SPACE HEATER.
2025-01-31 10:21 | YES | YES | 20020120 | 2002-11-20 | 2288 | CHATTANOOGA GAS CO | 900 MARKET STREET | CHATTANOOGA | HAMILTON | TN | 3 7403 | 4 | NO | 1015 | 2002-10-16 | 0 | 1 | 25000 | 16238.1305 | 39206.4373 | NO | 2 | 45 | 626405 | 20021016 |  |  | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 16 | 0.625 |  |  | 0 | 1895 | UNDER PAVEMENT |  | LARRY BUIE | 4234094232 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-09-26 | YES | 3 | 2002-09-26 | YES | NO DATA |  | A 16" CAST IRON NATURAL GAS MAIN WAS RUPTURED WHILE A CONTRACTOR WAS EXCAVATING TO PLUG A SEWER LINE. THE ESCAPING GAS IGNITED INJURING THREE WORKERS AND HOSPITALIZING ONE.
2025-01-31 10:21 | NO | NO | 20020121 | 2002-12-06 | 11288 | LAWRENCEBURG GAS CO | 100 TIGER BOULEVARD | LAWRENCEBURG | DEARBORN | IN | 4 7025 | 4 | NO | 1800 | 2002-11-07 | 0 | 0 | 56598 | 36761.8283 | 88760.2375 | NO | 41 | 0 | 628453 | 20021107 | 85 |  |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | STORAGE FIELD | OTHER | STORAGE FIELD | OTHER | STORAGE FIELD |  |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | SUSAN M GILB | 5132872752 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | A GEOTHERMAL WELL DRILLING CONTRACTOR PENETRATED THE STORAGE FIELD THAT WE UTILIZE TO STORE NATURAL GAS.
2025-01-31 10:21 | YES | YES | 20020122 | 2002-12-10 | 13480 | NIAGARA MOHAWK POWER CORP | 806 ERIE BLVD | ROME | ONEIDA | NY |  | 2 | NO | 1500 | 2002-10-30 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 0 | 627757 | 20021030 | 0.25 | 0.5 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 8 |  |  |  | 0 | 1953 | WITHIN/UNDER BUILDING |  | GEORGE TAYLOR | 2187981930 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20020123 | 2002-12-10 | 15931 | PUBLIC SERVICE CO OF COLORADO | 570 CHELAN ST | GOLDEN | JEFFERSON | CO | 8 0401 | 3 | NO | 1023 | 2002-11-05 | 0 | 0 | 300000 | 194857.5657 | 470477.2475 | NO | 1 | 14 | 628250 | 20021105 | 59 | 60 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.166 |  |  | 0 | 1994 | UNDER PAVEMENT |  | ROBERT A MACIAS | 3035713922 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES | 2002-11-01 | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 20020124 | 2002-12-13 | 31348 | TXU GAS DISTRIBUTION | 1201 N DWIGHT STREET | DALLAS | DALLAS | TX | 7 5211 | 3 | NO | 1836 | 2001-05-24 | 0 | 3 | 0 | 0 | 0 | YES | 6 | 0 |  | 20010524 | 18 | 55 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 1 |  | STEEL |  | 0 | 1957 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2001-05-11 | YES | 3 | 2001-05-11 | YES | NO DATA |  | A CONTRACTOR WORKING FOR THE CITY OF DALLAS DAMAGED A SERVICE LINE. THE CONTRACTOR FAILED TO REPORT THE DAMAGE. GAS SUBSEQUENTLY ESCAPED FROM THE DAMAGED SERVICE LINE AND ENTERED A STORM SEWER. THE GAS IN THE STORM SEWER WAS IGNITED BY A CIGARETTE LIGHTER AND THREE INDIVIDUALS WERE HOSPITALIZED.
2025-01-31 10:21 | NO | NO | 20020125 | 2002-12-17 | 15462 | PECO ENERGY CO | 639 FOX FIELDS RD | BRYN MAWR | DELAWARE | PA | 1 9010 | 3 | NO | 1143 | 2002-11-20 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 53 | 629716 | 20021120 | 6 | 50 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | OTHER |  | POLYETHYLENE PLASTIC |  | 1 | 0.09 | ASTM 2513 | DUPONT | 0 | 1984 | UNDER GROUND OR UNDER WATER |  | WILLIAM J SPROSS | 6109411599 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES |  | YES | 0 |  | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20020126 | 2002-12-18 | 4150 | EASTERN SHORE GAS CO | 304 BAY STREET | SNOW HILL | WORCESTER | MD | 2 1863 | 3 | NO | 1730 | 2002-09-01 | 1 | 8 | 0 | 0 | 0 | NO | 1 | 0 | 621704 | 20020901 |  | 5 | BY CFR 192.619(A)(3) | 6 | CORROSION | CORROSION | UNSPECIFIED CORROSION | SERVICE LINE |  | BODY OF PIPE |  | NO DATA |  | 1 |  |  |  | 0 | 1950 | WITHIN/UNDER BUILDING |  | JACQUES J REMMELL | 4105247060 | NO DATA | NO DATA |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | NO | NO | 20020127 | 2002-12-30 | 18484 | SOUTHERN CALIFORNIA GAS CO | HARVESTON & RUSTIC GLEN | TEMECULA | RIVERSIDE | CA |  | 3 | NO | 1345 | 2002-12-02 | 0 | 0 | 75000 | 48714.3914 | 117619.3119 | NO | 2 | 2 | 630656 | 20021202 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 |  |  | UPONOR | 2002 | 2002 | UNDER GROUND OR UNDER WATER |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR STRUCK 2" PE GAS MAIN, WHILE TRENCHING FOR CONDUITS. ESCAPING GAS IGNITED WHILE GAS COMPANY CREW WAS ATTEMPTING REPAIRS. TWO GAS COMPANY EMPLOYEES INJURED.
2025-01-31 10:21 | NO | NO | 20020128 | 2002-12-31 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 13850 BARNESFIELD RD | HERNDON |  | VA | 2 0171 | 3 | NO | 330 | 2002-12-04 | 0 | 0 | 0 | 0 | 0 | YES | 44 | 30 |  | 20021205 | 0 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER |  | REGULATOR/METER |  | NO DATA |  |  |  |  | MOONEY | 2001 | 2001 | ABOVE GROUND |  | NORMAN DUREN | 8043235312 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | IT IS SUSPECTED THAT A COMBINATION OF LOW AMBIENT AIR TEMPERATURES, HIGH FLOW RATE (GAS VOLUMES) AND INSUFFICIENT HEAT OBTAINED FROM THE WATER BATH HEATER, ALLOWED HYDRATES TO FREEZE IN THE DISCHARGE PORT(S) OF ONE OF THE PILOT REGULATORS UPSTREAM OF THE MONITOR/CONTROL REGULATOR SETTING, THEREBY RESULTING IN THE REGULATOR SETTINGS FAILURE IN THE CLOSED POSITION AND THE SUBSEQUENT LOSS OF PRESSURE TO THE SYSTEM TO APPROXIMATELY 3,700 CUSTOMERS
2025-01-31 10:21 | NO | NO | 20020129 | 2002-12-24 | 4483 | ENSTAR NATURAL GAS CO | 2900 SUN VALLEY DR | EAGLE RIVER |  | AK | 99577- | 2 | NO | 2012 | 2002-12-12 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 1 | 1 | 631648 | 20021212 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | REGULATOR/METER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | DRISCOPIPE |  | 1992 | 1992 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THURSDAY EVENING, DECEMBER 12, 2002 AT APPROXIMATELY 10:12 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE EAGLE RIVER FIRE DEPARTMENT OF A FIRE AT 2900 SUN VALLEY RD, EAGLE RIVER, ALASKA. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A SINGLE FAMILY HOME ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER ON THE HOME CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION REPAIR CREW WAS CALLED IN TO DIG UP AND SHUT OFF THE GAS. THE SERVICEMAN PINCHED OF THE SERVICE LINE AT 11:13PM AST. THE FIRE IS BELIEVED TO HAVE STARTED IN A FISH SMOKER BEING USED IN THE GARAGE. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20020130 | 2002-12-30 | 8070 | INDIANA GAS CO INC | 1749 SALEM ST | LAFAYETTE | TIPPECANOE | IN | 4 7905 | 3 | NO | 1000 | 2002-11-27 | 0 | 0 | 350000 | 227333.8266 | 548890.1221 | NO | 3 | 10 | 630319 | 20021127 | 55 | 60 | BY TEST | 95 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.216 | PE 2406 | DUPONT | 1973 | 1973 | UNDER PAVEMENT |  | RICK L SLAGLE | 8124914611 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-11-14 | YES | 3 | 2002-11-14 | YES | NO DATA |  | THIRD PARTY CONTRACTOR CONDUCTING BORING BY HORIZONTAL DIRECTIONAL DRILLING PIERCED 4-INCH PLASTIC GAS MAIN. GAS ESCAPING FROM MAIN ENTERED NEARBY SEWER SYSTEM. FOUR RESIDENTIAL STRUCTURES INOVOLVED IN EXPLOSION(S).
2025-01-31 10:21 | YES | NO | 20020131 | 2002-12-30 | 792 | ATLANTA GAS LIGHT CO | 503 MAIN STREET | VILLA RICA | CARROLL | GA | 3 0180 | 3 | NO | 1122 | 2002-12-10 | 0 | 0 | 300000 | 194857.5657 | 470477.2475 | NO | 1 | 8 | 631333 | 20021210 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4.5 | 0.391 | ASTM-D2513 |  | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | DUDLEY W SPRUILL | 7708367520 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-12-03 | YES | 2 |  | YES | NO DATA |  | A 4" PLASTIC NATURAL GAS MAIN WAS RUPTURED WHEN A CONTRACTOR WAS MAKING A DIRECTIONAL BORE WHILE INSTALLING FIBER OPTIC CABLE. THE ESCAPING GAS MIGRATED INTO A SEWER LATERAL WHICH HAD ALSO BEEN DAMAGED BY THE CONTRACTOR. GAS ENTERED HOUSE AND WAS IGNITIED BY UNKNOWN SOURCE CAUSING FIRE AND DESTRUCTION OF HOUSE.
2025-01-31 10:21 | YES | NO | 20020132 | 2002-12-30 | 18536 | SOUTHWEST GAS CORP | 6983 W POTTER DR | GLENDALE | MARICOPA | AZ | 8 5308 | 3 | NO | 1525 | 2002-12-03 | 0 | 0 | 80000 | 51962.0175 | 125460.5993 | NO | 1 | 36 | 626397 | 20021203 | 60 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | FITTING |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | D-1248 | PHILLIPS | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | BERNIE GALLENBECK | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A LEAK RESULTED FROM AN APPARENT FAILURE AT THE PIPE TO RISER CONNECTION. IGNITION OCCURRED RESULTING IN A FIRE AND SUBSEQUENT DAMAGE TO THE THE GARAGE AT THIS ADDRESS. THE CAUSE OF THE FAILURE IS CURRENTLY UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE FILED AFTER THE RESULTS OF THE LABORATORY ANALYSIS ARE COMPLETED. THERE WERE NO INJURIES AS A RESULT OF THIS INCIDENT.
2025-01-31 10:21 | NO | NO | 20030001 | 2003-01-02 | 30750 | MIDAMERICAN ENERGY COMPANY | 4010 2ND AVE | DES MOINES | POLK | IA | 50313-3508 | 4 | NO | 2015 | 2002-11-30 | 0 | 0 | 50000 | 32476.2609 | 78412.8746 | NO | 1 | 15 | 630516 | 20021130 |  | 10 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 |  | 250 | AMERICAN | 1982 | 1994 | ABOVE GROUND |  | ED DREESMAN | 7122777750 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | DAMAGE WAS CAUSED BY A CAR THAT STRUCK A HOUSE AND ITS GAS METER. THE INCIDENT CAUSED A FIRE.
2025-01-31 10:21 | YES | YES | 20030002 | 2003-01-02 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 9335 MIDDLEBELT | ROMULUS | WAYNE | MI | 48174 | 2 | NO | 1601 | 2002-12-11 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 11 | 631509 | 20021211 | 45 | 45 | BY TEST | 45 | ACCIDENTALLY CAUSED BY OPERATOR | INCORRECT OPERATION | UNSPECIFIED INCORRECT OPERATION | SERVICE LINE |  | NO DATA |  | OTHER PLASTIC |  | 0.625 |  |  |  | 0 | 0 | ABOVE GROUND |  | LAWRENCE K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | COMPANY EMPLOYEES CHANGE GAS VALVE WITH GAS FLOWING. IGNITION OF GAS OCCURRED AND EMPLOYEES RECEIVED FLASH BURNS AND TRANSPORTED TO AREA HOSPITAL FOR TREATMENT.
2025-01-31 10:21 | YES | NO | 20030003 | 2003-01-09 | 22476 | WESTERN KENTUCKY GAS CO | 2300 BARREN RIVER ROAD | BOWLING GREEN | WARREN | KY |  | 2 | NO | 2030 | 2002-12-09 | 0 | 0 | 78000 | 50662.9671 | 122324.0844 | NO | 1 | 5 | 633736 | 20030109 | 45 |  | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | JOINT |  | STEEL |  | 4 | 0.188 | API 5L |  | 1987 | 1987 | WITHIN/UNDER BUILDING |  | DOUGLAS E STEARNS | 2706858020 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A GIRTH WELD ON A 4" STEEL LINE OPERATING AT 45 PSIG CRACKED, ALLOWING GAS TO MIGRATE UNDERGROUND TO AN ASPHALT PLANT QC LAB BUILDING (NO GAS SERVICE). GAS IGNITION IN THE BUILDING DESTROYED THE LAB & TEST EQUIPMENT. VALUE OF CONTENTS WAS REPORTED TODAY. REPORT WAS MADE TO KY PSC ON 12/10/02.
2025-01-31 10:21 | YES | YES | 20030004 | 2003-01-16 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | 111 9TH STREET | PITTSBURGH | ALLEGHANY | PA | 1 5222 | 4 | NO | 1019 | 2002-12-19 | 0 | 4 | 0 | 0 | 0 | NO | 0 | 5 | 632260 | 20021219 | 0.433 | 0.505 | BY TEST | 96 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 6 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD M NOLAN JR | 4123953226 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA |  | A 4-MAN CREW WAS ASSIGNED TO INSTALL A LARGE METER SET AT THE CAPA BUILDING AT 111 9TH STREET, PITTSBURGH, PA ON DECEMBER 19, 2002. WHEN THE CREW ARRIVED AT APPROXIMATELY 10:00 AM, THEY FAILED TO ENSURE THAT THE INLET VALVE ON THE 6-INCH STEEL SERVICE LINE WAS CLOSED. ONE OF THE CREW MEMBERS PROCEEDED TO LOOSEN THE BOLTS ON THE 6-INCH BLIND FLANGE TO THE METER SET AND LEAKING GAS CAME INTO CONTACT WITH AN IGNITION SOURCE. THE RESULT WAS A BREIF FLASH FIRE THAT BURNED ALL FOUR CREW MEMBERS.
2025-01-31 10:21 | YES | YES | 20030005 | 2003-01-16 | 20211 | ATMOS ENERGY | #10 TATE ST | GAINESVILLE | HALL | GA | 3 0501 | 3 | NO | 1236 | 2002-12-17 | 1 | 1 | 60000 | 38971.5131 | 94095.4495 | NO | 2 | 30 | 632183 | 20021217 | 35 | 35 | BY TEST | 53 | CORROSION | CORROSION | EXTERNAL | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | OTHER | SEE COMMENTS | VAN NEESE | 7705343656 | EXTERNALLY | GENERAL CORROSION |  | OTHER | UNPROTECTED PIPE | NO DATA | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20030006 | 2003-01-14 | 12878 | MOUNTAINEER GAS CO | 5025 STOFFEL DR | ELKVIEW | KANAWHA | WV | 2 5302 | 2 | NO | 1600 | 2002-12-20 | 0 | 1 | 3000 | 1948.5757 | 4704.7725 | YES | 5 | 15 |  | 20021220 | 32 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 1 |  | 40 STAND |  | 0 | 0 | ABOVE GROUND |  | ROBERT BOSTIC | 3045563864 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | CAR BACKED OVER METER SET ASSEMBLY.
2025-01-31 10:21 | YES | YES | 20030007 | 2003-01-09 | 24030 | YORK COUNTY NATURAL GAS AUTH | 489 S HERLONG AVE | ROCK HILL | YORK | SC | 2 9730 | 3 | NO | 1118 | 2002-11-26 | 0 | 3 | 120000 | 77943.0263 | 188190.899 | NO | 1 | 40 | 630217 | 20021126 | 54 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | STEEL |  | 4 | 0.237 | FIG 143 | NORDSTROM | 0 | 1980 | UNDER GROUND OR UNDER WATER |  | G STEVE CLARK | 8033295255 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 10:00 ON NOVEMBER 26, 2002, YORK COUNTY NATURAL GAS AUTHORITY WAS NOTIFIED OF A STRONG ODOR OF GAS IN THE VICINITY OF 489 S HERLONG AVENUE, HERLONG PLAZA. THE CAUSE OF THE ODOR WAS DETERMINED TO BE A 4" UNDERGROUND VALVE (FIG. 143 NORDSTROM) NEAR THE NORTH ENTRANCE TO HERLONG PLAZA. THE LEAK APPEARED TO BE ORIGINATING FROM THE BODY OF THE VALVE. THEREFORE, THE AUTHORITY DECIDED TO DIG TWO (2) BELL HOLES ON EITHER SIDE OF THE VALVE, INSTALL TWO (2) STOPPER FITTINGS, ISOLATE THE SECTION OF MAIN AND REMOVE THE VALVE FROM SERVICE. THE FIRST BELL HOLE WAS EXCAVATED APPROXIMATELY 50 FT SOUTH OF THE LEAK. A STOPPER FITTING WAS BEING WELDED ON THE 4" PIPELINE. THE FORD F-700 DUMP BED TRUCK BRINGING THE TAPPING EQUIPMENT TO THE SITE PULLED INTO THE VICINITY OF THE LEAKING VALVE. TWO EMPLOYEES WENT TO HELP THE DRIVER KEEP AWAY FROM THE LEAK. ACCORDING TO THE DRIVER THE TRUCK STALLED. THE DRIVER ATTEMPTED TO RESTART THE TRUCK. IT DID NOT START. EMPLOYEE # 1 ASKED THE DRIVER TO GET OUT OF THE TRUCK AND HE GOT INTO THE DRIVERS SEAT. EMPLOYEE #2 WAS STANDING ON THE PASSENGER SIDE RUNNING BOARD TO DIRECT THE TRUCK AWAY FROM THE LEAKING VALVE. AT APPROXIMATELY 11:18, THE NATURAL GAS IGNITED BURNING THE THREE EMPLOYEES, THE TRUCK AND THE TAPPING EQUIPMENT. EMERGENCY PERSONNEL WERE NOTIFIED AND THE AREA WAS SECURED. THE AUTHORITY BEGAN SHUTTING VARIOUS VALVES AND SQUEEZING OFF A SECTION OF 4" PLASTIC PIPE TO ISOLATE THE BURNING SECTION. THE GAS INTO THE AREA WAS SHUT OFF AT APPROXIMATELY 12:37 AND THE FIRE WAS EXTINGUISHED AT APPROXIMATELY 12:58 BY THE ROCK HILL FIRE DEPARTMENT. THE THREE EMPLOYEES WERE TRANSPORTED TO PIEDMONT MEDICAL CENTER AND LATER TRANSFERRED TO THE DOCTORS HOSPITAL IN AUGUSTA GEORGIA WHERE THEY WERE TREATED FOR 2ND DEGREE BURNS ON THEIR HANDS, ARMS AND FACE. TWO OF THE EMPLOYEES WERE RELEASED ON NOVEMBER 28 AND THE THIRD WAS RELEASED ON NOVEMBER 29TH.
2025-01-31 10:21 | YES | NO | 20030008 | 2003-01-15 | 6390 | GILMORE CITY MUNICIPAL GAS SYSTEM INC | 604 SW 3RD ST | GILMORE CITY |  | IA | 5 0541 | 1 | Null | 805 | 2002-12-27 | 0 | 0 | 130000 | 84438.2785 | 203873.4739 | NO | 8 | 0 | 632815 | 20021227 | 50 | 30 | BY TEST | 50 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | JOINT |  | POLYETHYLENE PLASTIC |  | 0.075 | 0.1 |  | PLEXCO | 1995 | 1997 | UNDER GROUND OR UNDER WATER |  | LARRY NIELSEN | 5153736326 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20030009 | 2003-01-16 | 18536 | SOUTHWEST GAS CORP | 1650 E CAMBRIDGE | PHOENIX | MARICOPA | AZ | 8 5006 | 3 | NO | 1410 | 2003-01-02 | 0 | 2 | 200000 | 127468.5382 | 307768.635 | NO | 2 | 22 | 626397 | 20030102 | 30 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | OTHER PLASTIC |  | 1.25 | 0.098 | ASTM D-2513 | SWANSON | 1979 | 1979 | UNDER PAVEMENT |  | BERNIE GALLENBECK | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20030010 | 2003-01-13 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 9530 MANOR | DETROIT | WAYNE | MI | 48204- | 3 | NO | 127 | 2003-01-08 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 0 | 0 | 633591 |  | 2 | 2 | BY CFR 192.619(A)(3) | 2 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 1 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LAWRENCE CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | METER SWIVELS HAD BEEN DELIBERATELY LOOSENED ALLOWING RELEASE OF GAS RESULTING IN AN EXPLOSIION, FIRE AND COLLAPSE.
2025-01-31 10:21 | YES | NO | 20030011 | 2003-01-23 | 13710 | NORTHERN ILLINOIS GAS CO | 803 AMBRIANCE | BURR RIDGE | COOK | IL | 60521 | 3 | NO | 1431 | 2002-11-04 | 0 | 0 | 1500000 | 974287.8283 | 2352386.2375 | YES | 4 | 4 | 634823 |  | 60 |  | BY TEST | 105 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | METER DAMAGED | NO DATA | [5 empty] | 0 | 1997 | ABOVE GROUND |  | LETICIA QUEZADA | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | FIRE AT ABOVE ADDRESS, PRELIMINARY VERBAL REPORT FROM FIRE MARSHALL INDICIATED THAT THE LEFT SIDE OF HOUSE HAD FALLEN ON METER SET AND CAUSED RELEASE OF GAS, WHICH IGNITED. THE RELEASE WAS MADE SAFE BY CUTTING AND CAPPING THE 1" PE SERVICE LINE.
2025-01-31 10:21 | NO | NO | 20030012 | 2003-01-14 | 15462 | PECO ENERGY CO | HAMILTON RD & REVERE RD | MERION STATION | MONTGOMERY | PA | 19066- |  | NO | 1718 | 2002-12-12 | 0 | 0 | 20000 | 12990.5044 | 31365.1498 | YES | 3 | 7 | 631635 | 20021212 | 0.25 | 67 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | ASTM D 2513 | PLEXCO | 1996 | 1996 | UNDER GROUND OR UNDER WATER |  | KURT GRIFFIN | 6109411599 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-12-12 | NO | 0 |  | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20030013 | 2003-01-21 | 22435 | WEST TEXAS GAS INC | TEJAS FEEDERS HWY 152-13 MILES E | PAMPA | GRAY | TX | 79066- | 3 | NO | 1145 | 2002-10-20 | 0 | 1 | 205000 | 133152.6699 | 321492.7858 | NO | 0 | 5 |  | 20021020 | 30 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER P/L | NO DATA |  | OTHER PLASTIC |  | 2 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | J CHARLES MOREHEAD | 8066746069 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EITHER TEJAS FEEDERS, EMPLOYEES OR CONTRACTOR HAD REPAIRED THEIR SERVICE LINES AT AN UNKNOWN DATE WITH UNACCEPTABLE PLASTIC (PVC) PIPE REPAIR PROCEDURES. TWO OF THESE REPAIRS WERE FOUND. ONE REPAIR WAS MADE BY GLUEING A SPLIT SECTION OF PVC PIPE TO THE DAMAGED PIPE AND USING BAND CLAMPS TO HELP SECURE THE REPAIR. ALSO AN IMPROPER TRANSITION FITTING WAS USED TO MATE THE PLASTIC PIPE TO STEEL PIPE. BOTH OF THE REPAIRS WERE FOUND LEAKING UNDER AN AREA THAT WAS COVERED WITH CONCRETE ALLOWING THE LEAKING GAS TO MIGRATE UNDER THE BUILDING CAUSING THE EXPLOSION. ONE OF THE EMPLOYEES THAT LEFT THE BUILDING BEFORE THE EXPLOSION HAD RECOGNIZED THE PRESENCE OF A FOUL ODOR, BUT DID NOT REPORT IT TO THE FEED YARD MANAGEMENT OR WTG GAS.
2025-01-31 10:21 | YES | YES | 20030014 | 2003-02-04 | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 9127 WAYMOND AVENUE | HIGHLAND | LAKE | IN | 4 6322 | 3 | NO | 200 | 2003-01-19 | 1 | 0 | 70000 | 44613.9884 | 107719.0223 | NO | 3 | 0 | 634472 | 20030119 | 24 | 30 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | ASTM A53 | UKNOWN | 1964 | 1964 | ABOVE GROUND |  | SHAWN L PATTERSON | 2196475007 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AUTOMOBILE VEERED OFF ROAD AND STRUCK SERVICE LINE AND METER CAUSING GAS TO LEAK. GAS IGNITED AND BURNED HOUSE AND AUTOMOBILE. AUTOMOBILE DRIVER KILLED. THE HOUSE WAS NOT OCCUPIED AT THE TIME OF THE INCIDENT.
2025-01-31 10:21 | YES | YES | 20030015 | 2003-01-27 | 31159 | KANSAS GAS SERVICE | 400 SW FRANK PHILLIPS BOULEVARD | BARTLESVILLE | WASHINGTON | OK | 7 4003 | 3 | NO | 1002 | 2002-12-31 | 0 | 1 | 0 | 0 | 0 | NO | 8 | 58 |  | 20021231 | 49 | 49 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | METER BOX | FITTING |  | POLYETHYLENE PLASTIC |  | 3 | 0.318 | SDR 11 | PHILLIPS | 0 | 1984 | OTHER | WATER BOX | DAVID P SPEARS | 7852713924 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D - OTHER
2025-01-31 10:21 | NO | NO | 20030016 | 2003-01-28 | 18536 | SOUTHWEST GAS CORP | DALLAS & SACRAMENTO | BISBEE | COCHISE | AZ | 85603- | 3 | NO | 953 | 2002-12-31 | 0 | 0 | 70000 | 45466.7653 | 109778.0244 | NO | 0 | 3 | 634348 | 20021231 | 175 | 175 | BY TEST | 400 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | OTHER | CURB VALVE TEE | FITTING |  | STEEL |  | 2 |  | ANSI C1029 | MUELLER | 1999 | 1999 | ABOVE GROUND |  | RANDY SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20030017 | 2003-01-22 | 603 | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOUR | 510 RIDGEWAY BLVD | HOT SPRINGS | GARLAND | AR | 71901- | 3 | NO | 1455 | 2003-01-02 | 0 | 1 | 0 | 0 | 0 | NO | 6 | 20 | 633204 | 20030102 | 28 | 60 | BY TEST | 90 | ACCIDENTALLY CAUSED BY OPERATOR | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.25 | UNKNOWN | UNKNOWN | 0 | 1951 | UNDER GROUND OR UNDER WATER |  | KEITH KITTINGER | 5013774669 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | GAS IGNITION CAUSED BY CIGARETTE LIGHTER USE DURING A MAIN LEAK REPAIR.
2025-01-31 10:21 | YES | NO | 20030018 | 2003-02-13 | 10030 | K N ENERGY INC(KANSAS NEBRASKA GAS CO) (KMI) | 102 TRISTANT DRIVE | MOUNTAIN VILLAGE | SAN MIGUEL | CO | 8 1435 | 2 | NO | 1303 | 2002-09-20 | 0 | 0 | 3500000 | 2273338.2661 | 5488901.2209 | NO | 1 | 39 | 623558 | 20020920 | 36 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | NO DATA |  | NO DATA |  | NO DATA |  | 1 |  | PE 2406 |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | REBECCA VOSS FIELDS | 7133699418 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2002-09-19 | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20030019 | 2003-02-14 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | 2146 RHINE STREET | PITTSBURGH | ALLEGHENY | PA | 15212- | 3 | NO | 2227 | 2003-01-17 | 0 | 1 | 500000 | 318671.3456 | 769421.5876 | NO | 2 | 38 |  | 20030117 | 19 | 25 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | VALVE |  | OTHER | TBD BY METALLURGICAL ANALYSIS | 12 |  | UNKNOWN | CRANE | 0 | 1958 | WITHIN/UNDER BUILDING |  | EDWARD M NOLAN JR | 4123953226 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | EQUITABLE GAS HAS DETERMINED A CONTRIBUTING FACTOR TO BE LEAKAGE FROM A CRACK ON A 12" MAIN LINE VALVE LOCATED APPROXIMATELY 100 FEET FROM THE CORNER OF THE BUILDING AT 2146 RHINE STREET.
2025-01-31 10:21 | YES | NO | 20030020 | 2003-02-25 | 4483 | ENSTAR NATURAL GAS CO | 1676 BODENBURG LOOP | PALMER |  | AK | 9 9654 | 2 | NO | 2250 | 2003-02-05 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 20 | 10 | 635986 | 20030205 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | DRISCOPIPE |  | 1998 | 1988 | UNDER GROUND OR UNDER WATER |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON TUESDAY EVENING, FEBRUARY 4, 2003 AT APPROXIMATELY 10:50 PM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE BUTTE FIRE DEPARTMENT OF A FIRE AT 1676 BODENBURG LOOP, EAST OF PALMER ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL LOG HOME ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER TO BUILDING. A DISTRIBUTION REPAIR CREW WAS CALLED IN TO DIG UP AND SHUT OFF THE GAS. THE LINE WAS PINCHED OFF AT 1:00 AM, FEBRUARY 5, 2003. UPON INVESTIGATION, ENSTAR FOUND UNDERGROUND GAS CONCENTRATIONS NEAR THE FOUNDATION. THE SERVICE LINE WAS PRESSURE TESTED AND IT FAILED TO HOLD PRESSURE. THE LINE WAS DUG UP AND EXPOSED. AN UNAUTHORIZED REPAIR CONSISTING OF A PIECE OF RADIATOR HOSE AND TWO BAND CLAMPS WAS FOUND LEAKING ON ENSTARS SERVICE LINE. THE UNAUTHORIZED REPAIR WAS IN THE SAME TRENCH AS A RECENTLY INSTALLED WATER LINE. ENSTAR BELIEVES THE GAS LINE WAS DAMAGED DURING THE INSTALLATION OF THE WATER LINE AND THE UNAUTHORIZED REPAIRS WERE MADE AT THAT TIME. ENSTAR IS WORKING WITH THE HOMEOWNERS INSURANCE COMPANY TO DETERMINE WHO MADE THE UNAUTHORIZED REPAIRS TO THE GAS LINE.
2025-01-31 10:21 | YES | NO | 20030021 | 2003-02-24 | 6690 | GREAT PLAINS NATURAL GAS CO | 719 ANDREW STREET | BRECKENRIDGE | WILKIN | MN | 5 6520 | 3 | NO | 2345 | 2003-01-23 | 0 | 0 | 500000 | 318671.3456 | 769421.5876 | NO | 1 | 0 | 634903 | 20030124 | 15 |  | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | VALVE |  | STEEL |  |  |  | ASTM D2513-87 | CONTINENTAL IND | 2002 | 2002 | UNDER GROUND OR UNDER WATER |  | DOUGLAS M LEE | 7012227994 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE APPARENT CAUSE OF THIS INCIDENT WAS FAILURE OF A ROCKWELL 143 VALVE BODY POSSIBLY DUE TO STRESSES CAUSED FROM SETTLEMENT/FROST OR OTHER PIPE MOVEMENT IN CONJUNCTION WITH SUB-ZERO TEMPERATURES. THE VALVE WAS CAST IRON AND HOUSED IN A VALVE BOX IN AN ALLEY. GAS MIGRATED TO A HOME, ACCUMULATED IN THE BASEMENT, EXPLODED AND IGNITED AN ADJACENT GARAGE CONTAINING 2 VECHICLES AND AN ADJACENT HOME.
2025-01-31 10:21 | NO | NO | 20030022 | 2003-02-21 | 1560 | BLUEFIELD GAS CO | RTE 2 BOX 217, BLUE PRINCE RD | BLUEFIELD | MERCER | WV | 2 4701 | 3 | NO | 645 | 2003-01-27 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 45 | 635192 | 20030127 | 180 | 200 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | WELD |  | STEEL |  | 10 | 0.188 | API 5L GR B | UNKNOWN | 1968 | 1968 | UNDER GROUND OR UNDER WATER |  | ROBERT E PAINTER | 5407773801 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | BLUEFIELD GAS COMPANY IS SERVED BY 2 HIGH-PRESSURE GAS MAINS FROM ITS PRICENTON, WV GATE STATION WITH COLUMBIA GAS. THE TWO LINES COME TOGETHER AND GAS IS CARRIED BY A ONE 10-INCH GAS MAIN APPROXIMATELY 1 1/2 MILES LONG. FURTHER DOWNSTREAM THIS 10-INCH MAIN SPLITS AND FEEDS TWO SMALLER LINES. APPROXIMATELY 6:45 AM JANUARY TECHNICIANS NOTED A SIGNIFICANT INCREASE IN FLOW RATE TO THIS LINE FROM THE PRINCETON GATE STATION AS WELL SIGNIFICANT LOSS OF PRESSURE AT ALL TELEMETRY STATIONS DOWNSTREAMS IN BLUEFIELD. A LINE BREAK ON THE SECTION OF 10-INCH WAS THE MOST LIKELY AREA THAT WOULD HAVE THIS SUDDEN IMPACT TO THE ENTIRE SYSTEM. FIELD PERSONNEL LOCATED THE LINE BREAK AND VALVED OFF THE 10-INCH MAIN TO STOP THE FLOW OF GAS TO MAKE THE AREA SAFE AND SO THAT REPAIRS COULD BE MADE. THE AREA OF LEAKAGE WAS EXCAVATED AND A BROKEN WELD WAS DISCOVERED. THE AIR TEMPERATURE AT 7:00 A.M. ON JANUARY 27 WAS 1 DEGREE F. A FROST LAYER WAS NOTED DOWN NEAR THE TOP OF THE MAIN. AS A RESULT GAS SERVICE TO 4,300 CUSTOMERS DOWNSTREAM OF THE BREAK WAS INTERRUPTED.
2025-01-31 10:21 | YES | NO | 20030023 | 2003-02-07 | 21190 | VERMONT GAS SYSTEMS INC | 7681 WILLISTON ROAD | WILLISTON | CHITTENDEN | VT | 05495 | 3 | NO | 1632 | 2003-02-02 | 0 | 0 | 175000 | 111534.971 | 269297.5557 | NO | 0 | 58 | 635753 | 20030202 | 70 | 100 | BY TEST | 160 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | METER SET ASSEMBLY |  | JOINT |  | NO DATA |  | 0.75 | 0.133 | ASTM A53/733 | US MANUFACTURER | 1990 | 1990 | ABOVE GROUND |  | DAVID ATTIG | 8028634511 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | A LARGE SEGMENT OF ICE/SNOW SLID OFF THE ROOF OF A TWO STORY BUILDING. IT STRUCK A SING METER SET AND SHEARED A THREADED PIPE NIPPLE ON THE RISER BETWEEN THE SHUT-OFF VALVE AND REGULATOR. THE ESCAPING GAS IGNITED FROM AN UNKNOWN IGNITION SOURCE AND THE SUBSEQUENT FIRE DAMAGED A STRUCTURE.
2025-01-31 10:21 | NO | NO | 20030024 | 2003-02-05 | 15350 | DOMINION PEOPLES | XS-320 ON CARNEGIE DRIVE | LOWER BURRELL | WESTMORELAND | PA | 1 5068 | 3 | NO | 745 | 2003-01-16 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 25 | 635468 | 20030130 | 270 | 400 | BY TEST | 630 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | REGULATOR STATION | OTHER | NO COMPONENT FAILURE | STEEL |  | 4 |  | API 5L GR B | MAVERICK | 2000 | 2001 | UNDER GROUND OR UNDER WATER |  | JOYCE C DAILEY | 4124975668 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE INLET LINE TO REGULATOR STATION (XS-320) BECAME FROZEN AND BLOCKED OFF, THIS RESULTED IN A SERVICE OUTAGE TO 3,217 CUSTOMERS.
2025-01-31 10:21 | YES | NO | 20030025 | 2003-02-10 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 4832 SILVERDENE DRIVE | RALEIGH | WAKE | NC | 27616- | 2 | NO | 2045 | 2003-01-26 | 0 | 0 | 175000 | 111534.971 | 269297.5557 | NO | 2 | 37 | 635136 |  | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 |  |  |  | 0 | 2001 | ABOVE GROUND |  | JIMMY K JONES | 9198362419 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | DRIVER LOST CONTROL OF VEHICLE, RAN OFF STREET, AND CRASHED INTO SIDE OF SINGLE FAMILY DWELLING DAMAGING DOMESTIC METER SET AND CAUSING FIRE.
2025-01-31 10:21 | NO | NO | 20030026 | 2003-02-12 | 15359 | PEOPLES NATURAL GAS | 3005 ROSE DR SE | ROCHESTER | OLMSTED | MN | 55902- | 3 | NO | 330 | 2003-01-18 | 0 | 0 | 30000 | 19120.2807 | 46165.2953 | NO | 0 | 15 | 634451 | 20030118 | 20 | 20 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | GRADE B | N/A | 0 | 1981 | UNDER PAVEMENT |  | JIM ERICKSON | 5075295107 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2002-04-03 | YES | 0 |  | YES | NO DATA |  | 2 INCH STEEL MAIN HAD BEEN HIT, GOUGED, AND BURIED DURING SUMMER SEWER AND WATER CONSTRUCTION CAUSING A STRESS AREA ON THE PIPE. WINTER FROST CONDITIONS CAUSED THE PIPE TO CRACK IN THE GOUGE AND SEPARATE CAUSING A NATURAL GAS LEAK.
2025-01-31 10:21 | YES | YES | 20030027 | 2003-02-27 | 2596 | COLUMBIA GAS OF OHIO INC | 3335 1/2 MORSE RD | COLUMBUS | FRANKLIN | OH | 4 3231 | 3 | NO | 1815 | 2003-01-28 | 0 | 1 | 55000 | 35053.848 | 84636.3746 | NO | 0 | 35 | 635322 | 20030128 | 45 | 55 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 |  | UNKNOWN | OIL CREEK | 2002 | 2003 | OTHER | UNDERGROUND EXPOSED | RICK WILBERT | 4408912454 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2003-01-28 | YES | NO DATA |  | AMERICAN ELECTRIC POWER (AEP) WAS INSTALLING A SHRINK WRAP WHILE REPAIRING AN ELECTRIC LINE WHEN THEY BURNED THROUGH THE CUSTOMERS GAS SERVICE LINE WITH A PROPANE TORCH, CAUSING AN IGNITION AND FIRE. THE ELECTRIC LINE REQUIRED REPAIR BECAUSE A COLUMBIA GAS OF OHIO (COH) CREW INSTALLING A NEW TAP AND SERVICE LINE AT 3335 1/2 MORSE ROAD ON 1/28/03 AT APPROX 1400 HR DUG INTO AN UNMARKED AEP ELECTRIC LINE (PROPER ONE CALL NOTIFICATION WAS GIVEN BY COH). AT APPROX 1500 HR - AEP SHOWED UP ON SITE TO MAKE REPAIRS. THE NEWLY INSTALLED GAS SERVICE LINE WAS LEFT EXPOSED AND VISIBLE FOR AEP.
2025-01-31 10:21 | YES | NO | 20030028 | 2003-02-24 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 5510 SLVERPARK | HOUSTON | HARRIS | TX | 77041- | 3 | NO | 1030 | 2003-02-04 | 0 | 0 | 107810 | 68711.9155 | 165902.6827 | NO | 1 | 29 | 635928 | 20030204 | 49 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | NO DATA |  | 0.5 | 0.09 | D-2513 | UPONOR | 2002 | 2002 | UNDER GROUND OR UNDER WATER |  | TAL R CENTERS JR | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | THIRD PARTY DAMAGED .5 INCH I.P. POLY SERVICE LINE WITH A TRENCHER. ESCAPING GAS WAS IGNITED, DAMAGING TRENCHER AND A NEW HOUSE.
2025-01-31 10:21 | YES | YES | 20030029 | 2003-02-26 | 13660 | NORTH SHORE GAS CO | 1417 14TH STREET | NORTH CHICAGO | LAKE | IL | 6 0064 | 3 | NO | 1105 | 2003-01-30 | 0 | 1 | 100000 | 63734.2691 | 153884.3175 | NO | 1 | 28 | 635500 | 20030130 | 38 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 |  | UNKNOWN | UNKNOWN | 0 | 1968 | UNDER GROUND OR UNDER WATER |  | JOHN KLECZYNSKI | 8472634660 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-01-27 | YES | 0 |  | YES | NO DATA |  | WATER SERVICE CONTRACTOR HIT PROPERLY MARKED AND EXPOSED GAS SERVICE SEPARATING IT FROM THREADED RISER FITTING.
2025-01-31 10:21 | YES | NO | 20030030 | 2003-02-27 | 792 | ATLANTA GAS LIGHT CO | CUMMING HWY (HWY 9) | ALPHARETTA | FULTON | GA | 3 0004 | 3 | NO | 1503 | 2003-02-05 | 0 | 0 | 99158 | 63197.6266 | 152588.6116 | NO | 24 | 22 | 636061 | 20030205 | 230 | 300 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12.75 | 0.25 | X-42 | UNKNOWN | 0 | 1966 | UNDER GROUND OR UNDER WATER |  | JAMES BRAY | 7702053602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-01-29 | YES | 2 |  | YES | NO DATA |  | AN EXCAVATOR RUPTURED A 12" HP STEEL NATURAL GAS MAIN WHILE BORING A 24" CASING UNDERNEATH HWY 9 FOR A FUTURE WATER LINE. LOCATE MARKINGS WERE PRESENT AND WITHIN THE LOCATE TOLERANCE ZONE (24"). THE GAS MAIN WAS NOT SPOTTED BY THE EXCAVATOR AND THERE WAS NOT A RECEIVER HOLE PRESENT. THE ESCAPING GAS DID NOT IGNITE.
2025-01-31 10:21 | YES | NO | 20030031 | 2003-02-09 | 15469 | PHILADELPHIA GAS WORKS | 1200 LONGSHORE AVENUE | PHILADELPHIA |  | PA | 1 9122 | 4 | NO | 1617 | 2003-02-04 | 0 | 0 | 200000 | 127468.5382 | 307768.635 | NO | 0 | 43 | 635962 | 20030204 | 18 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 12 | 0.5 |  |  | 0 | 1944 | UNDER PAVEMENT |  | STEVEN A GROEBER | 2156846987 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON FEBRUARY 4, 2003 AT 1617HR A NATURAL GAS EXPLOSION OCCURRED AT THE RESIDENTIAL HOME OF 1200 LONGSHORE AVENUE, PHILADELPHIA, PA. PHILADELPHIA FIRE DEPARTMENT (PFD), IN RESPONSE TO AN ODOR COMPLAINT, ARRIVED ON SCENE SHORTLY BEFORE PGW EMPLOYEES AND EVACUATED ONE (1) ELDERLY PERSON FROM THE ADDRESS MINUTES BEFORE IGNITION. NO INJURIES OCCURRED. AFTER IGNITION, A GAS FIRE IN THE FOOTWAY DEVELOPED. AT 1833 HR, PRESSURE IN THE LINE WAS REDUCED TO 6.0 W.C. AND REPAIRS WERE MADE. AT 2000 HR A 12" CAST IRON MAIN WAS UNCOVERED REVEALING A CIRCUMFERENTIAL BROKEN MAIN. THE MAIN HAD A LARGE TREE ROOT DIRECTLY UNDERNEATH. THERE WAS ALSO FROST CONDITIONS AT THE TIME.
2025-01-31 10:21 | YES | NO | 20030032 | 2003-02-28 | 12390 | METROPOLITAN UTILITIES DISTRICT | 3709 S 14TH | OMAHA | DOUGLAS | NE | 6 8102 |  | NO | 1936 | 2003-02-20 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 2 | 30 | 637395 | 20030220 |  |  |  |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | NO DATA |  | NO DATA |  | 4 | 0.5 |  |  | 0 | 1911 | UNDER PAVEMENT |  | MICHAEL PALMESANO | 4024498210 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA |  | NONE
2025-01-31 10:21 | YES | YES | 20030033 | 2003-03-14 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 6 CIRCLE DRIVE | JACOBUS | YORK | PA | 1 7407 | 3 | NO | 1645 | 2003-02-12 | 0 | 3 | 250000 | 159335.6728 | 384710.7938 | NO | 0 | 40 | 636671 | 20030212 | 45 | 57 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | PIPE | STEEL |  | 2 | 0.188 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RAY M. GEESEY | 7177670250 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | YES | NO DATA |  | THIS INCIDENT RESULTED IN THE INJURY TO THREE PEOPLE, TWO ADULTS AND ONE CHILD, WHO RECEIVED FIRST AND SECOND DEGREE BURNS TO THE HANDS, ARMS, AND CHEST ON THE AFOREMENTIONED DATE. THEY WERE TAKEN TO JOHN HOPKINS BAYVIEW MEDICAL BURN UNIT FOR TREATMENT. NONE OF THE FAMILY MEMBERS WERE CONSIDERED CRITICAL AT ANYTIME ACCORDING TO THE ON-DUTY NURSE SUPERVISOR, CAROL HAYES. ONE OF THE TWO ADULT VICTIMS, CHRISTOPHER KRICHTEN, WAS RELEASED FROM BAYVIEW ON FEBRUARY 19, 2003 AND THE OTHER ADULT, AMY KRICHTEN, WAS RELEASED ON FEBRUARY 21, 2003. THE HOSPITAL RECORDS INDICATED THAT THE CHILD, MEGAN DID NOT SPEND THE NIGHT AT BAYVIEW. REFERENCE PART 3 OF RSPA 7100.1. THE OWNER REPORTED AN ODOR OF NATURAL GAS AT 16:19 TO COLUMBIA GAS. PRIOR TO THE COLUMBIA GAS SERVICE TECHNICIANS ARRIVAL AT 16:45, THE HOUSE WAS ON FIRE WITH A REPORT OF AN EXPLOSION. THE FIRE ALSO CONSUMED TWO VEHICLES THAT WERE PARKED IN THE LOWER LEVEL GARAGE AREA OF THE STRUCTURE. REFERENCE PART B/D OF RSPA 7100.1. UPON FURTHER INVESTIGATION, A DAMAGED STEEL PIPE LINE WAS FOUND TO BE CRACKED IN FRONT OF THE 6 CIRCLE DRIVE PROPERTY. THE ENTIRE EXCAVATION PROCESS TO SEEK AND FIND THE LEAK WAS OVERSEEN BY PETE STANLEY, GAS SAFETY INSPECTOR FOR THE PA PUBLIC UTILITY COMMISSION. UPON DISCOVERY OF THE LEAK, THERE WAS EVIDENCE OF PRIOR DAMAGE TO THE 2-INCH GAS MAIN. THE SECTION OF FAILED PIPE HAS WHAT APPEARS TO BE A TOOTH MARK FROM A BACKHOE BUCKET. AFTER FURTHER INVESTIGATION, NEARBY PROPERTY OWNERS INDICATED THAT A CONTRACTOR HAD INSTALLED A SEWER LINE IN THIS NEIGHBORHOOD IN 1998. THERE WAS ALSO EVIDENCE THAT THE AREA SURROUNDING THE PIPE HAD BEEN PREVIOUSLY DISTURBED BY THE PRESENCE OF CRUSHER RUN BACKFILL MATERIAL.
2025-01-31 10:21 | YES | NO | 20030034 | 2003-03-07 | 31770 | NEW ENGLAND GAS COMPANY | 14 STELLA STREET | PROVIDENCE |  | RI | 02909- | 3 | NO | 802 | 2003-02-09 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 2 | 43 | 636352 | 20030209 | 0.36 | 0.43 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.45 |  |  | 1924 | 1924 | UNDER PAVEMENT |  | CHARLES K MEUNIER | 4012725040 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: SUBSIDENCE |  | Null |  | Null | 0 |  | Null | NO DATA |  | A MAIN FAILURE OCCURRED FROM POSSIBLE SOIL SUBSIDENCE RESULTING IN GAS MIGRATION INTO A BUILDING, PROBABLY THROUGH A FRENCH DRAIN, WITH GAS IGNITION FROM AN UNKNOWN SOURCE.
2025-01-31 10:21 | YES | YES | 20030035 | 2003-03-07 | 31242 | AVISTA UTILITIES | INTERSECTION OF CATHERINE ST AND NEBO ST | ROSEBURG | DOUGLAS | OR | 9 7470 | 3 | NO | 1500 | 2003-01-21 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 5 | 634797 | 20030122 | 55 | 60 | BY TEST | 90 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | OTHER | OPERATOR ERROR | STEEL |  | 2 | 0.154 | API52 | UNKNOWN | 0 | 1977 | UNDER PAVEMENT |  | PAT AIKINS | 5094954413 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | AN AVISTA CREW WAS REPAIRING A LEAKING 3/4" SERVICE TEE ON A 2" STEEL MAIN. WHEN IT WAS DETERMINED THAT THE TAPPER IN THE TEE WAS NOT FUNCTIONAL AND AFTER ATTEMPTING UNSUCCESSFULLY TO CONTROL THE LEAKS BY ARC WELDING THE TEE, THE CREW DECIDED TO REDIRECT THE FLOW OF GAS TO THE SIDE OF THE TEE AWAY FROM THE WORK AREA. THE LEAK WAS INTENTIONALLY IGNITED TO ELIMINATE NATURAL GAS ACCUMULATION IN THE BELLHOLE. THE CREW THEN PROCEEDED TO WELD ON A STOPPLE FITTING TO ISOLATE THE LEAKING TEE. AS THIS WAS A SINGLE FEED LINE WITH ONLY 3 CUSTOMERS PAST THE LEAK SITE, A DECISION WAS MADE TO USE A SINGLE STOPPLE FITTING AND RELIGHT THE CUSTOMERS. AFTER THE FITTING WAS WELDED, IT WAS TESTED AND TAPPED. PRIOR TO TAPPING IT WAS NOTICED THAT A BY-PASS, OR BLEEDER VALVE, WAS NOT IN PLACE ON THE TAPPING MACHINE. A VALVE WAS REMOVED FROM A SWEEP MACHINE AND PLACED ON THE TAPPING MACHINE. THE TAP WAS MADE, THE TAPPING MACHINE REMOVED, AND THE SWEEP MACHINE WAS INSTALLED TO REMOVE ANY STEEL SHAVINGS PRIOR TO INSTALLING THE STOPPER. AT THIS POINT, THE CREW FAILED TO REPLACE THE BLEEDER VALVE THAT HAD BEEN REMOVED FROM THE SWEEP MACHINE. AS AN AVISTA EMPLOYEE OPENED THE SANDWICH VALVE TO INSERT THE SWEEP TOOL, A RELEASE OF GAS AT APPROXIMATELY 55 PSIG OCCURRED THROUGH A 1/4" HOLE WHERE THE BLEEDER VALVE SHOULD HAVE BEEN. THE GAS WAS IGNITED FROM THE STANDING FLAME ON THE LEAKING SERVICE TEE AND ROLLED THROUGH THE DITCH. THE AVISTA EMPLOYEE WAS ABLE TO REACT AND TURN AWAY FROM THE FLAME, BUT HIS ARM WAS BURNED FROM ABOVE HIS GLOVE AT THE RIGHT WRIST TO ABOVE HIS RIGHT ELBOW. THE EMPLOYEE WAS PULLED FROM THE DITCH, THE FIRE EXTINGUISHED AND THE SANDWICH VALVE WAS CLOSED TO PREVENT ANY FURTHER RELEASE OF GAS. THE EMPLOYEE WAS HOSPITALIZED FOR 3 DAYS AT THE EMANUEL BURN CENTER IN PORTLAND, OREGON. HE IS EXPECTED TO MAKE A FULL RECOVERY AND DID RETURN TO WORK A COUPLE OF WEEKS FOLLOWING THE INCIDENT. MEETINGS WERE HELD WITH FIELD PERSONNEL AND OTHER APPROPRIATE STAFF AFTER THIS INCIDENT TO DISCUSS AND REVIEW THE EVENT. AFTER A STEP BY STEP REVIEW OF THE INCIDENT, DISCUSSION WERE HELD AROUND WHAT WENT WRONG AND HOW TO PREVENT THIS IN THE FUTURE. TRAINING AND RECERTIFICATION WILL BE CONDUCTED FOR THE EMPLOYEES INVOLVED IN THE INCIDENT AS REQUIRED BY CFR 192.605. ALL REVIEWS REQUIRED BY CFR 192.805 FOR COVERED TASKS WERE CONDUCTED AND CONCLUSIONS WERE MADE THAT CHANGES WERE NOT NEEDED TO THE OPERATOR QUALIFICATION PROGRAM FOR THIS TASK. DAMAGE ESTIMATES FOR THIS INCIDENT WERE UNDER $50,000. DOT NOTIFICATION FORMS HAVE BEEN COMPLETED AND MAILED TO THE PROPER AUTHORITY. A COPY IS FORWARDED TO YOU WITH THIS REPORT FOR YOUR RECORDS.
2025-01-31 10:21 | NO | NO | 20030036 | 2003-02-28 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 8914 SAN LORENZO | HOUSTON | HARRIS | TX | 77017- | 3 | NO | 1449 | 2003-02-01 | 0 | 0 | 45000 | 28680.4211 | 69247.9429 | NO | 1 | 20 |  | 20030201 | 40 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | D-2513 | UPONOR | 2001 | 2001 | UNDER GROUND OR UNDER WATER |  | TAL R. CENTERS | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | THIRD PARTY DAMAGED 2" I.P. POLY MAIN WITH A TRENCHING MACHINE AND ESCAPING GAS WAS IGNITED. DAMAGING NEW HOUSE AND TRENCHER.
2025-01-31 10:21 | YES | NO | 20030037 | 2003-03-20 | 1088 | BALTIMORE GAS & ELECTRIC CO | 2739 EAST CHASE STREET | BALTIMORE |  | MD | 21213- | 3 | NO | 2332 | 2003-02-22 | 0 | 0 | 150000 | 95601.4037 | 230826.4763 | NO | 13 | 3 |  | 20030223 | 8 | 10 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  |  |  | 0 | 1929 | UNDER GROUND OR UNDER WATER |  | JOHN A. GARRISON | 4102915130 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | BALTIMORE CITY FIRE DEPARTMENT REPORTED EXPLOSION AT 2739 EAST CHASE STREET AT 23:32. METERS WERE OFF BY THE TIME THE OPERATORS FIRST RESPONDERS ARRIVED ON-SCENE (15 MINUTES LATER). SERVICE TO 2739 COMES FROM 6" LOW PRESSURE GAS MAIN LOCATED APPROXIMATELY 10 FEET IN FRONT OF THE ROW HOUSE BUILDINGS. SERVICE ENTERS 2739 AS BRANCH FROM 2737. SERVICE WAS LEAK TESTED AT 10" WC FOR 20 MINUTES-NO LEAKAGE DETECTED. GAS CONTINUED TO BE DETECTED AT FRONT WALL OF BUILDINGS AFTER SERVICE WAS CAPPED. USING SUBSURFACE SURVEY, OPERATOR LOCATE A BREAK IN THE GAS MAIN DIRECTLY IN FRONT OF 2739. WHEN EXCAVATING TO REPAIR MAIN BREAK, THE AMOUNT QUALITY OF THE WATER THAT CONTINUALLY FILLS THE EXCAVATION LEADS THE OPERATOR TO SUSPECT A WATER SYSTEM LEAK NEARBY. AFTER LOCATING AND TURNING OFF THE WATER SERVICE TO 2739 (WHICH RUNS ADJACENT TO THE LOCATION OF THE MAIN BREAK), THE FLOW OF WATER STOPPED. IT IS BELIEVED THAT THE LEAK IN THE WATER SERVICE UNDERMINED THE SUPPORT FOR THE MAIN AND CAUSED THE BREAK. THE CAUSE OF THE EXPLOSION AND THE IGNITION SOURCE ARE STILL NOT DEFINITIVELY KNOWN.
2025-01-31 10:21 | YES | NO | 20030038 | 2003-03-19 | 1344 | BERKSHIRE GAS CO | 24 INDUSTRIAL BLVD | TURNERS FALLS |  | MA | 1376 | 3 | NO | 150 | 2003-02-13 | 0 | 0 | 450000 | 286804.211 | 692479.4288 | NO | 2 | 40 | 636739 | 20030213 | 40 | 40 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | DRIP/RISER |  | STEEL |  | 1.25 |  | NA | PERFECTION | 0 | 2000 | UNDER GROUND OR UNDER WATER |  | RICHARD E. NASMAN | 4134450303 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THURSDAY, FEBRUARY 13TH AT APPROXIMATELY 1:50 A.M., BERKSHIRE GAS DISPATCH CENTER RECEIVED A CALL FROM THE TURNERS FALLS POLICE DEPARTMENT REPORTING A FIRE AND EXPLOSION AT THE ABOVE REFERENCED LOCATION. BERKSHIRE IMMEDIATELY DISPATCHED "ON-CALL" PERSONNEL TO THE SCENE AND WHO ARRIVED AT APPROXIMATELY 2:15 A.M.. UPON BERKSHIRES ARRIVAL, THE FIRE DEPARTMENT HAD EXTINGUISHED THE FIRE IN THE AREA OF MECHANICAL ROOM AND SHUT-OFF THE PROPANE TANKS. THE LOCATION IS SERVED BY BERSKHIRE PROPANE, A BERKSHIRE GAS AFFILIATE. THERE CONTINUED TO BE A "LAZY" FLAME (APPROXIMATELY 3 IN DIAMETER) EMANATING FROM THE GROUND IN THE AREA OF THE SERVICE RISER. UPON REVIEW OF THE AREA, BERKSHIRES RESPONDER NOTICED ANOTHER RISER IN THE AREA OF THE SERVICE RISER INDICATING THAT A NATURAL GAS SERVICE MAY BE PRESENT. AT APPROXIMATELY 2:30 A.M. A DISTRIBUTION EMPLOYEE WAS CALLED IN FOR ASSISTANCE. THE DISTRIBUTION EMPLOYEE ARRIVED ON-SITE AT APPROXIMATELY 2:45 A.M. SERVICE CARD INFORMATION WAS NOT AVAILABLE ON THE DISTRIBUTION EMPLOYEES LAPTOP COMPUTER RECORD SYSTEM. THEREFORE TIES TO THE CURB STOP VALVE WAS NOT AVAILABLE. ADDITIONAL CREWS AND EQUIPMENT WAS DISPATCHED IN ORDER TO SQUEEZE-OFF THE SERVICE. SNOW BANKS WERE REMOVED SO AS TO ACCESS THE SERVICE NEAR THE MAIN TEE. UPON EXCAVATION OF THE SERVICE, A "SQUEEZE-OFF" TOOL WAS UTILIZED TO SHUT OFF SERVICE AT APPROXIMATELY 4:30 A.M. THE SERVICE LINE IS A 1 1/4 "POLYETHYLENE SERVICE OPERATING AT 40 PSIG. UPON COMPLETING THE SQUEEZE-OFF, THE GROUND FLAME CEASED. A BERKSHIRE GAS SUPERVISOR WAS REQUESTED AND ARRIVED ON SITE AT APPROXIMATELY 6:30 A.M. BERKSHIRE ALSO REQUESTED THE ASSISTANCE OF FIRE SCIENCE TECHNOLOGY, A FIRE SCIENCE CONSULTING FIRM, TO PROVIDE PROFESSIONAL FIRE SCIENCE ANALYSIS. BASED ON THE CONDITION PRESENTED, IT WAS DECIDED AT THAT TIME TO CONDUCT A PRESSURE TEST OF THE PROPANE SERVICE LINE, AS WELL AS THE NATURAL GAS SERVICE LINE TO SEE IF EITHER HAD BEEN IMPACTED BY THE LOCALIZED FIRE. AT THE NATURAL GAS SERVICE LINE SQUEEZE-OFF LOCATION, THE CREW CUT THE SERVICE LINE AND FUSED ON A 1 1/4 SERVICE RISER AS A MEANS TO PRESSURE TEST THE LINE WITH NITROGEN. AT APPROXIMATELY 10:30 A.M. THE DISTRIBUTION CREW, PERFORMED THE PRESSURE TEST AND THE SERVICE WAS NOT ABLE TO SUSTAIN PRESSURE. AT THIS POINT IT WAS DECIDED TO EXCAVATE THE SERVICE RISER AT THE BUILDING LOCATION. THE RISER IS A PERFECTION ANODELESS SERVICE RISER WITH A POLYETHYLENE-TO-STEEL TRANSITION. UPON EXCAVATION ON THE RISER, DRIED SOILS, WERE LOCATED AROUND THE AREA OF THE MOISTURE SEAL OF THE PRE-MANUFACTURED "PERFECTION" RISER. THE SOIL CONDITIONS ENCOUNTERED IN THE IMMEDIATE AREA SURROUNDING THE MOISTURE SEAL PRESENTED THOSE TYPICALLY ASSOCIATED WITH A LEAK. PICTURES WERE TAKEN TO DOCUMENT ENCOUNTERED CONDITIONS. THE SERVICE LINE WAS RE-PRESSURE TESTED TO IDENTIFY IF THE RISER WAS THE LEAKAGE SOURCE. THE PRESSURE TEST DID INDICATE THAT LEAKAGE ON THE BOTTOM PORTION OF THE MOISTURE SEAL WAS PRESENT BASED ON VISUAL OBSERVATION AND EMPLOYEES FEELING LEAKAGE ALONG THIS AREA. IT WAS THEN DECIDED TO REMOVE THE SERVICE RISER AND PRESSURE TEST THE REMAINING PORTION OF THE SERVICE LINE TO CHECK ITS INTEGRITY. THE SERVICE RISER WAS REMOVED (CUT) FROM THE SERVICE LINE AT A POINT APPROXIMATELY EIGHT INCHES UPSTREAM OF THE FIELD/MANUFACTURED JOINT. A DEAD END CAP WAS FUSED ONTO THE SERVICE LINE. A PRESSURE TEST WAS THEN CONDUCTED TO TEST THE REMAINING PORTION OF THE SERVICE LINE. THE TEST WAS CONDUCTED AND THE SERVICE LINE MAINTAINED A PRESSURE OF 100 PSIG FOR A 30 MINUTE PERIOD. A PRESSURE RECORDING CHART WAS UTILIZED TO DOCUMENT TEST RESULTS. BASED ON THE FIELD RESULTS, IT IS FELT THE PRE-MANUFACTURED "PERFECTION" SERVICE RISER MAY HAVE BEEN INVOLVED IN THE INCIDENT. THE SERVICE RISER WAS TAKEN FROM THE SITE BY BERKSHIRE GAS AND TRANSFERRED OVER TO THE MASSACHUSETTS DEPARTMENT OF TELECOMMUNICATIONS AND ENERGY (MADTE) -PIPELINE ENGINEERING AND SAFETY DIVISION WHERE IT CURRENTLY RESIDES. A TESTING LABORATORY HAS BEEN IDENTIFIED AND
2025-01-31 10:21 | NO | NO | 20030041 | 2003-03-21 | 792 | ATLANTA GAS LIGHT CO | WINDWARD PKWY @ MORRIS RD | ALPHARETTA | FULTON | GA | 30004- | 3 | NO | 939 | 2003-02-25 | 0 | 0 | 62277 | 39691.7908 | 95834.5364 | NO | 4 | 36 | 637765 | 20030225 | 280 | 300 | BY TEST | 640 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6.625 | 0.188 | API 5L B | UNKNOWN | 0 | 2001 | UNDER GROUND OR UNDER WATER |  | JAMES BRAY | 7702053602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES | NO DATA |  | AN EXCAVATOR RUPTURED A 6" HP STEEL NATURAL GAS MAIN WITH A TRACK HOE WHILE CLEANING OUT A RETENTION POND. THE ESCAPING GAS DID NOT IGNITE.
2025-01-31 10:21 | YES | YES | 20030042 | 2003-03-24 | 4350 | ELIZABETHTOWN GAS CO | 240-242 NEW BRUNSWICK AVENUE | PERTH AMBOY | MIDDLESEX | NJ | 08861- | 4 | NO | 302 | 2003-02-27 | 0 | 2 | 1000000 | 637342.6912 | 1538843.1752 | NO | 0 | 48 | 637958 | 20030227 | 122 | 125 | BY TEST | 200 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | OTHER | NOT DETERMINED | NO DATA | [5 empty] | 0 | 0 | ABOVE GROUND |  | DOUGLAS A. STAEBLER | 9082895000 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A FEW MINUTES BEFORE 3:00 A.M. AN AUTOMOBILE WAS DRIVEN INTO A HIGH PRESSURE METER SET THAT FED A FIRST FLOOR LAUNDROMAT IN A 3-STORY BUILDING CAUSING A GAS LEAK. PERTH AMBOY POLICE AND FIRE DEPARTMENTS RESPONDED AND EVACUATED 13 BUILDING TENANTS AT THE INCIDENT LOCATION AND ABOUT 57 OTHER PEOPLE FROM NEIGHBORING APARTMENT BUILDINGS. THE METER SET INLET VALVE WAS TURNED OFF BY AN ELIZABETHTOWN GAS COMPANY CREW AFTER ARRIVAL AT 3:41 A.M., STOPPING THE GAS LEAK. SHORTLY THEREAFTER, A BUILDING EXPLOSION OCCURRED AT THE INCIDENT LOCATION.
2025-01-31 10:21 | YES | NO | 20030043 | 2003-04-02 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 4497 US-23 SOUTH | GREENBUSH | ALCONA | MI | 4 8738 | 3 | NO | 2340 | 2003-02-28 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 3 | 0 | 638175 | 20030301 | 60 | 60 | BY TEST | 60 | NO DATA | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | OTHER PLASTIC |  | 0.875 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LAWRENCE K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | PRIMARY IGNITION OF MIGRATING NATURAL GAS EMANATING FROM SERVICE LINE AS A RESULT OF DAMAGE DURING INSTALLATION,
2025-01-31 10:21 | YES | YES | 20030044 | 2003-04-02 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 8310 DOBEL | DETROIT | WAYNE | MI | 48234- | 3 | NO | 1358 | 2003-03-16 | 0 | 1 | 100000 | 63734.2691 | 153884.3175 | NO | 2 | 0 | 639625 | 20030316 | 2 | 2 | BY TEST | 2 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 |  |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | LAWRENCE K. CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | PRIMARY IGNITION OF NATURAL GAS AS A RESULT OF MAIN BREAK
2025-01-31 10:21 | YES | YES | 20030045 | 2003-04-02 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | BOX 132, RD1 | FORD CITY | ARMSTRONG | PA | 1 6626 | 2 | NO | 1800 | 2003-03-11 | 1 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 30 | 639168 | 20030311 | 0.433 | 0.25 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | WELL | NO DATA |  | STEEL |  | 6 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD M. NOLAN JR | 4123953226 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A PRODUCTION WELL, NOT OWNED BY EQUITABLE, HAD A CASING LEAK. MIGRATING GAS FROM THE CASING WAS A CONTRIBUTING FACTOR TO THE INCIDENT.
2025-01-31 10:21 | YES | YES | 20030046 | 2003-04-14 | 13840 | NORTHWEST NATURAL GAS CO | 4746 APPALOOSA COURT SE | SALEM | MARION | OR | 9 7301 | 3 | NO | 445 | 2003-03-14 | 0 | 3 | 50000 | 31867.1346 | 76942.1588 | NO | 1 | 36 |  | 20030314 | 38 | 45 | BY CFR 192.619(A)(3) | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | OTHER | OUTSIDE FORCES, NOT A MATERIAL FAILURE | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1971 | UNDER GROUND OR UNDER WATER |  | J.C. PEERY | 5032264211 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | NO |  | NO | 0 |  | Null | NO DATA |  | A PORTLAND GENERAL ELETRIC (PGE) CREW WAS WORKING IN THE APPALOOSA COURT AREA PRIOR TO THE INCIDENT DUE TO A POWER OUTAGE THAT OCCURRED AT ABOUT MIDNIGHT. SHORTLY BEFORE THE INCIDENT, A NEARBY RESIDENT NOTIFIED THE PGE CREW THAT HE SMELLED NATURAL GAS. AT APPROXIMATELY 0445 HOURS, THE HOUSE AT 4746 APPALOOSA COURT SE IGNITED AND WAS SUBSEQUENTLY TOTALLY DESTROYED BY FIRE. THE CAUSE OF THE INCIDENT IS UNDER INVESTIGATION, BUT IS BELIEVED TO BE THE RESULT OF OUTSIDE FORCES.
2025-01-31 10:21 | NO | NO | 20030047 | 2003-04-02 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | RED LION, DALLASTOWN, YOE, WINDSOR | EMIGSVILLE | YORK | PA | 1 7403 | 3 | NO | 841 | 2003-03-03 | 0 | 0 | 0 | 0 | 0 | NO | 2 | 5 |  |  | 128 | 936 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | REGULATOR/METER |  | NO DATA | [5 empty] | 0 | 0 | OTHER | REGULATOR | RAY M. GEESEY | 7177670250 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE REGULATOR AT THE EMIGSVILLE TAKE STATION FROZE UP, CAUSING DOWN STREAM LOSS OF PRESSURE TO RED LION, DALLASTOWN, YOE, AND WINDSOR IN YORK COUNTY. APPROX. 7000 CUSTOMERS WERE AFFECTED. THE COMPANY IS CURRENTLY WORKING WITH THE PUBLIC UTILITY COMMISSION ON THE INVESTIGATION OF ANY OTHER CAUSES RELATED TO THE OUTAGE. IF NECESSARY, A FOLLOW UP REPORT OF THE INVESTIGATION WILL BE PROVIDED.
2025-01-31 10:21 | YES | YES | 20030048 | 2003-04-04 | 18536 | SOUTHWEST GAS CORP | 2238 E. HEDRICK DRIVE, NO. 12 | TUCSON | PIMA | AZ | 85719 | 3 | NO | 126 | 2003-03-16 | 1 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 2 | 42 | 639581 | 20030316 | 60 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D2513 | DUPONT | 1981 | 1981 | UNDER GROUND OR UNDER WATER |  | JIM LANTTO | 5207946034 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null |  |  | SEE PART D
2025-01-31 10:21 | NO | NO | 20030049 | 2003-03-28 | 30769 | MISSOURI GAS ENERGY | 3441 CHESTNUT | KANSAS CITY | JACKSON | MO | 6 4128 | 2 | NO | 1035 | 2003-03-09 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 3 | 0 | 638920 | 20030309 | 1 | 2.2 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  | UNKNOWN | UNKNOWN | 0 | 1908 | WITHIN/UNDER BUILDING |  | JIM GORMAN | 8163605893 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | NO |  | NO | 0 |  | YES | NO DATA |  | THIRD PARTY ACTIVITY REMOVED SUPPORT FROM BENEATH A SIX INCH CAST IRON MAIN. A HOLE FILLED WITH GRAVEL AND SAND ALLOWED GAS TO MIGRATE.
2025-01-31 10:21 | YES | YES | 20030050 | 2003-03-26 | 18484 | SOUTHERN CALIFORNIA GAS CO | 1220 LYNDON AVENUE | PASADENA | LOS ANGELES | CA |  | 3 | NO | 1133 | 2003-03-17 | 1 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 37 | 639730 | 20030317 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT |  | STEEL |  | 0.75 |  |  |  | 0 | 0 | OTHER | ABOVE AND UNDER GROUND | W.J. KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | VEHICLE LEFT RUNNING AND UNATTENDED. VEHICLE TRAVELED ACROSS DRIVEWAY, OVER CURB, AND STRUCK RISER WALL IN CARPORT, CAUSING GAS ESCAPE. VEHICLE AND CARPORT CAUGHT FIRE. EIGHTY TWO YEAR OLD MALE ENTERED BURNING VEHICLE FROM THE REAR DRIVER-SIDE DOOR, WAS SOMEHOW OVERCOME AND UNABLE TO ESCAPE.
2025-01-31 10:21 | NO | NO | 20030051 | 2003-03-20 | 4483 | ENSTAR NATURAL GAS CO | 533 E. DOLPHIN AVE. | PALMER |  | AK | 9 9645 | 3 | NO | 106 | 2003-03-14 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 3 | 21 | 639430 | 20030314 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M 8000 HDPE | DRISCOPIPE | 1984 | 1984 | ABOVE GROUND |  | DAVID W. BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON FRIDAY MORNING, MARCH 14, 2003 AT APPROX 0106 HOURS AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE PALMER FIRE DEPARTMENT OF A FIRE AT 533 E. DOLPHIN AVE; PALMER, AK. AN ENSTAR SERVICEMAN AND DUTY SUPERVISOR WERE DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING THE RELEASE OF NATURAL GAS. A DISTRIBUTION CREW WAS CALLED IN TO DIG UP AND PINCH OFF THE SERVICE LINE. THE SERVICE LINE WAS DUG UP AND PINCHED OFF AT 0437 AST. THE FIRE IS UNDER INVESTIGATION, HOWEVER NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THIS FIRE.
2025-01-31 10:21 | NO | NO | 20030052 | 2003-03-20 | 15462 | PECO ENERGY CO | 261 OLD YORK ROAD | JENKINTOWN | MONTGOMERY | PA | 1 9046 | 3 | NO | 1658 | 2003-02-19 | 0 | 0 | 2000 | 1274.6854 | 3077.6864 | YES | 0 | 22 |  | 20030219 | 64 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | HIT BY SNOW PLOW | STEEL |  |  |  | NA | NA | 0 | 1997 | ABOVE GROUND |  | WILLIAM J. SPROSS | 6109411599 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | NO | NO DATA |  | SEE PART D
2025-01-31 10:21 | NO | NO | 20030053 | 2003-04-08 | 4483 | ENSTAR NATURAL GAS CO | 267 BAILY STREET | PALMER |  | AK | 99519- | 3 | NO | 1425 | 2003-04-03 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 30 | 641285 | 20030403 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | M 8000 HDPE |  | 1984 | 1984 | ABOVE GROUND |  | DAVID BREDIN, OPERATIONS MANAGER | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THURSDAY AFTERNOON, APRIL 3, 2003 AT APPROXIMATELY 2:25 PM AST, AN ENSTAR NATURAL GAS COMPANY SERVICE TECHNICIAN NOTICED SMOKE IN THE AIR FROM A STRUCTURE FIRE. UPON INVESTIGATION, THE SERVICE TECHNICIAN FOUND LOCAL FIRE FIGHTERS FIGHTING A RESIDENTIAL STRUCTURE FIRE AT 267 S. BAILEY STREET IN PALMER, AK. HEAT FROM THE FIRE MELTED THE POLYETHYLENE NATURAL GAS SERVICE RISER ATTACHED TO THE BUILDING, CAUSING A RELEASE OF NATURAL GAS. THE SERVICE TECHNICIAN WAS ABLE TO EXPOSE AND PINCH OFF THE SERVICE LINE AT 2:55 PM AST. THE CAUSE OF THE FIRE IS UNKNOWN BUT INVESTIGATORS DETERMINED NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20030054 | 2003-04-09 | 4483 | ENSTAR NATURAL GAS CO | 5011 KIANNA | WASILLA |  | AK | 9 9654 | 3 | NO | 738 | 2003-04-07 | 0 | 0 | 150000 | 95601.4037 | 230826.4763 | NO | 0 | 32 | 641516 | 20030407 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM | 0.625 | 0.09 | M 8000 HDPE |  | 1998 | 1998 | ABOVE GROUND |  | DAVID BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | NO | NO | 20030055 | 2003-04-16 | 31097 | ISLAND ENERGY | 1324 CLUB DRIVE | VALLEJO | SOLANO | CA | 9 4592 | 2 | NO | 1415 | 2003-04-09 | 0 | 0 | 3000 | 1912.0281 | 4616.5295 | YES | 0 | 15 |  |  | 27 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.145 |  |  | 1982 | 1982 | UNDER PAVEMENT |  | WILLIAM PLUMMER, GAS TECH/INSPECTOR | 7075625000 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2003-04-03 | YES | NO DATA |  | CONTRACTOR TRENCHING ACROSS GAS LINE FOR IRRIGATION (WATER) LINE.
2025-01-31 10:21 | YES | NO | 20030056 | 2003-04-22 | 14210 | OKLAHOMA NATURAL GAS CO | 710 WEST 4TH STREET | SKIATOOK | OSAGE | OK | 74070- | 3 | NO | 1400 | 2003-03-23 | 0 | 0 | 90000 | 57360.8422 | 138495.8858 | NO | 0 | 30 | 640380 | 20030324 | 54 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.5 | 0.173 | MARLEX | PHILLIPS | 0 | 1964 | UNDER GROUND OR UNDER WATER |  | JAMES R. KUNKEL, ENGINEER III | 4055516902 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20030057 | 2003-04-17 | 2297 | CHENEY MUNICIPAL UTILITY | 120 N. MAIN STREET | CHENEY | SEDGWICK | KS | 6 7025 | 3 | NO | 1803 | 2003-03-19 | 0 | 2 | 175000 | 111534.971 | 269297.5557 | NO | 1 | 20 | 639956 | 20030319 | 28 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | NO DATA |  | 1 | 0.14 | NA | NA | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RANDALL OLIVER, CITY SUPERINTENDENT | 3165423815 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | YES | NO DATA |  | A 1" DIAMETER SERVICE LINE PIPE BROKE ABOUT 3/4THS THE WAY THROUGH. PIPE WAS ABOUT 4 FOOT DEEP. THE CITY HAD EXPERIENCE HEAVY RAIN FOR 3 DAYS PRIOR TO THE BREAK. THE 1" PIPE HAD BEEN STRUCK BY CONSTRUCTION EQUIPMENT PROBABLY AROUND 1961 OR 1962. THE AREA AROUND THE PIPE WAS BACK-FILLED WITH RUBBLE AND SAND FROM A FORMER BUILDING THAT WAS ON SITE. THE LINE BREAK WAS IN THE AREA WHERE THE PIPE WAS STRUCK; THE MASTIC COATING WAS KNOCKED OFF THE PIPE IN THIS AREA. THE SERVICE LINE WAS CAPPED AND BURIED UNDER THE GROUND IN 1961 OR 1962 OR AROUND THAT DATE.
2025-01-31 10:21 | YES | NO | 20030058 | 2003-04-15 | 2748 | CONSUMERS ENERGY CO | 5699 HORTON ROAD | JACKSON | JACKSON | MI | 4 9201 | 2 | NO | 652 | 2003-03-16 | 0 | 0 | 200000 | 127468.5382 | 307768.635 | NO | 0 | 40 | 639682 | 20030317 | 50 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | VALVE |  | STEEL |  |  |  |  | ECLIPS | 1967 | 1967 | ABOVE GROUND |  | JOAQUIN J. AFFONSO JR., MANAGER OF CODES AND STANDARDS | 5177881835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON 3/16/03 AT 0652 HOURS. A PASSERBY HEARD HISSING COMING FROM THE METER LOCATION AT 5966 HORTON ROAD IN JACKSON, MI. A CONSUMERS ENERGY GAS SERVICE WORKER (GSW) WAS DISPATCHED TO THE ADDRESS. UPON ARRIVAL, THE GSW ATTEMPTED TO NOTIFY THE HOMEOWNER THAT HE WAS THERE TO INVESTIGATE A GAS LEAK. THE HOMEOWNER DID NOT ANSWER THE DOOR. THE GSW THEN PROCEEDED TO THE METER LOCATION AND DISCOVERED A LEAK BELOW THE SERVICE RISER SHUTOFF VALVE. HE ATTEMPTED TO TIGHTEN THE FITTING BELOW THE SHUTOFF VALVE WITHOUT SUCCESS. DUE TO THE NATURE OF THE LEAK THE GSW REQUESTED A DISTRIBUTION CREW TO REPLACE THE SERVICE RISER AND SHUTOFF VALVE. THE GSW ATTEMPTED TO RESTRICT THE FLOW OF GAS INTO THE ATMOSPHERE BY PLACING TAPE AT THE POINT OF RELEASE, BUT THAT ONLY AMPLIFIED THE HISSING SOUND. THE GSW WAS IN THE PROCESS OF APPROACHING THE METER LOCATION TO CORPORATE THE SHUTOFF VALVE WHEN THE GAS IGNITED. AFTER THE FIRE WAS EXTINGUISHED, A FUEL LINE WAS DISCOVERED FEEDING AN AUXILIARY HEATER IN THE ATTIC SPACE ABOVE THE METER LOCATION. THE AUXILIARY HEATER HAD A STANDING PILOT. THE OUTSIDE VENT FROM THE AUXILIARY HEATER WAS ON THE GROUND NEAR THE METER LOCATION AND CLOSE TO THE HOUSE. VERY LITTLE DAMAGE OCCURRED AT THE RISER SHUTOFF VALVE. THE FIRE IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | NO | 20030060 | 2003-04-23 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 2073 PONTIAC | PRUDENVILLE | ROSCOMMON | MI | 4 8651 | 3 | NO | 1350 | 2003-04-12 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 2 | 10 | 642016 | 20030412 | 0.25 | 0.25 | BY TEST | 0.25 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | NO DATA |  | STEEL |  | 0.5 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LAWRENCE K. CROWDER, INVESTIGATOR | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | APPLIANCE VALVE FOR GAS FIRED CLOTHES DRYER FOUND IN OPEN POSITION PROVIDING NATURAL GAS RESULTING IN AN EXPLOSION AND RESULTING IN A FIRE.
2025-01-31 10:21 | YES | NO | 20030061 | 2003-05-02 | 2604 | COLUMBIA GAS OF VIRGINIA INC | 13700 BLOCK OF HENSLEY ROAD | MIDLOTHIAN |  | VA | 2 3836 | 3 | NO | 1345 | 2003-04-03 | 0 | 0 | 200000 | 127468.5382 | 307768.635 | NO | 2 | 22 | 641255 | 20030403 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 8 | 0.639 | ASTM 02513 | DRISCO 6500 | 1996 | 1996 | UNDER GROUND OR UNDER WATER |  | PHILIP D. WILSON SR. COMPLIANCE SPECIALIST | 8043235334 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-03-19 | YES | 3 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20030062 | 2003-04-25 | 22189 | PUGET SOUND ENERGY | 32400 SW 340 ST. | FEDERAL WAY | KING | WA | 9 8023 | 3 | NO | 1002 | 2003-04-12 | 0 | 0 | 125683 | 80103.1415 | 193406.4268 | NO | 9 | 30 |  | 20030414 | 60 | 60 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 | 0.154 | N/R | N/R | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | DOUGLAS DAMM, STANDARDS PROGRAM MGR. | 4254623721 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ELECTRIC FAULT CURRENT ENERGIZED STEEL GAS MAIN AND COPPER WATER SERVICE "WELDING" THEM TOGETHER AT POINT WHERE WATER CONTACTED GAS MAIN. WATER FLOWED INTO GAS SYSTEM CAUSING LOSS OF SERVICE TO ABOUT 360 CUSTOMERS. COST TO CLEAN SYSTEM, SERVICES, AND METER ASSEMBLIES, AND TO RESTORE SERVICE, ESTIMATED TO BE OVER $50,000. TO DATE, COST TO CLEAN SYSTEM, SERVICES, AND METER ASSEMBLIES, AND TO RESTORE SERVICE IS $85.283. AS OF 6-16-03 THE COST TO CLEAN SYSTEM, SERVICES, AND METER ASSEMBLIES, AND TO RESTORE SERVICE IS $125,683.
2025-01-31 10:21 | YES | NO | 20030063 | 2003-04-24 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 115 LAKE SHORE DR. | YOUNGSVILLE | LAFAYETTE | LA | 7 0592 | 2 | NO | 1000 | 2003-03-31 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 0 | 45 | 640998 | 20030401 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | PE 3406 | UPONOR | 2002 | 2003 | UNDER GROUND OR UNDER WATER |  | DANIEL HEBERT, DIVISION OPERATIONS MGR. | 3373735224 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | TRENCHING WITHOUT CALLING LA ONE CALL FOR A UTILITY LINE LOCATE.
2025-01-31 10:21 | YES | YES | 20030064 | 2003-05-21 | 13710 | NORTHERN ILLINOIS GAS CO | 3116 W 141ST ST | BLUE ISLAND | COOK | IL | 6 0406 | 3 | NO | 1625 | 2003-04-23 | 0 | 1 | 3000000 | 1912028.0736 | 4616529.5257 | NO | 2 | 15 | 643044 | 20030423 | 58 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 |  |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | LETICIA QUEZADA | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | YES | NO DATA |  | PLUMBING CONTRACTOR WAS EXCAVATING TO INSTALL WATER AND SEWER SERVICE LINES TO A HOME UNDER CONSTRUCTION. 2" STEEL MAIN WAS DAMAGED, CAUSING A LEAK DOWNSTREAM OF THE DAMAGE. GAS MIGRATED ACROSS THE STREET AND CAUSED EXPLOSION.
2025-01-31 10:21 | YES | NO | 20030065 | 2003-05-06 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 5265 EAGLETRACE DRIVE | RALEIGH | WAKE | NC | 2 7604 | 3 | NO | 1737 | 2003-04-27 | 0 | 0 | 90000 | 57360.8422 | 138495.8858 | NO | 3 | 50 | 643422 | 20030428 | 60 | 60 | BY TEST | 880 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | FITTING |  | STEEL |  | 0.75 |  |  |  | 0 | 1998 | ABOVE GROUND |  | JIMMY K JONES | 9198362419 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | DRIVER LOST CONTROL OF VEHICLE, RAN OFF ROAD AND INTO RESIDENTIAL DUPLEX DWELLING DAMAGING DOMESTIC METER SET AND IGNITING THE LEAKING GAS. VEHICLE AND RESIDENTIAL STRUCTURE DAMAGED BY FIRE.
2025-01-31 10:21 | YES | YES | 20030066 | 2003-05-23 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | 667 CHESTNUT STREET | BRIDGEVILLE | ALLEGHENY | PA | 1 5017 | 3 | NO | 2000 | 2003-05-03 | 0 | 3 | 100000 | 63734.2691 | 153884.3175 | NO | 0 | 0 | 643963 | 20030503 | 0.43 | 0.5 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | WELL | NO DATA |  | STEEL | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD M NOLAN JR | 4123953226 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE RESULTS OF EXTENSIVE TESTING OF EQUITABLE GAS FACILITIES IN THE INCIDENT AREA INDICATE EQUITABLE GAS FACILITIES WERE NOT A CONTRIBUTING FACTOR. A PRODUCTION WELL, NOT OWNED BY EQUITABLE GAS, IS CURRENTLY UNDER INVESTIGATION AS A POSSIBLE CONTRIBUTING FACTOR TO THE INCIDENT. AT THE TIME OF THIS REPORT, EQUITABLE HAS RENEWED THEIR FACILITIES IN THE INCIDENT AREA; HOWEVER, THE INCIDENT AREA HAS BEEN MADE SAFE DUE TO CONTINUED GAS MIGRATION FROM A UNKNOWN SOURCE.
2025-01-31 10:21 | NO | NO | 20030067 | 2003-05-20 | 13850 | NORTHWESTERN PUBLIC SERVICE CO | 205 GRANT STREET | CLARK | CLARK | SD | 5 7225 | 3 | NO | 915 | 2003-04-28 | 0 | 0 | 68500 | 43657.9743 | 105410.7575 | NO | 0 | 15 | 643442 | 20030428 | 40 | 50 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 1.25 |  | REGULATOR | UNIVERSAL CONTROLS | 0 | 1959 | ABOVE GROUND |  | MELISSA BARUTH | 6053537462 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | Null | NO DATA |  | THE FIRE REPORTS INDICATES AT 9:15 AM JOHN BERGER AT 207 GRANT STREET NOTIFIED THE CLARK FIRE DEPARTMENT OF A FIRE AT 205 GRANT STREET. THE HOMEOWNERS, JERI AND LEE TERVEEN, OF 205 GRANT STREET WERE NOT HOME AT THE TIME OF THE INCIDENT. EMERGENCY CREWS RESPONDED AT 9:20 AM ON APRIL 28 TO THE FIRE CALL. NORTHWESTERN ENERGY RESPONDED TO THE INCIDENT AT 9:30 AM. THE REGULATOR AT PREMISE, 205 GRANT WAS FOUND DAMAGED. FIRE BROKE OUT AT THE PREMISE. DAMAGE TO THE PROPERTY EXCEEDS $50,000. INVESTIGATION BY NORTHWESTERN YIELDED NO ADDITONAL LEAKS AT THE PREMISE. POST INCIDENT ODORANT LEVELS WERE FOUND WITHIN THE ACCEPTABLE LIMIT. ON 6/27/2001 THE SERVICE WAS CHECKED AND NO ATMOSPHERIC CORROSION WAS FOUND. ON 8/21/2000. THE FIVE-YEAR LEAK SURVEY WAS PERFORMED AND NO LEAKS WERE IDENTIFIED. THE INCIDENT WAS REPORTED TELEPHONICALLY AS REQUIRED BY 49 CFR PART 191.5. THE TELEPHONE REPORT WAS MADE AT 11:20 AM ON THE MORNING OF APRIL 28, 2003. THE TELEPHONE OPERATOR WAS RAWLS THE REPORT WAS ASSIGNED THE NUMBER 643442. MR. MARTIN BETTMANN, THE PIPELINE SAFETY MANAGER FOR THE STATE OF SOUTH DAKOTA, INVESTIGATED THIS INCIDENT ON APRIL 29. ALL TIMES LISTED IN THIS REPORT ARE CENTRAL STANDARD TIME.
2025-01-31 10:21 | YES | NO | 20030068 | 2003-05-29 | 792 | ATLANTA GAS LIGHT CO | 1357 PINE LOG RD | CONYERS | ROCKDALE | GA | 3 0013 | 3 | NO | 1300 | 2003-05-13 | 0 | 0 | 148616 | 94719.3214 | 228696.7173 | NO | 1 | 39 | 644852 | 20030513 | 210 | 300 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | WELD |  | STEEL |  | 2.875 | 0.203 | API 5L A 25 | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DAVID HAWKES | 7706024110 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 1 |  | YES | NO DATA |  | AN EXCAVATOR RUPTURED A 2.5" HP STEEL NATURAL GAS MAIN WITH A LOADER WHILE DEMOLISHING AN OLD BUILDING. THE ESCAPING GAS DID NOT IGNITE. THIS RESULTED IN THE LOSS OF GAS SERVICE TO 1100 CUSTOMERS.
2025-01-31 10:21 | NO | NO | 20030069 | 2003-06-05 | 14210 | OKLAHOMA NATURAL GAS CO | VARIOUS | OKLAHOMA CITY | OKLAHOMA | OK | 7 3102 | 3 | NO | 2330 | 2003-05-09 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 644548 | 20030510 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | ABOVE GROUND |  | GREG WELSH | 4055566453 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON MAY 9, 2003, AT APPROXIMATELY 9:30 P.M. THROUGH 11:30 P.M., A STORM THAT GENERATED TORNADO STRUCK CENTRAL OKLAHOMA, AND MOST OF THE DAMAGE WAS LIMITED TO OKLAHOMA CITY, OKLAHOMA AND SURROUNDING SUBURBS. COMPLETE DEVASTATION OCCURRED TO SOME STRUCTURES, WHILE OTHERS SUSTAINED ONLY MINOR DAMAGE. A TOTAL OF 81 ACCOUNTS WERE TURNED OFF DUE TO SUSPECTED DAMAGE TO BUILDING STRUCTURES OR TO OKLAHOMA NATURAL GAS COMPANY FACILITIES. LIGHT DAMAGES WERE NOTED TO COMPANY FACILITIES. SERVICE HAS NOW BEEN RESTORED TO THOSE ACCOUNTS THAT WERE OFF IN ERROR, OR THAT HAVE BEEN REPAIRED BECAUSE OF MINOR DAMAGE. DAMAGES TO COMPANY FACILITIES AND COSTS TO RESTORE SERVICE TO DAMAGED PROPERTIES ARE APPROXIMATELY $17,900.
2025-01-31 10:21 | NO | NO | 20030070 | 2003-06-05 | 14210 | OKLAHOMA NATURAL GAS CO | EAST OF I-35, N 12TH ST | MOORE | CLEVELAND | OK | 7 3102 | 3 | NO | 1730 | 2003-05-08 | 0 | 0 | 0 | 0 | 0 | YES | 2 | 0 | 644467 | 20030509 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | ABOVE GROUND |  | TODD VERNON | 4055516543 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON MAY 8, 2003, AT APPROXIMATELY 5:30 P.M., A STORM THAT GENERATED TORNADOS STRUCK CENTRAL OKLAHOMA, AND MOST OF THE DAMAGE WAS LIMITED TO MOORE, OKLAHOMA. COMPLETE DEVASTATION OCCURRED TO SOME STRUCTURES, WHILE MANY OTHERS SUSTAINED ONLY MINOR DAMAGE. ALTHOUGH A TOTAL OF 902 ACCOUNTS WERE TURNED OFF DUE TO SUSPECTED DAMAGE TO BUILDING STRUCTURES OR TO OKLAHOMA NATURAL GAS COMPANY FACILITIES, ONLY 616 ACTUALLY SUSTAINED DAMAGE DUE TO THE INCIDENT. NO MAINS WERE DAMAGED, HOWEVER, 15 METER SETTINGS AND TWO DISTRICT REGULATOR STATIONS REQUIRED REPAIR. ONE DISTRICT REGULATOR STATION CAUSED SERVICE INTERRUPTION TO A SINGLE ACCOUNT. THE OTHER ONE SUPPLIED A SYSTEM WITH A TWO-WAY FEED, RESULTING IN NO ACCOUNTS BEING AFFECTED. SERVICE HAS NOW BEEN RESTORED TO THOSE ACCOUNTS THAT WERE OFF IN ERROR, OR THAT HAVE BEEN REPAIRED BECAUSE OF MINOR DAMAGE. DAMAGES TO COMPANY FACILITIES AND COSTS TO RESTORE SERVICE TO DAMAGED PROPERTIES ARE APPROXIMATELY $43,500.
2025-01-31 10:21 | YES | NO | 20030071 | 2003-06-09 | 2596 | COLUMBIA GAS OF OHIO INC | 36036 CORONIA CR | AVON | LORAIN | OH | 4 4011 | 3 | NO | 1125 | 2003-05-05 | 0 | 0 | 200000 | 127468.5382 | 307768.635 | NO | 0 | 20 | 644065 | 20030505 | 40 | 60 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | MICHAEL F SUCHARSKI | 6144602064 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | INTIAL INVESTIGATION HAS REVEALED THAT THE CAUSE OF FIRE AND EXPLOSION AT THE REFERENCED ADDRESS WAS LIKELY THE RELEASE OF NATURAL GAS; HOWEVER THE INCIDENT IS UNDER INVESTIGATION AND AS OF THE DATE OF THIS REPORT, IT IS UNKNOWN WHETHER THE SOURCE OF THE RELEASE WAS UPSTREAM OR DOWNSTREAM OF THE METER. A SUPPLEMENTAL REPORT WILL BE FILED WITH ADDITIONAL INFORMATION.
2025-01-31 10:21 | YES | YES | 20030072 | 2003-06-06 | 12420 | MICHIGAN GAS UTILITIES CO | 830 STEVENS TRAIL | MONROE | MONROE | MI | 48161- | 3 | NO | 1530 | 2003-02-15 | 0 | 1 | 110000 | 70107.696 | 169272.7493 | NO | 1 | 46 | 636944 | 20030215 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.333 | SDR 13.5 | PLEXCO | 1998 | 1998 | NO DATA |  | BILL J PARRISH | 7342425382 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-01-27 | YES | 2 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20030073 | 2003-06-16 | 15007 | PACIFIC GAS & ELECTRIC CO | 10101 IMPERIAL AVE | CUPERTINO | SANTA CLARA | CA |  | 3 | NO | 1350 | 2003-05-07 | 0 | 0 | 415000 | 264497.2168 | 638619.9177 | NO | 1 | 37 | 644324 | 20030507 | 57 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | TR 418 | UKNOWN | 0 | 1982 | UNDER PAVEMENT |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 3 | YELLOW USA PAINT | YES | NO DATA |  | DIRECTIONAL BORING SYSTEMS INC BORED INTO A TWO-INCH PLASTIC GAS MAIN AT APPROXIMATELY 1350 HOURS ON MAY 7, 2003. LEAKING GAS ACCUMULATED IN THE ADJACENT HOME AND IT EXPLODED AT 1438 HOURS.
2025-01-31 10:21 | NO | NO | 20030074 | 2003-06-16 | 31459 | KEYSPAN ENERGY DELIVERY | 1787 ORLEANS ROAD | EAST HARWICH |  | MA |  |  | NO | 1930 | 2003-05-16 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 0 |  | 20030517 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | SUSPECTED CUSTOMER | OTHER | LEAK ON CUSTOMER | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | THOMAS R TEEHAN | 7814665137 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | INVESTIGATION IS ONGOING. FIRE MARSHALLS OFFICE DISCOVERED THAT A CAP WAS REMOVED FROM THE DRIP PIPE OF THE BOILER. TOOLS WERE ALSO FOUND AT THE SCENE. SERVICE LINE PASSED PRESSURE TEST BY MASSACHUSETTS DTE. DTE ALSO PLANS TO TEST REGULATORS.
2025-01-31 10:21 | NO | NO | 20030075 | 2003-06-16 | 15462 | PECO ENERGY CO | 457 LANCASTER AVE | HAVERFORD |  | PA | 1 9041 | 3 | NO | 904 | 2003-05-17 | 0 | 0 | 0 | 0 | 0 | YES | 3 | 11 | 645212 | 20030517 | 7 | 25 | BY TEST | 100 | CORROSION | CORROSION | EXTERNAL | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 1.25 | 0.154 | UNKNOWN | UNKNOWN | 0 | 1940 | UNDER GROUND OR UNDER WATER |  | KURT A GRIFFIN | 6109411818 | EXTERNALLY | NO DATA |  | NO DATA |  | BARE | NO | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20030076 | 2003-06-19 | 15462 | PECO ENERGY CO | LEE PARK INDUSTRIAL BUILDING 555 N LA | CONSHOHOCKEN | MONTGOMERY | PA | 1 9428 | 1 | NO | 1045 | 2003-05-22 | 0 | 0 | 81000 | 51624.758 | 124646.2972 | YES | 2 | 2 |  | 20030522 | 17 | 35 | BY TEST | 50 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.316 | ASTMD 2513 | DUPONT | 0 | 1972 | UNDER GROUND OR UNDER WATER |  | ALLAN R BRANDT | 6109411599 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-05-14 | YES | 0 |  | YES | NO DATA |  | SEE PART D
2025-01-31 10:21 | YES | NO | 20030077 | 2003-06-24 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 519 CENTRAL AVE NW | ALBUQUERQUE | BERNALILLO | NM | 87102- | 3 | NO | 512 | 2003-05-05 | 0 | 0 | 125000 | 79667.8364 | 192355.3969 | NO | 0 | 55 | 645911 | 20030524 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | VALVE |  | CAST IRON |  | 1 |  | UNKNOWN | UNKNOWN | 0 | 0 | ABOVE GROUND |  | PAULA MCAFEE | 5052414504 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | CAUSE OF FIRE IS CURRENTLY UNDER INVESTIGATION BY LOCAL FIRE DEPARTMENT. ARSON IS SUSPECTED DUE TO LOCATION OF POSSIBLE IGNITION FROM STACKS OF CARDBOARD BOXES ON CORNER OF BUILDING. CARDBOARD BOXES WERE LOCATED NEXT TO THE RISER AND GAS METER. THE FIRE FROM THE CARDBOARD BOXES ENGULFED THE GAS METER RISER RESULTING IN ESCAPING GAS, WHICH PROVIDED FUEL FOR THE FIRE.
2025-01-31 10:21 | NO | NO | 20030078 | 2003-06-24 | 20010 | U G I CORP | 1009 N PRINCE STREET | LANCASTER | LANCASTER | PA | 17603- | 3 | NO | 1312 | 2003-04-14 | 0 | 0 | 70598 | 44995.1193 | 108639.2505 | YES | 7 | 3 |  | 20030523 | 126 | 135 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.25 | N/A | N/A | 0 | 1950 | UNDER PAVEMENT |  | JAMES R HEINTZ | 6107963528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-04-07 | YES | 3 |  | YES | NO DATA |  | TRACKHOE OPERATOR FOR BRIDGE CONTRACTOR HIT AND PUNCTURED 6" STEEL NATURAL GAS PIPELINE. OPERATOR WAS EXCAVATING FOR STORM WATER PIPE SYSTEM LOCATED ADJACENT TO GAS PIPELINE. GAS FACILITIES WERE PROPERLY MARKED.
2025-01-31 10:21 | YES | YES | 20030079 | 2003-06-25 | 11336 | LEBANON GAS DEPT, CITY OF | 1322 W MAIN ST | LEBANON | WILSON | TN | 3 7087 | 3 | NO | 1615 | 2003-06-12 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 30 | 647725 | 20030612 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 4 | 0.391 | MDPE 3810 | POLYPIPE | 2001 | 2003 | UNDER GROUND OR UNDER WATER |  | DON COZART | 6154432835 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES | 2003-06-12 | YES | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | YES | 20030080 | 2003-06-30 | 11800 | LOUISIANA GAS SERVICE CO | 166 W 3RD STREET | NORTH HODGE | JACKSON | LA |  | 3 | NO | 1121 | 2003-06-03 | 0 | 2 | 3000 | 1912.0281 | 4616.5295 | YES | 0 | 11 | 646777 | 20030603 | 30 | 90 | BY TEST | 125 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  |  | 0 | 1990 | UNDER GROUND OR UNDER WATER |  | ANTHONY BROWN | 5048494363 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2003-06-03 | NO | NO DATA |  | TOWN OF NORTH HODGE CONTRACTOR HIT GAS COMPANY FACILITIES CAUSING INCIDENT.
2025-01-31 10:21 | YES | YES | 20030081 | 2003-07-03 | 22784 | ALLIANT ENERGY - WISCONSIN POWER & LIGHT CO | ABLER ROAD AND PARK RIDGE COURT | TAYCHEEDAH | FOND DU LAC | WI | 5 4935 | 3 | NO | 1316 | 2003-05-27 | 0 | 2 | 0 | 0 | 0 | NO | 1 | 14 | 646133 | 20030527 | 58 |  | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | PE-2406 | PLEXCO | 1998 | 1998 | UNDER GROUND OR UNDER WATER |  | ROSANNE ROGERS LATSCH | 6084585540 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-04-30 | YES | 3 |  | YES | NO DATA |  | A SEWER CONTRACTOR WAS INSTALLING A NEW SANITARY LINE NEAR A NATURAL GAS PLASTIC DISTRIBUTION SYSTEM. WHILE SCRAPING OFF A LAYER OF DIRT ABOVE THE NATURAL GAS MAIN WITH A BACKHOE, THE CONTRACTOR SEVERED THE 2-INCH PLASTIC MAIN. TWO MEN ENTERED THE TRENCH WITH THE BLOWING NATURAL GAS AND ATTEMPTED TO SQUEEZE OFF THE PLASTIC PIPE WITH A SEWER PIPE SQUEEZE-OFF TOOL. STATIC ELECTRICITY IGNITED THE NATURAL GAS AND THE TWO MEN RECEIVED 1ST AND 2ND DEGREE BURNS.
2025-01-31 10:21 | NO | NO | 20030082 | 2003-07-03 | 18484 | SOUTHERN CALIFORNIA GAS CO | 21 LEWIS RD | CAMARILLO | VENTURA | CA |  | 3 | NO | 1254 | 2003-06-20 | 0 | 0 | 75000 | 47800.7018 | 115413.2381 | NO | 2 | 19 | 648541 | 20030620 | 45 | 100 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | JOINT |  | STEEL |  | 3 |  |  |  | 0 | 1958 | UNDER PAVEMENT |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | YES | NO DATA |  | CONTRACTOR STRUCK TWO FOOT LONG, THREE INCH STEEL STUB WHILE EXCAVATING ON BRIDGE JOB. PINCHING MAIN LINE RESULTED IN APPROXIMATELY 1000 OUTAGES. STUB WAS NOT IDENTIFIED ON ATLAS SHEET, NOT LOCATED AND MARKED.
2025-01-31 10:21 | YES | YES | 20030083 | 2003-07-10 | 31358 | TECO PEOPLES GAS LP OPERATIONS | 1500 BLOCK OF CATTLEMEN RD | SARASOTA | SARASOTA | FL | 3 4232 | 3 | NO | 944 | 2003-06-28 | 0 | 1 | 50000 | 31867.1346 | 76942.1588 | NO | 3 | 30 | 649513 | 20030630 | 50 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 | API 5L GRADE X42 | LTV | 1997 | 1998 | UNDER GROUND OR UNDER WATER |  | KEITH MARTIN | 8132284540 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES | NO DATA |  | A ROAD MIXER WAS BEING USED TO STABILIZE ROAD SUB-GRADE MATERIAL OVER A 6" (NPS) STEEL GAS MAIN. DURING THE OPERATION THE MIXER HIT THE GAS LINE, RUPTURING IT. GAS ESCAPING UNDER 50 PSIG ENGULFED THE EQUIPMENT AND OPERATOR, AND THEN IGNITED. THE OPERATOR WAS ABLE TO ESCAPE WITHOUT AID, BUT SUSTAINED BURN INJURIES TO ARMS AND FACE, WHICH REQUIRED HOSPITALIZATION FOR TREATMENT. HE WAS LISTED IN CRITICAL BUT STABLE CONDITION. THE ROAD MIXER SUSTAINED SIGNIFICANT DAMAGE, AND WAS VALUED IN EXCESS OF $50,000.
2025-01-31 10:21 | YES | YES | 20030084 | 2003-07-10 | 18536 | SOUTHWEST GAS CORP | LOT 71 COPPER SKY SUBDIVISION | SIERRA VISTA | COCHISE | AZ | 8 5635 | 3 | NO | 1444 | 2003-06-16 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 13 | 648080 | 20030616 | 25 | 25 | BY TEST | 100 | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | SERVICE LINE |  | OTHER | SEE PART D | POLYETHYLENE PLASTIC |  | 1 | 0.103 | ASTM D2513 | PHILLIPS DRISCO | 2003 | 2003 | OTHER | OPEN TRENCH | RANDY J SMITH | 5207946031 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | SEE PART D
2025-01-31 10:21 | YES | YES | 20030085 | 2003-07-10 | 12350 | MINNEGASCO INC | STATE HIGHWAY 23 & FOREST PARK FRONTAGE | WAKEFIELD | STEARNS | MN | 5 6320 | 3 | NO | 1330 | 2003-06-12 | 0 | 1 | 18000 | 11472.1684 | 27699.1772 | NO | 1 | 0 | 647700 | 20030612 | 55 | 55 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.23 | PE 2406 | PLEXCO | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | JOHN M WIINAMAKI | 6123215257 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20030086 | 2003-07-14 | 2392 | CITIZENS GAS & COKE UTILITY | INTERSTATE 74 (NEAR 3120 S FRANKLIN RD) | INDIANAPOLIS | MARION | IN | 4 6239 | 3 | YES | 1130 | 2003-06-10 | 0 | 0 | 435000 | 277244.0707 | 669396.7812 | NO | 1 | 15 | 647444 | 20030610 | 24 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.25 | UNKNOWN | UNKNOWN | 1959 | 1959 | UNDER GROUND OR UNDER WATER |  | JOHN J EDDINGTON | 3179274657 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2004-06-05 | YES | 1 |  | YES | NO DATA |  | CONTRACTOR WAS ATTEMPTING TO COMPACT SOIL IN AREA FOR INTERSTATE I74 RESTORATION PROJECT. CONTRACTOR APPEARS TO HAVE MADE ERROR IN MEASURING MAIN DEPTH AND BELIEVED THEY HAD SUFFICIENT CLEARANCE BUT DID NOT. THIS IS THE PRIMARY FACTOR IN THE MAIN BEING DAMAGED AND RESULTANT FIRE.
2025-01-31 10:21 | YES | YES | 20030088 | 2003-07-21 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | 47190 NORTH HIGHWAY #187 | DERRY | SIERRA | NM | 8 7933 | 1 | NO | 2230 | 2003-06-16 | 1 | 0 | 0 | 0 | 0 | NO | 1 | 40 | 648102 | 20030617 | 305 | 525 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | UNKNOWN | UNKNOWN | 0 | 1978 | ABOVE GROUND |  | JON W JONES | 5052414571 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | PNM IS PROVIDING A FOLLOW-UP WRITTEN NOTIFICATION TO THE INITIAL TELEPHONIC NOTIFICATION MADE ON JUNE 17, 2003, OF THE FATAL SINGLE CAR ACCIDENT WHICH OCCURRED ON JUNE 16, 2003, AT 47190 HWY 187 IN DERRY, NM. THE SOLE OCCUPANT OF THE VEHICLE WAS A TWENTY-SEVEN YEAR OLD MALE. MEDIA REPORTED THAT POLICE INDICATED THE ACCIDENT WAS ALCOHOL-RELATED. THE VEHICLE WAS TRAVELING SOUTHBOUND ON HWY 187 AT A HIGH RATE OF SPPED WHEN IT LEFT THE ROADWAY. AFTER LEAVING THE ROADWAY, THE VEHICLE SPUN OUT OF CONTROL FOR APPROXIMATELY 250+ FEET, CROSSED THE SOUTH AND NORTH BOUND LANES OF HWY 187, THE REAR OF THE VEHICLE STRUCK A LARGE COTTONWOOD TREE AND A BARRICADED CUSTOMER METER SET. THE MAIN LINE GAS PRESSURE WAS 305 PSI (MAOP 525 PSI). NO IGNITION OCCURRED. BASED UPON SKID MARKS AT THE ACCIDENT SCENE NM STATE POLICE ESTIMATED THE VEHICLE WAS TRAVELING IN EXCESS OF 80 MILES PER HOUR. INITIAL INFORMATION INDICATES THAT THE DRIVER DIED FROM BLUNT TRAUMA INJURIES RESULTING FROM THE IMPACT OF THE VEHICLE WITH THE TREE. THE VEHICLE SHEARED THE RISER WITHIN THE BARRICADED METER SET. PNM RESPONDED PROMPTLY. THE SERVICE TEE WAS EXPOSED AT THE MAIN TO SHUT OFF THE GAS.
2025-01-31 10:21 | NO | NO | 20030089 | 2003-07-21 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | WEST 18TH AND US HIGHWAY #70 | PORTALES | ROOSEVELT | NM | 8 8130 | 3 | NO | 1220 | 2003-06-18 | 0 | 0 | 0 | 0 | 0 | YES | 54 | 0 | 648506 | 20030620 | 42 | 48 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | OTHER | DISTRIBUTION PIPING | STEEL |  | 2 | 0.154 | UKNOWN | UNKNOWN | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JON W JONES | 5052414571 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON JUNE 18, 2003, DURING A ROUTINE REGULATOR INSPECTION AT THE PORTALES SOUTH BORDER STATION, A GAS MEASUREMENT TECHNICIAN WAS USING A GAUGE IN A "PETES PLUG" LOCATED ON THE OUTLET VALVE SET TO MONITOR PRESSURES WHILE WORKING ON THE REGULATORS. THE GAUGE INCORRECTLY REFLECTED THAT PRESSURE HAD DROPPED BELOW OPERATING PRESSURE. THE INCORRECT READING IS BELIEVED TO BE CAUSED BY A RESTRICTION IN THE PETES PLUG. BASED ON THE INCORRECT READING, THE TECHNICIAN ADJUSTED THE WORKER REGULATOR TO BRING THE PRESSURE BACK TO OPERATING PRESSURE, RESULTING IN AN OVER PRESSURE CONDITION IN THE DISTRIBUTION SYSTEM IN PORTALES, NEW MEXICO. INITIALLY, PNM CONSIDERED THIS TO BE A SAFETY RELATED CONDITION (EXCEEDING MAOP) BUT CORRECTABLE WITHIN THE REPORTING PERIOD AND, THEREFORE, NOT REPORTABLE AS A SAFETY RELATED CONDITION. THE OVER PRESSURE CONDITION WAS BROUGHT UNDER CONTROL WITHIN 2 HOURS. ON JUNE 20, 2003, UPON THE DISCOVERY OF FIVE (5) GRADE 1 LEAKS WITHIN THE DISTRIBUTION SYSTEM, PNM MADE THE DECISION THAT THE SAFETY RELATED CONDITION WAS NOW SIGNIFICANT AND REPORTABLE. WITHIN 54 HOURS OF THE OVERPRESSURE EVENT, A LEAK SURVEY OF THE DISTRIBUTION SYSTEM WAS COMPLETED. AN INITIAL LEAK SURVEY WAS STARTED AT 2100 HOURS ON JUNE 18, 2003 AND COMPLETED AT 1800 HOURS ON JUNE 20, 2003. A SECOND LEAK SURVEY WAS STARTED AT 0600 HOURS ON JUNE 23, 2003 AND COMPLETED AT 1800 HOURS ON JUNE 24, 2003. ALL KNOWN GRADE 1 AND 2 LEAKS WERE REPAIRED. A THIRD LEAK SURVEY WILL BE CONDUCTED IN MID-JULY 2003.
2025-01-31 10:21 | NO | NO | 20030090 | 2003-07-21 | 12876 | QUESTAR GAS COMPANY | 231 WEST 200 NORTH | VERNAL | UINTAH | UT | 8 4078 | 3 | NO | 1515 | 2003-06-17 | 0 | 0 | 60000 | 38240.5615 | 92330.5905 | NO | 0 | 20 | 648191 | 20030617 | 55 | 60 | BY CFR 192.619(A)(3) | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | STEEL |  | 0.75 | 0.113 | N/A | N/A | 0 | 0 | WITHIN/UNDER BUILDING |  | JEFFERY D HANSEN | 8013243645 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | THIRD PARTY CONTRACTOR HIT AND PULLED A 3/4" STEEL SERVICE LINE. A LEAK OCCURRED FURTHER DOWNSTREAM ON THE SERVICE LINE AT A COMPRESSION TYPE FITTING. THE SERVICE LINE WAS PULLED OUT OF THE COMPRESSION TYPE FITTING. THE LEAKING GAS MIGRATED INTO THE CRAWL SPACE OF THE HOME AND WAS IGNITED SHORTLY AFTER THE LINE WAS PULLED CAUSING AN EXPLOSION UNDERNEATH THE HOME (IN THE CRAWL SPACE).
2025-01-31 10:21 | YES | NO | 20030091 | 2003-07-17 | 15007 | PACIFIC GAS & ELECTRIC CO | 9294 MALHEUR WAY | ELK GROVE | SACRAMENTO | CA | 95758- | 3 | NO | 1815 | 2003-06-25 | 0 | 0 | 360000 | 229443.3688 | 553983.5431 | NO | 0 | 30 | 649043 | 20030625 | 50 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1991 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | A VEHICLE DRIVEN BY A THIRD PARTY VEERED OFF OF THE STREET AND SHEERED THE METER SET FROM THE RISER, CAUSING GAS TO ESCAPE. THE ESCAPING GAS IGNITED AND BURNED PART OF THE HOUSE AND TWO VEHICLES.
2025-01-31 10:21 | YES | NO | 20030092 | 2003-07-17 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 1600 N STEPHENSON | IRON MOUNTAIN | DICKENSON | MI |  | 2 | YES | 1127 | 2003-07-07 | 0 | 0 | 100000 | 63734.2691 | 153884.3175 | NO | 26 | 0 | 650906 | 20030715 | 150 | 150 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | OTHER | 2" NIPPLE | STEEL | [5 empty] | 0 | 0 | UNDER GROUND OR UNDER WATER |  | JOSEPH A DIDIA | 3132356921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES | NO DATA |  | CONTRACTOR STRUCK AND RUPTURED AN 8" XTC 150 PSIG NATURAL GAS MAIN. A 2" EXTRA HEAVY NIPPLE USED FOR PURGING WAS DAMAGED BY A BACKHOE.
2025-01-31 10:21 | YES | YES | 20030093 | 2003-08-01 | 3240 | CONECTIV | 1816 WEST 3RD ST | WILMINGTON | NEW CASTLE | DE | 1 9805 | 4 | NO | 1345 | 2003-07-02 | 0 | 3 | 300000 | 191202.8074 | 461652.9526 | NO | 4 | 13 | 649752 | 20030702 | 0.3 | 0.6 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | NO DATA |  | STEEL |  | 1.25 |  | UNKNOWN | UNKNOWN | 0 | 1962 | UNDER PAVEMENT |  | PHILIP L PHILLIPS JR | 3024293846 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | INITIAL INVESTIGATION, UNDER THE DIRECTION OF NTSB, INDICATES A CONTRACTOR REPLACING CURBS AND SIDEWALK FOR THE CITY OF WILMINGTON HIT A GAS SERVICE LINE CAUSING GAS TO LEAK. AN EXPLOSION AND FIRE RESULTED. THE CONTRACTOR HAD NOT NOTIFIED THE OPERATOR TO MARK THE WORK LOCATION AS REQUIRED BY DELAWARE LAW.
2025-01-31 10:21 | YES | NO | 20030094 | 2003-08-01 | 15007 | PACIFIC GAS & ELECTRIC CO | CALVINE 1/3 MI E/BRADSHAW | ELK GROVE | SACRAMENTO | CA | 9 5624 | 3 | NO | 848 | 2003-07-03 | 0 | 0 | 105000 | 66920.9826 | 161578.5334 | NO | 2 | 19 | 649882 | 20030703 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 6 | 0.491 | SDR 11.5 | DRISCO | 1989 | 1989 | UNDER PAVEMENT |  | SHAN BHATTACHARYA | 4159735998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | PAINT | YES | NO DATA |  | AT 1655 HOURS ON 7/3/03, PG&E DETERMINED THAT THE PROPERTY LOSS WOULD EXCEED $50,000, AND THE INCIDENT BECAME REPORTABLE AT THAT TIME.
2025-01-31 10:21 | YES | NO | 20030095 | 2003-08-01 | 30821 | ATMOS ENERGY CORPORATION | PRAIRIE ST AND OVERLOOK | OLATHE | JOHNSON | KS | 6 6061 | 2 | NO | 1447 | 2003-07-03 | 0 | 0 | 300000 | 191202.8074 | 461652.9526 | NO | 2 | 12 | 649869 | 20030703 | 35 | 40 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 | 0.409 | ASTM D2513 | DUPONT | 0 | 1975 | UNDER GROUND OR UNDER WATER |  | DOUGLAS L SHATAS | 9137640531 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-06-25 | Null | 0 |  | YES | NO DATA |  | EXCAVATOR WAS TILLING ROADWAY BASE ON A PUBLIC IMPROVEMENT PROJECT. EQUIPMENT WAS TURNING AROUND SOUTH OF THE ROADWAY AND CONTACTED MAIN.
2025-01-31 10:21 | YES | YES | 20030096 | 2003-07-31 | 18584 | SPRINGFIELD, CITY UTILITIES OF | 1001 W NORTON | SPRINGFIELD | GREENE | MO | 6 5803 | 3 | NO | 1208 | 2003-06-18 | 1 | 0 | 0 | 0 | 0 | NO | 0 | 52 | 648359 | 20030618 | 56.5 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  |  | 0 | 1971 | UNDER PAVEMENT |  | RODDY ROGERS | 4178318504 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 12:08 PM ON JUNE 18, 2003 THERE WAS AN EXPLOSION AT THE FRISCO BUILDING ON THE OZARK EMPIRE FAIRGROUNDS AT 1001 W NORTON ROAD. THERE WAS ONE FATALITY. CITY UTILITIES PROCEDURES FOR NATURAL GAS EMERGENCIES WERE FOLLOWED AND THE MISSOURI PUBLIC SERVICE COMMISSION (PSC) WAS NOTIFIED. GAS WAS SHUT OFF TO THE AREA BY 1:00PM ON JUNE 18. PSC REPRESENTATIVES ARRIVED ONSITE THAT AFTERNOON. CONSTRUCTION CREWS, PRESSURE CONTROL PERSONNEL, LEAK INVESTIGATORS, AND ENGINEERING PERSONNEL WORKED ON SITE IN A COORDINATED EFFORT AND REPRESENTATIVES FROM THE PSC WERE ON SITE MONITORING THE WORK THROUGH JUNE 21, 2003. SEVERAL READINGS OF GAS IN AIR AND LEL WERE TAKEN IN THE AREA OF THE PIPE, IN THE AREA BETWEEN THE PIPE AND THE BUILDING, AND IN THE BASEMENT AREA OF THE BUILDING. SAMPLES OF THE AIR WERE ALSO TAKEN. THIS DATA SHOWED THAT NATURAL GAS WAS IN THE BUILDING. THE SPRINGFIELD FIRE DEPARTMENT INVESTIGATION RULED THAT THE IGNITION SOURCE WAS A CIGARETTE LIGHTER AND THAT THE FUEL SOURCE WAS NATURAL GAS. CITY UTILITIES RETAINED A THIRD PARTY INVESTIGATOR WHO WORKED WITH CU PERSONNEL AND THE PSC FROM JUNE 19 JUNE 21 CONDUCTING AN ONSITE INVESTIGATION TO DETERMINE THE PRESENCE AND LOCATION OF A GAS LEAK. CITY UTILITIES ONSITE INVESTIGATION DETERMINED THAT THERE WAS A LEAK IN A 2-INCH PLASTIC GAS SERVICE PIPE RUNNING ROUGHLY PARALLEL TO THE WEST SIDE OF THE BUILDING AT A DISTANCE OF 48 FEET. THE LEAKING SECTION OF THE 2-INCH ALDYL A PLASTIC PIPE WAS REMOVED FROM THE GROUND FOR TESTING AND AFTER THE LINE HAD BEEN CUT IN SECTIONS FOR PRESSURE TESTING IT WAS PURGED OF GAS, CAPPED AND RETIRED. IN THE NORTH AND SOUTH EXTREMES OF THE EXCAVATION THAT WAS MADE TO TEST AND REMOVE THE LEAKING SECTION OF THE PIPE, SAND BACKFILL COULD BE OBSERVED AROUND THE PIPE. IN THE AREA OF THE LEAKING SECTION THE SAND BACKFILL WAS DISCONTINUOUS AND THERE WAS CONSTRUCTION DEBRIS AROUND THE PIPE. THERE WAS A ROCK IMPINGEMENT UNDER THE PIPE STRESSING THE PIPE AT THE POINT OF FAILURE. THE ORIGIN OF THE DEBRIS AND ROCK ARE NOT KNOWN. THE DAMAGE COULD BE DESCRIBED AS A TOTAL COLLAPSE OF THE FRISCO BUILDING. THE EAST WALL OF THE BASEMENT WAS BUCKLED INWARD. THE BUILDING AND ITS CONTENTS WERE A TOTAL LOSS. DEBRIS WAS SCATTERED WELL INTO THE PARKING LOT WEST OF THE FRISCO BUILDING. THERE WERE ALSO DAMAGES TO BUILDINGS SURROUNDING THE FRISCO BUILDING.
2025-01-31 10:21 | YES | YES | 20030097 | 2003-08-15 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | S.H. 75 @ AFRICAN HILL RD | WILLIS | MONTGOMERY | TX | 7 7378 | 3 | NO | 2319 | 2003-07-18 | 0 | 1 | 0 | 0 | 0 | NO | 7 | 31 | 651274 | 20030719 | 125 | 160 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | D R S | BODY OF PIPE |  | STEEL |  | 1 | 0.113 | API5L | UKNOWN | 0 | 1976 | ABOVE GROUND |  | TAL R CENTERS | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | THIRD PARTY DAMAGED A 1" STEEL D. R. S. WITH A VEHICLE, DAMAGING INLET RISER AND ESCAPING GAS WAS IGNITED.
2025-01-31 10:21 | NO | NO | 20030098 | 2003-08-15 | 31459 | KEYSPAN ENERGY DELIVERY | 33 FRANKLIN STREET | SOMERVILLE | MIDDLESEX | MA | 02143 |  | Null | 219 | 2003-01-22 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 2 | 38 |  |  | 23 | 27 |  |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  |  |  | 0 | 1909 | UNDER PAVEMENT |  | THOMAS R TEEHAN | 7814665137 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | OUTSIDE PRESSURE FROM FROST CAUSED A CRACK IN GAS MAIN.
2025-01-31 10:21 | YES | YES | 20030099 | 2003-08-22 | 17360 | RICHMOND DEPT OF PUBLIC UTILITIES, CITY OF | 3600 GROVE AVENUE | RICHMOND |  | VA | 2 3221 | 4 | NO | 205 | 2003-08-06 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 0 | 653176 | 20030807 | 20 | 30 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL | [5 empty] | 0 | 1986 | ABOVE GROUND |  | ROBERT M HOWARD | 8046468301 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | Null | NO DATA |  | INDIVIDUAL WAS DRIVING A PICK-UP TRUCK THE WRONG WAY DOWN ONE-WAY STREETS (FLOYD & BERRINGTON) TRAVELING SEVERAL BLOCKS. HE CROSSED A FOUR LANE DIVIDED HIGHWAY, LEFT THE RIGHT-OF-WAY OF THE ROAD, WENT APPROXIMATELY 300 FT THROUGH THE YARD, AND STRUCK A TREE. THE VEHICLE RICOCHET OFF THE TREE AND STRUCK A BUILDING AND A GAS METER. THE IMPACT RUPTURED THE SERVICE RISER AND CAUSED A RELEASE OF GAS. THE GAS IGNITED. THE INDIVIDUAL WAS HOSPITALIZED.
2025-01-31 10:21 | NO | NO | 20030100 | 2003-08-19 | 15413 | PERRYVILLE MUNICIPAL SYSTEM, CITY OF | 708 S KINGSHIGHWAY | PERRYVILLE | PERRY | MO | 6 3775 | 3 | NO | 1650 | 2003-07-23 | 0 | 0 | 59117 | 37677.7879 | 90971.792 | YES | 0 | 0 |  | 20030723 | 300 | 300 | BY TEST | 450 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 6 | 0.188 |  |  | 0 | 0 | UNDER GROUND OR UNDER WATER |  | DEAN A PARK | 6362968600 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | YES | 0 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20030101 | 2003-08-26 | 15007 | PACIFIC GAS & ELECTRIC CO | 3020 PARKWOOD COURT | CARMICHAEL | SACRAMENTO | CA | 95608- | 1 | NO | 2320 | 2003-07-28 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 6 | 0 | 652267 | 20030729 | 45 | 50 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.11 | 3/4" STL RISER | UNKNOWN | 0 | 1970 | ABOVE GROUND |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A TREE BRANCH BROKE AND FELL, STRIKING AND DAMAGING THE GAS METER CREATING A LEAK. A STRUCTURE FIRE ALSO RESULTED FROM DAMAGE CAUSED BY THE FALLING BRANCH. THE SOURCE OF IGNITION OF THE FIRE IS UNKNOWN.
2025-01-31 10:21 | YES | YES | 20030102 | 2003-08-18 | 792 | ATLANTA GAS LIGHT CO | 870 N MAIN ST | ALPHARETTA | FULTON | GA | 3 0005 | 3 | NO | 1747 | 2003-08-06 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 25 | 653138 | 20030806 | 58 | 60 | BY TEST | 120 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1.25 | 0.125 | PE 2406 | DRISCOPLEX | 2003 | 2003 | UNDER GROUND OR UNDER WATER |  | JAMES BRAY | 7702053602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 2 |  | YES | NO DATA |  | PLUMBING CONTRACTOR WAS SWEATING A FITTING ON A 2" COPPER WATER SERVICE WITH A PROPANE TORCH IN A DITCH WITH THE 1 1/4" PLASTIC NATURAL GAS SERVICE EXPOSED. THE PLUMBER INADVERTENTLY BROUGHT THE TORCH TOO CLOSE TO THE NATURAL GAS SERVICE THUS MELTING AND BURNING A HOLE IN THE LINE CAUSING THE GAS TO IGNITE. PLUMBER EXPERIENCED 1ST AND 2ND DEGREE BURNS ON ARMS AND FACE.
2025-01-31 10:21 | YES | YES | 20030103 | 2003-08-27 | 6141 | PUBLIC SERVICE COMPANY OF NEW MEXICO - GAS SVCS | NM STATE HIGHWAY #256 & HOBSON RD | ROSWELL | CHAVES | NM | 8 8201 | 1 | NO | 730 | 2003-08-12 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 30 | 653688 | 20030812 | 324 | 348 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1 | 0.132 | UNKNOWN | UNKNOWN | 0 | 1993 | ABOVE GROUND |  | JON W JONES | 5052414571 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | DRIVER OF A SOUTHBOUND VEHICLE SWERVED TO MISS A DOG AND LOST CONTROL OF VEHICLE. VEHICLE LEFT ROAD AND HIT A SINGLE LOOP GAS METER.
2025-01-31 10:21 | NO | NO | 20030104 | 2003-08-25 | 31840 | UNISOURCE ENERGY SERVICES | 2005 MOYA DRIVE | LAKE HAVASU | MOHAVE | AZ | 8 6406 | 3 | NO | 850 | 2003-08-13 | 0 | 0 | 1500 | 956.014 | 2308.2648 | YES | 1 | 30 | 653819 | 20030813 | 48 | 52 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | PVC | 0.5 | 0.062 | SCH DM 168 PSI | CABOT PIPING SYSTEM | 1965 | 1966 | UNDER GROUND OR UNDER WATER |  | JACK SCHOONMAKER | 9284500595 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | PLUMBER PROPANE WELDING IN BOTTOM OF BELL HOLE WITH NATURAL GAS SERVICE LINE LOCATED ABOVE. HEAT FROM PROPANE WELDING BURNED HOLE IN PVC SERVICE LINE RESULTING IN NATURAL GAS IGNITION AND FLASH BURN TO PLUMBER. PLUMBER WAS TREATED AND RELEASED FROM LOCAL HOSPITAL (FIRST-AID INJURY). SERVICELINE WAS SHUT OFF AND REPAIRED GAS RESTORED TO CUSTOMER ON 8/13/03.
2025-01-31 10:21 | NO | NO | 20030105 | 2003-09-03 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 157 SHAFFER DRIVE | SEWICKLEY | ALLEGHENY | PA | 1 5143 | 3 | NO | 1008 | 2003-07-31 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 51 | 652516 | 20030731 | 16 | 40 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | JOINT |  | STEEL |  | 2 | 0.188 |  |  | 0 | 1958 | UNDER GROUND OR UNDER WATER |  | RAY M GEESEY | 7177670250 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2003-07-15 | YES | NO DATA |  | THIRD PARTY CONTRACTOR, KUKURIN CONSTRUCTION, WHILE WORKING ON INSTALLING SEWER LINE, SEVERED AND PULLED THE 1 1/4" STEEL NATURAL GAS SERVICE LINE TO 156 SHAFFER DRIVE, WHICH IN TURN PULLED THE SERVICE LINE COUPLING AT THE METER APART, AND WHICH ALSO PULLED THE COUPLING AT THE MAIN APART, WHICH IS LOCATED IN THE STREET. THE DISTANCE FROM THE COUPLING AT THE MAIN TO THE HOUSE AT 157 SHAFFER DRIVE IS APROX. 18 FEET.
2025-01-31 10:21 | YES | NO | 20030106 | 2003-09-10 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 1400 US HWY 70 | HILLSBOROUGH | ORANGE | NC | 2 7278 | 3 | NO | 1816 | 2003-08-11 | 0 | 0 | 116000 | 73931.7522 | 178505.8083 | NO | 0 | 23 | 653621 | 20030811 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | SERVICE RISER BELOW SHUT-OFF | STEEL |  |  |  | N/A | EQUIMETER | 0 | 1986 | ABOVE GROUND |  | MARTIN E WOLFE | 9195987406 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | THE METER WAS DAMAGED WHEN AN UNOCCUPIED VEHICLE ROLLED INTO THE METER SET BREAKING THE SERVICE BELOW THE SERVICE SHUT-OFF. THE ESCAPING GAS WAS IGNITED CAUSING THE VEHICLE TO BURN AND IGNITING THE SIDE OF THE BUILDING. THE VEHICLE WAS A TOTAL LOSS AND DAMAGE TO THE SIDE OF THE BUILDING WAS EXTENSIVE.
2025-01-31 10:21 | YES | YES | 20030107 | 2003-09-12 | 4483 | ENSTAR NATURAL GAS CO | DENALI STREET & BENSON ROAD | ANCHORAGE |  | AK | 9 9519 | 3 | NO | 1250 | 2003-09-02 | 0 | 1 | 50000 | 31867.1346 | 76942.1588 | YES | 1 | 10 | 655753 | 20030902 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | DRISCOPIPE | 1976 | 1976 | UNDER GROUND OR UNDER WATER |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | ON TUESDAY AFTERNOON, SEPTEMBER 2, 2003 AT APPROXIMATELY 12:50 PM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED BY THE ANCHORAGE FIRE DEPARTMENT (AFD) OF A GAS MAIN BREAK AND FIRE AT THE CORNER OF DENALI STREET AND BENSON BLVD IN ANCHORAGE, ALASKA. SERVICE TECHNICIANS AND EMERGENCY CREWS WERE IMMEDIATELY DISPATCHED TO THE SCENE. UPON ARRIVAL ENSTAR PERSONNEL FOUND A DAMAGED 2" HDPE, 60 PSIG MAOP, GAS MAIN DAMAGED AND ON FIRE. THE MAIN WAS FED FROM TWO DIRECTIONS. ENSTAR PROCEEDED TO SIMULTANEOUSLY DIG UP THE GAS MAIN ON EITHER SIDE OF THE DAMAGE. ONE SIDE OF THE DAMAGE WAS PINCHED OFF AT 1:55 PM ADT AND THE OTHER SIDE WAS PINCHED OFF AT 2:00 PM ADT. ONE PERSON, SASHA CLAPPER, AN EMPLOYEE OF QUALITY ASPHALT AND PAVING, WAS BURNED OVER APPROXIMATELY 25% OF HIS CHEST AND ARMS. HE WAS TREATED AT PROVIDENCE ALASKA MEDICAL. WORKERS FOR QUALITY ASPHALT AND PAVING WERE USING A PROPANE WEED BURNER TORCH TO ATTACH A SHRINK SLEEVE OVER A JOINT IN A 10" STORM DRAIN. ENSTARS 2" HDPE GAS MAIN WAS EXPOSED IN THE EXCAVATION, APPROXIMATELY 12 INCHES FROM WHERE THE SHRINK SLEEVE WAS BEING APPLIED. IT IS BELIEVED HEAT FROM THE TORCH ACCIDENTLY MELTED THE 2" HDPE GAS MAIN AND IGNITED THE NATURAL GAS THAT WAS RELEASED.
2025-01-31 10:21 | NO | NO | 20030108 | 2003-07-18 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | LINCOLN & WESTERN | CHEBOYGAN | CHEBOYGAN | MI |  | 3 | NO | 1427 | 2003-05-14 | 0 | 0 | 69000 | 43976.6457 | 106180.1791 | NO | 19 | 23 | 651108 | 20030717 | 150 |  |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 6 |  |  |  | 0 | 0 | UNDER PAVEMENT |  | JOSEPH A DIDIA | 3132356921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES | NO DATA |  | CONTRACTOR STRUCK AND RUPTURED 6" STEEL NATURAL GAS MAIN # 150 PSIG.
2025-01-31 10:21 | NO | NO | 20030109 | 2003-09-17 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 432 ROYCEFIELD ROAD | HILLSBOROUGH | SOMERSET | NJ | 8844 | 3 | NO | 1410 | 2003-08-04 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 4 | 10 | 652912 | 20030804 | 20 | 60 | BY CFR 192.619(A)(3) |  | NO DATA | ALL OTHER CAUSES | UNSPECIFIED NATURAL OR OUTSIDE FORCE DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 0.75 | 0.154 |  | X-TRU | 0 | 1969 | WITHIN/UNDER BUILDING |  | WILLARD S CAREY | 9734307833 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON MONDAY, AUGUST 4, 2003, AT APPROXIMATELY 2:10 PM THE COMPANY RECEIVED A CALL FROM THE HILLSBOROUGH POLICE DEPARTMENT REPORTING A WORKING STRUCTURE FIRE AT 432 ROYCEFIELD ROAD, AND DOWNED POWER LINES BETWEEN 173 AND 175 VALLEY ROAD, HILLSBOROUGH, NJ. A SERVICE TECHNICIAN WAS IMMEDIATELY DISPATCHED, ARRIVED AT THE SCENE AT 2:32 PM, AND FOUND A GAS FED FIRE AT 432 ROYCEFIELD ROAD, HILLSBOROUGH AND UNCONTROLLED GAS IN THE BASEMENT OF 178 VALLEY ROAD, HILLSBOROUGH. THE 3/4 INCH GAS SERVICE TO 178 VALLEY ROAD, HILLSBOROUGH WAS SHUT OFF AT 3:50 PM. INVESTIGATION FOUND THAT THE 3/4 INCH INSULATOR WAS "CHARRED". THE INSULATOR WAS REPLACED, THE SERVICE WAS PRESSURE TESTED AT 90 PSIG, AND SERVICE WAS RESTORED TO THE CUSTOMER. AN EXCAVATION WAS MADE OVER THE MAIN CONNECTION FOR THE 3/4 INCH SERVICE THAT SUPPLIES 432 ROYCEFIELD ROAD. INVESTIGATION FOUND THAT THE GASKET OF A DRESSER COMPRESSION COUPLING WAS BURNED. PRELIMINARY INVESTIGATION INDICATES THAT A LIGHTNING STRIKE OCCURRED CAUSING THE "B" PHASE, CONDUCTOR SIZE 397, OF A 13 KV SPACER CABLE DISTRIBUTION CIRCUIT TO FALL TO THE GROUND. IT IS FELT THAT THIS CONDUCTOR OR THE DISCHARGE OF THE LIGHTNING THROUGH THE GROUNDING SYSTEM CAUSED THE DAMAGE TO THE ABOVE MENTIONED INSULATOR AND COMPRESSION COUPLING. BESIDES THE FIRE DAMAGE TO 432 ROYCEFIELD ROAD, A LOCAL CREEK ALSO OVERFLOWED DUE TO THE HEAVY RAINSTORMS CAUSING SEVERE WATER DAMAGE TO THE BASEMENT. SINCE THE INITIAL EVALUATION OF THE DAMAGE TO THIS STRUCTURE APPEARS TO EXCEED $50,000 THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED. (OPS REPORT NUMBER 652912)
2025-01-31 10:21 | YES | NO | 20030110 | 2003-09-23 | 20010 | U G I CORP | SCHOENECK ROAD | MACUNGIE |  | PA | 1 8062 | 2 | NO | 747 | 2003-08-23 | 0 | 0 | 135000 | 86041.2633 | 207743.8287 | NO | 3 | 33 | 654808 | 20030823 | 279 | 729 | BY TEST | 1220 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.219 | ERW | US STEEL | 1986 | 1986 | UNDER GROUND OR UNDER WATER |  | JAMES R HEINTZ | 6107963528 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES | NO DATA |  | PRIOR TO THE INCIDENT, UGI ATTENDED 4 SITE MEETINGS (JUNE 4TH, JULY 11TH, JULY 24TH, AND AUGUST 12TH 2003), ALL OF WHICH WERE ATTENDED BY A REPRESENTATIVE OF THE BUILDER (JAINDL) AND TWO OF WHICH WERE ATTENDED BY A REPRESENTATIVE OF THE EXCAVATOR (LIVENGOOD). THE ATTENDING PARTIES WERE MADE AWARE OF THE HIGH PRESSURE MAIN IN THE AREA. UGI MARKED THE LINE ON JULY 28, 2003 DUE TO PA ONE-CALL TICKET #2056320. THERE WERE NO SUBSEQUENT REQUESTS FOR LOCATES AFTER THAT TIME. ON AUGUST 23RD AT 7:47 A.M., UGI GAS CONTROL NOTICE LOW PRESSURE ALARMS ON THE BALLY LINE. AT 8:08 IT WAS CONFIRMED THAT THERE WAS A HIT CALLED IN BY THE CONTRACTOR. BY 8:30 UGI ARRIVE ON SCENE AND FOUND THAT THE 12" STEEL HIGH PRESSURE MAIN HAD BEEN HIT BY AN EARTH MOVER, WHICH WAS STILL PARKED OVER THE DAMAGED LINE. AT 11:20 ALL NECESSARY VALVES WERE SHUT OFF AND THE EMERGENCY WAS UNDER CONTROL. THE DAMAGED SECTION WAS REMOVED AND REPLACED.
2025-01-31 10:21 | YES | NO | 20030111 | 2003-09-15 | 31348 | TXU GAS DISTRIBUTION | 104 GOLDENRAIN TREET | EULESS | TARRANT | TX | 76039- | 3 | NO | 1535 | 2003-08-01 | 0 | 0 | 103000 | 65646.2972 | 158500.847 | YES | 0 | 20 | 652672 | 20030801 | 22 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  |  |  | PE 2406 | DRISCOPLEX | 2003 | 2003 | UNDER GROUND OR UNDER WATER |  | ELLEN WEAVER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | YES |  | YES | 3 |  | YES | NO DATA |  | A NON-ONCOR CONTRACTOR INSTALLING A SPRINKLER SYSTEM CUT A SERVICE LINE. THE ESCAPING GAS IGNITED. THE TRENCHER WAS DESTROYED IN THE FIRE AND A HOUSE WAS DAMAGED,
2025-01-31 10:21 | YES | YES | 20030112 | 2003-09-15 | 4473 | ENERGAS CO | 2803 MARIANA | MIDLAND | MIDLAND | TX | 79701- | 3 | NO | 607 | 2003-08-06 | 1 | 0 | 0 | 0 | 0 | NO | 0 | 43 |  | 20030806 | 15 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | COPPER TUBING | OTHER | COOPER TUBING (HOUSE LINE) |  |  |  |  | 0 | 0 | OTHER | WATER HEATER CLOSET | SAM JONES | 8067984466 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CUSTOMERS COPPER TUBING TO THE WATER HEATER WAS CUT, RELEASING GAS INTO THE RESIDENCE. THE RELEASED GAS IGNITED RESULTING IN A EXPLOSION.
2025-01-31 10:21 | NO | NO | 20030113 | 2003-09-15 | 4473 | ENERGAS CO | 2606 37TH STREET | LUBBOCK | LUBBOCK | TX | 7 9413 | 3 | NO | 2345 | 2003-08-11 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 30 |  | 20030811 | 0.375 | 0.9 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | OTHER | COPPER TUBING | OTHER | COPPER TUBING (HOUSE FIRE) |  |  |  |  | 0 | 0 | OTHER | UNDER FLOOR | CHARLES S JONES | 8067984466 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | COPPER GAS LINE SOLDER JOINT BROKE ALLOWING GAS TO ESCAPE UNDER AND INTO THE HOUSE. ACCUMLATED GAS IGNITED CAUSING AN EXPLOSION AND SUBSEQUENT FIRE.
2025-01-31 10:21 | YES | NO | 20030114 | 2003-09-25 | 13710 | NORTHERN ILLINOIS GAS CO | 347-49 PATRIOT DRIVE | HAINESVILLE | LAKE | IL | 6 0030 | 3 | NO | 1756 | 2003-08-28 | 0 | 0 | 800000 | 509874.153 | 1231074.5402 | NO | 2 | 15 | 655360 | 20030828 | 60 | 60 | BY TEST | 94 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | OTHER | FIRE MELTED METER SETS | STEEL | [5 empty] | 0 | 2002 | ABOVE GROUND |  | LETICIA QUEZADA | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | FIRE DAMAGED 2 METER SETS. NATURAL GAS IGNITED. UNITS WERE MODELS FOR NEW SUBDIVISION. CAUSE OF FIRE UNKNOWN.
2025-01-31 10:21 | YES | YES | 20030115 | 2003-10-14 | 13710 | NORTHERN ILLINOIS GAS CO | 1583 SOMERFIELD DRIVE | BOLINGBROOK | WILL | IL | 60490- | 3 | NO | 339 | 2003-09-13 | 1 | 0 | 0 | 0 | 0 | NO | 3 | 5 |  | 20030913 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | RISER ON METER | STEEL | [5 empty] | 0 | 0 | ABOVE GROUND |  | LETICIA QUEZADA | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | Null | NO DATA |  | DRIVER LOST CONTROL OF VEHICLE STRIKING A HOUSE AND THE METER SET. THE METER SET WAS DAMAGED. NATURAL GAS WAS RELEASED BUT THERE WAS NO IGNITION. FATALITY RESULTED FROM THE IMPACT OF THE VEHICLE ACCIDENT AND WAS NOT RELATED TO THE RELEASE OF THE NATURAL GAS.
2025-01-31 10:21 | YES | NO | 20030116 | 2003-10-14 | 6920 | GULF STATES UTILITIES CO | 196 S 14TH | BATON ROUGE | EAST BATON ROUGE | LA | 70802 | 3 | NO | 640 | 2003-09-13 | 0 | 0 | 150000 | 95601.4037 | 230826.4763 | NO | 2 | 45 | 656753 | 20030913 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 1 | 0.094 | N/A | N/A | 0 | 0 | ABOVE GROUND |  | TOMMY J SMITH | 2253543102 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | NO | NO DATA |  | PUBLIC STRUCK METER SET WITH VEHICLE (FLED SCENE)
2025-01-31 10:21 | YES | YES | 20030117 | 2003-10-13 | 12642 | MOBILE GAS SERVICE CORP | COACH W HAROLD CLARK DRIVE | PRICHARD | MOBILE | AL | 3 6610 | 3 | NO | 1000 | 2003-10-06 | 0 | 1 | 2000 | 1274.6854 | 3077.6864 | NO | 1 | 14 |  | 20031008 | 40 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 2 | 0.37 | UNKNOWN | UNKNOWN | 0 | 1953 | NO DATA |  | PETER A KEEGAN | 2514504759 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA
2025-01-31 10:21 | YES | NO | 20030118 | 2003-10-14 | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | RIVER ROAD NEAR BRIDGE AVENUE | CHATMAN | MORRIS | NJ | 07928- | 3 | NO | 1248 | 2003-09-15 | 0 | 0 | 95000 | 60547.5557 | 146190.1016 | NO | 6 | 37 | 656941 | 20030915 | 9 | 15 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 6 | 0.188 |  |  | 0 | 1973 | UNDER PAVEMENT |  | WILLIARD S CAREY | 9734307833 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-08-08 | YES | 0 |  | YES | NO DATA |  | ON MONDAY, SEPTEMBER 15, 2003, AT APPROXIMATELY 2:48 PM THE COMPANY RECEIVED A CALL FROM THE CHATHAM FIRE DEPARTMENT REPORTING A DAMAGED GAS MAIN AT RIVER ROAD NEAR BRIDGE AVENUE, CHATHAM, NJ. A DISTRIBUTION SUPERVISOR WAS IMMEDIATELY DISPATCHED, ARRIVED AT THE SCENE AT 1:15 PM, AND FOUND THAT INTER COUNTY PAVING WAS RECONSTRUCTING THE ROADWAY AND IN THE PROCESS OF DOING SO, DAMAGED A WATER MAIN. WHILE EXCAVATING TO ADDRESS THE BROKEN WATER MAIN THEY STRUCK THE 6 INCH, 15 PSIG, STEEL GAS MAIN WITH THEIR TRACK HOE AND PUNCTURED THE MAIN WITH A TOOTH OF THE BUCKET. FOLLOWING THE DAMAGE THE ESCAPING GAS IGNITED, AND BURNED THE OVERHEAD ELECTRIC, TELEPHONE AND CABLE WIRES AND EXTENSIVELY DAMAGED THE TRACK HOE. POLICE AND FIRE RESPONDERS CLOSED THE ROAD DURING THE INCIDENT. INITIAL INVESTIGATION INDICATES THAT A PUMP NEAR THE EXCAVATION THAT WAS USED TO DEWATER THE WORK SITE IS THE PROBABLE SOURCE OF IGNITION. SINCE THE INITIAL DOLLAR VALUE OF ALL DAMAGES CAUSED BY THIS INCIDENT APPEARS TO EXCEED $50,000, THE OFFICE OF PIPELINE SAFETY WAS NOTIFIED. (OPS REPORT NUMBER 656941) A BY-PASS WAS INSTALLED AROUND THE DAMAGE SECTION OF MAIN AND THE FIRE WAS EXTINGUISHED BY 9:25 PM ALLOWING THE REMOVAL OF THE TRACK HOE AND THE INITIATION OF REPAIRS. REPAIRS WERE COMPLETED AT 4:30 AM.
2025-01-31 10:21 | YES | NO | 20030119 | 2003-10-16 | 1088 | BALTIMORE GAS & ELECTRIC CO | 3100 FOUR SEASONS CT | BALTIMORE |  | MD | 2 1222 | 3 | NO | 2212 | 2003-09-26 | 0 | 0 | 250000 | 159335.6728 | 384710.7938 | NO | 2 | 15 | 701069 | 20030929 | 8 | 10 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | STEVEN J TROCH | 4102914540 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20030120 | 2003-10-22 | 13710 | NORTHERN ILLINOIS GAS CO | 1573-75 TAHOE CIRCLE | WHEELING | COOK | IL | 60090- | 3 | NO | 610 | 2003-09-24 | 0 | 0 | 500000 | 318671.3456 | 769421.5876 | NO | 2 | 45 | 700664 | 20030924 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL | [5 empty] | 0 | 1997 | ABOVE GROUND |  | LETICIA QUEZADA | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | NO |  | NO | 0 |  | YES | NO DATA |  | FIRE DAMAGED TWO METER SETS. NATURAL GAS IGNITED. COMPANY INVESTIGATION INDICATES INCIDENT RESULTED FROM A BROKEN BELOW GROUND CUSTOMER OWNED FUEL LINE FEEDING A GAS GRILL. SOURCE OF IGNITION IS UNKNOWN.
2025-01-31 10:21 | YES | NO | 20030121 | 2003-10-20 | 4483 | ENSTAR NATURAL GAS CO | LOT 9 BLK 5 MOOSE RANGE MEADOWS (KEYSTON | SOLDOTNA |  | AK | 99669- | 3 | NO | 130 | 2003-10-11 | 0 | 0 | 150000 | 95601.4037 | 230826.4763 | NO | 1 | 25 | 702212 | 20031011 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 |  | DRISCOPLEX HDPE | 2002 | 2002 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON SATURDAY MORNING, OCTOBER 11, 2003 AT APPROXIMATELY 1:30 AM ADT, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 9, BLOCK 5 MOOSE RANGE MEADOW, ON KEYSTONE DRIVE NEAR SOLDOTNA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. WITH THE HELP OF FIRE FIGHTERS, THE SERVICE TECHNICIAN HAND DUG THE SERVICE LINE, PINCHED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20030122 | 2003-10-29 | 22182 | WASHINGTON GAS LIGHT CO | 901 23RD STREET | WASHINGTON |  | DC | 20037- |  | Null | 1034 | 2003-10-07 | 0 | 1 | 10000 | 6373.4269 | 15388.4318 | NO | 0 | 42 | 701763 | 20031007 | 20 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | STEEL |  | 3 | 0.193 | ASTM 83 GRADE B | UNKNOWN | 0 | 1982 | UNDER PAVEMENT |  | THOMAS FRYER | 7037505849 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A DEMOLITION CONTRACTOR WAS EXCAVATING AT 901 23RD STREET NW AND STRUCK A THREE INCH GAS PIPELINE CAUSING A LEAK. A VEHICLE DRIVING NORTH ON 23RD STREET BROKE DOWN (STALLED ENGINE) IN THE VICINITY OF THE GAS LEAK. SEVERAL PEOPLE, INCLUDING THE PERSONNEL, WERE ON THE SCENE AT THIS POINT AND REPEATEDLY WARNED THE MOTORIST NOT TO START THE VEHICLE FOR FEAR OF CREATING AN IGNITION SOURCE FOR THE GAS LEAK. THE MOTORIST APPARENTLY DISREGARDED THE WARNINGS AND ATTEMPTED TO START THE VEHICLE. A FIRE ENSUED AND ENGULFED THE CAR CAUSING BURN INJURIES TO THE HANDS AND FACE OF THE MOTORIST.
2025-01-31 10:21 | NO | NO | 20030123 | 2003-10-27 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 2431 E 4TH STREET | SKIDWAY LAKE | OGEMAW | MI | 48756- | 4 | NO | 1039 | 2003-10-18 | 0 | 0 | 65000 | 41427.2749 | 100024.8064 | NO | 0 | 0 | 702904 |  | 60 | 60 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 0.625 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LARRY K CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CUSTOMER EXCAVATING STRUCK AND RUPTURED NATURAL GAS SERVICE LINE. THERE WAS A RELEASE AND IGNITION OF NATURAL GAS WITH FIRE RESULTING. MISS DIG WAS NOT CALLED.
2025-01-31 10:21 | NO | NO | 20030124 | 2003-11-06 | 18532 | TEXAS GAS SERVICE COMPANY | 5700 BLOCK OF AVENUE (PO OFFICE STREET) | GALVESTON | GALVESTON | TX | 7 7550 | 3 | NO | 1158 | 2003-10-22 | 0 | 0 | 55009 | 35059.5841 | 84650.2242 | NO | 12 | 2 | 703322 | 20031022 | 83 | 125 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | FITTING |  | STEEL |  | 14 | 0.25 | API 5L X42 | UNKNOWN | 0 | 1928 | UNDER GROUND OR UNDER WATER |  | ROBERT FEARRINGTON | 5124651103 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 1 |  | YES | NO DATA |  | A SUB-CONTRACTOR WORKING FOR HARRIS CONSTRUCTION WAS EXCAVATING PARALLEL TO AN EXISTING 14-INCH MAIN AS PART OF A MAIN REPLACEMENT PROJECT WHEN THE WALL OF THE TRENCH SHIFTED RESULTING IN THE MOVEMENT OF THE EXISTING MAIN. A DRESSER FITTING LOCATED ON THE EXISTING MAIN CAME LOOSE CAUSING NATURAL GAS TO ESCAPE. THE NATURAL GAS WAS IGNITED BY OVERHEAD HIGH VOLTAGE POWER LINES. WHILE THIS INCIDENT WAS INITALLY REPORTED TO INVOLVE CORROSION, THE INVESTIGATION REVEALED THE FAILURE OF A DRESSER FITTING CAUSED BY THE MOVEMENT OF THE MAIN IS THE CAUSE OF THE INCIDENT. NO CORROSION WAS FOUND. THIS INCIDENT WAS INACCURATELY COVERED BY THE NEWS MEDIA. APPROXIMATELY 140 CUSTOMERS TEMPORARILY LOST NATURAL GAS SERVICE.
2025-01-31 10:21 | YES | YES | 20030125 | 2003-11-04 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 565 HUDSON ST | WYANDOTTE | WAYNE | MI | 4 8192 | 3 | NO | 1325 | 2003-10-23 | 0 | 1 | 150000 | 95601.4037 | 230826.4763 | YES | 0 | 0 | 703451 | 20031023 | 2 | 2 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | JOSEPH A DIDIA | 3132356921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | CAUSE OF EXPLOSION UNKNOWN. STILL UNDER INVESTIGATION. SCENE SPOILED DUE TO FIRE DEPARTMENT ORDERED DOZER WITH FRONT-END LOADER TO KNOCK DOWN REMAINING WALLS.
2025-01-31 10:21 | YES | NO | 20030127 | 2003-11-20 | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 20 HIGHLAND AVENUE | CORNWALL | ORANGE | NY | 1 2518 | 3 | NO | 1459 | 2003-10-22 | 0 | 0 | 300000 | 191202.8074 | 461652.9526 | NO | 1 | 16 |  | 20031022 | 30 | 30 | BY TEST | 45 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | NO DATA |  | STEEL |  | 0.75 | 0.154 |  |  | 1931 | 1931 | WITHIN/UNDER BUILDING |  | DAVID W MERTE | 8454865521 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-07-11 | YES | 3 | MAIN AND SERVICE PAINTED | YES | NO DATA |  | ARGENIO BROTHERS, A NEWBURGH, NY CONTRACTOR WORKING FOR THE TOWN OF CORNWALL NEAR THE CURB LINE ON FIRTH STREET, STRUCK 3/4" GALVANIZED STEEL NATURAL GAS SERVICE PIPE FEEDING 20 HIGHLAND AVENUE. THE 30 PSIG MAOP SERVICE LINE WAS PULLED THROUGH THE BASEMENT WALL CAUSING SEPARATION AT A THREADED VALVE INSIDE THE BASEMENT OF THE RESIDENCE. THE SUBSEQUENT IGNITION AND STRUCTURE FIRE DESTROYED THE BUILDING AND ITS CONTENTS.
2025-01-31 10:21 | YES | NO | 20030128 | 2003-11-05 | 4483 | ENSTAR NATURAL GAS CO | LUCKY SHOT LANE | WASILLA |  | AK | 99654 | 3 | NO | 838 | 2003-10-30 | 0 | 0 | 150000 | 95601.4037 | 230826.4763 | NO | 1 | 41 | 704018 | 20031030 | 55 | 60 |  |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | DRISCOPIPE |  | 1995 | 1995 | ABOVE GROUND |  | DAVID W BREDIN | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON THURSDAY MORNING, OCTOBER 30, 2003 AT APPROXIMATELY 8:38 AM AST, ENSTAR NATURAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT LOT 3, BLOCK 1 GOLD RUSH ESTATES, ON LUCKY SHOT LANE NEAR WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STRUCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION CREW DUG UP THE SERVICE LINE, PINCHED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | NO | NO | 20030130 | 2003-11-24 | 22182 | WASHINGTON GAS LIGHT CO | 1615 CONSTITUTION AVE NE | WASHINGTON |  | DC |  |  | NO | 0 | 2001-08-30 | 0 | 0 | 51000 | 33648.6283 | 81243.5175 | NO | 8 | 30 | [6 empty] | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 |  | UNKNOWN | UNKNOWN | 0 | 1930 | UNDER PAVEMENT |  | ROMELIA KEMP | 7037505564 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | CAPITAL PAVING COMPANY PLOWED OVER APPROXIMATELY 150 FEET OF 4-INCH CAST IRON MAIN WITH A HOE RAM WHILE IN THE PROCESS OF BREAKING CONCRETE FOR A CURB AND GUTTER REPLACEMENT. THERE WAS NO MISS UTILITY TICKET NOR WERE THERE ANY MARKS INDICATING THE LOCATION OF THE GAS LINE. THIS INCIDENT WAS IDENTIFIED AS AN ODOR OF GAS TO OUR DISPATCH OPERATIONS CENTER. THERE WAS INITIAL RECOGNITION BY CAPITAL PAVING COMPANY THAT THEY STRUCK THE LINE.
2025-01-31 10:21 | YES | YES | 20030131 | 2003-11-26 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | FOREST GLENN BLVD & ASH GROVE LANE |  | TUSCALOOSA | AL | 3 5475 | 3 | NO | 1655 | 2003-11-19 | 0 | 1 | 4565 | 2909.4694 | 7024.8191 | NO | 5 | 40 | 705842 | 20031119 | 25 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 4 |  | PE 2406 | DRISCOPIPE | 1996 | 1996 | UNDER GROUND OR UNDER WATER |  | TOM JOHNSTONE | 2053262990 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-11-05 | YES | 0 |  | YES | NO DATA |  | C&M CONSTRUCTION, A CABLE TELEVISION CONTRACTOR, MAKING A DIRECTIONAL DRILL IN ASH GROVE LANE DRILLED INTO ALABAMA GAS 4" PLASTIC MAIN LOCATED IN FOREST GLENN BLVD. SUBSEQUENTLY, ALABAMA GAS WORK FORCES WERE DISPATCHED TO THE LEAK AREA. WHILE ALABAMA GAS WORK FORCES WERE MAKING TEMPORARY REPAIRS TO THE 4" PLASTIC MAIN, THE ESCAPING NATURAL GAS FOUND AN IGNITION SOURCE. ONE OF THE THREE ALABAMA GAS EMPLOYEES ON-SITE WAS SERIOUSLY BURNED ON THE HANDS AND BUTTOCK AREA REQUIRING AT LEAST ONE OVERNIGHT HOSPITAL STAY THE AREA WAS MADE SAFE AT 22:35 HRS AND SERVICE WAS BEING RESTORED TO THE 12 RESIDENTIAL CUSTOMERS, AS ACCESS PERMITTED. A PRELIMINARY TELEPHONE REPORT TO DOT WASHINGTON, DC WAS MADE AT 21:42 HRS ON 11/19/03; REPORT WAS NUMBERED 705842.
2025-01-31 10:21 | NO | NO | 20030132 | 2003-11-26 | 980 | VIRGINIA GAS DISTRIBUTION CO. | 318 WALNUT STREET | LEBANON | RUSSELL | VA | 2 4266 | 3 | NO | 1233 | 2003-11-19 | 0 | 0 | 0 | 0 | 0 | YES | 0 | 31 | 705906 | 20031120 | 58 | 100 | BY TEST | 150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 |  | PERMASERT | 0 | 1998 | UNDER GROUND OR UNDER WATER |  | STEVE BELLINI | 2768894001 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20030133 | 2003-11-26 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | BLACKHAWK ROAD | BEAVER FALLS | BEAVER | PA | 15010 | 3 | NO | 1130 | 2003-11-01 | 0 | 1 | 10000 | 6373.4269 | 15388.4318 | NO | 1 | 0 | 704188 | 20031101 | 1900 | 2400 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | GATE VALVE | VALVE |  | STEEL |  | 4 |  |  |  | 0 | 0 | ABOVE GROUND |  | RAY M GEESEY | 7177670250 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | MOLLY FITZGERALD WAS DRIVING AN ATV (PLATE #40309) ON COLUMBIA GAS PRIVATE PROPERTY, WITH TWO PASSENGERS LINDSAY GASPER & ABBY PERZA. THE ATV STRUCK AN ABOVE GROUND 4 INCH GATE VALVE THAT WAS STICKING OUT OF THE GROUND 3 FEET, CAUSING A LEAKAGE TO VALVE BELOW GRADE. ALL THE PASSENGERS WERE EJECTED FROM THE ATV, AND MOLLY SUSTAINED A BROKEN LEG AND THE PASSENGERS HAD MINOR INJURIES.
2025-01-31 10:21 | YES | YES | 20030134 | 2003-11-21 | 1088 | BALTIMORE GAS & ELECTRIC CO | 557 & 559 CHALCOT SQUARE | BALTIMORE |  | MD | 2 1221 | 3 | NO | 1728 | 2003-11-02 | 0 | 1 | 150000 | 95601.4037 | 230826.4763 | NO | 1 | 4 | 704238 | 20031102 | 6.5 | 10 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | CUSTOMER PIPING | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN A GARRISON | 4102915130 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | BALTIMORE CITY FIRE DEPARTMENT CALLED FOR ASSISTANCE WITH STRONG ODOR OF GAS AT 557 CHALCOT SQUARE AT 17:23. THEY CALLED BACK AT 17:30 TO REPORT AN EXPLOSION AT THE SAME ADDRESS WITH TWO FIREMEN TRAPPED IN THE RUBBLE. THE OPERATORS FIRST RESPONDER ARRIVED AT 17:41 AND SET OUT TO LOCATE THE CURB VALVE FOR THE SERVICE UNDER THE RUBBLE. GAS WAS OFF AT 18:27, FIREMEN WERE EXTRACTED. ONE RESIDENT SUSTAINED INJURIES REQUIRING HOSPITALIZAITON. POLICE AND FIRE DEPARTMENT ESTABLISHED A CRIME SCENE EXCLUSION AREA. FIRE INVESTIGATION BUREAU FOUND CUSTOMER GAS LINE TO DRYER DISCONNECTED. FLEXIBLE CONNECTOR AND PLIERS WERE RECOVERED FROM SCENE. (CONTD IN PART D - OTHER)
2025-01-31 10:21 | YES | YES | 20030135 | 2003-11-24 | 18536 | SOUTHWEST GAS CORP | 3002 E SHANGRI LA RD | PHOENIX | MARICOPA | AZ | 8 5028 | 3 | NO | 1547 | 2003-11-17 | 0 | 1 | 0 | 0 | 0 | NO | 0 | 53 | 705613 | 20031117 | 40 | 40 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | INCORRECT OPERATION | INCORRECT OPERATION | MAIN |  | JOINT |  | OTHER | ABS | 2 | 0.139 | ASTM D-2513 | UNKNOWN | 1960 | 1960 | OTHER | OPEN BELL HOLE | BERNIE GALLENBACK | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | ERROR IN OPERATING PROCEDURE APPLICATION |  | SEE PART D
2025-01-31 10:21 | NO | NO | 20030136 | 2003-11-25 | 18112 | SAN DIEGO GAS & ELECTRIC CO | 1753 GATEWAY DRIVE | SAN DIEGO | SAN DIEGO | CA |  | 3 | NO | 842 | 2003-11-09 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 13 | 704844 | 20031109 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | FITTING |  | NO DATA |  | 0.75 |  |  |  | 0 | 1953 | ABOVE GROUND |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | CUSTOMER BACKING VEHICLE FROM BACK YARD TO SIDE OF HOUSE STRUCK METER, CAUSING BLOWING GAS. GAS IGNITED, CAUSING FIRE THAT DAMAGED ATTACHED GARAGE. NO INJURIES.
2025-01-31 10:21 | NO | NO | 20030137 | 2003-12-02 | 13480 | NIAGARA MOHAWK POWER CORP | VLIET ST GRS 523 | COHOES | ALBANY | NY | 1 2047 | 3 | NO | 1012 | 2003-11-03 | 0 | 0 | 0 | 0 | 0 | YES | 44 | 0 | 704308 | 20031103 |  | 2 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | GAS REGULATING STATION | BODY OF PIPE |  | STEEL |  | 1 | 0.133 | APT - 5L | UNKNOWN | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | LAURIE T BROWN | 3154285859 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | NO | 0 |  | YES | NO DATA |  | ON 11/3/03 AT 10:12 AM, A THIRD PARTY DAMAGED A 1" CONTROL LINE IN FRONT OF THE VLIET ST. GRS #523 IN COHOES, NEW YORK. THE DAMAGE CAUSED THE STATION REGULATOR TO FAIL WIDE OPEN. AS A RESULT, THE LOW PRESSURE DISTRIBUTION SYSTEM IN COHOES WAS OVER PRESSURIZED FROM THE NORMAL 9" W.C. TO APPROXIMATELY 28" W.C. THE SYSTEM OVER PRESSURE PROTECTION PERFORMED AS DESIGNED IN THIS FAILURE SCENARIO. CUSTOMER PIPING AND APPLIANCE DESIGN WAS A CONCERN. THE COMPANY REDUCED PRESSURE TO 2-3" W.C. FOLLOWING THE EVENT AND ALL GAS SERVICES ON THE DISTRIBUTION SYSTEM WERE LOCKED OFF. THE SYSTEM WAS THEN REPRESSURIZED AND ALL GAS SERVICES WERE TURNED ON THE COMPANY CHECKING ALL SERVICES AND HOME APPLIANCES FOR SAFE OPERATION.
2025-01-31 10:21 | YES | YES | 20030138 | 2003-12-04 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 1273 ASHLAND | DETROIT | WAYNE | MI | 48213- | 3 | NO | 2100 | 2003-11-13 | 0 | 1 | 100000 | 63734.2691 | 153884.3175 | NO | 1 | 0 | 705293 | 20031113 | 2 |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | FUEL LINE | NO DATA |  | OTHER | COPPER | 0.375 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | LAWRENCE CROWDER | 3132359403 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | NO | 20030139 | 2003-12-11 | 22182 | WASHINGTON GAS LIGHT CO | 5715 COLON TERRACE | TEMPLE HILLS | PRINCE GEORGES | MD | 2 0748 | 3 | NO | 439 | 2003-11-12 | 0 | 0 | 400000 | 254937.0765 | 615537.2701 | NO | 0 | 58 | 705057 | 20031112 | 20 | 22 | BY TEST | 32 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 |  | UNKNOWN | UNKNOWN | 0 | 1964 | ABOVE GROUND |  | ROMELIA KEMP | 7037505564 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | UPON ARRIVAL AT THE ABOVE ADDRESS, THE FIRE WAS IN PROGRESS AND WASHINGTON GAS CUT THE GAS OFF AT THE STOPCOCK IN THE FRONT YARD. THE FIRE DEPARTMENT HAS NOT DETERMINED THE ORIGIN AND CAUSE OF THE FIRE. THE HOUSE ITSELF WAS CONSUMED BY THE FIRE AND THE ADJACENT HOUSE SUSTAINED SIGNIFICANT DAMAGE TO THE SIDE ROOFING, CARPORT AND A PARKED SUV. THE HOUSE HAD AN INSIDE METER AND IT WAS TOTALLY DESTROYED BY THE FIRE.
2025-01-31 10:21 | YES | NO | 20030140 | 2003-12-11 | 22182 | WASHINGTON GAS LIGHT CO | 920 HIGHLAND DRIVE | SILVER SPRING | MONTGOMERY | MD | 20910- | 3 | NO | 1749 | 2003-11-13 | 0 | 0 | 170000 | 108348.2575 | 261603.3398 | NO | 0 | 18 | 705288 | 20031113 | 20 | 22 | BY TEST | 32 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | OTHER | COPPER | 0.5 |  | UNKNOWN | UNKNOWN | 0 | 1965 | UNDER GROUND OR UNDER WATER |  | THOMAS FRYER | 7037505849 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | WASHINGTON GAS RECEIVED A CALL FROM THE MONTGOMERY COUNTY FIRE BOARD THAT AN ABOVE GROUND ELECTRIC LINE SPARKED A GAS LINE AND A FIRE WAS IN PROGRESS AT THIS ADDRESS. STRONG WINDS CAUSED THE ELECTRIC LINE TO SEPARATE FROM A POLE, DROP TO GROUND AND DISCHARGE ELECTRIC VOLTAGE THROUGH THE SOIL UNTIL IT PENETRATED THE 1/2 INCH COPPER SERVICE. THE LINE PENETRATED THE SOIL THROUGH THE VALVE BOX, BURNED A HOLE INTO THE 1/2 INCH SERVICE ON THE HOUSE SIDE AND A SECOND FIRE IMMEDIATELY ENSUED AT THE POINT OF GAS RELEASE.
2025-01-31 10:21 | NO | NO | 20030141 | 2003-12-09 | 30750 | MIDAMERICAN ENERGY COMPANY | 104 WEST 8TH ST LOT 350 | SERGEANT BLUFF | WOODBURY | IA | 5 0104 | 4 | NO | 1154 | 2003-10-16 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 0 | 51 |  | 20031016 | 40 | 40 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D 2513 PE 2406 | PLEXCO | 1998 | 1998 | ABOVE GROUND |  | ROGER N LORENZEN | 7122777678 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE HEAT FROM A FIRE CAUSED BY AN ELECTRICAL MALFUNCTION RESULTED IN THE PLASTIC PIPE IN THE SERVICES RISER TO MELT AND A SECONDARY GAS FIRE.
2025-01-31 10:21 | YES | NO | 20030142 | 2003-12-08 | 792 | ATLANTA GAS LIGHT CO | 5401 FAIRINGTON RD | DECATUR | DEKALB | GA | 30038- | 3 | NO | 1504 | 2003-11-13 | 0 | 0 | 875000 | 557674.8548 | 1346487.7783 | NO | 2 | 45 | 705253 | 20031113 | 245 | 300 | BY TEST | 620 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4.5 | 0.156 | API-5L-B | UNKNOWN | 0 | 1969 | UNDER GROUND OR UNDER WATER |  | DAVID HAWKES | 7706024110 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-10-30 | Null | 0 |  | YES | NO DATA |  | AN EXCAVATOR SEVERED A 4" HP STEEL NATURAL GAS MAIN WITH A GRADING PAN WHILE REMOVING EARTH FROM A HILL ON A COMMERICAL BUILDING SITE. THE ESCAPING GAS IGNITED DESTROYING THE GRADING PAN. ALSO, A SECOND GRADER MANUVERED OUT OF CONTROL DUE TO THE INCIDENT CAUSING DAMAGE TO A NEARBY VEHICLE. IN ADDITION, THE INCIDENT RESULTED IN THE LOSE OF GAS SERVICE TO 342 CUSTOMERS.
2025-01-31 10:21 | YES | NO | 20030143 | 2003-12-19 | 31358 | TECO PEOPLES GAS LP OPERATIONS | BONITA BEACH ROAD AND US 41 | BONITA SPRINGS | LEE | FL |  | 3 | NO | 1645 | 2003-11-20 | 0 | 0 | 500000 | 318671.3456 | 769421.5876 | NO | 17 | 0 | 705981 | 20031121 | 187 | 500 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 8 | 0.219 | API 5L X-52 |  | 0 | 2000 | UNDER GROUND OR UNDER WATER |  | TIMOTHY J KASPRZYK | 8132284831 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-10-23 | YES | 1 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20030144 | 2003-12-10 | 12350 | MINNEGASCO INC | INTERSECTION OF 43 AV NE & MACIVER | ST MICHAEL | WRIGHT | MN | 55376 | 3 | NO | 922 | 2003-11-13 | 0 | 0 | 52000 | 33141.8199 | 80019.8451 | NO | 1 | 35 | 705247 | 20031113 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 3 | 0.304 | ASTM D2513 PE 2406 | QUAIL PIPING PRODUCTS | 2003 | 2003 | UNDER GROUND OR UNDER WATER |  | JOHN M WILNAMAKI | 6123215257 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | YES |  | YES | 2 |  | YES | NO DATA
2025-01-31 10:21 | NO | NO | 20030145 | 2003-12-12 | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 400 BLOCK SOUTH BLOUNT STREET | RALEIGH | WAKE | NC | 2 7601 | 4 | NO | 1337 | 2003-11-20 | 0 | 0 | 0 | 0 | 0 | YES | 5 | 8 | 705924 | 20031120 | 0.25 | 0.25 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.45 | N/A | N/A | 0 | 1918 | UNDER PAVEMENT |  | JIMMY K JONES | 9198362419 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | PAINT | YES | NO DATA |  | PRIOR TO THE INCIDENT, A CONTRACTOR INSTALLING ELECTRICAL CONDUITS DISTRUBED THE COMPACTED SOIL AROUND A 6" CAST IRON GAS PIPE. THE INSTALLATION OF THE ELECTRICAL CONDUIT ALLOWED EXTERNAL STRESS FROM HEAVY STREET TRAFFIC TO BE TRANSMITTED TO THE CAST IRON PIPE RESULTING IN A 360 DEGREE FRACTURE.
2025-01-31 10:21 | YES | NO | 20030146 | 2003-12-11 | 15007 | PACIFIC GAS & ELECTRIC CO | 2425 WALNUT BLVD | WALNUT CREEK | CONTRA COSTA | CA |  | 3 | NO | 400 | 2003-11-11 | 0 | 0 | 750000 | 478007.0184 | 1154132.3814 | NO | 0 | 5 | 704965 | 20031111 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM AND RUBBER COMPONENTS | 0.75 |  | N/A | N/A | 0 | 0 | ABOVE GROUND |  | SHAN BHATTACHARYA, VICE PRESIDENT ENGINEERING | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THIS WAS AN ARSON FIRE AT THE WALNUT CREEK MIDDLE SCHOOL. THE FIRE STARTED IN THE DUMPSTER AND SPREAD TO THE BUILDING. THE HEAT FROM THE BURNING BUILDING MELTED SOME OF THE GAS FACILITIES, WHICH LED TO THE BLOWING GAS FLAME. THE OVERALL DAMAGE TO THE FACILITIES WAS ~$750,000. ALUMINUM EXTERNAL PARTS AND RUBBER AND PLASTIC COMPONENTS MELTED, WHICH LED TO THE GAS FIRE. THERE WAS EXTENSIVE NEWS MEDIA COVERAGE AND EXTENSIVE FIRE DAMAGE. IT IS ESTIMATED THAT ~$250,000 OF BUILDING DAMAGE CAN BE ATTRIBUTED TO THE GAS FIRE.
2025-01-31 10:21 | YES | NO | 20030147 | 2003-12-16 | 2652 | NSTAR GAS COMPANY | 533 SOUTH SECOND STREET | NEW BEDFORD | BRISTOL | MA | 02744- | 4 | NO | 745 | 2003-11-21 | 0 | 0 | 320000 | 203949.6612 | 492429.8161 | NO | 1 | 23 | 705992 | 20031121 |  |  | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | DARRELL W HOBART, DISTRIBUTION MANAGER | 7814418429 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON NOVEMBER 21, 2003 AT APPROXIMATELY 0745 HOURS NSTAR GAS RECEIVED NOTIFICATION FROM THE NEW BEDFORD FIRE DEPARTMENT OF AN EXPLOSION IN A HOUSE LOCATED AT 533 SOUTH SECOND STREET IN NEW BEDFORD. GAS DISTRIBUTION SERVICE AND SUPPLY CREWS WERE DISPATCHED IMMEDIATELY. UPON ARRIVING AT THE SITE THE CREWS DISCOVERED A THREE-STORY BUILDING ON FIRE THAT LATER COLLAPSED DUE TO FIRE DAMAGE. THE ORIGINAL STRUCTURAL DAMAGE TO THE BUILDING FROM THE EXPLOSION OCCURRED IN THE BACK LEFT HAND CORNER OF THE BUILDING BETWEEN THE FIRST AND SECOND FLOORS. THREE PERSONS EVACUATED THEMSELVES DUE TO THE EXPLOSION AND NO INJURIES WERE REPORTED. THE SECTION OF GAS MAIN IN FRONT OF THE BUILDING WAS SHUT DOWN AT 0919 HOURS. THE ORIGIN AND CAUSE OF THE EXPLOSION IS UNCLEAR AND IS CURRENTLY UNDER INVESTIGATION BY NSTAR, THE MASSACHUSETTS DEPARTMENT OF TELECOMMUNICATIONS AN ENERGY, AND THE STATE FIRE MARSHALLS OFFICE.
2025-01-31 10:21 | NO | NO | 20030148 | 2003-12-17 | 15329 | PEOPLES GAS LIGHT & COKE CO | 3151-57 W 26TH STREET | CHICAGO | COOK | IL | 6 0623 | 3 | NO | 932 | 2003-11-27 | 0 | 0 | 50000 | 31867.1346 | 76942.1588 | NO | 1 | 50 | 706492 | 20031127 | 22 | 25 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 1.5 | 0.145 | UNKNOWN | UNKNOWN | 1985 | 1985 | ABOVE GROUND |  | JOHN GOETZ, MANAGER DISTRIBUTION SOUTH | 7739624840 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | DRIVER OF STOLEN CAR HIT ABOVE GROUND METER SET INSTALLATION, RISER BROKE BELOW SHUT OFF.
2025-01-31 10:21 | YES | YES | 20030149 | 2003-11-18 | 18484 | SOUTHERN CALIFORNIA GAS CO | BUSHARD & HAZARD | GARDEN GROVE | ORANGE | CA |  | 3 | NO | 1230 | 2003-10-20 | 0 | 1 | 0 | 0 | 0 | NO | 2 | 16 | 703085 | 20031020 | 50 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 1 |  |  |  | 0 | 1961 | UNDER PAVEMENT |  | W J KOSKIE | 2132443283 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2003-09-10 | YES | 0 |  | YES | NO DATA |  | CONTRACTOR REMOVING PAVEMENT WITH HEAVY EQUIPMENT, STRUCK ABANDONED SERVICE FITTING ON TOP OF MAIN. ESCAPING GAS IGNITED. SEVERELY BURNING OPERATOR.
2025-01-31 10:21 | YES | NO | 20030150 | 2003-12-31 | 22182 | WASHINGTON GAS LIGHT CO | 5025 COLUMBIA PIKE | ARLINGTON |  | VA | 22204- | 3 | NO | 2345 | 2003-11-28 | 0 | 0 | 500000 | 318671.3456 | 769421.5876 | NO | 0 | 10 |  | 20031129 | 20 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 |  |  | UNKNOWN | 0 | 1957 | WITHIN/UNDER BUILDING |  | JERRY F KIDWELL | 7037507687 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | A FIRE BEGAN IN THE REAR STORAGE AREA OF THE BUSINESS AND SPREAD TO THE GAS METER, WHERE IT MELTED THE INDEX OFF, CAUSING GAS TO LEAK. THE REGULATOR GASKET MELTED, CAUSING THE REGULATOR TO FAIL AND THE RELIEF VALVE TO VENT OUTSIDE. THE LEAKING AND BLOWING GAS IGNITED, FURTHER CONTRIBUTING TO THE FIRE.
2025-01-31 10:21 | YES | YES | 20030151 | 2003-12-23 | 12876 | QUESTAR GAS COMPANY | 375 S 300 W | GARLAND | BOX ELDER | UT | 84312- | 3 | NO | 103 | 2003-11-29 | 0 | 2 | 102000 | 65008.9545 | 156962.0039 | NO | 3 | 0 | 706574 | 20031129 | 45 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA |  |  |  |  | REG:FISHER/METER:ROCKWELL | 1973 | 1973 | ABOVE GROUND |  | TROY D SORENSELI | 8013243152 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | QUESTAR PERSONNEL WERE NOTIFIED BY THE FIRE DEPARTMENT OF A RESIDENTIAL HOUSE FIRE IN PROGRESS. WHEN QUESTAR PERSONNEL ARRIVE ON SCENE THE FIRE HAD COMPLETELY INCINERATED THE METER AND HAD MELTED THE REGULATOR. THIS RESULTED IN A RELEASE OF NATURAL GAS. PERSONNEL FROM THE OFFICE OF THE STATE FIRE MARSHAL HAVE DETERMINED THAT THE RELEASE OF NATURAL GAS WAS INCIDENTAL DUE TO THE FIRE THAT HAD STARTED ELSEWHERE IN THE HOME.
2025-01-31 10:21 | YES | YES | 20030152 | 2003-12-31 | 1088 | BALTIMORE GAS & ELECTRIC CO | 7121 ROLLING BEND ROAD | BALTIMORE CITY |  | MD | 2 1244 | 3 | NO | 945 | 2003-12-08 | 0 | 1 | 300000 | 191202.8074 | 461652.9526 | NO | 1 | 22 | 707432 |  | 95 | 99 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM |  |  |  |  | 0 | 0 | OTHER | UTILITY ROOM | JOHN A GARRISON, GENERAL SUPERVISOR | 4102915130 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ODOR CALL RECEIVED FOR 7123 ROLLING BEND ROAD AT 8:28 AM. GAS MECHANIC WAS DISPATCHED AT 0830 AM AND ARRIVED 0853 TO FIND 7119, 7121, & 7123 INVOLVED IN MAJOR FIRE. METER CLOSETS IN ALL THREE BUILDINGS WERE DAMAGED AT THE TIME, BUT FIRE WAS BEGINNING TO REACH THE UPPER RIGHT CORNER OF 7121S METER CLOSET. FIRE ENGULFED 7121S METER CLOSET AND DESTROYED METERING EQUIPMENT, INCLUDING PRESSURE REGULATOR, WHICH CREATED RESTRICTED HP GAS FED FIRE. COULD NOT ACCESS VALVE DUE TO FIRE, GAS MAIN WAS PINCHED OFF ELIMINATING GAS FLOW TO FIRE. BAR HOLE TESTS WERE CONDUCTED IN FRONT AND REAR OF BUILDINGS WITH NO INDICATION OF NATURAL GAS MIGRATION.
2025-01-31 10:21 | YES | NO | 20030153 | 2003-12-26 | 15007 | PACIFIC GAS & ELECTRIC CO | GRACE ST AND PEARCE ST | HAYWARD | ALAMEDA | CA |  | 3 | NO | 1828 | 2003-11-26 | 0 | 0 | 90000 | 57360.8422 | 138495.8858 | NO | 0 | 5 | 706469 | 20031126 | 50 | 60 | BY TEST | 100 | ACCIDENTALLY CAUSED BY OPERATOR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | NO DATA |  | POLYETHYLENE PLASTIC |  | 1.025 | 0.166 | D2513 | DUPONT | 0 | 1973 | UNDER PAVEMENT |  | SHAN BHATTACHARYA | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OPERATOR ACTION |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | WHILE CREW WAS PERFORMING EMERGENCY EXCAVATION TO REPAIR GAS LEAK, DISTURBED SOIL RESULTED IN LEAK FROM SECOND, DEFECTIVELY FUSED FITTING ESCAPING GAS IGNITED. RESULTING FIRE DAMAGED BACKHOE.
2025-01-31 10:21 | YES | NO | 20040001 | 2004-01-06 | 15007 | PACIFIC GAS & ELECTRIC CO | 1740 YERBA BUENA RD | SAN JOSE | SANTA CLARA | CA | 9 5121 | 3 | NO | 1111 | 2003-12-11 | 0 | 0 | 130000 | 82854.5499 | 200049.6128 | YES | 1 | 24 | 708565 | 20031219 | 60 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.9 | D2513 | PHILLIPS DRISCO | 1975 | 1975 | UNDER PAVEMENT |  | SHAN BHATTACHARYA, VICE PRESIDENT | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2003-12-05 | YES | NO DATA |  | CONTRACTOR INSTALLING CABLE TELEVISION CONDUIT STRUCK A DISTRIBUTION SERVICE WITH A TRENCHER BECAUSE THE SERVICE WAS NOT MARKED ACCURATELY. GAS IGNITED AND TRENCHER EQUIPMENT WAS DESTROYED BY FIRE.
2025-01-31 10:21 | YES | YES | 20040002 | 2004-01-13 | 15462 | PECO ENERGY CO | 311 SPEAKER PL | TRAPPE | MONTGOMERY | PA | 1 9462 | 3 | NO | 1430 | 2003-12-17 | 2 | 0 | 0 | 0 | 0 | NO | 3 | 10 | 708391 | 20031217 | 16 | 99 | BY TEST | 150 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 0.5 | 0.09 | ASTM D-2513 | PLEXCO | 0 | 1997 | ABOVE GROUND |  | MICHAEL A WILLIAMS, SHIFT MANAGER | 6109411599 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA
2025-01-31 10:21 | YES | YES | 20040003 | 2004-01-16 | 11032 | LACLEDE GAS CO | 6 HAGERS MILL CT | MANCHESTER | ST LOUIS | MO | 6 3021 | 3 | NO | 622 | 2003-12-11 | 0 | 2 | 285000 | 181642.667 | 438570.3049 | NO | 2 | 38 | 707753 | 20031211 | 37 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | JOINT |  | POLYETHYLENE PLASTIC |  | 0.625 | 0.09 | ASTM D2513 | CONTINENTAL | 0 | 1974 | UNDER GROUND OR UNDER WATER |  | MARK D LAUBER, SUPERINTENDENT OF MAINTENANCE ENG | 3146585413 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER |  | Null |  | Null | 0 |  | Null | NO DATA |  | AN ASH TREE WAS PLANTED OVER THE NATURAL GAS SERVICE LINE TEE CONNECTION TO THE MAIN AT THIS LOCATION, APPARENTLY SHORTLY AFTER THE INSTALLATION OF THE SERVICE LINE. THE LARGE ROOT BALL GROWTH FROM THIS TREE CREATED A STRESS THAT PUSHED DOWN ON THE MAIN AND SERVICE TEE WHILE A ROOT OF THE TREE GROWING ALONG THE SERVICE LINE AND AWAY FROM THE LOCATION OF THE SERVICE FEE PRODUCED TENSILE STRESSES BY PULLING THE SERVICE LINE UP AND AWAY FROM THE MAIN. THE COMBINATION OF THESE STRESSES CAUSED THE SERVICE TO FAIL AT THE TEE CONNECTION. THE SERVICE TEE WAS REMOVED, AND AN INSPECTION REVEALED THERE WERE NO STEEL INSERT AND GRIP RING IN THE SERVICE CONNECTION. THE ABSENCE OF THE STEEL INSERT AND GRIP RING AND THEIR RELEVANCE TO THIS INCIDENT IS UNKNOWN AT THIS TIME.
2025-01-31 10:21 | YES | YES | 20040004 | 2004-01-22 | 2700 | CONNECTICUT NATURAL GAS CORP | 312 DAVIS AVENUE | GREENWICH | FAIRFIELD | CT | 6830 | 3 | Null | 2117 | 2003-12-05 | 0 | 2 | 100000 | 63734.2691 | 153884.3175 | NO | 0 | 0 |  | 20031206 | 31 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | ABOVE GROUND REGULATOR | REGULATOR/METER |  | CAST IRON |  |  |  | 0'-08' W | FISHER GOVERNOR | 1969 | 1970 | ABOVE GROUND |  | J R DISBENNETT, MANAGER | 2034226022 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | NO | NO DATA |  | ON DECEMBER 5, 2003 AT 2126 HOURS, CONNECTICUT NATURAL GAS CORPORATION (CNG) RECEIVED NOTIFICATION FROM THE TOWN OF GREENWICH FIRE DEPARTMENT OF AN ACTIVE HOUSE FIRE AT 312 DAVIS AVENUE. THERE WAS A HEAVY SNOWSTORM IN GREENWICH DURING THE INCIDENT. A CONTRACTOR HAD BEEN WORKING IN THE AREA PLOWING SNOW AT 312 DAVIS AVENUE. CNG RESPONDED AND HAD A REPRESENTATIVE ON SITE AT 2137 HOURS. THE GAS SERVING 312 DAVIS AVENUE WAS OFF UPON CNG ARRIVAL AT THE SITE. THE CNG REPRESENTATIVE FOUND THE SERVICE REGULATOR DAMAGED UPON HIS ARRIVAL. FIVE FIREFIGHTERS INCURRED INJURIES IN THE PROCESS OF FIGHTING THE FIRE. ON DECEMBER 6, CNG PERFORMED A LEAK TEST OVER THE SERVICE AT 312 DAVIS AVENUE ON DECEMBER 6, 2003. AN INVESTIGATION UNDER THE AUTHORITY OF THE GREENWICH FIRE AND POLICE DEPARTMENTS IS INCOMPLETE TO DATE.
2025-01-31 10:21 | YES | YES | 20040005 | 2003-01-29 | 2600 | COLUMBIA GAS OF PENNSYLVANIA | GIFFIN AVE | MOUNT OLIVER | PITTSBURGH | PA | 15210-2309 | 3 | NO | 1110 | 2003-12-23 | 1 | 0 | 0 | 0 | 0 | NO | 0 | 30 | 708846 | 20031223 | 0.25 | 0.25 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | OTHER | RANGE | NO DATA | [5 empty] | 0 | 0 | WITHIN/UNDER BUILDING |  | RAY M GEESEY, COMPLIANCE SPECIALIST | 7177670250 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | TERESA DUMBAUGH WAS FOUND DECEASED 12/23/2003. THERE WAS A RELEASE OF GAS FROM THE NON-JURISDICTIONAL PIPING INSIDE BUILDING AT RANGE BURNER DOWNSTREAM OF METER. NO FIRE OR EXPLOSION. CAUSE OF DEATH IS UNKNOWN.
2025-01-31 10:21 | YES | YES | 20040006 | 2004-02-06 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | 233 14TH COURT WEST | BIRMINGHAM | JEFFERSON | AL | 3 5204 | 3 | NO | 534 | 2004-01-20 | 1 | 0 | 125000 | 77766.9502 | 187765.769 | NO | 3 | 26 | 711026 | 20040120 | 23 | 25 |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 |  |  |  | 0 | 1948 | UNDER PAVEMENT |  | LEE PETERS, LEAD ENGINEER | 2053268186 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A NATURAL BREAK IN THE BODY OF THE MAIN.
2025-01-31 10:21 | YES | YES | 20040007 | 2004-02-11 | 24015 | YANKEE GAS SERVICES CO | 144 PEARL LAKE ROAD | WATERBURY | NEW HAVEN | CT | 06706- | 3 | NO | 2001 | 2003-03-11 | 0 | 2 | 0 | 0 | 0 | NO | 0 | 18 | 639171 | 20030311 | 57 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | VALVE |  | OTHER | BROZNE | 0.75 |  | N/A | A. Y. MCDONALD | 1986 | 1986 | WITHIN/UNDER BUILDING |  | KEVIN S DUPRE, FIELD OPERATIONS | 2035963080 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | A VEHICLE OPERATED BY AN OCCUPANT OF THE BUILDING STRUCK EQUIPMENT STORED IN FRONT OF THE GAS METER SET. EQUIPMENT DAMAGED THE SERVICE, CAUSING A LEAK. DRIVER INJURED BY CRASH. DRIVERS HUSBAND INJURED BY THE FOLLOWING CRASH.
2025-01-31 10:21 | NO | NO | 20040009 | 2004-02-12 | 13795 | NORTHERN UTILITIES INC (ME) | 95 MAIN STREET | LEWISTON | ANDROSCOGGIN | ME | 4240 | 3 | NO | 1600 | 2004-01-12 | 0 | 0 | 0 | 0 | 0 | YES | 1 | 30 |  | 20040113 | 0.5 | 0.5 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.25 | UNKNOWN | UNKNOWN | 1900 | 1900 | UNDER PAVEMENT |  | STEPHEN H BRYANT, PRESIDENT BAY STATE/NORTHERN UTILTIES | 5088367627 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | AT APPROXIMATELY 4:00 PM ON 1/12/04 AN EXPLOSION OCCURRED, APPARENTLY INSIDE A BUILDING LOCATED AT 95 MAIN ST. THE FUEL WHICH EXPLODED IS NOW UNKNOWN. NORTHERN UTILITIES PERSONNEL WERE IMMEDIATELY DISPATCHED TO THIS AREA. THEY FOUND NO SIGNIFICANT GAS LEAKAGE PRESENT AND NO INDICATION OF ANY NATURAL GAS LEAKS, WHICH MIGHT HAVE PLAYED A ROLE IN THE EXPLOSION. APPROXIMATELY 90 MINUTES LATER, A FIRE ERUPTED AT THE ADDRESS WHERE THE EXPLOSION HAD OCCURRED. ON 1/13/04 A BREAK ON A 6-INCH LOW PRESSURE CAST IRON GAS MAIN WAS FOUND LOCATED IN THE PAVED STREET IN FRONT OF THE ADDRESS. IT IS NOT KNOWN AT THIS TIME WHETHER THIS BREAK WAS CAUSED BY THE EXPLOSION OR EXISTED EARLIER. THE BREAK IN THE CAST IRON MAIN WAS REPAIRED PROMPTLY AFTER IT WAS LOCATED. UNDER THE SUPERVISION OF THE MAINE DEPT OF PUBLIC UTILITIES, THE SECTION OF PIPE WHERE THE FRACTURE WAS FOUND HAS BEEN TRANSPORTED TO AN INDEPENDENT LABORATORY FOR TESTING. THIS REPORT IS BEING FILED FOR THE PURPOSES OF REGULATORY COMPLIANCE. NORTHERN UTILITIES DOES NOT KNOW AT THIS TIME WHETHER AN "INCIDENT" OCCURRED WITHIN THE MEANING OF PART 192.
2025-01-31 10:21 | YES | NO | 20040010 | 2004-02-12 | 15462 | PECO ENERGY CO | 451 SUSQUEHANNA ROAD | HUNTINGDON VALLEY | MONTGOMERY | PA | 19006 | 3 | NO | 400 | 2004-01-11 | 0 | 0 | 300000 | 186640.6804 | 450637.8455 | NO | 1 | 54 |  | 20040111 | 75 | 99 | BY TEST | 120 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | FITTING |  | POLYETHYLENE PLASTIC |  | 2 | 0.216 | ASTMD-2513 | PERFECTION | 0 |  | UNDER GROUND OR UNDER WATER |  | DAVE MACFARLAND, MANAGER OCC | 6109419758 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | A PLASTIC MECHANICAL TEE BECAME UNSEALED FROM THE MAIN RESULTING IN A RELEASE OF GAS.
2025-01-31 10:21 | YES | YES | 20040011 | 2004-02-17 | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 502 GARRETT | PASADENA |  | TX | 7 7502 | 3 | NO | 1126 | 2004-01-17 | 0 | 1 | 0 | 0 | 0 | YES | 4 | 40 |  | 20040117 | 44 | 60 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | SERVICE LINE |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | API5L | UNKNOWN | 0 | 1944 | UNDER GROUND OR UNDER WATER |  | TAL R. CENTERS, MANAGER, GAS OPERATIONS & SYSTEM INTEGRITY | 7139678093 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | DAMAGED FROM OUTSIDE FORCES CAUSED DRESSER COUPLING ON A 3/4" SERVICE LINE AT 502 GARETT TO LEAK. GAS MIGRATED THROUGH PREVIOUSLY DAMAGED CUSTOMER OWNED SEWER LINE DROP. ON 1/17/04 GAS WAS IGNITED WHILE THRID PARTY CONTRACTOR WAS REPLACING SEWER LINE AT 502 GARRETT.
2025-01-31 10:21 | YES | YES | 20040012 | 2004-02-20 | 31770 | NEW ENGLAND GAS COMPANY | 130 TELL STREET | PROVIDENCE | PROVIDENCE | RI | 02909- | 3 | NO | 1908 | 2004-02-03 | 0 | 2 | 18000 | 11198.4408 | 27038.2707 | NO | 0 | 45 | 712357 | 20040203 | 9 | 12 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 4 | 0.4 |  |  | 0 | 1908 | WITHIN/UNDER BUILDING |  | RICHARD A. ABRAHAM | 4015742073 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | UNUSUALLY LONG PERIODS OF EXTREME COLD TEMPERATURES GENERATED FROST CONDITIONS REACHING THE MAINS DEPTH OF APPROXIMATELY 4.5 FEET, PRESUMABLY CAUSING EARTH MOVEMENT AND RESULTING PIPE FRACTURE.
2025-01-31 10:21 | YES | NO | 20040013 | 2004-02-20 | 22182 | WASHINGTON GAS LIGHT CO | 803 TRETON WOODS AVENUE | GREAT FALLS | FAIRFAX | VA | 2 2066 | 3 | NO | 29 | 2004-01-31 | 0 | 0 | 400000 | 248854.2405 | 600850.4607 | NO | 1 | 8 |  | 20040131 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | OTHER | HOUSELINE | BODY OF PIPE |  | OTHER | COPPER | 0.5 | 0.049 | UNKNOWN | UNKNOWN | 0 | 1989 | ABOVE GROUND |  | JAMES JONES | 7034086407 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE ROOF GUTTER ON THE HOUSE, WHICH WAS FILLED WITH ICE, FELL OFF AND SEVERED THE COPPER LINE THAT ENTERED THE HOUSE FROM THE METER BUILD UP. THE SEVERED LINE CAUSED GAS TO RELEASE WHICH WAS IDENTIFIED AS A SECONDARY CONTRIBUTOR TO THIS INCIDENT. THE ORIGIN AND CAUSE IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | NO | NO | 20040014 | 2002-01-09 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | 36081 ALABAMA HWY 69 | MOUNDVILLE | HALE | AL | 3 5474 | 3 | NO | 14 | 2004-02-06 | 0 | 0 | 65000 | 40438.8141 | 97638.1999 | NO | 6 | 0 |  | 20040206 | 302 | 400 | BY TEST | 600 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | UNSPECIFIED NATURAL FORCE DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.156 | API 5L | MAVERICK | 2002 | 2003 | UNDER GROUND OR UNDER WATER |  | TOM JOHNSTONE, LEAD ENGINEER | 2053262990 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: LANDSLIDE/WASHOUT |  | Null |  | Null | 0 |  | Null | NO DATA |  | SUDDEN HEAVY RAINS OF 4-5" FELL THEREBY CAUSING A RECENTLY CONSTRUCTED STATE HWY. ROADBED TO SOFTEN AND SLIDE INTO ALABAMA GAS 4" STEEL MAIN, WHICH WAS LOCATED NEAR THE TOE OF THE SLOPE.
2025-01-31 10:21 | YES | NO | 20040015 | 2004-02-19 | 2596 | COLUMBIA GAS OF OHIO INC | IN THE VICINITY OF CENTRAL COLLEGE ROAD | NEW ALBANY | FRANKLIN | OH | 4 3054 | 3 | NO | 900 | 2004-01-23 | 0 | 0 | 85000 | 52881.5261 | 127680.7229 | NO | 0 | 45 | 711363 | 20040123 | 55 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | OTHER | SERVICE TEE FITTING | FITTING |  | POLYETHYLENE PLASTIC |  |  |  | UNKNOWN | CENTRAL | 0 | 0 | UNDER GROUND OR UNDER WATER |  | RICK WILBERT, SENIOR ENGINEER | 4408912454 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | MARKING FAGS INSTALLED AS A RESULT OF NOTIFICATION | YES | NO DATA |  | A THIRD PARTY CONTRACTOR WAS INSTALLING WATER LINES WHEN THEY STRUCK A NATURAL GAS SERVICE TEE ON AN 8" PLASTIC MAIN LINE. A COLUMBIA GAS OF OHIO, INC. CREW RESPONDED TO THE SCENE AND SQUEEZED OFF THE 8" PLASTIC MAIN RESULTING IN AN OUTAGE TO APPROXIMATELY 1900 CUSTOMERS. SEE ATTACHED SERVICE FAILURE REPORTS AS REQUIRED BY PUBLIC UTILITIES COMMISSION OF OHIO.
2025-01-31 10:21 | YES | YES | 20040016 | 2004-02-18 | 4350 | ELIZABETHTOWN GAS CO | 63 DAWN DRIVE | CLARK | UNION | NJ | 7066 | 3 | NO | 353 | 2004-01-19 | 1 | 0 | 150000 | 93320.3402 | 225318.9227 | NO | 0 | 0 |  | 20040119 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | NO DATA |  | NO DATA |  | NO DATA | [5 empty] | 0 | 0 | NO DATA |  | MICHAEL P. SCACIFERO | 9082895000 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE FIRE. CAUSE UNDER INVESTIGATION. PARTS BELOW ARE NOT APPLICABLE
2025-01-31 10:21 | YES | NO | 20040017 | 2004-03-01 | 15518 | PIEDMONT NATURAL GAS CO INC | 30 YORK CIRCLE | GREENVILLE | GREENVILLE | SC | 2 9605 | 3 | NO | 1721 | 2004-02-18 | 0 | 0 | 1000000 | 622135.6012 | 1502126.1517 | NO | 2 | 0 | 713728 | 20040218 | 60 | 75 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | OTHER | ENTIRE ASSY. DESTROYED | STEEL |  |  |  | UNKNOWN | UNKNOWN | 0 | 0 | ABOVE GROUND |  | GEORGE E. WALLACE | 7047314602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | PLEASE SEE PART B
2025-01-31 10:21 | YES | NO | 20040018 | 2004-02-25 | 12642 | MOBILE GAS SERVICE CORP | 10650 OLD PASCAGOULA ROAD | GRAND BAY | MOBILE | AL | 3 6541 | 1 | NO | 125 | 2004-01-26 | 0 | 0 | 100000 | 62213.5601 | 150212.6152 | NO | 2 | 10 | 711577 | 20040126 | 225 | 250 | BY TEST | 400 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | WELD |  | STEEL |  | 4 | 0.237 | UNKNOWN | UNKNOWN | 0 | 0 | ABOVE GROUND |  | PETER KEEGAN, MANAGER OF ENGINEERING | 2514504759 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | Null | 0 |  | NO | NO DATA |  | VEHICLE LEFT ROADWAY AND DAMAGED PIPE AT RISER WHERE PIPELINE TRANSITIONS FROM UNDERGROUND TO ABOVEGROUND TO TRAVERSE THE BRIDGE.
2025-01-31 10:21 | YES | NO | 20040019 | 2004-03-03 | 31770 | NEW ENGLAND GAS COMPANY | 196 ELDRIDGE STREET | CRANSTON | PROVIDENCE | RI | 2910 | 3 | NO | 47 | 2004-02-07 | 0 | 0 | 100000 | 62213.5601 | 150212.6152 | NO | 0 | 45 | 712692 | 20040207 | 9 | 12 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.43 | UNKNOWN | UNKNOWN | 0 | 1931 | WITHIN/UNDER BUILDING |  | RICHARD A. ABRAHAM, DIVISION MANAGER | 4012532425 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | UNUSUALLY LONG PERIODS OF EXTREME COLD TEMPERATURES GENERATED FROST CONDITIONS REACHING THE MAINS DEPTH OF APPROXIMATELY 4.5 FEET, PRESUMABLY CAUSING EARTH MOVEMENT AND RESULTING PIPE FRACTURE.
2025-01-31 10:21 | YES | NO | 20040020 | 2004-02-27 | 13710 | NORTHERN ILLINOIS GAS CO | 1334 MCCAMERON AVE | LOCKPORT | WILL | IL | 6 0441 | 3 | NO | 2236 | 2004-01-31 | 0 | 0 | 100000 | 62213.5601 | 150212.6152 | NO | 3 | 2 |  | 20040201 | 60 | 60 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | MAIN |  | WELD |  | STEEL |  | 6 | 0.188 | UNKNOWN | UNKNOWN | 0 | 1963 | UNDER GROUND OR UNDER WATER |  | LETICIA QUEZADA, COORDINATOR TECHNICAL COMPLIANCE | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | GAS FROM LEAK ON 6" STELL MAIN MIGRATED ACROSS THE STREET CAUSING A SMALL EXPLOSION AND SUBSEQUENT FIRE. NO INJURIES, NO FATALITIES. NOTE: THIS INCIDENT WAS ORIGINALLY REPORTED BY PHONE TO THE NRC AS 306 FARRELL ROAD, LOCKPORT
2025-01-31 10:21 | NO | NO | 20040021 | 2004-03-02 | 18536 | SOUTHWEST GAS CORP | 22883 S. 210 ST | QUEEN CREEK | MARICOPA | AZ | 8 5242 | 3 | NO | 1635 | 2004-02-02 | 0 | 0 | 50000 | 31106.7801 | 75106.3076 | YES | 0 | 53 | 713575 | 20040203 | 60 | 60 | BY TEST | 98 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | FITTING |  | OTHER PLASTIC |  |  |  | D-1248 | PHILLIPS | 2002 | 2002 | UNDER GROUND OR UNDER WATER |  | BERNIE GALLENBECK, MANAGER/DIVISION COMPLIANCE | 6024845240 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | POOR WORKMANSHIP DURING CONSTRUCTION |  | SEE PART D
2025-01-31 10:21 | NO | NO | 20040022 | 2004-03-02 | 4510 | EQUITABLE RESOURCES (A.K.A EQUITABLE GAS CO) | 172 WALNUT RIDGE RD | FALLOWFIELD |  | PA | 1 5022 | 3 | NO | 1026 | 2004-01-25 | 0 | 0 | 60000 | 37328.1361 | 90127.5691 | NO | 1 | 4 | 711515 | 20040125 | 0.43 | 0.5 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION | OTHER | UNDER INVESTIGATION |  |  | UNKNOWN | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | EDWARD M NOLAN JR, SENIOR VICE PRESIDENT DISTRIBUTION | 4123953226 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE INCIDENT IS CURRENTLY UNDER INVESTIGATION TO DETERMINE IF EQUITABLE GAS FACILITIES WERE A CONTRIBUTING FACTOR.
2025-01-31 10:21 | NO | NO | 20040024 | 2004-03-09 | 15469 | PHILADELPHIA GAS WORKS | OGONTZ AND OLNEY AVENUES | PHILADELPHIA | PHILADELPHIA | PA | 1 9141 | 4 | NO | 1655 | 2004-01-13 | 0 | 0 | 75000 | 46660.1701 | 112659.4614 | NO | 18 | 37 |  | 20040213 | 20 | 35 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 20 |  |  |  | 0 | 1911 | OTHER | UNDERGROUND EVACUATION | STEVEN A. GROEBER, DIRECTOR, FIELD OPERATIONS | 2156846376 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 0 |  | YES | NO DATA |  | ON FEBRUARY 12, 2004 AT 2355, THE PHILADELPHIA WATER DEPARTMENT DISPATCHER (KING) NOTIFIED PHILADELPHIA GAS WORKS DISPATCHER (R. ROSAS) OF A BROKEN WATER MAIN AT OLNEY AND OGONTZ AVENUE. AT 1:00 AM ON FEBRUARY 13, 2004, A GAS WORKS CREW LEAD BY WILLIAM WALKER WAS DISPATCHED TO INVESTIGATE THIS WORK SITE. MR. WALKER REPORTED FINDING AN INDICATION OF A WATER LEAK ON THE NORTHEAST CORNER OF OLNEY AND OGONTZ AVENUE. HE MADE HIS NECESSARY CHECKS AND MARKED THE LOCATION OF A 20" HIGH-PRESSURE GAS MAIN IN THE ROADWAY ON THE NORTHEAST CORNER. ADDITIONALLY HE SAW YELLOW MARKS INDICATING THE LOCATION OF A 6" LOW PRESSURE MAIN ON THE NORTHEAST CORNER. HE WAS ON THIS LOCATION UNTIL 3:30 A.M. AND DID NOT SEE ANY WATER DEPARTMENT PERSONNEL. PGW DID RECIEVE AN EMERGENCY PA. ONE CALL TICKET (NUMBER 0445004) AT 1:21 A.M. ON FEBRUARY 13, 2004 WHILE MR. WALKER WAS ON THIS JOB SITE. ON FEBRUARY 13, 2004, PGW DISTRIBUTION INSPECTOR EUGENE ESPOSITO REPORTS ARRIVING ON THIS LOCATION AT 10:40 A.M. PWD WAS JUST ARRIVING ON LOCATION. PWD WILL BE EXCAVATING IN THE NORTH ROADWAY OF OLNEY AVENUE. PGW STRUCTURES ARE MARKED AND SAFE. HE MARKED THE GAS MAIN LOCATIONS ON THE WEST SIDE OF OGONTZ SOUTH OF THE NORTH CURB LINE OF OLNEY AVENUE. HE ALSO REPORTS SEEING YELLOW MARKS MADE BY SOMEONE OTHER THAN HIMSELF IN THE AREA OF THE JOB SITE. MR. ESPOSITO LEAVES THIS JOB SITE AT 11:00 A.M. AT 1525 MR. ESPOSITO RETURNS AND FINDS PWD BREAKING A HOLE IN THE ROADWAY ON THE NORTH SIDE OLNEY AVE. AT OGONTZ AVENUE. HE REPORTS COMPANY STRUCTURES ARE MAKRED AND SAFE. AT 1655 PGW RECIEVES A REPORT OF GAS FIRE/EXPLOSION AT THIS LOCATION. PGW AND PHILADELPHIA FIRE DEPARTMENT RESPOND AND BRING THE SITUATION UNDER CONTROL. APPROXIMATELY 400 PEOPLE WERE EVACUATED BY PHILADELPHIA FIRE DEPARTMENT. THERE WERE NO INJURIES REPORTED. DUE TO THE EXTENT OF THE FIRE THERE WAS PROPERTY DAMAGE TO PWD DIGGER LOADER, CREW TRUCK AND AIR COMPRESSOR. ADDITIONALLY THERE WAS DAMAGE TO PARKED CARS, COMCAST CABLE AND PECO OVERHEAD LINES AS WELL AS DAMAGE TO STREET LIGHTS, TRAFFIC SIGNALS AND STORE SIGNS ON SEVERAL PROPERTIES. PGW CREWS FOUND A 20" X 6" TEE LOCATED 21 SOUTH OF THE NORTH CURB LINE OF OLNEY AVE AND 13 WEST OF THE EAST CURB LINE OF OGONTZ AVE. HAD BEEN COMPLETELY PULLED APART AND BROKEN BY THE PWD DIGGER LOADER. THIS MADE A 20" HOLE ON THE SIDE OF THE GAS MAIN OPERATING AT 20 PSIG.
2025-01-31 10:21 | YES | NO | 20040025 | 2004-03-05 | 22182 | WASHINGTON GAS LIGHT CO | 3821 ARCHER PLACE | KENSINGTON | MONTGOMERY | MD | 2 0895 | 1 | NO | 1851 | 2004-02-06 | 0 | 0 | 400000 | 248854.2405 | 600850.4607 | NO | 2 | 24 | 717665 | 20040207 | 20 | 25 | BY TEST | 32 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.75 | 0.113 |  |  | 0 | 1959 | ABOVE GROUND |  | JEROLD ALSTON, SAFETY SPECIALIST | 7037504849 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | INCIDENT WAS BELIEVED TO BE DUE TO FAULTY WIRING IN THE KITCHEN AREA OF THE HOME. AS FIRE CONSUMED HOME, DAMAGE WAS DONE TO THE GAS METER LOCATED IN THE BASEMENT (BELOW KITCHEN). ESCAPING GAS PROVIDED A SECONDARY SOURCE OF EMISSION FOR THE FIRE.
2025-01-31 10:21 | YES | YES | 20040026 | 2004-02-26 | 13782 | NORTHERN STATES POWER CO | 711 BIRCH STREET N | ROYALTON | MORRISON | MN | 5 6373 | 3 | NO | 558 | 2004-01-13 | 0 | 1 | 200000 | 124427.1202 | 300425.2303 | NO | 0 | 42 | 710398 | 20040113 |  | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | EARTH MOVEMENT | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 1 | 0.099 | 2406 | DUPONT | 0 | 0 | WITHIN/UNDER BUILDING |  | DAN WOEHRLE, GAS SYSTEM ENGINEERING | 6512292211 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: OTHER | -1 | Null |  | Null | 0 |  | Null | NO DATA |  | THE SUSPECTED SOURCE OF THE GAS THAT CAUSED THE EXPLOSION IS A LEAK ON THE GAS SERVICE TO 715 STATE HIGHWAY 10. THIS SERVICE RUNS BETWEEN 709 AND 711 BIRCH STREET TO SERVE GENES REPAIR, A COMMERCIAL BUSINESS LOCATED BEHIND 711 BIRCH. THE LEAK IN THE SERVICE APPEARED TO BE FROM A GOPHER CHEW. GAS MIGRATING FROM THE LEAK ENTERED 711 BIRCH, WHICH WAS NOT SERVED BY GAS. THE GAS WAS IGNITED AND THE HOUSE EXPLODED, COMPLETELY DESTROYING THE HOUSE. THE EXPLOSION AND FIRE IS UNDER INEVSTIGATION BY THE STATE FIRE MARSHAL.
2025-01-31 10:21 | YES | NO | 20040027 | 2004-03-04 | 13710 | NORTHERN ILLINOIS GAS CO | 15 LIBERTY DRIVE | BARRINGTON | COOK | IL | 6 0010 | 3 | NO | 249 | 2004-02-03 | 0 | 0 | 750000 | 466601.7009 | 1126594.6137 | NO | 1 | 5 | 712346 | 20040203 | 60 | 60 | BY TEST | 90 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | STEEL |  | 0.5 |  |  |  | 0 | 1978 | ABOVE GROUND |  | LETICIA QUEZADA, COORDINATOR TECHNICAL COMPLIANCE | 6309838676 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | FIRE, WHICH STARTED INSIDE THE HOUSE NEAR GARAGE, CONSUMED THE ENTIRE STRUCTURE ALSO CAUSING DAMAGE TO THE METER SET ASSEMBLY. METER SET ASSEMBLY WAS LOCATED ON OPPOSITE SIDE OF LOCATION WHERE FIRE STARTED. NO INJURIES, NO FATALITIES.
2025-01-31 10:21 | YES | YES | 20040028 | 2004-03-05 | 2392 | CITIZENS GAS & COKE UTILITY | 373 S RITTER AVENUE | INDIANAPOLIS | MARION | IN | 6219--7141 | 3 | NO | 240 | 2004-02-04 | 0 | 2 | 900000 | 559922.0411 | 1351913.5365 | NO | 1 | 0 | 712367 | 20040204 | 24 | 30 | BY TEST | 90 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | UNKNOWN | OTHER | UNKNOWN AT THIS TIME | OTHER | UNKNOWN |  |  | UNKNOWN | UNKNOWN | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN J. EDDINGTON, SUPERINTENDENT OF FIELD OPERATIONS | 3179274657 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | HOUSE AT 373 S RITTER EXPLODED AT APPROXIMATELY 2:40 AM ON THE MORNING OF 02/04/04. NO CAUSE HAS BEEN DETERMINED AT THIS TIME AND THERE IS NO INDICATION FROM OUR INVESTIGATION THAT THE CAUSE WAS RELATED TO PIPING OWNED AND OPERATED BY CITIZENS GAS. THE INICIDENT IS STILL UNDER INVESTIGATION.
2025-01-31 10:21 | YES | YES | 20040029 | 2004-03-16 | 24015 | YANKEE GAS SERVICES CO | 39 HOSPITAL AVENUE | DANBURY | FAIRFIELD | CT | 06810- | 3 | NO | 230 | 2004-02-13 | 0 | 1 | 0 | 0 | 0 | NO | 2 | 0 | 713232 | 20040213 | 1.19 | 1.26 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | NATURAL FORCE DAMAGE | TEMPERATURE | MAIN |  | BODY OF PIPE |  | CAST IRON |  | 6 | 0.45 | UNKNOWN | UNKNOWN | 0 | 1954 | UNDER PAVEMENT |  | DAN FITZSIMMONS - AREA OPERATIONS MANAGER | 2037483228 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | EARTH MOVEMENT: FROST |  | Null |  | Null | 0 |  | Null | NO DATA |  | WHILE GAS EMPLOYEE WAS REPAIRING GAS MAIN, EMPLOYEE WAS OVERCOME BY OXYGEN DISPLACEMENT.
2025-01-31 10:21 | YES | YES | 20040030 | 2004-03-16 | 31358 | TECO PEOPLES GAS LP OPERATIONS | WEST 12TH AND DAHLIA | JACKSONVILLE | DUVAL | FL | 3 2254 | 3 | NO | 1018 | 2004-02-26 | 0 | 1 | 0 | 0 | 0 | NO | 1 | 0 | 714517 | 20040227 | 125 | 133 | BY TEST | 200 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 4 | 0.188 | API 5LX X42 | UNKNOWN | 0 | 1996 | UNDER GROUND OR UNDER WATER |  | TIM KASPRZYK, MANAGER, SAFETY AND OPERATIONAL TRAINING | 8132284831 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES |  | YES | 3 | 2004-01-21 | YES | NO DATA |  | CONTRACTOR HIT MAIN WHILE PERFORMING DIRECTIONAL BORING. TECO PEOPLES GAS EMPLOYEE WAS INJURED WHILE IN THE PROCESS OF REPAIRING DAMAGED MAIN.
2025-01-31 10:21 | YES | NO | 20040031 | 2004-03-16 | 4483 | ENSTAR NATURAL GAS CO | 1101 ROBIN'S SONG AVE | WASILLA |  | AK | 9 9654 | 3 | NO | 1057 | 2004-03-02 | 0 | 0 | 150000 | 93320.3402 | 225318.9227 | NO | 1 | 38 | 714905 | 20040302 | 55 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | SERVICE LINE |  | DRIP/RISER |  | POLYETHYLENE PLASTIC |  | 0.75 | 0.09 | DRISCOPIPE 8000 HDPE | UNKNOWN | 1997 | 1997 | ABOVE GROUND |  | DAVID W. BREDIN, OPERATIONS MANAGER | 9072643745 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON TUESDAY MORNING, MARCH 2, 2004 AT APPROXIMATELY 10:57 AM AST, ENSTAR NATRUAL GAS COMPANY WAS NOTIFIED OF A STRUCTURE FIRE AT 1101 ROBINS SONG AVE, WASILLA, ALASKA. AN ENSTAR SERVICEMAN WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE SERVICEMAN FOUND A RESIDENTIAL STURCTURE ON FIRE. HEAT FROM THE FIRE MELTED THE POLYETHYLENE SERVICE LINE RISER, CAUSING A RELEASE OF NATURAL GAS. A DISTRIBUTION CREW DUG UP THE SERVICE LINE, PINCED IT OFF, AND CAPPED IT. NATURAL GAS FROM ENSTARS FACILITIES DID NOT CAUSE OR CONTRIBUTE TO THE FIRE.
2025-01-31 10:21 | YES | NO | 20040035 | 2004-03-24 | 12350 | CENTERPOINT ENERGY MINNEGASCO | 402 1ST AVE NW | BUFFALO | WRIGHT | MN | 5 5313 |  | NO | 2240 | 2004-02-19 | 0 | 0 | 198000 | 123182.849 | 297420.978 | YES | 4 | 0 | 713920 | 20040220 | 55 | 60 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | SERVICE LINE |  | JOINT |  | NO DATA |  |  |  | ORANGEBERG PE 3306 | ORANGEBERG | 0 | 1967 | UNDER PAVEMENT |  | ANDREW BALGOBIN, DAMAGE PREVENTION SUPERVISOR | 6128618692 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THE SERVICE LINE MATERIAL PULLED OUT OF MECHANICAL FITTING. THIS FITTING AND STIFFENER COMBINATION DID NOT HAVE ADEQUATE TENSILE RESTRAINT TO COUNTER SOIL EFFECTS AND TEMPERTURE CONTRACTION EFFECTS OF THIS SERVICE. 6-16-05 MATERIALS: SERVICE MATERIAL IS ORANGEBURG 3306, 1/2" IPS SCH 40 WALL THICKNESS. OD AND WALL THICKNESS WERE MEASURED USING A PI TAPE AND A WALL MICROMETER. WALL THICKNESS MINIMUM =.109", MAXIMUM WALL = .117 O.D. AVERAGE = 0.853" COUPLING MATERIAL IS CONTINENTAL A572-2 WELD X COMPRESSION COUPLING.
2025-01-31 10:21 | NO | NO | 20040040 | 2004-03-17 | 1088 | BALTIMORE GAS & ELECTRIC CO | 4122 W. BELVEDERE AVENUE | BALTIMORE |  | MD | 2 1215 | 3 | NO | 2051 | 2004-02-16 | 0 | 0 | 50000 | 31106.7801 | 75106.3076 | NO | 1 | 32 | 713521 | 20040216 | 7 | 10 | BY CFR 192.619(A)(3) |  | DAMAGE BY OUTSIDE FORCES | OTHER OUTSIDE FORCE DAMAGE | UNSPECIFIED OUTSIDE FORCE DAMAGE | METER SET ASSEMBLY |  | REGULATOR/METER |  | OTHER | ALUMINUM |  |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | JOHN A GARRISON - SUPERVISOR GAS SERVICE | 4102915130 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | LIGHTNING OR FIRE |  | Null |  | Null | 0 |  | Null | NO DATA |  | BALTIMORE COUTY FIRE DEPT. (bcfd) REQUESTED OUR ASSISTANCE TO TURN OFF NATURAL GAS. A GAS MECHANIC WAS DISPATCHED AT 2051 AND ARRIVED AT 2111. THE METER/REGULATOR INSTALLATION HAD BEEN DAMAGED BY THE HEAT OF THE FIRE CREATING A RESTRICTED MP GAS FIRE AT THE METER INSTALLATION. BCFD TURNED OFF THE 1 1/4" GATE VALVE FEEDING THE METER INSTALLATION; STOPPING NATURAL GAS FLOW. BCFD INVESTIGATION DETERMINED THE CAUSE OF FIRE TO BE AN ACCIDENTAL SPILL OF FUEL BY OWNER FILLING OPERATING KEROSENE HEATER. BUILDING WAS COMPLETELY DESTROYED. SURFACE AND SUB-SURFACE SURVEYS WERE CONDUCTED AT BUILDING FOUNDATION, SERVICE AND OVER SERVICE TAP AT MAIN; NO INDICATION OF NATURAL GAS.
2025-01-31 10:21 | YES | YES | 20040041 | 2004-03-29 | 180 | ALABAMA GAS CORP (EX. MARENGO CORP PROPERTY) | 122 WEST CREST ESTATES | HUEYTOWN | JEFFERSON | AL | 3 5023 | 3 | NO | 1850 | 2004-03-21 | 1 | 0 | 18500 | 11509.5086 | 27789.3338 | NO | 0 | 20 |  | 20040321 | 39 | 50 |  |  | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | JOINT |  | STEEL |  | 34 | 0.113 | UNKNOWN | UNKNOWN | 0 | 0 | ABOVE GROUND |  | LEE PETERS, MANAGER - SYSTEM PLANNING | 2053268186 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | A VEHICLE ROLLED APPOX. 300 IN REVERSE FROM 512 WEST CREST ESTATES STRIKING A RESIDENTIAL GAS METER ASSEMBLY, RESIDENTIAL ELECTRICAL HOOKUP AND A MOBILE HOME. A FIRE RESULTED IN THE DEATH OF THE DRIVER OF THE VEHICLE. LATITUDE 33459 LONGITUDE -8700
2025-01-31 10:21 | NO | NO | 20040043 | 2004-04-05 | 31978 | TXU GAS COMPANY | 200 RAM | SADLER | GRAYSON | TX | 76264- | 3 | NO | 1310 | 2004-02-24 | 0 | 0 | 50000 | 31106.7801 | 75106.3076 | YES | 1 | 0 | 714263 | 20040224 | 9 | 10 | BY CFR 192.619(A)(3) |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | MAIN |  | BODY OF PIPE |  | STEEL |  | 2 |  |  |  | 0 | 0 | WITHIN/UNDER BUILDING |  | ELLEN WEAVER, MANAGER | 2145334602 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | A GAS LEAK OCCURRED AT DRESSERS CONNECTING A SERVICE LINE TO THE MAIN. GAS MIGRATED UNDER A SLAB AND INTO AN INTERIOR WALL. THE GAS IGNITION WAS SPARKED WHEN A WALL SWITCH WAS FLIPPED FROM THE "ON" POSITION TO THE "OFF" POSITION.
2025-01-31 10:21 | NO | NO | 20040048 | 2004-04-01 | 31632 | NORTHWESTERN ENERGY LLC | 203 SOUTH 3RD STREET | HAMILTON | RAVALLI | MT | 5 9701 | 3 | NO | 1022 | 2004-02-27 | 0 | 0 | 51000 | 31728.9157 | 76608.4337 | NO | 0 | 33 | 714561 | 20040227 | 30 | 35 | BY CFR 192.619(A)(3) |  | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 12 |  | ASTM D1248 | PERFORMANCE PIPE | 2002 | 2002 | UNDER GROUND OR UNDER WATER |  | JOHN CARMODY, DIRECTOR OF DISTRIBUTION ENGINEERING | 4064972612 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | THIRD PARTY WAS DIGGING IN THE BACKYARD AND HIT A 1/2 PLASTIC GAS SERIVCE SERVING A HAIR STYLING BUSINESS LOCATED IN THE OWNERS HOME. GAS IMMIGRATED INTO THE FOUNDATION AND AN EXPLOSION OCCURED CAUSING STRUCTURAL DAMAGE TO THE RESIDENCE.
2025-01-31 10:21 | NO | NO | 20040051 | 2004-04-21 | 22777 | WE ENERGIES | 224 SMITH STREET | NEENAH | WINNEBAGO | WI | 5 4956 | 3 | NO | 750 | 2004-01-22 | 0 | 0 | 63856 | 39727.091 | 95919.7675 | NO | 0 | 47 | 717536 | 20040331 | 47 | 60 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | METER SET ASSEMBLY |  | BODY OF PIPE |  | STEEL |  | 0.75 | 0.113 | A53 GR B | UNKNOWN | 0 | 1972 | ABOVE GROUND |  | DAVID E BARKEI, MANAGER REGULATORY COMPLIANCE | 4143894474 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | Null |  | Null | 0 |  | Null | NO DATA |  | ON JANUARY 22, 2004, AT ABOUT 0750 HOURS IN THE MORNING, TERA HEIL, WHILE DRIVING A FORD TAURUS VEHICLE (MODEL YEAR 2000) ON SMITH STREET IN NEENAH WISCONSIN, LOST CONTROL OF HER VEHICLE. THE VEHICLE LEFT THE HIGHWAY, TRAVELED ACROSS A LAWN, AND STRUCK THE GAS METER ASSEMBLY ON THE SIDE OF THE HOUSE AT 224 SMITH STREET. THE IMPACT OF THE VEHICLE WITH THE METER ASSEMBLY SHEARED THE METER ASSEMBLY AT THE THREADED AREA OF THE PIPE NIPPLE, JUST ABOVE THE RISER VALVE. MS. HEIL ESCAPED THE ACCIDENT WITHOUT INJURIES; HOWEVER, THE ESCAPING GAS WAS IGNITED BY VEHICLE AND SUBSEQUENTLY BURNED THE HOUSE AND THE VEHICLE. THE OCCUPANT OF THE HOUSE WAS ALSO ABLE TO EVACUATE SAFELY. THE CITY OF NEENHAH FIRE DEPARTMENT WAS CALLED TO THE SCENE TO EXTINGUISH THE FIRE. UPON ARRIVAL THEY FOUND A CAR ON TOP OF THE BROKEN RISER WITH THE HOUSE AND THE CAR BURNING DUE TO THE IGNITION OF THE ESCAPING GAS. UNABLE TO REACH THE RISER VALVE, THEY CONTACTED WISCONSIN ELECTRIC POWER COMPANY GAS OPERATIONS TO SHUT OFF THE GAS SUPPLY. IN THE MEANTIME, A TOTAL OF 19 AREA FAMILIES WERE EVACUATED FOR SAFETY AND THE STREET BARRICADED FROM PUBLIC USE. UPON THE GAS SERVICE CREWS ARRIVAL, THEY CLOSED THE GAS MAIN VALVE AT THE INTERSECTION OF SMITH AND ISABELLA STREETS, AND THE PROCEEDED TO CUT AND CAP THE 1/2" GAS SERVICE TO THE HOME. A PHONE NOTIFICATION MESSAGE WAS MADE THE SAME DAY TO MR. THOMAS STEMRICH, PIPELINE PROGRAM SAFETY MANAGER AT THE WISCONSIN PUBLIC SERVICE COMMISSION, AS A LOCAL NEWSWORTHY EVENT. MR. STEMRICH, WHO WAS ON VACATION AT THE TIME OF THE INCIDENT, WAS NOT REACHED UNTIL THE FOLLOWING DAY, JANUARY 23, 2004, AT WHICH TIME HE WAS VERBALLY NOTIFIED OF THE INFORMATION SURROUNDING THE INCIDENT KNOWN AT THAT TIME. INFORMATION RECEIVED AND COMPILED IN THE WEEKS AFTER THE INCIDENT, REVEALED THAT ALTHOUGH NO DEATHS OR INJURIES OCCURRED, THE TOTAL ASSESSED VALUE OF THE DAMAGE PROBABLY WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING A GAS DISTRIBUTION INCIDENT UNDER CFR 49, PARTS 191.5, 191.7, & 191.9,. THE CURRENT DAMAGE ASSESSMENT BASED ON THE 2003 ASSESSED VALUE OF THE HOUSE, NADA USED CONSUMER PRICE OF THE VEHICLE, METER SET AND LOST GAS IS JUST UNDER $50,000. THE VALUE OF THE CONTENTS OF THE RENTED HOUSE IS STILL NOT KNOWN, BUT ASSUMED TO BE LESS THAN $25,000. THUS, THE CURRENT ESTIMATE OF DAMAGES WAS MADE AT BETWEEN $50,000 & $75,000.
2025-01-31 10:21 | YES | NO | 20040053 | 2004-04-28 | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 1300 STATE STREET | ALPENA | ALPENA | MI | 49709 | 3 | NO | 1755 | 2004-04-06 | 0 | 0 | 435000 | 270628.9865 | 653424.876 | NO | 0 | 19 | 718170 | 20040407 | 60 | 60 | BY TEST | 60 | CONSTRUCTION/OPERATING ERROR | MATERIAL/WELD/EQUIP FAILURE | UNSPECIFIED MATERIAL/WELD FAILURE | SERVICE LINE |  | BODY OF PIPE |  | POLYETHYLENE PLASTIC |  | 11 |  |  |  | 0 | 0 | UNDER PAVEMENT |  | JOSEPH A DIDIA, INVESTIGATOR | 3132356921 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | PHYSICAL DAMAGE DURING CONSTRUCTION |  | CONTRACTOR, CORDESS CONSTRUCTION, DOING PUBLIC IMPROVEMENT WORK GRINDING ASPHALT ROAD, HIT 1-1/8" PLASTIC 60 LB SERVICE WHICH CAUSED A FIRE AND BURNT TRUCK AND EQUIPMENT.
2025-01-31 10:21 | YES | NO | 20040067 | 2004-06-02 | 792 | ATLANTA GAS LIGHT CO | RIVERVIEW RD | SMYRNA | COBB | GA | 3 0126 | 3 | NO | 900 | 2004-04-27 | 0 | 0 | 948000 | 589784.55 | 1424015.5918 | NO | 10 | 31 | 720026 | 20040427 | 180 | 500 | BY TEST | 750 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | BODY OF PIPE |  | STEEL |  | 12 | 0.25 | API 5L | USS | 1985 | 1985 | UNDER GROUND OR UNDER WATER |  | PHYLLIS W STALLINGS, P E DISTRIBUTION SUPERVISOR | 7704235720 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | YES | 2004-04-28 | Null | 0 |  | YES | NO DATA |  | A CONTRACTOR INSTALLING STORM DRAINS RUPTURED A 12" HIGH PRESSURE STEEL GAS MAIN WITH A TRACK HOE WHILE EXCAVATING.
2025-01-31 10:21 | YES | YES | 20040073 | 2004-02-12 | 6920 | ENTERGY GULF STATES INC | 2424 PLINY | BATON ROUGE | EAST BATON ROUGE | LA | 70808 | 3 | NO | 1142 | 2004-01-13 | 1 | 0 | 60000 | 37328.1361 | 90127.5691 | NO | 1 | 0 | 710443 | 20040210 |  |  |  |  | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | OTHER | N/A | OTHER | N/A | OTHER | N/A |  |  | cboSpec | CBOMANU | 0 | 0 | OTHER | FIRE INSIDE HOME STRUCTURE | TOMMY J SMITH, COMPLIANCE COORDINATOR | 2253543102 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | N/A NOT GAS RELATED
2025-01-31 10:21 | YES | YES | 20040093 | 2004-07-29 | 15462 | PECO ENERGY CO | 3018 DARBY RD | ARDMORE | DELAWARE | PA | 19003- | 3 | NO | 1230 | 2004-06-29 | 1 | 0 | 0 | 0 | 0 | NO | 0 | 5 | 726653 | 20040629 | 6.5 | 50 | BY TEST | 100 | OTHER | ALL OTHER CAUSES | MISCELLANEOUS | METER SET ASSEMBLY |  | REGULATOR/METER |  | NO DATA | [5 empty] | 0 | 0 | ABOVE GROUND |  | MICHAEL A WILLIAMS, SHIFT MANAGER | 6109411799 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | NO DATA |  | Null |  | Null | 0 |  | Null | NO DATA |  | FATAL VEHICLE ACCIDENT - VEHICLE STRUCK UTILITY POLE AND THEN STRUCK RESIDENTIAL GAS METER RESULTING IN RELEASE OF NATURAL GAS..
2025-01-31 10:21 | YES | NO | 20040108 | 2004-08-24 | 15007 | PACIFIC GAS & ELECTRIC CO | HWY 178 & 1ST STREET | TRONA | SAN BERNADINO | CA | 93562- | 3 | NO | 1000 | 2004-07-25 | 0 | 0 | 90500 | 56303.2719 | 135942.4167 | NO | 0 | 55 | 729746 | 20040727 | 45 | 55 | BY TEST | 100 | DAMAGE BY OUTSIDE FORCES | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | MAIN |  | NO DATA |  | STEEL |  | 3 | 0.156 | N/A | N/A | 0 | 0 | UNDER GROUND OR UNDER WATER |  | G. ANNETTE HOPE, LEAD DIRECTOR ENGINEERING & PLANNING | 4159736998 | NO DATA | NO DATA |  | NO DATA |  | NO DATA | Null | 0 | OUTSIDE/THIRD PARTY |  | NO |  | NO | 0 |  | YES | NO DATA |  | SEARLESS VALLEY MINERALS OPERATING A BACKHOE STRUCK AND PUNCTURED A 3" STEEL GAS MAIN ON 7/25/04 CAUSING SERVICE LOSS TO APPROX 779 CUSTOMERS. AT THE TIME OF THE INCIDENT, THE PROPERTY DAMAGE WAS ESTIMATED TO BE LESS THAN 50,000. HOWEVER, DUE TO THE REMOTENESS OF THE LOCATION AND COMPLICATIONS WITH A CONCURRENT WATER MAIN BREAK THAT DELAYED OUR REPAIRS, ON 7/27/04 IT WAS DETERMINED THAT THE PROPERTY DAMAGE WOULD EXCEED 50,000. THE INCIDENT WAS REPORTED AT THAT TIME.