2024-05-31 11:04 | NO | YES | NO | 20210083 | 39085 | 2021-09-24 13:43 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-08-25 09:55 | PACIFIC | YES | 2021 | RACE STREET & PARK AVENUE | SAN JOSE | SANTA CLARA | CA | 95126 | 37.326 | -121.9115 | [5 empty] | YES | YES |  |  | 2021-08-25 13:53 | 1314710 | 1314934 | NATURAL GAS |  | 6107 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 300 | 2021-08-25 09:55 |  |  |  | 2021-08-25 10:03 | 2021-08-25 09:55 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 3 | STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 498000 | 528751.213695596382 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 498000 | 223402.265565113844 | 528751.213695596382 | 15 | 0 | 28 | 0 | 1 | 28 | 15 | 50 | 50 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | YES | MEASURED DEPTH FROM GRADE | 48 | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | X118101646 | 811 DIG | YES | FACILITY OWNER | YES | YES | 23 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | rosa.duenas@pge.com | 510-298-7063 |  | SUSIE RICHMOND | gsr8@pge.com |  | ROSA DUENAS | GAS PROGRAM MANAGER | 510-298-7063 | rosa.duenas@pge.com | A THIRD-PARTY CONTRACTOR DAMAGED A UN-MARKED 3" STEEL GAS MAIN DURING HORIZONTAL BORING. THE 3" GAS MAIN WAS NOT LOCATED BY PG&E AND WAS STRUCK BY A 10" REAMER CAUSING A RELEASE OF GAS. GAS TRAVELED IN STORM AND SEWER SYSTEMS AS WELL AS COMMUNICATIONS VAULTS. CREWS ON SITE VENTED THE GAS TO PREVENT FURTHER MIGRATION AND ISOLATE. SAFE ZONES WERE ESTABLISHED, AND THE FD ASSISTED WITH EVACUATIONS WITHIN THE ESTABLISHED ZONE. THERE WERE NO INJURIES AND/OR FATALITIES. THIS INCIDENT IS BEING REPORTED DUE TO THE DAMAGE THRESHOLD REPORTING CRITERIA OF $122K+.
2024-05-31 11:04 | NO | YES | YES | 20210084 | 35921 | 2021-10-01 17:32 | SUPPLEMENTAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2021-09-02 18:35 | EASTERN | NO | 2021 | 27 PARK ST | MAYNARD | MIDDLESEX | MA | 01754 | 42.4268 | -71.4564 |  |  | YES |  |  |  |  | YES | TD WILLIAMSON THREE WAY STOPPERS | 2021-09-02 19:45 | 1315634 | 1315635, 1315730 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2021-09-02 16:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 4 | 2021-09-02 18:35 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-09-02 16:33 | 2021-09-02 17:12 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 4 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 2 | API5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN AT THIS TIME | 0.154 | [6 empty] | OTHER | [8 empty] | UNKNOWN TILL COMPLETION OF INCIDENT ANALYSIS | CLASS 3 LOCATION | 212051 | 225145.027340090177509 | 15874 | 16854.210373903407566 | 38676 | 41064.220764841135884 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 266601 | 119596.922493825132378 | 283063.458478834720959 | 0 | 0 | 1 | 3 | 0 | 3 | 0 | 58 | 56.8 | 60 | 192.619(C) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | DRIP |  | 0.1 |  | NO |  |  |  |  | OTHER | LEAK INVESTIGATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM NEVER EXCEEDED MAOP THUS NO INVESTIGATION WAS REQUIRED | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | MEGGAN PENA | MANAGER OPERATIONS GAS COMPLIANCE | meggan.pena@eversource.com | 5084689956 |  | MEGGAN PENA | meggan.pena@eversource.com | 5084689956 | MEGGAN PENA | MANAGER OPERATIONS GAS COMPLIANCE | 5084689956 | meggan.pena@eversource.com | REPORT FILED ON BY HALF OF NSTAR GAS COMPANY D/B/A EVERSOURCE ENERGY. BASED UPON THE INITIAL NARRATIVE PROVIDED BY THE MAYNARD FIRE DEPARTMENT TO EVERSOURCE, ON SEPTEMBER 2, 2021 AT 16:14, THE MAYNARD FIRE DEPARTMENT DISPATCH RESOURCES TO 27 PARK ST MAYNARD, MA DUE TO AN ODOR CALL. THE MAYNARD FIRE DEPARTMENT ARRIVED ON SITE AT 16:17 TO A STRUCTURE FIRE. EVERSOURCE RECEIVED A CALL FROM THE MAYNARD FIRE DEPARTMENT AT 16:33 NOTIFYING EVERSOURCE OF THE SUBJECT STRUCTURE FIRE. EVERSOURCE COORDINATED WITH THE MAYNARD FIRE DEPARTMENT, MASSACHUSETTS STATE FIRE MARSHALL, AND STATE REGULATORY AGENCY ON SITE. THE SITUATION WAS MADE SAFE THROUGH A MAINLINE REPAIR ON SEPTEMBER 3, 2021. A SECTION OF THE MAIN WITH A COUPLING WAS SECURED AND DELIVERED TO THE MASSACHUSETTS MATERIAL RESEARCH FACILITY FOR 3RD PARTY ANALYSIS. NEITHER THE MAYNARD FIRE DEPARTMENT NOR THE STATE FIRE MARSHALL REPORTS HAVE BEEN RELEASED AT THIS TIME. PLEASE NOTE THE FOLLOWING AS IT RELATES TO THIS REPORT: PART A.4, A.12 THIS WAS THE TIME THE COMPANY COMMENCED A LEAK INVESTIGATION DURING WHICH GAS READINGS WERE DETECTED. THE FINAL FAILURE AND CAUSE OF THE INCIDENT IS STILL PENDING THE INVESTIGATION. PART A.21 THE COMPANY RESPONDED YES BASED UPON THE INITIAL NARRATIVE PROVIDED BY THE MAYNARD FIRE DEPARTMENT AND GAS READINGS FOUND IN NEAR PROXIMITY TO THE STRUCTURE FIRE. NEITHER THE FIRE DEPARTMENT NOR THE STATE FIRE MARSHAL HAVE ISSUED THEIR FINDINGS AS TO WHETHER RELEASED GAS CAUGHT FIRE. PART A.21.A THE TIME THE MAYNARD FIRE DEPARTMENT ARRIVED ON SITE TO A STRUCTURE FIRE. PART A.21.D PER "SECTION III. CONCLUSION" OF THE MASSACHUSETTS FIRE DISTRICT FOURTEEN'S REGIONAL FIRE INVESTIGATION TEAM FIRE ORIGIN AND CAUSE INVESTIGATION REPORT, ISSUED TO EVERSOURCE ON OCTOBER 13, 2021, "THE MOST PLAUSIBLE HYPOTHESIS IS THAT OF FUEL GAS EXPLOSION. IT IS BELIEVED TO BE AN ACCIDENTAL LOW ORDER FUEL GAS EXPLOSION CAUSED [THE] FIRE." PART A.7,A.21.C, D2.F VALUES DEFAULTED TO 1 AND 0. THE AMOUNT OF GAS RELEASE IS UNKNOWN AT THIS TIME. PART D.2.A THE PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE IS CURRENTLY BASED ON A PROPERTY ASSESSMENT PROVIDED BY THE FIRE DEPARTMENT AS WELL AS COSTS ASSOCIATED WITH LANDSCAPING, PAVING AND CONCRETE. PART D.2.B THE REPAIR COST INCLUDES THE REPAIR COSTS AS WELL AS THE FOLLOW UP LEAK SURVEY COSTS PART E.2 AN AVERAGE OPERATING PRESSURE WAS OBTAINED PRIOR TO THE INCIDENT. PART E.3.B THE MAIN WAS INSTALLED IN 1968 PRE-CODE. THE DATE FOR MAOP WAS DEFAULTED TO 7/1/1970 AS THAT WAS WHEN 192.619(C) WAS ESTABLISHED. PART E.5 THE DRIP REFERENCED IS A DRIP ODORIZER - Z9000 PART E.6 THE COMPANY TOOK MULTIPLE READINGS NONE OF WHICH REACHED OR EXCEEDED 0.15%. THE READING PROVIDED WAS THE FIRST READILY DETECTABLE LEVEL RECORDED AT 0.07. THIS REPORT FUNCTIONALITY ROUNDED THE NUMBER UP TO 0.1.
2024-05-31 11:04 | NO | YES | NO | 20210086 | 36295 | 2021-10-11 22:58 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2021-09-13 10:24 | EASTERN | YES | 2021 | 10015 W FORT ST | DETROIT | WAYNE | MI | 48209 | 42.2925 | -83.1426 | [7 empty] | YES | BAG AND STOP SYSTEM | 2021-09-13 10:24 | 1316565 | 1316953 | NATURAL GAS |  | 2.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-09-11 17:08 |  |  |  | 2021-09-11 17:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1913 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 20000 | 21234.98850183118 | 1000 | 1061.749425091559 | 1000000 | 1061749.425091559 | 1000000 | 1061749.425091559 | DAMAGE TO GREAT LAKES WATER AUTHORITY, ATT, COMAST, AND DTE ELECTRIC. | 2.75 | 6 | 5.27242524916943521594684385382059800664 | 0 | 0 | 2021006 | 906622.3680158215499601328903654485049834 | 2145800.8605352899084352159468438538206 | 4 | 0 | 7 | 0 | 0 | 7 | 4 | 2 | 2 | 2 | 192.619(A)(1) | 1970-01-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE UNEXPECTED GROUND MOVEMENT RESULTED IN TWO MAJOR HEAVE AREAS AND DAMAGE TO EXISTING BUILDINGS, PAVEMENT, AND UTILITY STRUCTURES INCLUDING DTE GAS INFRASTRUCTURE AT/NEAR THE INTERSECTION OF FORT STREET AND DEARBORN STREET IN DETROIT, MICHIGAN. INVESTIGATIONS THUS FAR CONFIRM THE GROUND FAILURE OCCURRED DUE TO A RELATIVELY RAPID LOADING OF A LAYER OF SOFT CLAYS BETWEEN 25 AND 40 FT BELOW THE GROUND SURFACE. | [154 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  |  |  |  | FRENAE F SMITH | MANAGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | 9/12/21 GROUND HEAVE 10015 WEST FORT & DEARBORN STREET: GROUND HEAVE IMPACTED THE FOLLOWING UTILITIES: GREAT LAKES WATER AUTHORITY (GLWA), ATT, COMCAST, DTE ELECTRIC, AND DTE GAS (6-INCH CI 2 PSI, 16-INCH CI 10PSI, 24-INCH STEEL 145PSI). THE INVESTIGATION IS ONGOING WITH A UNIFORMED ICS (CITY OF DETROIT, MDOT, GLWA, DTE GAS) AND NO CAUSE HAS BEEN DETERMINED YET. A SUPPLEMENTAL REPORT WILL BE FILED WITH MORE DETAILS AND FOLLOW-UP OF THIS EVENT. 1/24/2022 UPDATE ON THE INCIDENT CAUSE: ON SEPTEMBER 11, 2021, SIGNIFICANT, UNEXPECTED GROUND MOVEMENT RESULTED IN TWO MAJOR HEAVE AREAS AND DAMAGE TO EXISTING BUILDINGS, PAVEMENT, AND UTILITY STRUCTURES INCLUDING DTE GAS INFRASTRUCTURE AT/NEAR THE INTERSECTION OF FORT STREET AND DEARBORN STREET IN DETROIT, MICHIGAN. INVESTIGATIONS THUS FAR CONFIRM THE GROUND FAILURE OCCURRED DUE TO A RELATIVELY RAPID LOADING OF A LAYER OF SOFT CLAYS BETWEEN 25 AND 40 FT BELOW THE GROUND SURFACE. DTE UNDERSTANDS THAT THE RELATIVELY RAPID LOADING WAS CAUSED BY THE INCREASE IN HEIGHT AND WEIGHT OF A MILL SCALE STOCKPILE AT THE FORT IRON AND METAL FACILITY. THE GROUND FAILURE OCCURRED CONCENTRICALLY AROUND THE LARGE STOCKPILE OF MATERIAL LOCATED AT THE PROPERTY, A METAL SCRAP YARD OWNED AND OPERATED BY FORT IRON & METAL COMPANY. ON INFORMATION AND BELIEF, THE MILL SCALE MATERIAL WAS STOCKPILED TO SOME DEGREE AT THIS LOCATION BY FORT SINCE AT LEAST MAY 2019.
2024-05-31 11:04 | NO | YES | YES | 20210087 | 36110 | 2021-10-12 22:18 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2021-09-13 20:00 | MOUNTAIN | NO | 2021 | 777 CANYON ROAD | SANTA FE | SANTA FE | NM | 87501 | 35.6804 | -105.9243 | [5 empty] | YES |  |  |  | 2021-09-13 20:55 | 1316663 | 1317031 | NATURAL GAS |  | 3.8 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-09-13 10:50 | OPERATOR/CONTRACTOR |  | 2.3 | NO | 0 | 2021-09-13 10:50 | NO |  |  | 2021-09-13 09:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1971 | 1971 | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 0.75 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | OTHER | [8 empty] | AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED (55 PSIG) 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS TO ISOLATE AND PLUG THE SERVICE LINE FOR ABANDONMENT. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15.21 | 58 | 50.9667774086378737541528239202657807309 | 0 | 0 | 58 | 38.05647840531561461794019933554817275748 | 50.9667774086378737541528239202657807309 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 2016-10-27 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.5 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED (55 PSIG) 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS TO ISOLATE AND PLUG THE SERVICE LINE FOR ABANDONMENT. CREW FAILED TO FOLLOW PROCEDURE. |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ANDREA MARTINEZ | PIPELINE SAFETY MANAGEMENT SYSTEMS MANAGER | andrea.martinez@nmgco.com | 505-697-3518 |  | ANDREA MARTINEZ | andrea.martinez@nmgco.com | 505-427-6343 | TOM BULLARD | VP ENG-GAS MGMT-TECH SERVICES | 505-697-3599 | tom.bullard@nmgco.com | ON 9/13/2021 AT 10:50 AM, WHILE A CREW WAS ISOLATING AND RETIRING A SERVICE, AN IGNITION OCCURRED WHEN A NEW MEXICO GAS COMPANY (NMGC) CONSTRUCTION CREW CUT INTO A PRESSURIZED 3/4-INCH STEEL SERVICE WITH FOUR-WHEEL CUTTERS. THE THREE-MAN CREW (ACTING FOREMAN & 2 CREWMEN) ARRIVED TO RETIRE THE 3/4-INCH STEEL SERVICE AND DISCOVERED THAT NEITHER CREW MEMBER NOR THE ACTING FOREMAN HAD BROUGHT THE SAW TO CUT THE ASPHALT TO ACCESS THE SERVICE TEE CONNECTION AND PROPERLY ISOLATE THE SERVICE FOR RETIREMENT. THE CREW DECIDED TO CONTINUE THE JOB WITHOUT RETURNING TO THE SHOP TO GET THE SAW, AND INSTEAD DECIDED TO PROCEED TO MAKE THE REPAIR HOT WITH WHAT THEY DESCRIBED AS A CUT AND PLUG PROCEDURE. DURING THE CUT AND PLUG, AN IGNITION OCCURRED, AND ONE CREWMEN SUFFERED FIRST DEGREE BURNS, AND THE OTHER SUFFERED FIRST AND SECOND DEGREE BURNS. NEITHER THE ACTING FOREMAN NOR THE CREWMEN REPORTED THE IGNITION FIRE OR INJURIES UNTIL APPROXIMATELY 14:30 THAT AFTERNOON WHEN CREWMAN #2 CALLED THE SUPERVISOR AND REPORTED THAT A FLASH HAD OCCURRED, AND HE HAD BEEN INJURED. HE WAS TOLD TO SEEK MEDICAL TREATMENT. HE WAS SEEN BUT RELEASED BY CONCENTRA. LATER THAT AFTERNOON, ALL THREE MEMBERS OF THE CREW REPORTED TO THE OFFICE FOR INTERVIEWS AT THE SANTA FE OFFICE AT APPROXIMATELY 17:20 AND UPON DISCOVERY OF THE SEVERITY OF THEIR INJURIES, THE CREWMEN WERE SENT THE HOSPITAL BY THE AREA MANAGER. BOTH CREWMEN PROCEEDED TO THE HOSPITAL, CREWMAN #2 WAS ADMITTED TO THE HOSPITAL AS THE RESULT OF THIS INJURIES, AND CREWMAN #1 WAS TREATED AND RELEASED THAT EVENING. THE INCIDENT MET REPORTABLE CRITERIA WHEN CREWMAN #2 WAS ADMITTED TO THE HOSPITAL, AND COULD NOT BE TESTED FOR DRUG AND ALCOHOL DUE TO HIS ADMITTANCE TO THE HOSPITAL. THE ACTING FOREMAN AND CREWMAN #1 WERE DRUG AND ALCOHOL TESTED. GAS ODORANT TESTING WAS PERFORMED BY NM GAS AT 21:11. READINGS CONFIRMED PROPER ODORANT AT 0.53% GAS-IN-AIR. CREW FAILED TO FOLLOW PROCEDURES.
2024-05-31 11:04 | NO | YES | NO | 20210088 | 36125 | 2021-10-20 15:18 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2021-09-28 18:00 | EASTERN | YES | 2021 | LONG STREET | FORT BRAGG | CUMBERLAND | NC | 28310 | 35.1493 | -79.0092 | [6 empty] | YES |  |  | 2021-09-28 21:49 | 1318145 | 1318329 | NATURAL GAS |  | 5269 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-09-28 18:57 | NO |  |  | 2021-09-28 18:57 |  | YES | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1965 | UNKNOWN |  |  |  |  | 8 | API 5L GRADE B | UNKNOWN | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 200000 | 212349.8850183118 | 15000 | 15926.241376373385 | 0 | 0 |  | 4.5 | 23711 | 20835.7458471760797342192691029900332226 | 0 | 0 | 238711 | 112006.6513298799344518272425249169435216 | 249111.8722418612647342192691029900332226 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 148 | 150 | 192.619(A)(1) | 1965-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT BEING A 3RD PARTY DAMAGE AND THE CONTRACTOR DAMAGED THE LINE WHILE BORING. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | NO | [5 empty] | YES | 48 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY ANALYST | christopher.ransome@duke-energy.com | (704) 731-4680 |  |  |  |  | FARRIS BERRY | MANAGER PIPELINE SAFETY | (704) 731-4618 | farris.berry@duke-energy.com | A 3RD PARTY CONTRACTOR BORED INTO A HIGH PRESSURE 8" STEEL DISTRIBUTION LINE WHILE INSTALLING TELECOMMUNICATION LINES. DAMAGE RESULTED IN 1 COMMERCIAL OUTAGE. EXCAVATION WAS PERFORMED ON A EXPIRED LOCATE TICKET. THE CONTRACTOR WAS AWARE THAT THEY WERE WORKING NEAR HIGH PRESSURE LINE. BETWEEN 07/27-08/05/2021 PIEDMONT WAS ON SITE WHILE THE CONTRACTOR WORKED NEAR THE GAS LINE. THE CONTRACTOR WAS ADVISED TO CONTACT PIEDMONT FOR ADDITIONAL STANDBYS WHEN NEEDED.
2024-05-31 11:04 | NO | YES | YES | 20210089 | 36201 | 2021-10-26 22:19 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-09-27 13:25 | CENTRAL | YES | 2021 | 501 WILLOW BLVD. | WILLOW SPRINGS | COOK | IL | 60480 | 41.7326 | -87.8787 | [5 empty] | YES |  |  |  | 2021-09-27 19:07 | 1318029 | 1318263 | NATURAL GAS |  | 238.9 | 18.5 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2021-09-27 13:25 | ALLOWED TO BURN OUT |  | 238.9 | NO | 0 | 2021-09-27 13:25 |  |  |  | 2021-09-27 14:06 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2009 | 2008 |  |  |  |  | 2 | ASTM D2513 | UPONOR PIPE COMPANY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 29700 | 31533.9579252193023 | 8625 | 9157.588791414696375 | 2845 | 3020.677114385485355 | 0 | 0 |  | 5.49 | 1312 | 1152.90365448504983388704318936877076412 | 102 | 89.63122923588039867109634551495016611296 | 42584 | 19396.6085155775048646511627906976744186 | 44954.7587147404142625581395348837209302 | 5 | 0 | 2 | 0 | 1 | 2 | 1 | 21 | 22 | 25 | 192.619(A)(2) | 2009-02-16 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | PROBING DEVICE | POLE | YES | x2581427 | J.U.L.I.E. |  | CONTRACT LOCATOR | NO | YES | 15 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | lquezad@southernco.com | 6305142036 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 6305142036 | lquezad@southernco.com | BLUE PEAK TENTS, INC. PUT UP A TENT ON TUESDAY, 9/21/21. THEY UTILIZED EXISTING HOLES IN THE PARKING LOT PAVEMENT, AND MADE A NEW HOLES IN THE PARKWAY FOR THE STAKES THAT HOLD DOWN THE TENT. WHEN THE EMPLOYEES FROM BLUE PEAK TENTS, INC. CAME BACK ON MONDAY 9/27/21 TO REMOVE THE TENT, THEY USED A GASOLINE-OPERATED HYDRAULIC STAKE PULLING MACHINE TO REMOVE THE STAKES. WHILE IN THE PROCESS OF REMOVING ONE OF THE STAKES, THERE WAS IGNITION OF NATURAL GAS. TWO EMPLOYEES FROM BLUE PEAK TENTS, INC. WERE INJURED. ONE EMPLOYEE WAS TAKEN TO THE HOSPITAL AND RELEASED THE FOLLOWING DAY, AND THE OTHER REFUSED MEDICAL ATTENTION. AFTER STOPPING THE FLOW OF NATURAL GAS AND EXPOSING THE 2-INCH GAS MAIN, IT WAS REVEALED THAT A 1-INCH DIAMETER STAKE HAD PIERCED THE MAIN. PART G3, QUESTION 14: WHEN SELECTING "EXCAVATION PRACTICES NOT SUFFICIENT (OTHER)" FROM THE DROP DOWN MENU, THERE IS NO ADDITIONAL FIELD AVAILABLE TO PROVIDE AN EXPLANATION, AS REQUESTED BY PHMSA AID PERSONNEL; THEREFORE, THE EXPLANATION IS PROVIDED HERE IN PART H. EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) MEANS THE EXCAVATOR EXCAVATED OUTSIDE THE SCOPE OF THE ONE CALL TICKET.
2024-05-31 11:04 | NO | YES | NO | 20210090 | 35924 | 2021-10-27 16:43 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-09-26 17:15 | EASTERN | NO | 2021 | 13950 ANDORRA DR. | WOODBRIDGE | PRINCE WILLIAM | VA | 22193 | 38.6503 | -77.3277 | [5 empty] | YES |  |  |  | 2021-10-18 17:21 | 1319785 | 1319926 | NATURAL GAS |  | 47.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-09-26 17:15 | OPERATOR/CONTRACTOR |  | 47.5 | NO | 3 | 2021-09-26 17:40 |  |  |  | 2021-09-26 18:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | 1997 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | METER & REGULATOR - ALUMINUM | [9 empty] | OTHER | [8 empty] | VEHICULAR IMPACT | CLASS 4 LOCATION | 574600 | 610081.2196576098014 | 18000 | 19111.489651648062 | 1120 | 1189.15935610254608 | 383 | 406.650029810067097 | ADMIN FEE - $383.00 | 5.31 | 252 | 221.441860465116279069767441860465116279 | 0 | 0 | 594355 | 266679.3170681949048595813953488372093023 | 631009.9605556355928560697674418604651163 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 30 | 30 | 33 | 192.619(A)(2) | 1997-03-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE CAUSED BY VEHICULAR IMPACT AND NOT CONTROLLER(S) OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES | YES | CITATIONS: UNREASONABLE REFUSAL, EXPIRED REGISTRATION AND OPERATING AN UNINSURED VEHICLE | YES | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [118 empty] | YES | [23 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT COMPLIANCE | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | manager dot compliance | 703-750-5558 | SHANNON MALONEY | MANAGER DOT COMPLIANCE | 703-750-5558 | smaloney@washgas.com | ON 9/26/2021 AT APPROXIMATELY 17:15 HRS A VEHICLE TRAVELLING FROM HEREFORD RD TO SOUTHBOUND MINNEVILLE RD. LEFT THE ROADWAY AND TRAVELLED APPROXIMATELY 90 FEET AND STRUCK A METER SET ASSEMBLY SUPPLIED BY A 3/4" NATURAL GAS SERVICE, LOCATED AT 13950 ANDORRA DR. WOODBRIDGE, VA. PRINCE WILLIAM COUNTY FIRE BOARD NOTIFIED WASHINGTON GAS. WASHINGTON GAS RESPONDED AND LOCATED THE NATURAL GAS SERVICE AND OBTAINED GAS OFF BY SQUEEZE IN THE AREA OF THE FRONT YARD OF THE ABOVE ADDRESS. THE DRIVER WAS TRANSPORTED TO THE LOCAL HOSPITAL FOR PRECAUTIONARY MEASURES. THE NATURAL GAS SERVICE LINE WAS CAPPED OFF DUE TO STRUCTURAL DAMAGE TO THE RESIDENCE. THIS REPORT WAS DELAYED DUE TO THE UNKNOWN ESTIMATED PROPERTY DAMAGE AND SITE ACCESS LIMITATIONS.
2024-05-31 11:04 | NO | YES | NO | 20210091 | 37292 | 2021-10-29 09:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2021-10-06 10:08 | EASTERN | YES | 2021 | 3500 LAKELAND ROAD | GAINESVILLE | HALL | GA | 30506 | 34.369 | -83.8042 |  |  |  | YES | [5 empty] | 2021-10-06 12:12 | 1318790 | 1318985 | NATURAL GAS |  | 0.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-06 10:08 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2021-10-06 10:08 |  |  |  | 2021-10-06 10:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | TYPICAL METER SET | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.5 | 0.5 |  | CLASS 3 LOCATION | 140000 | 148644.91951281826 | 200 | 212.3498850183118 | 200 | 212.3498850183118 | 0 | 0 |  | 6.65 | 3 | 2.63621262458471760797342192691029900332 | 0 | 0 | 140403 | 62985.2577665341571800664451827242524917 | 149072.255495479468317607973421926910299 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 125 | 125 | 125 | 192.619(A)(2) | 1983-08-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A NATURAL GAS METER ON THE SIDE OF A RESIDENTIAL BUILDING RUPTURED WHEN LIGHTNING HIT AN UNKNOWN LOCATION AND TRAVELED ALONG THE CUSTOMER'S FUEL LINE AND ARCED ONTO THE GAS METER. AN ELBOW THAT WAS PART OF THE CUSTOMER'S FUEL LINE APPEARED TO BE IN CONTACT WITH THE GAS METER AT THE POINT WHERE THE DAMAGE OCCURRED. THE INCIDENT OCCURRED DURING A THUNDERSTORM, AND ACCORDING TO THE CUSTOMER, POWER TO THE HOME HAD GONE OUT AND CAME BACK ON SHORTLY BEFORE THE FIRE OCCURRED. THE ESCAPING NATURAL GAS IGNITED AS A RESULT OF THE ARC AND DAMAGED THE EXTERIOR OF THE RESIDENTIAL BUILDING LOCATED ADJACENT TO THE METER. ADDITIONAL NRC REPORT NUMBER 1318985 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2024-05-31 11:04 | NO | YES | NO | 20210093 | 36232 | 2021-11-05 16:02 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-07-21 11:18 | EASTERN | NO | 2021 | JOHN JAMES WAY & JOHN MARSHALL HWY | HAYMARKET | PRINCE WILLIAM | VA | 20169 | 38.8116 | -77.6458 |  | YES |  |  |  | YES |  |  |  | 2021-10-14 14:57 | 1319484 | 1319786 | NATURAL GAS |  | 2892 | 2508 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-21 11:20 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-07-21 11:19 | 2021-07-21 12:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2001 | 2000 |  |  |  |  | 12 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 84887 | 90128.723447747168833 | 5476 | 5814.139851801377084 | 0 | 0 |  | 3.96 | 11452 | 10063.3023255813953488372093023255813953 | 9932 | 8727.621262458471760797342192691029900332 | 111747 | 54567.7747261562867276212624584717607973 | 114733.7868875884130266345514950166112956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2001-02-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA DOES NOT HAVE ANY CONTROL OVER THIS PORTION OF THE SYSTEM. IT IS MONITORING ONLY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | UNKNOWN/OTHER | GRADING | YES | A118200220 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [143 empty] | YES | [26 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | (703)639-7825 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | (703)639-7825 | SHANNON B. MALONEY | MANAGER PIPELINE SAFETY COMPLIANCE QUALITY | (703)750-5558 | smaloney@washgas.com | ON 7/21/21 AT 1118 HRS, WASHINGTON GAS RECEIVED A REPORT OF A NATURAL GAS BROKEN LINE AT JOHN MARSHALL HIGHWAY AND TRADING SQUARE HAYMARKET, VA. 20169 FROM PRINCE WILLIAM COUNTY FIRE BOARD. 1119 HRS WASHINGTON GAS DISPATCHED FIELD OPS CREWS FOR RESPONSE. 1120 HRS WASHINGTON GAS RECEIVED AN ALARM ON SCADA OF PRESSURE DROPPING AND PRESSURE OPERATIONS CREWS WERE DISPATCHED. THE FIRST FIELD OPS CREW ARRIVED AT 1200 HRS AND WORKED WITH THE FIRE DEPARTMENT TO SECURE THE SCENE AND RELAY INFORMATION TO WASHINGTON GAS DISPATCH FOR ADDITIONAL SUPPORT. THE FIRST ARRIVING CREWS BEGAN TO LOCATE THE CLOSEST DISTRIBUTION VALVE. THE AREA OF THIS VALVE #1 HAD BEEN RECENTLY REGRADED AND HAD EXTENSIVE VEGETATION GROWTH. THE CREWS LOCATED A BROKEN PORTION OF A LINE MARKER (IT HAD RECENTLY BEEN BUSHED HOGGED AND BROKEN OFF) AND FOUND THE VALVE COVER WAS FOUND UNDER 3-4" OF SOIL. CUSTOMER IMPACT THROUGH THE UTILIZATION OF CRITICAL VALVES TO STOP GAS, AND AREA OF THE DAMAGE (NATURAL GAS VENTING INTO THE ATMOSPHERE IN AN OPEN LOT AND THE CLOSEST STRUCTURE APPROXIMATELY 300FT. AWAY) WERE FACTORS CONSIDERED AS PART OF THE RESPONSE PLANNING. AT APPROXIMATELY 1445 HRS WASHINGTON GAS PRESSURE OPS BEGAN TO CONTROL THE FLOW OF NATURAL GAS, REDUCING THE PRESSURE TO 5PSIG BY USE OF VALVE #1. ONCE THE PRESSURE WAS STABILIZED CREWS BEGAN TO EXCAVATE UPSTREAM AND DOWNSTREAM OF THE BREAK AREA TO INSTALL (2) 2" BYPASSES. THESE BYPASSES WERE INSTALLED TO MAINTAIN THE DOWNSTREAM CUSTOMERS AND TO USE THE EXPOSED 12' PLASTIC TO DOUBLE SQUEEZE THE PIPE. GAS WAS SQUEEZED OFF AT 0400 HRS ON 7/22/2021. FURTHER INVESTIGATION AND REPAIRS COMMENCED. CURRENT VALVE ASSIGNMENTS WERE REVALUATED NETTING AN INCREASE OF CRITICAL VALES ON THE EXISTING INFRASTRUCTURE.
2024-05-31 11:04 | NO | YES | NO | 20210094 | 38468 | 2021-11-09 15:01 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-10-17 00:15 | PACIFIC | YES | 2021 | MARKET CIRCLE & HWY 183 | SALINAS | MONTEREY | CA | 93901 | 36.6863 | -121.6773 | [5 empty] | YES |  |  |  | 2021-10-17 04:37 | 1319672 | 1319741 | NATURAL GAS |  | 5485 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-10-16 17:07 | YES | OPERATOR | 2021-10-16 17:19 | 2021-10-16 18:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 4 | STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DIG IN | CLASS 1 LOCATION | 0 | 0 | 90860 | 96470.55276381905074 | 3785 | 4018.721573971550815 | 0 | 0 | 0 | 3 | 164550 | 144596.2624584717607973421926910299003322 | 0 | 0 | 259195 | 150426.4992511405764545182724252491694352 | 245085.5367962623623523421926910299003322 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 4 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ROSA DUENAS |  | r1dj@pge.com | [5 empty] | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-328-5776 | gsr8@pge.com | PG&E WAS NOTIFIED OF A DIG IN AT MARKET CIRCLE AND HWY 183 IN SALINAS, CA. FARM OPERATOR DUG AND DAMAGED TWO PG&E SUBSURFACE GAS FACILITIES: ONE 4-INCH STEEL DISTRIBUTION PIPE AND ONE 1 1/4-INCH STEEL SERVICE PIPE WITH MAOPS OF 60 PSI. PG&E CREW ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS ON 10/17 AT 02:44 HOURS. THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA REPORTED. POLICE AND FIRE DEPARTMENT WERE ONSITE. THIS INCIDENT WAS REPORTED TO THE DOT (#1319672) AND CPUC DUE TO THE RELEASE OF GAS ESTIMATED TO BE GREATER THAN 3MMCF.
2024-05-31 11:04 | NO | NO | NO | 20210095 | 36213 | 2021-11-16 21:13 | SUPPLEMENTAL FINAL | 1720 | BRENHAM UTILITY, CITY OF | 200 W VULCAN ST | BRENHAM | TX | 77834 | 2021-10-22 09:20 | CENTRAL | NO | 2021 | HWY 290 E @ S CHAPPELL HILL ST | BRENHAM | WASHINGTON | TX | 77833 | 30.142 | -96.3821 | YES |  |  |  |  | YES |  |  |  | 2021-10-22 11:35 | 1320155 | 1320663 | NATURAL GAS |  | 250 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-22 09:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | NO | 0 | 2021-10-22 09:20 | YES | OPERATOR | 2021-10-22 09:20 | 2021-10-22 09:27 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1994 | 1992 |  |  |  |  | 6 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2904 | 3083.320330465887336 | 583 | 618.999914828378897 | 2025 | 2150.042585810406975 | COST OF BRENHAM FD ALONG WITH 3 OTHER FIRE DEPARTMENTS MUTUAL AID | 8.05 | 2013 | 1768.898671096345514950166112956810631229 | 0 | 0 | 7525 | 3793.49954386494256058471760797342192691 | 7621.261502201018722950166112956810631229 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 28 | 28 | 60 | 192.619(A)(4) | 1980-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE CHANGES WAS FROM THE DAMAGE DUE TO THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | 2178065546 | TEXAS 811 IS THE ONLY ONE-CALL |  | UTILITY OWNER | YES | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ANDE BOSTAIN | GAS SUPERINTINDENT | abostain@cityofbrenham.org | 19793377416 | 19793377419 | ANDE BOSTAIN | abostain@cityofbrenham.org | 19794511772 | ANDE BOSTAIN | GAS SUPERINTINDENT | 19794511772 | abostain@cityofbrenham.org | THE EXCAVATOR WAS WORKING ON THE ACCESS ROAD FOR THE ENTRANCE TO THE NEW SHOPPING CENTER. THE PROJECT HAS BEEN ONGOING SINCE FEBRUARY. THEY HAD NOT STARTED ON THIS SECTION UNTIL THE LAST COUPLE OF MONTHS. AFTER REMOVING AN OLD DRIVEWAY THAT EXISTED ALONG THE ROAD THEY HAD CHANGED THE GRADE OF THE AREA BY REMOVING A PORTION OF THE DIRT THAT COVERED THE 6" MAIN. THERE HAD BEEN A LOCATE DONE FOR A FIBER CONTRACTOR THAT WAS BASICALLY ALONG THE SAME PATH OF THE ROAD CONTRACTORS WORKSITE. THE MAIN WAS FLAGGED AND MARKED CORRECTLY ALONG THE PATH. ALL THE MARKINGS WERE PRESENT WHEN BURTS CONSTRUCTION REMOVED SOME MORE MATERIAL WITH A DOZER AND THEN BROUGHT IN A RECLAIMER TO MIX THE DIRT AND ROAD BASE FOR STABILIZATION. WHEN THE MIXER STARTED TO TILL THE DIRT IT HIT THE LINE DAMAGING IT AND CAUSING AN IGNITION. THE EQUIPMENT OPERATOR SHUT OFF THE MACHINE AND JUMPED OFF BUT BUT DID GET HIS RIGHT ARM BURNT TO THE POINT HE WAS TAKEN TO THE HOSPITAL BY HELICOPTER. THE RECLAIMER WAS ENGULFED IN FLAMES AND COMPLETELY DESTROYED. WE CLOSED A VALVE OFF ON THE WEST SIDE OF THE DAMAGE AND THEN DUG UP THE 6" AND SQUEEZED IT OFF TO STOP THE FLOW OF GAS ON THE EAST SIDE. THE FIRE DEPARTMENT PUT THE FIRE OUT. I CONTACTED THE RRC BY PHONE AND ALSO THE NRC. THE RRC SENT INVESTIGATORS OUT TO ACCESS THE SCENE AND INVESTIGATE IT. I CHECKED ON THE EMPLOYEE WHO WAS INJURED AND HIS SUPERVISOR SAID HE WAS RELEASED FROM THE HOSPITAL THAT SAME NIGHT WITH SEVERE BURNS ON HIS RIGHT ARM. THE DAMAGED RECLAIMER WAS REMOVED FROM THE SPOT ON THE 25TH OF OCTOBER 2021. ON TUESDAY THE 26TH OCTOBER 2021 WE DUG UP, LOWERED AND REPAIRED THE LINE WAS DAMAGED WITH THE RRC INSPECTORS ON SITE. ON THURSDAY THE GAS DEPARTMENT EXPOSED THE GAS MAIN ALONG THE AREA IN 4 DIFFERENT SPOTS VERIFYING ITS LOCATION AND DEPTH. ALL WERE ALREADY CORRECTLY MARKED BUT THESE AREAS HAD NOT HAD DIRT REMOVED FROM THE TOP OF THEM. THE CITY OF BRENHAM GAS DEPOARTMENT WILL CONTINUE TO MARK OUR FACILITIES IN ACCORDANCE WITH THE TEXAS AMINISTRATIVE CODE TITLE 16 PART 1 CHAPTER 18 FOR UNDERGROUND PIPELINE DAMAGE PREVENTION. WE HAVE PUT IN PLACE IN OUR PLAN REVIEW FOR DEVELOPEMENT SERVICES UNDER THE GAS DEPARTMENT COMMENTS SECTION VERBIAGE STATING THAT THE BUILDER, CONTRACTOR, DEVELOPER AND/OR EXCAVATORS THAT TAKE PART IN THESE WORK PROJECTS WILL MAINTAIN CONTACT WITH THE CITY OF BRENHAM AND BE AWARE OF THEIR RESPONSIBILITY OF PROTECTION OF EXISTING CITY UNTILITIES ON THESE SITES DURING THE DURATION OF THE PROJECT.
2024-05-31 11:04 | NO | YES | YES | 20210096 | 36361 | 2021-11-17 17:43 | SUPPLEMENTAL FINAL | 22364 | WEST BATON ROUGE PARISH NATURAL GAS SYSTEM | 880 N ALEXANDER, P.O. BOX 807 | PORT ALLEN | LA | 70767 | 2021-11-01 17:00 | CENTRAL | YES | 2021 | 4826 WOODLAWN | ADDIS | WEST BATON ROUGE | LA | 70710 | 30.38 | -91.2778 |  | YES | [7 empty] | 2021-11-01 16:16 | 1320955 | 1321074 | NATURAL GAS |  | 0.23 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-11-01 11:30 | ALLOWED TO BURN OUT |  | 0.23 | NO | 0 | 2021-11-01 11:30 | YES | OPERATOR | 2021-11-01 17:30 | 2021-11-01 11:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2021 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | YES | NO | 0.75 | 2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 250 | 265.43735627288975 | 2000 | 2123.498850183118 | 0 | 0 |  | 5.59 | 1 | 0.8787375415282392026578073089700996677741 | 0 | 0 | 2251 | 1010.003731563952493355481727574750830565 | 2389.814943997535989202657807308970099668 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 2019-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [34 empty] | YES |  |  |  | YES | [10 empty] | ADRIAN GENRE |  | adrian.genre@wbrcouncil.org | 2253362406 |  |  |  |  | ADRIAN GENRE |  | 2253362406 | adrian.genre@wbrcouncil.org | GAS CREW WAS INSTALLING A NEW 3/4 INCH PE SERVICE LINE WITH A PLASTIC BOLT ON SERVICE TEE ON A 4" PE MAIN. THE SERVICE LINE BEING INSTALLED WITH AN EFV WAS CONNECTED TO THE SERVICE TEE AT THE MAIN. THE TAP CUTTER ON THE SERVICE TEE WAS SCREWED CLOCKWISE TO TAP INTO THE MAIN TO PROVIDE GAS TO THE NEW CUSTOMER. AFTER TAP WAS COMPLETED AND THE GAS HAD BEEN INTRODUCED INTO THE SERVICE LINE FOR APPROXIMATELY 30 MINUTES, THE TAP SIDE OF THE EFV, THE FITTING (NUT THAT FASTENS THE EFV TO THE TAP) BLEW OFF. THE EMPLOYEE THAT WAS INJURED JUMPED INTO THE HOLE AND ATTEMPTED TO SCREW THE TAP CUTTER BACK DOWN INTO THE MAIN TO STOP GAS FLOW. WHILE TURNING THE TAP, APPROXIMATELY 2 ROUNDS, THE GAS IGNITED. THE INDIVIDUAL JUMPED OUT OF THE HOLE AND A CREW MEMBER WENT TO A CLOSE BY MAIN LINE VALVE TO TURN OFF THE GAS FEEDING THE DAMAGED SERVICE LINE. THIS MAIN LINE VALVE SHUT OFF GAS DOWNSTREAM OF THE CLOSED VALVE. THERE WAS A WATER SERVICE LOCATED IN THE SAME EXCAVATION THAT MELTED AND THE WATER EXTINGUISHED THE FIRE. THE MAIN LINE VALVE WAS TURNED OFF ELIMINATING THE GAS FLOW.
2024-05-31 11:04 | NO | YES | YES | 20210097 | 36095 | 2021-11-19 15:20 | SUPPLEMENTAL FINAL | 2392 | CITIZENS GAS & COKE UTILITY | 2020 N MERIDIAN ST | INDIANAPOLIS | IN | 46202 | 2021-10-22 09:04 | EASTERN | YES | 2021 | 558 N RYBOLT AVE | INDIANAPOLIS | MARION | IN | 46222 | 39.7749 | -86.2324 |  | YES | [7 empty] | 2021-10-22 10:13 | 1320137 | 132033 & 132538 | NATURAL GAS |  | 46000 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2021-10-22 08:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 44000 | YES | 0 | 2021-10-22 08:42 |  |  |  | 2021-10-22 09:04 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1993 | 1993 | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.093 |  | 2406 | LEAK |  |  | OTHER | MELT HOLE FROM CUST. FIRE PIT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 6500 | 6901.3712630951335 | 22700 | 24101.7119495783893 | 0 | 0 |  | 4.6 | 211600 | 185940.863787375415282392026578073089701 | 0 | 0 | 240800 | 151939.6202251190716199335548172757475083 | 216943.947000048938082392026578073089701 | 0 | 0 | 6 | 3 | 1 | 1 | 0 | 26.5 | 27 | 30 | 192.619(C) | 1993-06-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION INDICATED THE CAUSE OF THE INCIDENT WAS DUE TO A CUSTOMER'S OUTDOOR FIRE PIT MELTING A HOLE IN THE PLASTIC NATURAL GAS SERVICE LINE. SCADA HAS NO CONTROL ON THIS DISTRIBUTION SERVICE LINE FAILURE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HEAT FROM THE CUSTOMER'S OUTDOOR FIRE PIT DAMAGED THE NATURAL GAS SERVICE LINE. | [154 empty] | BEN WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | bwarren@citizensenergygroup.com | 3176912514 |  |  |  |  | BEN WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | 3176912514 | bwarren@citizensenergygroup.com | THE FINDINGS OF THE INVESTIGATION BY THE FIRE DEPARTMENT REVEALED THE HOMEOWNER HAD INSTALLED A FIRE PIT DIRECTLY OVER THE NATURAL GAS DISTRIBUTION SERVICE LINE. THE NATURAL GAS SERVICE LINE IS A 1/2" PLASTIC DISTRIBUTION SERVICE LINE INSERTED INSIDE AN ABANDON 1 1/4" STEEL LINE. THE HEAT FROM THE FIRE, WITHIN THE FIREPIT, HEATED THE 1 1/4" STEEL CASING LINE THEREFORE CREATING A HOLE IN THE 1/2" PLASTIC SERVICE LINE THAT WAS INSERTED WITHIN THE 1 1/4" STEEL CASING LINE. THIS HOLE ALLOWED GAS TO ESCAPE INSIDE THE CASING AND TRAVEL TO THE RESIDENTIAL HOME IT WAS SERVING, 558 N. RYBOLT AVE. ACCUMULATION OF THE NATURAL GAS OCCURRED WITHIN THE HOME AND WAS IGNITED BY THE CUSTOMER WHEN HE TRIED TO LIGHT A CIGARETTE. CEG'S OWN INVESTIGATION FINDINGS WERE CONSISTENT WITH THE FIRE DEPARTMENT'S.
2024-05-31 11:04 | NO | YES | NO | 20210098 | 36039 | 2021-11-23 19:13 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2021-10-28 12:50 | PACIFIC | YES | 2021 | 6997 W CHRISTINE ST | RATHDRUM | KOOTENAI | ID | 83858 | 47.8134 | -116.8803 | [5 empty] | YES |  |  |  | 2021-10-28 14:52 | 1320698 | 1320844 | NATURAL GAS |  | 110 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-28 12:46 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8 | YES | 38 | 2021-10-28 12:46 | YES | OPERATOR | 2021-10-28 12:48 | 2021-10-28 10:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | 2015 |  |  |  |  | 2 | ASTM D2513 | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 750000 | 796312.06881866925 | 27619 | 29324.457371603768021 | 0 | 0 | 0 | 0 |  | 5.27 | 580 | 509.667774086378737541528239202657807309 | 0 | 0 | 778199 | 349219.6136725637229281794019933554817276 | 826146.1939643593967585415282392026578073 | 0 | 0 | 1 | 1 | 1 | 15 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 2016-04-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3.8 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2021440198 | PASSWORD |  | CONTRACT LOCATOR | YES | YES | 2 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BRIAN SCHULTZ | PIPELINE INTEGRITY PROGRAM MANAGER | brian.schultz@avistacorp.com | 509-495-2162 |  | JOSH FORT | josh.fort@avistacorp.com | 509-495-2656 | VERN MALENSKY | MANAGER NATURAL GAS INTEGRITY AND COMPLIANCE | 509-495-2706 | vern.malensky@avistacorp.com | AT APPROXIMATELY 10:00 A.M. PDT ON OCTOBER 28, 2021, PG CONTRACTORS, A THIRD-PARTY CONTRACTOR, WAS INSTALLING TELECOMMUNICATIONS INFRASTRUCTURE USING A HORIZONTAL DIRECTIONAL DRILL WHEN THEY SEVERED A 2" POLYETHYLENE (PE) MAIN AT THE INTERSECTION OF CHRISTINE STREET AND BEECHWOOD STREET IN FRONT OF 6997 W CHRISTINE ST., RATHDRUM, IDAHO. THE PE PIPE OPERATED AT A PRESSURE OF APPROXIMATELY 55 PSIG WITH AN MAOP OF 60 PSIG, WAS AT A DEPTH OF 36 INCHES, AND LOCATE MARKS WERE PRESENT AND ACCURATE. AVISTA WAS NOTIFIED AT 10:13 A.M. PDT AND WAS ON SITE AT 10:20 A.M. PDT. THE NORTHERN LAKES FIRE DISTRICT RESPONDED AND EVACUATED 3 NEARBY RESIDENCES AT 6971, 6997 AND 7025 W CHRISTINE STREET. THE LOCATION OF THE DAMAGE REQUIRED SQUEEZING THE 2" MAIN IN THREE LOCATIONS AS IT WAS CLOSE TO A TEE. THE SQUEEZES WERE COMPLETE AT 11:43 A.M. PDT TO CONTROL THE FLOW OF GAS. THE FIRE DEPARTMENT LEFT ONCE THE SCENE WAS SECURE. UNDERGROUND BARHOLE READINGS WERE TAKEN IN FRONT OF THE THREE EVACUATED HOUSES AND SHOWED 0 PERCENT LEL. INSIDE GAS READINGS WERE TAKEN AT 6997 W CHRISTINE STREET AT APPROXIMATELY 12:10 P.M. PDT AND SHOWED READINGS BETWEEN 10% AND 70% LEL. THE GAS SERVICEMAN EXITED THE HOUSE AND LEFT THE DOORS OPEN TO AIR OUT THE HOUSE. AT APPROXIMATELY 12:30 P.M. PDT THE HOMEOWNERS AT 7025 W CHRISTINE STREET CAME HOME AND REQUESTED TO ENTER THEIR HOUSE. A GAS SERVICEMAN CHECKED EACH ROOM OF THE HOUSE WITH A COMBUSTIBLE GAS INDICATOR AND FOUND READINGS OF 0% LEL, SO THE GAS SERVICEMAN CLEARED THE HOUSE FOR THE HOMEOWNERS TO REENTER. SHORTLY THEREAFTER, THE HOMEOWNERS AT 6997 W CHRISTINE STREET REQUESTED TO GET BACK INTO THEIR HOUSE. THE GAS SERVICEMAN CHECKED EACH ROOM WITH A COMBUSTIBLE GAS INDICATOR, WHICH NOW READ 0% LEL AND HE ALLOWED THE HOMEOWNERS BACK IN THEIR HOUSE. AT THIS TIME, THE GAS AND ELECTRICITY WERE STILL SHUT OFF TO THE HOUSE AND THE ELECTRIC METER HAD TO BE RE-INSTALLED. AFTER TURNING THE ELECTRICITY BACK ON THE HOMEOWNER REPORTED POPPING NOISES COMING FROM THE FURNACE. THE GAS SERVICEMAN CHECKED NEAR THE FURNACE AND FOUND 0% LEL AND DECIDED TO TURN THE FURNACE OFF AT THE THERMOSTAT. WHILE ENTERING THE HOUSE FROM THE GARAGE, THE GAS SERVICEMAN SAW A RED GLOW ABOVE HIS HEAD WHICH WAS AN IGNITION OF GAS AT APPROXIMATELY 12:46 P.M. PDT. THE GAS SERVICEMAN EXITED THROUGH THE OPEN GARAGE DOOR AND THE MALE HOMEOWNER EXITED THROUGH THE REAR GARAGE ACCESS DOOR. INDIVIDUALS ON SCENE THEN HELPED TO GET THE FEMALE HOMEOWNER OUT OF THE UPSTAIRS OF THE HOUSE THROUGH A WINDOW. SHORTLY THEREAFTER THE BUILDING WAS CONSUMED BY FLAMES. OPERATOR PERSONNEL ON SCENE CALLED 911 IMMEDIATELY AFTER THE GAS IGNITED AND THE NORTHERN LAKES FIRE DISTRICT WAS ON SCENE AT APPROXIMATELY 12:57 P.M. PDT. THE FEMALE HOMEOWNER WAS ASSESSED BY EMTS ON SITE AND THE MALE HOMEOWNER WENT TO THE HOSPITAL TO BE TREATED FOR SECOND DEGREE BURNS ON HIS FOREARM BUT WAS NOT ADMITTED. PRELIMINARY INVESTIGATION SUGGESTS THAT THERE WAS A POCKET OF GAS INSIDE THE HOUSE IN A LOCATION THAT COULD NOT BE DETECTED BY THE GAS SERVICEMAN'S INSTRUMENT. IT WAS THAT POCKET OF GAS THAT IGNITED CAUSING THE FIRE. THE BUILDING WAS DEEMED A TOTAL LOSS WITH A VALUE EXCEEDING $122,000 RESULTING IN THIS INCIDENT BEING REPORTABLE. AVISTA DENIES LIABILITY FOR DAMAGES AND INJURIES ASSOCIATED WITH THIS INCIDENT.
2024-05-31 11:04 | NO | NO | NO | 20210099 | 37698 | 2021-11-24 21:01 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-10-24 21:35 | CENTRAL | YES | 2021 | 1146 N 32ND ROAD | OTTAWA | LASALLE | IL | 61373 | 41.3961 | -88.9442 |  |  |  | YES | [5 empty] | 2021-10-25 01:08 | 1320321 | 1320522 | NATURAL GAS |  | 3.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-10-24 21:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.75 | NO | 0 | 2021-10-24 22:18 |  |  |  | 2021-10-24 23:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2020 | 2020 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | BACK OF METER BLOW OUT DUE TO ELECTRICAL DISCHARGE | CLASS 1 LOCATION | 75000 | 79631.206881866925 | 150 | 159.26241376373385 | 500 | 530.8747125457795 | 0 | 0 |  | 6.53 | 24 | 21.08970099667774086378737541528239202658 | 0 | 0 | 75674 | 33952.2563235684235405315614617940199336 | 80342.433709173116090863787375415282392 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0.25 | 0.25 | 0.3 | 192.619(A)(1) | 2020-10-16 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [186 empty] | YES | [31 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | [5 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | ON THE DATE OF THE INCIDENT, THERE WERE THUNDERSTORMS AND HIGH WINDS. IT IS BELIEVED THAT A LIGHTNING STRIKE DAMAGED A NEARBY POWER LINE. THE STATE FIRE MARSHAL INVESTIGATED THIS FIRE. THEIR INVESTIGATION SHOWS THAT CORNBELT ELECTRIC WAS AT THIS PROPERTY ABOUT ONE HOUR BEFORE THE FIRE WORKING ON A DROPPED NEUTRAL LINE. CORNBELT MADE THE REPAIRS AND MOVED ON. THE ELECTRIC AND GAS ENTER THE BUILDING IN THE SAME AREA. FIRE MARSHAL STATED THERE WERE TWO THEORIES. 1. THE DAMAGED POWER LINE MAY HAVE STARTED THE FIRE AND DROPDOWN MAY HAVE DAMAGED THE METER SET AND CAUSED THE GAS RELEASE. 2. LIGHTNING MAY HAVE STRUCK THE METER SET AND BEGAN THE FIRE. A SUB SURFACE LEAKAGE SURVEY WAS CONDUCTED OVER THE MAIN AND SERVICE LINE AND NO LEAKS WERE FOUND BELOW GRADE. THIS SERVICE LINE HAS A PROPERTY LINE REGULATOR. A GRADE 3 LEAK WAS FOUND ON THE ABOVEGROUND PROPERTY LINE REGULATOR PIPING. THIS MINOR LEAK DID NOT CAUSE OR CONTRIBUTE TO THE FIRE. NOTE: RECORDS INDICATE THAT THE SERVICE LINE WAS INSTALLED IN 1969, BUT THE METER SET WAS COMPLETELY REPLACED ON 10-16-20. SUPPLEMENTAL/FINAL REPORT SUBMITTED PER PHMSA AID REQUEST TO UPDATE THE INFORMATION IN A-4.
2024-05-31 11:04 | NO | NO | NO | 20210100 | 36071 | 2021-12-02 13:17 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-11-03 08:35 | EASTERN | NO | 2021 | DORMANSVILLE BLVD & CHURCH RD. | UPPER MARLBORO | PRINCE GEORGES | MD | 20774 | 38.8831 | -76.7594 | YES | YES |  |  |  | YES |  |  |  | 2021-11-03 13:54 | 1321098 | 1321235 | NATURAL GAS |  | 1150 | 2587 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-03 08:39 | YES | OPERATOR | 2021-11-03 08:43 | 2021-11-03 08:49 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 108 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2006 | 2006 |  |  |  |  | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 235 | 249.511114896516365 | 10018 | 10636.605740567238062 | 383 | 406.650029810067097 | ADMIN FEE | 3.96 | 4554 | 4001.770764119601328903654485049833887043 | 10245 | 9002.666112956810631229235880398671096346 | 25435 | 14481.6054948145792757740863787375415282 | 24297.2037623502334841328903654485049833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 55 | 192.619(A)(2) | 2006-09-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" PL NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 21845297 | MARYLAND 811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RICHARD FITZPATRICK | SUPERVISOR PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | smaloney@washgas.com | 7037505558 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON NOVEMBER 3, 2021, WASHINGTON GAS WAS NOTIFIED OF A DAMAGED FACILITY NEAR DORMANSVILLE BLVD. AND CHURCH RD. UPPER MARLBORO MD. WASHINGTON GAS DISPATCHED CREWS IN RESPONSE TO THE BROKEN LINE. ONCE ARRIVED, THE DAMAGED WAS DETERMINED TO BE A TWO-WAY FEED 8" PLASTIC MAIN. THE MAIN WAS STRUCK ON A CONSTRUCTION SITE BY A BACKHOE WITH A 48" BUCKET. NO TRAFFIC WAS AFFECTED DUE TO NEW CULVERT AND BRIDGE WAS BEING CONSTRUCTED. THE GAS MAIN WAS APPROXIMATELY 10' UNDER A CREEK BED KNOWN AS BLACK BRANCH HAD BEEN PREVIOUSLY BEEN DIVERTED DUE TO THE CONSTRUCTION OF A NEW BRIDGE. THE EXCAVATOR PLEASANTS CONSTRUCTION DID HAVE A VALID MISS UTILITY TICKET BUT FAILED TO MAINTAIN MARKS IN THE EXCAVATION AREA. WASHINGTON GAS EXCAVATED ON EACH SIDE OF THE DAMAGED FACILITY AND PERFORMED A SQEEZE OFF. THE WORK AREA WAS MADE SAFE TO ENTER TO COMMENCE REPAIRS.
2024-05-31 11:04 | NO | YES | NO | 20210101 | 36147 | 2021-12-16 14:01 | SUPPLEMENTAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 OLD TAYLOR ROAD MAIL CODE J48 | CAYCE | SC | 29033 | 2021-11-22 12:09 | EASTERN | NO | 2021 | 301 EL BETHEL ROAD | CONWAY | HORRY | SC | 29568 | 33.8613 | -79.092 | YES | [8 empty] | 2021-11-22 18:25 | 1322715 | 1322830 | NATURAL GAS |  | 162.34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-22 12:09 | YES | OPERATOR | 2021-11-22 17:31 | 2021-11-22 12:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 204 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2014 | 2014 |  |  |  |  | 6 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5.5 | 5.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 156189 | 165833.580955625508651 | 0 | 0 | 0 | 0 | N/A | 8.64 | 1403 | 1232.868770764119601328903654485049833887 | 0 | 0 | 157592 | 70986.7908735354669197408637873754152824 | 167066.4497263896282523289036544850498339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 2014-07-14 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE CHANGE DUE TO THE LEAK WAS NOT SUBSTANTIAL ENOUGH TO BE OBSERVED BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | 2111022187 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JERAMY FREE | ENGINEER III - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 803-260-3602 |  | DONALD WATFORD | donald.watford@dominionenergy.com | 843-745-7984 | CINDY OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-817-9245 | cynthia.ostrander@dominionenergy.com | SUPPLEMENTAL REPORT CREATED TO CHANGE A4 TO 12:09 P.M. WHEN THE DAMAGE WAS DONE. ON NOVEMBER 22, 2021, AT APPROXIMATELY 12:09 P.M., DOMINION ENERGY SOUTH CAROLINA (DESC) GAS OPERATIONS RESPONDED TO A NOTIFICATION FROM A THIRD PARTY CONTRACTOR CONCERNING A NATURAL GAS LEAK NEAR 301 EL BETHEL ROAD IN CONWAY, SC. THE CONTRACTOR WAS PERFORMING A DIRECTIONAL DRILLING OPERATION TO INSTALL A WATER LINE PARALLEL TO THE DESC 6-INCH PLASTIC GAS MAIN. THE BORING CONTRACTOR HAD PROPERLY NOTIFIED SC811 AND THE GAS FACILITIES WERE ACCURATELY LOCATED AND MARKED. THE CONTRACTOR PERFORMED THE BORE, AND WHILE PERFORMING THE PULL BACK, THE BORING EQUIPMENT DRIFTED OFF THE ORIGINAL BORE PATH INTO THE NATURAL GAS LINE, CAUSING A LEAK. DESC OPERATIONS CREWS WERE ABLE TO ISOLATE THE LEAK AT APPROXIMATELY BY OPERATING TWO ISOLATION VALVES. NO CUSTOMERS' GAS SERVICE WAS LOST AND THE LEAK GARNERED AND NO MEDIA COVERAGE. THE DAMAGED GAS MAIN REQUIRED EXTENSIVE REPAIRS AND A NEW GAS MAIN WAS INSTALLED. THE TOTAL COST OF THE REPAIR WAS APPROXIMATELY $156,189, WHICH EXCEEDED THE REPORTABLE THRESHOLD OF $122,000. LDF: 322718
2024-05-31 11:04 | NO | NO | NO | 20210102 | 36161 | 2021-12-20 19:51 | ORIGINAL FINAL | 39257 | INTERIOR GAS UTILITY | 2525 PHILLIPS FIELD ROAD | FAIRBANKS | AK | 99709 | 2021-11-21 17:10 | ALASKA | NO | 2021 | 2942 TRIA ROAD | FAIRBANKS | FAIRBANKS NORTH STAR BOROUGH | AK | 99709 | 64.8038 | -147.7973 | YES |  |  | YES | [5 empty] | 2021-11-22 10:10 | 1322689 | 1322785 | NATURAL GAS |  | 559 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-11-21 17:14 | NO |  |  | 2021-11-21 17:44 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2019 | UNKNOWN |  |  |  |  | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | RUPTURE |  |  |  |  | OTHER | SPIRAL | 120 | 0.5 |  | CLASS 2 LOCATION | 10000 | 10617.49425091559 | 32000 | 33975.981602929888 | 25000 | 26543.735627288975 | 0 | 0 |  | 11.704 | 6543 | 5749.579734219269102990033222591362126246 | 0 | 0 | 73543 | 34349.2925499449685249169435215946843854 | 76886.7912153537221029900332225913621262 | 91 | 0 | 48 | 0 | 0 | 144 | 91 | 62 | 55 | 60 | 192.621 M | 1998-06-01 | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | NO | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [6 empty] | YES |  | YES | YES |  |  |  | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [37 empty] | YES | [6 empty] | YES |  | YES |  |  | ERIK WEFLEN | MECHANICAL ENGINEER | eweflen@interiorgas.com | 9074527111 | 9074578111 |  |  |  | DAN BRITTON | GENERAL MANAGER | 9074527111 | dwbritton@interiorgas.com | THE INTERIOR GAS UTILITY (IGU) LNG STORAGE AND VAPORIZATION SITE NUMBER 3 (SS3) IN FAIRBANKS, ALASKA SENT COLD GAS AND POSSIBLY LNG TO THE DISTRIBUTION SYSTEM. WHEN THE COLD GAS OR LNG ENTERED THE DISTRIBUTION SYSTEM, IT EMBRITTLED THE 8' UNDERGROUND HDPE PIPE, WHICH SUBSEQUENTLY RUPTURED IN A SECTION OF PIPING WITHIN IGU PROPERTY. THE HIGHEST RECORDED PRESSURE DOWNSTREAM OF THE DISTRIBUTION REGULATORS AT SS3 WAS 62PSIG. AT APPROXIMATELY 4:10PM ON 11/21/2021, A TEMPERATURE SWITCH ON THE OUTLET OF THE VAPORIZER MALFUNCTIONED AND CLOSED A VALVE TO STOP THE FLOW OF LNG THROUGH THE VAPORIZER. WITH NO LNG TO VAPORIZE, THE GLYCOL HEATER TURNED OFF DUE TO LOW DEMAND. AT ABOUT 4:55PM, AN OPERATOR NOTICED THAT THE FLOW OF LNG HAD STOPPED, AND THE DISTRIBUTION PRESSURE WAS DROPPING. THE OPERATOR OPENED THE CLOSED VAPORIZER VALVE VIA REMOTE CONTROL. THE OPERATOR DID NOT NOTICE THAT THE BOILER WAS NOT FIRING AND DID NOT MONITOR THE SITE LONG ENOUGH TO VERIFY THE SYSTEM WAS STABLE AND PROPER TEMPERATURES WHERE BEING MAINTAINED. DUE TO THE MALFUNCTIONING TEMPERATURE SWITCH AND A TEMPERATURE TRANSMITTER THAT HAD NOT BEEN PROGRAMMED TO ACT AS A BACKUP TO THE TEMPERATURE SWITCH, THE CONTROL SYSTEM DID NOT STOP THE FLOW OF LNG THROUGH THE VAPORIZER, UPON A LOW GAS TEMPERATURE ON THE OUTLET OF THE VAPORIZER. THE BOILER ATTEMPTED TO FIRE ABOUT THREE MINUTES AFTER THE LNG FLOW RESUMED BUT FAILED TO STAY RUNNING. THE SYSTEM ATTEMPTED TO START A BACK-UP BOILER ABOUT 10 MINUTES LATER, ABOUT WHEN THE DISTRIBUTION LINE RUPTURED. THE STANDARD OPERATING PROCEDURES WILL BE REVISED TO NO LONGER ALLOW CONTROL CHANGES FROM VIA REMOTE CONTROL (EXCEPT FOR EMERGENCY SHUT DOWNS AND SPECIFIED EXCEPTIONS) AND INSTEAD REQUIRE THE MONITORING OPERATOR TO TRAVEL TO THE SITE TO MAKE THE NECESSARY ADJUSTMENTS AND CHANGES. THE VAPORIZER TEMPERATURE SWITCHES WILL BE RECOMMISSIONED, AND THE TEMPERATURE TRANSMITTERS WILL BE ADDED INTO THE VAPORIZER SHUTDOWN PROGRAMMING LOGIC TO ADD REDUNDANCY. ADDITIONALLY, A DOWNSTREAM TEMPERATURE TRANSMITTER LOCATED ON THE METER SKID WILL BE USED TO SHUT DOWN THE LNG PUMPS IF LOW TEMPERATURE IS DETECTED INDICATING THE VAPORIZER SHUTDOWNS FAILED TO ACTIVATE AS A RESULT OF LOW OUTLET TEMPERATURE.
2024-05-31 11:04 | YES | NO | NO | 20210103 | 37242 | 2021-12-21 11:45 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-11-22 21:37 | EASTERN | YES | 2021 | 3906 HOGARTH AVENUE | FLINT | GENESEE | MI | 48532 | 42.9961 | -83.7368 | [5 empty] | YES |  |  |  | 2021-11-23 00:14 | 1322727 | 1322826 | NATURAL GAS |  | 180 | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2021-11-22 21:37 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 180 | YES | 25 | 2021-11-22 21:37 |  |  |  | 2021-11-22 21:57 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1979 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | YES | NO | 1 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | A HOME EXPLOSION AT 3906 HOGARTH AVENUE, FLINT MI COMPROMISED THE NATURAL GAS FACILITIES (METER AND RISER) AT 3906 AND 3830 HOGARTH AVENUE CAUSING GAS TO BE RELEASED RESULTING IN SECONDARY IGNITION. | CLASS 3 LOCATION | 248800 | 264163.2569627798792 | 480 | 509.63972404394832 | 6904 | 7330.318030832123336 | 0 | 0 |  | 3.3 | 594 | 521.970099667774086378737541528239202658 | 0 | 0 | 256778 | 115313.6183035228664051561461794019933555 | 272525.1848173237249423787375415282392027 | 0 | 0 | 25 | 1 | 0 | 37 | 0 | 52 | 52 | 60 | 192.619(A)(2) | 2005-09-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON MONDAY, NOVEMBER 22, 2021 AT APPROXIMATELY 21:37 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION FROM EMERGENCY PERSONNEL OF A POSSIBLE HOME EXPLOSION IN THE 3900 BLOCK OF HOGARTH AVENUE, FLINT (GENESEE COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) AND DISTRIBUTION EMPLOYEES WERE DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 21:57 HOURS AND 22:43 HOURS RESPECTIVELY. THE GSW CONFIRMED AN EXPLOSION AND SUBSEQUENT IGNITION INVOLVING THREE HOMES 3830, 3906, AND 3910 HOGARTH AVENUE. PRIOR TO THE EXPLOSION, CONSUMERS ENERGY WAS NOT NOTIFIED OF ANY ISSUES AT THESE PROPERTIES. A HOME EXPLOSION AT 3906 HOGARTH AVENUE, FLINT MI COMPROMISED THE NATURAL GAS FACILITIES (METER AND RISER) AT 3906 AND 3830 HOGARTH AVENUE CAUSING GAS TO BE RELEASED RESULTING IN SECONDARY IGNITION. DUE TO SAFETY CONCERNS CONSUMERS ENERGY EMPLOYEES WERE UNABLE TO IMMEDIATELY ACCESS THE IMPACTED PROPERTIES BUT BEGAN INVESTIGATING THE SURROUNDING AREAS. AS A PRECAUTION, NATURAL GAS SERVICE WAS DISCONTINUED AT ALL ACCESSIBLE HOMES ON HOGARTH AVENUE BETWEEN NEDRA AVENUE AND WALTON AVENUE. CONSUMERS ENERGY ALSO ASSISTED IN THE EVACUATION OF AFFECTED RESIDENTS. ZERO UNDERGROUND GAS READS WERE DISCOVERED. THE DISTRIBUTION CREW SQUEEZED AND CAPPED THE SERVICE LINES AT THE MAIN FOR 3830, 3906, 3910 HOGARTH AVENUE. WHEN IT WAS SAFE TO DO SO, CONSUMERS ENERGY EMPLOYEES CONTINUED TO INVESTIGATE THE ACCESSIBLE AREAS FOR UNDERGROUND GAS READS. ZERO READS WERE DISCOVERED. THE FOLLOWING DAY, CONSUMERS ENERGY EMPLOYEES CONTINUED THEIR INVESTIGATION BY PERFORMING BAR HOLE TESTING OF THE SERVICE LINES AND THE PIPELINE AS WELL AS SEWERS LOCATED IN THE AREA. ADDITIONAL AIR TESTING OF THE NATURAL GAS FACILITIES WAS UNABLE TO BE PERFORMED UNTIL THE POLICE RECOVERY INVESTIGATION WAS COMPLETE. THERE WERE TWO FATALITIES AND ONE INJURY REQUIRING OVERNIGHT HOSPITALIZATION AS WELL AS PROPERTY DAMAGE TO OTHER NEIGHBORING HOMES. ON TUESDAY, NOVEMBER 30, 2021, CONSUMERS ENERGY EMPLOYEES PERFORMED AN AIR TEST AT THE OPERATING PRESSURE (52 PSIG) ON THE SERVICE LINES LOCATED AT 3830, 3906 AND 3910 HOGARTH AVENUE. ZERO LEAKS WERE DISCOVERED DURING THE TESTING. AN EVALUATION OF METER READING INFORMATION OBTAINED FROM CONSUMERS ENERGY'S METER DATA MANAGEMENT SYSTEM (MDMS) INDICATED A SIGNIFICANT INCREASE IN USAGE ON NOVEMBER 22, 2021 BETWEEN 02:00 HOURS AND 21:10 HOURS. HOWEVER, THERE WERE NO ISSUES IDENTIFIED WITH THE REGULATED FACILITIES THAT PROVIDED NATURAL GAS SERVICE TO THESE PROPERTIES. ON MONDAY, DECEMBER 6, 2021 AN INITIAL JOINT-SCENE INVESTIGATION WAS HELD AT THE SITE. A CONSUMERS ENERGY INVESTIGATOR WAS IN ATTENDANCE AND PROVIDED INFORMATION KNOWN TO DATE AS WELL AS RESULTS OF OUR INVESTIGATION. DURING THE EXAMINATION, A DISCONNECTED NATURAL GAS CUSTOMER FUEL LINE WAS DISCOVERED AT/NEAR THE WATER HEATER BY THE MICHIGAN STATE FIRE INVESTIGATOR. THE PIPE SEGMENT WAS EXAMINED AND PHOTOGRAPHED BY THOSE IN ATTENDANCE. FURTHER EXAMINATION OF THE SCENE WAS POSTPONED, AND THE SITE SECURED UNTIL ADDITIONAL EQUIPMENT COULD BE OBTAINED TO ALLOW FOR SAFE ACCESS INTO THE BASEMENT OF THE PROPERTY. IN FEBRUARY, 2022, AUTHORITIES REVISITED THE SITE AND RECOVERED EVIDENCE FOR FURTHER EXAMINATION BY IMPACTED STAKEHOLDERS. ON SEPTEMBER 7, 2022 A LABORATORY EXAMINATION OF EVIDENCE AND ARTIFACTS RECOVERED FROM THE EXPLOSION SITE WAS PERFORMED AT THE NELDERVELD INC. EXAMINATION CENTER. THE EXAMINATION CONCLUDED THAT A NATURAL GAS LEAK ORIGINATED FROM INSIDE THE HOME AT 3906 HOGARTH AVENUE, BUT AN IGNITION SOURCE COULD NOT BE DETERMINED DUE TO EXTENSIVE DAMAGE.
2024-05-31 11:04 | NO | YES | NO | 20210104 | 36172 | 2021-12-22 13:18 | ORIGINAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2021-11-29 11:00 | MOUNTAIN | NO | 2021 | 920 11TH STREET | RAPID CITY | PENNINGTON | SD | 57701 | 44.0777 | -103.2375 | [5 empty] | YES |  |  |  | 2021-11-29 11:28 | 1323119 | 1323315 | NATURAL GAS |  | 46.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-11-29 11:00 | ALLOWED TO BURN OUT |  | 10.85 | YES | 4 | 2021-11-29 10:27 | YES | OPERATOR | 2021-11-29 10:27 | 2021-11-29 10:27 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | INSIDE RESIDENTIAL STRUCTURE. | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1967 | UNKNOWN |  |  |  |  | 1 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DAMAGE PULLED DISTRIBUTION MAIN APART AT AN ELBOW FITTING CONNECTION. | CLASS 3 LOCATION | 210000 | 222967.37926922739 | 8000 | 8493.995400732472 | 6500 | 6901.3712630951335 | 0 | 0 |  | 6.22 | 288 | 253.076411960132890365448504983388704319 | 0 | 0 | 224788 | 100899.4291747040350863787375415282392027 | 238615.8223450151283903654485049833887043 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 30 | 30 | 34 | 192.619(A)(1) | 1993-09-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2129918149 |  |  | CONTRACT LOCATOR | NO | YES | 3 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 2083776032 |  | GREG WATKINS | greg.watkins@mdu.com | 2083776032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 2083776032 | greg.watkins@mdu.com | ON NOVEMBER 29, 2021 AT 9:22 A.M. MST, AN EXCAVATOR NOTIFIED MONTANA-DAKOTA UTILITIES CO. (MDU) THAT THEY DAMAGED A 1" MAIN NEAR 920 11TH STREET, RAPID CITY, SOUTH DAKOTA. AN MDU FIRST RESPONDER ARRIVED AT 10:27 A.M. MST AND AFTER CHECKING IN WITH LOCAL FIRE DEPARTMENT PERSONNEL ON SCENE, BEGAN INVESTIGATING. WHILE THE MDU EMERGENCY RESPONDERS WERE WORKING TO SECURE THE DAMAGE, THE LEAKING NATURAL GAS CAUSED BY THE EXCAVATION DAMAGE MIGRATED AND SUBSEQUENTLY IGNITED CAUSING AN EXPLOSION AND A FIRE AT 920 11TH STREET. AN MDU CREW EXCAVATED AND SQUEEZED THE 2" STEEL MAIN UPSTREAM OF THE DAMAGED 1" MAIN. THE INVESTIGATION DETERMINED THE THIRD-PARTY EXCAVATOR LOCATE TICKET EXPIRED PRIOR TO COMMENCING WORK ON THE DATE OF THE INCIDENT.
2024-05-31 11:04 | NO | YES | NO | 20210106 | 38029 | 2021-12-23 11:31 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2021-12-01 00:55 | EASTERN | NO | 2021 | 58 VERMONT STREET | BROOKLYN | KINGS | NY | 11207 | 40.6786 | -73.8959 |  |  | YES | [6 empty] | 2021-12-01 15:47 | 1323353 | 1323471 | NATURAL GAS |  | 3.95 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-01 00:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 3.95 | YES | 6 | 2021-12-01 00:55 |  |  |  | 2021-12-01 01:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER | [9 empty] | OTHER | [8 empty] | METER TAMPERING OCCURRED RESULTING IN A NATURAL GAS EXPLOSION. | CLASS 4 LOCATION | 129300 | 137284.2006643385787 | 2000 | 2123.498850183118 | 5369 | 5700.532663316580271 | 0 | 0 |  | 7.21 | 28 | 24.60465116279069767441860465116279069767 | 0 | 0 | 136697 | 61327.9388249882034959534883720930232558 | 145132.8368290010676686744186046511627907 | 0 | 0 | 3 | 2 | 0 | 3 | 0 | 0.29 | 0.29 | 0.3 | 192.623 | 2009-05-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF TRANSPORTED COMMODITY | [156 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | UPDATE 5/10/2023: WE HAVE REVIEWED THIS INCIDENT IN DETAIL AND HAVE REASON TO BELIEVE THAT THERE WAS INTENTIONAL DAMAGE TO THE METERING EQUIPMENT IN AN EFFORT TO STEAL OR ATTEMPT TO STEAL, THE TRANSPORTED GAS. ALSO, COST TO CUSTOMER PROPERTY UNKNOW; THEREFORE WE APPLIED THE MINIMUM REPORTABLE ESTIMATE OF $129,300. THIS WILL BE OUR FINAL SUBMITTAL FOR THIS INCIDENT. NATIONAL GRID WAS NOTIFIED ON 12/1/2021 AT 00:54 REGARDING A FIRE/DISTURBANCE AT 58 VERMONT ST., BROOKLYN NY BY THE FDNY. FIRST RESPONDER WAS DISPATCHED AT 00:55 AND ARRIVED AT 01:11. FDNY WAS ONSITE. LOCATION WAS MADE SAFE AT 01:32 BY SHUTTING THE CURB VALVES AT 54, 56, 58 AND 60 VERMONT ST. SERVICE TO THE RESIDENCE INVOLVED IN THE FIRE, 58 VERMONT ST, WAS LATER DISCONNECTED AT THE MAIN ON 12/2 AT 10:30. TWO RESIDENTS WERE TAKEN TO A NEARBY HOSPITAL FOR OBSERVATION. THE CAUSE OF THE FIRE AND EXPLOSION IS CURRENTLY UNKNOWN AND UNDER INVESTIGATION AS OF 12/8/2021. AS OF 12/8, WE HAVE NOT BEEN GRANTED ACCESS TO THE PREMISES SINCE THE TIME OF THE INCIDENT. AS OF 12/23 WE STILL HAVE NOT BEEN GRANTED ACCESS. FOR QUESTION A4, THE TIME AN INCIDENT CRITERIA WAS MET IS ESTIMATED. THE EXACT TIMELINE FOR FIRE AND DISTURBANCE IS NOT FULLY DIFFERENTIATED. FURTHERMORE, AT THE TIME OF REPORTING, IT IS STILL NOT KNOWN WHERE THE INCIDENT INITIATED AND WHETHER IT OCCURRED ON CUSTOMER-OWNED OR COMPANY-OWNED PIPING OR EQUIPMENT FOR REPORTING PURPOSES. FOR QUESTION E3B, INFORMATION IS FOR SERVICE PIPING.
2024-05-31 11:04 | NO | YES | NO | 20210107 | 36290 | 2021-12-23 11:51 | SUPPLEMENTAL FINAL | 31588 | COSERV GAS, LTD | 7701 SOUTH STEMMONS | CORINTH | TX | 76210 | 2021-12-03 20:58 | CENTRAL | NO | 2021 | 971 HWY. 121 | ALLEN | COLLIN | TX | 75013 | 33.1412 | -96.6793 | [5 empty] | YES |  |  |  | 2021-12-03 20:56 | 1323575 | 1323797 | NATURAL GAS |  | 59.065 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-03 20:24 | OPERATOR/CONTRACTOR |  | 0 | NO | 40 | 2021-12-03 20:24 |  |  |  | 2021-12-03 21:19 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2020 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | METER SET | [9 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 600000 | 637049.6550549354 | 50100 | 53193.6461970871059 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 650100 | 291634.1623371094578 | 690243.3012520225059 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.621 M | 2020-10-28 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 285 | NO | [142 empty] | RODNEY HALE | GAS COMPLIANCE MANAGER | rhale@coserv.com | 19402180258 |  | JASON WALKER | jawalker@coserv.com | 19729787928 | JASON WALKER | DIRECTOR OF GAS OPERATIONS | 19729787928 | jawalker@coserv.com | THE DRIVER WAS TRAVELING EAST ON RIDGEVIEW DR. AND FAILED TO CONTROL HIS SPEED AND LOST CONTROL OF THE VEHICLE. THE VEHICLE STRUCK THE CENTER MEDIAN, CROSSED THE WESTBOUND LANES, AND TRAVELED INTO THE BACK ENTRYWAY OF LIFETIME FITNESS. THE VEHICLE HIT THE GAS METER AT THE BACK OF THE LIFETIME FITNESS BUILDING AT 971 HWY. 121 IN ALLEN TX. IGNITING A FIRE. THE CAR WAS ON FIRE AND SITTING ON THE CURB VALVE. THE VALVE COULD NOT BE ACCESSED TO SHUT THE GAS OFF SO THE POLYETHYLENE GAS LINE FEEDING THE METER HAD TO BE EXCAVATED AND SQUEEZED TO STOP THE FLOW OF GAS AND PUT OUT THE FIRE.* THERE ARE SEVERAL NATURAL BARRIERS THAT WOULD PREVENT SOMETHING LIKE THIS FROM EVER HAPPENING AGAIN. THE CAR HAD TO BE ON ITS SIDE TO BE ABLE TO FIT BETWEEN THE CONCRETE WALL AND THE VERY LARGE TREE PROTECTING THE METER. THE VALVE WAS RE-LOCATED ACROSS THE STREET TO ENSURE THAT THERE WILL BE ACCESSIBLE IN THE EVENT SOMETHING ELSE HAPPENS TO THE METER.
2024-05-31 11:04 | NO | YES | YES | 20210108 | 36350 | 2021-12-31 17:15 | SUPPLEMENTAL FINAL | 2456 | CLARKE - MOBILE COUNTIES GAS DIST | 2003 COLLEGE AVENUE P.O. BOX 608 | JACKSON | AL | 36545 | 2021-12-01 17:24 | CENTRAL | NO | 2021 | 1177 ABB ROAD | CHATOM | WASHINGTON | AL | 36518 | 31.4419 | -88.197 |  |  |  | YES | [5 empty] | 2021-12-01 17:43 | 1323379 |  | NATURAL GAS |  | 0.126 | 0.126 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-12-01 11:23 | OPERATOR/CONTRACTOR |  | 0.12 | NO | 0 | 2021-12-01 11:23 | NO |  |  | 2021-12-01 11:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | CONTROLLED RELEASE / PURGING OPERATIONS. | CLASS 3 LOCATION | 0 | 0 | 134 | 142.274422962268906 | 107 | 113.607188484796813 | 0 | 0 |  | 4.525 | 1 | 0.8787375415282392026578073089700996677741 | 1 | 0.8787375415282392026578073089700996677741 | 243 | 109.42463372666028471096345514950166113 | 257.639086530122197405315614617940199336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 60 | 192.619(A)(2) | 2021-11-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.6 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | THE UTILIZED GROUNDING TECHNIQUES (TO MITIGATE STATIC ELECTRICITY) WERE INCONSISTENT WITH CMC GAS POLICY. INCONSISTENT WITH CMC GAS POLICY, TECH 1 FAILED TO EMPLOY A VENT STACK ON THE VENT OUTLET TO DIRECT THE GAS FLOW UPWARD. (SEE NARRATIVE) |  |  | YES |  |  | COMMISSIONING | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | MIKE SASSER | COMPLIANCE MANAGER | msasser@cmcgas.com | 2512462428 |  | MIKE SASSER | msasser@cmcgas.com | 2512462428 | MIKE SASSER | COMPLIANCE MANAGER | 2512462428 | msasser@cmcgas.com | REPORTABLE INCIDENT NARRATIVE ON 1 DECEMBER 2021, AT APPROXIMATELY 11:23 HOURS, A CMC GAS CREW COMMISSIONING A NEW 2-INCH MDPE MAIN OF APPROXIMATELY 6,100 LF EXPERIENCED AN UNEXPECTED INCIDENT WHERE THE VENTING GAS IGNITED, INJURING ONE EMPLOYEE. INJURIES CONSISTED OF NON-LIFE-THREATENING BURNS ON HIS UPPER BODY. A 2.0 X 0.75-INCH, HIGH-VOLUME TAP WAS INSTALLED ON THE OUTLET END OF THE PIPELINE SEGMENT. NATURAL GAS WAS INTRODUCED INTO THE PIPELINE SEGMENT FROM THE SUPPLY END OF THE PIPELINE FROM A "FARM TAP" REGULATOR STATION. GAS FLOWED, PUSHING THE AIR OUT OF THE PIPELINE FOR APPROXIMATELY 8 MINUTES. AT APPROXIMATELY THE 8-MINUTE MARK OF THE PURGE, THE PURGE TECHNICIAN (TECH 1) ON THE SITE APPROACHED THE TAP TEE WHERE GAS WAS VENTING. AS TECH 1 REACHED FOR THE TAP, AN UNEXPECTED IGNITION OF THE GAS OCCURRED. BEFORE BEING ABLE TO REMOVE HIMSELF FROM THE FLASH, TECH 1 RECEIVED MINOR BURNS ON THE FACE AND ARM AREAS. THE FIRE-WATCH TECHNICIAN (TECH 3) NOTIFIED THE TECHNICIAN OPERATING THE SUPPLY VALVE (TECH 2) OF THE INCIDENT AND REQUESTED THE SUPPLY VALVE BE CLOSED. AS THE VOLUME OF GAS IN THE PIPE DIMINISHED, THE TECH 3 EXTINGUISHED THE SMALL FLAME. APPROXIMATE 5 MINUTES ELAPSED FROM THE TIME OF IGNITION UNTIL THE FLAME WAS EXTINGUISHED. ON-SITE PERSONNEL NOTIFIED THE CONSTRUCTION AND MAINTENANCE MANAGER, WHO NOTIFIED OTHER MANAGEMENT. ON SITE PERSONNEL TRANSPORTED THE INJURED TECHNICIAN TO THE LOCAL HOSPITAL EMERGENCY ROOM, APPROXIMATELY 3 MILES AWAY. TECH 1 WAS TREATED AND TRANSPORTED TO UNIVERSITY HOSPITAL IN MOBILE, ALABAMA, WHERE HE WAS ADMITTED FOR FURTHER TREATMENT AND OBSERVATION. CMC GAS PERSONNEL PLACED A PIPE SQUEEZE DEVICE ON THE 2-INCH MDPE PIPE UNTIL THE PIPE WAS CUT AND CAPPED. UPON NOTIFICATION OF THE HOSPITALIZATION OF TECH 1 AT 17:24 HOURS, THE COMPLIANCE MANAGER NOTIFIED THE ALABAMA PUBLIC SERVICE COMMISSION, PIPELINE SAFETY DIVISION OF THE INCIDENT, AND THE NATIONAL RESPONSE CENTER. THIS CALL WAS MADE AT 17:43 HOURS. TECH 1 WAS RELEASED FROM THE UNIVERSITY HOSPITAL ON DECEMBER 8TH AND WAS SUBSEQUENTLY RELEASED TO RETURN TO WORK ON 20 DECEMBER 2021. AT THE TIME OF THIS REPORT, THE INVESTIGATION HAS REVEALED THE FOLLOWING: 1) THE BELIEVED SOURCE OF IGNITION WAS STATIC ELECTRICITY. A. AT THE TIME OF THE IGNITION, THE AMBIENT AIR RELATIVE HUMIDITY WAS REPORTED AT 20% B. AT THE TIME OF THE IGNITION, THE AMBIENT AIR TEMPERATURE WAS REPORTED AT 72 DEGREES FAHRENHEIT. 2) THE UTILIZED GROUNDING TECHNIQUES (TO MITIGATE STATIC ELECTRICITY) WERE INCONSISTENT WITH CMC GAS POLICY. 3) INCONSISTENT WITH CMC GAS POLICY, TECH 1 FAILED TO EMPLOY A VENT STACK ON THE VENT OUTLET TO DIRECT THE GAS FLOW UPWARD. 4) TECH 2 (THE VALVE OPERATOR ON THE SUPPLY END OF THE PIPELINE) WAS DETERMINED TO BE WORKING OUTSIDE HIS OPERATOR QUALIFICATION. 5) TECH 1, WHO WAS ALSO MONITORING THE PURGE OF GAS DID NOT EMPLOY A COMBUSTIBLE GAS METER (CGI) OR A PERSONAL PROTECTIVE ATMOSPHERIC METER, INCONSISTENT WITH CMC GAS POLICY. 6) TECH 1 DID NOT DON THE FIRE-RESISTANT CLOTHING AND OTHER PERSONAL PROTECTIVE EQUIPMENT (PPE) WHICH WERE PROVIDED BY CMC GAS AND IS CMC GAS STANDARD PROCEDURE. MITIGATIVE MEASURES TAKEN TO PREVENT RECURRENCE: 1) ALL RELEVANT MEMBERS OF THE 12/01/21 INCIDENT CREW HAVE BEEN DISQUALIFIED, RETRAINED, AND REQUALIFIED ON RELEVANT OQ TASKS. 2) ALL RELEVANT MEMBERS OF THE 12/01/21 INCIDENT CREW HAVE ATTENDED A POLICY, STATIC MITIGATION, AND PPE REVIEW SESSION. 3) INTERNAL DISCIPLINARY ACTIONS TAKEN AS RELEVANT.
2024-05-31 11:04 | NO | YES | NO | 20220002 | 36243 | 2022-01-07 14:08 | SUPPLEMENTAL FINAL | 22763 | WISCONSIN GAS LLC DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2021-12-11 09:02 | CENTRAL | NO | 2021 | 517 WISCONSIN STREET | WAUPACA | WAUPACA | WI | 54981 | 44.3617 | -89.0944 |  |  | YES | [6 empty] | 2021-12-11 12:37 | 1324303 | 1324403 | NATURAL GAS |  | 19 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-11 09:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 17 | YES | 8 | 2021-12-11 09:12 |  |  |  | 2021-12-11 10:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1991 | 1991 | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | FURNACE BUTT WELDED |  | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 400000 | 424699.7700366236 | 1700 | 1804.9740226556503 | 1500 | 1592.6241376373385 | 200000 | 212349.8850183118 | BOILER, WATER HEATER, BUILDING CONTENTS | 10 | 190 | 166.960132890365448504983388704318936877 | 0 | 0 | 603390 | 270719.5404425134283375415282392026578073 | 640614.2133481187542485049833887043189369 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1991-06-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE METERSET WAS STRUCK BY A SNOW PLOW THEREFORE NO CONTROLLER OPPORTUNITY TO INFLUENCE THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | PARKING LOT | 8 | NO | [118 empty] | YES | [23 empty] | LISA NYSTROM | GAS SYSTEM ANALYST | lisa.nystrom@wecenergygroup.com | 920-433-5704 |  | LISA NYSTROM | lisa.nystrom@wecenergygroup.com | 920-433-5704 | TIM STROMMEN | MANAGER GAS CODE COMPLIANCE | 414-221-5173 | tim.strommen@we-energies.com | AT 9:12 AM ON 12/11/21, WISCONSIN GAS COMPANY WAS NOTIFIED THAT A GAS METER ASSEMBLY WAS HIT AT 517 WISCONSIN STREET, WAUPACA, WI AND THAT A FIRE/EXPLOSION HAD OCCURRED. A COMPANY FIRST RESPONDER WAS DISPATCHED TO THE SCENE AND UPON ARRIVAL FOUND THAT A TRACTOR WITH A SNOW PLOW HIT THE GAS METER ASSEMBLY WHILE REMOVING SNOW, RESULTING IN THE GAS RELEASE. THE RELEASE OF GAS WAS STOPPED AT 10:35 AM BY USE OF A SERVICE CURB VALVE. NO FATALITIES OR PERSONAL INJURIES NECESSITATING IN-PATIENT HOSPITALIZATION OCCURRED; HOWEVER, IT WAS DETERMINED THAT THE GAS RELEASE CAUSED DWELLING DAMAGES IN EXCESS OF THE 191.3 REPORTING THRESHOLD OF $122,000. THE INVESTIGATION IDENTIFIED A SEVERED PIPE NIPPLE AT THE INLET TO THE METER SET REGULATOR AS THE SOURCE OF GAS RELEASE AFTER BEING HIT DURING THE SNOW PLOWING OPERATION. EIGHT RESIDENTS WERE EVACUATED FROM THE DWELLING IMMEDIATELY AFTER THE METER SET WAS STRUCK AND THE DWELLING REMAINS UNINHABITABLE DUE TO THE DAMAGES.
2024-05-31 11:04 | NO | NO | NO | 20220003 | 36421 | 2022-01-07 14:10 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-12-08 16:43 | EASTERN | YES | 2021 | E. 11 MILE ROAD | ROYAL OAK | OAKLAND | MI | 48067 | 42.4899 | -83.1414 | [5 empty] | YES |  |  |  | 2021-12-08 23:49 | 1324037 | 1324232 | NATURAL GAS |  | 3421 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-12-08 16:43 | NO |  |  | 2021-12-08 17:08 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | UNKNOWN |  |  |  |  | 4 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 3 | 9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 575 | 610.505919427646425 | 15392 | 16342.447151009276128 | 0 | 0 |  | 4.18 | 14300 | 12565.9468438538205980066445182724252492 | 0 | 0 | 30267 | 16545.6694302641129093887043189368770764 | 29518.8999142907431510066445182724252492 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 2016-07-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | WATER | YES | B013270027 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON WEDNESDAY, DECEMBER 8, 2021 AT APPROXIMATELY 16:43 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE EXCAVATION DAMAGE FROM THE CONTRACTOR PERFORMING (BORING) WORK IN THE 300 BLOCK OF ELEVEN MILE ROAD, ROYAL OAK, (OAKLAND COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:08 HOURS AND CONFIRMED A DAMAGED AND BLOWING 4-INCH NATURAL GAS PIPELINE AT 315 ELEVEN MILE ROAD. DISTRIBUTION EMPLOYEES WERE DISPATCHED AT 17:02 HOURS AND ARRIVED ONSITE AT APPROXIMATELY 18:34 HOURS. THE DISTRIBUTION CREW EXCAVATED AT REMOTE LOCATIONS AND APPLIED SQUEEZERS TO CONTAIN THE BLOWING GAS. THE DAMAGED PIPELINE SEGMENT WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FOOT OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE AND NORMAL OPERATIONS RESUMED ON THURSDAY, DECEMBER 9, 2021 AT APPROXIMATELY 14:00 HOURS. THREE COMMERCIAL CUSTOMERS EXPERIENCED A LOSS OF SERVICE AS A RESULT OF THE DAMAGE AND SUBSEQUENT REPAIR. CONSUMERS ENERGY SERVICE EMPLOYEES REMAINED ONSITE AND CONTINUOUSLY MONITORED THE LOCATION UNTIL THE GAS WAS CONTAINED AND THE PIPELINE SEGMENT WAS REPAIRED. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE DAMAGE.
2024-05-31 11:04 | NO | YES | NO | 20220004 | 36224 | 2022-01-08 15:17 | SUPPLEMENTAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2021-12-09 09:19 | CENTRAL | NO | 2021 | 3111 WYANDOTTE ST | KANSAS CITY | JACKSON | MO | 64111 | 39.0707 | -94.5884 |  | YES |  |  |  |  | YES |  |  | 2021-12-09 11:14 | 1324107 | 13242511324239 | NATURAL GAS |  | 9519 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2021-12-09 09:19 |  |  |  | 2021-12-09 09:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | UNKNOWN |  |  |  |  | 20 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 2.3 | [7 empty] | CLASS 3 LOCATION | 196989 | 209152.957499361115851 | 0 | 0 | 500 | 530.8747125457795 | 0 | 0 |  | 4.1195 | 39214 | 34458.8139534883720930232558139534883721 | 0 | 0 | 236703 | 114323.4697412962090838604651162790697674 | 244142.6461653952674440232558139534883721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 63 | 100 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 213344010 |  |  | CONTRACT LOCATOR | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY CONTRACTOR WAS PERFORMING SEWER WORK AND WHILE BREAKING OUT A SEWER BOX THE COMPANY'S 20-INCH COATED STEEL GAS MAIN WAS STRUCK RESULTING IN A LEAK. A TEMPORARY REPAIR WAS MADE BY INSTALLING A STYLE 126 REPAIR SLEEVE. A PERMANENT REPAIR WAS MADE BY INSTALLING STOPPER FITTINGS TO ISOLATE THE SECTION OF MAIN AND REPLACE 13-FEET OF 20-INCH COATED STEEL MAIN. THE COMPANY'S FACILITIES WERE ACCURATELY MARKED ON DECEMBER 2, 2021 BUT WERE NO LONGER VISIBLE THE DAY OF THE INCIDENT. THE EXCAVATOR DID NOT REQUEST A RENEWAL OF THE LOCATE MARKS. A 48 HOUR UPDATE TO THE NRC WAS MADE ON DECEMBER 9, 2021 AT 15:46. REPORT NUMBER 1324251.
2024-05-31 11:04 | NO | NO | NO | 20220005 | 36217 | 2022-01-10 09:47 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-12-16 12:13 | EASTERN | YES | 2021 | 7224 ANNAPOLIS RD | HYATTSVILLE | PRINCE GEORGE COUNTY | MD | 20784 | 38.9481 | -76.89 |  | YES | [7 empty] | 2021-12-16 14:11 | 1324714 |  | NATURAL GAS |  | 67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-16 11:44 | OPERATOR/CONTRACTOR |  | 67 | NO | 8 | 2021-12-16 12:13 |  |  |  | 2021-12-16 12:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN FREQUENCY OR SEAMLESS | UNKNOWN | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC BURNT HOLE IN THE PIPE. SEE DESCRIPTION IN NARRATIVE. | CLASS 4 LOCATION | 500 | 530.8747125457795 | 108 | 114.668937909888372 | 8400 | 8918.6951707690956 | 383 | 406.650029810067097 | ADMINISTRATION COSTS | 3.01 | 202 | 177.50498338870431893687707641196013289 | 0 | 0 | 9593 | 4345.334050170897655807308970099667774086 | 10148.3938344235348879368770764119601329 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 20 | 20 | 25 | 192.619(A)(4) | 1970-11-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 8" WRPD NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [147 empty] | YES | [20 empty] | MARK AIESI | SUPERVISOR DOT PIPELINE SAFETY | mark.aiesi@washgas.com | 5714054623 |  | MARK AIESI | mark.aiesi@washgas.com | 5714054623 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON DECEMBER 16, 2021 AT APPROXIMATELY 1213 HOURS WASHINGTON GAS WAS NOTIFIED OF A GAS FED FIRE IN FRONT OF 7224 ANNAPOLIS ROAD, HYATTSVILLE, MD. WASHINGTON GAS DISPATCHED CREWS TO THE LOCATION WHO ARRIVED AND PERFORMED AN ASSESSMENT OF SITUATION, WHICH RESULTED IN THE IDENTIFICATION OF AN 8" WRPD MAIN LINE THAT WAS FEEDING THE CONTROLLED FIRE. NO WASHINGTON GAS CREWS, OR CONTRACTORS WERE WORKING AT THIS LOCATION AT THE TIME OF IGNITION. IT WAS DETERMINED THAT A TRANSFORMER SHORTED AT SURREY LANE AND ANNAPOLIS ROAD, WHICH RESULTED IN AN ELECTRICAL DISCHARGE THROUGH AN ADJACENT METAL FENCE INTO THE GROUND. THE METAL FENCE THAT IS ESTIMATED TO BE ROUGHLY 20 YEARS OLD WAS INSTALLED DIRECTLY OVER THE 8" WRPD MAIN. EVIDENCE SUGGESTS THAT THE ELECTRICAL DISCHARGE FROM THE TRANSFORMER TRAVELED DOWN THE FENCE AND DISCHARGED AT 7224 ANNAPOLIS ROAD, RESULTING IN AN ELECTRICAL ARC TO THE PIPE. THE GAS WAS TURNED OFF UTILIZING VALVES WHICH EXTINGUISHED THE FIRE. ONCE THE AREA WAS DEEMED SAFE, CREWS STARTED PERMANENT REPAIRS TO THE PIPE, INCLUDING ADDING NEW CATHODIC PROTECTION ANODES AND A TEST STATION. THE PIPE WAS REPAIRED USING A FULL SEAL CLAMP AND WAS NOT ABLE TO BE EXAMINED FOR PIPE SPECIFICATION AND WALL THICKNESS AS A RESULT. THERE WAS ONLY MINOR PROPERTY DAMAGE, WHICH WAS TO THE CHAIN LINK FENCE THAT HAD TO BE REMOVED TO REPAIR THE MAIN.
2024-05-31 11:04 | NO | YES | NO | 20220006 | 36261 | 2022-01-20 23:52 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2021-12-21 08:52 | MOUNTAIN | NO | 2021 | 5723 SHADY OAKS DRIVE | WINDSOR | LARIMER | CO | 80528 | 40.4833 | -104.9838 | [5 empty] | YES |  |  |  | 2022-01-06 12:58 | 1326030 | 1326116 | NATURAL GAS |  | 299 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-12-21 08:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 299 | NO | 0 | 2021-12-21 08:52 | YES | OPERATOR | 2021-12-21 08:53 | 2021-12-21 08:52 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 17 |  |  | 2708 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 700000 | 743224.5975640913 | 21219 | 22529.261051017790421 | 2000 | 2123.498850183118 | 0 | 0 |  | 5.02 | 1501 | 1318.985049833887043189368770764119601329 | 0 | 0 | 724720 | 325420.1426838287156085780730897009966777 | 769196.3425151260954641893687707641196013 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2021-01-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | NO | [5 empty] | YES | 25 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK NOLAN | PRINCIPAL ENGINEER | mark.nolan@xcelenergy.com | 303.571.3931 |  | TAMMY BOWIE | tammy.l.bowie@xcelenergy.com | 970-225-7865 | CHRIS AKINS | MANAGER PIPELINE COMPLIANCE | 303.571.3298 | christopher.a.akins@xcelenergy.com | A CONTRACTOR FOR HOME BUILDER WAS DIGGING TO LOWER WATER PIT WHEN 4" PE MAIN WAS DAMAGED AND BLOWING GAS IGNITED. NO LOCATE REQUEST WAS MADE; EXCAVATOR WAS DIGGING OFF OLD UTILITY MARKS. THE DAMAGED HOME AND SERVICE INTERRUPTIONS OCCURRED ON HOMES THAT WERE NOT YET SOLD OR OCCUPIED. LOCAL OPERATIONS OBSERVED THE FIRE AND RESPONDED TO SCENE BEFORE BEING NOTIFIED BY OUR DISPATCH OR LOCAL FIRE DEPARTMENT. A21A IGNITION TIME IS ESTIMATED, BUT GAS HAD IGNITED PRIOR TO OUR PERSONNEL'S ARRIVAL ON SCENE. D2A PROPERTY DAMAGE IS ESTIMATED.
2024-05-31 11:04 | NO | YES | NO | 20220007 | 37504 | 2022-02-04 19:20 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-01-06 14:13 | PACIFIC | NO | 2022 | 4244 BULLFROG RD | CLE ELUM | KITTITAS | WA | 98922 | 47.2059 | -120.9798 |  |  |  | YES | [5 empty] | 2022-01-06 20:39 | 1326070 | 1326135 | NATURAL GAS |  | 112 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-01-06 14:13 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 9 | NO | 0 | 2022-01-06 14:41 |  |  |  | 2022-01-06 15:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2008 | 2008 | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | EQUIPMENT BODY SEPARATED BY EXTERNAL LOAD | CLASS 4 LOCATION | 510450 | 521579.48360655758625 | 9457 | 9663.193606557380925 | 1583 | 1617.514590163935075 | 0 | 0 |  | 11 | 1232 | 945.904208998548621190130624092888243832 | 0 | 0 | 522722 | 225844.645705346393991436865021770682148 | 533806.0960122774508711901306240928882438 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 50 | 60 | 192.619(A)(2) | 2008-05-02 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 8.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | HEAVY SNOWFALL | [213 empty] | MICHAEL KIDD | REGULATORY COMPLIANCE ANALYST | michael.kidd@pse.com | [5 empty] | YVONNE WANG | SUPERVISOR COMPLIANCE SUPPORT | 425-424-7477 | yvonne.wang@pse.com | ON JANUARY 6, 2022, CLE ELUM FIRE DEPARTMENT CALLED PSE AT 14:41 NOTIFYING OF A FIRE AT A COMMERCIAL METER SET THAT PROVIDED TWO PSIG TO A LAUNDRY BUSINESS. PSE'S GAS FIRST RESPONSE (GFR) PERSONNEL ARRIVED ONSITE AT 15:30 AND FOUND THAT THE OUTLET VALVE AT THE METER SET HAD BEEN TURNED OFF PRIOR TO THEIR ARRIVAL. THE FIRE HAD ALREADY BEEN EXTINGUISHED BY CLE ELUM FIRE DEPARTMENT. PSE'S GFR MADE THE SITUATION SAFE AND LOCKED OFF THE MSA VALVE AT 19:30 ON JANUARY 6, 2022. PSE'S CONTRACTOR INFRASOURCE (IFS) CUT AND CAPPED THE SERVICE ON JANUARY 7, 2022 AT 19:41. ONE CUSTOMER LOST SERVICE AND NO EVACUATION WAS REQUIRED. NO INJURIES OR FATALITIES OCCURRED IN CONNECTION TO THIS INCIDENT. A FIRE OF UNKNOWN SOURCE AND ORIGIN IN THE BUILDING MELTED SNOW NEAR THE PEAK OF THE BUILDING. A LARGE AMOUNT OF SNOW AND ICE SLID OFF THE ROOF AND BROKE THE RELIEF VALVE VENT PIPING ON THE GAS METERSET. GAS LEAKING FROM THE BROKEN VENT PIPE WAS IGNITED BY THE FIRE IN THE BUILDING. PSE NOTIFIED THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION (WUTC) ON JANUARY 6, 2022 AT 17:30 DUE TO UNINTENTIONAL IGNITION OF GAS. PSE MADE FIRST TELEPHONIC NOTICE TO DOT ON JANUARY 6, 2022 AT 20:39, NRC # 1326070 WHEN IT WAS DETERMINED THAT THE ESTIMATED PROPERTY DAMAGES EXCEEDED $ 122,000. THE SECOND TELEPHONIC NOTICE WAS MADE TO DOT WITHIN 48 HOURS ON JANUARY 7, 2022 AT 16:22, NRC # 1326135.
2024-05-31 11:04 | NO | YES | NO | 20220008 | 36717 | 2022-02-07 11:14 | SUPPLEMENTAL FINAL | 7348 | DOMINION ENERGY WEST VIRGINIA | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2022-01-08 20:00 | EASTERN | NO | 2022 | 305 POWELL STREET | GLENVILLE | GILMER | WV | 26351 | 38.9327 | -80.8371 |  | YES | [7 empty] | 2022-01-08 21:10 | 1326175 | 1326260 | NATURAL GAS |  | 7446 | 4265 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-08 11:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-08 12:00 | 2022-01-08 12:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1947 | UNKNOWN |  |  |  |  | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 116531 | 119071.757868852506775 | 0 | 0 | 66638 | 68090.92688524592895 | 0 | 0 |  | 3.361 | 25026 | 19214.4470246734397677793904208998548621 | 14335 | 11006.1175616835994194484760522496371553 | 222530 | 101643.410829070433796531204644412191582 | 217383.2493404554749122278664731494920174 | 51 | 0 | 111 | 0 | 0 | 111 | 51 | 2.18 | 0.5 | 0.75 | 192.623 | 1947-11-08 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE ALREADY MONITORING SYSTEM PRESSURES DUE TO COLD WEATHER AND WERE AWARE OF THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [40 empty] | YES |  | YES | [30 empty] | CHELSEA MINUTELLI | GAS PIPELINE COMPLIANCE ANALYST | chelsea.m.minutelli@dominionenergy.com | 3046769284 |  | CHELSEA MINUTELLI | chelsea.m.minutelli@dominionenergy.com | 3046769284 | CAROL HAGER | MANAGER- GAS OPERATIONS PIPELINE INTEGRITY | 3304379557 | carol.m.hager@dominionenergy.com | ON 1/8/2022, DEWV PERSONNEL WERE MONITORING SYSTEM PRESSURES BECAUSE OF COLD WEATHER. IN THE COURSE OF DOING THIS, THEY IDENTIFIED A PRESSURE INCREASE FROM 8 OUNCES TO 10 OUNCES AT 11:00 HOURS; AND ANOTHER INCREASE FROM 10 OUNCES TO 35 OUNCES AT 12:00 HOURS. THE PRESSURE RETURNED TO 8 OUNCES AT 13:00 HOURS, WHICH IS BELIEVED TO BE FROM AN INCREASE IN TEMPERATURE RELIEVING MOISTURE AND ICE FROM THE REGULATORS. DURING THE EVENT, A LEAK WAS DISCOVERED ON A MAINLINE. THREE REGULATING STATIONS THAT FEED THE SYSTEM WERE SHUT IN, CREATING AN OUTAGE FOR 162 CUSTOMERS. THE MAINLINE LEAK WAS REPAIRED, THE SYSTEM WAS LEAK SURVEYED WITH NO ADDITIONAL HAZARDOUS LEAKS FOUND, AND SAFETY CHECKS AND RESTORATION OF CUSTOMERS WERE INITIATED BEGINNING ON THE MORNING OF 1/9/2022.
2024-05-31 11:04 | NO | NO | NO | 20220009 | 36309 | 2022-02-08 12:13 | ORIGINAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2021-02-23 11:55 | EASTERN | NO | 2021 | GATEWAY BLVD. & WESLEY CHAPEL BLVD. | WESLEY CHAPEL | PASCO | FL | 33544 | 28.2382 | -82.3616 |  |  |  | YES | [5 empty] | 2022-02-08 08:10 | 1328385 |  | NATURAL GAS |  | 357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-23 11:55 |  |  |  | 2021-02-23 11:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 80 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 31000 | 32914.232177838329 | 42478 | 45100.992079039243202 | 0 | 0 |  | 9 | 3213 | 2823.383720930232558139534883720930232558 | 0 | 0 | 76691 | 35070.3496205901609351627906976744186047 | 80838.6079778078047601395348837209302326 | 50 | 0 | 821 | 0 | 0 | 821 | 50 | 45 | 45 | 60 | 192.619(A)(2) | 2004-12-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A 3RD PARTY LINE STRIKE TO OPERATOR'S SYSTEM, AND AS SUCH, THE CONTROLLER(S) OR CONTROL ROOM WERE NOT THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 028100002 | SUNSHINE STATE ONE CALL OF FLORIDA |  | FACILITY OWNER | YES | YES | 18 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | [5 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 4074206667 | rharris@tecoenergy.com | THIRD PARTY CONTRACTOR STRUCK PEOPLES GAS SYSTEM'S MAIN DURING HDD OPERATION. UPON ARRIVAL ON SCENE AFTER THE REPORT OF THE DAMAGE, THE OPERATOR DID NOT IDENTIFY ANY PHYSICAL EVIDENCE THAT THE THIRD PARTY PERFORMED SPOT DIGGING TO IDENTIFY THE UTILITIES. PIPELINE WAS TOO DEEP TO DIG UP AND SQUEEZE, SO OPERATOR TURNED OFF CRITICAL VALVE STOPPING FLOW OF GAS. PRETESTED PIPELINE WAS INSTALLED, REPAIRS FINALIZED, AND RESTORATION COMPLETED.
2024-05-31 11:04 | NO | YES | NO | 20220010 | 36314 | 2022-02-08 16:05 | ORIGINAL | 12672 | MONROE NATURAL GAS DEPT, CITY OF | 300 W. CROWELL STREET | MONROE | NC | 28112 | 2022-01-04 17:15 | EASTERN | NO | 2022 | INTERSECTION OF ROCKY RIVER RD AND SECREST SHORT CUT RD. | MONROE | UNION | NC | 28110 | 35.0571 | -80.5936 | YES | [8 empty] | 2022-01-04 18:00 | 1325889 | 1326041, 1326048 | NATURAL GAS |  | 4266.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-04 15:09 | YES | OPERATOR | 2022-01-04 15:13 | 2022-01-04 15:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 127 | NO | YES |  |  |  |  | YES | CASED, BORED/DRILLED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2006 | 2004 |  |  |  |  | 6 | API 5L GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 52266 | 53405.57016393444765 | 0 | 0 | 0 | 0 |  | 16.8755 | 71999 | 55279.3483309143686502177068214804063861 | 0 | 0 | 124265 | 63840.9861236289314547750362844702467344 | 108684.9184948488163002177068214804063861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 265 | 275 | 192.619(A)(1) | 2006-03-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 5.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BORING | WATER | YES | C213551031 | N/A |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | DARWIN DE LOS SANTOS | NATURAL GAS ENGINEERING AND COMPLIANCE MANAGER | ddelossantos@monroenc.org | 7042824697 | 704-283-6492 | ROBERT MILLER | rmiller@monroenc.org | 704-282-4638 | DAVID LUCORE | DIRECTOR OF ENERGY SERVICES | 704-282-4602 | dlucore@monroenc.org | ON 01/04/2022 AT 3:09 PM - CDM SMITH STRUCK THE CITY OF MONROE'S 6-INCH STEEL 275 PSIG GAS MAIN WHILE MAKING A BORE ACROSS THE INTERSECTION OF ROCKY RIVER ROAD AND SECREST SHORTCUT ROAD IN MONROE NC. THE BORE WAS FOR THE INSTALLATION OF A 42 INCH WATER MAIN WITHIN A 54" CASING. THE GAS MAIN WAS PROPERLY LOCATED AND THE CONTRACTOR FAILED TO PERFORM DUE DILIGENCE IN ACCORDANCE WITH NORTH CAROLINA GENERAL STATUTES CHAPTER 87 ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT. THE GAS MAIN WAS RUPTURED BY THE AUGER BORE MACHINE CAUSING THE RELEASE OF NATURAL GAS AND REQUIRING THE REPAIR OF THE GAS LINE. REPAIRS TO THE CITY OF MONROE NATURAL GAS MAIN WERE FINALIZED ON 01/06/2022 AT 3:30 AM. ON 1/04/2022 AT 05:15 PM THE CITY OF MONROE DETERMINED THAT THE INCIDENT REPORTING THRESHOLD WAS GOING TO BE MET BEFORE THE FACILITIES COULD BE REPAIRED. THEREFORE A DETERMINATION OF FILING THE INITIAL INCIDENT WITH NRC WAS MADE. THE NRC NOTIFICATION WAS MADE AT APPROXIMATELY 6:00 PM ON 1/4/2022. THE ACTUAL INCIDENT THRESHOLD OF 3,000 MCF WAS NOT MET UNTIL APPROXIMATELY 1/05/2022 AT APPROXIMATELY 05:26 AM. CDM WAS NEGLIGENT IN THE FOLLOWING REQUIREMENTS: NC ARTICLE 8A - UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT - 87-122. EXCAVATOR RESPONSIBILITIES C) AN EXCAVATOR SHALL COMPLY WITH THE FOLLOWING: (3) PLAN THE EXCAVATION OR DEMOLITION TO AVOID DAMAGE TO OR MINIMIZE INTERFERENCE WITH FACILITIES IN OR NEAR THE CONSTRUCTION AREA. (9) AN EXCAVATOR SHALL NOT PERFORM ANY EXCAVATION OR DEMOLITION WITHIN THE TOLERANCE ZONE UNLESS THE EXCAVATOR COMPLIES WITH ALL OF THE FOLLOWING CONDITIONS: A. THE EXCAVATOR SHALL NOT USE MECHANIZED EQUIPMENT, EXCEPT, NONINVASIVE EQUIPMENT SPECIFICALLY DESIGNED OR INTENDED TO PROTECT THE INTEGRITY OF THE FACILITY, WITHIN THE MARKED TOLERANCE ZONE OF AN EXISTING FACILITY UNTIL: 1. THE EXCAVATOR HAS VISUALLY IDENTIFIED THE PRECISE LOCATION OF THE FACILITY OR HAS VISUALLY CONFIRMED THAT NO FACILITY IS PRESENT UP TO THE DEPTH OF EXCAVATION; 2. THE EXCAVATOR HAS TAKEN REASONABLE PRECAUTIONS TO AVOID ANY SUBSTANTIAL WEAKENING OF THE FACILITY'S STRUCTURAL OR LATERAL SUPPORT, OR BOTH, OR PENETRATION OR DESTRUCTION OF THE FACILITIES OR THEIR PROTECTIVE COATINGS: B. THE EXCAVATOR SHALL MAINTAIN CLEARANCE BETWEEN A FACILITY AND THE CUTTING EDGE POINT OF ANY MECHANIZED EQUIPMENT, TAKING INTO ACCOUNT THE KNOWN LIMIT OF CONTROL OF THE CUTTING EDGE OR POINT, AS MAY BE REASONABLY NECESSARY TO AVOID DAMAGE TO THE FACILITY. THE CITY OF MONROE ACCURATELY MARKED THE 6-INCH STEEL GAS LINE. CDM SMITH DID NOT COMPLY WITH THE REQUIREMENTS WITHIN THE TOLERANCE ZONE. CDM SMITH DID NOT VISUALLY INSPECT THE GAS FACILITY AT THE DEPTH OF THE EXCAVATION. CDM SMITH IS RESPONSIBLE FOR THE DAMAGE DUE TO NEGLIGENCE AND NON-COMPLIANCE WITH THE NC UNDERGROUND UTILITY SAFETY AND DAMAGE PREVENTION ACT.
2024-05-31 11:04 | NO | NO | NO | 20220011 | 36473 | 2022-02-14 15:41 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-01-28 06:38 | EASTERN | NO | 2022 | FERN HOLLOW BRIDGE | PITTSBURGH | ALLEGHENY | PA | 15221 | 40.4396 | -79.8995 | YES | [8 empty] | 2022-01-28 07:50 | 1327481 | 1327626 | NATURAL GAS |  | 871 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-28 06:38 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-28 07:30 | 2022-01-28 07:05 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | PIPE THRU BRIDGE SUPPORT AND UNDERGROUND |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 16 | API-5L-B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 16 |  | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 22321 | 22807.670983606566525 | 0 | 0 |  | 10.3951 | 9054 | 6951.474600870827285921625544267053701016 | 0 | 0 | 31375 | 14827.0609725427717478809869375907111756 | 29759.145584477393810921625544267053701 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 45 | 45 | 50 | 192.619(A)(1) | 1972-10-29 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCENTINEL T50 | 0.4 |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CASUAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE. PEOPLES PIPELINE WAS DAMAGED BY THE BRIDGE COLLAPSE. | [154 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | manager compliance | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412 258-4453 | edward.a.palombo@peoples-gas.com | THE NTSB IS NOT LOOKING AT THE PIPELINE AS CAUSAL OR CONTRIBUTORY IN THE COLLAPSE OF THE BRIDGE AS THE EVIDENCE GATHERED TO DATE SUGGESTS THE PIPELINE WAS DAMAGED BY THE COLLAPSE. WHEN ALSO CONSIDERING THE RESPONSE TO THE RUPTURE STABILIZED THE SITUATION BEFORE ANY FIRE OR EXPLOSION EVENTS, THE NTSB SEES NO NEED TO CONDUCT ANY FURTHER EXAMINATION OF THE PIPE OR RELATED MATERIALS AND WILL NOT BE SECURING ANY SUCH MATERIALS FOR LATER TESTING. TEN PEOPLE WERE INJURED AS A RESULT OF THE BRIDGE COLLAPSE. NO INJURIES RELATED TO THE PIPELINE. THE PIPELINE WAS DAMAGED AT BOTH SIDES OF THE FERN HOLLOW BRIDGE: WEST SIDE ( 40.439536, -79.901115 ) AND EAST SIDE ( 40.439621, -79.899509 ).
2024-05-31 11:04 | NO | YES | YES | 20220013 | 36356 | 2022-02-17 21:08 | ORIGINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2022-01-18 11:10 | EASTERN | YES | 2022 | 869 FOX STREET | BRONX | BRONX COUNTY | NY | 10469 | 40.8186 | -73.8956 |  | YES |  | YES |  | YES |  |  |  | 2022-01-18 12:54 | 1326802 | 1326954 | NATURAL GAS |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2022-01-18 11:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-01-19 10:39 |  |  |  | 2022-01-18 11:19 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | UNKNOWN | UNKNOWN | [7 empty] | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [9 empty] | LEAK |  |  | OTHER | UNKNOWN-NO UTILITY INVOLVEMENT | [5 empty] | CLASS 4 LOCATION | 50000 | 51090.16393442625 | 0 | 0 | 2824 | 2885.5724590163946 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 52824 | 22805.24655737705784 | 53975.7363934426446 | 0 | 0 | 18 | 0 | 10 | 18 | 0 | 0.25 | 0.25 | 0.5 | 192.619(A)(2) | 1910-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO JURISDICTIONAL INVOLVEMENT | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | leono@coned.com | 7183192350 | 718-904-4607 | OSCAR LEON | leono@coned.com | 7183192350 | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 7183192350 | leono@coned.com | ON 1/18/22 AT 11:10, CON EDISON'S GERC RECEIVED A REPORT FROM THE FDNY OF AN ACTIVE BUILDING FIRE AND EXPLOSION AT 850 FOX STREET IN THE BRONX, WITH FDNY PERSONNEL ON LOCATION. NATURAL GAS WAS NOT REPORTED TO BE INVOLVED. CON EDISON GDS, GAS CONSTRUCTION, AND GAS ERG AND SUPERVISION WERE DISPATCHED TO THE LOCATION BY THE GERC. CON EDISON GAS ENGINEERING WAS NOTIFIED AND DEVELOPED AN ISOLATION PLAN INVOLVING CLOSURE OF DISTRIBUTION MAIN VALVE (MV) 94461 AND EXCAVATION OF A FIRE BANK AT INTERVALE AVENUE AND FOX STREET, OVER A 4-INCH LPPE GAS MAIN (INSTALLED IN 1988). CON EDISON GAS CONTROL WAS NOTIFIED AND REPORTED NORMAL OPERATING CONDITIONS AT NEARBY GAS REGULATOR STATION GR-128. AT 11:19, GDS ARRIVED AND BEGAN INVESTIGATING. GDS CORRECTED THE ADDRESS TO 869 FOX STREET AND CONFIRMED THAT A BUILDING EXPLOSION HAD OCCURRED AT THAT LOCATION. GDS ALSO REPORTED HAVING NO ACCESS TO THE HOS VALVE OR OUTDOOR METER SET AT 869 FOX STREET, WHICH IS SUPPLIED BY A 1 1/4-INCH LPPE GAS SERVICE LINE (INSTALLED IN 1986). GERC PROVIDED GDS WITH THE LOCATION OF MV 94461 (AT THE INTERSECTION OF TIFFANY STREET & FOX STREET). AT 11:48, GDS CLOSED MV 94461 TO BEGIN ISOLATING AND SHUTTING DOWN THE GAS MAIN. CON EDISON GAS CONSTRUCTION CREWS ARRIVED AND BEGAN EXCAVATING A FIRE BANK OVER THE 4-INCH LPPE GAS MAIN AT THE SOUTHEAST CORNER OF INTERVALE AVENUE AND FOX STREET. GDS CONDUCTED A SPECIAL SURVEY OF THE AREA AND DID NOT DETECT ANY NATURAL GAS LEAKS OR ODORS. ALL SUBSURFACE STRUCTURES AND TEST POINTS CHECKED DURING THE SPECIAL SURVEY WERE FOUND CLEAR OF NATURAL GAS READINGS. THE SPECIAL SURVEY WAS CONDUCTED WHILE THE GAS MAIN AND SERVICE LINES ON THE BLOCK WERE IN SERVICE AND BEFORE THEY WERE SHUT DOWN. GDS ALSO TOOK PRESSURE AND ODORANT READINGS AT 858 FOX STREET; BOTH WERE WITHIN ACCEPTABLE RANGE (7.9 INCHES WC FOR PRESSURE; 0.29% GAS-IN-AIR FOR ODORANT). AT 13:03, CON EDISON GAS CONSTRUCTION CREWS INSTALLED A SQUEEZE-OFF ON THE 4-INCH LPPE GAS MAIN IN THE FIRE BANK EXCAVATION, SHUTTING DOWN THE MAIN AND INTERRUPTING GAS SERVICE TO 18 SINGLE-FAMILY BUILDINGS. GAS CONSTRUCTION CREWS THEN CUT AND CAPPED THE SERVICE LINES SUPPLYING 865, 867 AND 869 FOX STREET. AT 18:48, GDS OPENED MV 94461, REINTRODUCING GAS INTO THE MAIN UP TO THE SQUEEZE-OFF. GDS CONDUCTED A DP-IR SURVEY OVER THE MAIN AND SERVICES LINES AND DID NOT DETECT ANY LEAKS. AT 19:08, GDS REMOVED THE SQUEEZE-OFF AND PERFORMED AN ADDITIONAL DP-IR SURVEY OF THE MAIN AND SERVICE LINES WITHOUT DETECTING ANY LEAKS. RESTORATION WAS COMPLETED AT 20:52. ON 1/18/22 AT 17:40, NYPD ARSON AND EXPLOSION SQUAD DETECTIVE DIMARE REPORTED THAT THE SOURCE OF THE EXPLOSION WAS UNKNOWN AND UNDER INVESTIGATION. ON 1/19/22 AT 10:39, FDNY CHIEF SAROCCO REPORTED THAT NATURAL GAS WAS BELIEVED TO BE INVOLVED WITH THE EXPLOSION. THERE IS, HOWEVER, NO INDICATION OF CON EDISON JURISDICTIONAL PIPING BEING INVOLVED AT THIS TIME. THIS INCIDENT REMAINS UNDER INVESTIGATION BY THE FDNY AND NYPD. THE EXPLOSION RESULTED IN TEN INJURIES AND ONE FATALITY, AND GREATER THAN $50,000 IN PROPERTY DAMAGE. PHSMA, DPS STAFF, AND NYCDEP WERE NOTIFIED AND UPDATED. NTSB INQUIRED AND WAS UPDATED. MEDIA WAS ON LOCATION.
2024-05-31 11:04 | NO | YES | NO | 20220015 | 36773 | 2022-02-23 19:59 | SUPPLEMENTAL FINAL | 6243 | HAWAII GAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2022-01-24 11:15 | HAWAII-ALEUTIAN | NO | 2022 | WAIAKAMILO ROAD (BETWEEN HART ST & KALANI ST) | HONOLULU | HONOLULU | HI | 96817 | 21.3224 | -157.8782 | YES | [8 empty] | 2022-01-24 12:30 | 1327229 | 1327369 and 1327376 | SYNTHETIC GAS |  | 550 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 100 | 2022-01-24 09:02 | YES | OPERATOR | 2022-01-24 10:19 | 2022-01-24 09:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1940 | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.625 | [6 empty] | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 4 LOCATION | 100000 | 102180.3278688525 | 25000 | 25545.081967213125 | 20000 | 20436.0655737705 | 0 | 0 |  | 46.67 | 25669 | 19708.1291727140783744557329462989840348 | 0 | 0 | 170669 | 77315.490018796569013062409288824383164 | 167869.6045825502033744557329462989840348 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | 33 | 50 | 192.619(C) | 1999-03-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | SEWER (SANITARY/STORM) | YES | 22000022 |  |  | UNKNOWN/OTHER | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [167 empty] | YES |  |  | CHRISTOPHER HALL | IMP ENGINEER | chall@hawaiigas.com | 808-594-5553 |  | CHRIS HALL | chall@hawaiigas.com | 808-594-5553 | KEVIN NISHIMURA | VICE PRESIDENT OPERATIONS | 808-594-5573 | knishimu@hawaiigas.com | INCIDENT SUMMARY ON MONDAY, JANUARY 24, 2022, FRANK COLUCCIO CONSTRUCTION ("FCC") WAS PERFORMING A SEWER INSTALLATION ON A PORTION OF WAIAKAMILO ROAD IN HONOLULU, HAWAII, WITH AN AUGER. AT APPROXIMATELY 9:02 A.M., ON THE PORTION OF WAIAKAMILO ROAD BETWEEN HART STREET AND KALANI STREET, THE AUGER STRUCK A HAWAI'I GAS ("HG") UNDERGROUND 8-INCH PIPELINE ("SUBJECT SEGMENT"). THE AUGER CAUSED AN APPROXIMATELY 3-INCH LONG FRACTURE ALONG THE TOP OF THE PIPELINE. THE SUBJECT SEGMENT BEGAN TO LEAK GAS. HG'S FIRST RESPONDER ARRIVED ON SITE AT APPROXIMATELY 9:15 A.M. AND CONFIRMED THE DAMAGE TO THE SUBJECT SEGMENT. DUE TO THE MAGNITUDE OF THE LEAK, HG CALLED THE HONOLULU FIRE DEPARTMENT ("HFD") AT APPROXIMATELY 10:19 A.M. TO ASSIST IN SECURING THE ROADWAY AND TO HELP MONITOR THE HOT ZONE. HG'S MAINTENANCE CREW ARRIVED ON SITE AT APPROXIMATELY 10:30 A.M. AND BEGAN ASSESSING REPAIRS. AT APPROXIMATELY 11:15 A.M., HFD BEGAN EVACUATING NEARBY COMMERCIAL BUILDINGS. HG WAS ABLE TO STOP THE FLOW OF GAS TO THE SUBJECT SEGMENT AT APPROXIMATELY 5:35 P.M., JANUARY 24, 2022. FINAL REPAIRS WERE COMPLETED AT APPROXIMATELY 11:00 P.M., JANUARY 24, 2022. HAWAI'I GAS INVOLVEMENT PRIOR TO INCIDENT HG INSTALLED THE SUBJECT SEGMENT IN 1940. THE SUBJECT SEGMENT IS AN 8-INCH BARE STEEL PIPE. HG MAPS AND RECORDS CONTAIN NO INDICATION THAT THE SUBJECT SEGMENT WAS REPAIRED, ALTERED OR EXCAVATED SINCE ITS INSTALLATION. ON MONDAY, JANUARY 3, 2022, FCC SUBMITTED ONE CALL TICKET NUMBER 22000022 TO THE HAWAII ONE CALL CENTER INDICATING THAT FCC WOULD BE EXCAVATING "ON WAIAKAMILO ROAD BETWEEN DILLINGHAM BOULEVARD AND HART STREET (EWA SIDE OF ROAD)" ("EXCAVATION AREA"). IN RESPONSE TO TICKET NO. 22000022, HG REVIEWED GIS MAPS OF THE EXCAVATION AREA AND DETERMINED THAT AN UNDERGROUND MAIN LINE WAS LOCATED WITHIN THAT AREA. ON JANUARY 10, 2022, HG PERSONNEL ATTEMPTED TO PERFORM TONING ON THE UNDERGROUND MAIN LINE IN THE EXCAVATION AREA BUT NOTED THAT THE LOCATION OF THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL. ALSO, PLEASE NOTE THAT THIS INVESTIGATION IS STILL ONGOING. UPDATE 6/10/2022 UPON COMPLETION OF THE INVESTIGATION BY HG, IT WAS DETERMINED THAT TONING OF THE SUBJECT SEGMENT WAS PERFORMED INADEQUATELY BY HG. AS INDICATED IN THE "INCIDENT SUMMARY" SECTION ABOVE, THE UNDERGROUND MAIN LINE HAD ALREADY BEEN MARKED BY ANOTHER PARTY IN YELLOW PAINT AND HG FAILED TO CONFIRM THE MARKINGS WERE CORRECT WHEN RESPONDING TO TICKET NO. 22000022. AS A RESULT OF THE INVESTIGATION, HG HAS INCORPORATED THE FOLLOWING MITIGATIVE ACTIONS INTO ITS TONING OPERATIONS AS OF MAY 2022: 1. REVISE "HG ONE CALL PIPE LOCATION GUIDELINES" DOCUMENT. A. ALL PAINTED UTILITY MARKINGS BY HG WILL HAVE A UNIQUE HG IDENTIFIER. B. ALL EXISTING UTILITY MARKINGS (WHETHER BY HG OR 3RD PARTY) SHALL BE REVERIFIED IN RESPONSE TO AN 811 TICKET. 2. UPDATE TRAINING REQUIREMENTS FOR ALL HG EMPLOYEES WHO CONDUCT UTILITY LOCATIONS. A. INITIAL TRAINING REQUIREMENTS (OQ & "HG ONE CALL PIPE LOCATION GUIDELINES" DOCUMENT REVIEW). B. REFRESHER TRAINING REQUIREMENTS (PIPE LOCATION REFRESHER TRAINING TO BE PROVIDED IN 2022 AND EVERY 3 YEARS AFTER OR WHEN PROBABLE CAUSE IS DETERMINED BY HG MANAGEMENT). C. DOCUMENTATION RETENTION REQUIREMENTS. HG IS CONFIDENT THE MITIGATIVE ACTIONS LISTED ABOVE WILL HELP TO FURTHER REDUCE TONING RELATED INCIDENTS GOING FORWARD. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL.
2024-05-31 11:04 | NO | YES | YES | 20220016 | 36388 | 2022-02-25 10:24 | ORIGINAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-01-27 10:58 | EASTERN | YES | 2022 | 217 BOSWELL RD | BALTIMORE | BALTIMORE COUNTY | MD | 21229 | 39.2819 | -76.7044 | [7 empty] | YES | TWO LEAKING CAST IRON JOINTS WERE ENCAPSULATED AND RENEWED ONE CAST IRON SERVICE AT INCIDENT | 2022-01-27 19:17 | 1327461 | N/A | NATURAL GAS |  | 0.003 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-01-27 10:28 | ALLOWED TO BURN OUT |  | 0 | YES | 0 | 2022-01-27 10:59 |  |  |  | 2022-01-27 11:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1920 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 12000 | 12261.6393442623 | 1200 | 1226.16393442623 | 0 | 0 | EMERGENCY RESPONSE PERSONNEL AND EQUIPMENT | 4.45 | 0 | 0 | 0 | 0 | 13200 | 5698.721311475412 | 13487.80327868853 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 10 | 10 | 10 | 192.623 | 1920-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | LEAKING CAST IRON JOINT | [11 empty] | YES | GAS FROM A LEAKING CAST IRON JOINT IGNITED CAUSING A MANHOLE COVER TO LIFT STRIKING A BALTIMORE CITY WELDING CONTRACTOR. |  | YES |  |  |  | OTHER | PACKING MATERIAL USED TO SEAL CAST IRON JOINTS DRIED RELEASING NATURAL GAS | NO | [86 empty] | JEFFREY WEATHERHOLTZ | MANAGER - GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-470-8858 | 410-470-9549 |  |  |  | DANIEL A NORDEN | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | 410-470-6435 | daniel.a.norden@bge.com | ON 1/27/2022, A CITY OF BALTIMORE CONTRACTOR WAS WELDING ON A WATER MAIN ON FREDERICK AVENUE NEAR THE INTERSECTION OF BOSWELL ROAD. WHILE PERFORMING THE WELDING OPERATION, AN IGNITION OCCURRED WHICH CAUSED A NEARBY MANHOLE COVER TO RAISE AND STRIKE A NEARBY CONTRACTOR, CAUSING INJURY TO THE CONTRACTOR'S FOOT AND REQUIRING OVERNIGHT IN-PATIENT HOSPITALIZATION. NATURAL GAS WAS CONFIRMED IN THE LOCALIZED AREA AND SURVEYS WERE IMMEDIATELY CONDUCTED TO FIND THE SOURCE OF THE LEAK. AN ADJACENT MEDIUM PRESSURE 12" CAST IRON NATURAL GAS MAIN WAS FOUND TO HAVE TWO LEAKY JOINTS AND THEY WERE SUBSEQUENTLY REPAIRED AS WELL AS RENEWING AN INTERCONNECTED NATURAL GAS SERVICE LINE. POST-INCIDENT SURVEYS WERE COMPLETED, AND NO READINGS WERE DETECTED SUCH THAT THE JOB COULD BE CLOSED OUT.. NOTE : PART A 21C IS NOTED AS 0.0 HOWEVER ACTUAL (MCF) IS 0.003.TO MATCH PART A 7. THIS ONLINE FORM WILL NOT ACCEPT THAT NUMBER.
2024-05-31 11:04 | NO | YES | NO | 20220017 | 36393 | 2022-02-25 16:16 | ORIGINAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2022-01-27 08:10 | CENTRAL | NO | 2022 | 8500 E PARMER LANE | MANOR | TRAVIS | TX | 78653 | 30.3511 | -97.5885 | YES | [8 empty] | 2022-01-27 08:32 | 1327404 | 1327531 | NATURAL GAS |  | 25858 | 0.71 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-27 01:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-27 00:42 | 2022-01-27 01:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2016 | 2015 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.237 | [6 empty] | OTHER | [8 empty] | THIRD PARTY VEHICLE STRUCK ABOVE GROUND STATION PIPING AND SHEERED FABRICATION AT 2 CIRCUMFERENTIAL WELDS BETWEEN PIPE AND REDUCERS. | CLASS 1 LOCATION | 0 | 0 | 250000 | 255450.81967213125 | 1115 | 1139.310655737705375 | 0 | 0 |  | 5.78 | 149459 | 114751.5399129172714078374455732946298984 | 4 | 3.0711175616835994194484760522496371553 | 400578 | 194098.0323996526619758345428156748911466 | 371344.7413583479103822568940493468795356 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 707 | 707 | 778 | 192.621 M | 2016-01-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE TO THE REGULATOR STATION BY THIRD-PARTY VEHICLE INITIATED SCADA ALARMS IN CONTROL ROOM. CONTROLLER FOLLOWED PROCEDURES TO INVESTIGATE ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 60 | YES |  | YES | [116 empty] | YES | [23 empty] | AMY MARK | REGULATORY COMPLIANCE SPECIALIST | amy.mark@onegas.com | 512-407-1571 |  | BRYAN WEEKS | bryan.weeks@onegas.com | 512-407-1529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 512-407-1529 | bryan.weeks@onegas.com | THIRD-PARTY VEHICLE RAN OFF THE ROADWAY TRAVELING WESTBOUND ON EAST PARMER LANE AT A HIGH SPEED AND CRASHED THROUGH FENCING, CONCRETE-FILLED STEEL BOLLARD POSTS WITH WELDED STEEL CROSSBARS, AND THE TEXAS GAS SERVICE (TGS) REGULATOR STATION AT SUBJECT LOCATION BEFORE DAMAGING AND COMING TO REST AGAINST ATMOS ENERGY'S METERING STATION, WHICH FEEDS TGS'S STATION AND DISTRIBUTION SYSTEM. THE VEHICLE'S IMPACT CAUSED THE PIPING TO SEPARATE, LEADING TO AN UNINTENTIONAL RELEASE OF GAS FROM THE INLET AND OUTLET SIDES OF TGS'S REGULATOR STATION. AFTER DAMAGING THE ATMOS ENERGY METERING STATION, THE VEHICLE CAME TO REST ON TOP OF THE ATMOS ENERGY PIPING. ATMOS ENERGY'S MEASUREMENT INSTRUMENTATION WAS DAMAGED AND COULD NOT PROVIDE A VOLUME OF GAS THAT FLOWED THROUGH THE STATION DURING AND AFTER THE INCIDENT. TGS HAS NO KNOWLEDGE OF THE DAMAGE ESTIMATES FOR ATMOS FACILITIES OR THE VEHICLE AT FAULT FOR THE INCIDENT.
2024-05-31 11:04 | NO | YES | NO | 20220018 | 36409 | 2022-03-02 10:16 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2022-02-01 07:42 | EASTERN | YES | 2022 | CUMBERLAND HILL RD BET AUGUSTINE ST AND FOUNDERS DR | WOONSOCKET | PROVIDENCE | RI | 02895 | 41.9925 | -71.4864 | [6 empty] | YES |  |  | 2022-02-02 19:28 | 1327936 | 1328004 | NATURAL GAS |  | 8500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 60 | 2022-02-02 11:00 | YES | OPERATOR | 2022-02-01 11:00 | 2022-02-01 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 25 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN - POSSIBLE OXYACETYLENE | 0.375 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 27 | 0.1 |  | CLASS 4 LOCATION | 0 | 0 | 300000 | 306540.9836065575 | 50000 | 51090.16393442625 | 0 | 0 |  | 7.21 | 61285 | 47053.3599419448476052249637155297532656 | 0 | 0 | 411285 | 186236.8204097171574746008708272859216255 | 404684.5074829285976052249637155297532656 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 47.9 | 50 | 60 | 192.621 M | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT CAUSE WAS A CRACK IN A WELD. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | [146 empty] | BUTT WELD |  |  | PIPE | [28 empty] | YES | [11 empty] | YES |  |  |  | NO | [55 empty] | YES | [30 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | JOSEPH F. CURLEY | joseph.curley@nationalgrid.com | 4013329815 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | THIS EVENT WAS DISCOVERED IN RESPONSE TO AN ODOR CALL FROM A COMMERCIAL LOCATION AT FORTIN DRIVE IN WOONSOCKET, RI RECEIVED AT APPROX. 11:00 AM ON 2/1/2022. TWO RESPONDERS INITIALLY RESPONDED AND REQUESTED ADDITIONAL SUPPORT TO LOCATE THE LEAK WITH BLOWING GAS AT CUMBERLAND HILL ROAD. ADDITIONAL SUPPORT ARRIVED TO HELP LOCATE THE LEAK AS WELL AS MUTUAL AID PERSONNEL. ADDITIONAL CREWS WORKED OVERNIGHT INTO THE NEXT DAY TO CONTINUE WORK IN LOCATING THE LEAK. ENGINEERING REVIEWED FACILITY MAPS TO DETERMINE THE APPROPRIATE ISOLATION VALVES TO SHUT OFF GAS SUPPLY AND INITIATE REPAIRS WHILE CREWS WORKED TO LOCATE THE IDENTIFIED VALVES; HOWEVER, SIGNIFICANT SNOWFALL FROM 01/28 THROUGH 1/30/22 HINDERED THE CREWS' EFFORTS. DUE TO THE SCOPE OF THE PROJECTED CUSTOMER IMPACT, A DECISION WAS MADE TO ISOLATE THE AFFECTED MAIN USING WELDED STOPPLE FITTINGS. AT 8:00 PM ON 2/2/2022 THE LEAK WAS SECURED. TWO BUILDINGS WERE EVACUATED, WITH AN ESTIMATED 50-60 PEOPLE IN THESE COMMERCIAL PROPERTIES AS ESTIMATED BY THE FD. APPROXIMATELY 5'6" OF 12" STEEL PIPE WERE REPLACED WITH PLASTIC. WE ARE REPORTING THIS INCIDENT SOLELY BASED ON THE VOLUME OF GAS RELEASED. NO INJURIES WERE INVOLVED IN THIS INCIDENT AND RESPONSE AND RESTORATION COSTS ARE RELATED TO THE REPAIR OF THE MAIN AND RESTORATION OF TWO CUSTOMERS THAT WERE SHUT OFF DURING THE RESPONSE.
2024-05-31 11:04 | NO | YES | NO | 20220019 | 36639 | 2022-03-03 13:41 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2022-02-16 10:20 | EASTERN | NO | 2022 | 944 MCELHANEY ROAD | TRAVELERS REST | GREENVILLE | SC | 29690 | 34.9544 | -82.4665 | [6 empty] | YES |  |  | 2022-02-16 15:27 | 1329042 | 1329121 | NATURAL GAS |  | 8710 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-16 10:20 | NO |  |  | 2022-02-16 11:39 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | M10048 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 226000 | 230927.54098360665 | 70000 | 71526.22950819675 | 0 | 0 |  | 4 | 34840 | 26749.4339622641509433962264150943396226 | 0 | 0 | 330840 | 147763.0931023817373584905660377358490566 | 329203.2044540675509433962264150943396226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 250 | 192.619(A)(2) | 1962-06-25 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | UTILITY | BORING | WATER | YES | 2112131188 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | THE USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES. WATER COMPANY CONTRACTOR WAS ON A SITE TO INSTALL WATER SERVICE TO A CUSTOMER. TAPPING WHAT THEY BELIEVED WAS THE WATER MAIN, WAS INSTEAD AN 8" HIGH PRESSURE GAS MAIN. THE WATER CONTRACTOR STOPPED WHEN GAS WAS RELEASED AND REPORTED A GAS LEAK.
2024-05-31 11:04 | NO | YES | NO | 20220020 | 36425 | 2022-03-04 14:28 | ORIGINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2022-02-04 07:30 | EASTERN | NO | 2022 | 65 BAY 35TH STREET | BROOKLYN | KINGS | NY | 11232 | 40.6735 | -74.009 |  |  | YES | [6 empty] | 2022-02-04 08:55 | 1328059 | 1328218 | NATURAL GAS |  | 5.092 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-04 07:31 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2022-02-04 07:31 |  |  |  | 2022-02-04 07:54 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN - OEM ARRIVED ONSITE AFTER THE EVENT; NATIONAL GRID ARRIVED APPROX. 20 MINUTES LATER. CAUSE IS UNDER INVESTIGATION | CLASS 4 LOCATION | 750000 | 766352.45901639375 | 7107 | 7261.955901639347175 | 8300 | 8480.9672131147575 | 0 | 0 |  | 7.47 | 38 | 29.17561683599419448476052249637155297533 | 0 | 0 | 765445 | 330464.2990483952812023657474600870827286 | 782124.557747983848869484760522496371553 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 9 | 9.1 | 12 | 192.623 | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | NATIONAL GRID DISPATCH WAS NOTIFIED ON 02/04/22 AT 7:23 AM FROM THE OFFICE OF EMERGENCY MANAGEMENT THAT AN EXPLOSION HAD OCCURRED AT 67 BAY 35TH STREET, BROOKLYN NY. THE EXPLOSION FULLY DESTROYED 65 BAY 35TH STREET AND PARTIALLY DAMAGED 69 BAY 35TH STREET, CAUSING IT TO PARTIALLY COLLAPSE. SERVICES AT 65, 69 AND 71 BAY 35TH STREET WERE CUT OFF AT THE MAIN. WITH RESPECT TO PART E, QUESTION 3A, THE MAOP WAS ESTABLISHED IN ACCORDANCE WITH 49 CFR 192.623, EFFECTIVE IN 1970; HOWEVER THE PIPELINE WAS PREDOMINANTLY INSTALLED IN 1965. THREE HOMES WERE DAMAGED AND/OR DEMOLISHED AS A RESULT OF THIS INCIDENT. AT THIS TIME, WE CANNOT ESTIMATE THE COST OF THIS DAMAGE, BUT LIKELY TO EXCEED THE $750,000 PROVIDED IN PART D. THIS INCIDENT IS STILL UNDER INVESTIGATION AND NATIONAL GRID HAS NOT BEEN GRANTED ACCESS AT THIS POINT.
2024-05-31 11:04 | NO | YES | NO | 20220022 | 36437 | 2022-03-08 09:39 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-02-08 07:45 | CENTRAL | NO | 2022 | 11699 NW H K DODGEN LOOP | TEMPLE | BELL | TX | 76504 | 31.1412 | -97.3446 | YES | [5 empty] | YES |  |  | 2022-02-08 18:41 | 1328466 | 1328674 | NATURAL GAS |  | 5036 | 18 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 07:45 | YES | OPERATOR | 2022-02-08 08:05 | 2022-02-08 08:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 65 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1985 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 11 | 1 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 104000 | 106267.5409836066 | 0 | 0 | 0 | 0 |  | 8.17 | 41144 | 31589.5152394775036284470246734397677794 | 147 | 112.863570391872278664731494920174165457 | 145291 | 68570.9249565776182293178519593613933236 | 137969.9197934759759071117561683599419449 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 168 | 168 | 200 | 192.619(A)(2) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2252816180 | TEXAS811 |  | CONTRACT LOCATOR | NO | YES | 20 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | DALE GAMBRELL | COMPLIANCE SUPERVISOR | dale.gambrell@atmosenergy.com | 512-844-8270 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-957-3295 | marlo.sutton@atmosenergy.com | AT 07:45 ON FEBRUARY 8, 2022, A THIRD PARTY CONTRACTOR DAMAGED A 6" ATMOS DISTRIBUTION LINE WITH A TRACKHOE AT 11699 NW H K DODGEN LOOP IN TEMPLE TX, CAUSING A RELEASE OF GAS. THE DAMAGE CAUSED AN INTERRUPTION IN SERVICE FOR 1 CUSTOMER; CNG WAS BROUGHT IN TO SHORE UP SERVICE FOR OTHER CUSTOMERS. GAS LOSS EXCEEDED THE REPORTING THRESHOLD. SERVICE WAS RESTORED AT 03:32 ON FEBRUARY 9, 2022. IT WAS DETERMINED THAT THE PIPELINE WAS NOT MARKED BY THE LOCATOR.
2024-05-31 11:04 | NO | YES | NO | 20220024 | 37266 | 2022-03-25 16:52 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-02-08 14:27 | EASTERN | NO | 2022 | PORTAGE | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2816 | -85.5722 | [5 empty] | YES |  | YES | SQUEEZE-OFF ISOLATION NORTH END PIPELINE SEGMENT & BAGGING OFF ISOLATION SOUTH END PIPELINE SEGMENT | 2022-02-25 09:33 | 1329679 | 1329801 | NATURAL GAS |  | 2277 | 0.007 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-02-08 14:27 | NO |  |  | 2022-02-08 14:44 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1901 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 332405 | 339652.518852459152625 | 318 | 324.93344262295095 | 0 | 0 |  | 4.48 | 10201 | 7832.117561683599419448476052249637155298 | 0 | 0 | 342924 | 149491.7884376264553632365747460087082729 | 347809.5698567657029944484760522496371553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 1 | 192.623 | 1901-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | EROSION OF SUPPORT DUE WATER AND ROADWAY CONSTRUCTION IN THE AREA RESULTING IN LESS THAN ADEQUATE COMPACTION AND SUPPORT OF THE NATURAL GAS PIPELINE. | [154 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON TUESDAY, FEBRUARY 8, 2022, AT APPROXIMATELY 14:27 HOURS CONSUMERS ENERGY WAS NOTIFIED BY OUR LEAK SURVEY CONTRACTOR (PERFORMING A DISCRETIONARY LEAK SURVEY) OF A POSSIBLE LEAK AT/NEAR 1004 PORTAGE ROAD, (KALAMAZOO COUNTY) KALAMAZOO, MI. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 14:44 HOURS AND CONFIRMED READS WHICH REQUIRED AN IMMEDIATE RESPONSE. A DISTRIBUTION CREW (CREW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 16:39 HOURS. THE CREW HAD RECENTLY COMPLETED A LEAK REPAIR ON A 6" CAST IRON PIPELINE AND BASED ON A PRELIMINARY INVESTIGATION AT THE SITE THOUGHT THE SOURCE COULD POTENTIALLY BE RESIDUAL GAS FROM THE INITIAL REPAIR. EXTRACTION EQUIPMENT WAS MOBILIZED TO REMOVE RESIDUAL GAS BUILD UP WHILE GSW'S AND THE CREW CONTINUED PINPOINTING TO DETERMINE IF THE SOURCE COULD BE ADDITIONAL LEAKS ON THE PIPELINE. OVER SEVERAL WEEKS, MULTIPLE LEAKS WERE DISCOVERED ON THE CAST IRON PIPELINE. THE FAILURE INVESTIGATION DETERMINED, THE RECENT (2021) WATER AND ROAD CONSTRUCTION LED TO REDUCED COMPACTION AND SUPPORT OF THE CAST IRON PIPELINE CAUSING MULTIPLE LEAKS OVER TIME. ALL IDENTIFIED LEAKS WERE REPAIRED, AND EXTRACTION EQUIPMENT WAS SIMULTANEOUSLY USED TO REMOVE RESIDUAL GAS FROM THE SOIL. CONSUMERS ENERGY PERSONNEL MONITORED THE SITE UNTIL ALL GAS READS WERE ZERO. A PIPELINE REPLACEMENT PROJECT, WHICH WOULD HAVE INCLUDED RETIRING THE 6-INCH CAST IRON PIPELINE WAS SCHEDULED FOR 2023. HOWEVER DUE TO THE AGE AND CONDITION OF THE PIPELINE A PORTION OF THE REPLACEMENT PROJECT WAS EXPEDITED, AND CONSTRUCTION STARTED IN APRIL. FEBRUARY 25, 2022 CE RETIRED APPROXIMATELY 1100' OF THE CAST IRON PIPELINE THAT WAS COMPROMISED BECAUSE OF THE WATER AND ROAD CONSTRUCTION ACTIVITIES THAT OCCURRED IN 2021.
2024-05-31 11:04 | NO | YES | NO | 20220025 | 36533 | 2022-03-31 18:46 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2022-03-01 10:37 | CENTRAL | NO | 2022 | 3 MILLERS CT | O'FALLON | SAINT CHARLES | MO | 63366 | 38.7758 | -90.7291 | [5 empty] | YES |  |  |  | 2022-03-01 12:33 | 1329957 | 1330159 | NATURAL GAS |  | 104.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-01 11:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 45 | YES | 3 | 2022-03-01 10:37 | NO |  |  | 2022-03-01 10:59 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 663261 | 677722.264426229780025 | 0 | 0 | 500 | 510.9016393442625 | 0 | 0 |  | 6.12 | 641 | 492.146589259796806966618287373004354136 | 0 | 0 | 664402 | 286927.2512839944936428011611030478955007 | 678725.3126548338393319666182873730043541 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 39.77 | 40 | 60 | 192.621 M | 2002-12-02 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 220521245 |  |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY TELECOMMUNICATIONS EXCAVATOR STRUCK A 2-INCH PLASTIC GAS MAIN WHILE BORING. THE EXCAVATOR HAD VALID LOCATES AND THE MAIN WAS MARKED WITHIN TOLERANCE BUT THE EXCAVATOR FAILED TO POT-HOLE THE BORE CROSSING. THE COMPANY IDENTIFIED GAS READINGS IN TWO HOMES UPON ARRIVAL AND EVACUATED BOTH RESIDENCES. WHILE CREWS WERE WORKING TO SHUT DOWN THE MAIN 3 MILLERS CT EXPLODED AND SUBSEQUENTLY CAUGHT FIRE. CREWS IMMEDIATELY SHUT DOWN THE MAIN FOLLOWING THE EXPLOSION. THE EXPLOSION CAUSED DAMAGE TO SEVERAL NEARBY HOMES AND THE FIRE SPREAD TO 5 MILLERS CT. THE DAMAGED GAS MAIN WAS REPLACED WITH A 15-FOOT SEGMENT OF 2-INCH PLASTIC. GAS SERVICE WAS INTERRUPTED AT 21 HOMES AND 2 HOMES WERE CONDEMNED. A 48 HOUR UPDATE TO THE NRC WAS MADE ON MARCH 3, 2021 AT 13:38. REPORT NUMBER 1330159.
2024-05-31 11:04 | NO | YES | NO | 20220026 | 36557 | 2022-04-06 09:33 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-03-10 09:18 | CENTRAL | NO | 2022 | ENTIRE CITY | SEGUIN | GUADALUPE | TX | 78155 | 29.5701 | -97.9641 |  | YES |  | YES | [5 empty] | 2022-03-10 09:18 | 1330725 | 1331011 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-08 10:30 | NO |  |  | 2022-03-08 13:00 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | LOSS OF GAS SUPPLY FROM SUPPLIER | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1121224 | 1145670.3593442627546 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1121224 | 484056.29573770510184 | 1145670.3593442627546 | 0 | 0 | 4300 | 0 | 0 | 4300 | 0 | 0 | 0 | 0 | 192.619(A)(1) | 2022-03-08 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | NOTIFICATION FROM SUPPLIER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOSS OF GAS SUPPLY FORM SUPPLIER | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM SUPPLIER | [47 empty] | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 |  | MICHAEL MAXWELL | mike.d.maxwell@centerpointenergy.com | 830-643-6914 | RANDALL SANDERS | REGIONAL OPERATIONS DIRECTOR TEXAS | 713-207-5728 | randall.x.sanders@centerpointenergy.com | LOSS OF GAS SUPPLY FROM ENTERPRISE PIPELINE TO CENTERPOINT ENERGY DISTRIBUTION SYSTEM IN SEGUIN, & MCQUEENEY, TEXAS, FORCED CENTERPOINT ENERGY TO PERFORM RE-LITE OF APPROXIMATELY 4300 CUSTOMERS.
2024-05-31 11:04 | NO | YES | NO | 20220027 | 36876 | 2022-04-06 09:44 | SUPPLEMENTAL FINAL | 13302 | NATIONAL GAS & OIL CORP | 1500 GRANVILLE ROAD | NEWARK | OH | 43055 | 2022-02-23 15:22 | EASTERN | YES | 2022 | 811 BLACKS RD SE | HEBRON | LICKING | OH | 43025 | 39.9878 | -82.5205 |  |  | YES | YES | [5 empty] | 2022-02-23 15:22 | 1329557 |  | NATURAL GAS |  | 7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-23 13:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7 | YES | 1 | 2022-02-23 14:10 | YES | OPERATOR | 2022-02-23 13:51 | 2022-02-23 14:17 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 1998 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 277236 | 283280.6537704919169 | 0 | 0 | 5000 | 5109.016393442625 | 0 | 0 |  | 39 | 273 | 209.603773584905660377358490566037735849 | 0 | 0 | 282509 | 122003.8054995360809109433962264150943396 | 288599.2739375194475603773584905660377358 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 44 | 44 | 60 | 192.619(A)(1) | 1998-04-24 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 7 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL LEAK OF THIS KIND WAS NOT DETECTABLE ON SUCH A LARGE SYSTEM THAT IS MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | [56 empty] | TREES/VEGETATION ROOTS | [5 empty] | NO | [188 empty] | YES | [29 empty] | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | cstorts@theenergycoop.com | 740-348-1203 | 740-348-1131 |  |  |  | CHRISTOPHER STORTS | COMPLIANCE ENGINEER | 740-348-1203 | cstorts@theenergycoop.com | ON WEDNESDAY, FEBRUARY 23, 2022, A HOMEOWNER REPORTED AN EXPLOSION AND CALLED 911. NATIONAL GAS & OIL COOPERATIVE WAS NOTIFIED APPROXIMATELY 10 MINUTES LATER. WHEN COOPERATIVE EMPLOYEES ARRIVED AT THE SCENE, THE SERVICE LINE CURB VALVE WAS SHUT AND THE FIRE DEPARTMENT EXTINGUISHED THE FLAMES. READINGS INDICATED THAT NATURAL GAS WAS PRESENT IN THE GROUND AROUND THE HOMEOWNER'S NATURAL GAS RISER. THE HOMEOWNER'S NATURAL GAS SERVICE LINE WAS TESTED AND LEAKAGE WAS FOUND AT THE RISER HEAD. ON TUESDAY, MARCH 22, 2022 AFTER ALL INSURANCE PARTIES AND FIRE AND EXPLOSION INVESTIGATORS COULD BE PRESENT, THE HOMEOWNER'S RISER WAS REMOVED AND THE SERVICE LINE CAPPED AT THE BASE OF THE RISER AND RETESTED. THE SERVICE LINE HELD THE PRESSURE TEST WITHOUT THE RISER. THE HOMEOWNER'S RISER WAS REMOVED AND SENT TO AN INDEPENDENT LABORATORY PLANNED FOR FURTHER INVESTIGATION (PLANNED FOR APRIL 21, 2022). THIS RISER WAS INSTALLED BY THE HOMEOWNER OR THE HOMEOWNER'S CONTRACTOR OR REPRESENTATIVE, NOT BY THE NATIONAL GAS & OIL COOPERATIVE. THE ROOT CAUSE OF THE EXPLOSION WAS DUE TO A PULLED RISER. A TREE ROOT APPROXIMATELY 6 FEET AWAY FROM THE BEND IN THE RISER GREW ACROSS THE SERVICE LINE. OVER TIME, THE ROOT PULLED THE SERVICE LINE MOST OF THE WAY OUT OF THE RISER CONNECTION, CAUSING A LEAK. THE HOUSE AT 811 BLACKS RD SE HAS BEEN TORE DOWN DUE TO THE DAMAGES CAUSED BY THE EXPLOSION. THE PUBLIC UTILITIES COMMISSION OF OHIO HAS COMPLETED THEIR INVESTIGATION AND WE, NATIONAL GAS AND OIL COOPERATIVE, ARE WAITING ON A COPY OF THEIR REPORT AS OF 7/19/2022.
2024-05-31 11:04 | NO | YES | NO | 20220028 | 36650 | 2022-04-08 10:32 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-03-10 14:50 | CENTRAL | NO | 2022 | 3307 89TH STREET | LUBBOCK | LUBBOCK | TX | 79412 | 33.513 | -101.8861 | [5 empty] | YES |  |  |  | 2022-03-10 16:55 | 1330768 | 1330843 | NATURAL GAS |  | 685 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-10 15:47 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 250 | YES | 7 | 2022-03-10 15:09 | YES | OPERATOR | 2022-03-10 15:09 | 2022-03-10 15:09 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 2.375 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 7938 | 8111.07442622951145 | 13455 | 13748.363114754103875 | 166000 | 169619.34426229515 | DAMAGE TO RESIDENCE. | 5.63 | 3857 | 2961.325108853410740203193033381712626996 | 6 | 4.60667634252539912917271407837445573295 | 191256 | 83116.1888766090387860232220609579100145 | 194444.7135884747014643323657474600870827 | 0 | 0 | 7 | 0 | 0 | 12 | 0 | 40 | 40 | 44 | 192.619(A)(2) | 2015-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 1 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2256245020 | TX811 |  | CONTRACT LOCATOR | YES | YES | 40 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 8062206849 |  | MIKE CULP | mike.culp@atmosenergy.com | 8062206849 | MIKE CULP | COMPLIANCE MANAGER | 8062206849 | mike.culp@atmosenergy.com | CITY OF LUBBOCK, TX WHILE REPAIRING A SEWER SERVICE LINE TO THE ASSOCIATED ADDRESS, CUT A 2" NATURAL GAS LINE WITH A BACKHOE. THE GAS LINE WAS CORRECTLY MARKED WITH PAINT AND FLAGS BEFORE START OF EXCAVATION. ATMOS ENERGY WAS NOTIFIED OF THE DAMAGED LINE AT 15:09 AND ARRIVED ON SCENE AT 15:16. REMOTE EXCAVATIONS SITES WERE USED TO SQUEEZE THE PE LINE AND SHUT THE FLOW OF GAS OFF, AREA WAS MADE SAFE AT 16:37. ATMOS ENERGY'S INVESTIGATION OF THIS INCIDENT IS CURRENTLY ONGOING.
2024-05-31 11:04 | NO | YES | NO | 20220029 | 36565 | 2022-04-08 11:56 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2022-03-09 16:22 | PACIFIC | NO | 2022 | 3817 N CRESTLINE ST | SPOKANE | SPOKANE | WA | 99207 | 47.6928 | -117.3791 | YES | [8 empty] | 2022-03-09 16:37 | 1330648 | 1330830 | NATURAL GAS |  | 45 | 22 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2022-03-03 18:08 | NO |  |  | 2022-03-03 19:03 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1956 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2000 | 2043.60655737705 | 177000 | 180859.180327868925 | 0 | 0 |  | 4.63 | 208 | 159.698113207547169811320754716981132075 | 102 | 78.31349782293178519593613933236574746009 | 179310 | 77455.8360893668950798258345428156748912 | 183140.7984962764539550072568940493468796 | 41 | 1 | 1127 | 0 | 0 | 1127 | 42 | 55 | 55 | 60 | 192.619(C) | 1956-06-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A PIPE LEAK THAT REQUIRED A SYSTEM OUTAGE TO REPAIR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2018-08-15 | NO | [12 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | JOSHUA FORT | SR. GAS ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | TIM HARDING | tim.harding@avistacorp.com | 509-495-2784 | BRIAN SCHULTZ | MANAGER - NAT. GAS COMPLIANCE AND INTEGRITY | 509-495-2162 |  | brian.schultz@avistacorp.com | THE SPOKANE CITY WATER DEPARTMENT RESPONDED TO A LEAKING WATER SERVICE AT 3817 N CRESTLINE ST. PRIOR TO EXCAVATING, THE WATER CREW SMELLED NATURAL GAS IN THE AREA THEY WERE GOING TO DIG. THEY CONTACTED AVISTA TO REPORT THE GAS ODOR. AN AVISTA FIRST RESPONDER ARRIVED AND DETERMINED THAT AN AVISTA CONSTRUCTION CREW WOULD NEED TO INVESTIGATE THE LEAK. THE AREA WAS EXCAVATED AND THE LEAK LOCATION WAS FOUND TO BE ON THE BOTTOM OF THE STEEL GAS MAIN. THE LEAK WAS COMING FROM A CRACK OR SMALL HOLE INSIDE THE DENT. THIS DENT WAS LIKELY CAUSED BY EXCAVATION DAMAGE SOMETIME IN THE PAST. TO REPAIR THE LEAK, THE CREW NEEDED TO WELD A STEEL FITTING OVER THE DENT. PRIOR TO WELDING ON THE FITTING, THE CREW ATTEMPTED REDUCE THE GAS FLOW FROM THE LEAK BY INSERTING A PLUG. UNFORTUNATELY THIS CAUSED THE LEAK RATE TO INCREASE AND IT WAS DECIDED THAT THE SYSTEM SHOULD BE SHUT DOWN TO SAFELY WELD ON THE REPAIR FITTING. TEN VALVES IN THE SYSTEM WERE CLOSED AT MIDNIGHT ON 3/4/22. THIS CAUSED AN OUTAGE FOR 1169 CUSTOMERS. THE STEEL MAIN REPAIR WAS COMPLETE AT 01:00 3/4/22. ALL GAS METERS IN THE SYSTEM WERE SHUT OFF, THE SYSTEM WAS PURGED OF ANY AIR, AND CUSTOMER RELIGHTS STARTED AT 14:00 ON 3/4/22. RELIGHTS WERE COMPLETE AT 17:00 ON 3/5/22 WITH THE EXCEPTION OF SOME CUSTOMERS WHOSE HOMES WE WERE UNABLE TO ENTER. ON 3/9/22 IS WAS DETERMINED THAT THE INCIDENT COST HAD EXCEEDED THE FEDERAL THRESHOLD AND IT WAS REPORTED TO PHMSA (NRC).
2024-05-31 11:04 | NO | YES | NO | 20220030 | 39125 | 2022-04-12 21:21 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-03-13 01:55 | EASTERN | YES | 2022 | 908 COLLEGE AVENUE | HOUGHTON | HOUGHTON | MI | 49931 | 47.1221 | -88.5626 |  | YES |  |  |  | YES |  |  |  | 2022-03-13 09:05 | 1330926 | NA | NATURAL GAS |  | 69.457 | 0.113 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-13 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 30 | 2022-03-13 01:55 |  |  |  | 2022-03-13 03:19 | 2022-03-13 03:49 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1966 | UNKNOWN |  |  |  |  | 2 | API 5L, SEAMLESS STEEL, GRADE B | UNKNOWN | STEEL |  | SEAMLESS |  | 0.17 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 500000 | 510901.6393442625 | 166100 | 169721.5245901640025 | 710001 | 725481.349672131438525 | 0 | 0 |  | 5.82 | 404 | 310.182873730043541364296081277213352685 | 1 | 0.7677793904208998548621190130624092888244 | 1376506 | 594324.3127677320298207402031930333817127 | 1406415.46425967840546621915820029027576 | 12 | 0 | 6 | 0 | 0 | 5 | 10 | 55 | 55 | 60 | 192.619(A)(2) | 1966-10-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RATE OF GAS VOLUME RELEASED WOULD NOT HAVE TRIGGERED ANY ALARMS OR AOCS THROUGH THE SCADA SYSTEM, AND THEREFORE THE CONTROLLERS WOULD NOT HAVE TAKEN ACTION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2021-07-20 | NO |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | MIB82061284 | GLADSTONE MICHIGAN | NO | FACILITY OWNER | UNKNOWN/OTHER | YES | 188 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | JENNIFER POND | MANAGER OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | MIKE KOSHT | michael.kosht@semcoenergy.com | (906) 250-7196 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | ON MARCH 13, 2022, AT 1:58, AM, SEMCO ENERGY GAS COMPANY RECEIVED A CALL FROM THE MICHIGAN STATE POLICE INDICATING 908 COLLEGE AVE., IN HOUGHTON, MI HAD EXPLODED. THE SEMCO TECHNICIAN ARRIVED ON SITE 21 MINUTES AFTER THE INITIAL CALL, (INDICATED TIME IS 3:19 AM DUE TO DAYLIGHT SAVINGS TIME CHANGING AT 2:00 AM ON MARCH 13TH). WHEN THE SEMCO TECHNICIAN ARRIVED, THE HOUGHTON FIRE DEPT. WAS ATTENDING TO A FIRE AT THE STRUCTURE. ONCE THE FIRE WAS UNDER CONTROL, THE TECHNICIAN WAS ABLE TO SECURE GAS AT THE GAS METER SET. THROUGH THE LEAK INVESTIGATION PROCESS, THE TECHNICIAN DETERMINED THERE WAS A PROBABLE UNDERGROUND LEAK BASED ON LEL READINGS FOUND AT THE REAR OF THE RESIDENCE. THE TECHNICIAN CONTINUED THE LEAK INVESTIGATION AND FOUND GAS READINGS AT SURROUNDING BUILDINGS AND EVACUATED BUILDINGS ON COLLEGE AVE. AND ON E LAKESHORE. GAS FLOW WAS THEN SHUTOFF IN THE AREA IN WHICH READINGS WERE FOUND AND GAS WAS PURGED IN THOSE AREAS TO REDUCE GAS TO SAFE LEVELS. AN INVESTIGATION INTO THE SOURCE OF THE GAS LEAK WAS CONDUCTED IN THE SPRING WHEN GROUND CONDITIONS PERMITTED. A CAMERA WAS USED TO EVALUATE THE INSIDE OF THE PIPE THAT WAS SHUT DOWN DUE TO THE LEAK. THAT PROCESS INDICATED A DEFORMATION, WHICH THEN LED TO AN EXCAVATION TO EVALUATE. THE 2 IN. STEEL GAS MAIN WAS FOUND TO BE DAMAGED AT THE CROSSING OF A SANITARY SEWER LINE. THE DAMAGE ON THE PIPE WAS CONSISTENT WITH THE DIMENSIONS OF AN EXCAVATOR BUCKET. A METALLURGICAL EXAMINATION OF THE PIPE REPORTED THE DAMAGE CONSISTED OF OVERALL BENDING DEFORMATION, FLATTENING OF THE PIPE, AND DAMAGE TO THE PROTECTIVE COATING ON THE EXTERIOR OF THE PIPE. THIS DAMAGE WEAKENED THE PIPE MAKING IT MORE SUSCEPTIBLE TO FRACTURE OR CRACKING FROM EXTERNAL FORCES SUCH AS FREEZE/THAW CYCLES. GAS LEAKED FROM A CRACK IN THE PIPE AND MIGRATED THROUGH THE FROZEN GROUND AND INTO THE HOUSE AT 908 COLLEGE AVE. THE METALLURGICAL EXAMINATION ALSO REPORTED THE FRACTURE IN THE GAS MAIN WAS BRITTLE AND DID NOT EXHIBIT WALL THINNING OR CORROSION TO SUGGEST THE CRACK OR A PARTIAL CRACK ORIGINATED YEARS PRIOR TO THE EXPLOSION. DURING THE INVESTIGATION AND EXCAVATION OF THE DAMAGED PIPE, THE INITIAL OBSERVATION BEFORE THE PIPE WAS EXPOSED INDICATED A HOLLOWING OF THE SOIL NEAR THE FOUND CRACK, AND NO EVIDENCE OF DRY DIRT OR HARDENING OF THE SOIL CONSISTENT WITH A LONGSTANDING GAS LEAK. PHOTOS OBTAINED THROUGH A FOIA REQUEST INDICATED THE NATURAL GAS MAIN WAS LOCATED AND MARKED BY SEMCO, A FACT CONSISTENT WITH SEMCO'S LOCATING RECORDS. BASED ON THE RECORDS AND PHOTOS OBTAINED, IT IS REASONABLE TO BELIEVE THE EXCAVATOR DUG WITHOUT HAND EXPOSING THE GAS MAIN, AND AFTER THE MICHIGAN ONE CALL TICKET HAD EXPIRED. PHOTOS SHOWING THE TIME STAMP INDICATE THE DAMAGE LIKELY OCCURRED BETWEEN AUGUST 27TH AND AUGUST 28TH, 2008. THE EXCAVATOR ALSO APPEARED TO HAVE DAMAGED CONDUIT FOR A TELECOMMUNICATIONS LINE. SEMCO ENERGY WAS NEVER NOTIFIED OF THE DAMAGE TO THE PIPE DURING THE SEWER CONSTRUCTION. BASED ON THE INFORMATION GATHERED DURING THE INVESTIGATION, METALLURGICAL EVALUATION, AND INFORMATION REQUESTS, SEMCO CONSIDERS THE INVESTIGATION TO BE COMPLETED.
2024-05-31 11:04 | NO | NO | NO | 20220031 | 37336 | 2022-04-13 10:55 | SUPPLEMENTAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2022-03-14 16:20 | EASTERN | YES | 2022 | 449 FIRST ST. | NEWBURGH | ORANGE | NY | 12550 | 41.5027 | -74.0278 |  |  | YES | [6 empty] | 2022-03-14 18:31 | 1331058 | 1331191 | NATURAL GAS |  | 7.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-03-14 16:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7.4 | YES | 6 | 2022-03-14 16:32 |  |  |  | 2022-03-14 16:32 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1951 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL PIPE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE SERVICE PIPE TO THE BUILDING FOUNDATION IS 2" AND THE PIPE REDUCES TO 1 1/4" NEAR THE FOUNDATION WALL. | CLASS 3 LOCATION | 0 | 0 | 9073 | 9270.821147540987325 | 13610 | 13906.74262295082525 | 0 | 0 |  | 9.1644 | 68 | 52.20899854862119013062409288824383164006 | 0 | 0 | 22751 | 9831.718543029816466865021770682148040639 | 23229.7727690404337651306240928882438316 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.31 | 0.31 | 0.5 | 192.623 | 1951-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | CONTRACTOR HIRED BY RESIDENTIAL CUSTOMER CUT PRESSURIZED 1 1/4" STEEL SERVICE IN THE BASEMENT OF THE HOUSE CAUSING A LEAK. THE CONTRACTOR INTENDED TO CUT THE PIPE. | [155 empty] | JERRY AMATO JR. | DIRECTOR OF GAS COMPLIANCE | jamato@cenhud.com | 845.486.5642 |  | JERRY AMATO | jamato@cenhud.com | 845-486-5642 | ERIC KISZKIEL | MANAGER OF GAS OPERATIONS AND ENGINEERING | 845-486-5472 | ekiszkiel@cenhud.com | AT 4:25 PM ON 3/14/2022, CENTRAL HUDSON WAS NOTIFIED BY THE CITY OF NEWBURGH OF A POSSIBLE GAS EXPLOSION AT 449 FIRST ST. IN NEWBURGH. THE FIRST CENTRAL HUDSON RESPONDER ARRIVED ON SITE AT 4:32 PM AND A SECOND CENTRAL HUDSON RESPONDER ARRIVED AT 4:33 PM. THE BUILDING WAS ON FIRE WHEN THE RESPONDERS ARRIVED. ADDITIONAL SUPPORTING PERSONNEL INCLUDING SUPERVISORS AND GAS CONSTRUCTION CREW WERE EN ROUTE. APPROXIMATELY 6 PEOPLE WERE EVACUATED BY THE FIRE DEPARTMENT. THE BUILDING AT 449 FIRST ST. WAS PRESENTLY BEING RENOVATED AND WAS FED BY A 4 INCH LOW PRESSURE CAST IRON MAIN AND 197 FT. LONG 2 INCH STEEL SERVICE. A CURB VALVE WAS PRESENT ON THE SERVICE. THERE WERE THREE GAS METERS LOCATED INSIDE THE BUILDING'S BASEMENT WITH VALVES THAT WERE CLOSED AND LOCKED ON OCTOBER 25TH 2021. A CENTRAL HUDSON REPRESENTATIVE ON SCENE ADVISED THE FIRE DEPARTMENT TO CONTAIN THE HOUSE FIRE BUT TO ALLOW THE NATURAL GAS TO BURN TO PREVENT A SECOND IGNITION. A POLICE OFFICER INFORMED AN ONSITE CENTRAL HUDSON SUPERVISOR OF A REPORT OF THE CUSTOMER'S CONTRACTOR CUTTING THE SERVICE LINE OR CUSTOMER PIPE INSIDE THE BUILDING. A COMMERCIAL REPRESENTATIVE STOPPED THE FLOW OF GAS TO THE HOUSE BY CLOSING THE CURB VALVE ON THE SERVICE AT APPROXIMATELY 5:00 PM. ELECTRIC TAPS FOR THIS ADDRESS WERE CUT AT APPROXIMATELY 5:05PM. BY THIS TIME, ADDITIONAL CH EMPLOYEES HAD ARRIVED ON THE SCENE TO ASSIST IN THE EMERGENCY RESPONSE. THE CENTRAL HUDSON SUPERVISOR INFORMED THE FIRE DEPARTMENT THAT THEY MAY PROCEED WITH EXTINGUISHING THE HOUSE FIRE. AFTER THE BUILDING WAS MADE ACCESSIBLE BY THE FIRE DEPARTMENT, ONE CENTRAL HUDSON PERSONNEL AND CITY OF NEWBURGH FIRE INVESTIGATOR INVESTIGATED THE BASEMENT OF THE HOUSE AND CONFIRMED THAT THE SERVICE PIPE AND CUSTOMER PIPE HAD BEEN CUT AND DISASSEMBLED IN MULTIPLE LOCATIONS INCLUDING AT LEAST ONE LOCATION OF UPSTREAM OF THE THREE LOCKED GAS METERS. CENTRAL HUDSON AND CONTRACTOR CREWS LEAK SURVEYED THE ENTIRE PROPERTY AND THE SURROUNDING AREA. NO NATURAL GAS LEAKS WERE FOUND AT 449 FIRST ST. THE AREA OF 244 VAN NESS ST. WAS ALSO LEAK SURVEYED, AS THE SERVICE TO 449 FIRST ST. WAS FED FROM THAT ROAD. NO LEAKS WERE FOUND AT EITHER ADDRESS. GAS ODORANT READINGS WERE TAKEN IN THE SURROUNDING AREA TO VERIFY APPROPRIATE ODORIZATION OF GAS. THE NATURAL GAS SERVICE TO 449 FIRST ST. WAS PERMANENTLY RETIRED THAT EVENING AND THE AREA WAS DECLARED SAFE AT 9:40 PM.
2024-05-31 11:04 | NO | YES | NO | 20220032 | 36654 | 2022-04-21 15:15 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2022-03-24 01:15 | EASTERN | NO | 2022 | HIGHWAY 9 | BOILING SPRINGS | SPARTANBURG | SC | 29316 | 35.059 | -81.9935 | [5 empty] | YES |  |  |  |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 0.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-03-24 01:52 | NO |  |  | 2022-03-24 01:52 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | IN A CREEK. | 72 | NO | YES | [6 empty] | YES | BORED/DRILLED | FAWN BRANCH TRIBUTARY 2 | 1 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | INVESTOR OWNED |  | MAIN |  | 2014 | UNKNOWN |  |  |  |  | 6 | MDPE | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 344000 | 351500.3278688526 | 7200 | 7356.98360655738 | 0 | 0 |  | 0.1 | 0 | 0 | 0 | 0 | 351200 | 151620.524590163992 | 358857.31147540998 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 68 | 70 | 192.619(A)(2) | 2014-07-10 | PRESSURE DID NOT EXCEED MAOP | OTHER | INJECTION |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | DUE TO LOCATION OF PIPE UNDER CREEK, DAMAGED PORTION OF PIPE WAS DEACTIVATED AND LEFT IN PLACE. | [45 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | A PASSERBY IN A VEHICLE CALLED STATING THAT THEY SMELLED GAS. ONCE INVESTIGATED, GAS WAS FOUND BLOWING THROUGH THE WATER IN THE CREEK. DUE TO THE NATURE OF THE PIPE BEING LOCATED IN THE CREEK AND BENEATH A CONCRETE BOX CULVERT, THE PIPE WAS NOT EXPOSED AND WAS LEFT IN PLACE. THE TRUE CAUSE OF THE LEAK, HOLE SIZE, AND GAS VOLUMES COULD NOT BE DETERMINED. NEW PIPE WILL BE BORED UNDER CREEK FOR REPAIR. THE NRC WAS NOT NOTIFIED AT THE TIME OF INCIDENT BECAUSE THE ESTIMATED COST WAS BELIEVED TO BE BELOW THE 122K THRESHOLD.
2024-05-31 11:04 | NO | YES | NO | 20220033 | 36728 | 2022-04-25 13:28 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2022-04-05 01:55 | CENTRAL | YES | 2022 | 4809 TROUP HWY | TYLER | SMITH | TX | 75703 | 32.2986 | -95.2662 |  |  |  | YES | [5 empty] | 2022-04-05 05:25 | 1332738 | 1332887 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-05 01:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.5 | NO | 0 | 2022-04-05 01:55 |  |  |  | 2022-04-05 02:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | REGULATOR BODY | [9 empty] | OTHER | [8 empty] | DURING A LOCAL STORM A PONTOON BOAT BELONGING TO TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. | CLASS 3 LOCATION | 125000 | 127725.409836065625 | 300 | 306.5409836065575 | 676 | 690.7390163934429 | 0 | 0 |  | 4.72 | 5 | 3.83889695210449927431059506531204644412 | 0 | 0 | 125981 | 54389.3904075757421774165457184325108853 | 128726.5287330177298992743105950653120464 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 60 | 192.619(A)(1) | 1970-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  |  | YES | THUNDER STORMS/HIGH WINDS | [178 empty] | YES |  |  | YES | [31 empty] | LESLIE DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-9325 |  | JASON SURRATT | jason.surratt@centerpointenergy.com | 7775006234 | RANDALL SANDERS | DIRECTOR OF OPERATIONS TX. REGION | 713-207-5708 | randall.x.sanders@centerpointenergy.com | DURING A LOCAL THUNDER STORM A PONTOON BOAT ON TRAILER OWNED BY TYLER CAR & TRUCK CENTER, ROLLED INTO METER SET AND TYLER CAR & TRUCK CENTER BUILDING, RESULTING IN DAMAGE TO REGULATOR ALLOWING GAS TO BE RELEASED. RESULTING IN IGNITION OF GAS DAMAGING BUILDING AND CONTENTS. (PART A, LINE #4 RESPONSE OF 0525AM WAS THE TIME OF CONFIRMED DISCOVERY THAT IT MET CRITERIA) DUE TO RESTRICTED ACCESS. DUE TO RESTRICTED ACCESS CONFIRMED DISCOVERY WAS NOT UNTIL 0525 AM THAT MORNING.
2024-05-31 11:04 | NO | YES | YES | 20220036 | 38763 | 2022-05-18 09:50 | SUPPLEMENTAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-04-23 07:28 | EASTERN | YES | 2022 | 5021 HIALEAH DR | PITTSBURGH | ALLEGHENY | PA | 15239 | 40.4862 | -79.7042 |  |  | YES | YES |  |  |  | YES | SERVICE LINE WAS CUT OFF AT MAIN LINE. | 2022-04-23 07:28 | 1334232 | 1334328 | NATURAL GAS |  | 0.106 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES | 2022-04-22 23:22 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.1 | YES | 7 | 2022-04-22 23:28 |  |  |  | 2022-04-23 00:12 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIS INCIDENT IS UNDER INVESTIGATION BY CHIEF DEPUTY FIRE MARSHAL DONALD A. BRUCKER CERTIFIED FIRE & EXPLOSION INVESTIGATOR ALLEGHENY COUNTY FIRE MARSHAL'S OFFICE. | CLASS 3 LOCATION | 185000 | 189033.606557377125 | 0 | 0 | 6148 | 6282.0465573770517 | 0 | 0 |  | 10.5425 | 1 | 0.7677793904208998548621190130624092888244 | 0 | 0 | 191149 | 82523.2385405315690834833091436865021771 | 195316.4208941445975998548621190130624093 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 8.7 | 8.7 | 10 | 192.621 M | 1961-01-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | wayne.dadig@peoples-gas.com | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412-258-4453 | edward.a.palombo@peoples-gas.com | AT THIS TIME THE INCIDENT IS UNDER INVESTIGATION BY CHIEF DEPUTY FIRE MARSHAL DONALD A. BRUCKER CERTIFIED FIRE & EXPLOSION INVESTIGATOR, ALLEGHENY COUNTY FIRE MARSHAL'S OFFICE. PEOPLES NATURAL GAS IS WORKING WITH AND ASSISTING THE INVESTIGATION TEAM. 11/7/2023 THE INCIDENT REMAINS UNDER INVESTIGATION BY CHIEF DEPUTY FIRE MARSHAL DONALD A. BRUCKER CERTIFIED FIRE & EXPLOSION INVESTIGATOR, ALLEGHENY COUNTY FIRE MARSHAL'S OFFICE.
2024-05-31 11:04 | YES | NO | NO | 20220037 | 36688 | 2022-05-20 16:22 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2022-04-22 04:18 | CENTRAL | YES | 2022 | 302 MAPLE | ONAWA | MONONA | IA | 51040 | 42.0212 | -96.0879 | [5 empty] | YES |  |  |  | 2022-04-22 06:06 | 1334144 | 1334323 | NATURAL GAS |  | 8.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-04-22 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.5 | NO | 1 | 2022-04-22 04:18 |  |  |  | 2022-04-22 00:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2000 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | 2406 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | OTHER | [8 empty] | LEAK CAUSED BY FIRE DAMAGE TO METER AND REGULATOR. | CLASS 4 LOCATION | 11200 | 11444.19672131148 | 3000 | 3065.409836065575 | 15000 | 15327.049180327875 | 0 | 0 |  | 8.14 | 69 | 52.97677793904208998548621190130624092888 | 0 | 0 | 29269 | 12645.8196245449618403483309143686502177 | 29889.6325156439720899854862119013062409 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 25 | 25 | 66.6 | 192.619(A)(1) | 2000-01-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [143 empty] | YES | [24 empty] | ANTHONY ENGLING | SUPERVISOR PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 15635854014 | 563-583-0850 | GARY HOGAN | gary.hogan@blackhillscorp,com | 1-402-221-2536 | TONY JOHN ENGLING | SUPERVISOR PIPE LINE SAFETY PROFESSIONAL | 15635854014 | tony.engling@blackhillscorp.com | ON 4/22/2022 AT 04:18 CENTRAL TIME BLACK HILLS ENERGY WAS NOTIFIED BY EMERGENCY RESPONDERS OF A RESIDENTIAL FIRE AND REQUESTED BHE TO RESPOND. THE LOCATION IS 302 MAPLE IN ONAWA IOWA. UPON ARRIVAL THE TECHNICIAN FOUND THE HOME ENGULFED IN FLAMES. THE FIRE HAD CAUSED DAMAGE TO THE METER AND REGULATOR. THE SERVICE LINE WAS EXCAVATED AT THE STREET AT A SAFE DISTANCE FROM THE FIRE AND CUT OFF AND CAPPED.
2024-05-31 11:04 | NO | YES | YES | 20220038 | 37230 | 2022-05-23 09:26 | SUPPLEMENTAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2022-04-24 14:33 | EASTERN | YES | 2022 | 10826 AVENUE N | BROOKLYN | KINGS | NY | 11234 | 40.641 | -73.8826 |  |  | YES | [6 empty] | 2022-04-24 19:19 | 1334317 | 1334342 | NATURAL GAS |  | 1.72 | 0 | YES | 0 | 0 | 2 | 0 | 0 | 2 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2022-04-24 14:33 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1.72 | NO | 3 | 2022-04-24 14:33 |  |  |  | 2022-04-24 15:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | AT THIS TIME, UNKNOWN PENDING INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN AT THIS TIME | CLASS 4 LOCATION | 122000 | 124660.00000000005 | 0 | 0 | 1537 | 1570.511639344262925 | 0 | 0 |  | 6.05 | 10 | 7.67779390420899854862119013062409288824 | 0 | 0 | 123547 | 53339.2886020367092048330914368650217707 | 126238.1894332485219235486211901306240929 | 0 | 0 | 2 | 10 | 0 | 2 | 0 | 0.29 | 0.32 | 0.43 | 192.623 | 1997-03-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SYSTEM CHANGES, ALARMS, OR ABNORMALITIES DURING THE TIME OF THE INCIDENT, AND INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NOT NECESSARY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 15169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 15169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 15169030596 | corinne.byrnes@nationalgrid.com | **UPDATE 10/14/2022- NO ADDITIONAL INFORMATION ON THIS INCIDENT IS AVAILABLE, AND NATIONAL GRID IS STILL AWAITING FINAL DISPOSITION.*** NATIONAL GRID WAS NOTIFIED ON 04/24/2022 AT 14:33 FROM FDNY 401 REGARDING FIRE IN PROGRESS AT 10826 AVENUE N, BROOKLYN, NY. A SERVICE PERSON WAS DISPATCHED AT 14:33 AND ARRIVED ON SITE AT 15:00. THE SERVICE WAS MADE SAFE AT 15:50 BY TURNING OFF THE CURB VALVE. IN ADDITION, THE RESIDENCE AT 10824 WAS SECURED AT THE METER BY THE FDNY AT 17:00. NATIONAL GRID CREW REMAINED ON SITE UNTIL THE FDNY WAS ABLE TO EXTINGUISH THE FIRE, BUT COULD NOT GAIN ACCESS TO THE PREMISE. NEWS RELEASES INDICATE THAT THERE WERE TWO FATALITIES, ONE RESIDENT, AND ONE FIREFIGHTER. NEWS RELEASES ALSO INDICATE THAT AT LEAST ONE FIREFIGHTER WAS HELD OVERNIGHT AT A NEARBY HOSPITAL. ESTIMATES ARE THAT AT LEAST TWO OTHER FIREFIGHTERS SUFFERED INJURIES NOT REQUIRING AN OVERNIGHT HOSPITAL STAY. AT THIS TIME, IT IS UNDETERMINED AS TO THE CAUSE AND LOCATION OF THE FIRE; HOWEVER, IF THE EVENT IS DETERMINED TO BE 'FIRE FIRST', WE WILL STILL FILE THIS REPORT DUE TO THE FATALITY AND INJURIES. NATIONAL GRID HAS MADE SEVERAL ATTEMPTS TO DETERMINE THE CAUSE AND STARTING POINT OF THE FIRE. IT IS STILL UNDER INVESTIGATION AS OF MAY 10, BUT WE WILL CONTINUE TO ATTEMPT TO GAIN MORE INFORMATION. PART A - QUESTION 22, TWO HOMES WERE SHUT OFF, ASSUMED MINIMUM OF 3 INDIVIDUALS EVACUATED. PART D - QUESTION 2B, NATIONAL GRID CANNOT MAKE REPAIRS AS OF YET, SO REPAIR COST UNKNOWN.
2024-05-31 11:04 | NO | YES | YES | 20220039 | 36740 | 2022-06-10 09:02 | ORIGINAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2022-05-13 20:10 | EASTERN | YES | 2022 | 611 WHITESTICK ST. | MABSCOTT | RALEIGH | WV | 25871 | 37.7758 | -81.2121 | [7 empty] | YES | FULL-CIRCLE BAND LEAK CLAMP | 2022-05-13 20:13 | 1335962 | 1336073 | NATURAL GAS |  | 14.887 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-05-13 14:10 | YES | OPERATOR | 2022-05-13 14:50 | 2022-05-13 14:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | ALDYL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 600 | 613.081967213115 | 500 | 510.9016393442625 | 0 | 0 |  | 6.739 | 100 | 76.77793904208998548621190130624092888244 | 0 | 0 | 1200 | 532.222905612791348330914368650217706821 | 1200.761545599467485486211901306240928882 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 30 | 30 | 40 | 192.619(A)(4) | 2016-08-24 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PUNCTURE DIDN'T REDUCE SYSTEM PRESSURE ENOUGH TO CAUSE AN ALARM AT GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 2213316772 | N/A |  | FACILITY OWNER | NO | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | EMERGENCY 1 CALL TICKET BUT DID NOT WAIT FOR MARKS | [169 empty] | PHILIP KINGREY | MANAGER ENGINEERING AND COMPLIANCE | philipkingrey@mgcwv.com | 3043892714 | 3049259605 | JOHN LIVELY | johnlively@mgcwv.com | 3046674669 | THOMAS WESTFALL | VICE PRESIDENT GAS SUPPLY AND TECHNICAL SERVICES | 3045395740 | thomaswestfall@mgcwv.com | BECKLEY WATER COMPANY WERE MAKING A WATER LEAK REPAIR AND CALLED IN AN EMERGENCY ONE-CALL TICKET. THEY DID NOT WAIT FOR UNDERGROUND UTILITIES TO BE LOCATED BEFORE DIGGING AND PUNCTURED MOUNTAINEER GAS COMPANY'S 2" PLASTIC NATURAL GAS DISTRIBUTION PIPELINE OPERATING NEAR 30 PSIG. BECKLEY WATER COMPANY NOTIFIED MOUNTAINEER GAS COMPANY'S DISPATCH CENTER. MOUNTAINEER EMPLOYEES WERE DISPATCHED TO THE SCENE. WHILE INSTALLING A FULL CIRCLE BAND CLAMP, TWO OF THEM WERE OVERCOME WITH GAS AND REMOVED FROM THE LEAK AREA BY PERSONNEL ONSITE. MOUNTAINEER NOTIFIED 911 AND EMERGENCY MEDICAL PERSONNEL RESPONDED TO THE SCENE TO PROVIDE MEDICAL TREATMENT. ONE EMPLOYEE WAS TAKEN TO THE HOSPITAL IN AN AMBULANCE AND THE OTHER WAS TAKEN TO THE HOSPITAL BY ANOTHER EMPLOYEE. BOTH EMPLOYEES WERE GIVEN A MEDICAL ASSESSMENT AT THE HOSPITAL, ONE WAS ADMITTED TO INPATIENT HOSPITALIZATION FOR OBSERVATION, AND THE OTHER WAS RELEASED.
2024-05-31 11:04 | NO | NO | NO | 20220040 | 37711 | 2022-06-10 14:10 | SUPPLEMENTAL FINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-05-12 14:30 | CENTRAL | YES | 2022 | 100333 IMC ROAD | ABERDEEN | MONROE | MS | 39730 | 33.7684 | -88.5722 | YES | [5 empty] | YES |  |  | 2022-05-12 14:42 | 1335844 | 1335944 | NATURAL GAS |  | 5914 | 379 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-05-12 08:45 | YES | OPERATOR | 2022-05-12 08:45 | 2022-05-12 09:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | 1969 |  |  |  |  | 8 | API 5LX-1968 | REPUBLIC STEEL | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | LEAK |  |  | OTHER | 2-INCH NIPPLE SHEARED OFF PIPE | [5 empty] | CLASS 1 LOCATION | 0 | 0 | 10001 | 10219.054590163938525 | 12575 | 12849.176229508201875 | 0 | 0 |  | 7.3268 | 43331 | 33268.648766328011611030478955007256894 | 2777 | 2132.123367198838896952104499274310595065 | 68684 | 36180.0091232244439684179970972423802612 | 58469.0029531989909079825834542815674891 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 250 | 350 | 385 | 192.619(A)(2) | 1969-11-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OTHER THAN PROVIDING ALERTS TO OPERATIONS AS THE EVENT OCCURRED, THE CONTROL ROOM HAD NO INVOLVEMENT IN THIS INCIDENT. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE EASEMENT | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 22042814572130 |  |  | CONTRACT LOCATOR | YES | YES | 11 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | DEAN MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6015925360 |  | WADE SHULTICE | wade.shultice@atmosenergy.com | 6622512018 | JAMES E. MCKENZIE | VICE PRESIDENT TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | ATMOS ENERGY'S SECOND-PARTY CONTRACTOR WAS IN THE PROCESS OF REPLACING A CRITICAL VALVE ON AN 8-INCH HIGH PRESSURE DISTRIBUTION LINE NEAR ABERDEEN, MS. THE PROJECT WAS BEING WORKED UNDER MISSISSIPPI ONECALL LOCATE TICKET #2204814572130, AND PROPER LOCATE PRACTICES WERE USED PRIOR TO BEGINNING THE PROJECT USING ALL AVAILABLE INFORMATION ON THE ASSETS IN THE AREA AND LOCATE TECHNOLOGY. UNKNOWN TO ATMOS ENERGY OR THE SECOND PARTY CONTRACTOR, THERE WAS AN UNLOCATABLE AND UNMAPPED 2-INCH NIPPLE AND VALVE LOCATED IN THE VERTICAL POSITION ON THE CARRIER PIPE, AND THIS UNMAPPED AND UNLOCATABLE ASSET WAS DAMAGED DURING EXCAVATION ACTIVITIES. THE CONTRACTOR RESPONDED TO THE DAMAGE USING APPROPRIATE EMERGENCY RESPONSE PRACTICES. IN ORDER TO ELIMINATE THE HAZARDOUS CONDITION, A STOPPLE FITTING WAS WELDED ONTO THE CARRIER PIPE AND TAPPED. DURING THE REPAIR, THE UNINTENTIONAL LOSS OF GAS EXCEEDED THE REPORTABLE THRESHOLD, AND ATMOS ENERGY REPORTED THE DAMAGE AS AN INCIDENT.
2024-05-31 11:04 | NO | YES | NO | 20220044 | 36927 | 2022-07-05 18:18 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2021-01-27 12:00 | EASTERN | YES | 2021 | LOCKHART ROAD | BELPRE | WASHINGTON | OH | 45714 | 39.2913 | -81.5726 | [7 empty] | YES | DEO DETERMINED THIS LEAK TO BE NON-HAZARDOUS BASED ON THE SIZE AND REMOTE LOCATION OF THE LEAK. |  | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 3.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-10-23 10:00 | NO |  |  | 2020-10-23 12:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | LEGACY PIPELINE BY-PASS/FITTING | 2004 | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 1321100 | 1402677.1654884585949 | 500 | 530.8747125457795 | 0 | 0 |  | 2.65 | 10 | 8.78737541528239202657807308970099667774 | 0 | 0 | 1321610 | 592874.9031703371047335548172757475083056 | 1403216.827576419656792026578073089701 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 160 | 175 | 192.619(A)(2) | 2004-06-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM DID NOT DETECT THE INCIDENT DUE TO MINIMAL SIZE OF LEAK AND MINIMAL RELEASE OF GAS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | A029702031 | OHIO811 |  | CONTRACT LOCATOR | UNKNOWN/OTHER | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [169 empty] | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | AMY KONCELIK | amy.l.koncelik@dominionenergy.com | 3308109842 | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 2167899152 | a.walters-thompson@dominionenergy.com | 2ND PARTY CONTRACTOR HIT AN UNMARKED DEO HP LINE STUB THAT HAD BEEN ORIGINALLY USED AS A BY-PASS CREATING A MINIMAL LEAK IN A REMOTE HEAVY TERRAIN AREA.
2024-05-31 11:04 | NO | YES | NO | 20220045 | 36950 | 2022-07-07 14:10 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-06-07 17:07 | PACIFIC | YES | 2022 | 7015 TELEGRAPH ROAD | COMMERCE | LOS ANGELES | CA | 90040 | 33.987 | -118.1346 | YES | [8 empty] | 2022-06-07 17:53 | 1338079 | 1338306 | NATURAL GAS |  | 2357 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-06-07 09:05 | YES | OPERATOR | 2022-06-07 09:08 | 2022-06-07 09:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 93 | YES | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.24 | [6 empty] | RUPTURE |  |  |  |  | LONGITUDINAL |  | 31.5 | 1.5 |  | CLASS 3 LOCATION | 0 | 0 | 250000 | 255450.81967213125 | 150000 | 153270.49180327875 | 0 | 0 |  | 6 | 14142 | 10857.9361393323657474600870827285921626 | 0 | 0 | 414142 | 180796.0572461872220609579100145137880987 | 419579.2476147423657474600870827285921626 | 55 | 36 | 12 | 0 | 0 | 12 | 91 | 223.58 | 115 | 125 | 192.619(C) | 1953-10-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NONE |  | 8.9 |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 18 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [61 empty] | YES | [5 empty] | YES | [5 empty] | MIGUEL GAMBOA | PIPELINE SAFETY AND COMPLIANCE ADVISOR | mgamboa@socalgas.com | 818-618-2564 |  | MIGUEL GAMBOA | mgamboa@socalgas.com | 818-618-2564 | MIGUEL GAMBOA | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 818-618-2564 | mgamboa@socalgas.com | ON 06-07-2022, SOCALGAS CREWS RESPONDED TO AN OVERPRESSURE ON A DISTRIBUTION MAIN IN THE CITY OF COMMERCE. THE OVERPRESSURE OCCURRED DURING THE PROCESS OF CONDUCTING AN IN-LINE INSPECTION RUN. THERE WERE NO INJURIES OR FATALITIES FROM THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC DUE TO ESTIMATED PROPERTY DAMAGE EXCEEDING $122,000. 8/5/22 UPDATE - AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THAT DURING THE ILI PIGGING OPERATION, EXCESS LIQUID DEBRIS LOCATED IN TRANSMISSION PIPELINE L-2000 WERE INADVERTENTLY DIRECTED INTO THE DISTRIBUTION SYSTEM, CAUSING A REGULATOR STATION TO STAY OPEN AND OVER PRESSURIZE A DISTRIBUTION PIPELINE. ALL REPAIRS TO THE PIPELINE HAVE BEEN COMPLETED AND NO FURTHER GAS LEAKAGE WAS FOUND. THE REGULATOR STATION WAS REBUILT, TESTED AND ALL LIQUIDS REMOVED. THERE HAVE BEEN NO FURTHER CONCERNS.
2024-05-31 11:04 | NO | NO | NO | 20220047 | 36836 | 2022-07-07 16:07 | ORIGINAL FINAL | 18508 | SOUTHERN INDIANA GAS & ELECTRIC CO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2022-05-23 15:30 | CENTRAL | YES | 2022 | 2710 WINDEMERE | EVANSVILLE | VANDERBURGH | IN | 47725 | 38.0637 | -87.5149 | [5 empty] | YES |  |  |  | 2022-05-23 18:25 | 1336798 |  | NATURAL GAS |  | 73.612 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-05-23 15:30 | OPERATOR/CONTRACTOR |  | 73.6 | NO | 12 | 2022-05-23 15:35 |  |  |  | 2022-05-23 16:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 60000 | 61308.1967213115 | 8000 | 8174.4262295082 | 500 | 510.9016393442625 | 10000 | 10218.03278688525 | CURRENT ESTIMATED 2.B IS FOR CAPPING ENDS. 10K WOULD BE IF ENDS WERE RECONNECTED | 5.175 | 381 | 292.523947750362844702467343976777939042 | 0 | 0 | 78881 | 34108.548204810976727140783744557329463 | 80504.081324799575344702467343976777939 | 0 | 0 | 2 | 0 | 0 | 5 | 0 | 58 | 58 | 60 | 192.619(A)(2) | 1997-03-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INITIATED BY A THIRD PARTY EXCAVATOR HITTING A PLASTIC DISTRIBUTION MAIN WHICH IGNITED ALMOST IMMEDIATELY. GAS CONTROL WAS NOT INVOLVED, COULD NOT HAVE RESPONDED TO OR MINIMIZED THE LOSS OR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | NO |  |  |  | CONTRACT LOCATOR | YES | YES | 2 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | SCOTT CHANDLER | LEAD OPERATION SPECIALIST | scott.chandler@centerpointenergy.com | 812-491-4117 |  | SCOTT CHANDLER | scott.chandler@centerpointenergy.com | 812-491-4117 | SHERRI BELL | MANAGER PIPELINE SAFETY AND COMPLIANCE | 812-491-4806 | sherri.bell@centerpointenergy.com | DCI WAS CONTRACTED BY CENTERPOINT INDIANA-ELECTRIC TO INSTALL UNDERGROUND ELECTRIC LINES AND A NEW JUNCTION BOX IN THE GREEN SPACE ACROSS FROM 2710 WINDEMERE DRIVE, EVANSVILLE, INDIANA 47725 (VANDERBURGH COUNTY). DCI HAD SUBCONTRACTED THE EXCAVATION WORK OUT TO EARLEY ELECTRIC. ON MAY 23, 2022, LESTER KNEPP WITH EARLEY ELECTRIC WAS OPERATING A CATERPILLAR 304E MINI EXCAVATOR TO EXPOSE UNDERGROUND ELECTRIC LINES ALONG THE SOUTH SIDE OF WINDEMERE DRIVE. DCI HAD CALLED FOR LOCATES BY CALLING INDIANA 811 AND GOT A LOCATE TICKET # 2205092040 ON MAY 9, 2022. EARLEY ELECTRIC AND MR. KNEPP WERE UNDER THE MISTAKEN IMPRESSION THEY COULD EXCAVATE UNDER DCI'S LOCATE AND THEREFORE DID NOT CALL FOR THEIR OWN LOCATE TICKET. AT APPROXIMATELY 1530HR., MR. KNEPP, WHILE OPERATING THE MINI EXCAVATOR, HIT A 2' PE UNDERGROUND GAS MAIN OWNED AND OPERATED BY SOUTHERN INDIANA GAS AND ELECTRIC COMPANY D.B.A CENTERPOINT ENERGY INDIANA ' SOUTH. THE GAS MAIN WAS OPERATING AT APPROXIMATELY 58 PSIG. EARLEY ELECTRIC EMPLOYEE AARON SCHROER WITNESSED THE EVENT, STATING MR. KNEPP UPON HITTING THE MAIN, EXITED THE EXCAVATOR LEAVING IT RUNNING. ACCORDING TO MR. SCHROER, THE GAS WAS BLOWING FOR ABOUT 25 SECONDS BEFORE IT IGNITED. MR. SCHROER NOTIFIED 911 IMMEDIATELY AT APPROXIMATELY 1530HRS. MR. SCHROER STATED THEY DID NOT NOTICE THE GAS LOCATE MARKS THAT WERE PART OF DCI'S MAY 9TH LOCATE TICKET. THE LOCATE WAS PERFORMED ON MAY 10, 2022. LOCATE PICTURES FROM THAT DATE SHOW THE GAS FACILITY WERE PROPERLY FLAGGED AND MARKED. AT THE TIME OF THE EVENT, GAS FACILITY LOCATE FLAGS HAD BEEN REMOVED AND MARKS WERE FAINT. CENTERPOINT DISPATCH WAS NOTIFIED BY 911 DISPATCH APPROXIMATELY 1535HRS. CENTERPOINT GAS CREW WAS NOTIFIED AT 1543HRS. AND ARRIVED ON SCENE AT 1615HRS. THE GAS FROM THE MAIN WAS STILL BURNING. THE PE MAIN WAS DUEL FED SO THE CENTERPOINT GAS CREW DUG UP AND EXPOSED THE MAIN ON THE EAST AND WEST SIDE OF THE DAMAGE. THE GAS CREW PERFORMED SQUEEZE OFF OPERATIONS STOPPING THE FLOW OF GAS AND EXTINGUISHING THE FIRE AT 1700HRS. PRIOR TO SQUEEZING OFF, TWO CUSTOMERS WERE TAKEN OUT OF SERVICE SO THAT GAUGES COULD BE INSTALLED. AT THE TIME OF INSTALLATION, THE EAST GAUGE READ 25PSIG WHERE THE WEST SIDE READ 4PSIG. AFTER SQUEEZE OFF, PRESSURE ON BOTH SIDES RETURN TO NEAR NORMAL PRESSURES. CENTERPOINT DISPATCH SENT OUT AN EMAIL ALERTING STAKEHOLDER, INCLUDING MEMBERS OF THE INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT OF THE INITIAL REPORT FROM 911 AT 1545HRS. CENTERPOINT PIPELINE SAFETY AND COMPLIANCE DEPARTMENT WAS IN CONTACT WITH MEMBERS OF THE INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT SHORTLY THEREAFTER. INDIANA UTILITY REGULATORY COMMISSION, PIPELINE SAFETY DEPARTMENT, CHIEF ENGINEER RICH MEDCALF ARRIVED ON SCENE AND INVESTIGATED. LOCAL NEWS MEDIA COVERAGE AS WELL AS MEMBERS OF THE PUBLIC POSTED VIDEO OF THE FIRE ON SOCIAL MEDIA SITES. ON BOTH SIDES OF THE DAMAGE, THE MAIN WAS CUT AND CAPPED OFF A SHORT DISTANCE FROM WHERE IT WAS SQUEEZED OFF. IT HAS YET TO BE DETERMINED IF OR WHEN THE MAIN WILL BE RESTORED TO DUAL FED STATUS. CENTERPOINT PIPELINE SAFETY AND COMPLIANCE DEPARTMENT LEAD OPERATION SPECIALIST DECIDED TO CONTACT THE NRC, DESPITE THE EVENT NOT MEETING REPORT CRITERIA, DUE TO THE AMOUNT OF ATTENTION AND VIDEO.
2024-05-31 11:04 | NO | NO | NO | 20220050 | 37104 | 2022-07-15 16:00 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2022-06-16 05:34 | EASTERN | YES | 2022 | 10611 14 MILE RD NE | ROCKFORD | KENT | MI | 49341 | 43.1764 | -85.4072 | [5 empty] | YES |  |  |  | 2022-06-16 11:25 | 1338925 | 1339649 | NATURAL GAS |  | 25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-06-16 09:12 | OPERATOR/CONTRACTOR |  | 0 | NO | 7 | 2022-06-16 05:38 |  |  |  | 2022-06-16 06:17 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | OTHER | BOTH UNDERGROUND AND ABOVEGROUND |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1981 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.625 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 3408 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 50000 | 51090.16393442625 | 0 | 0 | 26452 | 27028.7403278688633 | 0 | 0 | PROPERTY DAMAGE COST UNKNOWN. FIRE DAMAGE FROM ELECTRIC SURGE EST. $50,000 | 4.3 | 108 | 82.92017416545718432510885341074020319303 | 0 | 0 | 76560 | 33067.8735249470728961973875181422351234 | 78201.8244364605704843251088534107402032 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1981-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [134 empty] | YES | [8 empty] | YES | [24 empty] | JUSTIN C MORRIS | ENGINEER | justin.morris@dteenergy.com | 2484621760 |  |  |  |  | JUSTIN C MORRIS |  | 2484621760 | justin.morris@dteenergy.com | AT 05:38, FIRE DEPT NOTIFIED DTE GAS OF A RESIDENTIAL FIRE. FIRST CREW ARRIVED AT 06:17. INITIAL FIRE WAS CAUSED BY LIGHTNING OR DOWNED POWER LINE. BETWEEN 07:30 AND 11:00, SEVERAL SMALL GAS LEAKS WERE DISCOVERED. NRC WAS NOTIFIED AT 11:25, AND MICHIGAN PUBLIC SERVICE COMMISION AT 11:36. MULTIPLE HOUSES ALONG 14 MILE NE BECAME ENERGIZED BY THE LIGHTNING STRIKE OR DOWNED POWER LINE. THE ELECTRICAL SURGE LOCALLY ENERGIZED CABLES WITHIN HOMES, CAUSING FIRE DAMAGE. THE ELECTRICAL SURGE ALSO LOCALLY AFFECTED GAS SERVICE TRACER WIRES. TRACER WIRE DAMAGE TO PLASTIC GAS SERVICES RESULTED IN PINHOLE TYPE LEAKS. THE THREE AFFECTED SERVICE LINES THAT WERE COMPROMISED BY HOUSE FIRE AND SURGES TO TRACER WIRES WERE FULLY RENEWED WITHIN 24 HOURS. THE THREE AFFECTED RESIDENTIAL ADDRESSES WERE 10509 14 MILE RD NE, 10567 14 MILE RD NE, AND 10611 14 MILE RD NE. ALL THREE SERVICES WERE 5/8" HD PLASTIC INSTALLED IN 1981 OR 1988. TOTAL GAS LOSS IS MINIMAL DUE TO SIZE OF LEAKS AND ESTIMATED AT 25 MCF. AT 10611 14 MILE, A SMALL, PINHOLE LEAK WAS FOUND BURNED INTO THE SERVICE APPROXIMATELY 30' FROM THE HOME, BUT THE FIRE WAS ON THE INSIDE OF THE HOUSE, NOT THE OUTSIDE. AT 10567 14 MILE, THIS HOUSE HAD ALUMINUM SIDING THAT BECAME ENERGIZED. THE ELECTRICITY ARC'D FROM THE SIDING TO THE TRACER WIRE WHICH THEN WENT BELOW GRADE AND BURNED A SMALL HOLE IN THE SERVICE LINE. FIRE WAS ON OUTSIDE OF HOUSE INCLUDING METER MANIFOLD. AT 10509 14 MILE, SERVICE WAS ALSO RENEWED AS PRECAUTION. ALL THREE RESIDENCES HAD SERVICES RENEWED.
2024-05-31 11:04 | NO | YES | NO | 20220051 | 37524 | 2022-07-15 16:38 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-01-14 16:00 | CENTRAL | YES | 2022 | 9301 WHITE SETTLEMENT | WHITE SETTLEMENT | TARRANT | TX | 76108 | 32.7605 | -97.4754 | [6 empty] | YES |  |  | 2022-06-15 12:41 | 1338839 | 1339031 | NATURAL GAS |  | 15.369 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-01-14 16:00 | YES | OPERATOR | 2022-01-14 16:08 | 2022-01-14 16:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 16 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 129307 | 132126.316557377102175 | 32882 | 33598.93540983607905 | 0 | 0 |  | 7.874 | 121 | 92.90130624092888243831640058055152394775 | 0 | 0 | 162310 | 70089.8164371029793114804063860667634253 | 165818.1532734541101074383164005805515239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1955-08-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | SEWER (SANITARY/STORM) | YES | 2251192444 | TEXAS 811 |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | JULIE CAMPBELL | COMPLIANCE ANALYST | julie.campbell@atmosenergy.com | 214-535-6117 |  | ROBERT WILLIAMS | robert.williams@atmosenergy.com | 8172072998 | JEFF KNIGHTS | SR VP TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON JANUARY 14, 2022, A THIRD-PARTY CONTRACTOR WAS DIRECTIONAL DRILLING AND BORED INTO ATMOS ENERGY'S 16-INCH STEEL GAS MAIN AT 9301 WHITE SETTLEMENT ROAD. THE INTERMEDIATE PRESSURE MAIN IS A TWO-WAY FEED. THE TECHNICIAN ARRIVED ON THE SCENE AND CONFIRMED THE LEAK AT 4:00 PM. ASSISTANCE WAS REQUESTED AT 4:20 PM. AT 4:08 PM THE TECH NOTED THAT FIRE DEPARTMENT WAS ON SITE INDICATING THEY WERE CONTACTED PRIOR TO THAT TIME. THIS IS THE TIME PROVIDED IN PART A QUESTION 15. OTHER NOTES INDICATE THE POLICE DEPARTMENT WAS ALSO ON THE SCENE, HOWEVER THERE IS NOT A TIME GIVEN. FIRE AND POLICE REMAINED ON SCENE TO PROVIDE TRAFFIC AND PERIMETER ASSISTANCE. STOPPLE FITTINGS WERE APPLIED TO CONTROL THE RELEASE OF GAS AND A SPLIT-WELD SLEEVE WAS INSTALLED TO REPAIR THE LEAK. THESE PERMANENT REPAIRS WERE COMPLETED ON JANUARY 15, 2022, AT 6:30 AM. ON JUNE 15, 2022 AT APPROXIMATELY 12:06 PM, IT WAS DETERMINED THAT REPAIRS COSTS HAD MET THE REPORTING THRESHOLD. A REPORT WAS MADE TO NRC WITHIN THE HOUR. REGARDING PART C QUESTION 5 - THE DIAMETER OF THE PUNCTURE IS 0.226 INCHES, BUT THE FORM ONLY ALLOWS WHOLE NUMBERS. SUPPLEMENTED TO PROVIDE ANSWERS IN PART C, QUESTION 2A AND PART E, QUESTION 3B. 12/19/2022 - FURTHER SUPPLEMENTED TO CHANGE THE SUB-CAUSE FROM FACILITY MARKING OR LOCATION NOT SUFFICIENT TO INCORRECT FACILITY RECORDS/MAPS.
2024-05-31 11:04 | NO | YES | YES | 20220053 | 37368 | 2022-07-21 19:22 | SUPPLEMENTAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2022-06-20 11:15 | CENTRAL | YES | 2022 | 198 BRICK PLANT RD | CORDOVA | WALKER | AL | 35550 | 33.7578 | -87.2124 | YES | [8 empty] | 2022-06-20 13:24 | 1339286 | 1339308, 1339472 | NATURAL GAS |  | 575 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2022-06-20 11:15 | ALLOWED TO BURN OUT |  | 575 | NO | 0 | 2022-06-20 11:15 | NO |  |  | 2022-06-20 12:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.8 | 7 | [7 empty] | CLASS 1 LOCATION | 60000 | 61308.1967213115 | 23000 | 23501.475409836075 | 2000 | 2043.60655737705 | 119000 | 121594.590163934475 | RELIGHTS AND RECONNECTS | 13.07 | 7515 | 5769.862119013062409288824383164005805515 | 0 | 0 | 211515 | 92379.4566846701421770682148040638606676 | 214217.7309714721624092888243831640058055 | 66 | 1 | 400 | 0 | 1 | 400 | 67 | 138 | 138 | 150 | 192.619(A)(4) | 1987-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED TO THE SCADA INFORMATION AND MADE THE APPROPRIATE NOTIFICATIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | YES | [9 empty] | OCCUPANT | UNKNOWN/OTHER | DRAINAGE | NO |  |  |  | UNKNOWN/OTHER | NO | YES | 27 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [143 empty] | YES | [26 empty] | RANDY WILSON | DIRECTOR PIPELINE SAFETY AND COMPLIANCE | randy.wilson@spireenergy.com | 205-337-1337 |  | RANDY WILSON | randy.wilson@spireenergy.com | 205-337-1337 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A 4" HIGH PRESSURE STEEL MAIN WAS DAMAGED BY A FRONT END LOADER AND THE RELEASED GAS IGNITED. THE FIRE TOTALLY DESTROYED THE CONSTRUCTION EQUIPMENT, A MOTOR VEHICLE, AND SURROUNDING BRUSH. THE FRONT END LOADER OPERATOR WAS SEVERELY BURNED IN THE INCIDENT AND WAS HOSPITALIZED. THE EXCAVATOR DID NOT MAKE ANY NOTIFICATION TO THE ONE CALL CENTER FOR LINE LOCATES. HOWEVER, PIPELINE MARKER SIGNS WERE NEAR THE LOCATION THAT WAS DAMAGED. THE PIPELINE WAS SHUT DOWN TO STOP THE FIRE AND ALLOW FOR REPAIRS. 467 CUSTOMERS WERE WITHOUT SERVICE UNTIL REPAIRS WERE COMPLETED. CONFIRMATION OF THE INCIDENT CONDITION BEING MET OF INJURY LIKELY REQUIRING HOSPITALIZATION WAS DETERMINED AT 12:48 PM. THIS WAS WHEN THE OPERATOR OF THE FRONT-END LOADER WAS TRANSPORTED BY AMBULANCE TO THE HOSPITAL WITH INJURIES EXPECTED TO REQUIRE ADMITTANCE. THE NRC NOTIFICATION WAS THEN MADE SHORTLY THEREAFTER AT 1:24 PM.
2024-05-31 11:04 | NO | NO | NO | 20220054 | 36918 | 2022-07-29 12:17 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 OLD TAYLOR ROAD MAIL CODE J48 | CAYCE | SC | 29033 | 2022-07-07 16:00 | EASTERN | YES | 2022 | 4920 AUGUSTA RD | LEXINGTON | LEXINGTON | SC | 29073 | 33.9787 | -81.1941 | YES | [5 empty] | YES |  |  | 2022-07-07 18:03 | 1340874 | 1340979 | NATURAL GAS |  | 2451 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-07-07 15:30 | YES | OPERATOR | 2022-07-07 18:03 | 2022-07-07 15:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 12872 | 13152.6518032786938 | 9356 | 9559.9914754098399 | 189 | 193.120819672131225 | ADMINISTRATIVE | 12.38 | 30343 | 23296.7300435413642960812772133526850508 | 0 | 0 | 52760 | 27073.3755943515228640493468795355587808 | 46202.4941419020292210812772133526850508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 48 | 60 | 192.621 M | 2000-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ACTIONS WERE NOT REQUIRED IN THE IDENTIFICATION OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2207050401 |  |  | CONTRACT LOCATOR | YES | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK NOAH | MANAGER - COMPLIANCE AND INTEGRITY | mark.noah@dominionenergy.com | 704-810-3224 |  | ASHLEY FORTE | ashley.forte@dominionenergy.com | 803-217-6105 | CYNTHIA OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-217-9245 | cynthia.ostrander@dominionenergy.com | ON JULY 7, 2022, AT APPROXIMATELY 3:30 PM, DOMINION ENERGY SOUTH CAROLINA (DESC) RESPONDED TO A BROKEN GAS MAIN NEAR THE INTERSECTION OF I-20 AND US-1 (AUGUSTA RD), IN LEXINGTON, SC. SHORTLY AFTER THE DESC FIRST RESPONDER ARRIVED, THE FIRE DEPARTMENT ARRIVED AND TOOK CONTROL OF THE AREA. THE THIRD PARTY EXCAVATOR, A SUBCONTRACTOR OF THE COMPANY DOING WORK ON THE INTERSTATE, HAD GOUGED THE 6-IN STEEL, MEDIUM PRESSURE MAIN. THE EXCAVATOR DID NOT HAVE A CLEAR LOCATE TICKET. IN ADDITION, THE EXCAVATOR STATED THEY ASSUMED THE MAIN WAS ABANDONED. THE CONTRACTOR HAD SPOTTED THE MAIN AND FULLY EXPOSED IT BEFORE PROCEEDING TO PULL IT OUT OF THE GROUND. A NEARBY VALVE WAS CLOSED TO REDUCE THE LEAK RATE, THOUGH THE LINE STILL LEAKED AS IT WAS TWO-WAY FED. THE LEAK WAS STOPPED BY INSTALLING A STOPPER FITTING AT APPROXIMATELY 11:30 PM. THE DAMAGED PORTION OF PIPE WAS ALREADY SCHEDULED TO BE ABANDONED AT A LATER DATE. AFTER THE LEAK WAS STOPPED AND REPAIRS WERE MADE ON JULY 8, THIS SECTION OF PIPELINE WAS ABANDONED. DUE TO THE LOCATION OF THE DAMAGE, AND THE AMOUNT OF GAS THAT WAS ESCAPING THE DECISION WAS MADE TO SHUT DOWN AUGUSTA RD AND I-20 (BOTH DIRECTIONS OF TRAFFIC). THE INTERSTATE WAS SHUT DOWN DUE TO CARS DRIVING BY AND SPREADING THE PLUME OF GAS. GAS BLEW FOR APPROXIMATELY 8 HOURS AND THE INTERSTATE WAS SHUT DOWN FOR APPROXIMATELY 7 HOURS. DESC MANAGEMENT DECIDED TO MAKE A PHMSA NOTIFICATION DUE TO THE CONCERN THAT OUR ESTIMATED LOST GAS WOULD EXCEED 3,000 MCF AND THAT THIS EVENT WOULD BE CONSIDERED SIGNIFICANT IN NATURE. THOUGH THIS THRESHOLD WAS NOT EXCEEDED, THE INCIDENT WAS SIGNIFICANT IN THE JUDGMENT OF DESC, BECAUSE OF THE DURATION OF STOPPING TRAFFIC FLOW ON A MAJOR ARTERY AND SIGNIFICANT GOVERNMENT AND MEDIA ATTENTION. NOTE: E.3.B DATE MAOP ESTABLISHED IS ESTIMATED AS JAN 1, 2000. DECADE OF INSTALLATION IS KNOWN, BUT NOT EXACT DATE OF THE PIPELINE TEST. LDF: 517493
2024-05-31 11:04 | NO | YES | NO | 20220055 | 39057 | 2022-07-29 13:42 | SUPPLEMENTAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2022-07-03 12:05 | MOUNTAIN | YES | 2022 | 2126 S CREEKSIDE DR | WELLSVILLE | CACHE | UT | 84339 | 41.6944 | -111.8696 |  |  |  | YES | [5 empty] | 2022-07-03 14:16 | 1340511 | 1340630 | NATURAL GAS |  | 152.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-07-03 12:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 152.3 | NO | 0 | 2022-07-03 12:05 |  |  |  | 2022-07-03 12:20 | 2022-07-03 13:04 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2021 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | YES | NO | NO |  |  |  | OTHER | ALUMINUM METER/REGULATOR | [9 empty] | OTHER | [8 empty] | MELTED METER AND REGULATOR | CLASS 3 LOCATION | 283786 | 289973.46524590175565 | 1950 | 1992.51639344262375 | 0 | 0 | 0 | 0 |  | 8.045 | 1225 | 940.52975326560232220609579100145137881 | 0 | 0 | 286961 | 124060.6065773632960270537010159651669086 | 292906.5113926099817222060957910014513788 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 43 | 43 | 60 | 192.619(A)(2) | 2021-03-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | FIRE FIRST, SMOLDERING CIGARETTE IGNITED DECORATIVE WOOD CHIPS WHICH SPREAD TO THE STRUCTURE AND METER/RISER RESULTING IN ESCAPING GAS. NATURAL GAS FIRE WAS SECONDARY. | [47 empty] | STEVEN BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-324-3697 |  | STEVEN BURSETT | steve.bursett@dominionenergy.com | 8016718978 | REID HESS | MANAGER GAS OPERATIONS | 801-324-3374 | reid.hess@dominionenergy.com | ON JULY 3, 2022, DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 2126 CREEKSIDE DRIVE, WELLSVILLE, UTAH. DEU SENT A TECHNICIAN TO THE SITE. UPON ARRIVAL, THE TECHNICIAN NOTED THE METER WAS DAMAGED AND MELTED DUE TO THE FIRE. THE SERVICE LINE WAS EXPOSED BY EXCAVATION AND SQUEEZE BARS WERE USED TO STOP THE FLOW OF GAS TO THE METER. THE FIRE DEPARTMENT NOTED THAT THE DAMAGE TO THE STRUCTURE WAS ESTIMATED TO BE $283,786. DEU CREWS LEAK SCREENED THE AREA WITH NO LEAKS FOUND. DEU RETIRED THE SERVICE LINE TO THE RESIDENCE. THIS EVENT IS BELIEVED TO BE A FIRE FIRST EVENT. THE EXAMINATIONS CONDUCTED BY DEU'S RETAINED CONSULTANT S-E-A, DESCRIBED BELOW, SUBSTANTIATE OUR DETERMINATION. S-E-A SITE INVESTIGATION: ONSITE INVESTIGATION CONDUCTED AUGUST 16, 2022 S-E-A OBSERVED FIRE PATTERNS ON THE EXTERIOR OF THE STRUCTURE INDICATED THAT THE FIRE INITIATED NEAR, OR ON-GRADE, ON THE SOUTHEAST CORNER OF THE RESIDENCE. FIRE THEN SPREAD VERTICALLY AND TO THE WEST, ENTERING THE ATTIC NEAR THE CENTER OF THE RESIDENCE. THE RESIDENCE WAS ENCIRCLED BY LANDSCAPING WOOD CHIPS, WHICH EXTENDED APPROXIMATELY 3 FEET FROM THE EXTERIOR WALLS OF THE RESIDENCE. THE REMAINING PORTIONS OF THE DOMINION ENERGY EQUIPMENT WERE THE STEEL PIPE STUB UP TO THE METER SET AND THE DISCHARGE PIPING FROM THE METER SET. THE REGULATOR AND FLOW METER THEMSELVES HAD MELTED DURING THE FIRE AND DOMINION ENERGY EMPLOYEES FOUND THE REMAINS POOLED ON THE GROUND SHORTLY AFTER THE FIRE. BASED ON S-E-A'S EXAMINATION OF ALL AVAILABLE EVIDENCE, THE ONLY HEAT SOURCE FOR IGNITION OF THE FIRE WAS AN IMPROPERLY DISPOSED OF CIGARETTE. THE NATURAL GAS CONTAINED WITHIN THE ASSOCIATED UNDERGROUND SERVICE LATERAL, STUB-UP PIPING, AND METER SET CANNOT SELF-IGNITE, AND NO OTHER COMPETENT HEAT SOURCE WAS IDENTIFIED THAT MAY HAVE ORIGINATED FROM THE DOMINION ENERGY SUPPLIED EQUIPMENT. DOMINION ENERGY SERVICE LINE PRESSURE TEST PRESSURE TEST CONDUCTED AUGUST 19, 2022 FOLLOWING THE ONSITE INVESTIGATION, A PRESSURE TEST OF THE AFFECTED SERVICE LINE WAS CONDUCTED. AN AIR TEST WAS PERFORMED WITH THE RISER INCLUDED. PRESSURE WAS UNABLE TO BUILD AS THE AIR LEAKED CONTINUOUSLY FROM THE RISER. THE RISER WAS THEN EXCAVATED, REMOVED, AND BAGGED FOR EVIDENCE USING THE CHAIN OF CUSTODY PROCEDURE. THE SERVICE LINE WAS CAPPED AT THE POINT THE RISER WAS CUT FROM. AIR WAS INTRODUCED AT A PRESSURE OF 45 PSIG. THE SERVICE LINE WAS TESTED AT 45 PSIG FOR 15 MINUTES WITH NO PRESSURE LOSS INDICATING NO LEAKS ON THE SERVICE LINE. S-E-A LABORATORY EXAMINATION OF RISER PIPE - LEAK TEST CONDUCTED FEBRUARY 24, 2023: S-E-A DETERMINED THAT THE SOURCE OF THE LEAK WAS FROM MELTED POLYETHYLENE PIPING UPSTREAM OF THE STEEL BARB FITTING THAT WAS SUBJECTED TO HEAT FROM THE FIRE. AFTER THE BREACH, THE GAS ESCAPED THROUGH THE FLEXIBLE STEEL SLEEVE. THERE IS NO AVAILABLE EVIDENCE TO SUPPORT AN OPINION THAT A TEAR IN THE CORROSION PROTECTION, PRIOR TO THE FIRE, WAS CAUSAL TO THIS INCIDENT. - DESTRUCTIVE TEST CONDUCTED JUNE 13, 2023: S-E-A CONCLUDED THAT THE POLYETHYLENE MATERIAL DEPOSITED IN THE AREA PAST THE BARB FITTING RESULTED FROM THE POLYETHYLENE MELTING DURING THE FIRE AND THE CONTINUOUS GAS PRESSURE CAUSED THE SOFT POLYETHYLENE TO FLOW THROUGH THE BARB FITTING. UPON SECTIONING THE PORTION OF RISER PIPE NEAR THE BARB FITTING, EVIDENCE SHOWED THAT THE BARB FITTING WAS FULLY INSERTED INTO THE POLYETHYLENE PIPE, MEANING IT WAS CORRECTLY INSTALLED DURING THE MANUFACTURING PROCESS. AFTER COMPLETION OF BOTH LABORATORY EXAMINATIONS, THERE IS NO EVIDENCE AVAILABLE TO S-E-A TO SUPPORT AN OPINION THAT THE RISER PIPE WAS CAUSAL TO THE INCIDENT.
2024-05-31 11:04 | NO | YES | YES | 20220056 | 36988 | 2022-08-18 11:36 | ORIGINAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2022-07-19 18:00 | CENTRAL | NO | 2022 | 401 MORGAN AVENUE | CHESTERTON | PORTER | IN | 46304 | 41.609 | -87.0563 | [6 empty] | YES |  |  | 2022-07-19 18:19 | 1341980 | 1342191 | NATURAL GAS |  | 2.89 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-07-19 09:45 | NO |  |  | 2022-07-19 09:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1928 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | SERVICE TEE | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 9.555 | 28 | 21.49782293178519593613933236574746008708 | 0 | 0 | 28 | 16.05224963715529753265602322206095791001 | 21.49782293178519593613933236574746008708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 1970-12-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ISSUE DID NOT INVOLVE PRESSURE REGULATION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  |  | YES | THE INTERNAL COMPONENTS OF THE SERVICE TEE, WHICH WAS INSTALLED IN 1928, WERE NOT PRESENT. WHEN THE CAP ON THE TEE WAS REMOVED TO ACCESS THE COMPONENTS THAT WOULD SHUT OFF THE FLOW OF GAS TO THE SERVICE, THE GAS ESCAPED UNEXPECTEDLY AND CUT THE EMPLOYEES LEATHER-GLOVED HAND. | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [44 empty] | YES |  |  |  |  | RICK SMITH | MGR PIPELINE SAFETY AND COMPLIANCE | ricksmith@nisource.com | 219-252-4057 |  | RIC SMITH | ricksmith@nisource.com | 219-252-4057 | RICK SMITH | MGR PIPELINE SAFETY AND COMPLIANCE | 219-252-4057 | ricksmith@nisource.com | THE INTERNAL COMPONENTS OF THE SERVICE TEE, WHICH WAS INSTALLED IN 1928, WERE NOT PRESENT. WHEN THE CAP ON THE TEE WAS REMOVED TO ACCESS THE COMPONENTS THAT WOULD SHUT OFF THE FLOW OF GAS TO THE SERVICE, THE GAS ESCAPED UNEXPECTEDLY AND CUT THE EMPLOYEES LEATHER-GLOVED HAND. THE EMPLOYEE RECEIVED A SMALL LACERATION, BUT WAS CONCERNED IT MAY HAVE HAD GAS BLOWN INTO THE LACERATION UNDER THE SKIN. PER OUR PROCEDURES, THE EMPLOYEE WENT TO THE EMERGENCY ROOM TO HAVE THE INJURY LOOKED AT. THERE WAS NO DOCTOR PRESENT, SO HE WAS ADMITTED BASED ON THE ADMITTING NURSES RECOMMENDATION. THE EMPLOYEE RECEIVED BASIC FIRST AID, BUT WAS NOT SEEN BY A DOCTOR FOR 33HRS. UPON SEEING THE PHYSICIAN, IT WAS INDICATED THERE WAS NO EXPOSURE AND THAT THE EMPLOYEE SHOULD NOT HAVE BEEN ADMITTED. THE EMPLOYEE WAS RELEASED AND RETURNED TO WORK THE FOLLOWING DAY. THIS IS THE FINAL REPORT.
2024-05-31 11:04 | NO | YES | NO | 20220057 | 37046 | 2022-08-29 19:12 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-08-04 02:29 | PACIFIC | YES | 2022 | 667 NORTH F STREET | UPLAND | SAN BERNARDINO | CA | 91786 | 34.1016 | -117.6501 | [5 empty] | YES |  |  |  | 2022-08-04 02:29 | 1343499 | 48hr update NRC# 1343678 | NATURAL GAS |  | 8.7 | 426.9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-07-30 09:59 | NO |  |  | 2022-07-30 10:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | YES | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | STUB | 1930 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 14580 | 14897.8918032786945 | 344432 | 351941.7468852460428 | 0 | 0 |  | 6.3303 | 55 | 42.22786647314949201741654571843251088534 | 2702 | 2074.539912917271407837445573294629898403 | 361769 | 156573.7047700397933234833091436865021771 | 368956.4064679151581998548621190130624093 | 6 | 0 | 130 | 0 | 0 | 130 | 6 | 45 | 45 | 60 | 192.621 M | 1930-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A WATER INTRUSION INCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER INTRUSION CAUSED BY A WATER MAIN LEAK | [136 empty] | YES | [17 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 07/30/2022 SOCALGAS CREWS RESPONDED TO AN UNDER PRESSURE CONDITION AT 220 A STREET, UPLAND, SAN BERNARDINO. ON INVESTIGATION COMPLETED TO DATE REGARDING THE UNDER PRESSURE CONDITION, SOCALGAS IDENTIFIED A LEAKING 3" WATER MAIN AT THE CROSS POINT OF A 3/4" STEEL GAS STUB THAT AFFECTED MULTIPLE SERVICES AND THE MAIN. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO UNDER-PRESSURE. THIS WAS REPORTED TO THE DOT DUE TO GAS RELEASE AND DAMAGE EXCEEDING $129,300.
2024-05-31 11:04 | NO | YES | NO | 20220058 | 37803 | 2022-09-02 13:00 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2022-07-16 04:00 | EASTERN | YES | 2022 | 55 RT 24 | CHESTER TOWNSHIP | MORRIS | NJ | 07930 | 40.7793 | -74.7203 |  |  |  | YES | [5 empty] | 2022-08-15 04:03 | 1344582 | 1344584 | NATURAL GAS |  | 514 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-07-16 04:00 | OPERATOR/CONTRACTOR |  | 514 | NO | 0 | 2022-07-16 04:00 |  |  |  | 2022-07-16 04:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1983 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 225000 | 229905.737704918125 | 25000 | 25545.081967213125 | 0 | 0 |  | 5.31 | 2729 | 2095.269956458635703918722786647314949202 | 0 | 0 | 252729 | 109494.8489138452431059506531204644412192 | 257546.0896285898857039187227866473149492 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 60 | 192.619(A)(1) | 1983-08-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A JCP&L POWER LINE CAME DOWN 2 MILES AWAY FROM THE PSE&G POINT OF IGNITION. TEN OTHER IGNITIONS OF VARIOUS TYPES (NO OTHER GAS) OCCURRED IN THE 2 MILE AFFECTED ZONE. THE CAUSE FOR THE POWER LINE DROP HAS NEVER BEEN DETERMINED. | [154 empty] | ROGER GUNNELS | PRINCIPAL REGULATORY SPECIALIST | roger.gunnels@pseg.com | 9739871589 |  | ROGER GUNNELS | roger.gunnels@pseg.com | 9739871589 | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON SATURDAY JULY 16TH PSE&G RECEIVED NOTIFICATION THAT A DOWNED JCP&L ELECTRIC WIRE THAT FOUND ITS WAY TO NEARBY METAL GUARD RAIL AND RESULTED IN THE IGNITION OF A 6 INCH 60 LB. STEEL MAIN LOCATED AT 55 RT 24 IN CHESTER TOWNSHIP. THE LOCATION OF THE IGNITION INVOLVES A BRIDGE. THE MAIN WAS THROTTLED AND TEMPORARY BYPASS WAS INSTALLED TO CONTINUE TO SERVICE CUSTOMERS. THE LOCATION OF THE DOWNED WIRE WAS 2 MILES AWAY FROM THE IGNITION LOCATION. THE CAUSE FOR HOW THE WIRE CAME INTO CONTACT WITH THE GUARD RAIL IS UNKNOWN AT THIS TIME. THERE ARE NO INDICATIONS AT THIS TIME THAT ANY TYPE OF DAMAGE WAS INVOLVED. A PERMANENT REPAIR PLAN IS BEING DEVELOPED AT THIS TIME.
2024-05-31 11:04 | NO | YES | NO | 20220059 | 37563 | 2022-09-02 13:54 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2022-09-01 09:50 | EASTERN | YES | 2022 | 1601 GREEN MOUNTAIN PARKWAY | WILLIAMSBURG | JAMES CITY | VA | 23185 | 37.2083 | -76.5973 | [7 empty] | YES | DRESSER REPAIR SLEEVE | 2022-09-01 09:59 | 1346111 |  | NATURAL GAS |  | 1557 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-08-31 11:12 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-08-31 11:31 | 2022-08-31 11:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 56 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1960 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75000 | 76635.245901639375 | 50000 | 51090.16393442625 | 0 | 0 |  | 6.9676 | 10849 | 8329.638606676342525399129172714078374456 | 0 | 0 | 135849 | 60184.8373741940293904208998548621190131 | 136055.0484427419675253991291727140783745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 137 | 150 | 192.619(A)(4) | 1960-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT LARGE ENOUGH TO BE IDENTIFIED BY THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | B224300196 |  |  | CONTRACT LOCATOR | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [143 empty] | YES | [26 empty] | MICHAEL SMITH | DIRECTOR- COMPLIANCE AND SYSTEM INTEGRITY | mlsmi@southernco.com | 5408943733 |  | MICHAEL SMITH | mlsmi@southernco.com | 5408943733 | MICHAEL SMITH | DIRECTOR- COMPLIANCE AND SYSTEM INTEGRITY | 5408943733 | mlsmi@southernco.com | VIRGINIA NATURAL GAS (COMPANY) WAS MADE AWARE OF A LEAK ON AUGUST 31, 2022, NEAR THE INTERSECTION OF POCAHONTAS TRAIL AND GREEN MOUNT PARKWAY AT 1601 GREEN MOUNT PARKWAY IN WILLIAMSBURG, VA. SHIRLEY CONTRACTING COMPANY (CONTRACTOR) WAS CONSTRUCTING A NEW ROAD AND SHOULDER FOR VDOT FROM THE INTERSECTION OF POCAHONTAS TRAIL AND GREEN MOUNT PARKWAY FOR A DISTANCE OF APPROXIMATELY 900 FEET EAST OF THAT INTERSECTION. THE CONTRACTOR WAS EXCAVATING DIRECTLY ABOVE THE COMPANY'S 16-INCH STEEL PIPELINE WHEN IT SCRAPED THE PIPELINE CAUSING COATING DAMAGE, DENTING, AND RIPPING OFF AN EXISTING TAP CAUSING THE LEAK. THE FACILITY WAS MARKED CORRECTLY, BUT PARTS OF THE MARKS WERE DESTROYED BY THE CONTRACTOR DURING CONSTRUCTION. THE CONTRACTOR SHOULD HAVE CONTACTED VA811 TO GENERATE A 3-HOUR TICKET TO REMARK THE FACILITY BEFORE CONTINUING ITS WORK. THE COMPANY WORKED WITH THE LOCAL FIRE DEPARTMENT AND LAW ENFORCEMENT TO SHUT DOWN ROUTE 60 AND REDUCED THE PRESSURE ON THE PIPELINE FROM APPROXIMATELY 150 PSI TO 100 PSI UNTIL REPAIRS COULD BE MADE. THE COMPANY UTILIZED A REPAIR SLEEVE TO REPAIR THE LEAK.
2024-05-31 11:04 | NO | YES | YES | 20220060 | 38223 | 2022-09-17 19:04 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2022-09-15 20:05 | PACIFIC | YES | 2022 | 6500 URSULA PL S. | SEATTLE | KING | WA | 98108 | 47.5459 | -122.3103 | YES | [8 empty] | 2022-09-15 18:47 | 1347398 | 1347652 | NATURAL GAS |  | 0.01 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2022-09-15 14:24 | ALLOWED TO BURN OUT |  | 0.01 | NO | 0 | 2022-09-15 14:24 | NO |  |  | 2022-09-15 14:24 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1956 | UNKNOWN | [7 empty] | OTHER | WELD BETWEEN A FLANGE AND EXISTING RISER | [9 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 115000 | 117507.377049180375 | MEDICAL EXPENSES ONLY, NO DAMAGE TO PSE OR OTHER PROPERTY REQUIRING REPAIR. | 8.94 | 0 | 0 | 0 | 0 | 115000 | 49647.95081967215 | 117507.377049180375 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 135 | 250 | 192.619(A)(3) | 2014-05-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 6 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | UNINTENTIONAL IGNITION WHILE WELDING ON AN OUT OF SERVICE REGULATOR STATION, AND OUR WORKING ASSUMPTION IS THAT IT WAS GAS AND WE ARE TAKING CORRECTIVE ACTIONS ON THAT BASIS. | YES |  |  |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [40 empty] | YES | [8 empty] | JUSTIN WAHLBORG | SR. COMPLIANCE PROGRAM MANAGER | justin.wahlborg@pse.com | 4257661811 |  |  |  |  | ZAKARIA MOHAMED | MANAGER COMPLIANCE | 4252476751 | zakaria.mohamed@pse.com | PUGET SOUND ENERGY (PSE) AND INFRASOURCE (IFS) WERE PERFORMING REPLACEMENT WORK ON A REGULATOR STATION FACILITY. THE FACILITY WAS ISOLATED FROM THE SURROUNDING SYSTEM BY CLOSING THE INLET AND OUTLET VALVES AND HAD BEEN BLOWN DOWN AND PURGED OUT OF SERVICE USING NITROGEN. THE IFS CREW WAS WORKING REBUILDING A STATION REGULATOR RUN BY ON WELDING A FLANGE ONTO AN OPEN PIPE RISER WHEN UNINTENTIONAL IGNITION OCCURRED. TWO CREW MEMBERS WERE TRANSPORTED TO THE HOSPITAL: AN IFS WELD HELPER WAS TREATED IN THE ER AND RELEASED, AND A PSE PRESSURE CONTROL TECHNICIAN WAS ADMITTED TO THE HOSPITAL AT 20:05 FOR BURN TREATMENT. OUR INVESTIGATION WAS INCONCLUSIVE, BUT OUR WORKING ASSUMPTION IS THAT ONE OF THE CLOSED VALVES BYPASSED A SMALL AMOUNT OF GAS. THE CONSTRUCTION PROCEDURE THAT WAS BEING FOLLOWED DURING THE PROJECT CONTAINED SEVERAL ISOLATION AND MONITORING STEPS: - THE VALVES ISOLATING THE WORK AREA FROM THE ACTIVE SYSTEM WERE SUBJECTED TO A "SHUT IN TEST" AND PASSED THE TEST. - THE PIPING IN THE WELD AREA HAD BEEN INERTED USING NITROGEN, BUT THE IGNITION OCCURRED SEVERAL HOURS AFTER INTERTING PROCESS HAD BEEN COMPLETED. - THE CREW WAS MONITORING FOR GAS READS IN THE INERTED PIPE RISERS AS PART OF THE WELDING PROCESS AND CONFIRMED 0% GAS READS. INVESTIGATION AFTER THE INCIDENT FOUND GAS READS ON THE INERTED SIDE OF THE CLOSED STATION OUTLET VALVE. THE VALVE WAS GREASED TO BRING THESE READS TO 0% GAS. AS PART OF THE FOLLOW UP FROM A SAFETY DEPARTMENT LED ROOT CAUSE ANALYSIS, PSE IS REVISING ENERGY CONTROL PROCEDURES TO ADDRESS THE POSSIBILITY THAT GAS MIGHT LEAK BY A CLOSED VALVE. PSE IS ALSO ADDRESSING MANAGEMENT OF CHANGE FOR WRITTEN CONSTRUCTION PROCEDURE UPDATES, SINCE LAST MINUTE CHANGES NEEDED TO BE MADE TO THE PROCEDURE DOCUMENT FOR THE REGULATOR STATION CONSTRUCTION PROJECT BASED ON PIPING CONDITIONS FOUND IN THE FIELD.
2024-05-31 11:04 | NO | YES | NO | 20220061 | 37148 | 2022-09-22 12:57 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2022-08-24 13:00 | EASTERN | YES | 2022 | I40 & ROCK QUARRY RD | RALEIGH | WAKE | NC | 27610 | 35.7472 | -78.594 | [6 empty] | YES |  |  | 2022-08-24 19:04 | 1345455 | 1345507 | NATURAL GAS |  | 1886 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-08-24 13:05 | NO |  |  | 2022-08-24 13:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 210000 | 214578.68852459025 | 15000 | 15327.049180327875 | 0 | 0 |  | 5.75 | 10845 | 8326.5674891146589259796806966618287373 | 0 | 0 | 235845 | 103354.6753432154357764876632801161103048 | 238232.3051940327839259796806966618287373 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 55 | 55 | 60 | 192.621 M | 2020-03-18 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT REQUIRED TO IDENTIFY THE FAILURE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 10 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK NOAH | MANAGER - INTEGRITY AND COMPLIANCE | mark.noah@dominionenergy.com | 704-810-3224 |  | CURTIS RICE | curtis.rice@dominionenergy.com | 919-836-2448 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS | 704-810-3230 | scott.swindler@dominionenergy.com | ON AUGUST 24TH, 2022, AT APPROXIMATELY 1:00 PM, DOMINION ENERGY NORTH CAROLINA (DENC) RESPONDED TO A RUPTURED GAS MAIN NEAR THE INTERSECTION OF I-40 AND ROCK QUARRY ROAD, IN RALEIGH, NC. WHEN THE DENC FIRST RESPONDER ARRIVED, EMERGENCY RESPONDERS HAD ALREADY TAKEN CONTROL OF THE AREA. THE THIRD-PARTY EXCAVATOR, A SUBCONTRACTOR OF THE COMPANY DOING WORK ON THE INTERSTATE, HAD PIERCED THE 12-IN STEEL, DISTRIBUTION PRESSURE MAIN WHILE INSTALLING SOUND BARRIER PANELS ALONG THE INTERSTATE ROW. THE EXCAVATOR DID NOT HAVE A LOCATE TICKET. THE CONTRACTOR DID CALL IN A LOCATE REQUEST AFTER THE MAIN HAD BEEN DAMAGED. THE LEAK WAS STOPPED BY INSTALLING STOPPER FITTINGS AT APPROXIMATELY 12:30 AM. GAS BLEW FOR APPROXIMATELY 12 HOURS. DENC MANAGEMENT DECIDED TO MAKE A PHMSA NOTIFICATION DUE TO THE CONCERN THAT OUR REPAIR COSTS WOULD EXCEED $129,300 AND THAT THIS EVENT WOULD BE CONSIDERED SIGNIFICANT IN NATURE. REPAIRS HAVE BEEN COMPLETED AND THE LINE IS BACK IN SERVICE.
2024-05-31 11:04 | NO | YES | NO | 20220062 | 37441 | 2022-09-30 09:59 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2022-09-01 14:12 | EASTERN | NO | 2022 | 120 DEEDS DRIVE | DOVER | TUSCARAWAS | OH | 44622 | 40.5538 | -81.4983 | YES | [8 empty] | 2022-09-01 16:05 | 1346162 |  | NATURAL GAS |  | 13.208 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-01 14:12 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 13.2 | NO | 2 | 2022-09-01 14:12 | NO |  |  | 2022-09-01 14:14 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1989 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | DRISCO | PLASTIC |  |  |  |  | OTHER | DRISCO 8000 |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 2 | 1.3 | [7 empty] | CLASS 3 LOCATION | 310000 | 316759.01639344275 | 800 | 817.44262295082 | 5000 | 5109.016393442625 | 0 | 0 |  | 10.5828 | 140 | 107.489114658925979680696661828737300435 | 0 | 0 | 315940 | 136417.8514121202544876632801161103047896 | 322792.9645244951209796806966618287373004 | 6 | 0 | 0 | 1 | 0 | 0 | 8 | 58 | 58 | 80 | 192.619(A)(2) | 1989-04-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | A223704353 | OH811 |  | CONTRACT LOCATOR | YES | YES | 4 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | AMY LAURIE KONCELIK | SUPERVISOR PIPELINE COMPLIANCE | amy.l.koncelik@dominionenergy.com | 13308109842 |  | AMY LAURIE KONCELIK | amy.l.koncelik@dominionenergy.com | 13308109842 | AMY LAURIE KONCELIK | SUPERVISOR PIPELINE COMPLIANCE | 13308109842 | amy.l.koncelik@dominionenergy.com | A SUBCONTRACTOR FOR A THIRD PARTY CONTRACTOR WAS BORING TO INSTALL FIBER OPTIC LINES AND BORED THROUGH OPERATOR'S 4 INCH MAINLINE, WHICH WAS PROPERLY MARKED. THIRD PARTY CONTRACTOR ACKNOWLEDGED THAT THEIR SUB-CONTRACTOR DECIDED TO DO A PORTION OF THE JOB WITHOUT BEING INSTRUCTED TO DO SO AND FAILED TO POTHOLE, WHICH CREATED THIS EXCAVATION DAMAGE.
2024-05-31 11:04 | NO | YES | NO | 20220063 | 37556 | 2022-09-30 15:37 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-02 10:59 | EASTERN | YES | 2022 | 1631 N. JEROME ROAD (FARM FIELD WEST OF ADDRESS) | ARCADA TOWNSHIP | GRATIOT | MI | 48847 | 43.3113 | -84.6302 | YES | [8 empty] | 2022-09-02 19:44 | 1346279 | 1346357 | NATURAL GAS |  | 309 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-09-02 10:59 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-09-02 10:59 | 2022-09-02 11:32 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1944 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 12.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 250000 | 255450.81967213125 | 372 | 380.1108196721313 | 0 | 0 |  | 8.95 | 2766 | 2123.677793904208998548621190130624092888 | 0 | 0 | 253138 | 109676.6611430203365548330914368650217707 | 257954.6082857075902985486211901306240929 | 220 | 18 | 1294 | 0 | 0 | 1294 | 238 | 259 | 259 | 375 | 192.619(C) | 1968-11-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO | [5 empty] | YES | 30 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON FRIDAY, SEPTEMBER 2, 2022 AT APPROXIMATELY 10:59 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE BY A THIRD-PARTY CONTRACTOR INSTALLING DRAIN TILES IN A FARM FIELD WEST OF 1631 N. JEROME ROAD, ARCADA TOWNSHIP (GRATIOT COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:32 HOURS AND CONFIRMED A 4-INCH HIGH-PRESSURE PIPELINE FEEDING CONSUMERS ENERGY'S ITHACA REGULATION STATION HAD BEEN DAMAGED RESULTING IN A SEVERED PIPELINE. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 12:00 HOURS. TO CONTROL THE GAS FLOW, THE GAS MECHANICS CLOSED THE G-VALVE AT REGULATOR STATION #63831 AT 12:00 HOURS TO ISOLATE DOWNSTREAM OF THE DAMAGE TO MAINTAIN SERVICE TO CUSTOMERS. THE H-67 VALVE WAS CLOSED AT 12:20 HOURS TO ISOLATE AND SHUT-OFF GAS AT THE DAMAGE LOCATION. A REQUEST WAS MADE TO LARGE COMMERCIAL AND INDUSTRIAL CUSTOMERS TO REDUCE GAS USAGE IN AN EFFORT TO MAINTAIN THE PRESSURE REQUIRED TO SERVE THE CITY OF ITHACA. DESPITE EFFORTS TO MAINTAIN PRESSURE, A CONTINUED PRESSURE DROP WAS OBSERVED, AND A DECISION WAS MADE AT APPROXIMATELY 15:30 HOURS TO BEGIN SHUTTING OFF METERS FOR THE 1400+ CUSTOMERS SERVED BY THIS FEED. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 62-FEET OF 4-INCH HIGH-PRESSURE PIPELINE. REPAIRS WERE COMPLETED AND GAS SERVICE RESTORED TO THE HIGH PRESSURE PIPELINE ON SEPTEMBER 3, 2022, AT APPROXIMATELY 06:30 HOURS. RESTORATION TO THE MEDIUM PRESSURE PIPELINE WAS COMPLETED AT 15:30 AND SERVICE RESTORATION BEGAN AT 18:00 HOURS.
2024-05-31 11:04 | NO | YES | NO | 20220064 | 37991 | 2022-10-07 13:07 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-08 17:52 | EASTERN | YES | 2022 | 1102 LAKE STREET | KALAMAZOO | KALAMAZOO | MI | 49001 | 42.2809 | -85.5665 | [5 empty] | YES |  |  |  | 2022-09-08 21:02 | 1346805 | 1346828 | NATURAL GAS |  | 315 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-08 17:52 | ALLOWED TO BURN OUT |  | 315 | NO | 25 | 2022-09-08 17:52 |  |  |  | 2022-09-08 17:58 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | UNKNOWN |  |  |  |  | 4 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 6.2 | [7 empty] | CLASS 3 LOCATION | 112929 | 115391.222459016439725 | 26190 | 26761.02786885246975 | 165 | 168.597540983606625 | 0 | 0 |  | 8.95 | 2819 | 2164.370101596516690856313497822931785196 | 0 | 0 | 142103 | 61747.9887092246058594484760522496371553 | 144485.2179704490327908563134978229317852 | 11 | 0 | 86 | 2 | 0 | 86 | 11 | 54 | 54 | 60 | 192.619(A)(2) | 1991-05-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 6 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 2022082304088 |  |  | CONTRACT LOCATOR | NO | YES | 11 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON SEPTEMBER 8, 2022, AT APPROXIMATELY 17:52 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR 1102 LAKE STREET, KALAMAZOO (KALAMAZOO COUNTY), MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:58 HOURS. THE GSW CONFIRMED A 4-INCH MEDIUM-PRESSURE PLASTIC PIPELINE WAS DAMAGED BY A CONSUMERS ENERGY (2ND-PARTY) CONTRACTOR. DURING THE BORE SHOT PULL BACK, THE BORE REAMER DAMAGED THE PIPELINE CAUSING GAS TO BE RELEASED AND A SUBSEQUENT IGNITION. THE PREVIOUS NIGHT A CANDLELIGHT VIGIL WAS HELD NEAR THE DAMAGE LOCATION, CANDLES REMAINING AT THE SIGHT ARE THOUGHT TO BE THE IGNITION SOURCE. THE POLICE AND FIRE DEPARTMENT WERE ONSITE AND RESIDENTIAL AND COMMERCIAL STRUCTURES WITHIN ONE BLOCK IN ALL DIRECTIONS WERE EVACUATED AND ELECTRIC SERVICE DISCONTINUED. SEVERAL CONTRACT EMPLOYEES WORKING ON BEHALF OF THE OPERATOR SUSTAINED MINOR BURNS AND RECEIVED MEDICAL TREATMENT BUT OVERNIGHT HOSPITALIZATION WAS NOT REQUIRED. POST-ACCIDENT DRUG AND ALCOHOL TESTING WAS PERFORMED FOR ALL CONTRACT EMPLOYEES WORKING ON THIS PROJECT. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 18:40 HOURS AND SQUEEZED THE PIPELINE AT A REMOTE LOCATION WEST OF MILL STREET STOPPING GAS FROM BLOWING. ONCE THE GAS WAS CONTAINED, THE FIRE WAS ALLOWED TO EXTINGUISH BEFORE ASSESSING DAMAGE AND MAKING REPAIRS. IN ADDITION TO OPERATOR EMERGENCY RESPONSE AND REPAIRS COSTS, SIGNAGE, TRAFFIC CONTROL AND LIGHTING AND A NEARBY AUTOMOBILE WAS DAMAGED AND WILL REQUIRE REPLACEMENT AND/OR REPAIR. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 4-FEET OF 4-INCH MEDIUM-PRESSURE PLASTIC PIPE. REPAIRS WERE COMPLETED AND GAS SERVICE WAS RESTORED ON SEPTEMBER 9, 2022, AT APPROXIMATELY 04:30 HOURS. SERVICE RESTORATION TO IMPACTED CUSTOMERS BEGAN ON SEPTEMBER 9, 2022, AT APPROXIMATELY 15:30 HOURS. FURTHER INCIDENT INVESTIGATION DETERMINE THE THE CONTRACTOR PERFORMING WORK ON BEHALF OF CONSUMERS ENERGY AND RESPONSIBLE FOR LOCATING AND STAKING THE NATURAL GAS PIPELINE FAILED TO PROPERLY IDENTIFY AND MARK THE PIPELINE DOCUMENTED ON THE CONSTRUCTION PRINT. THE FAILURE RESULTED IN THE CREW UNKNOWINGLY BORING NEAR AN UNMARKED GAS FACILITY CAUSING A RELEASE OF GAS AND SUBSEQUENT IGNITION.
2024-05-31 11:04 | NO | YES | NO | 20220065 | 37666 | 2022-10-07 15:12 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-09-09 11:23 | EASTERN | YES | 2022 | HALL ROAD W/AVON LANE | CLINTON TOWNSHIP | MACOMB | MI | 48036 | 42.6299 | -82.8645 | [6 empty] | YES |  |  | 2022-09-09 20:03 | 1346895 |  | NATURAL GAS |  | 6068 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 12 | 2022-09-09 11:23 | YES | OPERATOR | 2022-09-09 13:15 | 2022-09-09 11:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1953 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1.2 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 68869 | 70370.570000000028225 | 183 | 186.990000000000075 | 0 | 0 |  | 8.95 | 54309 | 41697.3309143686502177068214804063860668 | 0 | 0 | 123361 | 60946.2780551524060950362844702467343977 | 112254.8909143686785177068214804063860668 | 13 | 0 | 7 | 0 | 0 | 7 | 13 | 329 | 329 | 400 | 192.619(A)(2) | 1994-10-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 2022080903891 |  |  | CONTRACT LOCATOR | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON SEPTEMBER 9, 2022, AT APPROXIMATELY 11:23 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE ON HALL ROAD (WEST OF AVON LANE), CLINTON TOWNSHIP (MACOMB COUNTY), MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 11:51 HOURS. THE GSW CONFIRMED THE DAMAGE WHICH WAS LATER DETERMINED TO BE A 2-INCH STUB (OFF A 6-INCH HIGH-PRESSURE PIPELINE) STRUCK BY A THIRD-PARTY CONTRACTOR INSTALLING DRAIN TILES. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 12:09 HOURS AND PROCEEDED TO EXCAVATE TWO REMOTE HOLES TO THE EAST AND WEST OF THE DAMAGE LOCATION. WHILE ATTEMPTING TO SQUEEZE THE PIPELINE ON THE WEST SIDE OF THE DAMAGE, THE PIPELINE CRACKED AND REQUIRED EXCAVATION AT A THIRD LOCATION. A MUELLER CONTROL FITTING WAS INSTALLED WEST OF THE DAMAGE TO CONTAIN THE BLOWING GAS. THE PIPELINE WAS A ONE-WAY FEED AND RESULTED IN A LOSS OF SERVICE TO 20 CUSTOMERS. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE INCIDENT. THE DAMAGED SEGMENT OF THE PIPELINE WAS CUT OUT AND REPLACED WITH APPROXIMATELY 6-FEET OF 6-INCH HIGH-PRESSURE PIPELINE. REPAIRS WERE COMPLETED AND GAS SERVICE WAS RESTORED ON SEPTEMBER 10, 2022, AT APPROXIMATELY 11:35 HOURS. SERVICE RESTORATION TO IMPACTED CUSTOMERS BEGAN AFTER REPAIRS TO THE PIPELINE WERE COMPLETED. AN INCIDENT INVESTIGATION DETERMINED THE A 2" NATURAL GAS STUB WAS DOCUMENTED ON THE RECORD BUT WAS NOT MARKED BY THE STAKING EMPLOYEE RESULTING IN A NATURAL GAS PIPELINE DAMAGE.
2024-05-31 11:04 | YES | NO | NO | 20220066 | 37623 | 2022-10-19 11:56 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2022-09-28 14:05 | EASTERN | YES | 2022 | 5409 INNISBROOKE PLACE | GREENWOOD | JOHNSON | IN | 46142 | 39.6189 | -86.2052 | [5 empty] | YES |  |  |  | 2022-09-28 15:22 | 1348530 | 1348695 | NATURAL GAS |  | 22.08 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-09-28 14:05 | OTHER | FIRE EXTINGUISHED BY OPERATOR SQUEEZING OFF THE GAS SERVICE LINE. | 22.08 | NO | 1 | 2022-09-28 14:24 | YES | OPERATOR | 2022-09-28 14:31 | 2022-09-28 14:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 | YES | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1992 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 400000 | 408721.31147541 | 1381 | 1411.110327868853025 | 2500 | 2554.5081967213125 | 0 | 0 |  | 6.4311 | 142 | 109.024673439767779390420899854862119013 | 0 | 0 | 404023 | 174445.4428374456395046298984034833091437 | 412795.954673439933304390420899854862119 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1992-11-04 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.2 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [150 empty] | YES | [16 empty] | YES | RANDA POWERS | LEAD OPERATIONS SPECIALIST - GAS COMPLIANCE | randa.powers@centerpointenergy.com | 317-997-3939 |  | RANDA POWERS | lead operations specialist - gas compliance | 317-997-3939 | SHERRI BELL | MANAGER PIPELINE SAFETY AND COMPLIANCE | 812-4914806 | sherri.bell@centerpointenergy.com | A CREW FROM JOHNSON COUNTY REMC WAS REPAIRING A BURIED 3 PHASE ELECTRIC SERVICE 4' FROM THE HOME LOCATED AT 5409 INNISBROOKE PL, GREENWOOD IN WHEN THE GAS SERVICE CAUGHT ON FIRE, CATCHING THE HOME ON FIRE. THE REMC CREW HAD BEEN USING A BLOW TORCH TO HEAT SHRINK THE REPAIR. THE 3-PHASE ELECTRIC REPAIR WAS APPROXIMATELY 7 INCHES BELOW THE GAS SERVICE LINE. REMC CREW STATED THEY HAD SPOTTED THE GAS SERVICE, WHICH WAS CORRECTLY LOCATED, USED A SHOVEL TO PROTECT THE PLASTIC GAS LINE BEFORE INTRODUCING FLAME NEAR IT. WHILE USING THE FLAME TO SHRINK WRAP THE REPAIR, THERE WAS AN IGNITION OF THE GAS LINE.
2024-05-31 11:04 | NO | YES | YES | 20220068 | 38008 | 2022-10-26 16:13 | SUPPLEMENTAL | 40247 | TEXAS REPUBLIC UTILITY, LLC | 19926 KEENAN CUT OFF RD. | MONTGOMERY | TX | 77316 | 2022-10-03 12:30 | CENTRAL | YES | 2022 | 14020 GROVER CREEK DR | CONROE | MONTGOMERY | TX | 77303 | 30.3531 | -95.3622 |  | YES |  |  |  | YES |  |  |  | 2022-10-04 17:27 | 1349031 | 1349815 (48 Hour Update) | NATURAL GAS |  | 2 | 0 | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES | 2022-10-03 12:30 | OPERATOR/CONTRACTOR |  | 2 | NO | 0 | 2022-10-03 12:30 | YES | OPERATOR | 2022-10-03 12:33 | 2022-10-03 12:33 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE VALVE |  | 2022 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 4" |  |  | 2406 | LEAK |  |  | OTHER | ELECTROFUSION JOINT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 5109.016393442625 | 0 | 0 | 0 | 0 |  | 11 | 22 | 16.89114658925979680696661828737300435414 | 0 | 0 | 5022 | 2171.219039234814876632801161103047895501 | 5125.907540031884796806966618287373004354 | 0 | 0 | 100 | 0 | 0 | 50 | 0 | 40 | 40 | 70 | 192.619(A)(2) | 2022-01-03 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SADDLE, ELECTROFUSION |  | 2022 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [8 empty] | YES |  |  |  | OTHER | SADDLE ELECTROFUSION JOINT DID NOT SEAL COMPLETELY | YES | 2022 | 105 | [69 empty] | YES | [14 empty] | MICHAEL SWAIM | OPERATIONS ADMINISTRATOR | mswaim@ldcgas.com | 936-539-3500 | 936-539-3501 | MICHAEL SWAIM | mswaim@ldcgas.com | 936-539-3500 | BOBBY BROWN JR | CHIEF OPERATING OFFICER | 936-539-3500 | bbrown@ldcgas.com | DURING A HOT TAP PROCEDURE TO CONNECT NEW SERVICE TO A RESIDENCE, THE ELECTROFUSION JOINT DID NOT SEAL COMPLETELY, RESULTING IN A LEAK. DURING AN ATTEMPT TO SQUEEZE OFF THE GAS SUPPLY SO REPAIRS COULD BE MADE, ONE OF TWO PROPERLY GROUNDED SQUEEZERS FAILED. AN ADDITIONAL SQUEEZER (ALSO GROUNDED) WAS BROUGHT INTO THE LOCATION TO SQUEEZE OFF THE SUPPLY ON THAT SIDE OF THE FUSION THE PROCEDURES WERE ADEQUATE AND FOLLOWED FOR ELECTROFUSION AND SQUEEZE OFF. EITHER A SPARK FROM INADVERTENT CONTACT OF METAL ON METAL OR STATIC ELECTRICITY CAUSED THE LEAK TO IGNITE, BURNING TWO OF OUR EMPLOYEES. ALL EMPLOYEES INVOLVED WHERE BOTH QUALIFIED TO PERFORM EACH TASK SUCH AS ELECTROFUSION AND SQUEEZE-OFF. ANOTHER NOTE TO ADD IS THAT THE NEW SERVICE LINE WAS PRESSURE TESTED PRIOR TO TAP.
2024-05-31 11:04 | NO | YES | NO | 20220069 | 38282 | 2022-11-02 15:29 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-10-03 13:23 | EASTERN | YES | 2022 | INTERSTATE 94 & PORTAGE ROAD | PORTAGE | KALAMAZOO | MI | 49002 | 42.2463 | -85.5587 | YES | [5 empty] | YES |  |  | 2022-10-03 16:47 | 1348944 | 1349071 | NATURAL GAS |  | 7578 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-10-03 13:23 | YES | OPERATOR | 2022-10-03 13:45 | 2022-10-03 13:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 2 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 31896 | 32591.4373770491934 | 62 | 63.35180327868855 | 0 | 0 |  | 8.95 | 67823 | 52073.1015965166908563134978229317851959 | 0 | 0 | 99781 | 52679.5113557305722284760522496371552975 | 84727.8907768445728063134978229317851959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 352 | 400 | 192.619(A)(2) | 1973-08-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2022092302752 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON OCTOBER 3, 2022, AT APPROXIMATELY 13:23 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR INTERSTATE HIGHWAY 94 (I-94) AND PORTAGE STREET, KALAMAZOO (KALAMAZOO COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 13:42 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR CUTTING IN A NEW ENTRANCE RAMP TO I-94 DAMAGED A NATURAL GAS PIPELINE, WHICH WAS LATER DETERMINED TO BE A 6-INCH STEEL HIGH PRESSURE PIPELINE. THE ROADWAY WAS ALREADY CLOSED TO TRAFFIC WHEN THE DAMAGED OCCURRED DUE TO THE ON-GOING CONSTRUCTION. POLICE AND FIRE DEPARTMENTS WERE ONSITE AND ENSURED NO CONSTRUCTION VEHICLES USED THE CONSTRUCTION ENTRANCES INTO THE AREA. AIR TRAFFIC INTO THE LOCAL AIRPORT WAS ALSO DIVERTED TO PREVENT THE POTENTIAL FOR INJURY. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE PIPELINE DAMAGE AND SUBSEQUENT GAS RELEASE. A DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 14:02 HOURS AND AN ISOLATION PLAN TO STOP GAS FROM BLOWING WAS DEVELOPED. TO ISOLATE, THE CREW UTILIZED AN EXISTING PRESSURE CONTROL FITTING TO THE NORTH OF THE DAMAGE LOCATION AND MULTIPLE VALVES WERE UTILIZED SOUTH OF THE DAMAGE LOCATION. GAS WAS CONTROLLED AT APPROXIMATELY 18:30 HOURS, THE DAMAGED SEGMENT WAS REMOVED AND REPLACED WITH 28-INCHES OF 6-INCH STEEL PIPELINE. REPAIRS WERE COMPLETED AND NORMAL OPERATIONS RESUMED ON OCTOBER 4, 2022, AT APPROXIMATELY 03:00 HOURS. NO LOSS OF SERVICE TO CUSTOMERS OCCURRED BECAUSE OF THE PIPELINE DAMAGE. FURTHER INVESTIGATION DETERMINED THE STAKING CONTRACTOR FAILED TO STAKE THE REQUESTED LOCATION AND PROVIDED AN INACCURATE POSITIVE RESPONSE CODE, CAUSING THE CONTRACTOR TO DAMAGE THE UNDERGROUND NATURAL GAS PIPELINE.
2024-05-31 11:04 | NO | NO | NO | 20220070 | 37834 | 2022-11-03 21:56 | SUPPLEMENTAL FINAL | 30839 | WALDEN, TOWN OF | PO BOX 489 513 HARRISON ST | WALDEN | CO | 80480 | 2022-08-31 13:00 | MOUNTAIN | YES | 2022 | 0.5 MILES EAST OF FAIR GROUNDS | WALDEN | JACKSON | CO | 80480 | 40.747 | -106.2604 | YES | [8 empty] | 2022-10-25 13:38 | 1350815 |  | NATURAL GAS |  | 6100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-09-02 05:30 | NO |  |  | 2022-09-02 09:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1970 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 2000 | 2043.60655737705 | 0 | 0 | 0 | 0 |  | 5.3514 | 32644 | 25063.3904208998548621190130624092888244 | 0 | 0 | 34644 | 19578.0725213543033091436865021770682148 | 27106.9969782769048621190130624092888244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 15 | 275 | 192.619(A)(2) | 1995-04-15 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM IS OPERATED BY THE GAS SUPPLIER (COLORADO INTERSTATE GAS). THEY DID NOT HAVE REASONABLE ALARMS SET FOR OUR SYSTEM AND NOTIFIED BY TELEPHONE US A WEEK AFTER THE LEAK LIKELY STARTED. SINCE THE EVENT, WE NOW RECEIVE REALISTIC VOLUME BASED ALARMS AS WELL AS DAILY VOLUME REPORTS FROM CIG. THE ALARM VALUES WILL LIKELY BE SET SEASONALLY GOING FORWARD. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  | 2022 |  |  |  |  | YES | COLD APPLIED TAPE |  | YES | [19 empty] | 2022-05-11 | NO | [182 empty] | YES | [44 empty] | JOEL SHUTE | OPERATIONS AND COMPLIANCE MANAGER | joel@pipeline.group | 7202272026 |  | GRAHAM CREWS | graham@waldengas.com | 9703818557 | JOEL SHUTE | OPERATIONS AND COMPLIANCE MANAGER | 7202272026 | joel@pipeline.group | ON AUGUST 31, 2022 THE WALDEN PIPELINE OPERATORS RECEIVED PHONE CALLS FROM THE CIG CONTROL CENTER, ABOUT CONCERNS FOR INCREASED GAS USAGE. ONLINE FLOW RECORDS SHOWED AN APPARENT 10X FLOW INCREASE AROUND AUGUST 23. CIG HAD CHECKED ITS DELIVERY METER AND FOUND NOTHING ABNORMAL. THE 50-MILE TRANSMISSION SYSTEM WAS SYSTEMATICALLY ISOLATED AND CHECKED BY SECTION, AND CIG NOTED AN ABRUPT DROP IN FLOW. THE LAST SECTION ISOLATED WAS THE HIGH-PRESSURE DISTRIBUTION SYSTEM IN COLORADO THAT FEEDS THE TOWN SYSTEMS IN COWDREY AND WALDEN.NEXT DAY WE PINPOINTED LOW PRESSURE ON THE 2-INCH SECTION THAT HELPS FEED WALDEN. THIS WAS THE ORIGINAL SUPPLY LINE TO WALDEN, BUILT CA 1958 OF COATED STEEL 2" PIPE. WE HAD FOUND AND FIXED A CORROSION PINHOLE LEAK ON THIS SEGMENT EARLIER IN JULY, THE ONLY LEAK FOUND IN 20+ YEARS ON ANY PIPELINE IN COLORADO. THIS 17,000 FT SEGMENT WAS LOOPED CA 1979 WITH A 3" COATED STEEL LINE, PARALLEL AND ABOUT 10 FT SOUTHEAST. THE 2" SECTION WAS ISOLATED AND QUICKLY PRESSURED DOWN. LATER, GAS WAS REINTRODUCED AND A LEAK SURVEY DONE IN THE AREA AROUND THE PREVIOUS LEAK. THE NEWER LEAK WAS DETECTED ABOUT 180 FT SW OF THE PREVIOUS REPAIR, RUNNING ALONG A SHALLOW SAGEBRUSH WASH. WITH THIS SEGMENT SHUT DOWN AND THE 3" LOOP CARRYING THE LOAD, WE EXCAVATED THE NEW LEAK AREA ON NOVEMBER 2, INTENDING A REPAIR. THE PIPE AND COATING LOOKED IDENTICAL TO THAT WITH THE NEARBY LEAK REPAIR, BUT WAS VERY SHALLOW. THE EXCAVATED MATERIAL WAS MOSTLY BLACK, SMELLY LEAK DIRT INDICATIVE OF A LONG-TERM GAS LEAK. THE EXCAVATOR STRIPPED OUT THE PIPE FOR 60 FT, AND WE INTRODUCED A SMALL AMOUNT OF GAS FROM THE NEARBY BLOCK VALVE. THE EXPOSED & CLEANED-OFF PIPELINE DIDN'T LEAK. BUT THE GAS DETECTOR PICKED UP GAS NEAR THE FRONT AND NORTH SIDE OF THE BACKHOE, WELL AWAY FROM THE EXPOSED 2" AND THE SIDE AWAY FROM THE 3" LOOP. AFTER FURTHER INVESTIGATION, DIGGING OUT MORE LEAK DIRT, WE EVENTUALLY FOUND A SECOND STRING OF 2" PIPE RUNNING PARALLEL TO THE EXPOSED LINE, ABOUT 7 FT NW AND 3.5 FT DEEPER. WE STRIPPED OUT A 10-FT SECTION OF THIS NEWLY-DISCOVERED PIPE. THE COATING WAS A COLD-APPLIED YELLOW TAPE WITH THICK BLACK MASTIC, LIKELY HAND-APPLIED WITH GOOD OVERLAPS AND NO WRINKLES. WE COULD FIND NO OBVIOUS DEFECTS OR HOLES, UNTIL GAS WAS INTRODUCED. IN LESS THAN 5 SECONDS, THE SHORT SECTION APPEARED TO LEAK IN AT LEAST 4 PLACES, INCLUDING A PINKIE-SIZE HOLE IN THE TAPE AND THE PIPE ON THE BOTTOM. ALTHOUGH THE TAPE LOOKED GOOD ON FIRST INSPECTION, THERE WERE SEVERAL DEEP MARKS AND DENTS, ALTHOUGH THE SOIL WAS ROCK-FREE, MOIST CLAY. THE DEEP DENTS MAY HAVE BEEN MADE DURING INSTALLATION, WHEN THE PIPE WAS LOWERED IN WITH LOG CHAINS INSTEAD OF SOFTER PIPE SLINGS. THIS 3RD LINE IS NOT SHOWN ON ANY MAPS OR DESCRIBED IN ANY DOCUMENTS CONVEYED FROM THE ORIGINAL OWNER ROCKY MOUNTAIN NATURAL GAS TO THE TOWN IN 1995. WITH 5 CORROSION LEAKS (DESPITE GOOD CP READINGS) IN 200 FT IN A FEW MONTHS; AND WITH LITTLE HYDRAULIC VALUE, WE DECIDED TO PERMANENTLY ABANDON THE 2-INCH SEGMENT. WE CUT OUT AN 8-FT SECTION OF THE LEAKING PIPE, AND WELD-CAPPED BOTH ENDS OF THE 17,000 FT SEGMENT, WITH DOCUMENTATION THAT THIS SECTION CAN'T BE USED AGAIN. THIS LEAK WAS ABOUT 1.2 MILES FROM THE EDGE OF WALDEN. THE NEAREST PUBLIC ROAD IS THE COUNTY RODEO & FAIRGROUNDS ABOUT 1/2 MILE AWAY, AND 0.9 MILE TO THE NEAREST RESIDENCE. WE BELIEVE THIS LEAK HAS PERSISTED FOR DECADES. IT WAS NOT REPORTED BY THE PUBLIC, SINCE IT IS VERY REMOTE AND THE PREVAILING WIND GENERALLY BLOWS FROM THE SOUTHWEST, AWAY FROM ANY RESIDENCES OR ROADS. THE UTILITY HAD LEAK-SURVEYED THE 2 KNOWN PARALLEL LINES AS REQUIRED BY DOT PART 192. THE VEHICLE-MOUNTED RIG WAS ALWAYS DRIVEN BETWEEN THE 2 PIPELINES THAT ARE ONLY 8 FT APART. THE UNKNOWN LINE WAS ABOUT 12 FT OUTSIDE THE LEAK SURVEY PATH. WE BELIEVE OLD UNDETECTED PINHOLE LEAKS BLEW OUT WITH THE RE-PRESSURIZATION AFTER THE PREVIOUS REPAIR. NO INJURIES OR DEATHS RESULTED FROM THIS LEAK. THE ONLY DAMAGE WAS THE VALUE OF LOST GAS.
2024-05-31 11:04 | NO | YES | NO | 20220071 | 39476 | 2022-11-07 12:22 | SUPPLEMENTAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-10-08 21:15 | PACIFIC | YES | 2022 | 2793 RIVER PLAZA DRIVE | SACRAMENTO | SACRAMENTO | CA | 95833 | 38.6091 | -121.5247 | [5 empty] | YES |  |  |  | 2022-10-09 00:36 | 1349399 | 1349521 | NATURAL GAS |  | 39.9 | 0.006 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-10-08 16:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 39.9 | YES | 24 | 2022-10-08 15:48 |  |  |  | 2022-10-08 16:00 | 2022-10-08 21:15 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE TEE CAP | 1987 | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 118868 | 121459.7121311475897 | 219513 | 224299.103114754188325 | 0 | 0 | 0 | 0 |  | 7.3 | 291 | 223.423802612481857764876632801161103048 | 0 | 0 | 338672 | 146253.1178356611466236429608127721335269 | 345982.239048514259882764876632801161103 | 10 | 0 | 8 | 0 | 0 | 8 | 0 | 54 | 54 | 60 | 192.619(A)(2) | 1987-08-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA NOT IN PLACE THEREFORE GAS CONTROL INVOLVEMENT IS NOT A FACTOR. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SADDLE, HEAT FUSION |  | 1987 | 1" | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [6 empty] | YES | [9 empty] | YES |  |  |  | OTHER | CRACK ON PLASTIC TEE CAP | NO | [86 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510-298-7063 |  | SUSIE RICHMOND | gsr8@pge.com | 925-786-0267 | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | 06/01 UPDATE - THE REVISION TO THIS REPORT PROVIDES UPDATED COSTS ASSOCIATED WITH THE EVENT. PG&E WILL CONTINUE TO DOCUMENT COSTS ASSOCIATED WITH THIS INCIDENT AND WILL PROVIDE A FINAL REPORT ONCE ALL INFORMATION IS CONFIRMED. ON SATURDAY, OCTOBER 8, 2022, AT APPROXIMATELY 15:48 HOURS, PG&E WAS NOTIFIED OF AN EXPLOSION AT 2793 RIVER PLAZA DR., SACRAMENTO, CA. A PG&E GAS SERVICE REPRESENTATIVE RESPONDED TO SHUT OFF THE GAS TO THE METER. DURING A SUBSEQUENT LEAK SURVEY, A LEAK AT A SERVICE TEE NEAR THE BUILDING WAS LOCATED. THE FIRE DEPARTMENT, POLICE, AND MEDIA WERE REPORTED ON SITE. NO FATALITIES OR INJURIES WERE REPORTED. THIS INCIDENT WAS REPORTED ONCE ESTIMATED DAMAGE WAS CONFIRMED TO BE AT LEAST $129,300K. THIS INCIDENT HAS BEEN REPORTED TO CPUC AND DOT (1349399/1349521). THE CRACK WAS DISCOVERED WHEN THE TEE WAS EXPOSED BY EXCAVATION DURING THE LEAK INVESTIGATION FOLLOWING THE INCIDENT. PG&E WILL CONTINUE ITS INVESTIGATION AND WILL PROVIDE A SUPPLEMENTAL/AMENDED REPORT ONCE ALL INFORMATION IS CONFIRMED.
2024-05-31 11:04 | NO | YES | NO | 20220072 | 37520 | 2022-11-08 08:36 | SUPPLEMENTAL FINAL | 2188 | CENTRAL FLORIDA GAS CORP | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2022-10-11 15:35 | EASTERN | NO | 2022 | ADAMS ST AT BRIDGERS AVE | AUBURNDALE | POLK | FL | 33823 | 28.0627 | -81.7804 | [5 empty] | YES |  |  |  | 2022-11-01 16:25 | 1351443 | 1351654 | NATURAL GAS |  | 2187.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-10-11 15:35 |  |  |  | 2022-10-11 16:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2015 | 2015 |  |  |  |  | 6 | D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 200000 | 204360.655737705 | 47000 | 48024.754098360675 | 1500 | 1532.7049180327875 | 0 | 0 |  | 5 | 10938 | 8397.970972423802612481857764876632801161 | 0 | 0 | 259438 | 113553.4425634681223004354136429608127721 | 262316.0857265222651124818577648766328012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 50 | 60 | 192.619(A)(2) | 2015-10-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 263201452 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [169 empty] | YES | MICHAEL MCCARTY |  | mmccarty@fpuc.com | 863 224-0417 |  | GEORGE FREEMAN | gfreeman@fpuc.com | 863 209-5030 | MICHAEL MCCARTY |  | 863 224-0417 | mmccarty@fpuc.com | ON 10/11/22 DRILLING SMART, DIRECTIONAL BORE CONTRACTOR, HIT A 6" PE GAS MAIN OPERATED BY CENTRAL FLORIDA GAS UNDER THE PAVING AT ADAMS ST AND BRIDGERS AVE IN AUBURNDALE, FLORIDA. THE 6" PE IS IN THE AREA WHERE THERE IS AN OLD ABANDONED 4" BARE STEEL GAS MAIN. THE CONTRACT LOCATOR FOR CENTRAL FLORIDA GAS WAS OFF ON HIS MARKINGS. DRILLING SMART EXPOSED THE 4" BARE STEEL AND ASSUMED IT WAS THE ACTIVE GAS MAIN AND BORED DEEPER THAN THAT LINE AND HIT THE ACTIVE 6" PE GAS MAIN. CENTRAL FLORIDA GAS RESPONDED AND USED PIPE SQUEEZERS ON BOTH SIDES OF THE INTERSECTION TO STOP THE FLOW OF GAS IN THIS DUAL FED GAS MAIN AND DID NOT LOSE SERVICE TO ANY CUSTOMERS. THE POINT OF DAMAGE WAS UNDER THE ROADWAY PAVING AND THE ACTUAL DAMAGE COULD NOT BE SEEN. ON 10/12/22, A NEW PIECE OF 6" PE WAS INSTALLED UNDER THE INTERSECTION VIA DIRECTIONAL BORE, TESTED AND TIED IN. GAS WAS RESTORED TO THAT MAIN ON 10/14/22. ON 11/1/22, THE CITY OF AUBURNDALE PRESENTED CENTRAL FLORIDA GAS WITH COSTS TO RESTORE THE ROAD BASE AND PAVING AT THAT INTERSECTION, PUSHING THE DAMAGE COST ABOVE THE PHMSA REPORTING THRESHOLD OF $122,000. A NOTICE WAS MADE TO THE NATIONAL REPORTING CENTER VIA TELEPHONE ON 11/1/22 AND A 48 HOUR FOLLOW UP ON 11/3/22. 12/28/2022 SUPPLEMENT CORRECTION MADE TO PART A (19) - INCORRECT NRC REPORT NUMBER ENTERED INITIALLY WITH A NUMBER LEFT OUT. CORRECT NRC REPORT NUMBER OF 1351443 ENTERED. PART J - EXCAVATION DAMAGE (EXCAVATION DAMAGE BY THIRD PARTY) REMOVED AS NOT NECESSARY SINCE LISTED IN G3. CHANGED CONTRIBUTING FACTOR TO INCORRECT OPERATION (FAILURE TO FOLLOW PROCEDURES) DUE TO CONTRACT LOCATOR BEING OFF ON MARKS AND NOT LISTING THE TYPE AND SIZE OF GAS MAIN IN THE POSITIVE RESPONSE FOR THE LOCATE TICKET. THE LOCATOR WAS OFF ON THE LOCATE MARKS BY A FEW FEET. THE EXCAVATOR SPOTTED A PIPE SEVERAL FEET AWAY IN A GRASSY AREA AND ASSUMED IT WAS THE GAS MAIN AND AT A CERTAIN DEPTH. THEY BORED THE ROAD AT A DEEPER DEPTH AND HIT THE LIVE PE GAS MAIN. THE PIPE THEY DUG UP AND SPOTTED FOR DEPTH WAS AN OLD RETIRED 4" BARE STEEL GAS MAIN AND NOT THE LIVE 6" PE GAS MAIN. THE CONTRACTOR LOCATOR TECHNICIANS WERE BROUGHT IN AND INSTRUCTED AGAIN TO LIST THE SIZE AND TYPE OF PIPE ON THE POSITIVE RESPONSE TO MARKED LOCATE TICKETS, PER PROCEDURES, TO ENSURE EXCAVATORS ARE SURE WHICH PIPES THEY ARE SPOTTING. NO OTHER DAMAGE INFORMATION OR COSTS REQUIRE UPDATING.
2024-05-31 11:04 | NO | YES | NO | 20220073 | 38489 | 2022-11-16 17:36 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2022-10-17 11:06 | EASTERN | YES | 2022 | 1372 BARRON LAKE ROAD | NILES | CASS COUNTY | MI | 49120 | 41.8533 | -86.177 | [5 empty] | YES |  | YES | RETIRED SERVICE LINE. | 2022-10-17 11:06 | 1350127 | 1350718 | NATURAL GAS |  | 7.04 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-10-17 07:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 7.04 | NO | 1 | 2022-10-17 07:57 |  |  |  | 2022-10-17 08:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | 1997 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | GAS METER | [9 empty] | OTHER | [8 empty] | CAR IMPACT DISLODGED METER FROM METER BAR AND PIPING. | CLASS 3 LOCATION | 200000 | 204360.655737705 | 990 | 1011.58524590163975 | 2240 | 2288.839344262296 | 0 | 0 |  | 8.94 | 63 | 48.37010159651669085631349782293178519594 | 0 | 0 | 203293 | 87774.8396928311737194484760522496371553 | 207709.4504294654524408563134978229317852 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1962-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES |  |  | NO | UNKNOWN | SMALL TRUCK | ROADWAY | 47 | NO | [142 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | JOHN O'BRYANT | john.obryant@semcoenergy.com | 269-506-3222 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | 8106503774 | phil.lenn@semcoenergy.com | ON 17 OCT 2022 AT APPROXIMATELY 07:57, SEMCO WAS NOTIFIED BY THE CASS CO CENTRAL DISPATCH THAT THERE WAS A STRUCTURE FIRE AT THE REFERENCED ADDRESS. UPON ARRIVING AT 8:15 AM, THE SEMCO TECHNICIAN CHECKED WITH THE HOWARD TWP. FIRE CHIEF WHOM INFORMED HIM THAT THE VEHICLE HAD STRUCK ANOTHER VEHICLE IN THE ROAD, VEERED OFF THE ROAD, TRAVELED THRU THE YARD, STRIKING THE GAS METER SET WHICH THEN IGNITED, CAUSING THE STRUCTURE FIRE. THE GAS WAS SECURED AT 8:33 AM AND THE FIRE DEPARTMENT DISTINGUISHED THE FIRE.
2024-05-31 11:04 | NO | NO | NO | 20220075 | 37413 | 2022-12-02 15:08 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-11-04 15:29 | EASTERN | YES | 2022 | N. ELM AVENUE & ROSEHILL ROAD | JACKSON | JACKSON | MI | 49201 | 42.2766 | -84.3842 | [5 empty] | YES | YES |  |  | 2022-11-04 22:02 | 1351782 | 1351886 | NATURAL GAS |  | 3444 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-11-04 15:29 | YES | OPERATOR | 2022-11-04 15:55 | 2022-11-04 15:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 2 | 9.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 36708 | 37508.3547540983757 | 73 | 74.591639344262325 | 0 | 0 |  | 5.77 | 19872 | 15257.3120464441219158200290275761973875 | 0 | 0 | 56653 | 27271.6524427181292303193033381712626996 | 52840.2584398867599408200290275761973875 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 53 | 53 | 60 | 192.619(A)(2) | 2022-05-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 2022083000497 |  |  | CONTRACT LOCATOR | NO | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON NOVEMBER 4, 2022, AT APPROXIMATELY 15:29 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE AT THE INTERSECTION OF N. ELM AVENUE AND ROSEHILL ROAD, JACKSON (JACKSON COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 15:55 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR PERFORMING ROADWAY EXCAVATION WORK DAMAGED A NATURAL GAS PIPELINE, WHICH WAS LATER DETERMINED TO BE A 6-INCH STEEL MEDIUM PRESSURE PIPELINE. POLICE AND FIRE DEPARTMENTS WERE ONSITE AND ASSISTED THE CONTRACTOR WITH ROAD CLOSURE TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. A DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 16:15 HOURS AND DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. THE DAMAGED SEGMENT WAS ISOLATED BY INSTALLING A PRESSURE CONTROL FITTING AT A REMOTE LOCATION EAST OF THE DAMAGE AND SQUEEZING THE PIPELINE AT A LOCATION WEST OF THE DAMAGE. THE BLOWING GAS WAS CONTAINED AT APPROXIMATELY 04:30 HOURS (NOVEMBER 5, 2022) AND A PERMANENT REPAIR WAS COMPLETED BY WELDING AN ENCAPSULATED FITTING AROUND THE DAMAGED SEGMENT. REPAIRS WERE COMPLETED AND NORMAL OPERATIONS RESUMED ON NOVEMBER 5, 2022, AT APPROXIMATELY 10:30 HOURS. SERVICE RESTORATION FOR ALL IMPACTED CUSTOMERS BEGAN AFTER THE PIPELINE REPAIR.
2024-05-31 11:04 | NO | YES | NO | 20220077 | 38088 | 2022-12-15 12:18 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-11-16 11:45 | PACIFIC | NO | 2022 | EAST SIDE OF GRANT ST, ACROSS THE STREET FROM RESIDENCE 2707 GRANT ST | CONCORD | CONTRA COSTA | CA | 94520 | 37.9878 | -122.0379 | [5 empty] | YES |  |  |  | 2022-11-16 12:23 | 1352705 | 1352897 | NATURAL GAS |  | 2076 | 2.37 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-16 10:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2076 | NO | 1 | 2022-11-16 10:30 |  |  |  | 2022-11-16 10:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 22 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1961 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 6 | [7 empty] | CLASS 3 LOCATION | 350750 | 358397.50000000014375 | 48695 | 49756.710655737724875 | 2533 | 2588.227704918033825 | 0 | 0 |  | 6.3 | 13079 | 10041.7866473149492017416545718432510885 | 15 | 11.51669085631349782293178519593613933237 | 415072 | 181049.1892281520561904499274310595065312 | 420795.7416988271651495645863570391872278 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 54 | 60 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | YES | X229201521 | 811 |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com |  |  | SUSIE RICHMOND | gas ops compliance and risk manager |  | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | ON NOVEMBER 16, 2022, AT APPROXIMATE 11:45 HOURS PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED THAT A DIG-IN LOCATED AT THE EAST SIDE OF GRANT STREET, ACROSS THE STREET FROM THE RESIDENCE OF 2707 GRANT STREET IN CONCORD, CA REACHED DOT REPORTABLE INCIDENT CRITERIA. THIRD-PARTY CONSTRUCTION EQUIPMENT STRUCK A 4" STEEL DISTRIBUTION MAIN RESULTING IN MULTIPLE PUNCTURES RESULTING IN A RELEASE OF GAS WITH SUBSEQUENT IGNITION. PG&E PERSONNEL RESPONDED AND STOPPED GAS FLOW APPROXIMATELY AT 12:27 HOURS. THERE WERE NO FATALITIES OR INJURIES. MEDIA, FIRE AND POLICE WERE REPORTED ON SITE. THIS INCIDENT WAS REPORTED TO THE DOT #1352705/1352897 AND CPUC 221116-15335 DUE TO MEDIA COVERAGE AND ONCE IT WAS CONFIRMED THAT THE INCIDENT RESULTED IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $129,300.
2024-05-31 11:04 | NO | YES | YES | 20220078 | 38138 | 2022-12-20 17:10 | SUPPLEMENTAL FINAL | 18704 | SULLIVAN GAS DEPT, CITY OF | 304 S HAMILTON ST | SULLIVAN | IL | 61951 | 2022-11-10 13:00 | CENTRAL | YES | 2022 | 1209 S HAMILTON ST. | SULLIVAN | MOULTRIE | IL | 61951 | 39.5875 | -88.6094 |  |  | YES | [6 empty] | 2022-11-14 08:19 | 1352505 | 1352759 | NATURAL GAS |  | 1.04 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2022-11-10 13:00 | YES | OPERATOR | 2022-11-10 13:00 | 2022-11-10 13:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 2 | GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 200 | 204.360655737705 | 35000 | 35763.114754098375 | 5000 | 5109.016393442625 | CITY EMPLOYEE AND CONSULTANTS TIME AND LABOR. | 3.32 | 3 | 2.30333817126269956458635703918722786647 | 0 | 0 | 40203 | 17356.9166052011772104499274310595065312 | 41078.7951414499676995645863570391872279 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 37 | 40 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 60 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ANDREW J WOODWORTH | CITY OF SULLIVAN GAS DEPARTMENT FOREMAN | gasdept@sullivanil.us | 2174339303 |  |  |  |  | ANDREW J WOODWORTH |  | 2174339303 | gasdept@sullivanil.us | ON NOVEMBER 10TH 2022, I (FOREMAN) AND THE REST OF MY CREW WERE INSTALLING A SECTION OF NEW GAS MAIN INSIDE THE CITY LIMITS OF SULLIVAN IL. AFTER I COMPLETED THE WELDING AND SUCCESSFUL PRESSURE TESTING OF TWO BOLT ON VALVE FLANGE WELDS AND ONE WELD SECURING THE 2 INCH TEE TO THE PREEXISTING 37 PSI, 2 INCH GAS MAIN, ALL FOUR OF US PROCEEDED TO COMMENCE DRILLING THE MAIN TO INTRODUCE GAS TO THE NEW MAIN BY UTILIZING ONE OF OUR MUELLER E-4 MODEL DRILLING MACHINES. UPON SUCCESSFUL COMPLETION OF THE DRILLING PROCESS TECHNICIAN 1 RAISED THE SHELL CUTTER INTO THE DRILLING MACHINE CHAMBER AND THE GATE VALVE WAS CLOSED TO STOP OFF GAS FLOW FROM THE TOP OF THE TEE. THE DRILLING MACHINE WAS DISASSEMBLED FROM THE GATE VALVE AND THE SHELL CUTTER DISASSEMBLED AND THE COMPLETION PLUG INSTALLED. ONCE TECHNICIAN 1 REASSEMBLED THE MACHINE IT WAS REATTACHED TO THE TOP OF THE GATE VALVE AND THE VALVE WAS OPENED ALLOWING THE COMPLETION PLUG TO BE LOWERED INTO THE TOP OF THE TEE AND THREADED INTO IT. ONCE THE PLUG WAS THREADED INTO THE TEE AND TIGHT THE SHAFT WAS REMOVED FROM THE COMPLETION PLUG AND THE MACHINE WAS REMOVED AGAIN FROM THE GATE VALVE. THE GATE VALVE WAS THEN REMOVED AND THE COMPLETION PLUG WRENCH WAS PUT INTO THE TOP OF THE COMPLETION PLUG BY TECHNICIAN 1. TECHNICIAN 1 PERFORMED ALL THE ASSEMBLY AND DISASSEMBLY OF THE MACHINE. TECHNICIAN 1 THEN TURNED THE PLUG TIGHTENING IT INTO THE TEE A 1/4 - 1/2 TURN AND THEN HANDED THE WRENCH TO TECHNICIAN 3 AND TOLD HIM TO FINISH TIGHTENING THE PLUG. TECHNICIAN 3 THEN FITTED THE WRENCH INTO THE TOP OF THE COMPLETION PLUG. HE IS RIGHT HANDED SO HE PUT HIS LEFT HAND ON TOP OF THE WRENCH TO SECURE IT AND HIS RIGHT HAND ON THE HANDLE TO TURN IT. AS SOON AS HE STARTED TO TURN THE PLUG IT BLEW OUT THE TOP. AT THE TIME THAT IT BLEW OUT I (FOREMAN) WAS SEATED ON THE EAST EDGE OF THE BELL HOLE, TECHNICIAN 2 WAS SEATED ON THE SOUTH EDGE, TECHNICIAN 3 WAS STANDING IN THE SOUTH WEST CORNER OF THE PREEXISTING AND NEW MAINS AND TECHNICIAN 1 WAS STANDING IN THE NORTH WEST CORNER OF THE PREEXISTING AND NEW MAINS. I ROLLED AWAY FROM THE EXCAVATION. I LOOKED TO MY LEFT AND SAW THAT TECHNICIAN 2 WAS CLEAR OF THE HOLE. I LOOKED RIGHT AND SAW TECHNICIAN 3 MOVING WEST IN THE DITCH AWAY FROM IT. I LOOKED RIGHT AND SAW TECHNICIAN 1 LOOKING AROUND ALL AROUND HIM I YELLED ARE YOU OK AND HE GAVE ME A THUMBS UP AND CONTINUED LOOKING AROUND HIM. I LOOKED AT TECHNICIAN 3 AND SAW HIS FACE WAS OBVIOUS SHOCK. I SAW HIM HOLDING HIS LEFT ARM AND THEN SAW HIS ARM STARTING TO BLEED. I THEN RAN AROUND THE NORTH SIDE OF THE HOLE AND GRABBED TECHNICIAN 3 AND PULLED HIM OUT OF THE DITCH AND TOOK HIM TO GET A FIRST AID KIT. AT THIS TIME I SAW HOW BAD HIS ARM WAS BLEEDING SO I KEYED UP ON THE CITY RADIO AND STATED SULLIVAN EMS SULLIVAN EMS YOU ARE NEEDED NOW AT THE H&R BLOCK BUILDING ON SOUTH HAMILTON STREET INJURED CITY EMPLOYEE WITH SHRAPNEL WOUNDS TO HIS LEFT FOREARM AND BICEP WITH SEVERE BLEEDING. I REPEATED THIS MESSAGE TWICE ON THE RADIO. I THEN TURNED TO TECHNICIAN 3 AND BEGAN MEDICAL TRIAGE. HE SAID IT FEELS LIKE SOMETHING IS MOVING UP MY ARM! I THEN TOOK OFF MY LEATHER BELT AND TOLD HIM IM GONNA TIE OFF YOUR ARM! I USED MY BELT JUST BELOW HIS LEFT ARMPIT TO APPLY A TOURNIQUET. I WRAPPED IT TIGHT AND GAVE HIM THE LOOSE END AND TOLD HIM TO HOLD IT AND NOT LET GO UNTIL THE EMTS TOLD HIM TO. MOMENTS LATER EMTS ARRIVED AND TOOK TECHNICIAN 3 TO ST MARYS HOSPITAL BY AMBULANCE IN DECATUR IL. I TURNED BACK TO TECHNICIANS 1 AND 2 AND THEY HAD ALREADY PUT THE GATE VALVE BACK ON AND SHUT DOWN THE GAS. TECHNICIAN 1 AND I PUT A NEW COMPLETION PLUG IN THE TEE AND THEN SECURED THE AREA AND WENT TO DO DRUG SCREENINGS PER HUMAN RESOURCES.
2024-05-31 11:04 | NO | YES | NO | 20220079 | 37670 | 2022-12-21 13:21 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2022-11-30 17:00 | PACIFIC | NO | 2022 | LA CIENEGA STREET AND PYLE AVE | LAS VEGAS | CLARK | NV | 89183 | 36.0055 | -115.1614 | [5 empty] | YES |  |  |  | 2022-11-30 17:44 | 1353841 | 1354008 | NATURAL GAS |  | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 6 | 2022-10-31 19:52 | YES | OPERATOR | 2022-10-31 23:01 | 2022-10-31 18:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1999 | 1998 |  |  |  |  | 2 | ASTM D-2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 180432 | 184366.0091803279428 | 12285 | 12552.853278688529625 | 0 | 0 |  | 5.4087 | 2704 | 2076.075471698113207547169811320754716981 | 0 | 0 | 195421 | 84750.2246628518719888679245283018867925 | 198994.937930714585632547169811320754717 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 48 | 55 | 60 | 192.619(A)(2) | 1999-01-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | MATERIAL DEGRADATION | NO | [73 empty] | YES | [12 empty] | MICHAEL ROSS | SUPERVISOR OF ENGINEERING | michael.ross@swgas.com | 7023652361 |  |  |  |  | ANTHONY HILLS | DIRECTOR OF GAS OPERATIONS | 7023652049 | anthony.hills@swgas.com | AT 17:35 ON OCTOBER 31, 2022, SOUTHWEST GAS RECEIVED A CALL ABOUT AN ODOR/HISSING ON A DIRT LOT NEAR THE INTERSECTION OF LA CIENEGA STREET AND PYLE AVENUE IN LAS VEGAS, NEVADA. CREWS ARRIVED ONSITE AT 18:23 AND BEGAN INVESTIGATION. AT 19:52, SOUTHWEST GAS IDENTIFIED A LEAK ON ITS FACILITIES AND MADE THE AREA SECURE. THE LEAK WAS ISOLATED AND GAS SUPPLY WAS SHUT OFF TO THE AFFECTED PIPE SEGMENT BY 21:24 ON OCTOBER 31, 2022. THIS SEGMENT OF THE MAIN WILL NOT BE RETURNED TO SERVICE. SOUTHWEST GAS EVACUATED A TOTAL OF SIX PERSONS FROM THREE NEARBY HOMES. AFTER GAS WAS SHUT OFF, CREWS BEGAN AERATING THE SURROUNDING SOIL TO REMOVE RESIDUAL GAS IN THE GROUND. ALTHOUGH RESIDUAL GAS READS WERE DROPPING, SOUTHWEST GAS REMAINED ONSITE CONTINUOUSLY MONITORING THE RESIDUAL READS AND AERATING THE SOILS. ON NOVEMBER 30, 2022 SOUTHWEST GAS DETERMINED THAT THE ACCUMULATED EMERGENCY RESPONSE COSTS EXCEEDED $129,300. THE INCIDENT COSTS WERE MOSTLY ATTRIBUTED TO EMPLOYEE LABOR UTILIZED TO CONTINUOUSLY AERATE AND REMEDIATE THE RESIDUAL GAS IN THE SOIL. SOUTHWEST DISCONTINUED ITS EMERGENCY RESPONSE AND DECOMMISSIONED THE INCIDENT COMMAND STRUCTURE ON DECEMBER 8, 2022 AFTER THE RESIDUAL GAS READS WERE REMEDIATED TO SAFE NON-HAZARDOUS CONDITIONS. LABORATORY ANALYSIS COMPLETED IN JANUARY 2023 CONCLUDED: FRACTOGRAPHIC AND ANALYTICAL EXAMINATION INDICATED THAT THE THROUGHWALL AXIAL FRACTURE RESPONSIBLE FOR THE LEAK PATH OCCURRED DUE TO INTERNAL THERMAL-OXIDATIVE DEGRADATION. THE FRACTURE PROGRESSED THROUGH THE WALL OF THE PIPE FROM THE INSIDE DIAMETER TO THE OUTSIDE DIAMETER BY WAY OF HOOP STRESS AND BRITTLE FRACTURE DUE TO DEGRADATION AND LOW SLOW CRACK GROWTH RESISTANCE OF THE PIPE MATERIAL. THIS SUPPLEMENTAL REPORT UPDATES THE CAUSE OF THE LEAK IN PART G BASED ON THE LABORATORY ANALYSIS TO BE A CRACK CAUSED BY DEGRADATION. IT ALSO UPDATES PART J AND THE COSTS ASSOCIATED WITH THE INCIDENT IN PART D.
2024-05-31 11:04 | NO | NO | NO | 20220080 | 37509 | 2022-12-22 13:57 | ORIGINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2022-11-24 18:02 | MOUNTAIN | NO | 2022 | 1621 SAN JUAN CIRCLE | EVANS | WELD | CO | 80620 | 40.3772 | -104.7056 |  |  |  | YES | [5 empty] | 2022-11-24 18:45 | 1353337 |  | NATURAL GAS |  | 5.61 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-24 18:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4.98 | NO | 4 | 2022-11-24 18:02 |  |  |  | 2022-11-24 18:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1995 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | STEEL NIPPLE | [9 empty] | OTHER | [8 empty] | VEHICLE HIT | CLASS 3 LOCATION | 90000 | 91962.29508196725 | 2100 | 2145.7868852459025 | 1400 | 1430.524590163935 | 0 | 0 |  | 10.97 | 62 | 47.60232220609579100145137880986937590711 | 0 | 0 | 93562 | 40401.4868900045360159651669085631349782 | 95586.2088795831832910014513788098693759 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 18 | 18 | 20 | 192.619(A)(2) | 1995-05-25 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [142 empty] | VONNA M SEEBER | COMPLIANCE | vonna.seeber@atmosenergy.com | 8163944940 |  | KURTIS RUTZ | kurtis.rutz@atmosenergy.com | 9705390057 | DOUGLAS L SHATAS | MANAGER COMPLIANCE | 8168630951 | doug.shatas@atmosenergy.com | DRIVER LOST CONTROL OF VEHICLE ON ROADWAY BEHIND 1621 SAN JUAN CIRCLE IN EVANS, COLORADO. VEHICLE WENT OFF THE ROAD THROUGH A PRIVATE FENCE AND HIT AN ATMOS GAS METER AND A HOUSE. THE HOUSE, THE METER, AND THE VEHICLE CAUGHT FIRE. THE DRIVER FLED THE SCENE. THE EVANS FIRE DEPARTMENT RESPONDED, PULLED THE VEHICLE AWAY FROM THE HOUSE, PUT OUT THE FIRE, AND SHUT OFF THE GAS RISER VALVE TO STOP THE RELEASE OF GAS. THREE HOMES AND FOUR PEOPLE WERE EVACUATED DURING THE INITIAL INVESTIGATION. ATMOS DETERMINED THAT THERE WAS NO DAMAGE TO UNDERGROUND PIPING.
2024-05-31 11:04 | NO | YES | YES | 20220081 | 38655 | 2022-12-22 16:15 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2022-11-22 14:29 | EASTERN | NO | 2022 | 1121 BAYARD ST | BALTIMORE | BALTIMORE CITY | MD | 21223 | 39.2799 | -76.6371 | [6 empty] | YES |  |  | 2022-11-22 16:39 | 1353220 |  | NATURAL GAS |  | 5.6 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2022-11-22 14:29 | OPERATOR/CONTRACTOR |  | 5.6 | YES | 0 | 2022-11-22 14:29 |  |  |  | 2022-11-22 14:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1904 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 600000 | 613081.967213115 | 0 | 0 | 20000 | 20436.0655737705 | 0 | 0 |  | 0.45 | 3 | 2.30333817126269956458635703918722786647 | 0 | 0 | 620003 | 267668.9329986438952104499274310595065312 | 633520.3361250567626995645863570391872279 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0.25 | 0.25 | 0.36 | 192.623 | 1904-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | THE FRACTURE IN THE CAST IRON GAS MAIN AT THIS LOCATION LIKELY OCCURRED WHEN THE LOAD EXCEEDED THE FRACTURE STRENGTH OF THE PIPE. | NO | [218 empty] | JEFFREY WEATHERHOLTZ | MANAGER GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 4105981601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 3025933732 | robert.rex@delmarva.com | ON NOVEMBER 22, 2022, A NATURAL GAS EXPLOSION OCCURRED AT 1121 BAYARD STREET IN BALTIMORE CITY, MARYLAND. IT WAS DETERMINED AFTER THE INCIDENT THAT A 4" CAST IRON LOW-PRESSURE GAS MAIN EXPERIENCED A FULL CIRCUMFERENTIAL BREAK WHICH ALLOWED NATURAL GAS TO MIGRATE UNDERGROUND. THE FRACTURE IN THE CAST IRON GAS MAIN AT THIS LOCATION LIKELY OCCURRED WHEN THE LOAD EXCEEDED THE FRACTURE STRENGTH OF THE PIPE. THE GAS ENTERED THE RESIDENCE LOCATED AT 1121 BAYARD STREET. THE GAS THAT ENTERED THIS PROPERTY REACHED AN EXPLOSIVE LIMIT AND WAS IGNITED BY AN UNKNOWN SOURCE.
2024-05-31 11:04 | NO | YES | NO | 20230001 | 37527 | 2023-01-03 13:43 | ORIGINAL FINAL | 12642 | SPIRE GULF INC. | 2828 DAUPHIN STREET | MOBILE | AL | 36606 | 2022-11-16 09:06 | CENTRAL | YES | 2022 | 1363 CREOLA AXIS LOOP RD | CREOLA | MOBILE COUNTY | AL | 36505 | 30.9317 | -88.0075 | [5 empty] | YES |  |  |  | 2022-11-16 10:12 | 1352681 | 1352863 | NATURAL GAS |  | 23 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-11-16 09:06 | ALLOWED TO BURN OUT |  | 23 | NO | 0 | 2022-11-16 09:06 | YES | OPERATOR | 2022-11-16 09:26 | 2022-11-16 09:26 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2022 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | OTHER | [8 empty] | LINE DAMAGED BY TRACKHOE TRACK. | CLASS 2 LOCATION | 0 | 0 | 10000 | 10218.03278688525 | 500 | 510.9016393442625 | 125000 | 127725.409836065625 | TRACKHOE DAMAGED BY FIRE | 6 | 138 | 105.953555878084179970972423802612481858 | 0 | 0 | 135638 | 58577.3523638440346806966618287373004354 | 138560.2978181732216799709724238026124819 | 1 | 0 | 62 | 0 | 0 | 62 | 1 | 40 | 40 | 60 | 192.619(A)(2) | 2022-04-11 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED TO THE SCADA AND MADE THE APPROPRIATE NOTIFICATIONS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE TRACK RAILS OF A TRACKHOE DUG INTO SOFT GROUND AND DAMAGED PIPE WHILE MOBILIZING FROM A JOB SITE. | [154 empty] | JUSTIN MONROE | MANAGER PIPELINE SAFETY DISTRIBUTION | justin.monroe@spireenergy.com | 205-572-2928 |  | JUSTIN MONROE | justin.monroe@spireenergy.com | 205-572-2928 | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON NOVEMBER 16, 2022 AT 9:06 AM, A THIRD-PARTY CONTRACTOR DAMAGED A 2-INCH MEDIUM PRESSURE (60 PSIG MAOP) PLASTIC MAIN LOCATED AT 1363 CREOLA AXIS LOOP, CREOLA AL. THE CONTRACTOR WAS MOVING A TRACKHOE IN A SOFT AREA OF DIRT AND SUNK THE TRACKS INTO THE UNDERGROUND PIPELINE, CAUSING A RUPTURE. A FIRE IGNITED AND DAMAGED THE TRACKHOE. THIS REPORT WAS SUBMITTED BY PORTAL ON DECEMBER 16, 2022 BUT HAD TO BE RESUBMITTED DUE TO TECHNICAL ISSUES IN THE PORTAL.
2024-05-31 11:04 | NO | YES | NO | 20230002 | 37992 | 2023-01-12 16:41 | SUPPLEMENTAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2022-12-13 09:30 | EASTERN | NO | 2022 | 3204 CREST ROAD | HARRISBURG | DAUPHIN | PA | 17109 | 40.2923 | -76.848 |  | YES | [7 empty] | 2022-12-13 10:39 | 1354879 | 1355040 | NATURAL GAS |  | 42.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-12-13 09:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 42.1 | YES | 11 | 2022-12-13 09:07 |  |  |  | 2022-12-13 09:25 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | EXCAVATOR STRUCK SERVICE LINE | 42 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1958 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | GAS WAS RELEASED AT A TEAR ON THE INSIDE ELBOW OF A DEFORMATION IN THE SERVICE LINE WHERE IT WAS PULLED BY THE EXCAVATOR AND AT A COMPLETE SEPARATION WHEREBY THE 3/4" DIAMETER SERVICE PIPE FRACTURED BY SHEAR WHERE IT ENTERED THE BASEMENT WALL | CLASS 3 LOCATION | 500000 | 510901.6393442625 | 25000 | 25545.081967213125 | 11000 | 11239.836065573775 | 0 | 0 |  | 9.17 | 386 | 296.362844702467343976777939042089985486 | 0 | 0 | 536386 | 231623.9146779605437445573294629898403483 | 547982.9202217518673439767779390420899855 | 0 | 0 | 14 | 2 | 0 | 23 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 1958-07-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 15.8 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FACILITY WAS HIT BY EXCAVATOR. GAS CONTROL DID NOT HAVE AN IMPACT ON THIS INCIDENT. | [12 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 20223461851 |  |  | FACILITY OWNER | NO | YES | 12 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | ROMAN HIGH | SR ENGINEER STANDARDS | rhigh@ugi.com | 484-332-8402 |  | JOSH BARRELL | jbarrell@ugi.com |  | PAM JOCSAK | VP ENGINEERING | 484-824-5508 | pjocsak@ugi.com | ON 12/12/2022 AT 13:175, UGI RECEIVED AN EMERGENCY EXCAVATION TICKET ("TICKET") (SERIAL # 20223461851) THROUGH THE PENNSYLVANIA ONE CALL SYSTEM, ISSUED BY AN EXCAVATOR, PRONTO PLUMBING, WITH A PROPOSED DIG DATE OF 08:00 ON 12/13/22 AT 3204 CREST ROAD, HARRISBURG (THE "PROPERTY"). UGI RESPONDED THROUGH THE ONE CALL SYSTEM ON 12/12/22 AT 13:18 STATING: "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". THE UGI DISPATCHER MISTAKENLY ASSIGNED THE TICKET TO A CONTRACTOR THAT DOES NOT PERFORM EMERGENCY LOCATES. ON 12/13/2022 AT 9:06, THE FIRE DEPARTMENT WAS DISPATCHED TO THE PROPERTY DUE TO A LINE HIT. AT 9:07, UGI DISPATCH RECEIVED A CALL FROM DAUPHIN COUNTY 911, REGARDING A HIT GAS LINE AT THE PROPERTY. ALSO AT 9:07, EXCAVATOR PLACED A RE-NOTIFY TICKET THROUGH THE ONE CALL SYSTEM. UGI RESPONDED TO THE RE-NOTIFY TICKET AT 9:09 STATING: "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". UGI DISPATCHED THE CLOSEST AVAILABLE QUALIFIED FIRST RESPONDER BASED ON THE CALL RECEIVED BY DISPATCH, WHO ARRIVED AT 9:25. AT 9:30, AN EXPLOSION OCCURRED AT THE PROPERTY. THE LINE HIT RESULTED WHEN EXCAVATOR, WHO WAS WORKING FOR THE PROPERTY OWNER, BEGAN DIGGING WITH A BACKHOE NEAR THE FRONT WALL OF THE PROPERTY BETWEEN 8:45 AND 9:00 ON 12/13/22 TO REPAIR A BLOCKED SEWER SERVICE LINE. EXCAVATOR BEGAN DIGGING BEFORE UGI'S LOCATOR ARRIVED TO COMPLETE THE RE-NOTIFY TICKET AND BEFORE UGI WAS ABLE TO CONTACT EXCAVATOR TO DISCUSS THE FACILITY CONFLICTS. THE RESIDENTS AT THE PROPERTY WERE EVACUATED PRIOR TO THE EXPLOSION. THE EXPLOSION INJURED UGI'S FIRST RESPONDER AND A RESIDENT OF AN ADJACENT HOME. BOTH INDIVIDUALS WERE TREATED AT A HOSPITAL AND RELEASED THE SAME DAY. THE SITUATION WAS MADE SAFE BY CLOSING THE MAIN LINE VALVE AT THE END OF THE STREET, SHUTTING OFF GAS TO 14 CUSTOMERS. UGI CONDUCTED A SUBSURFACE LEAK SURVEY WITH NO INDICATIONS OF A LEAK. GAS SERVICE WAS PROMPTLY RESTORED TO AFFECTED CUSTOMERS ABLE TO ACCEPT GAS SERVICE. THE INCIDENT INVESTIGATION IS ONGOING, AND INFORMATION RELATED TO PARTS B, C, D, AND G OF THE REPORT ARE STILL BEING DETERMINED. A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN MORE INFORMATION IS AVAILABLE. *ON APRIL 28, 2023 UGI IS FILING THIS SUPPLEMENTAL AND FINAL REPORT AT THE REQUEST OF PHMSA. UGI IS CONFIRMING THE ROOT CAUSE OF THIS INCIDENT IDENTIFIED IN PART G REMAINS "EXCAVATION PRACTICES NOT SUFFICIENT". AS STATED IN THE NARRATIVE ABOVE, UGI RECEIVED AN EMERGENCY EXCAVATION TICKET ON 12/12/2022 AT 13:17. UGI RESPONDED TO THIS REQUEST THROUGH ITS TICKET MANAGEMENT SYSTEM THE SAME DAY AT 13:18 REMARKING "CONFLICT LINES NEARBY DIRECT CONTACT TO FOLLOW BY FACILITY OWNER". WHILE UGI AVERS THE FACILITIES WERE NOT MARKED BY THE TIME THE EXCAVATOR BEGAN DIGGING, THE EXCAVATOR WAS MADE AWARE THE DAY PRIOR OF FACILITY CONFLICTS. IN UGI'S VIEW, THE EXCAVATOR BEGAN EXCAVATION THROUGH THE USE OF MECHANICAL EXCAVATION EQUIPMENT (BACKHOE) WITHOUT EXERCISING DUE CARE, AS REQUIRED IN PENNSYLVANIA THROUGH THE 2017 UNDERGROUND UTILITY LINE PROTECTION LAW (ACT 50). THE EXCAVATOR DID NOT HAVE SUFFICIENT INFORMATION TO SAFELY USE MECHANICAL EXCAVATION EQUIPMENT TO EXCAVATE AT THIS LOCATION AND OTHERWISE DID NOT EMPLOY PRUDENT EXCAVATION TECHNIQUES SUCH AS HAND DUG TEST HOLES, VACUUM EXCAVATIONS, OR SIMILAR DEVICES. AS A RESULT, UGI'S SERVICE LINE WAS STRUCK, PUNCTURED, AND TORN FROM THE RISER AT THE WALL OF THE RESIDENCE DUE TO THE EXCAVATOR'S ACTIONS. INFORMATION RELATED TO PART C IS STILL BEING DETERMINED. A SUPPLEMENTAL AND FINAL REPORT WILL BE FILED WHEN THE INFORMATION IS AVAILABLE.
2024-05-31 11:04 | YES | NO | NO | 20230003 | 37594 | 2023-01-19 14:28 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-12-20 08:48 | EASTERN | NO | 2022 | 1014 THIRD STREET | BANGOR | VAN BUREN | MI | 49013 | 42.319 | -86.1167 | [5 empty] | YES |  |  |  | 2022-12-20 13:35 | 1355473 | 1355602 | NATURAL GAS |  | 6.6 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2022-12-20 08:48 | ALLOWED TO BURN OUT |  | 6.6 | NO | 0 | 2022-12-20 08:48 |  |  |  | 2022-12-20 09:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1974 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 0.09 |  |  | 2708 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 143500 | 146628.7704918033375 | 2147 | 2193.811639344263175 | 548 | 559.9481967213117 | 0 | 0 |  | 6.17 | 41 | 31.4789550072568940493468795355587808418 | 0 | 0 | 146236 | 63139.0022109733994928156748911465892598 | 149414.0092828761692690493468795355587808 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 48 | 48 | 60 | 192.619(A)(2) | 1974-07-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON TUESDAY, DECEMBER 20, 2022, AT APPROXIMATELY 08:48 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION FROM EMERGENCY PERSONNEL OF A HOUSE FIRE AT 1014 3RD STREET, BANGOR, (VAN BUREN COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED AT THE SITE AT APPROXIMATELY 09:25 HOURS AND CONFIRMED THE STRUCTURE FIRE WITH A RELEASE AT THE NATURAL GAS EQUIPMENT (METER/RISER). THE GSW ADVISED A DISTRIBUTION CREW WOULD BE NEEDED TO CONTAIN THE BLOWING GAS. THE GSW BEGAN EXCAVATING AT A REMOTE LOCATION NEAR THE PIPELINE IN PREPARATION FOR SQUEEZING THE 5/8-INCH PLASTIC PIPELINE, THE PLASTIC PIPELINE (SERVICE) WAS INSERTED IN A STEEL PIPELINE MAKING IT NECESSARY FOR ADDITIONAL EQUIPMENT UTILIZED BY GAS DISTRIBUTION. DISTRIBUTION ARRIVED ONSITE AT APPROXIMATELY 10:45 HOURS AND SQUEEZED THE PIPELINE STOPPING GAS FROM BLOWING AT APPROXIMATELY 10:48 HOURS. EMERGENCY RESPONDERS WERE ONSITE AND CONFIRMED ONE FATALITY AND MULTIPLE PERSONS REQUIRING MEDICAL ATTENTION WERE TRANSPORTED TO THE LOCAL HOSPITAL. FURTHER INVESTIGATION PERFORMED BY THE MICHIGAN STATE POLICE CONFIRMED THE RELEASE AT THE NATURAL GAS EQUIPMENT (METER/RISER) WAS NOT THE PRIMARY CAUSE OF THE FIRE. THE NATURAL GAS EQUIPMENT WAS COMPROMISED BY THE STRUCTURE FIRE RESULTING IN A RELEASE AT THE NATURAL GAS EQUIPMENT. THIS REPORT IS BEING SUBMITTED BECAUSE IT CANNOT BE DETERMINED IF THE SECONDARY RELEASE AT THE NATURAL GAS FACILITIES CONTRIBUTED TO THE FATALITY.
2024-05-31 11:04 | NO | YES | NO | 20230004 | 37605 | 2023-01-20 15:54 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 OLD TAYLOR ROAD MAIL CODE J48 | CAYCE | SC | 29033 | 2022-12-15 16:08 | EASTERN | NO | 2022 | ROSEWOOD DRIVE / BELTLINE BLVD | COLUMBIA | RICHLAND | SC | 29205 | 33.9879 | -80.9832 |  |  |  | YES | [5 empty] | 2022-12-15 17:32 | 1355104 | 1355199 | NATURAL GAS |  | 1613 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2022-12-15 16:08 |  |  |  | 2022-12-15 16:57 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1980 | UNKNOWN | [7 empty] | STEEL |  | FURNACE BUTT WELDED |  | 0.25 | [6 empty] | OTHER | [8 empty] | BROKEN RELIEF VALVE FROM VEHICLE IMPACT | CLASS 3 LOCATION | 0 | 0 | 135265 | 138214.220491803334125 | 0 | 0 | 0 | 0 |  | 8.36 | 13485 | 10353.5050798258345428156748911465892598 | 0 | 0 | 148750 | 66127.6612809013046224238026124818577649 | 148567.7255716291686678156748911465892598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 145 | 175 | 192.621 M | 1980-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS IMPACT BY A MOTOR VEHICLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  | YES |  |  |  | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 35 | YES |  | YES | [140 empty] | JOHNNIE WALLER | ENGINEER III - COMPLIANCE | johnnie.waller@dominionenergy.com | 803-491-4644 |  | ASHLEY MCJUNKIN | ashley.mcjunkin@dominionenergy.com | 803-457-0541 | CYNTHIA OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-530-4135 | cynthia.ostrander@dominionenergy.com | AN INCIDENT WAS REPORTED AT THE INTERSECTION OF ROSEWOOD DRIVE & BELTLINE BLVD. WHERE A VEHICLE CRASHED INTO ONE OF DOMINION ENERGY REGULATING STATIONS. OPERATOR RESOURCES WERE DISPATCHED TO THE SCENE AND REPAIR PLAN WAS INITIATED. THE LEAK WAS STOPPED AND FINAL REPAIRS WERE COMPLETED APPROXIMATELY 50 MINUTES FROM INITIAL REPORT. AT THIS TIME, THERE WAS NO LOSS OF CUSTOMERS AND NO ONE WAS INJURED RELATED TO RELEASE OF GAS. THE OFFICE OF REGULATORY STAFF FOR SOUTH CAROLINA WAS NOTIFIED AROUND 4:30 P.M. THE PRELIMINARY COST ESTIMATE WAS STATED TO EXCEED THE $129K THRESHOLD, THEREFORE TRIGGERING AN INITIAL 1-HR NOTIFICATION AND 48-HR TO THE NRC. THIS CALL WAS MADE AT APPROXIMATELY 5:32 P.M. (NRC REPORT # 1355104 AND 1355199). THE COST ESTIMATE WAS APPROXIMATELY $35,000 ON 12/22/2022, BUT SUBSEQUENTLY, ADDITIONAL COST WERE COLLECTED AFTER THE INITIAL ESTIMATE WHICH PUT THE FINAL COST OVER THE FEDERAL THRESHOLD. THE DATE OF DETERMINING COST THRESHOLD BEING EXCEEDED WAS 12/22/2022, WHICH WAS THE DATE USED FOR DETERMINING THE SUBMITTAL TIMEFRAME FOR THIS REPORT. RECORDED ON OUR LDF REPORT # 548785
2024-05-31 11:04 | NO | YES | NO | 20230005 | 37961 | 2023-01-27 12:12 | SUPPLEMENTAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2022-12-29 15:09 | EASTERN | NO | 2022 | 1210 ROBBINS AVENUE | NILES | TRUMBULL | OH | 44446 | 41.1828 | -80.7425 |  |  |  | YES |  |  |  | YES | CUT AT MAIN | 2022-12-29 16:07 | 1356293 | 1356377, 1356388 (corrected 48 hour update) | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-12-29 15:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 0 | 2022-12-29 15:49 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-12-29 15:53 | 2022-12-29 16:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNDER INVESTIGATION | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDER INVESTIGATION | CLASS 3 LOCATION | 176100 | 179939.5573770492525 | 200 | 204.360655737705 | 5000 | 5109.016393442625 | 5000 | 5109.016393442625 | UPDATE ESTIMATED COST DUE TO JOINT SITE EXAMINATION WITH HOMEOWNER'S INSURANCE. | 6.89 | 0 | 0 | 0 | 0 | 186300 | 80429.680327868883 | 190361.9508196722075 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.48 | 0.47 | 1 | 192.623 | 1926-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10.8 |  | NO |  |  |  |  | OTHER | PUBLIC UTILITIES COMMISSION STAFF MEMBER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | ALLISON S WALTERS-THOMPSON | a.walters-thompson@dominionenergy.com | 12167899152 | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 12167899152 | a.walters-thompson@dominionenergy.com | THE FIRE/EXPLOSION THAT OCCURRED ON DECEMBER 29, 2022 IS STILL CURRENTLY UNDER INVESTIGATION AS TO ITS CAUSE, SO RESPONSES TO CERTAIN SECTIONS OF THIS FORM ARE UNKNOWN OR LEFT BLANK. ALTHOUGH SECTION A21 IS CHECKED, YES, THE SOURCE OF IGNITION IS NOT YET DETERMINED. A JOINT SITE EXAMINATION TOOK PLACE ON FEBRUARY 8, 2022, AND PHYSICAL EVIDENCE FROM INSIDE THE SUBJECT PROPERTY IS BEING PRESERVED BY THE HOMEOWNER'S INSURANCE COMPANY FOR POTENTIAL LABORATORY EXAMINATION. AS OF THIS SUPPLEMENTAL REPORT, NO LABORATORY TESTING HAS BEEN CONDUCTED OR SCHEDULED FOR THE NON-JURISDICTIONAL PIPING. THE INVESTIGATION REMAINS ONGOING, AND THE APPARENT CAUSE AND CONTRIBUTING CAUSES (IF ANY) OF THIS INCIDENT ARE YET TO BE DETERMINED.
2024-05-31 11:04 | NO | NO | NO | 20230006 | 37843 | 2023-02-01 18:30 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2023-01-05 06:22 | PACIFIC | NO | 2023 | 2761 ROLLINGWOOD DRIVE | SAN PABLO | CONTRA COSTA | CA | 94806 | 37.9655 | -122.3345 | [5 empty] | YES |  |  |  | 2023-01-06 10:32 | 1356987 | 1357066 | NATURAL GAS |  | 5358 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 3 | 2023-01-05 06:22 |  |  |  | 2023-01-05 06:44 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1943 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 3 LOCATION | 0 | 0 | 13571 | 13571 | 596 | 596 | 0 | 0 |  | 6 | 32148 | 32148 | 0 | 0 | 46315 | 29990.3384754357951532948960302457466919 | 46315 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 54 | 54 | 60 | 192.619(A)(3) | 1966-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPE RUPTURED AS A RESULT OF NATURAL FORCE DAMAGE, EARTH MOVEMENT DUE TO HEAVY RAIN. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | HEAVY RAIN (BOMB CYCLONE + ATMOSPHERIC RIVER) | [213 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510/298-7063 |  |  |  |  | SUSIE RICHMOND | GAS REGULATORY COMPLIANCE MANAGER | 925/786-0267 | gsr8 | ON JANUARY 6, 2023, AT 09:50, PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED EXTENT OF CONDITION OF AN UNINTENTIONAL RELEASE OF GAS DUE TO A COMPLETELY SEVERED PIPE. ON JANUARY 5, AT APPROXIMATELY 06:22, A 4" STEEL MAIN NEAR OUR FACILITIES IN SAN PABLO BROKE AS A RESULT OF NATURAL FORCE DAMAGE, EARTH MOVEMENT DUE TO HEAVY RAIN, RESULTING IN A GAS LEAK. PG&E CREWS CONDUCTED REPAIRS. THIS SECTION OF MAIN CROSSES THE HAYWARD FAULT LINE, AND GEOSCIENCES EXAMINED THE AREA. AFTER THEIR INSPECTION IT WAS DETERMINED THAT CREEP HAS LOADED THE PIPE SINCE IT WAS INSTALLED. BASED ON A NEARBY USGS MONITORING STATION, THE AREA WHERE THE FAILURE OCCURRED CREEPS AT A RATE OF ABOUT 5 MM/YEAR. THE PIPE RUPTURED AT A PARTIAL PENETRATION GIRTH WELD. THE ORIENTATION OF THE PIPE RELATIVE TO THE FAULT AND THE SENSE OF MOVEMENT ON THE FAULT CAUSES THE PIPE TO BE LOADED IN EXTENSION, WHICH IS CONSISTENT WITH THE SEPARATION OF THE PIPE THAT WAS OBSERVED AT THE BREAK. GIVEN THAT NO OTHER BREAKS OCCURRED WHERE DISTRIBUTION MAINS IN THE AREA INTERSECT THE HAYWARD FAULT, PG&E CONCLUDES THAT THE BREAK WAS DUE TO A COMBINATION OF HEAVY RAIN FALL AND LONG-TERM CREEP LOADING. A DETAILED ASSESSMENT OF HISTORICAL LEAKS IN THE AREA DID NOT SHOW A CORRELATION BETWEEN LEAKS IN THE AREA AND THE HAYWARD FAULT. NO MEDIA WAS REPORTED ONSITE. THE FIRE DEPARTMENT AND POLICE WERE ONSITE. NO FATALITIES OR INJURIES WERE REPORTED. THREE HOMES WERE EVACUATED, AND GAS SERVICE WAS INTERRUPTED FOR EIGHT CUSTOMERS AS PART OF THE ISOLATION STRATEGY. THIS INCIDENT WAS REPORTED TO DOT (NRC #1356987/ 1357066) AND CPUC ONCE IT WAS CONFIRMED THAT THE UNINTENDED GAS LOSS WAS OVER 3 MILLION CUBIC FEET.
2024-05-31 11:04 | NO | YES | YES | 20230007 | 38650 | 2023-02-10 11:11 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2023-01-18 11:57 | CENTRAL | NO | 2023 | 4616 CORTEZ CIRCLE | MANDAN | MORTON | ND | 58554 | 46.8667 | -100.9446 | [5 empty] | YES |  |  |  | 2023-01-18 13:04 | 1357989 | 1358143 | NATURAL GAS |  | 8.21 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-01-18 11:57 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 8.21 | YES | 2 | 2023-01-18 11:57 |  |  |  | 2023-01-18 12:26 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2017 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 105000 | 105000 | 270 | 270 | 1100 | 1100 | 0 | 0 |  | 6.74 | 55 | 55 | 0 | 0 | 106425 | 44983.3743259927955807750472589792060491 | 106425 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 30 | 30 | 60 | 192.619(A)(2) | 1983-09-30 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 15 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THERE WAS A CRACKED NIPPLE BETWEEN THE RISER VALVE AND THE REGULATOR. THE ANALYSIS CONCLUDES THAT THE NIPPLE DAMAGE WAS DUE TO AN UNKNOWN OUTSIDE FORCE. IT IS UNKNOWN WHEN THE NIPPLE DAMAGE OCCURRED. | [154 empty] | SAMANTHA CALDWELL | MANAGER POLICY AND PROCEDURE | samantha.caldwell@mdu.com | 208-509-2140 |  | SAMANTHA CALDWELL | samantha.caldwell@mdu.com | 208-509-2140 | JOSH SANDERS | DIRECTOR POLICY AND PROCEDURE | 701-222-7773 | josh.sanders@mdu.com | ON JANUARY 18, 2023, MDU RESPONDED TO A STRUCTURE FIRE/EXPLOSION AT 4616 CORTEZ CIRCLE IN MANDAN, ND. AN UNINTENTIONAL RELEASE AND IGNITION OF NATURAL GAS OCCURRED. MDU PERSONNEL SECURED THE RELEASE BY SQUEEZING OFF THE SERVICE LINE. ON JANUARY 19, 2023, THE MANDAN FIRE DEPARTMENT AND ATF CONDUCTED AN INVESTIGATION AT 4616 CORTEZ CIRCLE IN MANDAN, ND, WITH REPRESENTATIVES FROM MDU AND THE ND PSC PRESENT. DURING EXAMINATION OF THE STRUCTURE'S INTERIOR, APPROXIMATELY TEN (10) FEET DOWNSTREAM OF THE GAS METER, THE NON-JURISDICTIONAL GAS PIPING WAS FOUND TO BE SEPARATED AT A CONNECTION POINT. A NATURAL GAS RANGE AND NATURAL GAS FURNACE WERE THE ONLY TWO FUEL FIRED APPLIANCES LOCATED IN THE STRUCTURE. THE CONNECTIONS AND PIPING TO THE RANGE AND FURNACE APPEARED TO BE INTACT. THE HEAT SOURCE OR CAUSE OF IGNITION WAS INCONCLUSIVE. FOLLOWING THE INVESTIGATION ON JANUARY 19, 2023, MDU MADE ATTEMPTS TO COORDINATE THE INVESTIGATION OF JURISDICTIONAL FACILITIES WITH ALL PARTIES. AFTER FAILED ATTEMPTS TO COORDINATE, THE COMPANY PROVIDED NOTIFICATION TO ALL PARTIES THAT AN INVESTIGATION WOULD COMMENCE ON AUGUST 15, 2023. MDU AND THE NORTH DAKOTA GAS PIPELINE SAFETY PROGRAM MANAGER/INSPECTOR CONDUCTED AN INVESTIGATION OF JURISDICTIONAL FACILITIES AT 4616 CORTEZ CIRCLE IN MANDAN, ND. A PRESSURE TEST WAS PERFORMED ON THE SERVICE LINE. THE PRESSURE TEST PASSED, HOLDING AT SYSTEM PRESSURE. ABOVE GROUND PIPING WAS INTACT UP TO THE RISER VALVE. THERE WAS A CRACKED NIPPLE BETWEEN THE RISER VALVE AND THE REGULATOR. THE ANALYSIS CONCLUDES THAT THE NIPPLE DAMAGE WAS DUE TO AN UNKNOWN OUTSIDE FORCE. IT IS UNKNOWN WHEN THE NIPPLE DAMAGE OCCURRED. MDU WAS ALLOWED TO INVESTIGATE JURISDICTIONAL FACILITIES ONLY. OCTOBER 11, 2023 - CORRECTED TIME IN FIELD A4. UPDATED FROM 12:26 TO 11:57.
2024-05-31 11:04 | NO | YES | NO | 20230008 | 37951 | 2023-02-10 19:46 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-01-10 15:49 | CENTRAL | NO | 2023 | 1520 BIG TIMBER RD | ELGIN | KANE | IL | 60123 | 42.0585 | -88.3153 | YES | [5 empty] | YES |  |  | 2023-01-11 11:45 | 1357409 | 1357625 1357628 | NATURAL GAS |  | 1830 | 21 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 50 | 2023-01-10 15:49 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-01-10 16:03 | 2023-01-10 16:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 114 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 353550 | 353550 | 284225 | 284225 | 0 | 0 |  | 6.59 | 12060 | 12060 | 138 | 138 | 649973 | 278573.9684812255043983459357277882797732 | 649973 | 12 | 0 | 0 | 0 | 0 | 0 | 6 | 160 | 160.6 | 165 | 192.621 M | 1979-06-30 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS MAIN AT INCIDENT LOCATION IS NOT MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A22299449 | JULIE OTHER JULIE DIG #S - A223211418 A223402053 |  | CONTRACT LOCATOR | YES | YES | 41 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOSE L DELREAL | MANAGER OPS QA | jdelrea@southernco.com | 630-918-4934 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | 630-514-2036 | lquezad@southernco.com | THIRD PARTY CONTRACTOR, VERITA TELECOMMUNICATIONS CORP, WAS DIRECTIONAL DRILLING ALONG THE EAST SIDE OF MCLEAN BLVD, AT/NEAR THE INTERSECTION OF BIG TIMBER RD. THE VERITA HDD CREW WAS DRILLING ACROSS BIG TIMBER RD. A VERITA CREW-PERSON CALLED A NICOR GAS EMPLOYEE AT 15:49 ON JANUARY 10, 2023, INDICATING THEY SMELLED GAS. COMPANY EMERGENCY RESPONDERS WERE DISPATCHED IN RESPONSE TO THE NOTIFICATION. UPON EVALUATION, IT WAS DETERMINED THAT A 12-INCH MAIN HAD BEEN DAMAGED AND THE SYSTEM COULD BE ISOLATED USING TWO EXISTING VALVES (EAST & WEST OF THE DAMAGE) AND A LINE STOP FITTING (NORTH OF THE DAMAGE). THE RELEASE WAS SECURED AT APPROXIMATELY 22:42 ON JANUARY 11, 2023. NICOR INSTALLED A 250-FOOT LONG, 4-INCH BYPASS TO MINIMIZE THE RISK OF ADDITIONAL GAS SERVICE INTERRUPTION TO CUSTOMERS THAT WERE NOT ALREADY IMPACTED BY THE INCIDENT. THE BYPASS WAS IN SERVICE AT APPROXIMATELY 03:00 (24-HOUR TIME) ON JANUARY 12, 2023. THE DAMAGED SECTION OF MAIN WAS EXPOSED AND EXAMINED, AND A CLAMP WAS INSTALLED TO REPAIR THE DAMAGED SECTION. THE SYSTEM WAS RETURNED TO SERVICE IN SECTIONS, WITH THE LAST SECTION RETURNING TO NORMAL OPERATION BY 21:46 ON JANUARY 12, 2023. AT THE TIME OF THE INCIDENT, THERE WAS A VALID ONE-CALL TICKET AND MARKINGS WERE ACCURATE. THE CONTRACTOR INDICATED THEY POTHOLED DOWN TO 4.5 FEET AND OBSERVED THE TOP OF WHAT THEY THOUGHT WAS A GAS MAIN. THERE WAS NO EVIDENCE THAT THE CONTRACTOR HAD EXPOSED THE 12-INCH GAS MAIN TO OBSERVE THE DRILLING EQUIPMENT PASS THE GAS MAIN DURING THEIR OPERATION. THE DAMAGE TO THE 12-INCH MAIN OCCURRED AT A DEPTH OF 9.5 FEET.
2024-05-31 11:04 | NO | YES | NO | 20230009 | 37866 | 2023-02-14 09:13 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2023-01-14 13:02 | EASTERN | NO | 2023 | 1906 PROMENADE WAY | JACKSONVILLE | DUVAL | FL | 32207 | 30.3014 | -81.6437 | [6 empty] | YES |  |  | 2023-01-14 13:02 | 1357662 | 1357780 | NATURAL GAS |  | 9.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-01-12 08:44 | YES | OPERATOR | 2023-01-13 08:16 | 2023-01-12 09:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 72103 | 72103 | 165852 | 165852 | 65078 | 65078 | 0 | 0 |  | 10 | 93 | 93 | 0 | 0 | 303126 | 128103.6803514254659030378071833648393195 | 303126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 220 | 250 | 192.619(A)(4) | 1999-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR HAIR-LINE CRACK WAS IDENTIFIED WITH NO IMPACT TO ALARMS WITHIN THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2022-09-27 | YES | 1999 | 250 | [10 empty] | YES | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER |  | NO |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [144 empty] | YES | [25 empty] | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | rharris@tecoenergy.com | 407-420-6667 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR OF SAFETY | 813-228-1784 | kjkelley@tecoenergy.com | PEOPLES GAS RECEIVED A LEAK REPORT ON 1/12/23, RESPONDED TO THE SCENE AND BEGAN AN INVESTIGATION. A DETERMINATION OF THE SOURCE AND LOCATION WAS IDENTIFIED, AND THE SCENE WAS MADE SAFE WITH FIRST RESPONDER SUPPORT. BASED ON THE LOCATION OF THE IDENTIFIED LEAK, DEPTH OF PIPELINE AND POTENTIAL CUSTOMER LOSS, THE CORRECTIVE ACTION PLAN TO MAKE THE SCENE SAFE WAS TO INSTALL A TEMPORARY BY-PASS TO REMEDIATE THE IDENTIFIED LEAK. THE DAMAGED PIPE WAS ISOLATED, AND THE LEAKAGE STOPPED. A NEW PRETESTED SECTION OF PIPE WAS INSTALLED FOR PERMANENT REPAIR, AND THE TEMPORARY BYPASS WAS CAPPED AND TAKEN OUT OF SERVICE. DURING THE ASSESSMENT, A PREVIOUS UNREPORTED LONGITUDINAL GOUGE (EXCAVATION DAMAGE) WAS IDENTIFIED ON THE 8" PIPELINE, THAT OVER TIME RESULTED IN A LEAK. LEAK SURVEY PERFORMED ON 9/27/2022 DID NOT IDENTIFY A LEAK AT THIS LOCATION. PART G, #9 IS "NO" DUE TO LIMITATIONS OF THE FORM, IN FACT IS UNKNOWN WHETHER A LOCATE TICKET WAS CALLED OR NOT AT THE TIME OF THE EXCAVATION/DAMAGE.
2024-05-31 11:04 | NO | YES | NO | 20230010 | 37778 | 2023-03-03 13:29 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-02-03 17:05 | CENTRAL | NO | 2023 | 136 E. LAKE ST | BLOOMINGDALE | DUPAGE | IL | 60108 | 41.9572 | -88.0754 | [5 empty] | YES |  |  |  | 2023-02-03 19:03 | 1359221 | 1359323 | NATURAL GAS |  | 201.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-02-03 17:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 201.4 | NO | 0 | 2023-02-03 17:17 |  |  |  | 2023-02-03 17:48 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1993 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | PE RISER- STEEL-ALUMINUM REGULATOR/METER | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 1255000 | 1255000 | 200 | 200 | 2207 | 2207 | 0 | 0 |  | 6.12 | 1233 | 1233 | 0 | 0 | 1258640 | 532186.7282730767790549206049149338374291 | 1258640 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 54.8 | 58 | 60 | 192.619(A)(2) | 1993-01-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | DRIVEWAY | 25 | YES | YES | [141 empty] | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | lquezad@southernco.com | 6305142036 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | A BANK DRIVE-THRU CUSTOMER LOST CONTROL OF HER VEHICLE, CRASHING THROUGH THE BUILDING BRICK WALL. THE COLLISION DAMAGED THE METER SET LOCATED IN FRONT OF THE WALL, CAUSING A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. THE NATURAL GAS IGNITED, AND THE FIRE SPREAD INTO THE BANK BUILDING. THE DRIVER OF THE VEHICLE WAS NOT INJURED AND EXITED THE VEHICLE PRIOR TO THE GAS IGNITION.
2024-05-31 11:04 | NO | YES | YES | 20230011 | 37940 | 2023-03-10 14:23 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2023-02-10 04:58 | MOUNTAIN | NO | 2023 | 1414 DEGEEST DRIVE | RAPID CITY | PENNINGTON | SD | 57703 | 44.0725 | -103.1423 | [5 empty] | YES |  |  |  | 2023-02-10 06:00 | 1359693 | 1359810 | NATURAL GAS |  | 22 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES | 2023-02-10 04:24 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 22 | NO | 8 | 2023-02-10 04:58 |  |  |  | 2023-02-10 04:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2000 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ANODELESS SERVICE RISER | [9 empty] | OTHER | [8 empty] | VEHICLE STRUCK METER SET, SHEARING OFF RISER AT GROUND LEVEL. | CLASS 3 LOCATION | 750000 | 750000 | 500 | 500 | 2000 | 2000 | 0 | 0 |  | 6.284 | 138 | 138 | 0 | 0 | 752638 | 318041.235360179747065217391304347826087 | 752638 | 0 | 0 | 2 | 0 | 0 | 3 | 0 | 50 | 50 | 55 | 192.619(A)(2) | 2000-11-06 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 9 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | YES | 80 | SMALL TRUCK | ROADWAY | 62 | NO | [118 empty] | YES | [23 empty] | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | danny.hood@mdu.com | 7015162749 |  | TOBY BORDEWYK | toby.bordewyk@mdu.com | 6053554054 | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | 7015162749 | danny.hood@mdu.com | ON FEBRUARY 10, 2023, AT 04:24 AM, MONTANA DAKOTA UTILITIES (MDU) RECEIVED A CALL REPORTING A HOUSE FIRE AT 1414 DEGEEST DRIVE IN RAPID CITY SOUTH DAKOTA. UPON ARRIVAL THE MDU SERVICE TECHNICIAN DETERMINED A VEHICLE TRAVELING IN A RESIDENTIAL SUBDIVISION LEFT THE ROADWAY AND STRUCK AN OUTSIDE METER SET ON THE HOUSE, SHEARING OFF THE RISER AT GROUND LEVEL, CAUSING A RELEASE OF NATURAL GAS THAT IGNITED. THE DRIVER OF THE VEHICLE DID NOT SURVIVE, AND 4 RESIDENTS OF THE HOUSE WERE TRANSPORTED TO THE HOSPITAL. THE FOUR RESIDENTS OF 1414 DEGEEST DR WERE EVACUATED, OCCUPANTS AT 1426 DEGEEST DR AND 1392 DEGEEST DR WERE ALSO EVACUATED. NUMBER OF PEOPLE EVACUATED IN PART A IS AN ESTIMATE AS NUMBER OF OCCUPANTS FROM 1426 DEGEEST AND 1392 DEGEEST IS UNKNOWN AT THE TIME OF THIS REPORT. GAS SERVICE TO 1414 DEGEEST DR AND 1426 DEGEEST DR WAS LOST DURING THE INCIDENT. GAS SERVICE TO 1426 DEGEEST DR WAS RESTORED AT APPROXIMATELY 10:00 AM. GAS SERVICE TO 1414 DEGEEST DR HAS BEEN RETIRED. THE HOME AT 1414 DEGEEST WAS A TOTAL LOSS. THE HOUSE AT 1426 DEGEEST SUSTAINED DAMAGE, A CAMPER AT THIS LOCATION WAS A TOTAL LOSS. THREE 3 VEHICLES SUSTAINED DAMAGE. UPDATE: APRIL 12, 2023- THE POLICE REPORT INDICATED THE SPEED OF THE VEHICLE WAS ESTIMATED AT 80 MPH USING INFORMATION FROM A WITNESS. POLICE REPORT INDICATES THE INJURIES TO THE DRIVER OF THE VEHICLE AND THE RESULTING FIRE PROVED TO BE FATAL. NO INDICATION OF THE CAUSE OF THE FATALITY IN THE POLICE OR FIRE REPORT. THE FIRE REPORT INDICATES ACCESS TO THE VEHICLE AFTER THE GAS LINE WAS CLAMPED AND THE FIRE WAS CONTROLLED ALLOWING RECOVERY OF THE VICTIM. THE NUMBER OF REPORTED INJURIES VARIES FROM 2 TO 5 INDIVIDUALS ON THE POLICE, FIRE, AND COMPANY FIRST RESPONDER REPORTS. NO INFORMATION IN THE REPORTS COULD CONFIRM IF THE INJURIES REQUIRED HOSPITALIZATION. THE HOUSES AT 1414 DEGEEST DR, 1426 DEGEEST AND 1392 DEGEEST DR. WERE EVACUATED BY UNKNOWN PERSONS. THE NUMBER OF RESIDENTS EVACUATED IS AN ESTIMATE AS NO SPECIFIC INFORMATION ON THE NUMBER OF EVACUATIONS IS INCLUDED IN THE POLICE OR FIRE REPORTS. THE POLICE REPORT INDICATES TOTAL LOSS OR DAMAGE TO 1 CAMPER TRAILER, 1 UTILITY TRAILER, AND 6 VEHICLES. ESTIMATED VALUE OF TRAILERS AND VEHICLES - $100,000. UPDATED THE ESTIMATED PROPERTY DAMAGE INFORMATION, USING INFORMATION FROM POLICE AND FIRE REPORTS. 1414 DEGEEST DR. - $500,000 INCLUDING POSSESSIONS, 1426 DEGEEST DR. - $100,000 AND 1392 DEGEEST DR. - $50,000 TOTAL ESTIMATED LOSS TO NON-OPERATOR - $750,000
2024-05-31 11:04 | NO | YES | NO | 20230012 | 37877 | 2023-03-22 16:09 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-02-20 16:00 | CENTRAL | NO | 2023 | 2101 TEXAS AVE | COLLEGE STATION | BRAZOS | TX | 77840 | 30.612 | -96.3147 | [5 empty] | YES |  |  |  | 2023-02-21 18:07 | 1360544 | 1360697 | NATURAL GAS |  | 1058.34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 8 | 2023-02-20 16:00 | YES | OPERATOR | 2023-02-20 16:00 | 2023-02-20 16:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 180 | YES | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 113589 | 113589 | 14330 | 14330 | 0 | 0 |  | 7.7224 | 8173 | 8173 | 0 | 0 | 136092 | 60149.6702299820828901720226843100189036 | 136092 | 1 | 0 | 10 | 0 | 0 | 17 | 1 | 34 | 34 | 50 | 192.619(A)(2) | 2004-10-14 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2354567778 | TEXAS 811 |  | CONTRACT LOCATOR | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LUIS CISNEROS | COMPLIANCE SUPERVISOR | luis.cisneros@atmosenergy.com | 979-324-8823 |  |  |  |  | JEFF KNIGHTS | SR VP TECHNICAL AND OPERATING SERVICES | 214-206-2701 | jeffrey.knights@atmosenergy.com | ON FEBRUARY 20, 2023, AT 4PM, A THIRD-PARTY CONTRACTOR WAS DIRECTIONAL DRILLING AT 2101 TEXAS AVENUE / RICHARDS ST, COLLEGE STATION AND BORED INTO ATMOS ENERGY'S 2-INCH POLY MAIN AT A DEPTH OF 15 FEET. THE TECHNICIAN ARRIVED ON THE SCENE AND CONFIRMED THE LEAK AT 4:30PM. COLLEGE STATION FIRE DEPARTMENT EVACUATED 8 STRUCTURES AND GAS WAS SUBSEQUENTLY TURNED OFF TO 10 HOUSES AND 1 COMMERCIAL ENTITY ON RICHARDS ST. UPON ARRIVAL ON THE SCENE, ATMOS ENERGY'S CREW WORKED CONTINUOUSLY TO CONDUCT THE NECESSARY EXCAVATION TO LOCATE AND REPAIR THE DAMAGED LINE. ON FEBRUARY 21, 2023 AT 2:30PM, A SQUEEZE TOOL WAS INSTALLED ON THE 2-INCH POLY PIPE TO STOP GAS FLOW WHERE THE PIPE WAS DAMAGED. AT 5PM, THE 2-INCH MAIN WAS REPLACED AND GAS SERVICE WAS RESTORED TO THE 11 CUSTOMERS. REGARDING PART A QUESTION 22 - THIS NUMBER REFERS TO THE 8 STRUCTURES THAT WERE EVACUATED AND NOT PEOPLE. THE TOTAL OF PEOPLE THAT WERE EVACUATED IS NOT KNOWN.
2024-05-31 11:04 | NO | YES | NO | 20230013 | 37860 | 2023-03-23 10:39 | ORIGINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2023-03-01 22:30 | PACIFIC | NO | 2023 | 65 HAYS STREET | BRIDGEPORT | MONO | CA | 93517 | 38.254 | -119.2268 |  |  |  | YES | [5 empty] | 2023-03-02 13:33 | 1361287 |  | PROPANE GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-03-01 22:30 |  |  |  | 2023-03-03 08:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN LOCATION - UNDER INVESTIGATION | CLASS 3 LOCATION | 130000 | 130000 | 300 | 300 | 0 | 0 | 0 | 0 | ESTIMATE NOT AWARE OF AN ACTUAL DOLLAR AMOUNT | 3 | 0 | 0 | 0 | 0 | 130300 | 55052.9520295203053 | 130300 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.5 | 0.5 | 10 | 192.619(A)(3) | 1965-07-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | ON 3/1/2023 AROUND 22:30 LOCAL TIME SYSTEM MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS THAT AN AUTO PARTS BUILDING THAT HAD L.P GAS SERVICE WAS ON FIRE. EMERGENCY RESPONDERS THEN CLOSED THE RISER SERVICE VALVE AND SECURED/LOCKED IT AT THAT TIME. CAUSE OF FIRE IS UNCLEAR, ESTIMATED COST OF DAMAGES IS UNKNOWN. THE INCIDENT IS UNDER INVESTIGATION, THIS FORM IS SUBMITTED AS A PRECAUTIONARY MEASURE. | [47 empty] | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | bill.runyans@amerigas.com | 2564591078 |  | KYLE MUIR | kyle.muir@amerigas.com | 7067090195 | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | 2564591078 | bill.runyans@amerigas.com | ON 3/1/2023 AROUND 22:30 LOCAL TIME SYSTEM MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS THAT AN AUTO PARTS BUILDING THAT HAD L.P GAS SERVICE WAS ON FIRE. EMERGENCY RESPONDERS THEN CLOSED THE RISER SERVICE VALVE AND SECURED/LOCKED IT AT THAT TIME. CAUSE OF FIRE IS UNCLEAR, ESTIMATED COST OF DAMAGES IS UNKNOWN. THE INCIDENT IS UNDER INVESTIGATION, THIS FORM IS SUBMITTED AS A PRECAUTIONARY MEASURE.
2024-05-31 11:04 | NO | YES | NO | 20230014 | 37863 | 2023-03-23 15:41 | ORIGINAL FINAL | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2022-02-02 08:59 | EASTERN | NO | 2022 | 2592 CARMEL AVE | BREWSTER | PUTMAN | NY | 10509 | 41.3993 | -73.625 |  |  |  | YES | [5 empty] | 2022-02-03 17:45 | 1328021 | 1328415 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2022-02-02 08:20 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 3 | 2022-02-02 08:20 | YES | OPERATOR | 2022-02-02 08:30 | 2022-02-02 07:07 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | 2X1 MECHANICAL TAPPING TEE | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 425000 | 434266.393442623125 | 100 | 102.1803278688525 | 5000 | 5109.016393442625 | 0 | 0 |  | 37.09 | 37 | 28.4078374455732946298984034833091436865 | 0 | 0 | 430137 | 185704.5479668800819288824383164005805515 | 439505.9980013801757946298984034833091437 | 1 | 0 | 2 | 0 | 0 | 1 | 1 | 52 | 52 | 56 | 192.619(A)(2) | 1997-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | TAPPING TEE |  | PERFECTION | UNKNOWN | PLASTIC |  | PULLED OUT | [21 empty] | YES | TEE NOT INSTALLED IN ACCORDANCE WITH MANUFACTURER INSTRUCTIONS | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | DAN BLANCE | ENGINEER | dcblance@nyseg.com | 607-240-3821 |  |  |  |  | BARRY KACHMARYK | MANAGER GAS ENGINEERING | 585-315-1227 | barry_kachmaryk@rge.com | ON THE MORNING OF FEBRUARY 2, 2022, NYSEG COMPANY PERSONNEL INVESTIGATING A GAS ODOR COMPLAINT AT 2586 CARMEL AVE, BREWSTER NOTICED SMOKE COMING FROM THE RESIDENCE NEXT DOOR AT 2592 CARMEL AVE ("THE RESIDENCE"). NYSEG PERSONNEL IMMEDIATELY SHUT OFF THE SERVICE LINE TO THE RESIDENCE AND CALLED THE FIRE DEPARTMENT. THE FIRE CONTINUED FOR SEVERAL HOURS BEFORE IT WAS EXTINGUISHED. ALL OCCUPANTS OF THE RESIDENCE ESCAPED AND, TO NYSEG'S KNOWLEDGE, NO INJURIES WERE REPORTED AT THAT TIME. AFTER THE FIRE WAS EXTINGUISHED, NYSEG CONDUCTED A LEAK SURVEY OF THE SURROUNDING AREA AND IDENTIFIED A LEAK IN THE GAS MAIN AT A PERMALOCK TAPPING TEE APPROXIMATELY 20 FT - 30 FT FROM THE FOUNDATION OF THE RESIDENCE. THE PERMALOCK TAPPING TEE WAS MANUFACTURED BY PERFECTION CORPORATION (NOW KNOWN AS EAMCO, LLC), WHICH IS TODAY A SUBSIDIARY OF HONEYWELL INTERNATIONAL, INC. AFTER THE FIRE THE COMPANY CONDUCTED PRESSURE TESTS AND CONFIRMED THAT THERE WERE NO LEAKS IN THE SERVICE LINE TO THE RESIDENCE. FACTS LEARNED THROUGH THE INCIDENT INVESTIGATION RAISE QUESTIONS AS TO THE ACTUAL CAUSE OF THE FIRE. SPECIFICALLY, NYSEG LEARNED THAT A NEW FURNACE WAS INSTALLED IN THE RESIDENCE'S BASEMENT BY A CONTRACTOR UNAFFILIATED WITH NYSEG THE DAY BEFORE THE FIRE. ACCORDING TO INVESTIGATIVE FINDINGS SHARED WITH THE COMPANY BY A REPRESENTATIVE OF THE HOMEOWNER'S INSURER, THE TENANTS OF 2592 CARMEL AVE STARTED SMELLING GAS IMMEDIATELY AFTER THE NEW FURNACE WAS INSTALLED AND THROUGHOUT THE NIGHT BEFORE THE FIRE, HOWEVER, THEY DID NOT NOTIFY NYSEG BECAUSE THE INSTALLER HAD TOLD THEM THAT THIS WAS "NORMAL." THIS MATTER IS NOW THE SUBJECT OF MULTIPLE CIVIL LAWSUITS FOR PROPERTY DAMAGE IN WHICH THE CAUSE OF THE FIRE WILL BE THE SUBJECT OF DISCOVERY AND EXPERT TESTIMONY. THE COMPANY DID NOT HAVE ADEQUATE CAUSE TO REPORT WITHIN THE REQUIRED 30 DAYS. ALTHOUGH THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION AND CURRENTLY THE SUBJECT OF LITIGATION, THE COMPANY IS MAKING THIS FILING NOW IN AN ABUNDANCE OF CAUTION AND TO THE EXTENT IT MEETS THE CRITERIA SET FORTH UNDER 49 CFR PART 191.3(3).
2024-05-31 11:04 | NO | YES | NO | 20230016 | 38043 | 2023-03-27 09:57 | SUPPLEMENTAL FINAL | 7685 | HUNTSVILLE GAS SYSTEM | P.O. BOX 2048 | HUNTSVILLE | AL | 35804 | 2023-03-11 13:43 | CENTRAL | NO | 2023 | 278 BREVARD BLV | HUNTSVILLE | MADISON | AL | 35811 | 34.8088 | -86.4832 |  | YES |  | YES |  | YES |  |  |  | 2023-03-11 13:43 | 1362057 | 1362183 | NATURAL GAS |  | 64.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-11 13:38 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 50 | YES | 7 | 2023-03-11 13:00 | YES | OPERATOR | 2023-03-11 13:43 | 2023-03-11 12:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 390000 | 390000 | 5000 | 5000 | 500 | 500 | 0 | 0 |  | 5 | 324 | 324 | 0 | 0 | 395824 | 167344.3266903368773052930056710775047259 | 395824 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 47 | 49 | 50 | 192.619(A)(2) | 2005-01-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT DID NOT INDICATE ANY PRESSURE ISSUES ON THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 230581806 |  |  | CONTRACT LOCATOR | NO | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | TODD GENTLE | GAS OPERATIONS DIRECTOR | todd.gentle@hsvutil.org | 2563484852 |  | TODD GENTLE | todd.gentle@hsvutil.org | 2563484852 | TODD GENTLE | GAS OPERATIONS DIRECTOR | 2563484852 | todd.gentle@hsvutil.org | AT APPROXIMATELY 1245 (12:45PM CST) ON MARCH 11, 2023, HUNTSVILLE UTILITIES (HU) DISPATCH CENTER RECEIVED A TELEPHONE CALL FROM A CONTRACTOR NOTIFYING HU THAT HE HAD CUT A GAS SERVICE LINE AT 278 BREVARD BLVD. ON-CALL CREWS FROM HU GAS DEPARTMENT RECEIVED NOTIFICATION AT 1245 (12:45PM CST) OF AN OUTSIDE LEAK DUE TO A DIG IN. HU GAS DEPARTMENT HELPER ARRIVED ON SCENE AT 1258 (12:58PM CST) AND NOTICED A STRONG SMELL OF GAS. THE FIRST RESPONDER KNOCKED ON THE FRONT DOOR, BUT NO ONE ANSWERED. THE METER WAS THEN TURNED OFF AND CONTACT WAS MADE WITH ONE OF THE HOMEOWNERS THAT ARRIVED AT THE HOUSE. DUE TO THE RESIDENT NOT BEING ABLE TO SPEAK ENGLISH, HU EMPLOYEE HAD TO REQUEST HELP FROM THE CONTRACTOR FOR TRANSLATION. AFTER THE CONTRACTOR TRANSLATED THE INFORMATION, THE RESIDENT WENT INSIDE AND RETRIEVED A RESIDENT THAT COULD SPEAK ENGLISH. THE HU EMPLOYEE WENT INTO THE HOUSE AND COULD SMELL GAS IN THE LAUNDRY ROOM. HE INSTRUCTED THE RESIDENT TO GET EVERYONE IN THE HOUSE OUT AND TO NOT TURN ON ANY SWITCHES. THE RESIDENT PROCEEDED TO TURN ON SOME LIGHT SWITCHES AND THE HU EMPLOYEE REITERATED NOT TO TURN ON/OFF ANYTHING AND TO GET EVERYONE OUT OF THE HOUSE. AT APPROXIMATELY 1315 (01:15PM CST) HU LEADMAN ON-CALL ARRIVED AND NOTICED GAS WAS BLOWING OUT OF THE GROUND NEAR THE SERVICE RISER. ONE CREW MEMBER BEGAN TO ATTEMPT TO TEST THE ATMOSPHERE IN THE HOUSE WITH A GAS DETECTION UNIT. IN HIS ATTEMPT TO GET INTO THE HOUSE, THE RESIDENCE LOCKED THE DOOR THUS HE HAD TO FIND THE RESIDENT TO UNLOCK THE DOOR. ALSO, HU PERSONNEL WERE BEGINNING TO IDENTIFY THE MAINLINE VALVES THAT WOULD ISOLATE THIS SECTION OF MAIN SERVING THE RESIDENCE. AT 1333 (01:33PM CST) THE SUPERVISOR ON-CALL ARRIVED AT THE SCENE AND BEGAN ACCESS THE SCENE. DURING THIS TIME OTHER CREW MEMBERS BEGAN DIGGING A HOLE NEAR THE AREA THAT THE SERVICE LINE WAS DAMAGED TO VENT THE GAS AWAY FROM THE HOUSE. UPON GAINING ACCESS TO THE RESIDENCE TO TEST THE ATMOSPHERE WITH THE GAS DETECTION UNIT, THE CREW MEMBER IN THE HOUSE HEARD WHAT SOUNDED LIKE THE GARAGE DOOR OPENING AND HEARD A LOUD ROARING SOUND. AS HE SAW THE FLAMES, HE RAN OUT THE FRONT DOOR. THE CREW MEMBERS DIGGING IN THE YARD HEARD WHAT THEY ASSUMED WHAT THE GARAGE DOOR OPENING IMMEDIATELY FOLLOWED BY AN EXPLOSION AT 1343 (01:43PM CST). CREW MEMBERS RE-ASSEMBLED NEAR THE STREET, THE SUPERVISOR ON SCENE CALL 911 AT 1343 (01:43PM CST) WHILE THE OTHER CREW MEMBERS CHECKED ON THE HEALTH STATUS OF ALL INDIVIDUALS AT THE SCENE. UPON FINDING NO ONE WAS INJURED, THE CREWS BEGAN TO LOCATE THE NEAREST MAIN LINE VALVES TO BEGIN TO SHUT OFF GAS TO THE WHOLE AREA. AFTER THE SUPERVISOR ENDED HIS CALL WITH 911, HE BEGAN TO CALL ADDITIONAL CREWS TO BRING SOME EQUIPMENT TO DIG THE SERVICE UP AND CAP IT OFF. ADDITIONAL CREWS ARRIVED ON SCENE AT 14:00 (02:00 PM CST) TO BEGIN DIGGING THE SERVICE UP ACROSS THE STREET SQUEEZE IT OFF AND CAP BOTH ENDS OF THE CUT. DURING THIS TIME ADDITIONAL CREW MEMBERS BEGAN LEAK SURVEYING THE SURROUND AREA AND PERFORMING BAR HOLE TEST AROUND THE MAIN. ONCE THE FIRE WAS EXTINGUISHED, CREWS MOVED ONTO THE PROPERTY AND CONTINUED LEAK SURVEY THE SURROUNDING AREA AND BAR HOLING THE SCENE. THE FIRE MARSHAL INSTRUCTED US TO REMAIN AWAY FROM THE STRUCTURE TILL THEIR INVESTIGATION WAS COMPLETE. AN INVESTIGATION INTO THE CAUSE OF THE INCIDENT IS ONGOING. CONTRIBUTING FACTORS MAY HAVE BEEN THE CUT GAS SERVICE LEAKING INTO THE HOUSE WITH AN UNKNOW IGNITION SOURCE. THE LOCAL WEATHER CONDITIONS AT THE TIME OF THE INCIDENT WERE A TEMPERATURE OF 60 DEGREES FAHRENHEIT, THE WIND SPEED WAS 4 MPH, NO WIND GUST, EAST WIND AND PARTLY CLOUDY. A SUPPLEMENTAL OR SUPPLEMENTAL PLUS FINAL REPORT WILL BE FILLED AS SOON AS NEW, UPDATED AND/OR CORRECTED INFORMATION IS KNOWN. IT HAS BEEN DETERMINED THAT THE ROOT CAUSE OF THE INCIDENT WAS LOCATES NOT BEING PERFORMED WITHIN THE ALLOTTED TIME FRAME. THE CONTRACTOR CORRECTLY LOCATED THE SERVICE LINE THEMSELVES, BUT DID NOT POT-HOLE THE UTILITIES.
2024-05-31 11:04 | NO | YES | YES | 20230019 | 38071 | 2023-04-14 16:55 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2023-03-17 20:40 | MOUNTAIN | YES | 2023 | 8913 PADILLA DRIVE | EL PASO | EL PASO | TX | 79907 | 31.6878 | -106.334 | [5 empty] | YES |  |  |  | 2023-03-17 21:12 | 1362513 | 1362610 | NATURAL GAS |  | 5.772 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-03-17 16:49 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.54 | NO | 4 | 2023-03-17 17:49 |  |  |  | 2023-03-17 17:31 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | 2017 |  |  |  |  | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | DR11 |  |  | 2708 | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 129383 | 129383 | 5000 | 5000 | 7895 | 7895 | 0 | 0 |  | 5.82 | 34 | 34 | 0 | 0 | 142312 | 60139.1550513047773810245746691871455577 | 142312 | 0 | 0 | 1 | 2 | 0 | 1 | 0 | 49 | 50 | 60 | 192.619(A)(2) | 2017-11-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DAMAGED DURING SEWER CLEAN OUT AT A CROSS BORE. | [149 empty] | YES |  |  |  |  | BRYAN WEEKS | DIRECTOR OF ENGINEERING | bryan.weeks@onegas.com | 5124071529 | 5124651133 | BRYAN WEEKS | bryan.weeks@onegas.com | 5124071529 | BRYAN WEEKS | DIRECTOR OF ENGINEERING | 5124071529 | bryan.weeks@onegas.com | POST-INCIDENT INVESTIGATION REVEALED A 2-INCH PE PIPE WAS MOST LIKELY PUNCTURED WHEN A RESIDENT'S PLUMBER USED A MECHANICAL TOOL TO CLEAR A CLOGGED SEWER LATERAL. THE GAS PIPE HAD BEEN INADVERTENTLY CROSS-BORED THROUGH THE SEWER LATERAL BY THE ORIGINAL GAS LINE INSTALLATION CONTRACTOR IN 2017. CAMERA INSPECTIONS WERE PERFORMED ON THE REMAINDER OF THE ORIGINAL INSTALLATION PROJECT AND NO ADDITIONAL AREAS WERE DISCOVERED TO HAVE CROSS-BORES. TEXAS GAS SERVICE COMPANY'S PUBLIC AWARENESS TO THE AFFECTED PUBLIC INCLUDES OUTREACH ON THE POSSIBILITY OF CROSS-BORES. SUPPLEMENTAL INFORMATION 5/19/23 TGS SELECTED 20:40 AS THE EARLIEST LOCAL TIME THAT THE INCIDENT REPORTING CRITERIA WERE MET BASED ON ITS PRELIMINARY EVALUATION THAT NATURAL GAS FROM ITS SYSTEM WAS LIKELY TO HAVE CAUSED THE FIRE AND THE PRESUMPTION THAT ONE OF THE HOME'S OCCUPANTS COULD BE ADMITTED TO THE HOSPITAL FOR CARE OR THAT THE TOTAL COST OF DAMAGES COULD EXCEED $129,300. WHILE THE ORIGINAL TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER NOTED THE POTENTIAL THAT AN EXPLOSION HAD OCCURRED, THE INVESTIGATION MADE NO OBSERVATIONS OR FORMAL REPORTS OF AN EXPLOSION.
2024-05-31 11:04 | NO | YES | YES | 20230022 | 39369 | 2023-04-23 13:24 | SUPPLEMENTAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2023-03-24 16:55 | EASTERN | YES | 2023 | 17 S 2ND AVENUE | WEST READING | BERKS | PA | 19611 | 40.3344 | -75.9422 |  | YES | [7 empty] | 2023-03-24 19:09 | 1363061 | 1363191 | NATURAL GAS |  | 83 | 0.09 | YES | 0 | 0 | 0 | 0 | 7 | 7 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 2023-03-24 16:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 83 | YES | 0 | 2023-03-24 17:00 |  |  |  | 2023-03-24 17:19 | 2023-03-24 17:19 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 35 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE TAPPING TEE | 1982 | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COSTS FOR ITEMS 2A-2D ARE STILL BEING DETERMINED. | 2.11 | 175 | 175 | 0 | 0 | 175 | 130.671077504725897920604914933837429112 | 175 | 14 | 4 | 11 | 7 | 0 | 18 | 7 | 53 | 53 | 60 | 192.619(A)(2) | 1982-04-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 9 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL DID NOT HAVE AN IMPACT ON THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JOHN TOUMEH | MANAGER DIMP LEAK SURVEY | jtoumeh@ugi.com | 717-675-4606 |  |  |  |  | PAM JOCSAK | VP EHS AND TECHNICAL SUPPORT | 484-824-5508 | pjocsak@ugi.com | PURSUANT TO THE NTSB'S FEB 22, 2024 FACTUAL RECORD PUBLICATION IN ITS WEST READING INVESTIGATION (ID PLD23LR002), UGI HEREBY PROVIDES A SUPPLEMENTAL UPDATE TO THIS INCIDENT REPORT. A SUPPLEMENTAL REPORT WILL BE FILED WHEN A CAUSE HAS BEEN DETERMINED AND THE NTSB ISSUES ITS FINAL REPORT ON THE MATTER. ON FRIDAY, MARCH 24, 2023, AT 4:55 P.M. EASTERN STANDARD TIME, A NATURAL GAS-FUELED EXPLOSION AND FIRE OCCURRED AT R. M. PALMER COMPANY (PALMER) CANDY FACTORY BUILDING 2 AT 17 SOUTH 2ND AVENUE IN WEST READING, PENNSYLVANIA. SEVEN EMPLOYEES WERE KILLED AND 11 PEOPLE WERE INJURED. UGI FIRST RESPONDERS BEGAN ARRIVING ONSITE AT 5:19 P.M AND ISOLATED THE DISTRIBUTION SYSTEM SUPPLYING NATURAL GAS TO THE AREA BY 6:15 P.M. MECHANICAL AND VISUAL EXAMINATION INDICATED THAT NATURAL GAS WAS LEAKING FROM A DUPONT ALDYL A SERVICE TEE THAT WAS INSTALLED IN 1982. UGI EXPOSED AND RETIRED THE SERVICE LINE THAT WAS CONNECTED TO THIS SERVICE TEE IN 2021 WHEN THE NATURAL GAS METER WAS RELOCATED FROM THE BASEMENT TO THE EXTERIOR OF BUILDING 2. PALMER OWNED SUBSURFACE INFRASTRUCTURE RAN UNDERNEATH THE PUBLIC RIGHT OF WAY ALONG CHERRY STREET, BETWEEN PALMER BUILDINGS 1 AND 2 AND INCLUDED A STEAM, CONDENSATE, AND SEVERAL HEATED CHOCOLATE PIPELINES. THE PALMER STEAM PIPE WAS LOCATED APPROXIMATELY 23.4 INCHES TO THE WEST AND 15.5 INCHES ABOVE THE 1982 RETIRED TEE (CENTER OF PIPE TO TOP OF TEE). THE STEAM PIPE LAID PERPENDICULAR TO THE GAS MAIN, WITH STEAM FLOWING FROM 77 S. 2ND AVE TO 17 S. 2ND AVE (FROM SOUTH TO NORTH). THE STEAM LINE WAS FOUND TO BE DEFORMED, CORRODED, AND CRACKED ALONG ITS EAST SIDE. THE STEAM LINE CRACK WAS MEASURED TO BE APPROXIMATELY 5-INCHES BY 2-INCHES AT THE 3 O'CLOCK POSITION ON THE STEAM PIPE. A PALMER MECHANIC INDICATED THAT ON THE DAY BEFORE THE ACCIDENT, A CHOCOLATE UNLOADER ENTERED THE MAINTENANCE SHOP AROUND 6:00 PM AND TOLD THE MECHANIC THAT HE SMELLED GAS AROUND THE MECHANIC'S CAR. SEVERAL EMPLOYEES WORKING THE SECOND SHIFT IN BUILDING 1 REPORTED THAT THEY SMELLED GAS ON THE DAY OF ACCIDENT. ONE EMPLOYEE REPORTED THAT SHE SMELLED GAS AS EARLY AS 2:58 P.M., AND AT 4 P.M. THREE EMPLOYEES REPORTED THE ODOR TO THE SECOND SHIFT SUPERVISOR BETWEEN 4:20-4:46 P.M. SOME OF THE EMPLOYEES REPORTED THAT THEY DID NOT FEEL THEY COULD EVACUATE FOR FEAR OF LOSING THEIR JOB. NO EVACUATION ORDER WAS GIVEN BY PALMER MANAGEMENT FOR BUILDINGS 1 AND 2 PRIOR TO THE EXPLOSION. UGI STATES THAT NO CALL WAS MADE TO THEM REGARDING THE SMELL OF GAS ODORANT ON THE DAY BEFORE OR DAY OF THE ACCIDENT. PART A.7 DOES NOT INCLUDE ESTIMATED GAS RELEASED UNINTENTIONALLY PRIOR TO IGNITION AS UGI HAS NO BASIS TO ESTIMATE GAS LOSS PRIOR TO IGNITION AS THE STARTING TIME OF THIS LEAK HAS NOT BEEN DETERMINED. PARTS A.10 AND A.22, HAVE NOT CHANGED SINCE INITIAL REPORTING. UGI WILL AMEND THIS SECTION IN ITS FINAL AND SUPPLEMENT REPORT PURSUANT TO THE RELEASE OF THE NTSB'S FINAL REPORT ON THIS MATTER. PART A.21.C WAS ESTIMATED BASED UPON A SERVICE TAP DIAMETER OF 0.807 INCHES TO ESTIMATE GAS CONSUMED BY THE SUBSEQUENT FIRE.
2024-05-31 11:04 | NO | NO | NO | 20230023 | 37981 | 2023-04-26 10:26 | ORIGINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2023-04-01 01:30 | PACIFIC | YES | 2023 | 205 JUNIPER DRIVE | MAMMOTH LAKES | MONO | CA | 93546 | 37.6355 | -118.9959 |  | YES |  | YES | [5 empty] | 2023-04-01 16:15 | 1363726 | 1364037 | PROPANE GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-04-01 01:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 0 | 2023-04-01 01:30 |  |  |  | 2023-04-01 02:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN | CLASS 2 LOCATION | 100000 | 100000 | 300 | 300 | 0 | 0 | 0 | 0 | ESTIMATED AMOUNT - COST UNKNOWN | 3 | 0 | 0 | 0 | 0 | 100300 | 42377.6752767527753 | 100300 | 0 | 0 | 27 | 0 | 0 | 1 | 0 | 0.51 | 0.51 | 10 | 192.619(A)(1) | 1980-07-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | ON 4/1/2023 AT APPROXIMATELY 01:30 AM LOCAL TIME MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS, THAT A SINGLE FAMILY RESIDENCE THAT HAD GAS SERVICE WAS ON FIRE. AT THAT TIME EMERGENCY RESPONDERS, SHUT OFF GAS SERVICE TO THE RESIDENCES AND SECURED THE SCENE. THE CAUSE OF THE FIRE IS UNCLEAR, ESTIMATED COSTS AND DAMAGES IS UNKNOWN. THIS INCIDENT IS UNDER INVESTIGATION, THIS FORM IS BEING SUBMITTED AS A PRECAUTIONARY MEASURE. | [47 empty] | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | bill.runyans@amerigas.com | 2564591078 |  | KYLE MUIR | kyle.muir@amerigas.com | 7067090195 | BILL L RUNYANS | FIELD SAFETY COMPLIANCE MANAGER | 2564591078 | bill.runyans@amerigas.com | ON 4/1/2023 AT APPROXIMATELY 01:30 AM LOCAL TIME MANAGEMENT WAS NOTIFIED BY EMERGENCY RESPONDERS, THAT A SINGLE FAMILY RESIDENCE THAT HAD GAS SERVICE WAS ON FIRE. AT THAT TIME EMERGENCY RESPONDERS, SHUT OFF GAS SERVICE TO THE RESIDENCES AND SECURED THE SCENE. THE CAUSE OF THE FIRE IS UNCLEAR, ESTIMATED COSTS AND DAMAGES IS UNKNOWN. THIS INCIDENT IS UNDER INVESTIGATION, THIS FORM IS BEING SUBMITTED AS A PRECAUTIONARY MEASURE.
2024-05-31 11:04 | NO | YES | NO | 20230024 | 39284 | 2023-05-03 16:47 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-04-04 15:21 | EASTERN | YES | 2023 | 7307 THORNAPPLE LAKE ROAD | NASHVILLE | BARRY | MI | 49073 | 42.6245 | -85.1473 | [6 empty] | YES |  |  | 2023-04-05 10:02 | 1364022 | 1364164 | NATURAL GAS |  | 4971 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-04-04 15:21 | YES | OPERATOR | 2023-04-05 10:00 | 2023-04-04 15:24 | 2023-04-05 09:30 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  | 66 | NO | YES | [6 empty] | YES | UNCASED | THORNAPPLE RIVER | UNKNOWN | BELOW WATER, PIPE ON OR ABOVE BOTTOM | INVESTOR OWNED |  | MAIN |  | 1950 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - LOW FREQUENCY |  | 0.219 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 18.8 |  | CLASS 1 LOCATION | 3800 | 3800 | 3995456 | 3995456 | 422 | 422 | 0 | 0 |  | 2.16 | 10737 | 10737 | 0 | 0 | 4010415 | 1697918.08302234282069784877126654064272 | 4010415 | 414 | 22 | 4002 | 0 | 0 | 4002 | 436 | 385 | 385 | 400 | 192.619(C) | 1969-11-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | RCA RESULTS INDICATE THAT LINE 1022F CROSSING THE THORNAPPLE RIVER FAILED DUE TO OVERSTRESS FROM EXTERNAL FORCES EXHIBITED DURING A FLOOD EVENT. ACCELERATED WATER FLOW AND DEBRIS APPLIED STRESS ONTO THE UNSECURED PIPE CREATING AN INITIAL FRACTURE AND LEAK THAT PROGRESSED INTO A FULL SEPARATION OVER APPROXIMATELY A 13-HOUR PERIOD. | YES |  |  |  | YES | FLOODING EVENT | [178 empty] | YES | [34 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON APRIL 4, 2023, AT APPROXIMATELY 15:21 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION OF A POSSIBLE NATURAL GAS LEAK ON THE PIPELINE THAT CROSSES THE THORNAPPLE RIVER NEAR 7307 THORNAPPLE LAKE ROAD NASHVILLE, (BARRY COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 15:24 HOURS. THE GSW CONFIRMED A LEAK INDICATION AT THE THORNAPPLE RIVER CROSSING ON A 6-INCH HIGH-PRESSURE, STEEL, SINGLE-FEED PIPELINE SERVING OVER FOUR THOUSAND DOWNSTREAM CUSTOMERS. A GAS DISTRIBUTION SUPERVISOR WAS NOTIFIED AND ARRIVED ONSITE TO ASSIST WITH THE RESPONSE. DUE TO EXTREME FLOODING CONDITIONS AND MINIMAL REMAINING DAYLIGHT, AN INITIAL RESPONSE PLAN WAS IMPLEMENTED TO CONTINUOUSLY MONITOR THE LEAK LOCATION. A CONTINGENCY PLAN ALSO WAS PREPARED FOR IMMEDIATE CONTAINMENT USING EMERGENCY VALVES TO ISOLATE THE AFFECTED SEGMENT SHOULD THE CONDITION WORSEN DURING THE NIGHT. GAS OPERATIONS AND GAS ENGINEERING ALSO EVALUATED AND ASSESSED THE SITUATION IN DEVELOPING A LONG-TERM REMEDIATION PLAN. THE FOLLOWING DAY, AN INCIDENT COMMAND STRUCTURE (ICS) WAS ACTIVATED BECAUSE OF THE POTENTIAL IMPACT TO CUSTOMERS IN HASTINGS, MI. THE REMEDIATION PLAN WAS FINALIZED, AND IMPLEMENTATION WAS ALREADY UNDERWAY WHEN OPERATIONS PERSONNEL DISCOVERED THE LEAK WAS WORSENING AND DUE TO AN ANTICIPATED TEMPERATURE DECREASE SERVICE LOSS FOR CUSTOMERS WAS LIKELY TO OCCUR. CONSEQUENTLY, ADDITIONAL COMMUNICATION WAS UNDERTAKEN WITH KEY STAKEHOLDERS AND CUSTOMERS NOTIFYING THEM OF THE POTENTIAL INTERRUPTION IN NATURAL GAS SERVICE. A HIGH-PRESSURE BYPASS WAS INSTALLED TO ALLOW FOR FASTER RESTORATION OF NATURAL GAS SERVICE TO IMPACTED CUSTOMERS ONCE THE RELEASE WAS CONTAINED. ON APRIL 6, 2023, GAS WAS SHUT-OFF AT THE LEAK LOCATION BY INSTALLING PRESSURE CONTROL FITTINGS AT THE EAST AND WEST SIDES OF THE LOCATION. CONCURRENT TO THE PRESSURE CONTROL WORK, MULTIPLE GSW'S WERE TURNING OFF AFFECTED CUSTOMERS' SERVICE-LINE VALVE PRIOR TO ADMITTING GAS BACK INTO THE SYSTEM. THE BYPASS WAS ACTIVATED AT APPROXIMATELY 07:21 HOURS. PURGING FROM AIR TO GAS OF THE PIPELINE WAS PERFORMED IN STAGES PRIOR TO TURNING SERVICE-LINE VALVES AND RELIGHTING CUSTOMERS. CONSTRUCTION FOR PERMANENT PIPELINE REPLACEMENT WAS ALSO UNDER WAY DURING THIS TIME. CUSTOMER RESTORATION STARTED ON APRIL 7, 2023, AND AS OF THIS REPORT'S DATE, SERVICE HAS BEEN RESTORED TO ALL IMPACTED CUSTOMERS OR THEY RECEIVED NOTIFICATION REQUESTING ACCESS TO THEIR PROPERTIES FOR SERVICE RESTORATION. WEEKLY RESTORATION STATUSES ARE PROVIDED TO THE MICHIGAN PUBLIC SERVICE COMMISSION STAFF. THE PERMANENT PIPELINE REPLACEMENT REQUIRED INSTALLATION OF APPROXIMATELY ONE THOUSAND FEET OF 6-INCH HIGH-PRESSURE STEEL PIPELINE. THE PIPELINE REPLACEMENT WAS COMPLETED, AND NORMAL OPERATIONS RESUMED ON APRIL 11, 2023, AT APPROXIMATELY 19:50 HOURS. THE ROOT CAUSE INVESTIGATION IDENTIFIED THE FAILURE OF THE PIPELINE CROSSING THE THORNAPPLE RIVER WAS A RESULT OF OVERSTRESS INDUCED BY EXTERNAL FORCES DURING THE FLOODING EVENT. THE COMBINATION OF ACCELERATED WATER FLOW AND DEBRIS IN THE WATERWAY EXERTED SIGNIFICANT PRESSURE ON THE UNSECURED PIPELINE, LEADING TO AN INITIAL FRACTURE THAT ULTIMATELY RESULTED IN COMPLETE SEPARATION.
2024-05-31 11:04 | NO | YES | NO | 20230025 | 38039 | 2023-05-04 15:40 | SUPPLEMENTAL FINAL | 31044 | LOWER VALLEY ENERGY, INC. | 236 N. WASHINGTON BLVD/P.O. BOX 188 | AFTON | WY | 83110 | 2023-03-25 02:56 | MOUNTAIN | YES | 2023 | 900 SNOW KING DR | JACKSON | TETON | WY | 83001 | 43.4698 | -110.7489 |  |  |  | YES | [5 empty] | 2023-03-25 07:10 | 1363085 | 1363250 | NATURAL GAS |  | 27 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-03-25 03:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27 | NO | 0 | 2023-03-25 05:30 |  |  |  | 2023-03-25 03:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | SERVICE RISER |  | 2006 | 2006 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | THREADS | 0.113 | [6 empty] | OTHER | [8 empty] | METER CAIN SHEARED OFF RIGHT AT THE METER | CLASS 2 LOCATION | 3000000 | 3000000 | 100 | 100 | 540 | 540 | 0 | 0 |  | 27 | 729 | 729 | 0 | 0 | 3001369 | 1268342.41955510315595190926275992438563 | 3001369 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(3) | 2006-05-05 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS ON A RESIDENTIAL METER | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | NO | [218 empty] | CRAIG COLES | DIRECTOR OF GAS OPERATIONS | ccoles@lvenergy.com | 307 885 6151 | 307 885 5787 |  |  |  | CRAIG COLES | DIRECTOR OF GAS OPERATIONS | 307 885 6151 | ccoles@lvenergy.com | ON MARCH 25TH 2023 LOWER VALLEY ENERGY WAS CALLED TO A HOUSE FIRE WHERE THE METER CAIN HAD BEEN BROKEN BY SNOW AND ICE FALLING OFF THE ROOF AND BREAKING IT. THE GAS IGNITED BY AN UNKNOW SOURCE. LOWER VALLEY WAS CALLED BY THE FIRE DEPARTMENT TO THE SCENE WHERE IT WAS DECIDED TO PUT THE FLAME OUT AND TURN THE VALVE OFF WHICH DID STOP THE FLOW OF GAS. THE SITUATION WAS CONTROLLED BY 6:30 AM THAT DAY. THE HOUSE WAS A TOTAL LOSS FROM THE FIRE. THERE WERE NO INJURIES AS NO ONE WAS HOME AT THE TIME OF THE FIRE.
2024-05-31 11:04 | NO | YES | YES | 20230026 | 38016 | 2023-05-05 13:02 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2023-04-06 14:59 | EASTERN | YES | 2023 | 2027 HENDRIX DR. | GROVE CITY | FRANKLIN | OH | 43123 | 39.9156 | -83.0429 |  |  | YES | [6 empty] | 2023-04-06 15:18 | 1364142 | 1364239 | NATURAL GAS |  | 66.4 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2023-04-06 12:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 66.3 | NO | 0 | 2023-04-06 12:53 |  |  |  | 2023-04-06 13:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1986 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES | 1 | PE 2306 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 70000 | 70000 | 800 | 800 | 4800 | 4800 | 0 | 0 |  | 5.04 | 335 | 335 | 0 | 0 | 75935 | 32191.8391939117937474480151228733459357 | 75935 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 48 | 48 | 60 | 192.619(A)(2) | 1996-08-24 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 48 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | A THIRD-PARTY FENCING EXCAVATOR DAMAGED A ONE-INCH PLASTIC SERVICE LINE WITH AN AUGER ATTACHED TO A SKID STEER. AFTER STRIKING THE SERVICE LINE THE SKID STEER OPERATOR BACKED UP SLIGHTLY AND A COWORKER BEGAN TO REMOVE SOIL FROM THE HOLE WHEN GAS IGNITED BURNING THE CONTRACTORS FACE AND HANDS. IN ADDITION, THE FIRE DAMAGED THE SKID-STEER. THE THIRD-PARTY FENCING EXCAVATOR CALLED IN A ONE CALL TICKET TO A BUILDING ONE STREET OVER. THE DAMAGE OCCURED AT A LOCATION WITHOUT A ONE CALL TICKET. THE ODORANT READING AT THE TIME OF THE INCIDENT WAS .42 AND DUE TO A SYSTEM ISSUE, I WAS UNABLE TO DOCUMENT THE READING IN SECTION E6. PLEASE CONSIDER THIS REPORT BOTH AND INITIAL AND FINAL REPORT. NO FURTHER REPORTS WILL BE FILED.
2024-05-31 11:04 | NO | YES | NO | 20230027 | 38242 | 2023-05-18 17:22 | SUPPLEMENTAL FINAL | 20050 | AMERENUE | 1901 CHOUTEAU | SAINT LOUIS | MO | 63103 | 2023-04-19 09:05 | CENTRAL | YES | 2023 | 106 STATE HWY 114 | ESSEX | STODDARD | MO | 63846 | 36.811 | -89.8615 | YES | [8 empty] | 2023-04-19 09:55 | 1365146 | 1365278 | NATURAL GAS |  | 33.28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-04-19 08:27 | ALLOWED TO BURN OUT |  | 33.28 | NO | 3 | 2023-04-19 09:05 |  |  |  | 2023-04-19 09:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | FITTING | [9 empty] | OTHER | [8 empty] | VEHICLE DROVE OVER A METER SET. THE UNION BROKE OFF ABOVE THE RISER VALVE. | CLASS 3 LOCATION | 450000 | 450000 | 1100 | 1100 | 65724 | 65724 | 0 | 0 | . | 0.94 | 31 | 31 | 0 | 0 | 516855 | 218386.0551970926536973459357277882797732 | 516855 | 21 | 0 | 161 | 0 | 0 | 161 | 21 | 14.98 | 15 | 18 | 192.619(A)(4) | 1998-05-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | SMALL TRUCK | ROADWAY | 15 | NO | [142 empty] | MARK BRANDT | MANAGER GAS COMPLIANCE AND PROGRAM MANAGEMENT | mbrandt2@ameren.com | 573-694-1794 |  | MARK BRANDT | mbrandt2@ameren.com | 573-694-1794 | PAM HARRISON | DIRECTOR MISSOURI GAS OPERATIONS | 573-619-3124 | pharrison@ameren.com | ON 4/19/2023, PRIOR TO 8:27AM A VEHICLE (VEHICLE 1) WAS PULLING OUT OF A PARKING LOT NEAR THE ESSEX ONE STOP CONVENIENCE STORE AND STRUCK AN ONCOMING VEHICLE (VEHICLE 2). VEHICLE 2 LOST CONTROL AND SLAMMED INTO THE GAS STATION WALL DRIVING OVER THE GAS METER, BREAKING THE GAS METER PIPING AT THE UNION ABOVE THE METER VALVE, CAUSING A LEAK. VEHICLE 2 CAME TO REST ON TOP OF THE BROKEN GAS PIPING. SHORTLY AFTER, THE GAS IGNITED LEADING TO A VEHICLE AND STRUCTURE FIRE. THE EXACT TIME OF IGNITION IS UNKNOWN. THE EXACT NUMBER OF INDIVIDUALS EVACUATED IS UNKNOWN, BUT IS ESTIMATED TO BE BETWEEN 3-5. AT 8:27 EMERGENCY RESPONSE PERSONNEL NOTIFIED THE AMEREN CALL CENTER OF THE FIRE. AT 8:30, AN AMEREN GAS FIRST RESPONDER WAS DISPATCHED. AT 9:05, THE FIRST AMEREN GAS PERSONNEL ARRIVED AT THE LOCATION. EMERGENCY RESPONSE PERSONNEL EXTINGUISHED THE STRUCTURE FIRE WHILE ALLOWING THE GAS FED FIRE TO BURN IN A CONTROLLED MANNER. AT 12:32, AMEREN PERSONNEL CLOSED AN EMERGENCY VALVE TO ISOLATE FLOW OF GAS TO SERVICE RISER. AT 12:48 THE FIRE BURNED OUT. AFTER VEHICLE 2 WAS REMOVED FROM THE SCENE, THE SERVICE WAS EXCAVATED AND PHYSICALLY ISOLATED FROM THE MAIN. AFTER WHICH, GAS SERVICE WAS RESTORED FOLLOWING ALL APPLICABLE STANDARD OPERATING PRACTICES. THE STRUCTURE AND VEHICLE 2 WERE TOTAL LOSSES. THE EXACT VALUE IS UNKNOWN, BUT IS ESTIMATED TO BE APPROXIMATELY $450,000.
2024-05-31 11:04 | NO | YES | YES | 20230028 | 39546 | 2023-06-13 13:39 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2023-05-02 10:00 | EASTERN | YES | 2023 | 26010 PENN STREET | INKSTER | WAYNE | MI | 48141 | 42.2854 | -83.2925 | [5 empty] | YES |  |  |  | 2023-05-02 10:40 | 1366173 | 1366323 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-05-02 10:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2023-05-02 10:00 | YES | OPERATOR | 2023-05-02 10:01 | 2023-05-02 10:00 | 2023-05-02 10:01 | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | EXPLOSION ORIGINATED IN HOME CRAWL SPACE |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1952 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CORROSION | [5 empty] | CLASS 3 LOCATION | 49000 | 49000 | 300 | 300 | 10000 | 10000 | 0 | 0 |  | 3.85 | 0 | 0 | 0 | 0 | 59300 | 25054.7970479704843 | 59300 | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 9.1 | 10 | 10 | 192.619(A)(1) | 1952-08-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 7 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | YES |  |  |  | YES | CORROSION APPEARS TO HAVE OCCURRED AT THE GROUND-TO-ATMOSPHERE TRANSITION AREA |  |  | YES |  |  |  | NO | [11 empty] | YES | YES | UNKNOWN |  | UNKNOWN | [19 empty] | 2022-07-22 | NO | [182 empty] | YES | YES | [43 empty] | MARINA DARLING | SUPERVISOR - CODES AND STANDARDS | marina.darling@dteenergy.com | 15868724760 |  |  |  |  | MARINA I. DARLING | SUPERVISOR - CODES AND STANDARDS | 15868724760 | marina.darling@dteenergy.com | A DTE CREW WAS IN THE PROCESS OF REPLACING THE SERVICE LINE TO 26010 PENN STREET, INKSTER, MI, 48141, SINCE 8:30 AM, WHEN THE HOUSE EXPLODED INJURING ONE (1) HOMEOWNER AND ONE (1) DTE GAS EMPLOYEE. THE INVESTIGATION DETERMINED THAT A LEAK OCCURRED AT A CORRODED SECTION OF THE 3/4-INCH SERVICE RISER IN THE CRAWL SPACE OF THE HOUSE DURING REMOVAL OF THE METER MANIFOLD ASSEMBLY. THE CORROSION APPEARS TO HAVE OCCURRED AT THE GROUND-TO-ATMOSPHERE TRANSITION AREA AND THE DISTURBANCE OF THE PIPING DURING REMOVAL CAUSED THE LEAK. EMPLOYEES WERE UNAWARE OF THE LEAKING GAS AS IT ACCUMULATED IN THE CRAWL SPACE AND IGNITED. A SOURCE OF IGNITION HAS NOT BEEN DETERMINED. ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY (PART A.7) AND ESTIMATED VOLUME OF GAS CONSUMED BY FIRE (PART A.21C) COULD NOT BE DETERMINED DUE TO UNKNOWN SIZE AND DURATION OF THE LEAK AND IS ASSUMED TO BE MINIMAL. NOTE: DTE MADE THE INITIAL REPORT TO THE NRC AT 10:40 AM, HOWEVER, WAS ON HOLD FOR 18 MINUTES, WHICH MATCHES THE NRC'S REPORT FOR INITIAL OPERATOR REPORT TIME TO NRC OF 10:58 AM.
2024-05-31 11:04 | NO | NO | NO | 20230029 | 38184 | 2023-06-16 16:06 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-05-20 10:29 | EASTERN | YES | 2023 | HARPER AVENUE & FIERZ STREET | CLINTON TOWN | MACOMB | MI | 48035 | 42.5674 | -82.8717 | [5 empty] | YES |  |  |  | 2023-05-20 19:29 | 1367814 | 1367873 | NATURAL GAS |  | 3360 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-05-20 10:29 | YES | OPERATOR | 2023-05-20 10:55 | 2023-05-20 10:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 4 | 9.6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 100491 | 100491 | 2435 | 2435 | 0 | 0 |  | 2.19 | 7358 | 7358 | 0 | 0 | 110284 | 48981.343292015158751141776937618147448 | 110284 | 1 | 0 | 1 | 0 | 0 | 1 | 1 | 55 | 54 | 60 | 192.619(A)(2) | 1969-10-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2023031501225 |  |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON MAY 20, 2023, AT APPROXIMATELY 10:29 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR THE INTERSECTION OF HARPER AVENUE AND FIERZ STREET, CLINTON TOWNSHIP (MACOMB COUNTY) MICHIGAN. THE GAS DISTRIBUTION SUPERVISOR WAS ONSITE AT APPROXIMATELY 10:55 HOURS AND A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:02 HOURS. THE GSW CONFIRMED A THIRD-PARTY CONTRACTOR DAMAGED A 4-INCH STEEL (MEDIUM PRESSURE) PIPELINE WHILE BORING TELECOMMUNICATION CONDUIT. THE GSW BEGAN MONITORING THE AREA FOR GAS MIGRATION AND SERVICE PERSONNEL MONITORED THE AREA UNTIL THE GAS WAS CONTAINED. POLICE AND FIRE PERSONNEL WERE ONSITE AND CLOSED THE ROAD TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. A DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 12:12 HOURS AND DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. BECAUSE THE PIPELINE DEPTH WAS GREATER THAN 6-FEET, SHORING EQUIPMENT WAS REQUIRED TO SAFELY ACCESS THE PIPELINE. THE DAMAGED SEGMENT WAS ISOLATED AT APPROXIMATELY 18:04 HOURS BY SQUEEZING THE 6-INCH S-MP PIPELINE TO THE NORTH AND SOUTH OF THE 4-INCH S-MP PIPELINE WHERE THE DAMAGE OCCURRED. ONCE GAS WAS CONTAINED, CONTROL FITTINGS WERE INSTALLED ON THE 6-INCH S-MP PIPELINE AND THE TWO SECTIONS USED DURING THE SQUEEZING OPERATION WERE REPLACED. THE SECTION OF THE 4-INCH S-MP PIPELINE WHERE THE INITIAL DAMAGE OCCURRED WAS REPLACED AND NORMAL OPERATIONS RESUMED ON MAY 21, 2023, AT APPROXIMATELY 10:45 HOURS. SERVICE RESTORATION FOR ALL IMPACTED CUSTOMERS BEGAN AFTER THE PIPELINE REPAIR.
2024-05-31 11:04 | NO | YES | NO | 20230030 | 38490 | 2023-06-26 21:38 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2023-05-26 12:10 | EASTERN | YES | 2023 | 29920 JAMESTOWN DRIVE | CHESTERFIELD TOWNSHIP | MACOMB | MI | 48051 | 42.6832 | -82.8084 |  | YES |  |  |  | YES |  |  |  | 2023-05-26 13:19 | 1368330 | 1368665 | NATURAL GAS |  | 15.09 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-05-26 10:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15.09 | NO | 2 | 2023-05-26 10:53 |  |  |  | 2023-05-26 11:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 140000 | 140000 | 3278 | 3278 | 14025 | 14025 | 0 | 0 |  | 4.5 | 68 | 68 | 0 | 0 | 157371 | 66512.7436819453382590491493383742911153 | 157371 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1981-07-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD PARTY DAMAGE. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2023052503098 |  |  | FACILITY OWNER | YES | YES | 21 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JENNIFER POND | SUPERVISOR OF CODES AND STANDARDS | jennifer.pond@semcoenergy.com | 8102422381 |  | ADAM DZIEDZIC | adam.dziedzic@semcoenergy.com | (810) 887-5027 | PHIL LENN | DIRECTOR OF OPERATIONS SUPPORT | (810) 887-5027 | phil.lenn@semcoenergy.com | ON 05/26/23, A GAS MAIN LOCATED AT 29920 JAMESTOWN DRIVE, CHESTERFIELD TWP, MI, WAS STRUCK BY A THIRD-PARTY EXCAVATOR WHILE ATTEMPTING TO FIX A LEAKING WATER LINE. THE CONTRACTOR THEN CALLED 911 AND BEGAN EVACUATING NEARBY RESIDENTS. ACCORDING TO THE CONTRACTOR, THE GAS LEAK IGNITED WITHIN APPROXIMATELY 5 MINUTES OF THE GAS MAIN HIT. THE FIRE THEN SPREAD TO THE HOME. SEMCO DISPATCH WAS NOTIFIED OF THE INCIDENT BY THE LOCAL POLICE DEPARTMENT AT 10:53 AM. SEMCO CREWS ARRIVED, AND ONCE LOCAL FIRE PERSONNEL SECURED THE SCENE, SEMCO CREWS SECURED THE 2" PLASTIC MAIN BY 12:09 PM. REPAIRS, PURGING, AND RE-ACTIVATION OF GAS MAINS WERE COMPLETED BY 05/26/23 22:38 PM. THE FOLLOWING MORNING 05/27/23 SEMCO CREWS BEGAN RELIGHTING 26 CUSTOMERS AT 08:00 AM AND COMPLETED THE RELIGHTS BY APPROXIMATELY 11:45 AM. UPON INVESTIGATION, THE EXCAVATOR DUG USING A MINI-EXCAVATOR WITHIN THE 4' CAUTION ZONE OF THE MARKED GAS LINES WITHOUT HAND EXPOSING, RESULTING IN DAMAGE TO THE GAS LINE AND A RELEASE OF GAS. IT WAS ALSO DETERMINED THAT ALTHOUGH THE MAIN AND SERVICE LINES FEEDING THE ADDRESSED HOUSE WERE MARKED ACCURATELY, A PORTION OF MAIN LOCATED TO THE WEST OF THE SERVICE LINE WAS NOT MARKED, DUE TO A MAP ERROR. ADDITIONALLY, THE CONTRACTOR HIT AN UNDERGROUND ELECTRICAL SERVICE LINE IN THE SAME EXCAVATION WHICH WAS LIKELY THE SOURCE OF IGNITION.
2024-05-31 11:04 | NO | YES | YES | 20230032 | 38962 | 2023-07-03 13:59 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2023-06-08 15:30 | PACIFIC | YES | 2023 | 15630 ALUM ROCK AVENUE | SAN JOSE | SANTA CLARA | CA | 95127 | 37.3859 | -121.8146 | YES | YES | [7 empty] | 2023-06-08 15:55 | 1369527 | 1369698 | NATURAL GAS |  | 716 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2023-06-08 03:00 | YES | OPERATOR | 2023-06-08 03:05 | 2023-06-08 03:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1925 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DISLODGMENT OF PLUG | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 4538 | 4538 | 4050 | 4050 | 0 | 0 | NO FACILITIES WERE DAMAGED DUE TO THIS INCIDENT, NOR WAS RESTORATION REQUIRED. | 9.2 | 6587 | 6587 | 0 | 0 | 15175 | 8546.968582370134385731568998109640831758 | 15175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 54 | 60 | 192.619(A)(3) | 1966-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ROSA DUENAS | PROGRAM MANAGER | r1dj@pge.com | [5 empty] | SUSIE RICHMOND | GAS REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON THURSDAY, JUNE 8, 2023, PG&E INCIDENT ON-DUTY PERSONNEL CONFIRMED THAT A RELEASE OF GAS FROM A PIPELINE RESULTED IN AN INJURY NECESSITATING IN-PATIENT HOSPITALIZATION. THE PG&E EMPLOYEE WAS ADMITTED TO THE HOSPITAL, WAS UNDER OBSERVATION AFTER SUFFERING FACIAL INJURIES, AND IS IN STABLE POSITION. THE INJURIES OCCURRED WHILE WORKING ON A 4-INCH STEEL DISTRIBUTION MAIN AND INVOLVED THE DISLODGMENT OF A PLUG DURING A SCHEDULED LEAK REPAIR. LOCAL FIRE AND POLICE DEPARTMENT PERSONNEL RESPONDED, AND THE EMPLOYEE WAS TRANSPORTED FOR TREATMENT IN AN AMBULANCE. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO A RELEASE OF GAS RESULTING IN AN INJURY REQUIRING HOSPITAL ADMISSION AND AT LEAST ONE OVERNIGHT STAY. PER THE INVESTIGATION REPORT THE DIRECT CAUSE FOR THIS INCIDENT IS INADEQUATE THREAD ENGAGEMENT DUE TO DEBRIS. A LACK OF PROFICIENCY COMBINED WITH THE FAILURE TO IDENTIFY AN AOC LED TO THE DISLODGEMENT OF THE PLUG. THE CE TEAM COMPLETED A HAZARD BARRIER ANALYSIS OF THE EXPECTED CONTROLS AROUND THE WORK TASK, AS WELL AS UTILIZED THE HUMAN FACTORS ANALYSIS AND CLASSIFICATION SYSTEM TO DETERMINE HUMAN PERFORMANCE PRECURSORS THAT MAY HAVE CONTRIBUTED TO THE EVENT. ON JUNE 7, 2023, PG&E CREWS RESPONDED TO A GRADE 3 LEAK AT 15630 ALUM ROCK AVE. IN SAN JOSE. AS PART OF THE LEAK REPAIR PROCESS, TWO 4" MUELLER LINE STOPPER FITTINGS WERE SUCCESSFULLY INSTALLED, AND LEAK REPAIRS WERE PERFORMED. UPON COMPLETION OF THE LEAK REPAIRS, WORKERS WERE IN THE PROCESS OF INSTALLING AND TIGHTENING TWO COMPLETION PLUGS WITH A WRENCH WHEN A FAILURE OF THE PRESSURE BOUNDARY WAS EXPERIENCED. AT APPROXIMATELY 0300AM ON JUNE 8TH, THE FINAL COMPLETION PLUG HAD BEEN INSTALLED AND WAS BEING TIGHTENED WITH A WRENCH WHEN IT INADVERTENTLY BLEW OUT OF THE FITTING AND EXPOSED TWO COWORKERS TO A DIRECT STREAM OF GAS AT DISTRIBUTION PRESSURE. THIS RESULTED IN AN UNCONTROLLED RELEASE OF GAS WITHOUT IGNITION CAUSING INJURIES TO ONE COWORKER IN THE FORM OF METAL SHAVINGS LODGED IN THEIR FACE AND EYES. THE INJURED COWORKER WAS ALSO POTENTIALLY STRUCK IN THE HEAD WITH EITHER A TIGHTENING WRENCH AND OR THE COMPLETION PLUG WHEN THE COMPLETION PLUG BECAME DISLODGED. TWO COWORKERS WORKING IN THE TRENCH WERE EVACUATED AND THE CREWS WERE MOVED A SAFE DISTANCE FROM THE GAS STREAM. EMERGENCY RESPONDERS ARRIVED AND INJURED COWORKER WAS TRANSPORTED TO A LOCAL HOSPITAL FOR TREATMENT. THE CAUSE EVALUATION (CE) TEAM CONDUCTED INTERVIEWS WITH THE INJURED COWORKER (ICW) ALONG WITH OTHER COWORKERS (CW1, CW2) WHO WERE AT THE WORK SITE AT THE TIME OF INCIDENT. THE CE TEAM COMPLETED A HAZARD BARRIER ANALYSIS OF THE EXPECTED CONTROLS AROUND THE WORK TASK TO DETERMINE HUMAN PERFORMANCE PRECURSORS THAT MAY HAVE CONTRIBUTED TO THE EVENT. AFTER REVIEWING THE COLLECTED INFORMATION, DOCUMENTATION AND RELATED FACTORS, THE DIRECT CAUSE FOR THIS INCIDENT IS INADEQUATE THREAD ENGAGEMENT DUE TO DEBRIS. THIS IS BASED ON THE SME EVALUATION OF THE EQUIPMENT POST INCIDENT WHERE MINIMAL THREAD DAMAGE IS PRESENT, AND THE EQUIPMENT PERFORMED AS DESIGNED. THE FIRST APPARENT CAUSE (AC1) IS WORKERS WERE QUALIFIED BUT NOT PROFICIENT WITH THE MUELLER LINE STOPPER PROCESS CONTAINED IN UTILITY PROCEDURE. THE SECOND APPARENT CAUSE (AC2) IS LESS THAN ADEQUATE (LTA) JOB PREPARATION PROVIDED TO WORKERS. A LACK OF PROFICIENCY COMBINED WITH THE FAILURE TO IDENTIFY AN AOC LED THEM TO FURTHER TIGHTEN THE COMPLETION PLUG, WHICH DISLODGED. ADDITIONAL DETAILS AND RESULTS OF THE CAUSAL ANALYSIS ARE DOCUMENTED IN THE CAUSE EVALUATION REPORT THAT HAS PREVIOUSLY BEEN SUBMITTED TO PHMSA AND CPUC.
2024-05-31 11:04 | NO | YES | NO | 20230033 | 38576 | 2023-07-07 14:07 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2023-06-07 09:31 | EASTERN | YES | 2023 | STATE ROAD 31 & STATE ROAD 80 | FT.MYERS | USA | FL | 33905 | 26.7014 | -81.7602 | [7 empty] | YES | LOWERED PRESSURE AT SUPPLYING GATE FROM 350 PSI TO 250 PSI. | 2023-06-07 10:05 | 1369358 | 1369590 | NATURAL GAS |  | 4797 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-06-07 02:00 | YES | OPERATOR | 2023-06-07 06:46 | 2023-06-07 02:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 162 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2000 | UNKNOWN |  |  |  |  | 8 | API 5L X52 | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 354400 | 354400 | 37000 | 37000 | 0 | 0 |  | 9 | 43173 | 43173 | 0 | 0 | 434573 | 197607.0388674586482052930056710775047259 | 434573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 350 | 476 | 192.619(A)(2) | 2013-02-15 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | OTHER | WATER DEPARTMENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATOR DAMAGE TO FACILITY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DRILLING | ENGINEERING/SURVEYING | YES | 132300796 |  |  | FACILITY OWNER | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | 407-420-6617 |  |  |  |  | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 407-420-6667 | rharris@tecoenergy.com | ON JUNE 7, 2023, AT APPROXIMATELY 02:00 HOURS, PGS WAS NOTIFIED THAT A THIRD-PARTY CONTRACTOR HAD STRUCK A GAS PIPELINE AT STATE ROAD 31 & STATE ROAD 80 IN FT MYERS, FLORIDA. RESPONDING CREWS WERE DISPATCHED AND ARRIVED TO FIND A SOIL SAMPLING RIG WAS THE CAUSE OF THE DAMAGED PIPELINE AND ESCAPING GAS. AN ASSESSMENT WAS MADE OF THE SCENE, INCLUDING THE ABILITY TO SAFELY MANAGE THE SITE. AN EVALUATION OF OPTIONS FOR THE ONE-WAY-FED 8" STEEL PIPELINE, CONCLUDED THAT THE PIPELINE WOULD REMAIN IN SERVICE TO CONTINUALLY SUPPLY APPROXIMATELY 25,300 CUSTOMERS DOWNSTREAM, UNTIL A BYPASS COULD BE INSTALLED TO ISOLATE THE DAMAGED SECTION OF PIPELINE. OVER THE FOLLOWING DAYS, CREWS WORKED TO INSTALL 750' OF 8" STEEL BYPASS AROUND THE DAMAGED SECTION OF PIPELINE. THE BYPASS WAS ABLE TO ISOLATE THE DAMAGED SECTION OF PIPELINE ON JUNE 10, 2023, AT 13:25, AND COMPLETE STOPPAGE OF THE ESCAPING GAS. A ROOT CAUSE INVESTIGATION WAS CONCLUDED AND FOUND TWO PRIMARY CONTRIBUTING FACTORS: 1. THE GAS PIPELINE IN THE LOCATION OF THIS INCIDENT WAS/IS CLASSIFIED AS A "HIGH PRIORITY SUBSURFACE INSTALLATION (HPSI)" BY PGS THROUGH THE POSITIVE RESPONSE CODE OF "2C". PER FLORIDA STATUE CHAPTER 556 HPSI REQUIRES SPECIAL PROCEDURES WHEN DIGGING NEAR AN HPSI. WITH THIS CLASSIFICATION, BEFORE ANY DIGGING OR DEMOLITION, THE EXCAVATOR MUST NOTIFY THE MEMBER OPERATOR OF THE START DATE AND TIME OF THE EXCAVATION. IN ACCORDANCE WITH F.S. 556, THIS HPSI WAS MARKED BY PGS, AND A RESPONSE COMMUNICATED BACK TO THE REQUESTING EXCAVATOR USING A 2C (MARKED WITH EXCEPTIONS: HIGH PROFILE SUBSURFACE INSTALLATION IN CONFLICT). THE INSTRUCTIONS PROVIDED AND COMMUNICATED TO THE EXCAVATOR INDICATED, "EXCAVATOR MUST NOTIFY THE MEMBER OPERATOR OF THE EXCAVATION OR DEMOLITION START DATE AND TIME" WHICH THE EXCAVATOR FAILED TO DO. IN ADDITION, PEOPLES GAS ALSO SENT AN E-MAIL TO THE EXCAVATOR NOTIFYING THE EXCAVATOR ABOUT THE HPSI AND REQUESTING THE START DATE AND TIME. THE FAILURE BY THE EXCAVATOR TO NOTIFY PGS OF THE TIMING OF THEIR EXCAVATION AND THE SPECIFIC LOCATION DID NOT ALLOW PGS TO GIVE ADDITIONAL LOCATION INFORMATION AND SPECIFICATIONS RELATED TO THE PIPELINE IDENTIFIED AS "IN CONFLICT". THE FAILURE ALSO PREVENTED THE POSSIBILITY OF A PEOPLES GAS LOCATOR BEING ON-SITE DURING THE EXCAVATION. 2. THE DEPTH OF THE PIPELINE AT THE DAMAGED LOCATION WAS OVER THIRTEEN FEET DEEP. WHEN PGS' LOCATOR PERFORMED THE INITIAL LOCATE MARKING, THE LOCATE SIGNAL UNKNOWINGLY JUMPED OFF THE GAS PIPELINE ONTO AN ADJACENT TELECOMMUNICATION FACILITY. THIS CAUSED THE LOCATE MARKINGS TO VEER OFF THE GAS PIPELINE BY APPROXIMATELY 36" TO 48" AT THE DAMAGED LOCATION.
2024-05-31 11:04 | NO | YES | NO | 20230034 | 38874 | 2023-07-11 17:38 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-06-12 14:35 | CENTRAL | YES | 2023 | HIGHWAY 108 AT BAYOU DINDE | SULPHUR | CALCASIEU | LA | 70665 | 30.2031 | -93.3253 | YES | [8 empty] | 2023-06-12 14:35 | 1369874 | 1369973, 1370823 | NATURAL GAS |  | 384.72 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-06-09 13:36 | YES | OPERATOR | 2023-06-09 20:56 | 2023-06-09 13:36 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDER WATERWAY | 48 | NO | YES | [6 empty] | YES | UNCASED | BAYOU DINDE | 13 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | INVESTOR OWNED |  | MAIN |  | 1982 | 1981 |  |  |  |  | 6 | API 5L GRADE B | JONES AND LAUGHLIN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.28 | [6 empty] | LEAK |  |  | OTHER | NOT EXCAVATED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 1213000 | 1213000 | 20594 | 20594 | 12540 | 12540 | BOOM RENTAL TO CONTAIN AREA FOR MONITORING. | 3.7 | 1423 | 1423 | 0 | 0 | 1247557 | 527565.6532341883930782344045368620037807 | 1247557 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 430 | 430 | 500 | 192.619(A)(2) | 1982-06-17 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | REPLACED MAIN AND ABANDONED STEEL MAIN IN PLACE. LOCATION OF LEAK IS UNDER WATER CROSSING AND WAS NOT VERIFIED. DECISION WAS MADE NOT TO REMOVE PIPE DUE TO EXCESSIVE COSTS AND ENVIRONMENTAL CONCERNS. | [45 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 | 337-373-1520 | DOUGLAS BOUDREAUX JR | douglas.boudreauxjr@centerpointenergy.com | 337-475-6362 | DOUGLAS BOUDREAUX JR | REGION OPERATIONS DIRECTOR | 337-475-6362 | douglas.boudreauxjr@centerpointenergy.com | REPORTED INDICATION OF LEAK ON FRIDAY JUNE 9, 2023. AFTER INITIAL INVESTIGATION AND SQUEEZING 2" MAIN, IT WAS DETERMINED THAT LEAK WAS PROBABLE ON 6" STEEL MAIN. MORE INVESTIGATION REVEALED THAT WE WOULD HAVE TO BORE IN NEW PIPE TO REPLACE LEAKING FACILITY. IT WAS THEN DISCOVERED THAT COST WOULD EXCEED REPORTABLE CRITERIA AND A CALL TO THE NRC WAS PLACED ON MONDAY JUNE 12, 2023 AT 14:35 PM CENTRAL TIME. ONGOING REPAIRS AND 24 HOUR MONITORING CONTINUED UNTIL WEDNESDAY JUNE 21, 2023 WHEN INDICATIONS REVEALED THAT LEAK MAY BE GETTING WORSE AND A DECISION WAS MADE TO TURN SYSTEM OFF. SYSTEM WAS COMPLETELY PURGED @ 1:20 AM THURSDAY JUNE 22, 2023. REPAIRS WERE COMPLETE AND SYSTEM RETURNED TO SERVICE ON FRIDAY JUNE 23, 2023.
2024-05-31 11:04 | NO | YES | YES | 20230035 | 38513 | 2023-07-14 09:26 | SUPPLEMENTAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-06-14 18:12 | CENTRAL | YES | 2023 | 1025 W LOOP 820 N | FORT WORTH | TARRANT | TX | 76108 | 32.7782 | -97.4755 | [5 empty] | YES |  |  |  | 2023-06-14 19:54 | 1370100 | 1370268 | NATURAL GAS |  | 88 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-06-14 18:12 | OPERATOR/CONTRACTOR |  | 88 | NO | 0 | 2023-06-14 18:27 |  |  |  | 2023-06-14 19:03 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | 2005 | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | 18500 | 18500 | 7897 | 7897 | 5359 | 5359 | 0 | 0 |  | 6.4084 | 564 | 564 | 0 | 0 | 32320 | 13838.3371675304679355841209829867674858 | 32320 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 29 | 29 | 60 | 192.619(A)(1) | 2006-06-20 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 30 | YES | YES | [141 empty] | STEVE KLEIN | FIELD SUPERVISOR | william.klein@atmosenergy.com | 469-261-2011 |  | STEVE KLEIN | william.klein@atmosenergy.com | 469-261-2011 | JEFF KNIGHTS | SR. V.P. TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON JUNE 14, 2023, AT APPROXIMATELY 6:12 PM, AN ATMOS ENERGY SERVICE TECH RECEIVED A PHONE CALL FROM DISPATCH INFORMING HIM OF A VEHICLE STRIKING A METER. UPON ARRIVAL AT THE SITE AT APPROXIMATELY 6:27 PM, THE TECH CONFIRMED THE ADDRESS WAS 1025 W LOOP 820 N. THE GAS METER HAD BEEN STRUCK BY A VEHICLE, AND THE FIRE DEPARTMENT WAS PRESENT AT THE SITE WHEN THE TECH ARRIVED. THE POLICE REPORT STATES: "[THE VEHICLE] STRUCK TWO METAL POST[S] AND A NATURAL GAS PIPELINE. [THE VEHICLE] CAME TO REST ON TOP OF THE NATURAL GAS PIPELINE. THE NATURAL GAS PIPELINE RUPTURED AND BEGAN LEAKING NATURAL GAS. [THE VEHICLE] AND THE LEAKING NATURAL GAS CAUGHT FIRE." THE TECH REQUESTED ADDITIONAL OPERATOR RESOURCES. A CONSTRUCTION CREW ARRIVED AT APPROXIMATELY 7:03 PM. TO ELIMINATE THE GAS FLOW, THE CONSTRUCTION CREW SQUEEZED OFF THE 6-INCH POLY MAIN AT APPROXIMATELY 8:03 PM. TO RESTORE SERVICE, THE STATION WAS REBUILT IN A DIFFERENT LOCATION, AND SERVICE WAS RESTORED AT 2:15 PM ON JUNE 16, 2023.
2024-05-31 11:04 | NO | YES | NO | 20230036 | 38450 | 2023-07-20 16:44 | SUPPLEMENTAL | 32074 | SUMMIT NATURAL GAS OF MISSOURI | 116 CHIEFS COURT | BRANSON | MO | 65616 | 2023-06-27 17:30 | CENTRAL | YES | 2023 | WEST 4TH STREET | MOUNTAIN GROVE | WRIGHT | MO | 65711 | 37.1318 | -92.2638 |  | YES | [7 empty] | 2023-06-27 17:35 | 1371439 | 1371439 | NATURAL GAS |  | 152 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-06-26 17:50 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 6 | 2023-06-26 17:35 | YES | OPERATOR | 2023-06-26 17:45 | 2023-06-26 17:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 72 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 2 | ASTM D2513 - SDR 11 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 250000 | 250000 | 4500 | 4500 | 15000 | 15000 | 0 | 0 |  | 10.529 | 1600 | 1600 | 0 | 0 | 271100 | 115060.9431566905669952741020793950850662 | 271100 | 3 | 0 | 3 | 0 | 0 | 3 | 3 | 38 | 38 | 50 | 192.619(A)(1) | 1995-05-15 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.6 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY MECHANICAL DAMAGE OF BLIND BORING | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 231690282 |  |  | FACILITY OWNER | YES | YES | 26 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | JORDAN SLAYTON | OPERATIONS MANAGER | jslayton@summitnaturalgas.com | 417-349-0512 |  | JORDAN SLAYTON | jslayton@summitnaturalgas.com | 417-349-0512 | MITCH PEBLEY | DIRECTOR OF OPERATIONS - MISSOURI | 720-981-2116 | mpebley@summitutilities.com | ON JUNE 26TH, 2023, A&A CABLE WAS INSTALLING A NEW FIBER OPTIC LINE IN MOUNTAIN GROVE, MISSOURI. A&A WAS SUBCONTRACTING FOR MASTEC DOING FIBER INSTALLATIONS. A&A WAS BLIND BORING APPROXIMATELY 300 FEET, CROSSING MULTIPLE NATURAL GAS LINES, COMMUNICATIONS LINES, A SEWER MAIN, AND A WATER MAIN WITHOUT EXPOSING OR POTHOLING ANY OF THE UTILITIES BEFORE EXCAVATION TOOK PLACE. DURING THIS BLIND BORE SHOT A 2' PE NATURAL GAS MAIN OPERATED BY SUMMIT NATURAL GAS WAS STRUCK. THE GAS LINE WAS LOCATED ACCURATELY BY A SNGMO TECHNICIAN UNDER THE LOCATE REQUEST NUMBER 231690282. ONCE THE GAS LINE WAS STRUCK BY THE BORING MACHINE THE NATURAL GAS MIGRATED FOLLOWING THE PATH OF A SEWER DRAIN AND ENTERED AN EMPTY DETACHED GARAGE / WASH BAY OWNED AND OPERATED BY CRAIG HURT FUNERAL HOME. THE GARAGE CONTAINED A HANGING STYLE FURNACE WITH A STANDING PILOT. ONCE AN ADEQUATE VOLUME OF GAS HAD ENTERED THE STRUCTURE TO REACH THE LEL THE GAS IGNITED, AND A HARD IGNITION AND FIRE WAS THE RESULT. THE LACK OF DEBRIS FIELD AND REVIEW OF VIDEO INDICATED THERE WAS NO SUDDEN AND VIOLENT RELEASE OF ENERGY CONSTITUTING AN EXPLOSION. APPROXIMATELY 152 MCF OF NATURAL GAS WAS LOST DUE TO THE RUPTURE OF THE GAS MAIN. TWO VEHICLES AND OTHER PRIVATELY OWNED MATERIALS WERE LOST IN THE SUBSEQUENT FIRE IN THE GARAGE. THE STRUCTURE AND CONTENTS WERE A TOTAL LOSS.
2024-05-31 11:04 | NO | YES | YES | 20230038 | 38430 | 2023-07-25 12:06 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2023-06-26 08:30 | CENTRAL | YES | 2023 | 10412 PACIFIC ST | OMAHA | DOUGLAS | NE | 68114 | 41.2493 | -96.0763 |  |  |  | YES | [5 empty] | 2023-06-26 13:30 | 1371294 | 1371476 | NATURAL GAS |  | 0.1 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2023-06-26 08:30 | OPERATOR/CONTRACTOR |  | 0.1 | NO | 0 | 2023-06-26 08:30 | YES | OPERATOR | 2023-06-26 08:40 | 2023-06-26 08:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | OPERATOR OWNED | SERVICE VALVE |  | 1973 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.133 | [6 empty] | OTHER | [8 empty] | RESIDUAL GAS, AFTER SERVICE VALVE WAS REPLACED AND GAS WAS OFF. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 200 | 200 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 200 | 84.5018450184502 | 200 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 60 | 60 | 60 | 192.619(A)(3) | 1973-09-06 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS NOT RELATED TO NOR IDENTIFIABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | DURING SERVICE VALVE REPLACEMENT, ENVIRONMENTAL CONDITIONS ALLOWED FOR RESIDUAL GAS TO BE IGNITED. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | TYSON ROBARDS | CLAIMS ADJUSTER | tyson_robards@mudnebr.com | 4025047108 |  | TYSON ROBARDS | tyson_robards@mudnebr.com | 4025047108 | TYSON ROBARDS | CLAIMS ADJUSTER | 4025047108 | tyson_robards@mudnebr.com | FOLLOWING A SERVICE VALVE REPLACEMENT, ENVIRONMENTAL CONDITIONS ALLOWED FOR RESIDUAL GAS TO BE IGNITED AND RESULTED IN BURNS ON TWO EMPLOYEES. NOTE - FOR QUESTION A4 THE DISTRICT USED 8:30 AM AT THE DIRECTION OF PHMSA. THIS WAS NOT THE TIME THAT THE INCIDENT BECAME REPORTABLE. THAT TIME WAS WHEN THE EMPLOYEE WAS HOSPITALIZED WHICH OCCURED AT 13:30. NOTE - FOR QUESTIONS A7 & A21 THE DISTRICT USED 0.1 AT THE DIRECTION OF PHMSA. ALL GAS RELEASED PRIOR TO THIS INCIDENT WAS INTENTIONAL.
2024-05-31 11:04 | NO | YES | NO | 20230039 | 38330 | 2023-07-27 13:14 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2023-06-27 16:25 | EASTERN | YES | 2023 | GRANVILLE ST. AND SARATOGA AVE. | NEWARK | LICKING | OH | 43055 | 40.0663 | -82.4178 | YES | [8 empty] | 2023-06-27 17:09 | 1371435 | 1371598 | NATURAL GAS |  | 1813.8 | 17 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 200 | 2023-06-27 16:25 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-06-26 10:00 | 2023-06-26 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 7 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 2.4 | [6 empty] | MECHANICAL PUNCTURE | 6 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 279186 | 279186 | 2800 | 2800 | 0 | 0 |  | 5.04 | 9142 | 9142 | 86 | 86 | 291214 | 126032.1589366555509774933837429111531191 | 291214 | 18 | 0 | 793 | 0 | 0 | 200 | 0 | 45 | 45 | 55 | 192.619(A)(3) | 1969-07-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | MILLING EQUIPMENT | MILLING | YES | A317201755 | OHIO 811 |  | CONTRACT LOCATOR | YES | YES | 75 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | ON JUNE 26, 2023, A ROADWAY MILLING CONTRACTOR DAMAGED AN 8" BARE STEEL MAIN THAT HAD BEEN IMPROPERLY LOCATED BY COLUMBIA'S SECOND-PARTY LOCATOR. THE MAINLINE WAS SHUT OFF FOR SAFETY RESULTING IN AN 811-CUSTOMER OUTAGE. THE FOLLOWING DAY, COLUMBIA BEGAN CALCULATING THE COST OF RESTORATION TO THESE 811 CUSTOMERS AND DETERMINED THAT THE COST EXCEEDED THE REPORTABLE CRITERIA ESTABLISHED IN 49 CFR PART 191.3. THEREFORE, COLUMBIA PROMPTLY REPORTED THIS EVENT WHEN THE CRITERIA WAS MET. PLEASE CONSIDER THIS A FINAL REPORT.
2024-05-31 11:04 | NO | YES | NO | 20230040 | 38350 | 2023-08-03 11:44 | ORIGINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2023-07-03 12:21 | CENTRAL | YES | 2023 | 3027 LINCOLN BLVD. | OMAHA | DOUGLAS | NE | 68131 | 41.2686 | -95.958 |  |  |  | YES | [5 empty] | 2023-07-03 13:56 | 1372035 | 1372153 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-07-03 12:21 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 8 | 2023-07-03 12:25 |  |  |  | 2023-07-03 12:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | POLITICAL SUBDIVISION-STATE NEBRASKA | INSIDE METER/REGULATOR SET |  | 2012 | 2012 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | COATED STEEL | [9 empty] | OTHER | [8 empty] | UNKNOWN AT THIS TIME | CLASS 3 LOCATION | 350000 | 350000 | 12000 | 12000 | 3000 | 3000 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 365000 | 154215.867158671615 | 365000 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0.25 | 0.25 | 1 | 192.619(A)(3) | 1900-08-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 55 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CONTAINED TO THE SINGLE RESIDENCE | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | mike_conrad@mudnebr.com | 4025047165 |  | MICHAEL CONRAD | mike_conrad@mudnebr.com | 4025047165 | MICHAEL CONRAD | SENOR CLAIMS INVESTIGATOR | 4025047165 | mike_conrad@mudnebr.com | ON JULY 3,2023 AT APPROXIMATELY 1221HRS THE METROPOLITAN UTILITIES DISTRICT (DISTRICT) WAS NOTIFIED BY THE OMAHA FIRE DEPARTMENT (OFD) OF AN EXPLOSION AND WORKING HOUSE FIRE AT 3027 LINCOLN BLVD., OMAHA NEBRASKA. DISTRICT PERSONNEL ARRIVED AND CUT OFF THE GAS TO THE RESIDENCE. THERE WAS A POSSIBILITY NATURAL GAS CONTRIBUTED TO THIS INCIDENT/LOSS BUT THERE WAS NO DETERMINATION MADE AT THIS TIME. THE EXACT CAUSE OF THE FIRE HAS NOT BEEN DETERMINED. ON THE DAY OF THE LOSS, DISTRICT PERSONNEL PERFORMED A GAS LEAK SURVEY AND AN ODORANT TEST OF THE GAS DISTRIBUTION AND SERVICE LINES IN THE AREA. THE GAS LEAK SURVEY SHOWED NO ISSUES WITH THE GAS DISTRIBUTION LINE OR ANY CONNECTING SERVICES. THE ODORANT TESTS INDICATED SUFFICIENT ODORANT AT ALL TEST LOCATIONS IN THIS AREA. ON MONDAY AUGUST 7,2023 THERE IS A SCHEDULED COMBINED INVESTIGATION OF INTERESTED PARTIES AT THIS LOCATION TO INVESTIGATE FURTHER.
2024-05-31 11:04 | NO | YES | NO | 20230041 | 38369 | 2023-08-09 13:34 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-07-14 20:17 | PACIFIC | NO | 2023 | 343 N. LIMA STREET | SIERRA MADRE | PASADENA | CA | 91024 | 34.168 | -118.06 | [7 empty] | YES | INSTALLED/WELDED 2-2" TOP HALVE PRESSURE CONTROL FITTINGS. | 2023-07-14 20:17 | 1373115 | 48hr update NRC#1373261 | NATURAL GAS |  | 464 | 0.05 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-07-14 06:05 | NO |  |  | 2023-07-14 06:26 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1956 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | A WATER MAIN CROSSING OVER A SOCALGAS GAS MAIN BORED A HOLE INTO THE GAS MAIN AND FILLED THE NATURAL GAS MAIN WITH WATER. GAS PRESSURE WAS OVERCOME BY WATER PRESSURE. | CLASS 3 LOCATION | 0 | 0 | 6367 | 6367 | 233048 | 233048 | 0 | 0 |  | 6 | 2784 | 2784 | 0 | 0 | 242199 | 103233.8362955935983067769376181474480151 | 242199 | 19 | 0 | 652 | 0 | 0 | 645 | 26 | 42 | 42 | 50 | 192.621 M | 1956-05-15 | PRESSURE DID NOT EXCEED MAOP | OTHER | SELF SEASONED |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER MAIN LEAK CAUSED DAMAGED TO NATURAL GAS PIPELINE. | [136 empty] | YES | [17 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 07/14/2023 SOCALGAS CREWS RESPONDED TO AN UNDER-PRESSURE CONDITION AT 343 N. LIMA STREET, SIERRA MADRE, PASADENA. ON INVESTIGATION COMPLETED TO DATE REGARDING THE UNDER-PRESSURE CONDITION, SOCALGAS IDENTIFIED A LEAKING 6-INCH WATER MAIN AT THE CROSS POINT OF A 2" STEEL GAS MAIN THAT BORE A HOLE INTO THE GAS MAIN AND FILLED THE GAS MAIN WITH WATER, THE GAS PRESSURE WAS OVERCOME BY THE WATER PRESSURE, AFFECTING MULTIPLE SERVICES AND THE MAIN. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO UNDER-PRESSURE. THIS WAS REPORTED TO THE DOT DUE TO GAS RELEASE AND DAMAGE EXCEEDING $139,700.
2024-05-31 11:04 | NO | YES | NO | 20230042 | 38400 | 2023-08-15 14:41 | ORIGINAL | 18584 | SPRINGFIELD, CITY UTILITIES OF | 301 E. CENTRAL | SPRINGFIELD | MO | 65802 | 2023-07-17 11:25 | CENTRAL | YES | 2023 | 5012 S. CHARLESTON | SPRINGFIELD | GREENE | MO | 65804 | 37.1229 | -93.2632 | YES | YES |  | YES | [5 empty] | 2023-07-17 13:25 | 1373341 | 1373504 | NATURAL GAS |  | 1210 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-07-17 11:25 | ALLOWED TO BURN OUT |  | 1087 | NO | 4 | 2023-07-17 11:20 | YES | OPERATOR | 2023-07-17 11:21 | 2023-07-17 11:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | TRANSITION AREA | OTHER | UNEXPOSED FITTING NEAR EXPOSED VALVE |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 12 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 100000 | 100000 | 250000 | 250000 | 10000 | 10000 | 0 | 0 |  | 6.86 | 8301 | 8301 | 0 | 0 | 368301 | 158301.6102581631010207939508506616257089 | 368301 | 0 | 0 | 4 | 4 | 0 | 4 | 0 | 134 | 148 | 200 | 192.619(A)(3) | 1987-07-20 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ASPECT OF THE CONTROL ROOM OPERATIONS WERE A CONTRIBUTING FACTOR TO THE INCIDENT AND THERE WERE NO ACTIONS THAT THE CONTROLLER COULD HAVE TAKEN THAT WOULD HAVE CHANGED THE OUTCOME OF THE INCIDENT. | [12 empty] | YES | 7 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JACOB ANDERSON | NATURAL GAS CODE COMPLIANCE ENGINEER | jacob.anderson@cityutilities.net | 4177662756 |  | JACOB ANDERSON | jacob.anderson@cityutilities.net | 4177662756 | CASEY HAYNES | DIRECTOR - NATURAL GAS AND WATER ENGINEERING | 4172095426 | casey.haynes@cityutilities.net | A NATURAL GAS CONSTRUCTION CREW WAS PERFORMING MAINTENANCE ON A DISTRIBUTION LINE BEHIND 5012 S CHARLESTON AVENUE. AT THAT LOCATION, A FLANGED CROSS FITTING CONNECTED SECTIONS OF GAS PIPELINE VIA VALVES TO THE NORTH, WEST, AND SOUTH IN AN EXPOSED VALVE CLUSTER PIT. IN PREPARATION FOR MAINTENANCE, THE VALVES TO EACH OF THE NORTH, WEST, AND SOUTH PIPELINES WERE CLOSED. GAS REMAINED IN THE NORTH AND WEST PIPELINE BUT HAD ALREADY BEEN PURGED FROM THE SOUTH PIPELINE. CREWS REMOVED THE FLANGED CROSS FITTING AND THE VALVE TO THE SOUTH. THOUGH THE VALVE TO THE NORTH WAS EXPOSED, IT WAS ATTACHED TO A SECTION OF PIPE CONNECTED TO THE UPSTREAM PIPELINE BY A COMPRESSION COUPLING THAT WAS UNDERGROUND AND NOT VISIBLE TO THE CREW. SHORTLY AFTER THE CREW REMOVED THE FLANGED CROSS FITTING, THEY HEARD A SOUND THEY RECOGNIZED TO BE A GAS LEAK, SO THEY BEGAN TO EVACUATE THE AREA AND CONTACTED EMERGENCY SERVICES. WITHIN APPROXIMATELY 5 MINUTES, THE BLOWING GAS IGNITED. GAS WAS THEN SHUT OFF FROM THE INCIDENT SITE AND THE FLAMES WERE EXTINGUISHED. EVENTUALLY IT WAS DISCOVERED THAT THE NORTH VALVE AND SECTION OF PIPE IT WAS ATTACHED TO HAD PULLED OUT OF THE COMPRESSION COUPLING CONNECTING IT WITH THE REST OF THE NORTH PIPELINE.
2024-05-31 11:04 | NO | YES | YES | 20230043 | 39130 | 2023-08-15 17:44 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2023-07-15 09:24 | CENTRAL | YES | 2023 | 500 MILL ST | GEORGETOWN | VERMILLION | IL | 61846 | 39.9784 | -87.6295 | YES | [8 empty] | 2023-07-15 10:23 | 1373141 | 1373156, 1373298 | NATURAL GAS |  | 182 | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 0 | YES | 2023-07-15 07:49 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 182 | NO | 0 | 2023-07-15 08:21 |  |  |  | 2023-07-15 09:10 | 2023-07-15 09:52 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1954 | 1954 | [7 empty] | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.237 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 3 LOCATION | 15000 | 15000 | 309635 | 309635 | 800000 | 800000 | 0 | 0 |  | 4.054 | 738 | 738 | 0 | 0 | 1125373 | 475719.7209627579188859451795841209829868 | 1125373 | 50 | 0 | 1280 | 0 | 0 | 1280 | 50 | 118 | 118 | 125 | 192.621 M | 1954-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VEHICLE HIT A PRESSURE REGULATOR STATION AND GAS CONTROL HAD NO CAUSE OR CONTRIBUTING FACTORS IN THAT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | 35 | PASSENGER CAR | ROADWAY | 271 | YES |  | YES | [116 empty] | YES | [23 empty] | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MANAGMENT | jbozarth@ameren.com | 2176256854 |  |  |  |  | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MANAGMENT | 2176256854 | jbozarth@ameren.com | AMEREN ILLINOIS RECEIVED NOTIFICATION THAT A CAR HAD LEFT THE ROADWAY AND DROVE INTO A FENCED REGULATOR STATION IN GEORGETOWN, IL. IGNITION OF THE GAS AT THIS ABOVE GRADE FACILITY OCCURRED UPON IMPACT. THE DISTANCE TRAVELLED BETWEEN THE LOCATION WHERE THE CAR LEFT THE ROADWAY AND THE FENCE AROUND THE REGULATOR STATION IS APPROXIMATELY 261 FEET. THE DRIVER AND THE ONE OTHER PASSENGER BOTH WERE PRONOUNCED DECEASED. THE INLET SUPPLY OF GAS WAS STOPPED BY CLOSING AN UPSTREAM VALVE. GAS PRESSURE WAS LOST ON THE DOWNSTREAM SIDE OF THE REGULATOR STATION, WHICH WAS A ONE WAY FEED TO THE TOWN OF GEORGETOWN. THE RESULT WAS A LOSS OF SERVICE TO 1330 GAS CUSTOMERS, FOLLOWED BY REPAIRS TO THE GAS SYSTEM AND SUBSEQUENT RESTORATION OF GAS SERVICE. *REVISED AND FINAL INCLUDE COSTS RELATED TO PERMANENT REBUILD OF REGULATOR STATION.
2024-05-31 11:04 | NO | NO | NO | 20230044 | 38425 | 2023-08-18 13:59 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2023-07-20 11:11 | EASTERN | YES | 2023 | N. GRAND AVENUE & SAGINAW STREET | LANSING | INGHAM | MI | 48933 | 42.7408 | -84.5511 | [5 empty] | YES | YES |  |  | 2023-07-20 17:01 | 1373673 | 1373742 | NATURAL GAS |  | 6728 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 1 | 2023-07-20 11:11 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-07-20 11:34 | 2023-07-20 11:34 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 92 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2003 | UNKNOWN |  |  |  |  | 6 | D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 2708 | MECHANICAL PUNCTURE | 2 | 29.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 39409 | 39409 | 35 | 35 | 0 | 0 |  | 2.2 | 14802 | 14802 | 0 | 0 | 54246 | 27717.9869558241926784045368620037807183 | 54246 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 2003-01-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | STATE HIGHWAY | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 2023070500130 |  |  | FACILITY OWNER | YES | YES | 17 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARMELLA Q. KING | PRINCIPAL ENGINEER TECHNICAL ANALYST | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | SENIOR MANAGER ENGINEERING | 989-598-5031 | jason.pionk@cmsenergy.com | ON JULY 20, 2023, AT APPROXIMATELY 11:11 HOURS CONSUMERS ENERGY RECEIVED NOTIFICATION OF A NATURAL GAS PIPELINE DAMAGE NEAR THE INTERSECTION OF N. GRAND AVENUE & SAGINAW STREET, LANSING (INGHAM COUNTY) MICHIGAN. THE GAS DISTRIBUTION CREW ARRIVE ONSITE AT APPROXIMATELY 11:34 HOURS AND A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 11:43 HOURS. GAS DISTRIBUTION CREW CONFIRMED A GAS CONSTRUCTION (FIRST PARTY) EMPLOYEE DAMAGED A 6-INCH PLASTIC MEDIUM PRESSURE PIPELINE WHILE INSTALLING SHORING EQUIPMENT TO PERFORM TIE-IN WORK. THE GSW BEGAN MONITORING THE AREA FOR GAS MIGRATION AND GAS SERVICE EMPLOYEE(S) REMAINED ONSITE AND MONITORED THE AREA UNTIL THE GAS WAS CONTAINED. POLICE AND FIRE PERSONNEL WERE ONSITE AND EVACUATED ONE COMMERCIAL BUILDING BEFORE THE CREW ARRIVED. IT IS UNKNOWN THE NUMBER OF OCCUPANTS WITHIN THE BUILDING AT THE TIME IT WAS EVACUATED. POLICE AND FIRE ALSO ASSISTED CONSUMERS ENERGY EMPLOYEES WITH ROAD CLOSURES TO ENSURE THE SAFETY OF PEDESTRIANS AND VEHICLE TRAFFIC. NO FATALITIES OR INJURIES OCCURRED BECAUSE OF THE DAMAGE AND SUBSEQUENT NATURAL GAS RELEASE. THE DISTRIBUTION CREW DEVELOPED A PLAN TO ISOLATE AND ARREST THE BLOWING GAS. BECAUSE THE LOCATION HAD A FOUR-WAY BACK-FEED TO THE DAMAGE LOCATION, EXCAVATION AT MULTIPLE LOCATIONS WAS REQUIRED. TWO PLASTIC PIPELINES WERE SQUEEZED, AND EXISTING CONTROL FITTINGS WERE UTILIZED AT TWO ADDITIONAL LOCATIONS TO STOP THE GAS FROM BLOWING. BECAUSE THE PIPELINE DEPTH WAS GREATER THAN 6-FEET, SHORING EQUIPMENT WAS NEEDED TO SAFELY ACCESS THE PIPELINE TO COMPLETE THE REPAIR. THE DAMAGE SEGMENT WAS CUT OUT AND REPLACED WITH 3-FOOT OF 6-INCH PLASTIC PIPELINE. THE PIPELINE WAS PURGED, AND NORMAL OPERATIONS RESUMED ON JULY 21, 2023, AT 04:20 HOURS.
2024-05-31 11:04 | NO | YES | NO | 20230045 | 39096 | 2023-08-25 16:06 | SUPPLEMENTAL FINAL | 32198 | MINNESOTA ENERGY RESOURCES CORPORATION | 2685 145TH STREET WEST | ROSEMOUNT | MN | 55068 | 2023-07-26 01:37 | CENTRAL | NO | 2023 | 19210 EUCLID PATH | FARMINGTON | DAKOTA | MN | 55024 | 44.6709 | -93.1789 |  |  |  | YES | [5 empty] | 2023-07-26 15:00 | 1374754 | 1374279 | NATURAL GAS |  | 0.25 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-07-27 01:37 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.25 | NO | 2 | 2023-07-26 01:37 |  |  |  | 2023-07-26 02:47 | 2023-07-26 01:37 | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2008 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 346700 | 346700 | 500 | 500 | 500 | 500 | 0 | 0 |  | 3.91 | 1 | 1 | 0 | 0 | 347701 | 146907.2042564471282765595463137996219282 | 347701 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 2 | 2 | 5 | 192.623 | 2008-01-11 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | LINDSAY K LYLE | ENGINEERING MANAGER | lindsay.lyle@minnesotaenergyresources.com | 651-322-8909 | 920-272-4000 | SHAWN WALLS | shawn.walls@minnesotaenergyresources.com | 651-322-8942 | LINDSAY LYLE | ENGINEERING MANAGER | 651-322-8909 | lindsay.lyle@minnesotaenergyresources.com | EMPLOYEE RESPONDED TO HOUSE FIRE THAT RESULTED IN FIRE DEPARTMENT SHUTTING OFF METER STOP VALVE. LIGHTNING STRIKE HIT A NEARBY TREE. BACK OF THE METER WAS CRACKED. UNSURE IF SECOND LIGHTNING STRIKE HIT METER DIRECTLY OR THE FIRE CAUSED A CRACK TO IGNITE.
2024-05-31 11:04 | NO | NO | NO | 20230046 | 38482 | 2023-08-31 11:24 | ORIGINAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 401 DOUGLAS STREET PO BOX 778 | SIOUX CITY | IA | 51101 | 2023-08-02 21:45 | CENTRAL | YES | 2023 | 1400 NW 86TH STREET | CLIVE | POLK | IA | 50325 | 41.6031 | -93.7365 | YES | YES | [7 empty] | 2023-08-02 22:33 | 1375040 | 1375241 | NATURAL GAS |  | 6771 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 17 | 2023-08-02 17:09 |  |  |  | 2023-08-02 17:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 2000 | 2000 | 36755 | 36755 | 0 | 0 |  | 2.3395 | 15841 | 15841 | 0 | 0 | 54596 | 28202.6909541779757847731568998109640832 | 54596 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 90 | 90 | 125 | 192.619(A)(4) | 1988-10-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | CABLE TV | YES | 232061755 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHRISTOPHER PAYER | GAS STANDARDS ENGINEER | chris.payer@midamerican.com | 7122777941 | 7122527369 | CHRISTOPHER PAYER | chris.payer@midamerican.com | 7122777941 | NICK NATION | VICE PRESIDENT GAS DELIVERY | 5156973256 | nick.nation@midamerican.com | HARTCO CABLE, INC. (THIRD PARTY CONTRACTOR) BORED INTO A 16-INCH NATURAL GAS STEEL MAIN WHILE INSTALLING CABLE TV AT 1400 NW 86TH STREET IN CLIVE, IOWA ON AUGUST 2, 2023. THE BORING HEAD PUNCTURED A FOUR-INCH BY TWO-INCH HOLE IN THE LOWER THIRD OF THE MAIN THAT WAS AT A SIX-FOOT DEPTH. NO SERVICES WERE INTERRUPTED AND THERE WAS NO IGNITION OR INJURIES. DUE TO THE SIZE AND DEPTH OF THE MAIN, IT TOOK A SIGNIFICANT AMOUNT OF TIME TO REPAIR THE DAMAGE AND 6.771 MCF OF NATURAL GAS WAS RELEASED TO ATMOSPHERE. THE NRC WAS INITIALLY NOTIFIED (REPORT 1375040) ON AUGUST 2 AND A 48-HOUR FOLLOW-UP REPORT WAS SUBMITTED (REPORT 1375241).
2024-05-31 11:04 | NO | YES | NO | 20230047 | 38598 | 2023-08-31 14:50 | SUPPLEMENTAL | 35505 | HASKINS GAS SERVICE | 1791 ROUTE 30 | DORSET | VT | 05251 | 2023-07-11 04:30 | EASTERN | YES | 2023 | 20 INNOVATION DRIVE | NORTH CLARENDON | RUTLAND | VT | 05759 | 43.5286 | -72.9561 | YES | YES |  | YES | YES |  |  |  |  | 2023-08-25 11:00 | 1377516 |  | PROPANE GAS |  | 1272 | 848 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 3 | 2023-07-11 04:30 |  |  |  | 2023-07-11 05:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | YES | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UG 30,000 PROPANE TANK | 2005 | 1974 | [7 empty] | STEEL |  | CONTINUOUS WELDED |  | 0.05 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | 7000 | 7000 | 200000 | 200000 | 6000 | 6000 | 50000 | 50000 | CRANE & EXCAVATION | 1.5 | 1908 | 1908 | 1272 | 1272 | 266180 | 113494.406350490746459357277882797731569 | 266180 | 0 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 9 | 14 | 192.619(A)(1) | 2005-07-09 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | AREA RECEIVED UNUSUAL AMOUNT OF RAIN IN SHORT PERIOD OF TIME, 9" IN A 12 HOUR PERIOD OF TIME. THIS HEAVY RAINS CAUSED SOIL TO BECOME OVER SAURATED WITH WATER AND FLOAT THE TANK. | YES |  |  |  | YES | EXTREME RAIN FALL IN SHORT PERIOD OF TIME, CAUSING FLOODING. | [178 empty] | YES | [34 empty] | VICKIE HASKINS | PRESIDENT | hasgas@aol.com | 802-867-5741 |  |  |  |  | VICKIE HASKINS | PRESIDENT | 8028675741 | hasgas@aol.com | RECEIVED A CALL FROM CLARENDON, VERMONNT FIRE CHIEF, FOR SMELL OF PROPANE AT 20 INNOVATION DRIVER. UPON ARRIVAL THE GAS WAS SHUT OFF, NO LONGER RELEASING GAS. THE UNDERGROUND 30,000 GALLON PROPANE TANK HAD BECOME UNEARTHED ON ONE END. THE SUPPLY LINE TO REGULATOR CRACKED, AS TANK FLOATED OUT OF GROUND. NO DAMAGE TO CONTAINER OCCURED. WE HAD EXCESSIVE RAIN AND FLOODING IN THE AREA IN VERMONT. THE TANK HAS BEEN BURIED AT THIS LOCATION FOR OVER 20 YEARS WITHOUT ISSUE. WE EVACUATED PRODUCT FROM THE TANK, THEN FLARED OFF REMAINING PROPANE VAPOR.
2024-05-31 11:04 | NO | YES | NO | 20230049 | 38511 | 2023-09-06 17:02 | ORIGINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2023-08-07 17:58 | EASTERN | YES | 2023 | 1321 VIRGINIA AVE | DUNBAR | KANAWHA | WV | 25064 | 38.3647 | -81.7418 | [7 empty] | YES | FULL CIRCLE LEAK CLAMP | 2023-08-07 19:18 | 1375509 | 1375718 | NATURAL GAS |  | 209 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-07 17:58 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.56 | YES | 3 | 2023-08-07 19:30 | YES | OPERATOR | 2023-08-07 17:58 | 2023-08-07 14:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 | YES | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 8.5 | 4 | [7 empty] | CLASS 3 LOCATION | 200000 | 200000 | 3000 | 3000 | 14000 | 14000 | 10000 | 10000 | EMERGENCY RESPONDERS | 6.739 | 1408 | 1408 | 0 | 0 | 228408 | 96960.9362509504287958412098298676748582 | 228408 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0.5 | 0.5 | 0.5 | 192.623 | 1968-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2321330168 |  |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | PHILIP KINGREY | MANAGER-ENGINEERING AND COMPLIANCE | philipkingrey@mgcwv.com | 8884204427 |  | RICKY DYE | rickydye@mgcwv.com | 8884204427 | THOMAS WESTFALL | VP GAS SUPPLY AND TECHNICAL SERVICES | 8884204427 | thomaswestfall@mgcwv.com | 3J UNDERGROUND LLC WORKING FOR B N D SERVICES LLC WORKING FOR FIBER MANAGEMENT SERVICES LLC/SECURENET FIBER INTERNET TO INSTALL FIBER CONDUIT WITH A DIRECTIONAL BORE MACHINE. 3J FAILED TO HAND-DIG OR SPOT THE GAS FACILITIES WHILE BORING. ON THE FIRST OF TWO TRIES, THE BORING HEAD PUNCHED THROUGH THE CENTER OF THE 4 STEEL MAIN AND GAS MIGRATED INTO A NEARBY DAMAGED SEWER LINE. 3J THEN BORED A SECOND HOLE ABOVE THE MGC PIPE AND INSTALLED THE PLASTIC CONDUIT, CALLED MGC'S LOCATOR DIRECTLY TO REPORT AN ODOR OF GAS, AND LEFT THE SCENE BEFORE MGC LOCATOR ARRIVED ON SCENE AND NOTIFIED MGC DISPATCH. WHILE MGC PERSONNEL WERE INVESTIGATING THE ODOR OF GAS, THE HOUSE AT 1321 VIRGINIA AVE EXPLODED AND CAUGHT FIRE. ADDITIONAL MGC PERSONNEL AND EQUIPMENT WERE CALLED IN TO FIND AND REPAIR THE DAMAGED PIPE. DAMAGE TO THE PIPE SHOWS EVIDENCE OF MULTIPLE POINTS OF CONTACT.
2024-05-31 11:04 | NO | YES | NO | 20230050 | 38536 | 2023-09-12 16:02 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2023-08-14 10:46 | EASTERN | YES | 2023 | 24244 STATE ROUTE 37 | WATERTOWN | JEFFERSON | NY | 13601 | 44.0165 | -75.9016 | [5 empty] | YES |  |  |  | 2023-08-14 17:50 | 1376286 | 1376491 | NATURAL GAS |  | 223 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-08-14 10:57 | YES | OPERATOR | 2023-08-14 15:05 | 2023-08-14 10:57 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1987 | UNKNOWN |  |  |  |  | 6 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 24 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 70134 | 70134 | 309939 | 309939 | 0 | 0 |  | 3.48 | 776 | 776 | 0 | 0 | 380849 | 161163.7816007366417332079395085066162571 | 380849 | 39 | 2 | 214 | 0 | 0 | 214 | 41 | 40 | 40 | 45 | 192.621 M | 1986-10-30 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROL ROOM ISSUES WERE THE CAUSE OF OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | TRENCHER | WATER | YES | 08083001181 | U-DIG |  | CONTRACT LOCATOR | NO | YES | 18 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | CONTRACTOR STRUCK AND DAMAGED NATIONAL GRID'S 6-INCH PLASTIC DISTRIBUTION MAIN, WHILE TRENCHING TO INSTALL A NEW WATER MAIN. THIS CAUSED AN UNPLANNED INTERRUPTION OF OVER 230 CUSTOMERS IN THE AREA. THE 6-INCH MAIN WAS PROPERLY MARKED OUT, AND HAD INTACT TRACER WIRE OVER IT. THE CONTRACTOR DID NOT FOLLOW PROPER HAND EXCAVATING AND DID NOT KEEP MARKINGS VISIBLE AS THEY PROGRESSED IN EXCAVATING. THE INCIDENT OCCURRED ON MONDAY 8/14 AT APPROX. 10:49 AM, AND NATIONAL GRID ARRIVED AT 10:57; HOWEVER, WE WERE NOT AWARE THAT THIS INCIDENT WOULD POTENTIALLY MEET PHMSA REPORTING LIMITS OF $137K MINIMUM THRESHOLD UNTIL TUESDAY 8/15 AT 4:20 PM. UPON CONFIRMATION, THE NRC WAS NOTIFIED AT 5:50 PM. AS OF SEPTEMBER 9, ALL CUSTOMERS HAVE BEEN RESTORED EXCEPT FOR INACTIVE/REMOVED METERS. TOTAL INACTIVE/REMOVED METERS IS 8. SUPPLEMENTAL REPORT FILED 9/13/2023 TO REVISE INCIDENT REPORTING TIME TO 10:46 ON 8/14/2023.
2024-05-31 11:04 | NO | YES | NO | 20230051 | 38532 | 2023-09-13 09:58 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2023-08-27 02:40 | CENTRAL | YES | 2023 | 1630 12TH AVENUE NORTH | NASHVILLE | DAVIDSON | TN | 37208 | 36.1782 | -86.8042 | [5 empty] | YES |  |  |  | 2023-08-27 07:59 | 1377405 | 1377582 | NATURAL GAS |  | 6.706 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-27 02:40 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6.7 | NO | 3 | 2023-08-27 02:40 |  |  |  | 2023-08-27 03:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | VEHICLE BROKE RISER VALVE OFF. | [5 empty] | CLASS 3 LOCATION | 150000 | 150000 | 0 | 0 | 5000 | 5000 | 0 | 0 |  | 3.3 | 22 | 22 | 0 | 0 | 155022 | 65505.3571104709276843100189035916824197 | 155022 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 60 | 60 | 75 | 192.619(A)(2) | 2002-04-03 | PRESSURE DID NOT EXCEED MAOP | NONE |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE HIT A GAS METER TO A HOME. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | PASSENGER CAR | ROADWAY | 30 | NO | [142 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER-PIPELINE SAFETY GOVERNANCE | 704-731-4618 | farris.berry@duke-energy.com | A DRIVER TRAVELING AT A HIGH RATE OF SPEED, LOST CONTROL OF HIS VEHICLE, RUNNING INTO THE GAS METER AND HOME CAUSING A NATURAL GAS FED HOUSE FIRE. BOTH THE GAS METER AND HOME WAS DESTROYED.
2024-05-31 11:04 | NO | YES | NO | 20230052 | 38876 | 2023-09-15 17:50 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-08-16 22:00 | CENTRAL | YES | 2023 | 1202 FRANKIE ST | NEW IBERIA | IBERIA | LA | 70560 | 29.9772 | -91.8305 |  |  |  | YES | [5 empty] | 2023-08-17 14:08 | 1376485 | 1376682 | NATURAL GAS |  | 0.824 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-16 21:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0.03 | NO | 0 | 2023-08-16 21:07 |  |  |  | 2023-08-16 21:36 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | METER INSTALLATION HIT BY VEHICLE. | CLASS 3 LOCATION | 450000 | 450000 | 0 | 0 | 291 | 291 | 0 | 0 |  | 4.05 | 3 | 3 | 0 | 0 | 450294 | 190254.3415516291617706786389413988657845 | 450294 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 20 | 20 | 60 | 192.619(A)(4) | 2000-01-03 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 14 | NO | [142 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 | 337-373-1520 | DOUGLAS BOUDREAUX JR. | douglas.boudreauxjr@centerpointenergy.com | 337-475-6362 | DOUGLAS BOUDREAUX JR. | REGIONAL OPERATIONS DIRECTOR | 337-475-6362 | douglas.boudreauxjr@centerpointenergy.com | CALL RECEIVED @ 21:07 ON AUGUST 16, 2023. NEW IBERIA POLICE DEPT REPORTING THAT TRAILER BACKED OVER GAS METER. CALL WAS THEN UPDATED TO STATE THAT HOME IS NOW ON FIRE AND FIRE DEPT IS IN ROUTE. EMERGENCY ORDER CREATED AND DISPATCHED TO CNP FIRST RESPONDER @ 21:16. CNP FIRST RESPONDER ARRIVED 21:36, METER WAS OFF BY FIRE DEPT UPON ARRIVAL. UPON FURTHER INVESTIGATION, THE REGULATOR WAS DAMAGED BY THE VEHICLE THAT STRUCK IT AND WAS REMOVED AT THE REQUEST OF THE FIRE DEPARTMENT LATER THAT EVENING. DURING THE CNP INVESTIGATION IT WAS DETERMINED THAT THE NEIGHBOR STRUCK THE METER INSTALLATION CAUSING THE LEAK THAT WAS ORIGINALLY REPORTED. UPON RECEIVING ESTIMATED DAMAGES FROM FIRE REPORT ON AUGUST 17, 2023, IT WAS DETERMINED THAT INCIDENT CRITERIA WAS MET AND CALL WAS MADE TO NRC.
2024-05-31 11:04 | NO | NO | NO | 20230053 | 38666 | 2023-09-20 14:23 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2023-08-25 03:10 | EASTERN | YES | 2023 | 14249 SPERRY ROAD | NEWBURY | GEAUGA | OH | 44065 | 41.4793 | -81.2881 |  |  | YES | YES | [5 empty] | 2023-08-25 03:25 | 1377222 | 1377291 | NATURAL GAS |  | 2178 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-08-25 12:20 | OPERATOR/CONTRACTOR |  | 2178 | NO | 3 | 2023-08-25 02:53 |  |  |  | 2023-08-25 02:47 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | OTHER | HP FIRST CUT REGULATOR |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | HP FIRST CUT REGULATOR | UNKNOWN | UNKNOWN | [7 empty] | OTHER | HP FIRST CUT REGULATOR | [9 empty] | OTHER | [8 empty] | ELECTRICAL ARCING FROM DOWN POWER LINE. | CLASS 3 LOCATION | 0 | 0 | 3000 | 3000 | 5000 | 5000 | 0 | 0 |  | 4.3223 | 9414 | 9414 | 0 | 0 | 17414 | 10409.431078620805731568998109640831758 | 17414 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(C) | 1969-07-25 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [136 empty] | YES | [31 empty] | ALLISON WALTERS-THOMPSON | MANAGER GAS OPERATIONS | a.walters-thompson@dominionenergy.com | 2167899152 |  | ALLISON WALTERS-THOMPSON | a.walters-thompson@dominionenergy.com | 2167899152 | ALLISON S WALTERS-THOMPSON | MANAGER GAS OPERATIONS | 2167899152 | a.walters-thompson@dominionenergy.com | DURING SEVERE WINDS OCCURRING IN NE OHIO, A LIVE POWER LINE FELL ONTO AN HP FIRST CUT REGULATOR AT 14249 SPERRY RD NEWBURY, OH CAUSING APPROXIMATELY A 2-INCH DIAMETER HOLE IN THE TOP OF THE RELIEF VALVE. THE HOLE CAUSED MP GAS TO ESCAPE AND IGNITE. ALTHOUGH THERE WAS AN IGNITION OF NATURAL GAS, THERE WAS NO EXPLOSION. DAMAGES DID NOT EXCEED $139,700, NOR DID GAS LOSS EXCEED 3 MILLION CUBIC FEET, AND THERE WERE NO INJURIES NOR FATALITIES. RESIDENTS AT 14249 SPERRY ROAD (A FEMALE AND TWO CHILDREN) WERE EVACUATED. GAS WAS ISOLATED AT 9:23AM. THE CAUSE FOR THE DELAY IN GAS SHUT OFF WAS DUE TO LIVE POWER LINES LAYING IN WATER NEXT TO THE HP FIRST CUT REGULATOR. ONCE THE POWER COMPANY (THE ILLUMINATING COMPANY) CONFIRMED IT WAS SAFE TO ENTER THE YARD, DEO FIRST RESPONDERS EXTINGUISHED THE FLAME AND ISOLATED THE LEAK. REPAIRS WERE MADE AND THE CUSTOMER WAS BACK IN-SERVICE THE SAME DAY.
2024-05-31 11:04 | NO | YES | NO | 20230054 | 38726 | 2023-09-20 18:01 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-08-21 12:17 | PACIFIC | YES | 2023 | MISSION LAKES BLVD & WESTERN AVE | DESERT HOT SPRINGS | SAN BERNARDINO | CA | 92240 | 33.9763 | -116.5537 | YES |  |  |  |  | YES |  |  |  | 2023-08-21 10:26 | 1376821 | 1377032 | NATURAL GAS |  | 8436 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-08-21 09:58 | NO |  |  | 2023-08-21 09:58 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 46 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1964 | UNKNOWN |  |  |  |  | 6 | 5LX-42 | UNKNOWN | STEEL |  | OTHER | DT-ERW / SMLS | 0.16 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 6 |  | CLASS 1 LOCATION | 0 | 0 | 3500000 | 3500000 | 60000 | 60000 | 0 | 0 |  | 6 | 50616 | 50616 | 0 | 0 | 3610616 | 1541927.39709400902313799621928166351607 | 3610616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 385 | 395 | 192.619(A)(2) | 2012-09-04 | PRESSURE DID NOT EXCEED MAOP | OTHER | SELF-SEASONED |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, DAMAGE CAUSED BY STORM-RELATED EVENT. THUS THERE WERE NO ISSUES FROM THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | HURRICANE HILLARY | YES | YES | [217 empty] | SANDIE TO | PIPELINE SAFETY AND COMPLIANCE ADVISOR | slto1@socalgas.com | 978-719-3485 | 909-335-3989 | SANDIE TO | slto1@socalgas.com | 978-719-3485 | SANDIE TO | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 978-719-3485 | slto1@socalgas.com | ON 8/21/2023, SOCALGAS CREWS RESPONDED TO A PIPELINE RUPTURE ON SL 41-53 AT MISSION LAKES BLVD & WESTERN AVE, DESERT HOT SPRINGS, SAN BERNARDINO. UPON INVESTIGATION, THE 6-INCH DISTRIBUTION LINE RUPTURED FROM RUSHING WATER FOUND IN AREA WITH DEBRIS AND EARTH IN THE EXTREME WEATHER CONDITIONS OF HURRICANE HILLARY. THE DISTRIBUTION PIPELINE HAD BEEN ISOLATED AND IS STILL CURRENTLY OUT OF SERVICE WITH REPAIRS ONGOING. NO INJURIES OR FATALITIES RESULTED FROM THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO GAS RELEASE AND DAMAGES EXCEEDING $139,700. UPDATE 10/27/2023: > PART A4 EARLIEST LOCAL TIME INCIDENT REPORTING CRITERIA WAS MET: 12:17 > REPAIRS HAVE BEEN COMPLETED AS OF 09/22/2023, AND SERVICE HAD BEEN RESTORED AS OF 09/25/2023. > PART G2 NATURAL FORCE DAMAGE SUB-CAUSE CHANGED TO "HEAVY RAINS/FLOODS". SPECIFICATION: "OTHER, HURRICANE HILLARY". UPDATE 10/31/2023: > UPDATED REPORT TYPE TO "FINAL"
2024-05-31 11:04 | NO | YES | YES | 20230056 | 38597 | 2023-09-28 09:51 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-08-31 17:11 | CENTRAL | YES | 2023 | 200 S. AVENUE A | LONGVIEW | GREGG | TX | 75604 | 32.5053 | -94.7927 | [5 empty] | YES |  |  |  | 2023-08-31 20:29 | 1377864 |  | NATURAL GAS |  | 53.47 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2023-08-31 17:11 | ALLOWED TO BURN OUT |  | 53.47 | NO | 0 | 2023-08-31 17:11 | YES | OPERATOR | 2023-08-31 17:11 | 2023-08-31 17:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1925 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.094 | [6 empty] | OTHER | [8 empty] | RUBBER STOPPER BLEW OUT RELEASING GAS AS WELDER WAS INSTALLING END CAP. | CLASS 3 LOCATION | 0 | 0 | 2500 | 2500 | 2500 | 2500 | 0 | 0 |  | 2.82 | 151 | 151 | 0 | 0 | 5151 | 2225.296598051047060491493383742911153119 | 5151 | 2 | 0 | 3 | 1 | 0 | 3 | 2 | 48 | 48 | 60 | 192.619(A)(3) | 1925-01-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [45 empty] | YES |  |  | YES | LESLIE DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 | CLINT GOEN | clinton.goen@centerpointenergy.com | 832-374-0745 | JERRY GANN | DIRECTOR REGIONAL OPERATIONS | 713-967-7101 | jerry.gann@centerpointenergy.com | ON AUGUST 31ST, 2023, A CONSTRUCTION CREW FROM CENTERPOINT ENERGY INITIATED REPAIRS TO CORRECT A NON-HAZARDOUS GRADE C LEAK. A DECISION WAS MADE TO ELIMINATE THE AFFECTED PIPE BY ABANDONING THE DEAD-END SECTION. THE CREW HAD SUCCESSFULLY STOPPED THE FLOW OF GAS AND USED A 4-WHEEL CUTTER TO REMOVE THE PIPE. ONCE THE PIPE WAS CUT, THE CREW BEGAN TO INSTALL THE WELD CAP, AT WHICH TIME THEY EXPERIENCED AN IGNITION OF GAS. THE IGNITION RESULTED IN THE INJURY OF ONE CENTERPOINT ENERGY EMPLOYEE. THE EMPLOYEE WAS TRANSPORTED TO GOOD SHEPHERD HOSPITAL IN LONGVIEW, TX, FOR TREATMENT, THEN AT 20:04, EMPLOYEE WAS TRANSFERRED TO PARKLAND HOSPITAL IN DALLAS, TX FOR FURTHER EVALUATION.
2024-05-31 11:04 | NO | YES | NO | 20230057 | 39364 | 2023-10-06 15:50 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2023-09-07 14:18 | MOUNTAIN | YES | 2023 | 4100 RIDGELEY DR NE | ALBUQUERQUE | BERNALILLO | NM | 87108 | 35.0804 | -106.5988 | [5 empty] | YES |  | YES | 2X3 LEAK CLAMP ON MAIN AND PLUGGED OFF RISER | 2023-09-07 18:30 | 1378470 | 1378626 | NATURAL GAS |  | 1 | 0.083 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-07 14:18 | OTHER | NO RESIDUAL FIRE AFTER INITIAL IGNITION EVENT. | 1 | YES | 19 | 2023-09-07 18:16 |  |  |  | 2023-09-07 14:52 | 2023-09-07 18:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 45 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | 2017 |  |  |  |  | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | LEAK |  |  | OTHER | LACK OF COMPLETE FUSION | [5 empty] | CLASS 3 LOCATION | 500000 | 500000 | 0 | 0 | 11250 | 11250 | 0 | 0 |  | 4.99 | 5 | 5 | 0 | 0 | 511255 | 216011.5747877706016327977315689981096408 | 511255 | 0 | 0 | 10 | 2 | 0 | 10 | 0 | 56 | 56 | 60 | 192.619(A)(3) | 2015-11-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXISTING SCADA EQUIPMENT WOULD HAVE GIVEN NO INDICATION OF AN ISSUE AT THIS LOCATION. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2017 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | ROBERT R SMITH | MANAGER PSMS TECHNICAL TRAINING | robert.smith@nmgco.com | 5056973169 |  |  |  |  | ANDREA MARTINEZ | DIRECTOR SAFETY PIPELINE SAFETY TECH TRAINING | 5056973518 | andrea.martinez@nmgco.com | ON SEPTEMBER 7, 2023, AN EXPLOSION OCCURRED AT 14:18 AT 4100 RIDGELEY AVE NE IN ALBUQUERQUE, NM 87108. AT 14:37, NMGC WAS NOTIFIED BY ALBUQUERQUE FIRE AND RESCUE OF A HOUSE EXPLOSION. NMGC ARRIVED AT THE PROPERTY AT 14:52. GAS WAS ESCAPING FROM THE RISER WHEN THE NMGC TECHNICIAN ARRIVED. GAS WAS UNDER CONTROL AT 15:33 AT THE RISER. NMGC BEGAN PROBING FOR GAS AT 15:33. THE NMGC RESPONDING CREW DISCOVERED GAS CONCENTRATION READINGS OF 100% GAS IN THE STREET DIRECTLY IN FRONT OF 4100 RIDGELEY AVE NE. NMGC EXPOSED THE 2-INCH PE PIPE, WHERE THE SECTION OF MAIN WAS OFFSET WITH A DOGLEG THAT WAS INSTALLED IN 2017. A 2X3-INCH LEAK CLAMP WAS INSTALLED AS A TEMPORARY REPAIR. THE SECTION OF MAIN WAS SQUEEZED OFF AT 21:30 AND CAPPED AS A PERMANENT REPAIR. THERE WERE TWO RESIDENTS OF 4100 RIDGELEY AVENUE WHO WERE TREATED FOR NON-LIFE THREATENING INJURIES AND RELEASED. AT 17:15, GAS ODORANT TESTING WITH A HEATH ODOROMETER WAS CONDUCTED REVEALING SUFFICIENT ODORANT AT 0.50% GAS-IN-AIR (12.5% LEL). ADDITIONAL GAS ODORANT TESTING WITH A HEATH ODOROMETER WAS PERFORMED SHOWING APPROPRIATE ODORANT LEVELS. LABORATORY TESTS WERE CONDUCTED ON OCTOBER 25, 2023 WHICH REVEALED A LACK OF COMPLETE FUSION ON BUTT WELD. REGARDING QUESTIONS PART A #7 AND PART A #21C, THE FORM DOES NOT ALLOW AN ENTRY OF "UNKNOWN" BECAUSE A CALCULATION CANNOT BE PERFORMED DUE TO LIMITED OR UNKNOWN INFORMATION NEEDED TO PERFORM THE CALCULATION.
2024-05-31 11:04 | NO | YES | NO | 20230058 | 39469 | 2023-10-09 16:08 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2023-09-09 05:58 | EASTERN | YES | 2023 | 532 WEST ELM STREET | ONEIDA | MADISON COUNTY | NY | 13421 | 43.2233 | -75.4601 | [5 empty] | YES |  |  |  | 2023-09-09 10:12 | 1378590 | 1378603, 1378732 | NATURAL GAS |  | 13.24 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-09 05:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 4.51 | YES | 7 | 2023-09-09 03:14 |  |  |  | 2023-09-09 04:05 | 2023-09-09 04:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1990 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.063 |  | 3408 | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 1 LOCATION | 140000 | 140000 | 1700 | 1700 | 2800 | 2800 | 0 | 0 |  | 3.06 | 41 | 41 | 0 | 0 | 144541 | 61083.1973925599481389413988657844990548 | 144541 | 0 | 0 | 6 | 0 | 0 | 7 | 0 | 41.5 | 41.5 | 45 | 192.621 M | 1990-08-27 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONTROLLER ACTIONS THAT COULD BE TAKEN TO PREVENT THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  |  | YES | POLICE ON-SITE. DAMAGE BY PRIVATE VEHICLE (NON-HOME OWNER). DETAILS OF CITATION UNKNOWN. | NO | UNKNOWN | PASSENGER CAR | OFF-ROAD | 162 | YES |  |  |  |  | YES | YES | METER LOCATED AT BUILDING WALL, OFF ROAD/DRIVEWAY. | [135 empty] | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5164924469 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN PROGRAM MGR REGULATORY MOC | 5169030596 | corinne.byrnes@nationalgrid.com | ON SATURDAY, SEPTEMBER 9, 2023, AT 03:14, THE NIAGARA MOHAWK POWER CORPORATION D/B/A NATIONAL GRID ("NATIONAL GRID" OR THE "COMPANY") UPSTATE NY (UNY) GAS DISPATCH WAS NOTIFIED BY THE MADISON COUNTY 911 CALL CENTER THAT A MEMBER OF THE PUBLIC (WHO WAS SUBSEQUENTLY ARRESTED AND CHARGED WITH 30 SEPARATE CRIMES, INCLUDING GRAND LARCENY 3RD AND 4TH DEGREE, CRIMINAL POSSESSION OF STOLEN PROPERTY, CRIMINAL MISCHIEF, RECKLESS ENDANGERMENT, UNAUTHORIZED USE OF A MOTOR VEHICLE, DWI, AND TRAFFIC VIOLATION) DROVE A VEHICLE INTO THE GAS METER OF A RESIDENCE AT 532 WEST ELM STREET. THE GAS SYSTEM AT THE LOCATION BEGAN TO LEAK GAS. THE UNY GAS DISPATCH ORGANIZATION INITIATED ITS AFTER-HOURS CALL-OUT PROCEDURES. A REPRESENTATIVE FROM NATIONAL GRID'S CUSTOMER METER SERVICE (CMS) ORGANIZATION ACCEPTED THE CALL OUT AT 03:24 AND ARRIVED AT THE SITE AT 04:05 AFTER THE LOCAL FIRE DEPARTMENT HAD EVACUATED SIX OF THE NEIGHBORING HOMES AT 521, 526, 529, 531, 537, AND 538 WEST ELM STREET. THE CMS REPRESENTATIVE CONFIRMED THAT GAS AT 532 WEST ELM STREET WAS BEING RELEASED AND DETERMINED THAT THE VEHICLE DESTROYED THE RISER CAUSING GAS TO BE RELEASED UNCONTROLLABLY. THE CMS REPRESENTATIVE FOLLOWED STANDARD OPERATING PROCEDURES TO LOCATE AN ALTERNATIVE POINT OF SHUT OFF (THE PRIMARY SHUT OFF AT THE RISER WAS DESTROYED) AND DETERMINED THERE WAS NO CURB VALVE PRESENT. AT 04:25 THE CMS REPRESENTATIVE CALLED FOR ADDITIONAL RESOURCES FROM GAS FIELD OPERATIONS (GFO). UNY GAS DISPATCH INITIATED ITS AFTER-HOURS CALL-OUT PROCEDURES FOR GFO SUPPORT AT 04:41. A REPRESENTATIVE FROM NATIONAL GRID'S GFO ORGANIZATION ACCEPTED THE CALL OUT AT 04:46 AND ARRIVED AT THE REPORTED SITE AT 06:31. WHILE THE GFO CREW WAS EN ROUTE, AN EXPLOSION OCCURRED AT APPROXIMATELY 05:55. THE CMS FIRST RESPONDER NOTIFIED UNY GAS DISPATCH OF THE EXPLOSION AT 05:58. FOLLOWING GAS FIELD OPERATIONS (GFO) ARRIVAL AT THE SCENE AT 06:31, THE CREW EXCAVATED THE SERVICE TO ACCESS THE GAS DISTRIBUTION SERVICE PIPE AND SHUT OFF GAS SUPPLY TO THE INCIDENT LOCATION AT 532 WEST ELM STREET. GAS WAS CONTROLLED AT 07:10. AFTER WITNESSING THE EXPLOSION, THE CMS FIRST RESPONDER CALLED FOR FURTHER CMS SUPPORT. ADDITIONAL CMS PERSONNEL ARRIVED ON SCENE TO ASSIST AND THEN RELIEVE THE INITIAL FIRST RESPONDER AND TO SHUT OFF GAS SERVICE TO FIVE OF THE SURROUNDING HOMES AT: 526, 529, 531, 537 AND 538 WEST ELM STREET AND REMOVE THE GAS METERS. THE HOUSE LOCATED AT 521 WEST ELM STREET WAS EVACUATED BUT GAS SERVICE WAS NOT SHUT OFF. IT WAS LATER REPORTED THAT THE VEHICLE INVOLVED IN THE ACCIDENT WAS STOLEN. NATIONAL GRID DETERMINED THAT THE VEHICLE HAD SEVERED THE SERVICE RISER IN ADDITION TO DAMAGING THE METER. NOTE, PART A, QUESTION 22, REPRESENTS A MINIMUM ESTIMATE OF 1 CUSTOMER PER RESIDENCE EVACUATED.
2024-05-31 11:04 | NO | YES | NO | 20230059 | 38679 | 2023-10-20 10:36 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2023-09-20 11:27 | EASTERN | YES | 2023 | 2049 SYLVAN ROAD SW | ATLANTA | FULTON | GA | 30310 | 33.6983 | -84.4182 | YES | YES |  |  |  | YES |  |  |  | 2023-09-20 11:35 | 1379609 | 1379789 | NATURAL GAS |  | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-20 10:48 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 500 | NO | 3 | 2023-09-20 10:48 |  |  |  | 2023-09-20 10:54 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2001 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3.7 | 3.7 | [7 empty] | CLASS 3 LOCATION | 300000 | 300000 | 87500 | 87500 | 68196 | 68196 | 0 | 0 |  | 2.815 | 1408 | 1408 | 0 | 0 | 457104 | 193587.1059926478634918412098298676748582 | 457104 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 45 | 60 | 192.619(A)(2) | 2001-04-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TRAFFIC SIGNAL | YES | 230731005543 |  |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [169 empty] | YES | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK LONN | DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (CABLE EAST) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 4-INCH PLASTIC GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL TRAFFIC SIGNAL CONDUIT LINES NEAR 2049 SYLVAN ROAD SW, ATLANTA. ESCAPING GAS FROM THE DAMAGE WAS IGNITED BY AN UNKNOWN IGNITION SOURCE AND A SUBSEQUENT FIRE OCCURRED AT THE STREET RESULTING IN SIGNIFICANT PROPERTY DAMAGE. AT LEAST ONE VEHICLE AS WELL AS A TRACTOR AND THE DIRECTIONAL BORING RIG WERE DAMAGED IN THE FIRE; THERE WAS ALSO HEAT DAMAGE TO A LARGE COMMERCIAL SIGN AND A DIESEL PUMP AT A NEARBY CHEVRON GASOLINE STATION. UPON ARRIVAL, AGLC PERSONNEL SECURED THE AREA AND MONITORED THE SURROUNDING AREA FOR GAS. GAS WAS SHUT-OFF TO THE DAMAGED AREA AT 12:06 PM BY OPERATING TWO (2) VALVES AND PERFORMING ONE (1) SQUEEZE OFF OPERATION. A LOCATE REQUEST WAS MADE ON SEPTEMBER 6, 2023, BY CABLE EAST (EXCAVATOR) TO "LOCATE THE INTERSECTION OF SR 166 RAMPS EAST BOUND OFF & ON AND SYLVAN RD SW 200' IN ALL DIRECTION ENTIRE ROW". AGLC FACILITIES WERE MARKED BY STAKE CENTER LOCATING TO SATISFY THIS REQUEST ON SEPTEMBER 20, 2023, AT 10:19 AM. INVESTIGATION OF THE SITE REVEALED THAT THE LOCATE MARKS WERE NOT ACCURATE AT THE POINT OF DAMAGE; THE NEAREST LOCATE MARK TO WHERE THE 4-INCH PLASTIC MAIN WAS DAMAGED WAS APPROXIMATELY SEVEN (7) FEET AWAY. BECAUSE THE EXCAVATOR DID NOT VERIFY THE LOCATION OF AGLC FACILITIES BY POT HOLING AND INSTEAD BLINDLY CROSSED THE MARKS ON THE GROUND WHICH RAN PARALLEL TO THE ACTUAL LOCATION OF THE GAS MAIN, THE GAS MAIN WAS DAMAGED. HAD THE EXCAVATOR POTHOLED, IT WOULD HAVE DETERMINED THE LOCATION OF THE MAIN WAS NOT CONSISTENT WITH THE MARKS ON THE GROUND AT THE POINT OF CROSSING AND TAKEN STEPS TO DETERMINE THE ACTUAL LOCATION OF THE GAS MAIN. ADDITIONAL NRC REPORT NUMBER 1379789 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2024-05-31 11:04 | NO | YES | NO | 20230060 | 39040 | 2023-10-20 16:32 | SUPPLEMENTAL FINAL | 2188 | CENTRAL FLORIDA GAS CORP | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2023-09-21 11:38 | EASTERN | YES | 2023 | TURKEY CREEK RD. | PLANT CITY | HILLSBOROUGH | FL | 33566 | 27.9888 | -82.1705 | YES | YES | [7 empty] | 2023-09-21 17:40 | 1379739 | 1379888 | NATURAL GAS |  | 98 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-09-21 11:38 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-09-21 12:25 | 2023-09-21 12:25 | 2023-09-21 12:25 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 96 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | 2010 |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 160000 | 160000 | 1000 | 1000 | 0 | 0 |  | 3.8 | 372 | 372 | 0 | 0 | 161372 | 68301.7546160338854801512287334593572779 | 161372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 165 | 175 | 192.619(A)(2) | 2010-05-06 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 251301840 |  | NO | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [169 empty] | YES | MICHAEL MCCARTY |  | mmccarty@fpuc.com | 863 224 0417 |  | MICHAEL MCCARTY | mmccarty@fpuc.com | 863 224-0417 | MICHAEL MCCARTY |  | 863 224-0417 | mmccarty@fpuc.com | A SUB-CONTRACTOR FOR A SITE CONTRACTOR WAS DRIVING STEEL SHEET SHORING IN THE GROUND ON TURKEY CREEK RD. THE SHEET SHORING STOPPED ABOUT 8' DEEP AND WOULD NOT DRIVE ANY FURTHER. THE SITE CONTRACTOR USED A TRACK HOE TO DIG DOWN TO SEE WHAT THE OBSTRUCTION WAS AND STRUCK A 6" STEEL GAS MAIN AND POKED A SMALL HOLE IN THE PIPE. FLORIDA PUBLIC UTILITIES (CENTRAL FLORIDA GAS) TECHNICIANS WERE DISPATCHED AND CLOSED A KEY VALVE AND A SYSTEM VALVE ON EITHER SIDE OF THE DAMAGE, STOPPING THE ESCAPING NATURAL GAS. DUE TO THE DEPTH OF THE PIPE AND EXTENSIVE GROUND WATER, A NEW SECTION OF STEEL PIPE WILL NEED TO BE INSTALLED BY DIRECTIONAL BORE. THE SUB-CONTRACTOR DID NOT HAVE A VALID LOCATE TICKET, THE SITE CONTRACTOR WHO HIT AND PUNCTURED THE LINE DID HAVE MULTIPLE VALID LOCATE TICKETS. A CONTRACT LOCATOR FOR FPU HAD PREVIOUSLY MARKED MULTIPLE TICKETS BUT DID NOT MARK THE LAST UPDATE TICKET AND PUT IN THE NOTES THAT IT WAS AN ONGOING PROJECT. A CONTRACTOR FOR CENTRAL FLORIDA GAS BEGAN REPLACING THE DAMAGED PIPE BY DIRECTIONAL BORE ON 9/26/23. THE NEW 6" MAIN WAS INSTALLED, PIGGED, TESTED, TIED IN, PURGED AND PUT BACK IN SERVICE ON 10/17/23. 12/29/2023 - FINAL REPORT. NO SIGNIFICANT CHANGES TO PREVIOUSLY SUBMITTED INFORMATION. 1/4/2024 - NEW SUPPLEMENTAL AND FINAL TO MAKE CHANGES TO A (4) AND C (3A) SUGGESTED BY PHMSA SENIOR INVESTIGATOR, ACCIDENT INVESTIGATION DIVISION.
2024-05-31 11:04 | NO | YES | NO | 20230061 | 39408 | 2023-10-23 13:56 | SUPPLEMENTAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2023-09-23 13:15 | EASTERN | YES | 2023 | 14 W PROVIDENCE ROAD | YEADON | DELAWARE | PA | 19050 | 39.9297 | -75.2709 | [7 empty] | YES | NONE | 2023-09-23 16:39 | 1379904 | 1380020 | NATURAL GAS |  | 470 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-09-23 10:25 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 121 | 2023-09-23 10:25 |  |  |  | 2023-09-23 10:49 | 2023-09-23 10:49 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | ELECTRICAL ARCING - SEE PART H | [5 empty] | CLASS 3 LOCATION | 350000 | 350000 | 10582 | 10582 | 75703 | 75703 | 0 | 0 |  | 6.31 | 2966 | 2966 | 0 | 0 | 439251 | 186549.1253601099676106143667296786389414 | 439251 | 0 | 0 | 6 | 0 | 0 | 7 | 0 | 57 | 57 | 99 | 192.619(C) | 1969-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 7.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WAS NOT RELATED TO ABNORMAL PRESSURE CONDITION | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [138 empty] | YES | [29 empty] | JOHN STAUDENMAYER | SENIOR ENGINEER | john.staudenmayer@exeloncorp.com | 856-313-6432 |  |  |  |  | ROBERT EDLING | MANAGER GAS STANDARDS AND COMPLIANCE | 215-341-6934 | robert.edling@exeloncorp.com | ON SEPTEMBER 23, 2023, AT APPROXIMATELY 10:25, PECO WAS NOTIFIED BY THE FIRE DEPARTMENT OF A FIRE IN THE ROADWAY ON PROVIDENCE RD IN YEADON, PENNSYLVANIA. UPON ARRIVAL, IT WAS DETERMINED THAT A TREE CAME DOWN DUE TO STORMS IN THE AREA WHICH CAUSED A PRIMARY ELECTRIC WIRE TO FALL INTO THE STREET. IT IS BELIEVED AT THIS TIME THE DOWNED ELECTRICAL WIRE ENERGIZED A FOREIGN FACILITY, WHICH CAUSED AN ELECTRICAL ARC BETWEEN THE FOREIGN FACILITY AND PECO GAS MAIN, WHICH BURNED HOLES IN THE BURIED 6" GAS MAIN AND IGNITED AT THE LOCATION OF THE DOWN WIRE. ALL 6 HOMES IN THAT IMMEDIATE AREA WERE EVACUATED. GAS FROM THE DAMAGED 6" MAIN THEN MIGRATED INTO 14 W. PROVIDENCE RD AND AT APPROXIMATELY 1315 THERE WAS AN IGNITION INSIDE THE HOME. PECO GAS CREWS THEN EXCAVATED DOWN AND INSTALLED A CLAMP OVER THE DAMAGED SECTION OF 6" MAIN AT APPROXIMATELY 1545. PECO INVESTIGATION IS CONTINUING.
2024-05-31 11:04 | NO | YES | NO | 20230062 | 38702 | 2023-10-26 12:39 | ORIGINAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2023-09-27 02:16 | EASTERN | YES | 2023 | WASHINGTON PIKE AND VANADIUM ROAD | BRIDGEVILLE | ALLEGHENY | PA | 15017 | 40.3702 | -80.1008 | YES | YES | [7 empty] | 2023-09-27 02:29 | 1380223 | 1380525 | NATURAL GAS |  | 4970 | 48.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 69 | 2023-09-27 00:25 | NO |  |  | 2023-09-27 00:44 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 10 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.279 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 128591 | 128591 | 31608 | 31608 | 0 | 0 |  | 4.88 | 24254 | 24254 | 237 | 237 | 184690 | 85972.7859743720434688487712665406427221 | 184690 | 2 | 0 | 17 | 0 | 0 | 67 | 2 | 171 | 175 | 200 | 192.619(A)(1) | 1982-06-03 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 33 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA TELEMETRY DID NOT TRIGGER ALERTS OR ALARMS AT THE TIME OF THE INCIDENT. GAS CONTROL WAS NOTIFIED BY COLUMBIA'S INTEGRATION CENTER AT THE TIME OF THE INCIDENT. THE INCIDENT WAS CLEARLY THE RESULT OF EXCAVATOR DAMAGE BY A THIRD-PARTY CONTRACTOR. NO INVESTIGATION WAS WARRANTED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2023553872 |  |  | FACILITY OWNER | YES | YES | 45 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | RICHARD BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 7243217155 |  | RICHARD BURKE | rburke@nisource.com | 7243217155 | BRIAN MCCAUL | VICE PRESIDENT GAS OPERATIONS | 4129926929 | bmccaul@nisource.com | AT 00:15 ON SEPTEMBER 27, 2023, COLOSIMO CONSTRUCTION, A THIRD-PARTY SUBCONTRACTOR WORKING FOR PENNSYLVANIA AMERICAN WATER INSTALLING A WATER MAIN STRUCK AND DAMAGED A 10 INCH HIGH PRESSURE STEEL MAIN WITH A HYDRAULIC HAMMER CAUSING A GAS LOSS OF 4.9 MILLION CUBIC FEET OF GAS. COLUMBIA'S FACILITY LOCATORS CORRECTLY MARKED THE SECTION OF MAINLINE THAT WAS DAMAGED. BECAUSE OF THIS DAMAGE, APPROXIMATELY 69 BUILDINGS WERE EVACUATED, AND COLUMBIA HAD TO SHUT OFF SERVICE TO 19 CUSTOMERS FOR 45 HOURS WHILE REPAIRS WERE MADE.
2024-05-31 11:04 | NO | NO | NO | 20230063 | 38704 | 2023-10-26 14:46 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-09-26 23:04 | PACIFIC | YES | 2023 | 9208 ATLANTIC AVE | SOUTH GATE | LOS ANGELES | CA | 90280 | 33.948 | -118.1804 | [6 empty] | YES |  |  | 2023-09-27 05:55 | 1380225 | 1380442 | NATURAL GAS |  | 6700 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-09-26 17:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-09-26 16:58 | 2023-09-26 17:17 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 46 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1980 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 0 |  | 6 | 40200 | 40200 | 6 | 6 | 55206 | 36359.1317601266761531190926275992438563 | 55206 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 1980-06-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | GRADER/SCRAPER | BUILDING CONSTRUCTION | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [143 empty] | YES | [26 empty] | FRANK SANTA CRUZ |  | fsantacruz@socalgas.com | 2134070168 |  |  |  |  | FRANK SANTA CRUZ |  | 2134070168 | fsantacruz@socalgas.com | ON 9/26/2023 SOCALGAS RESPONDED TO AN EXCAVATION INCIDENT. A THIRD-PARTY CONTRACTOR STRUCK A 6IN STEEL GAS MAIN WITH GRADING EQUIPMENT WHICH CAUSED THE RELEASE OF NATURAL GAS. SOCALGAS CREWS CONTROLLED THE FLOW OF GAS AND ABANDONED THE MAIN AS PART OF THE PERMANENT REPAIRS. UPON INVESTIGATION OF THE INCIDENT, IT WAS DISCOVERED THAT THE THIRD-PARTY CONTRACTOR WAS PERFORMING EXCAVATION ACTIVITIES WITHOUT A VALID USA TICKET. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE CPUC ONCE SOCALGAS WAS MADE AWARE OF MEDIA COVERAGE AND THEN REPORTED TO DOT ONCE GAS RELEASE REACHED 3MM.
2024-05-31 11:04 | NO | YES | YES | 20230064 | 38755 | 2023-11-06 17:38 | ORIGINAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2023-10-05 15:00 | CENTRAL | YES | 2023 | 310 SE OLD CANNON BALL RD | HOLT | CLINTON COUNTY | MO | 64048 | 39.4575 | -94.3359 | [6 empty] | YES |  |  | 2023-10-05 18:29 | 1380998 | 1381071 | NATURAL GAS |  | 56 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2023-10-05 15:09 | YES | OPERATOR | 2023-10-05 15:15 | 2023-10-05 15:15 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 63 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | COLD ROLLED SEAM | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | GAS BLEEDING BY STOPPLE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 261 | 261 | 500 | 500 | 0 | 0 |  | 10.96 | 614 | 614 | 0 | 0 | 1375 | 779.99832936892701856143667296786389414 | 1375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 125 | 150 | 192.619(A)(3) | 1962-04-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ERIN MILKERT | MANAGER DISTRIBUTION INTEGRITY | erin.milkert@spireenergy.com | 314-349-2932 |  | ERIN MILKERT | erin.milkert@spireenergy.com | 314-349-2932 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A COMPANY CONTRACTOR CREW WAS A PERFORMING A 12-INCH STEEL MAIN RELOCATION AND RETIRING A SECTION OF MAIN BETWEEN 2 STOPPLE FITTINGS. THE STOPPLES WERE IN POSITION TO SHUT OFF THE FLOW OF GAS AND THE PIPE HAD BEEN CUT BETWEEN THE STOPPLES AND BLOWN DOWN. THE CONTRACTOR EMPLOYEE WAS PREPARING TO CAP DOWNSTREAM OF ONE STOPPLE. TWO VENT STACKS (V1 & V2) WERE INSTALLED DOWNSTREAM OF THE STOPPLE WITH A VALVE AND AIR HANDLER ON THE VENT NEAREST THE STOPPLE FITTING (V1). THE CONTRACTOR EMPLOYEE INSERTED A GRIPPER PLUG IN THE 12-INCH MAIN UP TO THE V1 VENT STACK LOCATION. GAS WAS BLEEDING PAST THE STOPPLE FITTING. THE VALVE ON V1 VENT STACK WAS CLOSED. THIS RESULTED IN A PRESSURE BUILD-UP BETWEEN THE STOPPLE FITTING AND THE GRIPPER PLUG AND CAUSED THE GRIPPER PLUG TO BE EJECTED FROM THE OPEN-CUT END OF THE 12-INCH STEEL MAIN. THE GRIPPER PLUG CAUSED A HAND INJURY WITH THE CONTRACTOR EMPLOYEE AND HE WAS ADMITTED TO THE HOSPITAL FOR TREATMENT. A 48-HOUR UPDATE TO THE NRC WAS MADE ON OCTOBER 5, 2023 AT 18:49 - REPORT NUMBER 1380998.
2024-05-31 11:04 | NO | YES | NO | 20230065 | 39249 | 2023-11-09 18:13 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2023-10-09 14:36 | CENTRAL | YES | 2023 | 321 LINCOLN AVE. | WOODSTOCK | MCHENRY | IL | 60098 | 42.3167 | -88.4507 | [5 empty] | YES |  |  |  | 2023-10-09 15:10 | 1381297 | 1381456 | NATURAL GAS |  | 238 | 0.152 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-10-09 14:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 52 | 2023-10-09 13:09 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-10-09 14:53 | 2023-10-09 13:09 | 2023-10-09 14:36 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2018 | 2018 |  |  |  |  | 2 | ASTM D2513 | DURA-LINE POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 1.5 | 7 | [7 empty] | CLASS 3 LOCATION | 1700000 | 1700000 | 20000 | 20000 | 5000 | 5000 | 0 | 0 |  | 4.36 | 1038 | 1038 | 1 | 1 | 1726039 | 729604.2261385753190453686200378071833649 | 1726039 | 8 | 0 | 44 | 2 | 0 | 44 | 8 | 22.2 | 23 | 25 | 192.619(A)(2) | 2018-10-09 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 11 | 1 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SEWER LATERAL CLEANING | [153 empty] | YES | LETICIA QUEZADA | DIR COMPLIANCE AND PIPELINE RISK MANAGEMENT | lquezad@southernco.com |  |  | LETICIA QUEZADA | dir compliance and pipeline risk management |  | LETICIA QUEZADA | DIR COMPLIANCE AND PIPELINE RISK MANAGEMENT | 6305142036 | lquezad@southernco.com | THE CITY OF WOODSTOCK HIRED A SEWER CONTRACTOR TO PERFORM SEWER CLEANOUT WORK. AT APPROXIMATELY 12:35PM CST, A REPRESENTATIVE FROM THE CITY OF WOODSTOCK CALLED A COMPANY SUPERVISOR DIRECTLY AND INFORMED HIM THE MAIN WAS HIT IN THE SEWER BY THEIR CONTRACTOR. AT APPROXIMATELY 12:50 PM CST, COMPANY CUSTOMER SERVICE REPRESENTATIVE RECEIVES PHONE CALL FROM THE SEWER CONTRACTOR REPORTING THE DAMAGE. INITIAL INVESTIGATIONS INDICATE THAT WHILE PERFORMING CONTRACTED DUTIES, THE CONTRACTOR DAMAGED A NATURAL GAS MAIN AT THE INTERSECTION OF TRYON ST. AND LINCOLN AVE. WHILE COMPANY CREWS WERE IN THE PROCESS OF SHUTTING OFF THE FLOW OF GAS, AN EXPLOSION OCCURRED AT 321 LINCOLN AVE. IT IS BELIEVED THAT THE GAS FROM THE DAMAGED MAIN TRAVELED THROUGH THE SEWER AND INTO THE PREMISE, CAUSING A SUBSEQUENT HOUSE EXPLOSION. NO ONE WAS INSIDE THE PREMISE AT THE TIME OF THE EXPLOSION. THERE WERE NO FATALITIES AND THE ONLY REPORTED INJURIES WERE TO TWO FIREFIGHTERS THAT WERE TAKEN TO THE HOSPITAL FOR OBSERVATION AND WERE RELEASED. GAS MAIN WAS PREVIOUSLY INSTALLED THROUGH THE SANITARY SEWER BY A SECOND PARTY CONTRACTOR IN 2018. NOTE: IN PART F, THE INDIVIDUAL THAT FAILED DRUG SCREEN WAS A MANAGEMENT EMPLOYEE AND WAS NOT PART OF THE CREWS PERFORMING EMERGENCY RESPONSE AND REPAIR ACTIVITIES.
2024-05-31 11:04 | NO | NO | NO | 20230066 | 38816 | 2023-11-10 17:23 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-10-13 11:44 | PACIFIC | YES | 2023 | 4200 VALLEY BLVD | WALNUT | LOS ANGELES | CA | 91789 | 34.035 | -117.825 |  | YES |  | YES | [5 empty] | 2023-10-13 20:57 | 1381706 | 48hr update NRC#1381791 | NATURAL GAS |  | 3664 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-13 11:44 | NO |  |  | 2023-10-13 11:58 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 15 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | UNKNOWN |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.322 | [6 empty] | OTHER | [8 empty] | THIRD PARTY DIG IN DAMAGE | CLASS 3 LOCATION | 0 | 0 | 15000 | 15000 | 20000 | 20000 | 0 | 0 |  | 6 | 21984 | 21984 | 0 | 0 | 56984 | 31203.0969803081800850661625708884688091 | 56984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 47 | 52 | 192.621 M | 2013-01-07 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | B230670145 | N/A |  | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | jjcervantes@socalgas.com | 310-970-4854 | 909-335-7895 | JAMES CERVANTES | jjcervantes@socalgas.com | 310-970-4854 | JAMES CERVANTES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 310-970-4854 | jjcervantes@socalgas.com | ON 10-13-2023, A THIRD-PARTY CONTRACTOR DAMAGED AN 8-INCH STEEL GAS MAIN AT 4200 VALLEY BLVD, WALNUT, CA WHILE GRADING. SOCALGAS CREW RESPONDED AND CONTROLLED THE RELEASE OF GAS. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. INVESTIGATION OF THE INCIDENT SHOWED THERE WAS A VALID USA TICKET. HOWEVER, THE CONTRACTOR'S EXCAVATION PRACTICES WERE INADEQUATE AS IT FAILED TO POT-HOLE THE 8-INCH MAIN. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE EXCEEDING 3,000,000 CUBIC FEET. NOTE: ON 11-16-2023 A CHANGE WAS MADE TO PART A 4 TO REFLECT THE REQUEST FROM PHMSA TO CHANGE THE TIME FROM TIME INCIDENT BECAME REPORTABLE TO THE TIME THE COMPANY WAS NOTIFIED. PER PHMSA NOTE "EARLIEST TIME WOULD BE THE TIME THE 3RD PARTY NOTICED THE LEAK. A4 IS NOT TO BE CONFUSED WITH THE TIME OF CONFIRMED DISCOVERY."
2024-05-31 11:04 | NO | YES | NO | 20230067 | 39390 | 2023-11-15 16:31 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2023-10-15 14:55 | EASTERN | YES | 2023 | TEVEBAUGH ROAD | FREEDOM | BEAVER | PA | 15042 | 40.666 | -80.2159 |  |  |  | YES | [5 empty] | 2023-10-15 16:56 | 1381816 | 138956 | NATURAL GAS |  | 0 | 48 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-15 14:55 | NO |  |  | 2023-10-15 15:00 | 2023-10-15 15:00 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1985 | UNKNOWN | [7 empty] | OTHER | NO ISSUE WITH MATERIAL FOR THIS EVENT | [9 empty] | OTHER | [8 empty] | THERE WAS NO RELEASE OF GAS. THIS INCIDENT WAS REPORTED AS A SIGNIFICANT EVENT BECAUSE GAS SERVICE WAS SHUT OFF FOR SAFETY TO 3,728 CUSTOMERS. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1353839 | 1353839 | 89181 | 89181 | LODGING, MEALS, ETC. FOR RESPONDING EMPLOYEES. | 4.88 | 0 | 0 | 234 | 234 | 1443254 | 609863.9878905406429349338374291115311909 | 1443254 | 37 | 0 | 3691 | 0 | 0 | 3691 | 37 | 15 | 15 | 18 | 192.619(A)(4) | 1999-06-07 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | OTHER | CUSTOMER NO GAS CALLS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SLUG OF AIR ENTERED COLUMBIA'S SYSTEM FROM THE MERIDIAN WELL PURCHASE POINT. | [47 empty] | MATTHEW MICELI | OPERATIONS COMPLIANCE MANAGER | mmiceli@nisource.com | 7248122844 |  | MATTHEW MICELI | mmiceli@nisource.com | 7248122844 | BRIAN MCCAUL | VICE PRESIDENT GAS OPERATIONS | 4129926929 | bmccaul@nisource.com | ON OCTOBER 15, 2023, COLUMBIA BEGAN RECEIVING "NO GAS" CALLS FROM CUSTOMERS IN ECONOMY, PA. SERVICE TECHNICIANS REPORTED NORMAL PRESSURE BUT ALSO REPORTED EVIDENCE OF AIR IN THE SYSTEM. THIS CONTINUED THROUGHOUT THE MORNING. COLUMBIA'S SYSTEMS WERE SUPPLIED BY A LOCAL PRODUCER IN CLOSE PROXIMITY TO THE MEDIUM PRESSURE SYSTEMS. IT WAS CONCLUDED THAT AIR HAD BEEN INTRODUCED TO THE COLUMBIA GAS SYSTEM THROUGH THE MERIDAN WELL PURCHASE POINT AND THEREFORE, FOR SAFETY REASONS, GAS WAS TURNED OFF TO THE TWO MEDIUM PRESSURE SYSTEMS SO THE AIR COULD BE PURGED FROM THE SYSTEMS. THIS AFFECTED 3,728 CUSTOMERS. THERE WERE TWO MEDIUM PRESSURE SYSTEMS AFFECTED. PART E (ADDITIONAL OPERATING INFORMATION) DOES NOT ALLOW THE INCLUSION OF TWO SYSTEMS. BELOW IS THE REQUIRED INFORMATION FOR THE SECOND SYSTEM: E1. ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT (PSIG) 21 E2. NORMAL OPERATING PRESSURE AT THE POINT AND TIME OF THE INCIDENT (PSIG) 21 E3. MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) AT THE POINT AND TIME OF THE INCIDENT (PSIG) 40 E3A. MAOP ESTABLISHED BY 49 CFR SECTION: 192.619 (A)(4) E3B. DATE MAOP ESTABLISHED: 03/20/09. E4. DESCRIBE THE PRESSURE ON THE SYSTEM RELATING TO THE INCIDENT: PRESSURE DID NOT EXCEED MAOP. E5. TYPE OF ODORIZATION SYSTEM FOR GAS AT POINT OF FAILURE: NONE. E6. ODORANT LEVEL NEAR THE POINT OF FAILURE MEASURED AFTER FAILURE: NOT MEASURED E7. WAS SUPERVISORY CONTROL DATA ACQUISITION (SCADA)-BASED SYSTEM IN PLACE ON THE PIPELINE OR FACILITY INVOLVED IN THE INCIDENT? NO. E8. WAS AN INVESTIGATION INITIATED INTO WHETHER OR NOT THE CONTROLLER(S) OR CONTROL ROOM ISSUES WERE THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT? NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT.
2024-05-31 11:04 | NO | YES | NO | 20230068 | 38814 | 2023-11-16 15:35 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2023-10-17 12:45 | EASTERN | YES | 2023 | 565 E MILWAUKEE AVE | DETROIT | WAYNE | MI | 48202 | 42.3719 | -83.0656 | [6 empty] | YES |  |  | 2023-10-19 08:15 | 1382137 | 1382278 | NATURAL GAS |  | 4872 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-17 12:45 | NO |  |  | 2023-10-17 12:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1900 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 4 | 12 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 53500 | 53500 | 67600 | 67600 | 0 | 0 |  | 3.1 | 15103 | 15103 | 0 | 0 | 136203 | 62443.1544932651688788279773156899810964 | 136203 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 7.5 | 10 | 10 | 192.619(A)(3) | 1/1/1899 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | OTHER | NOTIFICATION FROM 2ND PARTY CONTRACTOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 2023080805604 |  |  | FACILITY OWNER | YES | YES | 34 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | UNMAPPED 6" STUB EXTENDING 4' SOUTH OFF OF 12" CAST IRON MAIN INSTALLED IN 1899 | [169 empty] | JUSTIN MORRIS |  | justin.morris@dteenergy.com | [5 empty] | MARINA DARLING |  | 5868724760 | marina.darling@dteenergy.com | 2ND PARTY CONTRACTOR IMPACTED AN OBJECT WHILE BORING FOR NEW GAS MAIN AT 12:45 ON 10/17/23. THIS OBJECT IN-TURN IMPACTED A REDUCING FITTING ON A 12" 10 PSI CAST-IRON MAIN THAT WAS ADJACENT TO THE BORE PATH, CAUSING A CRACK AND A LEAK. THE REDUCING FITTING WAS ON AN UNMAPPED STUB FROM ACTIVITY DONE IN YEAR 1950. GAS WAS SHUT OFF AT 02:28 ON 10/18/23. REPAIR ACTIVITIES WERE INITIALLY NOT EXPECTED TO EXCEED $10K TOTAL COST, NOR ANY OTHER REPORTING THRESHOLD, SO MICHIGAN PUBLIC SERVICE COMMISSION WAS NOT INITIALLY NOTIFIED. OPERATIONS UPDATED AT 07:33 THE FOLLOWING MORNING THAT A DECISION HAD BEEN MADE TO REPLACE 25' OF THE MAIN RATHER THAN PERFORM THE INITIALLY INTENDED REPAIR, IN ORDER TO AVOID CUSTOMER OUTAGES. THIS CHANGE CAUSED THE REPAIR COST TO EXCEED THE $10K THRESHOLD AND THE MPSC INCIDENT REPORTING LINE WAS NOTIFIED AT 08:19 ON 10/18/23. AFTER REPAIR, GAS LOSS WAS CALCULATED AND ESTIMATED AT 4872MCF, WHICH CAUSED THIS INCIDENT TO BE PHMSA REPORTABLE. ALSO NOTIFIED CHEMICAL SAFETY BOARD (CSB).
2024-05-31 11:04 | NO | NO | NO | 20230069 | 38836 | 2023-11-20 13:40 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2023-10-12 17:15 | EASTERN | YES | 2023 | 11301 MAPLEVIEW DRIVE | SILVER SPRING | MONTGOMERY COUNTY | MD | 20902 | 39.0427 | -77.0688 | YES |  |  |  |  | YES | YES |  |  | 2023-11-03 13:40 | 1383374 | 1383517 | NATURAL GAS |  | 5950 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-10-12 17:15 | NO |  |  | 2023-10-12 17:46 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | IN A WATER FLOODED EXCAVATION | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN FREQUENCY OR SEAMLESS | UNKNOWN | [6 empty] | OTHER | [8 empty] | WATER MAIN LINE AT A 100-PSI BURST CREATING A HOLE AT THE BOTTOM OF THE 4-INCH GAS MAIN. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 10947 | 10947 | 383 | 383 | ADMINISTRATIVE COSTS | 1.26 | 7497 | 7497 | 0 | 0 | 18827 | 10384.9784805976612969187145557655954631 | 18827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 25 | 192.619(A)(2) | 1978-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 4-INCH STEEL NATURAL GAS LINE WAS A TWO-WAY FEED SYSTEM AND PRESSURE DID NOT DROP BELOW ALARM SET POINT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER ESCAPING FROM A BURST WATER MAIN. | [154 empty] | ARTHUR M GROFF | SUPERVISOR DOT PIPELINE SAFETY | agroff@washgas.com | 5713187993 |  | ART GROFF | agroff@washgas.com | 5713187993 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON OCTOBER 12, 2023, AT APPROXIMATELY 17:15 HOURS WASHINGTON GAS WAS NOTIFIED OF A POSSIBLE LEAK AT 11301 MAPLEVIEW DR SILVER SPRING MD. WASHINGTON GAS DISPATCHED CREWS TO THE LOCATION WHO ARRIVED AND PERFORMED AN ASSESSMENT OF SITUATION, WHICH RESULTED IN THE IDENTIFICATION OF A LEAKING 4-INCH STEEL MAIN LINE. WASHINGTON SURBURBAN SANITARY COMMISSION WAS WORKING ON A LEAKING WATER MAIN IN THE AREA THAT EVENTUALLY CAUSED THE GAS MAIN LEAK. THE CAUSE OF THE LEAK ON THE 4-INCH GAS MAIN LINE WAS A LEAK THAT ORIGINATED ON A 30-INCH WATER MAIN LINE AT A 100 PSI WHICH CREATED AN APPROXIMATELY 3-INCH DIAMETER HOLE AT THE BOTTOM OF THE 4-INCH GAS MAIN. THE GAS MAIN WAS SUBMERGED IN THE EXCAVATION DUE TO THE WATER LEAK. ON OCTOBER 14 AT APPROXIMATELY 1220 HOURS THE GAS WAS TURNED OFF UTILIZING VALVES, STOPPLE FITTING AND SQUEEZE OFF METHOD.
2024-05-31 11:04 | NO | YES | YES | 20230070 | 38870 | 2023-11-30 09:15 | ORIGINAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-10-16 11:18 | CENTRAL | YES | 2023 | 800 WEST MAIN STREET | ANOKA | ANOKA | MN | 55303 | 45.2085 | -93.4079 | [5 empty] | YES |  |  |  | 2023-10-31 15:12 | 1383136 | 1383193 | NATURAL GAS |  | 576 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 8 | 2023-10-16 11:18 |  |  |  | 2023-10-16 11:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2021 | 2021 |  |  |  |  | 6 | PE2708,SDR11.5 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2708 | MECHANICAL PUNCTURE | 4 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 969 | 969 | 2350 | 2350 | 0 | 0 |  | 4.2717 | 2460 | 2460 | 0 | 0 | 5779 | 3239.170121861899405483931947069943289225 | 5779 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 50 | 66 | 192.619(A)(2) | 2021-11-05 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 232842550 |  |  | CONTRACT LOCATOR | YES | YES | 2 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | dean.headlee@centerpointenergy.com | 612.321.5366 | 612.321.0000 | DEAN HEADLEE | dean.headlee@centerpointenergy.com | 612.321.5366 | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612.321.5366 | dean.headlee@centerpointenergy.com | SHAFER CONTRACTING CO., INC. DAMAGED AN UNMARKED 6" PLASTIC CLASS 6 (50-55PSIG) GAS MAIN WITH A BACKHOE DURING ROAD RECONSTRUCTION WHILE WORKING UNDER GSOC TICKET #232891215. THE EXCAVATOR WAS WORKING ON A ROAD PROJECT FOR MNDOT WITH A PROJECT START OF EXCAVATION ON 04/03/23. DURING THIS TIME THERE WERE MULTIPLE UPDATE TICKETS AND FIELD MEETS WITH THE LINE LOCATOR(S) AND THE EXCAVATOR(S). ON THE MORNING OF THE DAMAGE DURING A SITE MEET WITH THE EXCAVATOR AND THE LINE LOCATOR, THE LINE LOCATOR WAS ALLEGED TO HAVE CLEARED THE WORK AREA IN THE STREET WHERE THE MAIN WAS CONTACTED, TELLING THE EXCAVATOR THAT THE LIVE MAIN WAS BEHIND THE CURB (SOUTH OF THE CURB) WHERE YELLOW HARD MARKS DENOTED THE PRESENCE OF GAS FACILITIES. AS A RESULT, THE LOCATOR FAILED TO MARK THE LIVE GAS MAIN, AND IT WAS SUBSEQUENTLY DAMAGED WITH MECHANIZED EQUIPMENT. THE CONTRACT LOCATE VENDOR WAS UNABLE TO PROVIDE SUFFICIENT DOCUMENTATION OF THE SITE MEETING THAT WOULD COUNTER THE ALLEGATIONS OF THE EXCAVATOR. NOTE, AT THE TIME OF THE DAMAGE THERE WAS NO EVIDENCE OF MINIMUM REPORTABLE CRITERIA FOR A MNOPS OR FEDOPS REPORT. IT WASN'T UNTIL A FIELD MEETING WITH MNDOT (JULIE) ON 10/24/23 THAT CENTERPOINT ENERGY'S DAMAGE PREVENTION COORDINATORS WERE MADE AWARE OF THE INJURY THAT OCCURRED ON THE DAY OF THE DAMAGE.
2024-05-31 11:04 | NO | YES | YES | 20230071 | 38907 | 2023-12-01 13:54 | SUPPLEMENTAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2023-11-02 12:12 | EASTERN | NO | 2023 | 7 BRICK ROW | WAPPINGERS FALLS | DUTCHESS | NY | 12590 | 41.6014 | -73.918 |  | YES | [7 empty] | 2023-11-02 12:54 | 1383286 | 1383403, 1383446 | NATURAL GAS |  | 6 | 0 | NO | [5 empty] | 0 | YES | 0 | 5 | 0 | 0 | 4 | 9 | YES | 2023-11-02 12:15 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 6 | YES | 25 | 2023-11-02 12:15 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-11-02 12:18 | 2023-11-02 12:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1952 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THE PIPE WAS HIT DURING EXCAVATION AND IS STILL UNDER INVESTIGATION. | CLASS 3 LOCATION | 751800 | 751800 | 4581 | 4581 | 25867 | 25867 | 2250 | 2250 | CONTRACTOR CHARGES FOR LEAK SURVEY. | 3.7871 | 23 | 23 | 0 | 0 | 784521 | 331474.8159794642032588695652173913043478 | 784521 | 0 | 0 | 6 | 1 | 5 | 9 | 0 | 24 | 24 | 30 | 192.619(C) | 1952-05-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 2.5 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 0918300138801 | UDIG NY |  | CONTRACT LOCATOR | YES | YES | 9 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | THE ROOT CAUSE HAS NOT BEEN IDENTIFIED AND IS STILL UNDER INVESTIGATION. | [169 empty] | JERRY AMATO | DIRECTOR - GAS COMPLIANCE | jamato@cenhud.com | 845-416-3887 |  | JERRY AMATO | jamato@cenhud.com | 845-416-3887 | ERIC KISZKIEL | MANAGER - GAS ENGINEERING AND OPERATIONS | 845-486-5472 | ekiszkiel@cenhud.com | A CONTRACTOR WAS PERFORMING WORK FOR CENTRAL HUDSON THAT INCLUDED A MAIN AND SERVICE REPLACEMENTS ON BRICK ROW IN WAPPINGERS FALLS. THE SCOPE OF WORK CONSISTED OF REPLACING APPROXIMATELY 200 FT. OF 2-INCH STEEL MAIN AND 6 SERVICES. THE MAOP OF THE MAIN IS 30 PSIG. THE GAS SERVICES ON THE STREET WERE EITHER STEEL OR PLASTIC. ON THURSDAY, NOVEMBER 2, 2023, AT APPROXIMATELY 12:15 PM, CENTRAL HUDSON WAS NOTIFIED FROM A CENTRAL HUDSON EMPLOYEE AT 7 BRICK ROW, WAPPINGERS FALLS, OF A GAS LINE THAT WAS HIT WHERE THE COMPANY CONTRACTOR WAS EXCAVATING, WHICH RESULTED IN AN EXPLOSION AND STRUCTURE FIRE. MULTIPLE REPORTS OF A POSSIBLE GAS EXPLOSION WERE RECEIVED AFTER THIS CALL BY OUR DISPATCH CENTER. THE RESPONDING FIRE DEPARTMENTS PERFORMED EVACUATIONS AND THEN A SEARCH AND RESCUE EFFORT FOR THE PUBLIC AND WORKERS ON SITE WAS COMPLETED. A TOTAL OF 15 PEOPLE WERE TREATED FOR MEDICAL EVALUATION BY EMERGENCY MEDICAL SERVICES AND TRANSPORTED IF NECESSARY. IN PART A22 OF THIS REPORT, THE GENERAL PUBLIC EVACUATED IS ESTIMATED AT 25 PEOPLE AND CANNOT BE CONFIRMED DUE TO THE FIRE DEPARTMENT RESPONSE AND CENTRAL HUDSON CREWS ARRIVING AFTER THE RESIDENTS HAVE BEEN EVACUATED ALREADY. A CENTRAL HUDSON GAS FOREMAN WAS ON SITE AT THE TIME OF DAMAGE AND DURING THE IGNITION. THE FIRST CENTRAL HUDSON RESPONDER ARRIVED ON SITE AT 12:19 PM AND THE BUILDING WAS ON FIRE. ADDITIONAL CENTRAL HUDSON PERSONNEL INCLUDING COMMERCIAL REPRESENTATIVES, GAS CONSTRUCTION CREWS, AND SUPERVISORS WERE CONTACTED AND ARRIVED TO THE SITE. AT 12:33, THE GAS CREW SHUT GAS OFF TO BRICK ROW BY CLOSING A DISTRIBUTION LINE VALVE. AT 12:43 PM, THE ELECTRICITY WAS SHUT OFF THAT SERVICES BRICK ROW AND THE ADJACENT AREA. THE NATURAL GAS MAIN AND SERVICES WERE RETIRED AND ABANDONED ON BRICK ROW FOLLOWING THIS INCIDENT. ONCE THE FIRE WAS CONTAINED, CENTRAL HUDSON AND CONTRACTOR CREWS PERFORMED LEAK SURVEYS OF THE IMMEDIATE AND SURROUNDING AREAS TO ENSURE THERE WERE NO ADDITIONAL RISKS. GAS ODORANT READINGS WERE TAKEN IN THE SURROUNDING AREAS TO VERIFY APPROPRIATE ODORIZATION OF GAS AND WAS CONFIRMED. CENTRAL HUDSON IS CONDUCTING AN ONGOING INVESTIGATION OF THE INCIDENT. SUPPLEMENTAL NOTIFICATIONS WILL BE PROVIDED, AS APPROPRIATE, UNTIL A CONCLUSION ON THE CAUSE OF THE INCIDENT IS ASCERTAINED.
2024-05-31 11:04 | NO | YES | NO | 20230072 | 38898 | 2023-12-04 12:02 | ORIGINAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2023-11-04 08:00 | EASTERN | YES | 2023 | 126 PRINCE ST | NEEDHAM | NORFOLK | MA | 02492 | 42.276 | -71.2219 |  |  | YES | [6 empty] | 2023-11-04 09:31 | 1383441 | 1383554 | NATURAL GAS |  | 72 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-11-04 07:51 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 72 | YES | 0 | 2023-11-04 07:48 | YES | OPERATOR | 2023-11-04 07:52 | 2023-11-04 08:16 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 19 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1963 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 1 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.133 | [6 empty] | OTHER | [8 empty] | EXCAVATION DAMAGE FROM CONTACT WITH SMALL EXCAVATOR | CLASS 3 LOCATION | 350900 | 350900 | 2771 | 2771 | 37907 | 37907 | 0 | 0 | 2A: BASED ON ASSESSED DWELLING VALUE. RESPONSIBILITY FOR REIMBURSEMENT TBD. | 7.68 | 553 | 553 | 0 | 0 | 392131 | 165858.237948088395915429111531190926276 | 392131 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 55.9 | 55.9 | 60 | 192.619(A)(2) | 1963-06-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS AN EXCAVATOR DAMAGE BY 2ND PARTY CONTRACTOR. | [12 empty] | NO |  |  | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | UNKNOWN/OTHER | NATURAL GAS | YES | 2023431452 |  |  | CONTRACT LOCATOR | NO | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [142 empty] | YES | [27 empty] | KATHERINE SILVER | MANAGER COMPLIANCE | katherine.silver@eversource.com | 5088641836 |  | KATHERINE SILVER | katherine.silver@eversource.com | 5088641836 | KATHERINE SILVER | MANAGER COMPLIANCE | 5088641836 | katherine.silver@eversource.com | DURING A PLANNED SERVICE LINE REPLACEMENT, A SECOND PARTY CONTRACTOR STRUCK A SERVICE LINE CAUSING AN IGNITION AND HOUSE FIRE. THE RESIDENTS WERE NOT HOME AT THAT TIME. A CONTRACTOR EMPLOYEE SUSTAINED A MINOR INJURY. THE SERVICE LINE WAS CUT OFF AT THE MAIN WHEN THE SITUATION WAS DEEMED SAFE. THE BUILDING WAS DEMOLISHED THE DAY OF THE INCIDENT. G3.7: MINI EXCAVATOR WAS BEING UTILIZED. G3.12: ON NOVEMBER 4, THE ORIGINAL MARKS IN THE PUBLIC WAY SHOWING THE SERVICE LINE FROM THE SERVICE TEE TO THE PROPERTY LINE AT THE LEFT SIDE OF THE PROPERTY WERE VISIBLE AND ACCURATE. THERE WERE NO VISIBLE MARKINGS OR FLAGS ON THE PRIVATE PROPERTY. PRIVATE PROPERTY MARKINGS WERE EITHER NOT APPLIED OR NOT MAINTAINED. G3.14 THE CREW WAS MECHANICALLY EXCAVATING THE TRENCH FOR THE NEW SERVICE ON THE PRIVATE PROPERTY WHEN THEY STRUCK THE ACTIVE 1" STEEL SERVICE.
2024-05-31 11:04 | NO | YES | NO | 20230073 | 39481 | 2023-12-06 16:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2023-11-09 18:45 | EASTERN | NO | 2023 | NORTHSIDE DRIVE NW AT OLD POWERS FERRY ROAD | SANDY SPRINGS | FULTON | GA | 30339 | 33.9018 | -84.4275 | YES |  |  |  |  | YES |  |  |  | 2023-11-09 18:49 | 1383916 | 1384000 | NATURAL GAS |  | 17423 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-08 15:53 |  |  |  | 2023-11-08 16:13 | 2023-11-09 18:49 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 66 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2.5 | [7 empty] | CLASS 3 LOCATION | 2734 | 2734 | 3480 | 3480 | 75278 | 75278 | 0 | 0 |  | 1.83 | 31884 | 31884 | 0 | 0 | 113376 | 58238.645400707321516574669187145557656 | 113376 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 230 | 300 | 192.619(A)(4) | 1968-03-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 15.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 231102003911 |  | Unknown | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | ON NOVEMBER 8, 2023, AT APPROXIMATELY 15:53 HOURS, A THIRD-PARTY PARTY EXCAVATOR (WASHINGTON COMMUNICATION) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 6-INCH STEEL GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL ELECTRIC CONDUIT LINES AT THE INTERSECTION OF NORTHSIDE DRIVE AND OLD POWERS FERRY ROAD, SANDY SPRINGS, GA. UPON ARRIVAL, AGLC PERSONNEL SECURED THE AREA AND MONITORED THE SURROUNDING AREA FOR GAS MIGRATION. BASED ON A FIELD ASSESSMENT OF CONDITIONS SURROUNDING THE LOCATION OF THE INCIDENT AND TO NOT SHUT DOWN A LARGE METRO AREA SHOULD AN EXISTING VALVE NORTH OF THE DAMAGE BEEN USED IN CONJUNCTION WITH THE OTHER TWO VALVES OPERATED, A DECISION WAS MADE TO SQUEEZE THE PIPE AT A SAFE DISTANCE NORTH OF THE DAMAGE. UPON EXCAVATING TO EXPOSE THE EXISTING PIPE, IT WAS DISCOVERED THAT THE PIPE WAS APPROXIMATELY 66 INCHES DEEP AND UNDER APPROXIMATELY 36-INCHES OF ASPHALT, GAS WAS SHUT-OFF TO THE DAMAGED AREA ON NOVEMBER 8, 2023, AT 23:54 HOURS BY OPERATING TWO (2) VALVES AND PERFORMING ONE (1) SQUEEZE OFF OPERATION. A LOCATE REQUEST WAS MADE ON NOVEMBER 2, 2023, BY WASHINGTON COMMUNICATION (EXCAVATOR) TO LOCATE "W NORTHSIDE DR, OLD POWERS FERRY RD, LOCATE THE ENTIRE INTERSECTION FOR 50FT IN ALL DIRECTIONSBOTH SIDES OF THE RD AND WITHIN THE R/O/W ON BOTH SIDES OF THE ST, THIS IS A 3 LEG INT, IT DOES NOTINCLUDE LOCATING ALONG RIVERVIEW RD NW". AGLC FACILITIES WERE MARKED BY USIC LOCATING COMPANY TO SATISFY THIS REQUEST ON NOVEMBER 6, 2023, AT 11:26 HOURS. ON NOVEMBER 8, 2023, AT 13:00 HOURS, USIC REMARKED AGLC'S FACILITIES AS REQUESTED BY THE EXCAVATOR DUE TO FACILITY MARKINGS NO LONGER BEING VISIBLE. INVESTIGATION OF THE SITE REVEALED THAT THE LOCATE MARKS WERE ACCURATE AT THE POINT OF DAMAGE. HAD THE EXCAVATOR POTHOLED, IT WOULD HAVE DETERMINED THE LOCATION OF THE GAS MAIN. ONCE THE DAMAGED SECTION OF MAIN WAS EXPOSED AND ALL THE VARIABLES WERE OBTAINED TO PERFORM THE GAS LOSS CALCULATION, IT WAS IDENTIFIED THAT THE AMOUNT OF GAS RELEASED EXCEEDED THE THRESHOLD FOR REPORTING AND THE NATIONAL RESPONSE CENTER (NRC) WAS NOTIFIED AT THAT TIME ON NOVEMBER 9, 2023, AT 18:49 HOURS WHERE AN INITIAL NRC REPORT NUMBER 1383916 WAS CREATED. AN ADDITIONAL NRC REPORT NUMBER 1384000 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2024-05-31 11:04 | NO | YES | NO | 20230074 | 38920 | 2023-12-06 18:18 | ORIGINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2023-11-08 18:00 | PACIFIC | NO | 2023 | 24701 US 195 | PULLMAN | WHITMAN | WA | 99163 | 46.7603 | -117.2655 | YES | [6 empty] | YES | WILLIAMS TURNED MAINLINE VALVES OFF, AVISTA TURNED OFF STATION VALVES AS APPLICABLE | 2023-11-08 18:10 | 1383817 | 1383977 | OTHER GAS | N/A - NO GAS RELEASED | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-08 12:42 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-11-08 12:54 | 2023-11-08 13:08 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 41 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | GAS CUSTOMER OUTAGE | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | OTHER | INTERSTATE PIPELINE PIPE | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | OTHER | TOP OF THE INTERSTATE PIPELINE (WILLIAMS) PIPE WAS DAMAGED BY PLOW. NO RELEASE OF AVISTA GAS - REPORTABLE DUE TO LOSS OF SERVICE TO ~36,000 CUSTOMERS. | 12 | 12 |  | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 4600000 | 4600000 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 4600000 | 1943542.4354243546 | 4600000 | 3665 | 26 | 31588 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1971-06-15 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE GAS OUTAGE WAS BEYOND OPERATOR'S CONTROL | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM INTERSTATE TRANSMISSION PIPELINE (WILLIAMS) AS A RESULT OF PIPELINE RUPTURE AND ISOLATION. SEE WILLIAMS NRC CASE #1383793. | [20 empty] | YES | [26 empty] | JOSHUA FORT | SR. GAS ENGINEER | josh.fort@avistacorp.com | 509-495-2656 |  | RANDY BAREITHER | randy.bareither@avistacorp.com | 509-434-6783 | BRIAN SCHULTZ | MANAGER - NATURAL GAS COMPLIANCE AND INTEGRITY | 509-495-2162 | brian.schultz@avistacorp.com | ON WEDNESDAY 11/8/23, AT 1242 PACIFIC TIME, AVISTA BECAME AWARE OF PRESSURE ISSUES IN OUR SE WASHINGTON SERVICE AREA (PULLMAN GATE STATION). AT 1254 THE AVISTA GAS CONTROL ROOM (GCR) RECEIVED NOTIFICATION FROM WHITMAN COUNTY (WA) EMERGENCY DISPATCH THAT AN EXCAVATOR HAD HIT A GAS LINE AND GAS WAS BLOWING NEAR US HIGHWAY 195 MILEPOST 27 AND THAT THE HIGHWAY HAD BEEN SHUT DOWN. AT THE SAME TIME, THE AVISTA GCR RECEIVED NOTIFICATION FROM WILLIAMS PIPELINE GCR THAT THEY WERE EXPERIENCING GAS PRESSURE ISSUES WITH THEIR LEWISTON LATERAL GAS LINE AND HAD A TECH IN ROUTE TO INVESTIGATE. AVISTA PROVIDED WILLIAMS SOME OF THE DETAIL WE HAD JUST LEARNED FROM WHITMAN COUNTY DISPATCH. WITHIN A SHORT TIME, IT BECAME KNOWN THAT A FARMER HAD HIT WILLIAMS PIPELINE'S 12" TRANSMISSION LINE AND AVISTA WOULD LIKELY LOSE ALL GAS CUSTOMERS IN THE REGION. AVISTA MANAGEMENT PROCEEDED TO "STAND UP" ITS EMERGENCY OPERATING PLAN (EOP) TO RESPOND TO THE INCIDENT. (WILLIAMS NRC CASE #1383793) WITHIN A MATTER OF HOURS, AVISTA HAD LOST GAS SERVICE TO ROUGHLY 36,000 CUSTOMERS IN THE WASHINGTON TOWNS/CITIES OF PULLMAN, PALOUSE, ALBION, UNIONTOWN, COLTON, CLARKSTON AND ASOTIN AND THE IDAHO TOWNS/CITIES OF MOSCOW, TROY, DEARY, BOVILL, GENESEE, AND LEWISTON. AVISTA IMMEDIATELY CONTACTED THE AMERICAN GAS ASSOCIATION (AGA) TO SEEK THEIR ASSISTANCE IN MOBILIZING MUTUAL AID RESOURCES FROM OTHER GAS PROVIDERS IN THE REGION. AT APPROXIMATELY 1800, AVISTA CONTACTED THE NATIONAL RESPONSE CENTER AND REPORTED THE INCIDENT (AVISTA NRC CASE #1383817) DUE TO EXCESSIVE COSTS THAT WOULD BE EXPENDED TO RESOLVE THE OUTAGE. OVER THE NEXT TWO DAYS, A MASSIVE EFFORT WAS UNDERTAKEN TO TURN OFF ALL THE AFFECTED GAS CUSTOMERS, PRIMARILY WITH AVISTA PERSONNEL RESOURCES. ONCE WILLIAMS HAD COMPLETED THEIR REPAIRS AND REPRESSURIZED THEIR PIPELINE, AVISTA PROCEEDED TO REPRESSURE ITS HIGH- PRESSURE PIPELINE NETWORK. PURGE PLANS WERE ESTABLISHED AND RELIGHT AREAS WERE FORMALIZED BY GAS ENGINEERING AND GAS OPERATIONS PERSONNEL. THANKS TO GREAT ASSISTANCE FROM AGA, AVISTA'S MUTUAL AID REQUEST WAS ANSWERED BY EIGHT GAS COMPANIES AND MUNICIPALITIES FROM AS FAR AWAY AS SOUTH DAKOTA AND CALIFORNIA. ALTHOUGH SOME RELIGHTS HAD BEGUN AS EARLY AS FRIDAY 11/10/23, THE MAJOR RELIGHT EFFORTS BEGAN THE MORNING OF SATURDAY 11/11/23 WITH ASSISTANCE FROM MUTUAL AID PERSONNEL AND SOME LOCAL HVAC CONTRACTOR RESOURCES. RELIGHTS CONTINUED OVER THE COURSE OF THE NEXT FOUR DAYS. BY THE END OF THE DAY ON TUESDAY 11/14/23, THE FIRST WAVE OF VISITING ALL CUSTOMERS HAD BEEN COMPLETED AND OVER 95% OF CUSTOMERS WERE BACK IN SERVICE. CUSTOMERS WHO WERE NOT PRESENT DURING THE FIRST VISIT RECEIVED A DOORHANGER AND WERE INSTRUCTED HOW TO CONTACT AVISTA TO GET THEIR GAS SERVICE REESTABLISHED AT THEIR CONVENIENCE.
2024-05-31 11:04 | NO | YES | YES | 20230075 | 38940 | 2023-12-07 17:29 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2023-11-08 15:46 | CENTRAL | NO | 2023 | 7700 E 13TH, #69 | WICHITA | SEDGWICK | KS | 67206 | 37.7115 | -97.2472 | [5 empty] | YES |  |  |  | 2023-11-08 17:50 | 1383808 | 1383811, 1383997 | NATURAL GAS |  | 29.9 | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-08 15:46 | YES | OPERATOR | 2023-11-08 16:28 | 2023-11-08 16:07 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1998 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | OTHER | [8 empty] | AFTER INITIAL MECHANICAL PUNCTURE, THE LINE WAS CUT BY THIRD PARTY EXCAVATOR IN AN ATTEMPT TO INSERT A REPAIR FITTING. | CLASS 3 LOCATION | 0 | 0 | 500 | 500 | 1000 | 1000 | 159 | 159 | GAS LOST | 5.31 | 159 | 159 | 0 | 0 | 1818 | 819.66681198948108196786389413988657845 | 1818 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 18 | 18 | 60 | 192.619(A)(2) | 1998-10-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.9 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | OTHER | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | AUGER | FENCING | NO | [5 empty] | YES | 2 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | 9135303219 |  | RANDY SPECTOR | randy.spector@onegas.com | 9135303219 | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 9135303219 | randy.spector@onegas.com | ON NOVEMBER 18, 2023, AN INDIVIDUAL STRUCK A SERVICE LINE WHILE REPAIRING A PRIVACY FENCE. A LOCAL HANDYMAN WAS REPAIRING A PRIVACY FENCE AT 7700 E. 13TH STREET, UNIT 69, IN WICHITA, KANSAS, WHICH INVOLVED EXCAVATING AROUND KANSAS GAS SERVICE FACILITIES. THE HANDYMAN DID NOT LIVE AT THE RESIDENCE AND HAD NOT REQUESTED KANSAS GAS SERVICE LOCATE ITS FACILITIES BEFORE STARTING THE REPAIR. WHILE EXCAVATING WITH A 6" AUGER, THE HANDYMAN STRUCK A KANSAS GAS SERVICE SERVICE LINE. BASED ON A REVIEW OF THE SITE, IT APPEARS THE HANDYMAN ATTEMPTED TO REPAIR THE DAMAGED SERVICE LINE. WHEN KANSAS GAS SERVICE TECHNICIAN ARRIVED ON-SITE AS A RESULT OF A THIRD-PARTY LEAK CALL, THEY FOUND THE HANDYMAN UNCONSCIOUS IN THE EXCAVATION AREA. KANSAS GAS SERVICE'S TECHNICIAN MOVED THE HANDYMAN AWAY FROM THE EXCAVATION AREA AND CALLED 911. EMERGENCY SERVICES ARRIVED AT THE SCENE AND TRANSPORTED THE HANDYMAN TO A LOCAL HOSPITAL. KANSAS GAS SERVICE WAS ADVISED THE HANDYMAN PASSED AWAY APPROXIMATELY FOUR DAYS LATER AT THE HOSPITAL.
2024-05-31 11:04 | NO | YES | YES | 20230076 | 39491 | 2023-12-12 15:07 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2023-11-13 14:46 | EASTERN | NO | 2023 | 3332 WALWORTH AVENUE | CINCINNATI | HAMILTON | OH | 45226 | 39.118 | -84.4417 | [5 empty] | YES |  |  |  | 2023-11-13 17:35 | 1384207 | 1384233 | NATURAL GAS |  | 10 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2023-11-13 14:46 | OTHER | FIRE EXTINGUISHED ITSELF AFTER THE INITIAL BURST OF FLAME. | 10 | NO | 0 | 2023-11-13 14:46 | NO |  |  | 2023-11-13 14:46 | 2023-11-13 14:46 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1975 | UNKNOWN |  |  |  |  | 3 | PE-2306 | DUPONT ALDYL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 15000 | 0 | 0 | 0 | 0 |  | 5.79 | 58 | 58 | 0 | 0 | 15058 | 6380.946504928188440453686200378071833648 | 15058 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 24.95 | 24.95 | 35 | 192.619(A)(2) | 1975-10-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE WAS NOT A FACTOR | [12 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CREW DID NOT FOLLOW ESTABLISHED PROCEDURES. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CREW WAS ON SITE INVESTIGATING A GRADE 2 LEAK. WHILE CONDUCTING THE LEAK ANALYSIS AND TRYING TO PINPOINT THE LEAK'S LOCATION, A DAMAGE OCCURRED ON THE 3" PLASTIC MAIN. THE DAMAGE WAS CAUSED BY PROBING BAR HOLES TO TAKE READS AND PINPOINTING THE LEAK'S LOCATION. ONCE THE DAMAGE OCCURRED THE LEAK WAS THEN UPGRADED TO A GRADE 1 LEAK AND THE CREW BEGAN TO EXCAVATE TO MAKE REPAIRS. AT THIS TIME, THE CREW DID NOT FOLLOW PROCEDURE FOM-PR-1060 WORKING SAFELY IN A GASEOUS ENVIRONMENT. DURING THE PROCESS OF EXCAVATING THE LEAK TO MAKE REPAIRS, THE LEAKING GAS IGNITED CAUSING BURN INJURIES TO 2 EMPLOYEES. ONE OF THE EMPLOYEE'S INJURIES REQUIRED OVERNIGHT HOSPITALIZATION. THE GRADE 2 LEAK WAS REPAIRED AT A LATER DATE.
2024-05-31 11:04 | NO | YES | YES | 20230077 | 39070 | 2023-12-15 14:09 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2023-11-17 08:30 | CENTRAL | YES | 2023 | 1801 KIPLING @ WOODHEAD | HOUSTON | HARRIS | TX | 77098 | 29.7405 | -95.4047 | [5 empty] | YES | YES |  |  | 2023-11-17 11:00 | 1384557 | 1384618 | NATURAL GAS |  | 1280.452 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2023-11-17 08:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1280 | NO | 4 | 2023-11-17 09:00 |  |  |  | 2023-11-17 09:00 | 2023-11-17 10:40 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 8 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2023 | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | CENTRAL | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 12258 | 12258 | 761900 | 761900 | DAMAGE TO EQUIPMENT AND HOME | 6.452 | 8261 | 8261 | 0 | 0 | 782419 | 333257.3182290613676164120982986767485822 | 782419 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 44 | 44 | 60 | 192.619(A)(1) | 2023-07-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED THE THRESHOLD | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | < 18” |  | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | YES | 2381471224 | TEXAS 811 | Unknown | CONTRACT LOCATOR | YES | YES | 16 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | LESLIE J DAVENPORT | SR COMPLIANCE COORDINATOR | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 | SAM COOK | sam.cook@centerpointenergy.com | 713-967-8026 | JERRY GANN | REGIONAL OPERATIONS DIRECTOR | 713-967-7101 | jerry.gann@centerpointenergy.com | ON NOVEMBER 17, 2023, AT APPROXIMATELY 8:30AM, THE HOUSTON FIRE DEPARTMENT NOTIFIED CENTERPOINT ENERGY ABOUT A GAS LEAK AT THE 3600 BLOCK OF WOODHEAD AND KIPLING STREET IN HOUSTON TEXAS. ONCE CENTERPOINT ARRIVED ON SITE IT IDENTIFIED A GAS LINE HAD BEEN STRUCK BY MECHANIZED EQUIPMENT OPERATED BY MAIN LINE INDUSTRIES (MC2). THE DAMAGE OCCURRED ON A 2" POLYETHYLENE GAS LINE WHICH WAS AN OFFSET TO DECONFLICT THE 6" STEEL, WITH ANOTHER UTILITY PLACEMENT. WHILE THE CONTRACTOR WAS PREPARING THE SUB-BASE FOR THE PROPOSED ROADWAY, THE CONTRACTOR CAME IN CONTACT WITH CNP FACILITY WITH ROAD RECLAIMER (ASPHALT GRINDER). AFTER INITIAL REVIEW, IT WAS DETERMINED THAT MC2 HAD A VALID ONE CALL TICKET (NO. 2381471224) FOR THIS WORK, AND THE LOCATE VENDOR RESPONDED TO THE LOCATE REQUEST IN THE REQUIRED TIME. AFTER FURTHER REVIEW IT WAS DETERMINED THAT THIS 2" POLYETHYLENE LINE WAS NOT AVAILABLE IN CNP MAPPING SYSTEM.
2024-05-31 11:04 | NO | YES | YES | 20230078 | 39090 | 2023-12-19 08:09 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2023-11-19 20:00 | EASTERN | NO | 2023 | 3405 E 139TH STREET | CLEVELAND | CUYAHOGA | OH | 44120 | 41.4664 | -81.5857 |  |  | YES | [6 empty] | 2023-11-19 22:18 | 1384728 | 1384755 | NATURAL GAS |  | 27 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2023-11-19 20:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27 | YES | 4 | 2023-11-19 20:00 |  |  |  | 2023-11-19 20:07 | 2023-12-19 21:50 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER AND METER MANIFOLDS | [9 empty] | OTHER | [8 empty] | OUT OF CONTROL VEHICLE STRUCK OUTSIDE WALL OF BUILDING DIRECTLY OPPOSITE INDOOR METER MANIFOLD, CAUSING UNKNOWN SCOPE OF DAMAGE TO METERING EQUIPMENT AND HOUSELINE THAT BEGAN TO LEAK. | CLASS 3 LOCATION | 119600 | 119600 | 2000 | 2000 | 5000 | 5000 | 0 | 0 |  | 3.445 | 93 | 93 | 0 | 0 | 126693 | 53559.1102407243452200378071833648393195 | 126693 | 0 | 0 | 2 | 2 | 0 | 2 | 0 | 0.28 | 0.28 | 1 | 192.619(A)(4) | 1970-11-12 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 50 | YES |  |  |  |  | YES | YES | LOW PRESSURE METER MANIFOLD WAS LOCATED INSIDE OF STRUCTURE.. | [135 empty] | DANIEL EVANS | SUPERVISOR PIPELINE COMPLIANCE | daniel.a.evans@dominionenergy.com | 13305715796 |  | DANIEL EVANS | daniel.a.evans@dominionenergy.com | 13305715796 | DANIEL EVANS | SUPERVISOR PIPELINE COMPLIANCE | 13305715796 | daniel.a.evans@dominionenergy.com | IN THE MINUTES IMMEDIATELY PRECEDING APPROXIMATELY 20:00 ON SUNDAY, NOVEMBER 19TH, AN OUT-OF-CONTROL VEHICLE STRUCK THE FRONT WALL OF AN APARTMENT BUILDING AT ADDRESS 3401/3405 E 139TH STREET IN CLEVELAND, OH (THE APARTMENT BUILDING HAD TWO MAILING ADDRESSES). THE VEHICLE THEN ATTEMPTED TO FLEE THE SCENE AND STRUCK THE NEIGHBORING HOME (3421 E 139TH STREET). THE DRIVER/OCCUPANTS OF THE VEHICLE FLED THE SCENE. RESIDENTS OF THE BUILDINGS THAT HAD BEEN STRUCK BY THE VEHICLE CALLED 911, AND THE CLEVELAND FIRE DEPARTMENT AND CLEVELAND POLICE DEPARTMENT RESPONDED. WHEN THE FIRE DEPARTMENT ARRIVED AT THE SCENE, THEY WITNESSED AN EXPLOSION AT THE APARTMENT BUILDING AT 3401/3405 E 139TH STREET THAT COMPLETELY DESTROYED ONE QUARTER OF THE BUILDING. THE FIRE DEPARTMENT THEN CALLED DEO DISPATCH TO ASSIST WITH SHUTTING OFF THE GAS. DEO EMPLOYEES RESPONDED AND ARRIVED AT THE SCENE AT 20:07 AND SHUT THE GAS OFF AND PERFORMED A FIRE INVESTIGATION AND SHUT OFF GAS TO THE SECOND HOME (3421 E 139TH STREET) THAT HAD BEEN STRUCK BY THE VEHICLE AS A PRECAUTION. DEO PIPELINE SAFETY WAS NOTIFIED AT 21:50 AND THE INCIDENT WAS REPORTED TO PHMSA AND THE PUCO. DURING THE POLICE AND FIRE INVESTIGATION THE FOLLOWING MORNING (MONDAY, NOVEMBER 20TH) THE FIRE DEPARTMENT RECOVERED ONE FATALITY FROM THE DEBRIS WHO MATCHED THE DESCRIPTION OF A RESIDENT REPORTED MISSING BY FAMILY MEMBERS. TWO FD PERSONNEL WERE TREATED AT THE HOSPITAL DUE TO INJURIES SUSTAINED WHILE RESPONDING TO THE EMERGENCY, AND ONE RESIDENT WAS RECOVERED ALIVE FROM THE DEBRIS WHO REFUSED TREATMENT AT THE SCENE IN THE MINUTES IMMEDIATELY AFTER THE INITIAL EXPLOSION. DEO PERSONNEL PARTICIPATED IN THE RECOVERY OF METERING EQUIPMENT FROM THE STRUCTURE, TESTING OF SERVICE LINE, AND TESTING OF ODORIZATION. ALL TESTS SHOWED JURISDICTIONAL FACILITIES WERE IN COMPLIANCE. GAS SERVICE WAS RESTORED TO 3421 E 139TH STREET ON NOVEMBER 20TH AFTER INVESTIGATION SHOWED THAT THE VEHICLE IMPACT DID NOT COMPROMISE ANY GAS FACILITIES. DUE TO EXTENSIVE DAMAGE, NO DATA WAS ABLE TO BE RECOVERED FROM THE METERS AT 3401/3405 E 139TH STREET. BASED ON THE LOCATION OF THE INDOOR METER/MANIFOLD AND VEHICLE TRACKS AND OTHER EVIDENCE AT THE SCENE, IT IS APPARENT THAT THE VEHICLE COLLIDED DIRECTLY WITH THE EXTERIOR BUILDING WALL OPPOSITE THE INDOOR METER MANIFOLD. IT IS MORE THAN LIKELY THAT THE COLLISION CAUSED A RUPTURE AND LEAK IN SOME COMBINATION OF OPERATOR EQUIPMENT AND HOUSELINE PIPING LEADING TO A LEAK. DUE TO THE SUBSEQUENT EXPLOSION AND DAMAGE TO THE BUILDING, METERING EQUIPMENT, AND HOUSELINE, THE EXACT FAILURE LOCATIONS OF THE EQUIPMENT AND SOURCE OF IGNITION IS UNKNOWN. 1/18/2024: FINALIZING REPORT. NO NEW INFORMATION AVAILABLE. NO SUSPECT OR CHARGES ANNOUNCED FOR DRIVER OF VEHICLE THAT INITIATED EVENT.
2024-05-31 11:04 | NO | NO | NO | 20230079 | 38989 | 2023-12-19 15:40 | ORIGINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2023-11-20 11:00 | EASTERN | NO | 2023 | 1410 COVENTRY MEADOWS DR. | SYKESVILLE | BALTIMORE | MD | 21784 | 39.332 | -76.492 | YES | [8 empty] | 2023-11-20 14:08 | 1384778 | 1384902 | NATURAL GAS |  | 0 | 19.67 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-11-20 11:00 | NO |  |  | 2023-11-20 11:00 | 2023-11-20 11:00 | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1992 | 1992 | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.154 | [6 empty] | OTHER | [8 empty] | INTENTIONAL RELEASE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TOTAL COST UNDER INVESTIGATION | 2.29 | 0 | 0 | 45 | 45 | 45 | 33.60113421550094517958412098298676748582 | 45 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 259 | 92 | 99 | 192.619(A)(2) | 1992-01-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO A FAILURE DURING MAINTENANCE OPERATIONS, THE CONDITION WAS NOTED BY THE FIELD TECHNICIANS ALREADY ON SITE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [82 empty] | JEFF WEATHERHOLTZ | MANAGER GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-598-1601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 302-593-3732 | robert.rex@delmarva.com | AT APPROXIMATELY 11:00 AM ON 11/20/2023, DURING A ROUTINE INSPECTION OF A DISTRICT REGULATOR STATION LOCATED AT 1410 COVENTRY-MEADOWS DRIVE IN SYKESVILLE, MD, AN ABNORMAL OPERATING CONDITION OF OVER PRESSURIZATION WAS DISCOVERED ON THE GAS SYSTEM. DURING THE INSPECTION OF THE REGULATOR, A CONTROL LINE DIDN'T CLOSE PROPERLY CAUSING HIGHER PRESSURE GAS (250PSIG) TO FLOW INTO A MAIN WITH AN MAOP OF 99PSIG FOR SEVERAL MINUTES. THE CREW RECOGNIZED THE PROBLEM AND STARTED VENTING GAS TO ATMOSPHERE TO REDUCE PRESSURE IMMEDIATELY. THE EVENT LASTED LESS THAN 15MIN BEFORE THE CREW WAS ABLE TO CLOSE THE CONTROL VALVE. A LEAK SURVEY OF THE IMPACTED AREA WAS PERFORMED, AND CREWS CHECKED ALL HOUSES IN THE AREA TO VERIFY PRESSURE AND TURN SERVICES OFF FOR SAFETY. 15 SERVICES WERE IMPACTED IN TOTAL, AND ALL WERE TURNED ON LATER THAT DAY AFTER INSPECTIONS WERE PERFORMED.
2024-05-31 11:04 | NO | YES | NO | 20230080 | 39019 | 2023-12-26 10:47 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2023-11-28 15:45 | EASTERN | NO | 2023 | 1475 MCNEILL ROAD | SANFORD | LEE | NC | 27330 | 35.5086 | -79.1801 | [5 empty] | YES |  |  |  | 2023-11-28 17:00 | 1385340 | 1385490 | NATURAL GAS |  | 284.63 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-11-28 15:45 | OPERATOR/CONTRACTOR |  | 284.63 | NO | 3 | 2023-11-28 15:32 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-11-28 15:45 | 2023-11-28 15:35 | 2023-11-28 15:35 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | DRISCOPLEX DRISCO/PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5 | 0.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15271 | 15271 | 0 | 0 | 217500 | 217500 | ESTIMATED VEHICLE(S) AND EQUIPMENT DAMAGES | 3.25 | 925 | 925 | 0 | 0 | 233696 | 99038.5848150447658385803402646502835539 | 233696 | 1 | 0 | 2 | 0 | 0 | 2 | 1 | 55 | 55 | 60 | 192.621 M | 1997-07-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS NOT A CONTRIBUTING FACTOR IN THIS INCIDENT AS THE SYSTEM PRESSURE DID NOT DECREASE TO THE POINT OF PASSING AN ALARM THRESHOLD. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2022-06-29 | NO |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | MEASURED DEPTH FROM GRADE | 36 | UTILITY | BACKHOE/TRACKHOE | WATER | YES | A233322409 |  | Unknown | CONTRACT LOCATOR | YES | YES | 14 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHNNIE WALLER | ENGINEER III | johnnie.waller.jr@dominionenergy.com | 803-491-4644 |  | KEN GRIFFIN | ken.griffin@dominionenergy.com | 919-819-9850 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS | 704-718-4231 | scott.swindler@dominionenergy.com | THE CITY OF SANFORD WATER DEPARTMENT DAMAGED A 4-INCH PLASTIC GAS MAIN WHILE REPAIRING A WATER LINE NEAR THE INTERSECTION OF MCNEILL ROAD AND HAWKINS AVENUE IN SANFORD, NC. THE GAS MAIN HAD BEEN PROPERLY LOCATED AND MARKED BEFORE THE WATER DEPARTMENT BEGAN ITS WORK. DURING THE COURSE OF THE WATER DEPARTMENT'S EXCAVATION WORK, THE BELL HOLE BECAME MUDDY AND WORKERS LOST SIGHT OF THE GAS LINE, DAMAGING THE GAS MAIN WITH A BACKHOE. OPERATOR RESOURCES WERE DISPATCHED TO THE SCENE AND A REPAIR PLAN INITIATED. OPERATOR ULTIMATELY REPLACED 30 FEET OF PIPE. THE AREA WAS MADE SAFE WITHIN 5 MINUTES OF ARRIVING ONSITE AND FINAL REPAIRS WERE COMPLETED APPROXIMATELY 14 HOURS AFTER THE INITIAL REPORT. PROPERTY DAMAGE EXCEEDING THE REPORTING CRITERIA WAS CONFIRMED AT 4:56 P.M. THE NRC WAS CONTACTED AT 5:00 P.M. AND THE NCUC WAS CONTACTED AT 5:12 P.M. RECORDED ON OUR LDF # 614354.
2024-05-31 11:04 | NO | YES | NO | 20240001 | 39401 | 2024-01-12 18:11 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2023-12-15 15:26 | PACIFIC | NO | 2023 | 3401 W EMPIRE AVE | BURBANK | LOS ANGELES | CA | 91504 | 34.1926 | -118.3491 | [7 empty] | YES | PC FITTINGS | 2023-12-16 18:22 | 1386895 | 1387044 | NATURAL GAS |  | 3528 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-12-15 15:25 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-12-15 15:25 | 2023-12-15 15:25 | 2023-12-16 18:22 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN VALVE |  | 1969 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 250000 | 250000 | 100000 | 100000 | 0 | 0 |  | 6 | 21168 | 21168 | 0 | 0 | 371168 | 163684.2023172594946124763705103969754253 | 371168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 110 | 125 | 192.619(A)(2) | 1969-12-01 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCG USES ODORANT INJECTION PUMP SYSTEMS AT POINT OF ENTRY GAS SUPPLIES. | 10 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE IS NO CONTROLLER OR CONTROL ROOM THAT OPERATES THIS ASSET. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | SMALL CRACK IN THE FITTING | [65 empty] | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | cchavez@socalgas.com | 213-264-6814 |  | CARLOS CHAVEZ | cchavez@socalgas.com | (213)264-6814 | CARLOS CHAVEZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | (213)264-6814 | cchavez@socalgas.com | ON 12/15/2023, SOCALGAS RESPONDED TO A GAS LEAK AT 3401 W EMPIRE AVE, BURBANK, CA. SOCALGAS SAFELY CONTROLLED THE RELEASE OF GAS. UPON CONTROLLING THE GAS, IT WAS DISCOVERED THAT A MATERIAL FAILURE ON A 6-IN VALVE CAUSED THE RELEASE OF NATURAL GAS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO COSTS ASSOCIATED WITH THE INCIDENT POTENTIALLY EXCEEDING $139,700. THE DAMAGED VALVE WAS REMOVED AND REPLACED WITH NEW PIPE.
2024-05-31 11:04 | NO | YES | NO | 20240002 | 39093 | 2024-01-19 11:26 | ORIGINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2023-12-18 15:45 | EASTERN | NO | 2023 | 3264 LONGLEAF PINE PKWY | ST JOHNS | USA | FL | 32259 | 30.0893 | -81.5799 | [5 empty] | YES |  |  |  | 2023-12-18 18:37 | 1387045 | 1387186 | NATURAL GAS |  | 130 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-12-18 15:45 | YES | OPERATOR | 2023-12-18 20:02 | 2023-12-18 09:02 | 2023-12-18 09:02 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 168 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2015 | 2015 |  |  |  |  | 6 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | LEAK |  |  | OTHER | STILL RESEARCHING DUE TO DEPTH | [5 empty] | CLASS 3 LOCATION | 30000 | 30000 | 75000 | 75000 | 0 | 0 | 50000 | 50000 | RESTORATION OF GAS TO CUSTOMERS. | 10 | 1300 | 1300 | 0 | 0 | 156300 | 66459.6293221911545274102079395085066163 | 156300 | 84 | 0 | 1450 | 0 | 0 | 0 | 0 | 50 | 50 | 60 | 192.619(A)(2) | 2015-09-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | (407)420-6617 |  | JAMES WHITE JR. | jtwhitejr@tecoenergy.com | (904)739-4888 | RUSSELL HARRIS | MANAGER OF PIPELINE SAFETY COMPLIANCE | (407)420-6667 | rharris@tecoenergy.com | ON DECEMBER 18, 2023, AT APPROXIMATELY 09:02 HOURS, PGS WAS NOTIFIED BY THE PUBLIC OF A GAS ODOR AT 3264 LONGLEAF PINE PARKWAY, ST. JOHNS COUNTY FLORIDA. RESPONDING CREWS WERE DISPATCHED AND UPON ARRIVAL, THE PIPELINE WAS SQUEEZED OFF, STOPPING THE ESCAPING GAS TO MAKE SAFE AT 15:45. AN ASSESSMENT WAS MADE OF THE SCENE, INCLUDING THE ABILITY TO SAFELY MANAGE THE SITE. AN EVALUATION OF OPTIONS FOR THE ONE-WAY FEED PE PIPELINE CONCLUDED THAT IT WAS SAFER TO TAKE THE LINE OUT OF SERVICE TO INSTALL A BYPASS. AS A RESULT, 1,534 CUSTOMERS WERE OUT OF SERVICE. THE INCIDENT REMAINS UNDER INVESTIGATION AND ADDITIONAL INFORMATION WILL BE PROVIDED AS THE ROOT CAUSE ANALYSIS IS COMPLETED.
2024-05-31 11:04 | NO | NO | NO | 20240003 | 39095 | 2024-01-21 14:44 | ORIGINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2023-12-21 14:00 | EASTERN | NO | 2023 | 9827 LOVE RD. | FORT MEADE | ANNE ARUNDEL | MD | 20755 | 39.1076 | -76.7625 | [5 empty] | YES |  |  |  | 2023-12-22 10:34 | 1387317 | 1387444 | NATURAL GAS |  | 5900 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2023-12-21 14:20 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-12-21 14:20 | 2023-12-21 16:14 | 2023-12-22 09:45 | YES | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2012 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | CHEVRON PHILLIPS PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 2 | 4 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 4000 | 4000 | 0 | 0 |  | 2.29 | 13511 | 13511 | 0 | 0 | 17511 | 11778.5907756052988960302457466918714556 | 17511 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 92 | 92 | 99 | 192.619(A)(2) | 2012-09-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [8 empty] | YES |  | NO | NO | > 36” |  | CONTRACTOR | BACKHOE/TRACKHOE | STREET LIGHT | YES | 23898792 | MISS UTILITY OF MARYLAND | Unknown | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JEFF WEATHERHOLTZ | MANAGER - GAS ENGINEERING AND STANDARDS | jeffrey.weatherholtz@bge.com | 410-598-1601 |  |  |  |  | ROBERT REX | SR. MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 302-593-3732 | robert.rex@delmarva.com | ON DECEMBER 21, 2023 AT 14:00, A THIRD-PARTY CONTRACTOR STRUCK A 4" PLASTIC HIGH PRESSURE GAS MAIN ON NSA PROPERTY. THE MAIN WAS NOT SHUT OFF UNTIL 24:00, RESULTING IN THE RELEASE OF 5900 MCF OF NATURAL GAS INTO THE ATMOSPHERE. THE MAIN WAS REPAIRED AND SERVICE WAS RESTORED TO CUSTOMER ON DECEMBER 22ND. THE ONE CALL CENTER WAS NOTIFIED PRIOR TO START OF WORK AND THE GAS MAIN WAS MARKED WITHIN TOLERANCE PRIOR TO EXCAVATION.
2024-05-31 11:04 | NO | YES | NO | 20240004 | 39103 | 2024-01-23 10:49 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2023-12-24 11:52 | EASTERN | NO | 2023 | 418 EAST RUSSELL STREET | FAYETTEVILLE | CUMBERLAND | NC | 28301 | 35.0285 | -78.5224 | [5 empty] | YES |  |  |  | 2023-12-25 03:28 | 1387491 | 1387539 | NATURAL GAS |  | 602 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2023-12-24 11:30 | OTHER | SQUEEZED OFF | 602 | NO | 0 | 2023-12-25 11:52 |  |  |  | 2023-12-25 12:22 | 2023-12-25 12:22 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | CASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1986 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | OTHER | 2" PE MAIN INSERTED IN 4" STEEL CASING | [9 empty] | RUPTURE |  |  |  |  | OTHER | MELTED. | 2 | 2 |  | CLASS 4 LOCATION | 0 | 0 | 2000000 | 2000000 | 10000 | 10000 | 0 | 0 |  | 3 | 1806 | 1806 | 0 | 0 | 2011806 | 850592.0679552732812665406427221172022684 | 2011806 | 0 | 0 | 3 | 2 | 0 | 3 | 0 | 57 | 57 | 60 | 192.619(A)(4) | 1986-05-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | EXPOSED CASING LEAKING AND ON FIRE UNDER A BRIDGE. | [47 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | FAYETTEVILLE FIRE DEPARTMENT RESPONDED TO A FIRE AT 418 EAST RUSSELL STREET AT A FOUR LANE DIVIDED HIGHWAY BRIDGE WITH A TRAIN BRIDGE BETWEEN THE TWO LANES. DURING THE COURSE OF EXTINGUISHING THE FIRE, THE FIRE DEPARTMENT REQUESTED ASSISTANCE FROM PIEDMONT NATURAL GAS, PWC WATER, SPECTRUM, NCDOT, CENTURY LINK, CSX, PWC ELECTRICITY, CITY STREET MAINTENANCE AND THE FAYETTEVILLE POLICE DEPARTMENT. A PIEDMONT TECHNICIAN FOUND THE EXPOSED CASING ON A 4" STEEL DISTRIBUTION PIPELINE LEAKING AND ON FIRE. AFTER BEING DUG UP, THE LINE WAS CLAMPED ON BOTH SIDES OF THE BRIDGE WHILE THE FIRE DEPARTMENT CONTINUED TO SPRAY WATER TO COOL THE BRIDGE. THE WOODED TRAIN TRESTLE HAD DAMAGE AND FIRE WAS ON THE UNDER SIDE. THE LINE WAS ABANDONED. THE CAUSE OF THE FIRE IS UNDETERMINED AFTER INVESTIGATION. THERE WERE HOMELESS PERSONS STAYING UNDER THE BRIDGE AND IT COULD NOT BE RULED OUT THAT A CAMPFIRE OR OTHER OPEN FLAME WAS THE CAUSE.
2024-05-31 11:04 | NO | YES | YES | 20240005 | 39109 | 2024-01-24 13:38 | ORIGINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-12-24 09:03 | CENTRAL | NO | 2023 | 105 W GULF AVE | ROGERS | BELL | TX | 76569 | 30.9342 | -97.2265 | [5 empty] | YES | YES |  |  | 2023-12-24 11:14 | 1387457 | 1387538 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2023-12-24 09:03 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 9 | 2023-12-24 09:30 |  |  |  | 2023-12-24 10:45 | 2023-12-24 11:21 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1996 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 48390 | 48390 | 0 | 0 |  | 9.2031 | 9 | 9 | 0 | 0 | 48399 | 20451.9416290571260790359168241965973535 | 48399 | 0 | 0 | 10 | 4 | 0 | 10 | 0 | 14.5 | 14.5 | 35 | 192.619(A)(2) | 1996-01-09 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 10.8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WILLIAM BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | DALE GAMBRELL | dale.gambrell@atmosenergy.com | 512-844-8270 | JEFFREY KNIGHTS | SR. VP TECHNICAL AND OPERATING SERVICES | 2142062701 | jeff.knights@atmosenergy.com | ON DECEMBER 24, 2023, AT APPROXIMATELY 9:30 A.M., ATMOS ENERGY RECEIVED A NOTIFICATION OF AN EXPLOSION AND STRUCTURE FIRE. THE FIRST ATMOS ENERGY TECH ARRIVED ON THE SCENE AT 9:34 A.M. AND REQUESTED ADDITIONAL COMPANY RESOURCES. AT 5:43 P.M., THE GAS SYSTEM IN THE VICINITY WAS ISOLATED AND SHUT OFF. ACCORDING TO THE REPORT OF THE BELL COUNTY FIRE MARSHALL'S OFFICE, THERE WAS 1 FATALITY, 1 HOSPITALIZATION, AND 4 OTHER INDIVIDUALS WITH NON-LIFE THREATING INJURIES REPORTED AT THE AFFECTED RESIDENCE. THIS EVENT IS STILL UNDER INVESTIGATION. THE VOLUME OF GAS RELEASED (PART A, 21C) IS STILL UNKNOWN AT THIS TIME. A VALUE OF 1 WAS ENTERED AS IT IS THE LOWEST VALUE THAT WILL VALIDATE IN THE FIELD. THE COST ESTIMATES IN PART D HAVE NOT BEEN FINALIZED.
2024-05-31 11:04 | NO | YES | NO | 20240006 | 39555 | 2024-01-24 14:13 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2023-12-25 23:30 | CENTRAL | NO | 2023 | 241 PLANTATION DRIVE | COPPELL | DALLAS | TX | 75019 | 32.9631 | -96.9997 | [5 empty] | YES |  |  |  | 2023-12-26 01:18 | 1385719 | 1387679 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 11 | 2023-12-25 23:50 |  |  |  | 2023-12-25 23:50 | 2023-12-26 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1989 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 66406 | 66406 | 0 | 0 | 55707 | 55707 | 0 | 0 |  | 9.2031 | 9 | 9 | 0 | 0 | 122122 | 51600.5892305331465520359168241965973535 | 122122 | 0 | 0 | 18 | 0 | 0 | 11 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 1989-07-06 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 3.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | NO | [50 empty] | WILLIAM BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | JEFFREY BROWN | jeffrey.brown@atmosenergy.com | 214-208-7729 | JEFFREY KNIGHTS | SR. VP TECHNICAL AND OPERATING SERVICES | 2142062701 | jeff.knights@atmosenergy.com | ON DECEMBER 25, 2023, AT APPROXIMATELY 11:30 P.M., ATMOS ENERGY RECEIVED A NOTIFICATION OF AN EXPLOSION. THE FIRST ATMOS ENERGY TECH ARRIVED ON THE SCENE AT 11:50 A.M. ON DECEMBER 25, 2023, AND REQUESTED ADDITIONAL COMPANY RESOURCES. AT 4:42 A.M., ON DECEMBER 26, 2023, THE GAS SYSTEM IN THE VICINITY WAS ISOLATED AND SHUT OFF. THERE WERE NO FATALITIES OR INJURIES AT THE AFFECTED RESIDENCE. THE RELEASE WAS FROM A SERVICE TAP TEE CAP WHICH WAS OVER-TIGHTENED DURING INSTALLATION WHICH CAUSED A CRACK AND ULTIMATELY FAILURE. THE VOLUME OF GAS RELEASED (PART A, 21C) IS STILL UNKNOWN. A VALUE OF 1 WAS ENTERED AS IT IS THE LOWEST VALUE THAT WILL VALIDATE IN THE FIELD. THE CONSTRUCTION ACTIVITY REFERENCED IN PART G7, 4 OCCURRED PRIOR TO THE ADOPTION OF THE COMPANY'S OPERATOR QUALIFICATION PLAN.
2024-05-31 11:04 | NO | YES | NO | 20240007 | 39135 | 2024-01-30 15:22 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2024-01-04 14:08 | EASTERN | NO | 2024 | 3900 BRAGG BOULEVARD | FAYETTEVILLE | CUMBERLAND | NC | 28303 | 35.0811 | -78.9435 | [6 empty] | YES |  |  | 2024-01-04 16:13 | 1388195 | 1388341 | NATURAL GAS |  | 3735 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 8 | 2024-01-04 14:22 |  |  |  | 2024-01-04 14:22 | 2024-01-04 14:22 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 3RD PARTY DAMAGED 2" TEE TORE OFF OF 12" STEEL MAIN | CLASS 1 LOCATION | 0 | 0 | 300000 | 294078.792167964 | 100000 | 98026.264055988 | 0 | 0 |  | 3 | 11205 | 11205 | 0 | 0 | 411205 | 174034.685879595335349716446124763705104 | 403310.056223952 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 55 | 60 | 60 | 192.619(A)(1) | 1958-01-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET |  |  | YES | [5 empty] | NO | NO | > 36” |  | UTILITY | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | YES | C233490205 |  | Unknown | FACILITY OWNER | UNKNOWN/OTHER | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO NO RESPONSE FROM OPERATOR/CONTRACT LOCATOR | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR WAS DIGGING UP ASPHALT DURING A STORM DRAIN INSTALLATION AND STRUCK A 2" RETIRED STUB RIPPING THE TEE OFF THE 12" STEEL MAIN WITH A CAT 326 TRACKHOE. INTERNAL LOCATOR DID NOT MARK LINES FOR THIS SPECIFIC TICKET AS THEY WERE ADVISED BY CONTACT ON THE TICKET THAT THE WORK WAS ALREADY COMPLETED. THERE WERE MARKS FROM PREVIOUS LOCATES IN THIS AREA.
2024-05-31 11:04 | NO | YES | NO | 20240008 | 39171 | 2024-02-09 08:53 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2024-01-12 08:40 | EASTERN | NO | 2024 | 3315 GREENFIELD RD | MELVINDALE | WAYNE COUNTY | MI | 48122 | 42.2895 | -83.1698 | YES | [8 empty] | 2024-01-12 14:58 | 1388827 | 1389180 | NATURAL GAS |  | 4666 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-01-12 08:40 | YES | OPERATOR | 2024-01-12 08:50 | 2024-01-12 08:50 | 2024-01-12 14:51 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 84 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1921 | UNKNOWN |  |  |  |  | 24 | CAST IRON | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75000 | 73519.698041991 | 70000 | 68618.3848391916 | 0 | 0 |  | 3.75 | 17498 | 17498 | 0 | 0 | 162498 | 73120.2656209563336389413988657844990548 | 159636.0828811826 | 9 | 0 | 180 | 0 | 0 | 180 | 9 | 45 | 45 | 50 | 192.621 M | 1921-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | COUNTY ROAD | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | BORING | WATER | YES | 2023121501129 |  | NO | FACILITY OWNER | YES | YES | 9 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | JUSTIN MORRIS |  | justin.morris@dteenergy.com | 2484621760 |  |  |  |  | MARINA DARLING |  | 5868724760 | marina.darling@dteenergy.com | BRICCO CONSTUCTION, A CONTRACTOR FOR THE CITY OF MELVINDALE, WAS BORING WATER MAIN. ON PULLBACK, A 24" 50PSIG CAST IRON MAIN WAS HIT, CAUSING A 4" DIAMETER HOLE. THE LINE WAS MARKED BUT THE CONTRACTOR DID NOT VERIFY LOCATION VIA POTHOLES. THIS WAS REPORTED TO THE MICHIGAN PUBLIC SERVICE COMMISSION AT 10:20AM ON 01/12/24 DUE TO THE COST BEING OVER $10K TO REPAIR, THE CLOSURE OF GREENFIELD RD, 189 CUSTOMERS AFFECTED, POTENTIAL MEDIA, AND OVER 1MMCF OF GAS LOSS. THIS WAS ALSO REPORTED TO PHMSA/NRC AT 14:58 ON 01/12/24 UPON GAS LOSS CALCULATION ESTIMATED TO BE OVER 3MMCF. THE GAS WAS SHUT OFF AT 17:10 ON 01/12/24 VIA MAIN LINE VALVES, AND A REPAIR WAS MADE AND GAS WAS RESTABLISHED AT 00:30 ON 01/13/24, AND AT 01:45 THE 189 CUSTOMERS BEGAN TO BE RELIT AND CONTINUED THROUGHOUT THE DAY ON 01/13/24.
2024-05-31 11:04 | NO | YES | NO | 20240009 | 39362 | 2024-02-15 16:31 | SUPPLEMENTAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2024-01-17 12:50 | MOUNTAIN | YES | 2024 | 1413 S 4TH ST. W | MISSOULA | MISSOULA | MT | 59801 | 46.8657 | -114.0177 | YES | [8 empty] | 2024-01-17 02:19 | 1389218 | 1389458 | NATURAL GAS |  | 16.284 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-17 12:50 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 50 | 2024-01-17 12:50 | YES | OPERATOR | 2024-01-17 12:00 | 2024-01-17 10:35 | 2024-01-17 01:40 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 3.625 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - LOW FREQUENCY |  | 0.322 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 400000 | 392105.056223952 | 2500 | 2450.6566013997 | 10000 | 9802.6264055988 | 0 | 0 |  | 9 | 147 | 147 | 0 | 0 | 412647 | 170954.8922731625572542533081285444234405 | 404505.3392309505 | 4 | 0 | 46 | 0 | 0 | 46 | 4 | 31 | 31 | 35 | 192.619(A)(4) | 1995-01-26 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | MELISSA BARUTH | SUPERVISOR DOT | melissa.baruth@northwestern.com | 6053537462 |  |  |  |  | MELISSA BARUTH | DOT SUPERVISOR | 605-353-7462 | melissa.baruth@northwestern.com | A7 - UNABLE TO DETERMINE AS TIME PIPE HAS BEEN LEAKING IS UNKNOWN 21C - NO ADDITIONAL GAS WAS RELEASED BEYOND UNDERGROUND PIPE LEAKING FOR UNKNOWN AMOUNT OF TIME PART C 4.A. - EDUCATED GUESS DUE TO AGE OF PIPE TIMELINE OF EVENTS PRIOR TO EXPLOSION: 10:35 AM: RECEIVED ODOR CALL FOR 1342 S. 5TH ST W 10:52 AM: ARRIVED AT THE SITE OF THE ODOR CALL 1342 S. 5TH ST W WORKED INSIDE, CHECKING APPLIANCES, VENTING, AMBIENT CHECKED OUTSIDE AMBIENT, METER SET, BAR HOLED ALONG SERVICE 11:30 AM: REQUESTED ADDITIONAL HELP WITH LEAK SURVEYING 11:36 AM: GAS SUPERVISOR INFORMING ABOUT ACTIVE LEAK, UNDER INVESTIGATION 11:42 - 11:48 AM: EMERGENCY LOCATES REQUESTED 11:50 AM: ADDITIONAL HELP ARRIVED ONSITE AND BEGAN TO MONITOR AMBIENT, SURVEY SURROUNDINGS, MAPPING 12:00 PM: NOTIFIED MISSOULA FIRE DEPARTMENT (MFD), GAS LEAK, REQUESTED FD TO BE DISPATCHED BEGIN EVACUATING HOMES 12:04 PM: DE-ENERGIZED POWER @ 1410 A/B S. 5TH ST W. MFD ASSISTANCE CHECKING AMBIENT INSIDE HOMES 12:36 PM: DE-ENERGIZED SECONDARY POWER TO 1410 A/B S. 5TH ST W. 12:36 - 12: 48 PM: BEGUN BARHOLING PRIOR 12:48 PM: REQUESTED BACKHOE TO ASSIST WITH BARHOLING 12:50 PM: HOUSE EXPLOSION POST EXPLOSION: 12:50PM: 1413 S. 4TH ST W HOUSE EXPLOSION 12:50 PM: DE-ENERGIZE PRIMARY FOR MULTIPLE BLOCKS FROM RUSSELL & 5TH ' EAST (FOUR BLOCKS EAST) MFD - INCREASED PERIMETER CONTINUED EVACUATIONS, ROAD CLOSURES, FIRE IC DAVE ANY INJURIES RESULTED: HIS RESPONSE NO ONE WAS HOME, NO INJURIES 1:05 PM: DE-ENERGIZED PRIMARY RUSSELL & 5TH ' EAST (FOUR BLOCKS EAST) 1:10 PM: ADDITIONAL SUPPORT ARRIVED ONSITE. INFORMED FIRE IC DAVE ' OF PLAN TO OPERATE ZV # 24, TO ELIMINATE GAS FLOW FROM EAST AND INSTALL PRESSURE CONTROL FITTING (PCF) TO ELIMINATE GAS FLOW FROM WEST 1:39 PM ZONE VALVE # 24 STOPPING FEED FROM THE EAST. 1:40 PM: BEGAN BELLHOLE EXCAVATION AT 1501 S. 4TH ST W ALLEY 2:00 PM: BEGAN SHUTTING OFF ALL LOCKWING VALVES 2:15 PM: MFD SHUT OFF LOCKWING VALVE TO 1413 S. 4TH ST W 4:00 PM: PCF # 1 PILOT BIT BROKE (WEST OF RUSSELL) 4:00 PM: BEGAN PCF # 2 (WEST OF RUSSELL) 5:10 PM: PCF # 2 STOPPERED, FEED FROM WEST WAS SHUT OFF. 5:15 PM: GAS SUCCESSFUL STOPPED.CONFIRMED FEED FROM WEST WAS SHUT OFF BY BREAKING DOWN METER SET AT 1501 S. 4TH ST W. 5:15 PM TO 1 AM: CONTINUED BARHOLING, AMBIENT MONITORING, TURNED OFF ALL THE LOCKWING VALVES EAST OF PRINCE. RESTORATION EFFORTS COMPLETED IN THE FOLLOW DAYS.
2024-05-31 11:04 | NO | YES | YES | 20240010 | 39195 | 2024-02-15 17:08 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2024-01-16 00:46 | CENTRAL | NO | 2024 | 3325 N 53RD ST, LINCOLN NE | LINCOLN | LANCASTER | NE | 68504 | 40.8459 | -96.6474 | [5 empty] | YES |  |  |  | 2024-01-16 04:19 | 1389085 | 1389208 | NATURAL GAS |  | 118.64 | 118.64 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2024-01-16 00:46 | OTHER | FIRE EXTINGUISHED AFTER SERVICE WAS SQUEEZED OFF. | 118.64 | NO | 1 | 2024-01-16 00:58 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-01-16 00:58 | 2024-01-16 01:43 | 2024-01-16 03:19 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIS IS STILL UNDER INVESTIGATION. | CLASS 3 LOCATION | 1 | 0.98026264055988 | 1700 | 1666.446488951796 | 1 | 0.98026264055988 | 1 | 0.98026264055988 | ESTIMATES UNKNOWN AT THIS TIME. TOTAL LOSS TO HOME AND VEHICLE AT PROPERTY | 5.43 | 644 | 644 | 644 | 644 | 2991 | 1667.07065516545842569565217391304347826 | 2957.38727687347564 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 8 | 8 | 12 | 192.619(A)(4) | 1952-12-18 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS ASSOCIATED WITH THIS INCIDENT WAS NOT LARGE ENOUGH TO HAVE BEEN INDICATED IN THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | THOMAS DORSHORST |  | tom.dorshorst@blackhillscorp.com | 3087604592 |  |  |  |  | THOMAS DORSHORST |  | 3087604592 | tom.dorshorst@blackhillscorp.com | EXPLOSION AT PRIVATE RESIDENCE OF 3325 N 53RD ST IN LINCOLN NE. THIS RESULTED IN DAMAGE TO THE RESIDENCE AND INJURY TO THE SINGLE OCCUPANT. THE GAS METER SERVING THIS RESIDENCE WAS DAMAGED FROM THE STRUCTURE'S EXPLOSION, RELEASED NATURAL GAS, AND IGNITED. GAS SERVICE TO THE METER WAS SHUT OFF AFTER DIGGING IT UP CLOSE TO THE MAIN AND PINCHING OFF. CAUSE OF EXPLOSION IS UNKNOWN AND STILL UNDER INVESTIGATION. PROPERTY LOSS IS YET UNKNOWN AND UNDER INVESTIGATION.
2024-05-31 11:04 | NO | YES | NO | 20240011 | 39202 | 2024-02-16 11:45 | ORIGINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2024-01-18 09:40 | EASTERN | NO | 2024 | 1223 MARION BARRY AVE SE | WASHINGTON | WASHINGTON | DC | 20020 | 38.8671 | -76.9879 |  | YES | [7 empty] | 2024-01-18 11:32 | 1389264 | 1389445 | NATURAL GAS |  | 162.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-18 09:55 | OPERATOR/CONTRACTOR |  | 162.7 | YES | 20 | 2024-01-18 09:40 |  |  |  | 2024-01-18 10:16 | 2024-01-18 10:16 | NO | PUBLIC PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1981 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | MECHANICAL DAMAGE DUE TO IMPACT BY A VEHICLE. | CLASS 4 LOCATION | 500000 | 490131.32027994 | 79220 | 77656.4063851536936 | 16988 | 16652.70173783124144 | 0 | 0 |  | 2.49 | 405 | 405 | 0 | 0 | 596613 | 247233.8827250427190186162570888468809074 | 584845.42840292493504 | 33 | 0 | 3 | 1 | 0 | 3 | 33 | 20 | 20 | 25 | 192.619(A)(2) | 1991-07-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS AN ACCIDENTAL HIT BY A VEHICLE TO THE SERVICE RISER. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | LARGE TRUCK | ROADWAY | 13 | NO | [142 empty] | MARK AIESI | SUPERVISOR | mark.aiesi@washgas.com | 5714054623 |  |  |  |  | SHANNON MALONEY | MANAGER | 5712055471 | smaloney@washgas.com | ON JANUARY 18, 2024, AT APPROXIMATELY 0930, A DELIVERY TRUCK STRUCK A METER AND RISER WHICH WAS LOCATED AT 1223 MARION BARRY AVE SE, WASHINGTON D.C.. WASHINGTON GAS WAS NOTIFIED AT 0940 VIA FIREBOARD OF THIS INCIDENT. THE RESULTING DAMAGE, WHICH WAS A BROKEN RISER, CAUSED A BLOWING GAS LEAK. SUBSEQUENTLY, A FLASH FIRE OCCURRED ON THE SECOND FLOOR AT 1225 MARION BARRY AVE SE. MINUTES LATER, AT APPROXIMATELY 1001, AN EXPLOSION OCCURRED AT 1223 MARION BARRY AVE SE. ONE PERSON WAS INJURED AND WAS TAKEN TO THE HOSPITAL WITH MINOR INJURIES. THE FIRST WASHINGTON GAS CREW ARRIVED AT 1016. WASHINGTON GAS STOPPED THE FLOW OF GAS USING VALVES AT 1251, CREATING AN OUTAGE OF 36 CUSTOMERS. CREWS HAVE RESTORED SERVICE TO THE CUSTOMERS THAT WERE AFFECTED.
2024-05-31 11:04 | NO | YES | YES | 20240012 | 39508 | 2024-02-16 15:47 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-20 09:47 | CENTRAL | NO | 2024 | 214 ENGLISH RD | AMARILLO | POTTER | TX | 79108 | 35.2352 | -101.7055 |  |  |  | YES | [5 empty] | 2024-01-20 11:07 | 1389461 | 1389595 | NATURAL GAS |  | 43.92 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-01-20 09:47 | OPERATOR/CONTRACTOR |  | 43.92 | NO | 0 | 2024-01-20 09:47 |  |  |  | 2024-01-20 10:05 | 2024-01-20 10:35 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1985 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | STRUCK BY VEHICLE | [5 empty] | CLASS 1 LOCATION | 25000 | 24506.566013997 | 2575 | 2524.176299441691 | 2006 | 1966.40685696311928 | 0 | 0 | N/A | 4.73 | 208 | 208 | 0 | 0 | 29789 | 12406.8749351336473833856332703213610586 | 29205.14917040181028 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 15 | 15 | 60 | 192.619(A)(1) | 1985-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 20 | YES | [5 empty] | YES | ABANDON FACILITIES INCLUDING MAIN STUB AND SERVICE LINE. | [111 empty] | YES | [23 empty] | DUSTIN CROSLEY | MGR. COMPLIANCE | dustin.crosley@atmosenergy.com | 806-290-5751 |  | ANTHONY RAMIREZ | anthony.ramirez@atmosenergy.com | 806-344-7638 | DUSTIN MCKNIGHT | V.P. TECHNICAL SERVICES | 512-591-1302 | dustin.mcknight@atmosenergy.com | UNIT 1 WAS EASTBOUND ON THE 10000 BLOCK OF AMARILLO BLVD EAST. UNIT 1 FAILED TO CONTROL SPEED STRIKING CHAIN LINK FENCE AND NW CORNER OF BUILDING OF 2014 EAGLE LANE LODGING THE VEHICLE ON A METER RISER CAUSING AN IGNITION OF NATURAL GAS.
2024-05-31 11:04 | NO | YES | YES | 20240013 | 39392 | 2024-02-20 14:35 | SUPPLEMENTAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-20 04:10 | CENTRAL | NO | 2024 | 1811 HIGHLAND DRIVE | CARROLLTON | DALLAS | TX | 75006 | 32.9532 | -96.8928 | [5 empty] | YES |  |  |  | 2024-01-20 05:49 | 1389442 | 1390832 | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-01-20 04:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 8 | 2024-01-20 05:00 |  |  |  | 2024-01-20 04:58 | 2024-01-20 05:00 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1974 | UNKNOWN |  |  |  |  | 3 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 55000 | 53914.4452307934 | 25971 | 25458.40103798064348 | 25627 | 25121.19068962804476 | 0 | 0 |  | 9.1461 | 9 | 9 | 0 | 0 | 106607 | 44156.4148088986379110359168241965973535 | 104503.03695840208824 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 46 | 46 | 55 | 192.619(A)(2) | 1974-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | WILLIAM BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 8067879422 |  | JEFFREY BROWN | jeffery.brown@atmosenergy.com | 214-208-7729 | JEFFREY KNIGHTS | SR. VP TECHNICAL AND OPERATING SERVICES | 2142062701 | jeff.knights@atmosenergy.com | ON JANUARY 20, 2024, AT APPROXIMATELY 4:10 A.M., ATMOS ENERGY RECEIVED NOTIFICATION OF AN EXPLOSION. THE FIRST ATMOS ENERGY TECH ARRIVED ON THE SCENE AT 4:58 A.M. ON JANUARY 20, 2024, AND FOUND THE GAS HAD BEEN SHUT OFF BY THE FIRE DEPARTMENT. THE CAUSE OF THE LEAK IS STILL UNDER INVESTIGATION. A VALUE OF 1 WAS ENTERED IN THE ESTIMATED VOLUME OF GAS CONSUMED BY FIRE, (PART A, 7) AND IN THE VOLUME OF GAS RELEASED (PART A, 21C). THESE ARE INDETERMINATE AMOUNTS. EIGHT (8) HOMES WERE EVACUATED. THE NUMBER OF PEOPLE EVACUATED IS UNKNOWN. A VALUE OF 8 WAS ENTERED INTO A22. TWENTY-FIVE (25) HOMES LOST SERVICE, WHICH INCLUDES THE 8 HOMES THAT WERE EVACUATED.
2024-05-31 11:04 | NO | YES | NO | 20240014 | 39223 | 2024-02-20 16:55 | ORIGINAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 401 DOUGLAS STREET PO BOX 778 | SIOUX CITY | IA | 51101 | 2024-01-22 07:32 | CENTRAL | YES | 2024 | 33 NORTH 12TH STREET | FORT DODGE | WEBSTER | IA | 50501 | 42.5071 | -94.1824 |  | YES | [5 empty] | YES | WELDED 2" CAP ON MAIN AT 100 NORTH 12TH STREET | 2024-01-22 14:53 | 1389637 | 1389832 | NATURAL GAS |  | 18 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-22 07:32 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 18 | YES | 4 | 2024-01-22 07:32 | YES | OPERATOR | 2024-01-22 07:33 | 2024-01-22 07:32 | 2024-01-22 07:32 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 4 LOCATION | 167800 | 164488.071085947864 | 10000 | 9802.6264055988 | 60000 | 58815.7584335928 | 0 | 0 |  | 2.7 | 49 | 49 | 0 | 0 | 237849 | 98526.2159586330374514177693761814744802 | 233155.455925139464 | 6 | 0 | 27 | 0 | 0 | 3 | 6 | 32 | 32 | 35 | 192.619(A)(4) | 1989-09-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 4 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | THE SOURCE OF THE NATURAL GAS THAT EXPLODED WAS FROM A LEAK ON AN UNDERGROUND 2" GAS MAIN THAT WAS ABANDONED IN-PLACE UNDER PAVEMENT. THE MIGRATION PATH AND SOURCE OF IGNITION IS NOT KNOWN. | [45 empty] | CHRISTOPHER PAYER | GAS STANDARDS ENGINEER | chris.payer@midamerican.com | 7122777941 | 7122527369 | CHRISTOPHER PAYER | chris.payer@midamerican.com | 7122777941 | BRADLEY LEWIS | VICE PRESIDENT GAS DELIVERY | 7122334840 | bradley.lewis@midamerican.com | MIDAMERICAN ENERGY RESPONDED TO A GAS LEAK CALL AT 15 NORTH 12TH STREET IN FORT DODGE, IOWA AT 16:53 ON JANUARY 21, 2024. INITIAL INVESTIGATION DID NOT FIND THE SOURCE OF THE LEAK AND BARHOLING AND INTERIOR INVESTIGATIONS IN THE AREA CONTINUED FOR THE NEXT 6 HOURS WITH NO PINPOINTED SOURCE. THEY MAIN WAS EXPOSED AND CREWS CONTINUED TO MONITOR AND CHECK GAS LEVELS IN AND AROUND THE BUILDINGS IN THE AREA. THE LOCATION OF THE EXPLOSION DID NOT HAVE A GAS READING THE NIGHT OF THE 21ST. WHILE CONTINUING TO INVESTIGATE FOR THE LEAK ON THE MORNING OF THE 22ND OF JANUARY, NATURAL GAS IN A NEARBY STRIPMALL AT 33 NORTH 12 STREET GAS IGNITED WITH A FLASH FIRE AND THE INTERIOR OF THE MALL WAS DAMAGED BY AN EXPLOSION. THE SOURCE OF THE GAS WAS A LEAK ON A 2" MAIN. THE MAIN WAS WAS ABANDONED IN-PLACE AND A REPLACED BY A BORED IN PLASTIC MAIN. THE GAS THAT EXPLODED IS THOUGHT TO HAVE MIGRATED INTO THE STRIPMALL OVER NIGHT.
2024-05-31 11:04 | NO | NO | NO | 20240015 | 39239 | 2024-02-22 16:13 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-01-23 15:54 | CENTRAL | YES | 2024 | 15818 CAMINO DEL SOL | HOUSTON | FORT BEND | TX | 77083 | 29.6932 | -95.6651 | [5 empty] | YES |  |  |  | 2024-01-23 18:04 | 1389745 | 1389887 | NATURAL GAS |  | 39.368 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-23 15:54 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 12 | YES | 10 | 2024-01-23 15:54 |  |  |  | 2024-01-23 15:54 | 2024-01-23 17:18 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1982 | UNKNOWN |  |  |  |  | 1.25 | 2306 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.166 |  | 2306 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 100000 | 98026.264055988 | 13831 | 13558.01258158370028 | 6547 | 6417.77950774553436 | 0 | 0 |  | 0.6506 | 26 | 26 | 0 | 0 | 120404 | 49876.3712899081641325482041587901701323 | 118028.05614531723464 | 0 | 0 | 38 | 0 | 0 | 38 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 1982-01-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | IMPROPER CONSTRUCTION PRACTICES (BACKFILLING) BY UNKNOWN/UNIDENTIFIED CONTRACTORS WORKING AROUND OR NEAR THE SEWER SYSTEM IN THE AREA. | [153 empty] | YES | ELMER SELVERA | SR. COMPLIANCE COORDINATOR | elmer.selvera@centerpointenergy.com | 281-755-2470 | 713-967-7307 | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JAMIE HERDOCIA | DIRECTOR GAS OPERATIONAL STANDARDS | 713-207-4675 | jamie.herdociaaa@centerpointenergy.com | BASED ON SIGNS OF CONSTRUCTION ACTIVITY IN THE REAR EASEMENT, IT IS BELIEVED THAT IMPROPER CONSTRUCTION PRACTICES BY UNKNOWN/UNIDENTIFIED PARTIES RESULTED IN LOSS OF SUPPORT UNDER THE 1 1/4 INCH POLY MAIN. THIS LOSS OF SUPPORT PLACED STRESS ON THE MAIN, ALLOWING GAS TO ESCAPE AND MIGRATE THROUGH THE SOIL INTO STRUCTURE, RESULTING IN FIRE/EXPLOSION BY UNKNOWN/UNDETERMINED IGNITION SOURCE.
2024-05-31 11:04 | NO | YES | NO | 20240016 | 39484 | 2024-02-22 16:38 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-01-24 03:19 | CENTRAL | YES | 2024 | 12702 CAMPSITE TRAIL | CYPRESS | HARRIS | TX | 77429 | 29.9598 | -95.6249 |  |  |  | YES | [5 empty] | 2024-01-24 06:40 | 1389765 | 1389940 | NATURAL GAS |  | 57.83 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-24 03:19 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 57.83 | NO | 0 | 2024-01-24 03:19 |  |  |  | 2024-01-24 04:14 | 2024-01-24 05:45 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | 0.113 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 275000 | 269572.226153967 | 300 | 294.078792167964 | 5628 | 5516.91814107100464 | 0 | 0 |  | 0.6506 | 38 | 38 | 0 | 0 | 280966 | 116380.3264810972825012627599243856332703 | 275421.22308720596864 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 1974-01-02 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HEAVY RAIN AND HIGH WINDS, CAUSED LARGE OAK TREE TO UPROOT, CAUSING DAMAGE TO ABOVE GROUND FACILITIES (ELECTRIC AND GAS) THAT RESULTED IN GAS IGNITION. | [119 empty] | YES |  |  | YES |  | YES | [29 empty] | ELMER SELVERA | COMPLIANCE COORDINATOR | elmer.selvera@centerpointenergy.com | 281-755-2470 | 713-967-7307 | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JAMIE HERDOCIA | DIRECTOR GAS OPERATIONAL STANDARDS | 713-207-4675 | jamie.herdocia@centerpointenergy.com | ON THE MORNING OF JANUARY 24, 2024, A WEATHER EVENT WITH HEAVY RAIN AND HIGH WINDS CAUSED LARGE OAK TREE TO UPROOT, FALLING LIMBS DAMAGED RESIDENTIAL ELECTRIC FACILITIES AND ABOVE GROUND METER SET. ESCAPING GAS IGNITED, RESULTING IN HEAVY DAMAGE TO SINGLE FAMILY RESIDENCE.
2024-05-31 11:04 | NO | YES | NO | 20240017 | 39241 | 2024-02-22 16:56 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2024-01-29 19:45 | CENTRAL | YES | 2024 | 502 AVE D | VICTORIA | VICTORIA | TX | 77901 | 28.7962 | -96.9851 | [5 empty] | YES |  |  |  | 2024-01-29 20:49 | 1390282 | 1390441 | NATURAL GAS |  | 93.55 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-29 17:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 33.5 | YES | 8 | 2024-01-29 17:09 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-01-29 17:45 | 2024-01-29 17:09 | 2024-01-29 19:45 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 82 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | 2020 |  |  |  |  | 2 | ASTM D2513 | DURALINE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 175000 | 171545.962097979 | 7562 | 7412.74608791381256 | 25310 | 24810.4474325705628 | 0 | 0 |  | 0.9446 | 88 | 88 | 0 | 0 | 207960 | 86160.0569227474233452400756143667296786 | 203857.15561846337536 | 0 | 0 | 1 | 0 | 2 | 1 | 0 | 50 | 50 | 60 | 192.619(A)(1) | 2020-10-14 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [5 empty] | YES |  |  | NO | NO | MEASURED DEPTH FROM GRADE | 82 | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2451816135 | TEXAS 811 | YES | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | ELMER SELVERA | COMPLIANCE COORDINATOR | elmer.selvera@centerpointenergy.com | 281-755-2470 |  | ELMER SELVERA | elmer.selvera@centerpointenergy.com | 281-755-2470 | JAMIE HERDOCIA | DIRECTOR GAS OPERATIONAL STANDARDS | 713-207-4675 | jamie.herdocia@centerpointenergy.com | ON JANUARY 29 2024, AROUND 4:40PM G3 UNDERGROUND (SUB OF ONYX CONSULTING WORKING FOR SPARKLIGHT), WAS PULLING BACK FIBER CONDUIT WITH A DIRECTIONAL DRILLING RIG AND DAMAGED 2" POLY MAIN WITH A MAKESHIFT ATTACHMENT THAT EXPANDS THE BORE HOLE THEY ORIGINALLY BORED. THE MAIN THAT WAS DAMAGED, WAS NOT POTHOLED PRIOR TO CONTRACTOR BORING. THE MAIN WAS PROPERLY AND CORRECTLY MARKED AND FLAGGED BY USIC. ESCAPING GAS FROM THE DAMAGED 2" POLY MAIN MIGRATED TO 502 AVE D RESULTING IN IGNITION OF GAS.
2024-05-31 11:04 | NO | YES | YES | 20240018 | 39251 | 2024-02-23 18:54 | ORIGINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-24 08:36 | CENTRAL | NO | 2024 | 185 BRISTOL BLVD. | JACKSON | HINDS | MS | 39204 | 32.288 | -90.2444 | [5 empty] | YES |  |  |  | 2024-01-24 11:43 | 1389804 | 1389988 | NATURAL GAS |  | 15 | 0.15 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-01-24 08:36 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15 | NO | 2 | 2024-01-24 11:19 |  |  |  | 2024-01-24 09:06 | 2024-01-24 11:19 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | NTSB INVESTIGATION ONGOING | 30 | YES | NO | [11 empty] | INVESTOR OWNED |  | OTHER | NTSB INVESTIGATION ONGOING | UNKNOWN | UNKNOWN | [7 empty] | OTHER | NTSB INVESTIGATION ONGOING. | [9 empty] | OTHER | [8 empty] | NTSB INVESTIGATION ONGOING. | CLASS 3 LOCATION | 200000 | 196052.528111976 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.8657 | 43 | 43 | 0 | 0 | 200043 | 82866.1094804403897920604914933837429112 | 196095.528111976 | 0 | 0 | 13 | 1 | 0 | 13 | 0 | 36 | 36 | 40 | 192.619(A)(3) | 1970-12-16 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 12 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | DEAN G MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6018425875 | 6013601489 | DEAN MORRIS | dean.morris@atmosenergy.com | 6018425875 | JAMES MCKENZIE | VICE PRESIDENT - TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | THE INVESTIGATION, TO WHICH THE MISSISSIPPI PUBLIC SERVICE COMMISSION AND PHMSA ARE PARTIES, IS ONGOING UNDER THE DIRECTION OF THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). ACCORDINGLY, THE RESPONSES IN THE REPORT WILL BE SUPPLEMENTED WHEN THE INFORMATION IS PERMITTED TO BE RELEASED BY THE NTSB.
2024-05-31 11:04 | NO | YES | NO | 20240019 | 39252 | 2024-02-23 19:16 | ORIGINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2024-01-27 04:53 | CENTRAL | NO | 2024 | 1146 SHALIMAR DRIVE | JACKSON | HINDS | MS | 39204 | 32.2793 | -90.2391 | [5 empty] | YES |  |  |  | 2024-01-27 07:45 | 1390069 | 1390197 | NATURAL GAS |  | 60 | 0.035 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-01-27 04:34 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 60 | YES | 2 | 2024-01-27 07:28 |  |  |  | 2024-01-27 05:35 | 2024-01-27 07:28 | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | NTSB INVESTIGATION ONGOING | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | OTHER | NTSB INVESTIGATION ONGOING | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | NTSB INVESTIGATION ONGOING. | CLASS 3 LOCATION | 220000 | 215657.7809231736 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.8657 | 172 | 172 | 0 | 0 | 220172 | 91245.8329048549391682419659735349716446 | 215829.7809231736 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 36 | 36 | 40 | 192.619(A)(3) | 1970-12-16 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | DEAN MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6018425875 | 6013601489 | DEAN MORRIS | dean.morris@atmosenergy.com | 6018425875 | JAMES MCKENZIE | VICE PRESIDENT - TECHNICAL SERVICES | 6016249408 | james.mckenzie@atmosenergy.com | THE INVESTIGATION, TO WHICH THE MISSISSIPPI PUBLIC SERVICE COMMISSION AND PHMSA ARE PARTIES, IS ONGOING UNDER THE DIRECTION OF THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB). ACCORDINGLY, THE RESPONSES IN THIS REPORT WILL BE SUPPLEMENTED WHEN THE INFORMATION IS PERMITTED TO BE RELEASED BY THE NTSB. THE HOUSE INVOLVED WAS VACANT.
2024-05-31 11:04 | NO | YES | NO | 20240020 | 39372 | 2024-03-26 13:28 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2024-02-29 10:08 | EASTERN | NO | 2024 | BRUNSWICK FOREST PARKWAY | LELAND | BRUNSWICK | NC | 28451 | 34.1762 | -78.0392 | [5 empty] | YES |  |  |  | 2024-02-29 11:40 | 1392655 | 1392744 | NATURAL GAS |  | 386.36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-02-29 10:08 | ALLOWED TO BURN OUT |  | 386.36 | NO | 0 | 2024-02-29 10:08 | YES | OPERATOR | 2024-02-29 10:18 | 2024-02-29 10:08 | 2024-02-29 10:08 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2023 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 189744 | 185998.95447039387072 | 37600 | 36857.875285051488 | 0 | 0 |  | 3 | 1159 | 1159 | 0 | 0 | 228503 | 95024.4823255060108485141776937618147448 | 224015.82975544535872 | 0 | 0 | 436 | 1 | 0 | 436 | 0 | 58 | 60 | 60 | 192.619(A)(1) | 2008-09-14 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN INCIDENT IN THE FIELD OCCURRED AND WAS CALLED IN BY ONSITE PERSONNEL. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | > 36” |  | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | C240540966 |  | YES | FACILITY OWNER | YES | YES | 22 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | ON FEBRUARY 29, 2024, AT 10:08AM IN LELAND, NC A PIEDMONT NATURAL GAS COMPANY CREW STRUCK A 4 INCH PLASTIC NATURAL GAS MAIN WHEN OPERATING MECHANICAL EXCAVATION EQUIPMENT. THE EQUIPMENT MADE CONTACT WITH A 2" TAPPING TEE ON TOP OF A 4" MAIN, BREAKING THE TEE OFF THE MAIN. THE ESCAPING GAS BUILT UP A STATIC CHARGE ON THE EXPOSED PLASTIC PIPE THAT IMMEDIATELY CAUSED AN IGNITION OF THE GAS. THE EQUIPMENT OPERATOR RECEIVED MINOR BURNS AND WAS TREATED ON SITE AND SUBSEQUENTLY TRANSPORTED TO A MEDICAL FACILITY, BUT NOT ADMITTED. THE EQUIPMENT OPERATOR FAILED TO MAINTAIN ADEQUATE EXCAVATION CLEARANCE FROM THE 4" PLASTIC PIPE WHILE EXCAVATING STRIKING THE PIPE WHILE DIGGING. THE INCIDENT RESULTED IN 436 CUSTOMER OUTAGES ON FEBRUARY 29TH. ALL CUSTOMERS WERE BACK IN SERVICE ON MARCH 1ST.
2024-05-31 11:04 | NO | YES | NO | 20240022 | 39441 | 2024-04-15 12:08 | ORIGINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2024-03-14 08:25 | EASTERN | YES | 2024 | 6812 INDIANTOWN ROAD | JUPITER | PALM BEACH | FL | 33458 | 26.9337 | -80.1401 | [6 empty] | YES |  |  | 2024-03-14 17:45 | 1393899 | 1393961 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-03-14 08:25 |  |  |  | 2024-03-14 09:04 | 2024-03-14 09:04 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 180 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2006 | 2006 |  |  |  |  | 4 | ASTM D2513 | DRIXELPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 130700 | 128120.327121176316 | 0 | 0 | 0 | 0 |  | 10 | 0 | 0 | 0 | 0 | 130700 | 54132.0201305339573 | 128120.327121176316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 45 | 60 | 192.619(A)(2) | 2006-08-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE OF PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | INTERSTATE HIGHWAY | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | AUGER | ROAD WORK | YES | 047404343047 |  | NO | FACILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoeenergy.com | 407-420-6617 |  | TRACY YALLEDY | atyalledy@tecoenergy.com | 1-561-741-4704 | RUSSELL HARRIS | MANAGER OF PIPELINE SAFETY COMPLIANCE | 407-466-7137 | rharris@tecoenergy.com | ON MARCH 14, 2024, AT APPROXIMATELY 8:25 AM, A 4-INCH PE HIGH PRIORITY GAS MAIN WAS DAMAGED BY A THIRD-PARTY CONTRACTOR ATTEMPTING TO DRIVE A STEEL PILE INTO THE GROUND, SUBSEQUENTLY STRIKING THE GAS FACILITY. A LOCATE TICKET RECEIVED A POSITIVE RESPONSE FROM PGS ON FEBRUARY 20TH, REQUESTING CONTRACTOR CONTACT PGS PRIOR TO INITIATION OF EXCAVATION. THE DAMAGE WAS MADE SAFE AT APPROXIMATELY 06:27PM ON 03/14/2024 BY CONSTRUCTING A TEMPORARY BYPASS. FURTHER INVESTIGATION OF THE INCIDENT IS ONGOING AND WILL BE SUBMITTED IN SUBSEQUENT INCIDENT REPORTING.
2024-05-31 11:04 | NO | YES | NO | 20240023 | 39465 | 2024-04-19 12:34 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2024-03-22 16:55 | EASTERN | YES | 2024 | 990 E. WATER ST. | PROSPECT | MARION | OH | 43342 | 40.4527 | -83.1787 | [6 empty] | YES |  |  | 2024-03-22 17:35 | 1394537 | 1394682 | NATURAL GAS |  | 38 | 0.072 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-03-20 15:02 | NO |  |  | 2024-03-20 15:02 | 2024-03-22 16:55 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 38 | NO | YES |  |  | YES | CASED | [7 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | OTHER | UNKNOWN, PIPE NOT EXCAVATED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 141982 | 139179.65023197288216 | 14972 | 14676.49225446252336 | 0 | 0 |  | 4.35 | 165 | 165 | 0 | 0 | 157119 | 65128.8436964170005383251417769376181474 | 154021.14248643540552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 50 | 192.619(A)(4) | 1995-01-27 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VOLUME RELEASED WAS NOT ENOUGH TO TRIGGER ANY ACTION BY CONTROLLERS. PRESSURE CONTROL WAS NOT A FACTOR IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | ABANDON PIPE IN PLACE FILLED CARRIER PIPE WITH CONCRETE PER RAIL ROAD | [5 empty] | YES | UNKNOWN |  |  |  |  | YES | UNKOWN | YES | NO |  | NO | NO | [8 empty] | N/A Bare/Ineffectively Coated Pipe | NONE |  | NO | [19 empty] | 2022-03-25 | NO | [227 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | rrsmith@nisource.com | 1-614-460-5491 |  | ROB R. SMITH | rrsmith@nisource.com | 1-614-460-5491 | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE- RISK MANAGEMENT | 1-614-460-5491 | rrsmith@nisource.com | WHILE CONDUCTING A LEAKAGE SURVEY, A GRADE ONE HAZARDOUS LEAK WAS DETECTED. COLUMBIA DISCOVERED A BARE STEEL LINE LEAKING WITHIN THE CONFINES OF A STEEL CASING UNDER A RAILWAY. THE ENDS OF THE STEEL CASING WERE EXCAVATED AND THE LEAK MIGRATION PATH WAS BROKEN AND NO LONGER PRESENTED A HAZARD. COLUMBIA CREWS COORDINATED THE REPAIR WITH THE RAILROAD OPERATOR WHILE CONTINUOUSLY MONITORING THE LEAK UNTIL THE LINE WAS REPLACED. THE COST OF REPAIR TRIGGERED THE REPORTING CRITERIA AS WRITTEN IN 49 CFR PART 191.3. THE PIPE WAS REPLACED SUCCESSFULLY AND THE LEAK WAS MADE SAFE ON 03-29-24 AT 19:15 HOURS. PLEASE CLOSE YOUR FILE ON THIS EVENT.
2024-05-31 11:04 | NO | YES | NO | 20240024 | 39466 | 2024-04-19 15:48 | ORIGINAL | 603 | SUMMIT UTILITIES INC. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2024-04-03 16:05 | CENTRAL | YES | 2024 | RE-277 (HIGHWAY 28) | ROVER | YELL | AR | 72860 | 34.9452 | -93.415 |  | YES | [8 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE | See narrative. Section H | NATURAL GAS |  | 0 | 0.715 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-04-03 09:09 | YES | OPERATOR | 2024-04-03 15:00 | 2024-04-03 08:30 | 2024-04-03 09:30 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | SEE NARRATIVE SECTION H | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | DISTRIBUTION FACILITIES MAINS, SVC LINES, REGS, METERS | UNKNOWN | UNKNOWN | [7 empty] | OTHER | STEEL, PLASTIC | [9 empty] | OTHER | [8 empty] | RELEASE OF DIESEL FUEL DUE TO ENERGY TRANSFER PIGGING OPERATION, INTO(RE)-277 SUMMIT DISTRIBUTION SYSTEM | CLASS 1 LOCATION | 120250 | 117876.58252732557 | 1650000 | 1617433.356923802 | 30000 | 29407.8792167964 | 175000 | 171545.962097979 | ESTIMATED COSTS | 7.97 | 0 | 0 | 6 | 6 | 1975256 | 818093.789736823218209357277882797731569 | 1936269.78076590297 | 7 | 0 | 22 | 0 | 0 | 24 | 7 | 35 | 35 | 60 | 192.619(A)(2) | 2022-01-10 | PRESSURE DID NOT EXCEED MAOP | WICK |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SEE NARRATIVE. SECTION H | [47 empty] | RON WOODS | MANAGER OF OPERATIONS-NORTH REGION | rwoods@summitutilities.com | 870-219-8765 |  | RON WOODS | rwoods@summitutilities.com | 870-219-8765 | CINDY WESTCOTT | VP OF OPERATIONS AND ENGINEERING | 501-508-9290 | cwestcott@summitutilities.com | ON 4-03-2024, SUA RECEIVED A LOW-PRESSURE CUSTOMER COMPLAINT FROM A RURAL EXTENSION (RE)-277 NEAR ROVER, ARKANSAS. A TECHNICIAN WAS DISPATCHED IMMEDIATELY, UPON INVESTIGATION FOUND A FOREIGN LIQUID IN THE CUSTOMER'S SERVICE LINE AND HOUSE PIPING. THE SYSTEM HAS 31 TOTAL CUSTOMERS (22 ACTIVE RESIDENTIAL, 7 COMMERCIAL AND 2 INACTIVE RESIDENTIAL). IT WAS DETERMINED THAT ENERGY TRANSFER, THE PIPELINE SUPPLIER TO THE LDC, HAD BEEN PERFORMING AN INLINE INSPECTION OF THE PIPELINE THAT SERVES (RE)-277. PART OF THAT PROCESS INCLUDED INJECTING SEVERAL THOUSAND GALLONS OF DIESEL FUEL BOTH IN FRONT OF AND BEHIND THE INSPECTION TOOL. ENERGY TRANSFER STATED THAT THEY HAD FAILED TO CLOSE OFF A VALVE TO THE LDC STATION AND HAD INADVERTENTLY PUSHED DIESEL FUEL OUT OF THEIR SYSTEM INTO THE SUA DISTRIBUTION SYSTEM. ADDITIONAL DETAILS OF ENERGY TRANSFER'S PROCESS OR GAS HANDLING PLAN ARE NOT AVAILABLE FOR INCLUSION IN THIS REPORT.
2024-05-31 11:04 | NO | YES | YES | 20240025 | 39467 | 2024-04-19 18:01 | ORIGINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2024-03-20 05:52 | MOUNTAIN | YES | 2024 | 67 N 370 E | AMERICAN FORK | UTAH | UT | 84003 | 40.3783 | -111.7891 |  |  |  | YES | [5 empty] | 2024-03-20 07:42 | 1394296 | 1394442 | NATURAL GAS |  | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2024-03-20 05:52 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | YES | 3 | 2024-03-20 06:06 |  |  |  | 2024-03-20 06:22 | 2024-03-20 06:22 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER OWNED FUEL LINE | UNKNOWN | UNKNOWN | [7 empty] | STEEL |  | OTHER | 1/2" BLACK STEEL PIPE | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 3 LOCATION | 1000000 | 980262.64055988 | 1500 | 1470.39396083982 | 10000 | 9802.6264055988 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1011500 | 418932.9637493121485 | 991535.66092631862 | 0 | 0 | 2 | 0 | 1 | 4 | 0 | 0.25 | 0.25 | 0.25 | 192.619(A)(1) | 1996-06-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BEING ON A RESIDENTIAL CUSTOMER OWNED FUEL LINE. | [12 empty] | YES | 1 | 0 | YES | 1 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | STEVE BURSETT | SUPERVISOR GAS OPERATIONS | steve.bursett@dominionenergy.com | 801-548-7520 |  | JUSTIN WITHERS | justin.withers@dominionenergy.com | 801-209-0814 | RYAN JAMISON | MANAGER GAS OPERATIONS | 801-574-0111 | ryan.jamison@dominionenergy.com | AT APPROXIMATELY 6:00 AM, ON MARCH 20, 2024, QUESTAR GAS COMPANY D/B/A DOMINION ENERGY UTAH (DEU) RECEIVED A CALL FROM 911 REPORTING A RESIDENTIAL EXPLOSION AT 67 NORTH 370 EAST, AMERICAN FORK, UTAH. DEU RESPONDED TO THE SCENE AND OBSERVED AN ACTIVE FIRE IN THE DUPLEX STRUCTURE. AMERICAN FORK FIRE DEPARTMENT SHUT OFF THE FLOW OF NATURAL GAS. IT WAS REPORTED THAT THE RESIDENT OF 69 NORTH 370 EAST WAS FOUND DECEASED. THE STRUCTURE AT 67 AND 69 NORTH 370 EAST WERE DESTROYED. THE HOME AT 53 NORTH 370 EAST SUSTAINED STRUCTURAL DAMAGE. ONCE THE SCENE WAS SECURE, DEU PERFORMED PRESSURE TESTS ON THE MAIN AND SERVICE LINES ASSOCIATED WITH 67 AND 69 NORTH 370 EAST. 67 AND 69 NORTH 370 EAST WERE SERVED BY A SINGLE SERVICE LINE AND DUAL METER SETS. DEU TESTED THE MAIN AND SERVICE LINES AT OPERATING PRESSURE OF 45 PSI FOR 15 MINUTES. EACH HELD PRESSURE, INDICATING NO LEAKS ON THE MAIN AND SERVICE LINES. THESE PRESSURE TESTS WERE WITNESSED BY A REPRESENTATIVE OF UTAH PIPELINE SAFETY. DEU ALSO EXECUTED ITS LEAK SCREEN PROCEDURE, SCREENING FOR LEAKS ON THE OTHER MAIN AND SERVICE LINES IN THE NEIGHBORHOOD AND FOUND NO LEAKS. DEU'S CAUSE AND ORIGIN INVESTIGATION IS ONGOING. AT THE FIRE DEPARTMENTS DIRECTION, DEU REMOVED THE METER SETS AND RISER FOR 67 AND 69 NORTH 370 EAST AND SURRENDERED THEM TO THE FIRE DEPARTMENTS CUSTODY ON THE DAY OF THE INCIDENT . THIS EQUIPMENT WILL BE TESTED AT A LATER DATE. INITIAL NRC INCIDENT REPORT #1394296, WAS MADE ON 03/20/2024 AT 7:42AM MT. 48-HOUR UPDATE NRC #1394442, WAS MADE ON 03/21/2024 AT 7:30PM MT. NOTE: PART E: QUESTION 3.A: THIS QUESTION WILL BE REVISITED AT THE CONCLUSION OF THE INVESTIGATION.
2024-05-31 11:04 | NO | YES | NO | 20240026 | 39479 | 2024-04-24 14:01 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-03-25 12:37 | EASTERN | YES | 2024 | 2661 CAMPBELLTON ROAD SW | ATANTA | FULTON | GA | 30311 | 33.7024 | -84.4761 | [5 empty] | YES |  |  |  | 2024-03-25 13:30 | 1394734 | 1394916 | NATURAL GAS |  | 4352.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-03-25 12:37 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1614 | YES | 20 | 2024-03-25 10:11 |  |  |  | 2024-03-25 10:33 | 2024-03-25 12:37 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2011 | UNKNOWN |  |  |  |  | 6 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4.5 | 4.5 | [7 empty] | CLASS 3 LOCATION | 300000 | 294078.792167964 | 80079 | 78498.45199339463052 | 108314 | 106176.16764960284232 | 0 | 0 |  | 1.45 | 6311 | 6311 | 0 | 0 | 494704 | 206990.1054352769623942967863894139886578 | 485064.41181096147284 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 39 | 39 | 45 | 192.619(A)(2) | 2011-04-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 13 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 13 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | NO | NO | > 36” |  | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 240112001811 |  | NO | CONTRACT LOCATOR | YES | YES | 13 | EXCAVATION ISSUE | EXCAVATOR DUG PRIOR TO VERIFYING MARKS BY TEST-HOLE (POTHOLE) | [170 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | MANAGER COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A THIRD-PARTY PARTY EXCAVATOR (NEXTIER INFRASTRUCTURE SOLUTIONS) STRUCK AND DAMAGED AN ATLANTA GAS LIGHT COMPANY (AGLC) 6-INCH PLASTIC GAS MAIN WHILE DIRECTIONALLY BORING TO INSTALL TELECOMMUNICATION FIBER MAIN NEAR 2661 CAMPBELLTON ROAD SW, ATLANTA. ESCAPING GAS FROM THE DAMAGE MIGRATED TO A NEARBY STRUCTURE AT 2683 CAMPBELLTON ROAD SW, ATLANTA (PO FREDDIE'S BBQ RESTAURANT) AND WAS IGNITED BY AN UNKNOWN IGNITION SOURCE WHERE A SUBSEQUENT EXPLOSION AND FIRE OCCURRED AT THE RESTAURANT RESULTING IN SIGNIFICANT PROPERTY DAMAGE. AT LEAST ONE VEHICLE WAS DAMAGED BY FALLING DEBRIS FROM THE EXPLOSION. UPON ARRIVAL, AGLC PERSONNEL WORKED WITH EMERGENCY RESPONDERS TO SECURE THE AREA AND MONITOR THE SURROUNDING AREA FOR GAS. GAS WAS SHUT-OFF TO THE DAMAGED AREA AT 14:00 HOURS BY PERFORMING FOUR (4) SQUEEZE-OFF OPERATIONS. A LARGE PROJECT MARKING ' UTILITY FACILITY LOCATING AGREEMENT WAS SIGNED ON MAY 5, 2023, WITH NEXTIER INFRASTRUCTURE SOLUTIONS (EXCAVATOR) TO LOCATE THE AREA AS A LARGE PROJECT EXCAVATION. AS TO THE LOCATION OF THIS INCIDENT, THE LARGE PROJECT MARKING AGREEMENT STATED 'CONTINUE LOCATES EAST ON THE NORTH SIDE OF CAMPBELLTON ROAD SW TO THE NORTHWEST CORNER OF CAMPBELLTON ROAD SW AND DODSON DRIVE SW. LOCATE THIS CORNER 50 FEET IN ALL DIRECTIONS. THEN CONTINUE EAST ON THE NORTH SIDE OF CAMPBELLTON ROAD SW TO THE NORTHWEST CORNER OF WILLIS MILL ROAD AND CAMPBELLTON ROAD SW AND LOCATE IT 50 FEET IN ALL DIRECTIONS'. AGLC FACILITIES WERE LAST MARKED BY STAKE CENTER LOCATING TO SATISFY THIS REQUEST ON MARCH 13, 2024. INVESTIGATION OF THE SITE REVEALED THAT THE LOCATE MARKS WERE ACCURATE AT THE POINT OF DAMAGE, HOWEVER, BECAUSE THE EXCAVATOR DID NOT VERIFY THE LOCATION AND DEPTH OF AGLC FACILITIES BY POT HOLING AND INSTEAD BLINDLY CROSSED THE MARKS ON THE GROUND, THE GAS MAIN WAS DAMAGED. AGLC INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1394734. ADDITIONAL NRC REPORT NUMBER 1394916 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2024-05-31 11:04 | NO | YES | NO | 20240027 | 39503 | 2024-04-30 19:32 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2024-04-15 11:22 | MOUNTAIN | NO | 2024 | 27TH AVE & NORTHERN AVE | PHOENIX | MARICOPA | AZ | 85051 | 33.5533 | -112.1172 | YES | [8 empty] | 2024-04-15 11:40 | 1396485 | 1396605 | NATURAL GAS |  | 11773.13 | 0.29 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 555 | 2024-04-15 10:47 |  |  |  | 2024-04-15 10:47 | 2024-04-15 11:22 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2019 | UNKNOWN | [7 empty] | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.375 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION 2-INCH BYPASS BROKEN WHEN STRUCK BY THIRD-PARTY VEHICLE. | CLASS 3 LOCATION | 20000 | 19605.2528111976 | 250000 | 245065.66013997 | 21512 | 21087.40992372413856 | 0 | 0 |  | 1.1414 | 13438 | 13438 | 0 | 0 | 304950 | 130769.5729301519043751833648393194706994 | 299196.32287489173856 | 0 | 0 | 0 | 3 | 0 | 0 | 4 | 388 | 388 | 400 | 192.619(A)(4) | 1987-05-14 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REG STATION WAS HIT BY A 3RD PARTY VEHICLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | SMALL TRUCK | ROADWAY | 10 | YES | YES | [141 empty] | SHAWN L. BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 6027230987 | 6024845322 | SHAWN L. BRINK | shawn.brink@swgas.com | 6027230987 | ROBERT MCGEE | DIRECTOR CENTRAL SUPPORT | 6024845367 | robert.mcgee@swgas.com | ACC- PL2024-0058 ON APRIL 15, 2024 AT 10:35 SOUTHWEST GAS (SWG) DISPATCH WAS NOTIFIED BY THE PHOENIX FIRE DEPARTMENT OF A VEHICLE THAT HAD COLLIDED WITH REGULATOR STATION (DR #423886) AT THE NORTHWEST CORNER OF 27TH AVENUE AND NORTHERN AVENUE IN PHOENIX, ARIZONA. CONSTRUCTION CREWS RESPONDED AND DISCOVERED A MULTIPLE-VEHICLE ACCIDENT HAD CAUSED ONE VEHICLE TO COLLIDE WITH THE REGULATOR STATION AND SHEARED OFF THE ABOVE-GROUND 2-INCH BYPASS PIPE FROM THE REGULATOR STATION RESULTING IN A RELEASE OF GAS. GAS FLOW WAS CONTROLLED UTILIZING THREE VALVES TO ISOLATE THE DAMAGED REGULATOR STATION AND GAS OFF AT 12:22. APPROXIMATELY 555 INDIVIDUALS WERE EVACUATED FROM A SCHOOL AS A PRECAUTION BY THE FIRE DEPARTMENT. THREE PEOPLE WERE TRANSPORTED TO THE HOSPITAL DUE TO MINOR INJURIES SUSTAINED IN THE VEHICLE ACCIDENTS. THERE WERE NO OUTAGES, OR FATALITIES DUE TO THE GAS INCIDENT. THE DISTRICT REGULATOR STATION WAS TEMPORARILY TAKEN OUT OF SERVICE FOR REPLACEMENT / RELOCATION AT A LATER DATE. ON APRIL 15, 2024, THE ARIZONA CORPORATION COMMISSION (ACC) WAS TELEPHONICALLY NOTIFIED AT 11:27 OF THE INCIDENT INVOLVING THE EVACUATION OF THE SCHOOL AND THAT ESTIMATED INCIDENT COSTS WOULD EXCEED $139,700. ON APRIL 15, 2024, PHMSA/NRC WAS TELEPHONICALLY NOTIFIED AT 11:40 THAT INCIDENT COSTS WOULD EXCEED $139,700 AND WAS ASSIGNED NRC REPORT #1396485. ON APRIL 16, 2024, A FOLLOW-UP PHMSA/NRC WAS TELEPHONICALLY UPDATED AT 14:11 AND WAS ASSIGNED NRC REPORT #1396605.
2024-05-31 11:04 | NO | YES | NO | 20240028 | 39522 | 2024-05-03 17:04 | ORIGINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2024-04-05 13:07 | EASTERN | YES | 2024 | 2190 NW NORTH RIVER DRIVE | MIAMI | DADE | FL | 33125 | 25.7896 | -80.2309 | [7 empty] | YES | PRESSURE WAS REDUCED, GAS FLOW WAS NOT INTERRUPTED & SERVICE WAS CONTINUOUSLY PROVIDED TO CUSTOMERS. | 2024-04-05 17:18 | 1395698 | 1395827 | NATURAL GAS |  | 11784 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2024-04-05 13:07 | YES | OPERATOR | 2024-04-05 16:55 | 2024-04-05 13:15 | 2024-04-05 13:15 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 1 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 10 | API 5L | UNKNOWN | STEEL |  | CONTINUOUS WELDED |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 140000 | 137236.7696783832 | 0 | 0 | 0 | 0 | 0 | 10 | 117840 | 117840 | 0 | 0 | 257840 | 145973.9713433026017769376181474480151229 | 255076.7696783832 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 65 | 65 | 100 | 192.619(A)(2) | 2016-01-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 100 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE OF PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [5 empty] | NO | NO | > 36” |  | CONTRACTOR | AUGER | SITE DEVELOPMENT | YES | 088406955 |  | NO | FACILITY OWNER | UNKNOWN/OTHER | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | CONTRACTOR FAILED TO CONTACT PGS LOCATOR AS REQUESTED. | [169 empty] | IYANNA JONES | COMPLIANCE ANALYST | iejones@tecoenergy.com | (407)-420-6617 |  | MYLENE ARZA | mxarza@tecoenergy.com | (305) 970-1325 | RUSSELL HARRIS | MGR PIPELINE SAFETY COMPLIANCE | (407)-420-6667 | rharris@tecoenergy.com | ON APRIL 5, 2024, AT APPROXIMATELY 13:07 PM, A 10-INCH STEEL HIGH PRIORITY GAS MAIN WAS DAMAGED BY A THIRD-PARTY CONTRACTOR ATTEMPTING TO DRIVE A STEEL SHEET PILE INTO THE GROUND, SUBSEQUENTLY STRIKING THE GAS FACILITY. A LOCATE TICKET RECEIVED A POSITIVE RESPONSE FROM PGS ON APRIL 2ND, REQUESTING THE CONTRACTOR TO CONTACT PGS PRIOR TO INITIATION OF EXCAVATION. PRELIMINARY INVESTIGATION DID NOT FIND WHERE THE CONTRACTOR CONTACTED PGS PER THE COMMUNICATED INSTRUCTIONS. THE DAMAGE WAS MADE SAFE AT APPROXIMATELY 04:24AM ON 04/15/2024 BY CONSTRUCTING A PERMANENT OFFSET. FURTHER INVESTIGATION OF THE INCIDENT IS ONGOING AND WILL BE SUBMITTED IN A SUBSEQUENT INCIDENT REPORTING.
2024-05-31 11:04 | NO | YES | NO | 20240029 | 39524 | 2024-05-05 11:08 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2024-03-30 01:19 | EASTERN | YES | 2024 | 114 CLIFF STREET | PATERSON | PASSAIC | NJ | 07501 | 40.9258 | -74.1789 | [5 empty] | YES |  |  |  | 2024-04-09 10:59 | 1395960 | 1396116 | NATURAL GAS |  | 55 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-03-30 01:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 49 | NO | 10 | 2024-03-30 01:19 |  |  |  | 2024-03-30 01:36 | 2024-04-09 10:15 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | VEHICLE STRUCK THE METER SET CAUSING IT AND THE VALVE TO BE COMPLETELY TORN OFF THE SWEEP. | CLASS 4 LOCATION | 150000 | 147039.396083982 | 89 | 87.24337500982932 | 1385 | 1357.6637571754338 | 0 | 0 |  | 18.588 | 1022 | 1022 | 0 | 0 | 152496 | 63499.106982853311929856332703213610586 | 149506.30321616726312 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 15 | 15 | 15 | 192.619(A)(2) | 2005-08-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | PASSENGER CAR | ROADWAY | 25 | NO | [118 empty] | YES | [23 empty] | HENRY VARUM | PRINCIPAL REGULATORY SPECIALIST | henry.varum@pseg.com | 7323433421 |  | HENRY VARUM | henry.varum@pseg.com | 7323433421 | CHRIS LAROSSA | DISTRICT MANAGER REGULATORY POLICY PROCEDURE | 9738967617 | christopher.larossa@pseg.com | ON SATURDAY, 3/30/3024 AT 01:19 HRS, PSE&G WAS INITIALLY NOTIFIED OF AN SUV THAT STRUCK A METER-SET COMPLETELY SEPARATING IT FROM THE SERVICE SWEEP AT 106 CLIFF ST, PATERSON, WHICH HAS SINCE BEEN UPDATED TO 114 CLIFF STREET. THE DAMAGE TO THE METER-SET, WHICH IS FED BY A 1.25" 15# SERVICE CREATED THE CONDITION OF UNCONTROLLED GAS THAT FED A FIRE ON THE PREMISES. A PSE&G FIRST RESPONDER ARRIVED ON SITE AT 01:36 HRS AND CONFIRMED THE GAS FED FIRE. A PSE&G CREW REPORTED TO THE SCENE AND ONCE THE FIRE DEPARTMENT WAS EXTINGUISHED THE FIRE, RETIRED THE SERVICE TO 114 CLIFF STREET AT THE MAIN AND SHUT GAS OFF AT THE CURB TO 112 AND 106 CLIFF STREET. THE BUILDING THAT WAS STRUCK WAS EVACUATED AND RESIDENTS OF 106 CLIFF STREET THAT WERE INITIALLY EVACUATED WERE ALLOWED BACK INTO THEIR HOMES AT 4:15 AM. THERE WERE NO INJURIES TO BE REPORTED, BUT THE DRIVE AND ONE PASSENGER OF THE SUV WERE TRANSPORTED TO THE HOSPITAL FOR OBSERVATIONS.
2024-05-31 11:04 | NO | YES | NO | 20240030 | 39527 | 2024-05-07 12:52 | ORIGINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2024-04-08 07:46 | EASTERN | YES | 2024 | 3619 EAST INDEPENDENCE BLVD | CHARLOTTE | MECKLENBURG | NC | 28205 | 35.2022 | -80.7817 |  | YES | [7 empty] | 2024-04-08 09:59 | 1395857 | 1395963 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2024-04-08 07:46 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 0 | NO | 0 | 2024-04-08 08:01 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-04-08 08:01 | 2024-04-08 08:05 | 2024-04-08 08:05 | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | 2004 | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES |  |  |  | STEEL |  | SEAMLESS |  | 0.191 | [6 empty] | OTHER | [8 empty] | FIRE | CLASS 3 LOCATION | 0 | 0 | 139700 | 136942.690886215236 | 1100 | 1078.288904615868 | 0 | 0 |  | 3 | 0 | 0 | 0 | 0 | 140800 | 58315.1372178973312 | 138020.979790831104 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 70 | 70 | 192.619(A)(2) | 2004-01-12 | PRESSURE DID NOT EXCEED MAOP | DRIP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STRUCTURE FIRE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY GOVERNANCE MANAGER | 704-731-4618 | farris.berry@duke-energy.com | ON 4/8 AT 7:46AM, A CALL CAME IN REGARDING A FIRE THAT TOOK PLACE AT 3619 EAST INDEPENDENCE BLVD. THE FIRST RESPONDER ARRIVED ON THE SCENE WHERE THERE WAS AN ACTIVE FIRE AT THE METER. AN UNDERGROUND CREW WAS DISPATCHED AND THE GAS SERVICE VALVE WAS TURNED OFF. BOTH METERS WERE MELTED. THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION. WE WILL FILE A SUPPLEMENTAL REPORT WITH ANY MISSING INFORMATION FOLLOWING RESULTS OF THE INVESTIGATION.
2024-05-31 11:04 | NO | NO | NO | 20240031 | 39530 | 2024-05-08 16:11 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2024-04-29 14:42 | MOUNTAIN | YES | 2024 | CHARLES ST AND COLLEGE DR | CHEYENNE | LARAMIE | WY | 82001 | 41.1493 | -104.7611 | [6 empty] | YES |  |  | 2024-05-06 14:30 | 1398244 |  | NATURAL GAS |  | 4782 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-04-29 15:11 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2024-04-29 14:42 | 2024-04-29 15:11 | 2024-05-06 10:56 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | UNKNOWN |  |  |  |  | 4 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 4 | 12.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 130 | 150 | 192.619(A)(1) | 2010-02-09 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE. CONTROLLER NOT INVOLVED IN RELEASE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES |  |  | NO | NO | 18” – 36” |  | CONTRACTOR | BORING | ELECTRIC | YES | 20241701720 |  | Unknown | FACILITY OWNER | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | JACOB KILMURRAY | PIPELINE SAFETY PROFESSIONAL | jake.kilmurray@blackhillscorp.com | 3072865179 |  | MELINDA BARRETT | melinda.barrett@blackhillscorp.com | 6055800515 | JAKE KILMURRAY | PIPELINE SAFETY PROFESSIONAL | 3072865179 | jake.kilmurray@blackhillscorp.com | ON 4/29/24, AN ELECTRIC CONTRACTOR BORED INTO 4 INCH 130 PSI DISTRIBUTION MAIN CAUSING 4 INCH HOLE IN THE PIPE. GAS WAS RELEASED FOR 90 MINUTES BEFORE FLOW OF GAS WAS STOPPED. 2 FEET OF 4 INCH PIPE WAS REPLACED AND MAIN WAS RETURNED TO SERVICE. GAS LOSS CALCULATIONS WERE COMPLETED ON 5/6/24 AND IT WAS DETERMINED THE GAS LOSS EXCEEDED THE REPORTABLE THRESHOLD.
2024-05-31 11:04 | NO | YES | YES | 20240032 | 39541 | 2024-05-10 14:17 | ORIGINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2024-04-15 21:37 | EASTERN | YES | 2024 | 2175 SAVANNAH HIGHWAY | JESUP | WAYNE | GA | 31545 | 31.6309 | -81.8651 | [5 empty] | YES |  |  |  | 2024-04-15 22:23 | 1396518 | 1396669 | NATURAL GAS |  | 51 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2024-04-15 17:24 |  |  |  | 2024-04-15 18:15 | 2024-04-15 18:15 | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 300 | 294.078792167964 | 600 | 588.157584335928 | 0 | 0 |  | 1.285 | 66 | 66 | 0 | 0 | 966 | 422.034671300923152930056710775047258979 | 948.236376503892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(4) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | RALPH MCCOLLUM | PRINCIPAL COMPLIANCE ENGINEER | rmccollu@southernco.com | 4045843733 | (404) 584-4710 |  |  |  | RICK SLAGLE | MANAGER COMPLIANCE AND QA | 4045844910 | rslagle@southernco.com | ON APRIL 15, 2024, AN AGL EMPLOYEE WAS DISPATCHED TO A LEAK CALL CONCERNING AN OUTSIDE LEAK AT 2175 SAVANNAH HIGHWAY, JESUP, GA ("PREMISES"). ACCORDING TO THE HOMEOWNER, THE EMPLOYEE DETERMINED THAT THE 3/4" PLUG ON THE OUTLET OF THE SERVICE RISER VALVE WAS LEAKING ABOVE GROUND. UPON INFORMATION AND BELIEF, BECAUSE THERE WAS NO METER AT THIS PREMISES, THE EMPLOYEE PLANNED TO ELIMINATE THE ABOVE-GROUND LEAK BY RETIRING THE ABOVE-GROUND FACILITIES BY CUTTING AND PLUGGING THE SERVICE LINE BELOW GROUND. AT APPROXIMATELY 17:05-17:10 HOURS, THE HOMEOWNER FOUND THE EMPLOYEE UNRESPONSIVE AND CALLED 911. ACCORDING TO THE CITY OF JESUP FIRE DEPARTMENT, THE EMPLOYEE WAS FOUND LYING ON THE GROUND PARTIALLY WITHIN THE EXCAVATION HOLE THAT HE HAD PRESUMEDLY DUG AND GAS BLOWING IN THE HOLE. WAYNE COUNTY EMS TRANSPORTED THE EMPLOYEE TO WAYNE MEMORIAL HOSPITAL, WHERE THE EMPLOYEE WAS PRONOUNCED DECEASED. AGL WAS CONTACTED BY 911 AT 17:24 HOURS AND DISPATCHED ADDITIONAL AGL CREWS TO THE PREMISES. UPON THEIR ARRIVAL, AGL CREWS FOUND A HOLE MEASURING APPROXIMATELY 3 FEET DEEP AND 14 INCHES BY 16 INCHES IN DIAMETER AND GAS BLOWING FROM A CUT TO THE BELOW-GROUND PLASTIC PORTION (PIGTAIL) OF THE RISER. AGL CREWS PULLED BACK APPROXIMATELY 20 FEET FROM THE BLOWING GAS AND SQUEEZED OFF THE SERVICE LINE TO STOP THE LEAK. THE INCIDENT REMAINS UNDER INVESTIGATION PENDING AUTOPSY RESULTS. AGL INITIALLY NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) UNDER NRC REPORT NUMBER 1396518. ADDITIONAL NRC REPORT NUMBER 1396669 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.