## lng2011toPresentFields
Liquefied Natural Gas (LNG) Facilities Incidents for 2011 - present (PHMSA Form 7100.3 Rev. 9-2019) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | DATE | Data as of date | Not on the form
SIGNIFICANT | VARCHAR2 | Identify if record meets the significant criteria or not: If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury then SERIOUS = ‘YES’ else SERIOUS = ’NO’. | Not on the form
REPORT_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report | Top of first page
SUPPLEMENTAL_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report submission | Top of first page
REPORT_RECEIVED_DATE | DATE | Date when Original Report submitted | Top of first page
REPORT_TYPE | VARCHAR2 | Report Type (Original, Supplemental, Final) | PART A - KEY REPORT INFORMATION
OPERATOR_ID | NUMBER | Operator's OPS-issued Operator Identification number | PART A - KEY REPORT INFORMATION
NAME | VARCHAR2 | Operator Name | PART A - KEY REPORT INFORMATION
OPERATOR_STREET_ADDRESS | VARCHAR2 | Operator Address - Street | PART A - KEY REPORT INFORMATION
OPERATOR_CITY_NAME | VARCHAR2 | Operator Address - City | PART A - KEY REPORT INFORMATION
OPERATOR_STATE_ABBREVIATION | VARCHAR2 | Operator Address - State | PART A - KEY REPORT INFORMATION
OPERATOR_POSTAL_CODE | VARCHAR2 | Operator Address - Zip | PART A - KEY REPORT INFORMATION
LOCAL_DATETIME | DATE | Earliest local time (24-hr clock) and date an of the Iincident reporting criteria was met | PART A - KEY REPORT INFORMATION
TIME_ZONE | VARCHAR2 | Time Zone for local time | PART A - KEY REPORT INFORMATION
DAYLIGHT_SAVINGS_IND | VARCHAR2 | Is Daylight Saving in effect? (Yes/No) | PART A - KEY REPORT INFORMATION
IYEAR | NUMBER | Year incident occurred, derived from incident date | Not on the form
NRC_RPT_NUM | VARCHAR2 | Initial Operator National Response Center Report Number | PART A - KEY REPORT INFORMATION
NRC_RPT_DATETIME | DATE | National Response Center time and date of initial telephonic report | PART A - KEY REPORT INFORMATION
ADDITIONAL_NRC_REPORT_NUMBERS | VARCHAR2 | Additional NRC Report numbers submitted by the operator | PART A - KEY REPORT INFORMATION
UNINTENTIONAL_RELEASE_IND | VARCHAR2 | Incident resulted from - Unintentional release of commodity (Yes/No) | PART A - KEY REPORT INFORMATION
INTENTIONAL_RELEASE_IND | VARCHAR2 | Incident resulted from - Intentional release of commodity (Yes/No) | PART A - KEY REPORT INFORMATION
EMERGENCY_SHUTDOWN_IND | VARCHAR2 | Incident resulted from - Emergency shutdown (Yes/No) | PART A - KEY REPORT INFORMATION
RESULTED_FROM_OTHER_IND | NUMBER | Incident resulted from - Other reason (Yes/No) | PART A - KEY REPORT INFORMATION
RESULTED_FROM_OTHER_DETAILS | NUMBER | Incident resulted from - Other reason Details | PART A - KEY REPORT INFORMATION
COMMODITY_RELEASED_TYPE | VARCHAR2 | Type of Commodity released | PART A - KEY REPORT INFORMATION
COMMODITY_DETAILS | NUMBER | Sub type of commodity released - Name of Other Sub-type | PART A - KEY REPORT INFORMATION
UNINTENTIONAL_RELEASE | NUMBER | Estimated volume of commodity released unintentionally in Thousand Cubic Feet (MCF) | PART A - KEY REPORT INFORMATION
INTENTIONAL_RELEASE | NUMBER | Estimated volume of intentional and controlled release/blowdown in Thousand Cubic Feet (MCF) | PART A - KEY REPORT INFORMATION
VOLUME_TO_GROUND | VARCHAR2 | Estimated volume of liquid spilled to the ground in Barrels | PART A - KEY REPORT INFORMATION
FATALITY_IND | VARCHAR2 | Fatalities (Yes, No) | PART A - KEY REPORT INFORMATION
NUM_EMP_FATALITIES | NUMBER | Number of Fatalities of Operator Employees | PART A - KEY REPORT INFORMATION
NUM_CONTR_FATALITIES | NUMBER | Number of Fatalities of Contractor Employees working for the Operator | PART A - KEY REPORT INFORMATION
NUM_ER_FATALITIES | NUMBER | Number of Fatalities of Non-Operator emergency responders | PART A - KEY REPORT INFORMATION
NUM_GP_FATALITIES | NUMBER | Number of Fatalities of General Public | PART A - KEY REPORT INFORMATION
FATAL | NUMBER | Total number of Fatalities | PART A - KEY REPORT INFORMATION
INJURY_IND | VARCHAR2 | Injuries (Yes, No) | PART A - KEY REPORT INFORMATION
NUM_EMP_INJURIES | NUMBER | Number of Injuries of Operator Employees | PART A - KEY REPORT INFORMATION
NUM_CONTR_INJURIES | NUMBER | Number of Injuries of Contractor Employees working for the Operator | PART A - KEY REPORT INFORMATION
NUM_ER_INJURIES | NUMBER | Number of Injuries of Non-Operator emergency responders | PART A - KEY REPORT INFORMATION
NUM_GP_INJURIES | NUMBER | Number of Injuries of General Public | PART A - KEY REPORT INFORMATION
INJURE | NUMBER | Total number of Injuries | PART A - KEY REPORT INFORMATION
SHUTDOWN_DUE_ACCIDENT_IND | VARCHAR2 | The pipeline/facility shutdown due to the Incident (Yes, No, Null) | PART A - KEY REPORT INFORMATION
SHUTDOWN_EXPLAIN | VARCHAR2 | Explain No shutdown | PART A - KEY REPORT INFORMATION
SHUTDOWN_DATETIME | DATE | The pipeline/facility shutdown due to the Incident - Local time and date of shutdown | PART A - KEY REPORT INFORMATION
RESTART_DATETIME | DATE | The pipeline/facility shutdown due to the Incident - Local time pipeline/facility restarted | PART A - KEY REPORT INFORMATION
STILL_SHUTDOWN_IND | VARCHAR2 | The pipeline/facility shutdown due to the Incident - Still shut down (Yes, Null) | PART A - KEY REPORT INFORMATION
IGNITE_IND | VARCHAR2 | Commodity ignite (Yes, No) | PART A - KEY REPORT INFORMATION
GAS_CONSUMED_BY_FIRE_IN_MCF | NUMBER | Estimated volume of gas consumed by fire (in mcf) | PART A - KEY REPORT INFORMATION
EXPLODE_IND | VARCHAR2 | Commodity exploded (Yes, No) | PART A - KEY REPORT INFORMATION
NUM_PUB_EVACUATED | NUMBER | Number of general public evacuated | PART A - KEY REPORT INFORMATION
NUM_OPER_AND_CONTRACTOR_EVAC | NUMBER | Number of operator/contractor personnel evacuated | PART A - KEY REPORT INFORMATION
NUM_PERSONS_HOSP_NOT_OVNGHT | NUMBER | Estimated number of persons with injuries requiring treatment in a medical facility but not requiring overnight in-patient hospitalization | PART A - KEY REPORT INFORMATION
NUM_INJURED_TREATED_BY_EMT | NUMBER | Estimated number of persons with injuries requiring treatment by EMTs at the site of incident: | PART A - KEY REPORT INFORMATION
NUM_RESIDENT_BUILDING_AFFCTD | NUMBER | Number of residential buildings affected (evacuated or required repair or gas service interrupted) | PART A - KEY REPORT INFORMATION
NUM_BUSINESS_BUILDING_AFFCTD | NUMBER | Number of business buildings affected (evacuated or required repair or gas service interrupted) | PART A - KEY REPORT INFORMATION
FACILITY_NAME | VARCHAR2 | Name of LNG Plant / Facility | PART B - ADDITIONAL FACILITY INFORMATION
NPMS_LNG_ID | VARCHAR2 | National Pipeline Mapping System (NPMS) LNG ID | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_STATUS | VARCHAR2 | Plant / Facility Status | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_LATITUDE | VARCHAR2 | Plant / Facility Location - Latitude | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_LONGITUDE | VARCHAR2 | Plant / Facility Location - Longitude | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_STATE | VARCHAR2 | Plant / Facility Location - State | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_LIQUID_VAPOR_RATE | VARCHAR2 | Process - Liquefaction/Vaporization Rate (MMCF/D) at the time of the Incident | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_NUM_VAPORIZERS | VARCHAR2 | Process - Number of Vaporizers in service at the time of the Incident | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TOTAL_CAPACITY | VARCHAR2 | Process - Total Capacity (MMCF/D) | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_TRUCK_IND | VARCHAR2 | LNG Source - | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_RAILROAD_IND | VARCHAR2 | LNG Source - | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_MARINE_IND | VARCHAR2 | LNG Source - | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_SOURCE_LIQUEFY_IND | VARCHAR2 | LNG Source - | PART B - ADDITIONAL FACILITY INFORMATION
INTER_INTRA | VARCHAR2 | Interstate means the plant operates under a FERC certificate | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_NUMBER_TANKS | VARCHAR2 | LNG Storage - Number of LNG Tanks | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_VOLUME_STORAGE | VARCHAR2 | LNG Storage - Volume of LNG in Storage at the time of the Incident (Bbls) | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_BASE_LOAD_IND | NUMBER | Type of LNG Plant / Facility - Based Load | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_PEAK_SHAVE_IND | VARCHAR2 | Type of LNG Plant / Facility - Peak Shaving | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_SATELLITE_IND | VARCHAR2 | Type of LNG Plant / Facility - Satellite | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_MOBILE_TEMP_IND | VARCHAR2 | Type of LNG Plant / Facility - Mobile / Temporary | PART B - ADDITIONAL FACILITY INFORMATION
SUB_MOBILE_TEMP_INTRASTATE_IND | VARCHAR2 | Type of LNG Plant / Facility - Mobile / Temporary - InTRAstate | PART B - ADDITIONAL FACILITY INFORMATION
SUB_MOBILE_TEMP_INTERSTATE_IND | VARCHAR2 | Type of LNG Plant / Facility - Mobile / Temporary - InTERstate | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_OTHER_IND | VARCHAR2 | Type of LNG Plant / Facility - Other | PART B - ADDITIONAL FACILITY INFORMATION
FACILITY_TYPE_OTHER_DETAILS | VARCHAR2 | Type of LNG Plant / Facility - Other Details | PART B - ADDITIONAL FACILITY INFORMATION
FUNCTION_MARINE_TERMINAL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Marine Terminal | PART B - ADDITIONAL FACILITY INFORMATION
SUB_MARINE_IMPORT_TERMINAL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Marine Import Terminal | PART B - ADDITIONAL FACILITY INFORMATION
SUB_MARINE_EXPORT_TERMINAL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Marine Export Terminal | PART B - ADDITIONAL FACILITY INFORMATION
FUNCTION_STORAGE_IND | NUMBER | Function of LNG Plant / Facility at the time and date of the Incident - Storage | PART B - ADDITIONAL FACILITY INFORMATION
SUB_STORAGE_WITH_LIQUEFY_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Storage With Liquefaction | PART B - ADDITIONAL FACILITY INFORMATION
SUB_STORAGE_WO_LIQUEFY_IND | NUMBER | Function of LNG Plant / Facility at the time and date of the Incident - Storage Without Liquefaction | PART B - ADDITIONAL FACILITY INFORMATION
FUNCTION_STRANDED_UTILITY_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Stranded Utility | PART B - ADDITIONAL FACILITY INFORMATION
FUNCTION_VEHICULAR_FUEL_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Vehicular Fuel | PART B - ADDITIONAL FACILITY INFORMATION
FUNCTION_NITRO_SPECIAL_USE_IND | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Nitrogen Rejection Unit or Other Special Use | PART B - ADDITIONAL FACILITY INFORMATION
FUNCTION_SPECIAL_USE_DETAILS | VARCHAR2 | Function of LNG Plant / Facility at the time and date of the Incident - Nitrogen Rejection Unit or Other Special Use Details | PART B - ADDITIONAL FACILITY INFORMATION
ITEM_INVOLVED | VARCHAR2 | Item involved in Incident | PART B - ADDITIONAL FACILITY INFORMATION
ITEM_INVOLVED_DETAILS | VARCHAR2 | Item Involved in Incident Other - Details | PART B - ADDITIONAL FACILITY INFORMATION
EST_COST_OPER_PAID | NUMBER | Estimated Property Damage - Estimated cost of public and non-Operator private property damage | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OPER_PAID_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_PROP_DAMAGE | NUMBER | Estimated Property Damage - Estimated cost of Operator’s property damage & repairs | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_PROP_DAMAGE_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_EMERGENCY | NUMBER | Estimated Property Damage - Estimated cost of Operator’s emergency response | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_EMERGENCY_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_OTHER | NUMBER | Estimated Property Damage - Estimated other costs | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OTHER_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_OTHER_DETAILS | VARCHAR2 | Estimated Property Damage - Estimated other costs Specified | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_UNINTENTIONAL_RELEASE | NUMBER | Estimated Property Damage - Estimated cost of gas released unintentionally | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_UNINTENT_REL_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
EST_COST_INTENTIONAL_RELEASE | NUMBER | Estimated Property Damage - Estimated cost of commodity released during intentional and controlled blowdown | PART C - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_INTENT_REL_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
TOTAL_COST | NUMBER | Sum of EST_COST_OPER_PAID, EST_COST_PROP_DAMAGE, EST_COST_EMERGENCY, EST_COST_OTHER, EST_COST_GAS_RELEASED, and EST_COST_INTENTIONAL_RELEASE | PART C - ADDITIONAL CONSEQUENCE INFORMATION
TOTAL_COST_IN84 | NUMBER | Converted Property Damage to 1984 dollars | Not on the form
TOTAL_COST_CURRENT | NUMBER | Converted Property Damage to Current Year dollars | Not on the form
CCS_IN_PLACE_IND | NUMBER | Was a computerized Control System in place | PART D - ADDITIONAL OPERATING INFORMATION
CCS_OPERATING_IND | NUMBER | Computerized Control System in place - was it operating at the time of the Incident | PART D - ADDITIONAL OPERATING INFORMATION
CCS_FUNCTIONAL_IND | VARCHAR2 | Computerized Control System in place - Was it fully functional at the time of the Incident | PART D - ADDITIONAL OPERATING INFORMATION
ACCIDENT_IDENTIFIER | VARCHAR2 | The Operator’s initial indication of the Failure | PART D - ADDITIONAL OPERATING INFORMATION
ACCIDENT_DETAILS | VARCHAR2 | The Operator’s initial indication of the Failure - Specify Other | PART D - ADDITIONAL OPERATING INFORMATION
EMPLOYEE_DRUG_TEST_IND | VARCHAR2 | Operator employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART E - DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_TESTED | NUMBER | Number of employees tested | PART E - DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_FAILED | NUMBER | Number of employees failed | PART E - DRUG & ALCOHOL TESTING INFORMATION
CONTRACTOR_DRUG_TEST_IND | VARCHAR2 | Operator contractor employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART E - DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_TESTED | NUMBER | Number of contractors tested | PART E - DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_FAILED | NUMBER | Number of contractors failed | PART E - DRUG & ALCOHOL TESTING INFORMATION
CAUSE | VARCHAR2 | Apparent Cause of the Incident | PART F - APPARENT CAUSE
CAUSE_DETAILS | VARCHAR2 | Sub-Cause of Incident | PART F - APPARENT CAUSE
MAP_CAUSE | VARCHAR2 | Cause by PHMSA for 20 year Incident trending | Not on the form
MAP_SUBCAUSE | VARCHAR2 | SubCause by PHMSA for 20 year Incident trending | Not on the form
INTERNAL_EXTERNAL | VARCHAR2 | Corrosion Failure Sub-Cause (Internal, External) | PART F1 - Corrosion Failure
NATURAL_FORCE_TYPE | VARCHAR2 | Natural Force Damage Sub-Cause | PART F2 - Natural Force Damage
NF_OTHER_DETAILS | VARCHAR2 | Natural Force Damage - Other Natural Force Damage, or Sub-type Details | PART F2 - Natural Force Damage
NF_EXTREME_WEATHER_IND | VARCHAR2 | Natural Force Damage - Natural forces causing incident generated in conjunction with an extreme weather event (Yes, No, Null) | PART F2 - Natural Force Damage
NF_HURRICANE_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Hurricane (Yes, Null) | PART F2 - Natural Force Damage
NF_TROPICAL_STORM_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Tropical Storm (Yes, Null) | PART F2 - Natural Force Damage
NF_TORNADO_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Tornado (Yes, Null) | PART F2 - Natural Force Damage
NF_OTHER_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Other type (Yes, Null) | PART F2 - Natural Force Damage
NF_EXTREME_WEATHER_DETAILS | VARCHAR2 | Natural Force Damage - Extreme weather - Other type Details | PART F2 - Natural Force Damage
PARTY_TYPE | VARCHAR2 | Excavation Damage Sub-Cause | PART F3 - Excavation Damage
OUTSIDE_FORCE_TYPE | VARCHAR2 | Other Outside Force Damage Sub-Cause | PART F4 - Other Outside Force Damage
OSF_VEHICLE_SUBTYPE | NUMBER | Other Outside Force Damage - Sub-cause Damage by Car, Truck, or Other Motorized Vehicle/Equipment NOT Engaged in Excavation - Vehicle/Equipment operated by | PART F4 - Other Outside Force Damage
OSF_HURRICANE_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Hurricane (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_TROPICAL_STORM_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Tropical Storm (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_TORNADO_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Tornado (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_HEAVY_RAINS_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Heavy Rains/Flood (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_OTHER_WEATHER_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Other type (Yes, Null) | PART F4 - Other Outside Force Damage
OSF_OTHER_WEATHER_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Other type Details | PART F4 - Other Outside Force Damage
OSF_INTENTIONAL_SUBTYPE | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Specify | PART F4 - Other Outside Force Damage
OSF_INTENTIONAL_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Specify Other Details | PART F4 - Other Outside Force Damage
OSF_INTENT_SECURITY_BREACH_IND | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Specify - Did the Intentional Damage involve a breach of security | PART F4 - Other Outside Force Damage
OSF_OTHER_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Other Details | PART F4 - Other Outside Force Damage
PWJF_FIELD_EXAM_IND | NUMBER | Material Failure of Pipe or Weld - Based on Field Examination | PART F5 - Material Failure of Pipe or Weld
PWJF_METALLURGICAL_IND | VARCHAR2 | Material Failure of Pipe or Weld - Based on Determined by Metallurgical Analysis | PART F5 - Material Failure of Pipe or Weld
PWJF_OTHER_ANALYSIS_IND | VARCHAR2 | Material Failure of Pipe or Weld - Based on Other Analysis | PART F5 - Material Failure of Pipe or Weld
PWJF_OTHER_ANALYSIS_DETAILS | VARCHAR2 | Material Failure of Pipe or Weld - Based on Other Analysis Details | PART F5 - Material Failure of Pipe or Weld
PWJF_STILL_UNDER_INVEST_IND | VARCHAR2 | Material Failure of Pipe or Weld - Sub-cause is Tentative or Suspected; Still Under Investigation | PART F5 - Material Failure of Pipe or Weld
PWJF_FAILURE_TYPE | VARCHAR2 | Material Failure of Pipe or Weld Sub-cause | PART F5 - Material Failure of Pipe or Weld
PWJF_INSULATION_DEGRAD_IND | VARCHAR2 | Material Failure of Pipe or Weld - Sub-cause Low temperature embrittlement - Was insulation degradation a factor in this failure | PART F5 - Material Failure of Pipe or Weld
EQ_FAILURE_TYPE | VARCHAR2 | Equipment Failure Sub-Cause | PART F6 - Equipment Failure
EQ_FAILURE_DETAILS | VARCHAR2 | Equipment Failure - Other Equipment Failure Details | PART F6 - Equipment Failure
EQ_LOW_TEMP_EMBRITTLEMENT_IND | VARCHAR2 | Equipment Failure - Did this failure involve Low Temperature Embrittlement due to process fluids | PART F6 - Equipment Failure
EQ_INSULATION_DEGRADATION_IND | VARCHAR2 | Equipment Failure - Was insulation degradation a factor in this failure | PART F6 - Equipment Failure
OPERATION_TYPE | VARCHAR2 | Incorrect Operation Sub-Cause | PART F7 - Incorrect Operation
OPERATION_DETAILS | VARCHAR2 | Incorrect Operation - Other Incorrect Operation Details | PART F7 - Incorrect Operation
RELATED_INADEQUATE_PROC_IND | VARCHAR2 | Incorrect Operation Incident related to - Inadequate procedure (Yes, Null) | PART F7 - Incorrect Operation
RELATED_NO_PROC_IND | VARCHAR2 | Incorrect Operation Incident related to - No procedure established (Yes, Null) | PART F7 - Incorrect Operation
RELATED_FAILURE_FOLLOW_IND | VARCHAR2 | Incorrect Operation Incident related to - Failure to follow procedure (Yes, Null) | PART F7 - Incorrect Operation
RELATED_OTHER_IND | VARCHAR2 | Incorrect Operation Incident related to - Other (Yes, Null) | PART F7 - Incorrect Operation
OPERATION_RELATED_DETAILS | VARCHAR2 | Incorrect Operation Incident related to - Other Details | PART F7 - Incorrect Operation
OTHER_TYPE | VARCHAR2 | Other Incident Cause Sub-Cause | PART F8 - Other Incident Cause
MISC_DETAILS | VARCHAR2 | Other Incident Cause - Miscellaneous Details | PART F8 - Other Incident Cause
UNKNOWN_SUBTYPE | VARCHAR2 | Other Incident Cause - Unknown Sub-type | PART F8 - Other Incident Cause
EXTRNL_COR_GALVANIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Galvanic" | PART I - CONTRIBUTING FACTORS
EXTRNL_COR_ATMOSPHERIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Atmospheric" | PART I - CONTRIBUTING FACTORS
EXTRNL_COR_STRAY_CURRENT_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Stray Current Induced" | PART I - CONTRIBUTING FACTORS
EXTRNL_COR_MICROBIOLOGIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Microbiologically Induced" | PART I - CONTRIBUTING FACTORS
EXTRNL_COR_SELECTIVE_SEAM_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Selective Seam" | PART I - CONTRIBUTING FACTORS
INTRNL_COR_CORROSIVE_CMDTY_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Corrosive Commodity" | PART I - CONTRIBUTING FACTORS
INTRNL_COR_WTR_DRPOUT_ACID_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Water drop-out/Acid" | PART I - CONTRIBUTING FACTORS
INTRNL_COR_MICROBIOLOGIC_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Microbiological" | PART I - CONTRIBUTING FACTORS
INTRNL_COR_EROSION_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Erosion" | PART I - CONTRIBUTING FACTORS
NF_EARTH_MOVEMENT_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Earth Movement, NOT due to Heavy Rains/Floods" | PART I - CONTRIBUTING FACTORS
NF_HEAVY_RAINS_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Heavy Rains/Floods" | PART I - CONTRIBUTING FACTORS
NF_LIGHTNING_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Lightning" | PART I - CONTRIBUTING FACTORS
NF_TEMPERATURE_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Temperature" | PART I - CONTRIBUTING FACTORS
NF_HIGH_WINDS_IND | VARCHAR2 | Contributing Factors - Natural Forces, "High Winds" | PART I - CONTRIBUTING FACTORS
NF_SNOW_ICE_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Snow/Ice" | PART I - CONTRIBUTING FACTORS
NF_VEGITATION_ROOT_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Tree/Vegetation Root" | PART I - CONTRIBUTING FACTORS
EXCVTN_DMG_OPERATOR_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Operator (First Party)" | PART I - CONTRIBUTING FACTORS
EXCVTN_DMG_OP_CONTRACTOR_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Operator’s Contractor (Second Party)" | PART I - CONTRIBUTING FACTORS
EXCVTN_DMG_THIRD_PARTY_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Third Party" | PART I - CONTRIBUTING FACTORS
EXCVTN_DMG_PREVIOUS_DAMAGE_IND | VARCHAR2 | Contributing Factors - "Previous Damage due to Excavation Activit"y | PART I - CONTRIBUTING FACTORS
OSF_NEARBY_INDUSTRIAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Nearby Industrial, Man-made, or Other Fire/Explosion" | PART I - CONTRIBUTING FACTORS
OSF_VEHICLE_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Damage by Car, Truck, or Other Motorized Vehicle/Equipment NOT Engaged in Excavation" | PART I - CONTRIBUTING FACTORS
OSF_BOAT_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Damage by Boats, Barges, Drilling Rigs, or Other Adrift Maritime Equipment" | PART I - CONTRIBUTING FACTORS
OSF_OTHER_MARITIME_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Routine or Normal Fishing or Other Maritime Activity NOT Engaged in Excavation" | PART I - CONTRIBUTING FACTORS
OSF_ELECTRICAL_ARCING_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Electrical Arcing from Other Equipment or Facility" | PART I - CONTRIBUTING FACTORS
OSF_PREVIOUS_MECHANICAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Previous Mechanical Damage NOT Related to Excavation" | PART I - CONTRIBUTING FACTORS
OSF_INTENTIONAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Intentional Damage" | PART I - CONTRIBUTING FACTORS
OSF_OTHER_UNDERGROUND_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Other underground facilities buried within 12 inches of the failure location" | PART I - CONTRIBUTING FACTORS
PWF_DESIGN_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Design-related" | PART I - CONTRIBUTING FACTORS
PWF_CONSTRUCTION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Construction-related" | PART I - CONTRIBUTING FACTORS
PWF_INSTALLATION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Installation-related" | PART I - CONTRIBUTING FACTORS
PWF_FABRICATION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Fabrication-related" | PART I - CONTRIBUTING FACTORS
PWF_MANUFACTURING_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Original Manufacturing-related" | PART I - CONTRIBUTING FACTORS
EQF_CONTROL_RELEAF_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Malfunction of Control/Relief Equipment" | PART I - CONTRIBUTING FACTORS
EQF_THREADED_COUPLING_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Threaded Connection/Coupling Failure" | PART I - CONTRIBUTING FACTORS
EQF_NON_THREADED_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Non-threaded Connection Failure" | PART I - CONTRIBUTING FACTORS
EQF_VALVE_FAILURE_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Valve Failure" | PART I - CONTRIBUTING FACTORS
IO_DAMAGE_BY_OPERATOR_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Damage by Operator or Operator’s Contractor NOT Excavation and NOT Vehicle/Equipment Damage" | PART I - CONTRIBUTING FACTORS
IO_VALVE_POSITION_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Valve Left or Placed in Wrong Position, but NOT Resulting in Overpressure" | PART I - CONTRIBUTING FACTORS
IO_EQUIPMENT_OVERPRESSURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Pipeline or Equipment Overpressured" | PART I - CONTRIBUTING FACTORS
IO_NOT_INSTALLED_PROPERLY_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Equipment Not Installed Properly" | PART I - CONTRIBUTING FACTORS
IO_WRONG_EQUIPMENT_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Wrong Equipment Specified or Installed" | PART I - CONTRIBUTING FACTORS
IO_INADEQUATE_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Inadequate Procedure" | PART I - CONTRIBUTING FACTORS
IO_NO_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "No procedure established" | PART I - CONTRIBUTING FACTORS
IO_FOLLOW_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Failure to follow procedures" | PART I - CONTRIBUTING FACTORS
PREPARER_NAME | VARCHAR2 | Preparer's Name (Person filing the report) | PART H - PREPARER AND AUTHORIZED PERSON
PREPARER_TITLE | VARCHAR2 | Preparer's Title | PART H - PREPARER AND AUTHORIZED PERSON
PREPARER_EMAIL | VARCHAR2 | Preparer's Email address | PART H - PREPARER AND AUTHORIZED PERSON
PREPARER_TELEPHONE | VARCHAR2 | Preparer’s Telephone number | PART H - PREPARER AND AUTHORIZED PERSON
PREPARER_FAX | VARCHAR2 | Preparer's Facsimile number | PART H - PREPARER AND AUTHORIZED PERSON
PREPARED_DATE | VARCHAR2 | Date of filing | PART H - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_NAME | VARCHAR2 | Authorized Signature’s name | PART H - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_TITLE | VARCHAR2 | Authorized Title | PART H - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_TELEPHONE | VARCHAR2 | Authorized Telephone number | PART H - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_EMAIL | VARCHAR2 | Authorized Email address | PART H - PREPARER AND AUTHORIZED PERSON
NARRATIVE | VARCHAR2 | Narrative description of the incident | PART G - NARRATIVE DESCRIPTION OF THE INCIDENT

## lng2011toPresent
DATAFILE_AS_OF | SIGNIFICANT | SERIOUS | REPORT_NUMBER | SUPPLEMENTAL_NUMBER | REPORT_RECEIVED_DATE | REPORT_TYPE | OPERATOR_ID | NAME | OPERATOR_STREET_ADDRESS | OPERATOR_CITY_NAME | OPERATOR_STATE_ABBREVIATION | OPERATOR_POSTAL_CODE | LOCAL_DATETIME | TIME_ZONE | DAYLIGHT_SAVINGS_IND | IYEAR | NRC_RPT_NUM | NRC_RPT_DATETIME | ADDITIONAL_NRC_REPORT_NUMBERS | UNINTENTIONAL_RELEASE_IND | INTENTIONAL_RELEASE_IND | EMERGENCY_SHUTDOWN_IND | RESULTED_FROM_OTHER_IND | RESULTED_FROM_OTHER_DETAILS | COMMODITY_RELEASED_TYPE | COMMODITY_DETAILS | UNINTENTIONAL_RELEASE | INTENTIONAL_RELEASE | VOLUME_TO_GROUND | FATALITY_IND | NUM_EMP_FATALITIES | NUM_CONTR_FATALITIES | NUM_ER_FATALITIES | NUM_GP_FATALITIES | FATAL | INJURY_IND | NUM_EMP_INJURIES | NUM_CONTR_INJURIES | NUM_ER_INJURIES | NUM_GP_INJURIES | INJURE | SHUTDOWN_DUE_ACCIDENT_IND | SHUTDOWN_EXPLAIN | SHUTDOWN_DATETIME | RESTART_DATETIME | STILL_SHUTDOWN_IND | IGNITE_IND | GAS_CONSUMED_BY_FIRE_IN_MCF | EXPLODE_IND | NUM_PUB_EVACUATED | NUM_OPER_AND_CONTRACTOR_EVAC | NUM_PERSONS_HOSP_NOT_OVNGHT | NUM_INJURED_TREATED_BY_EMT | NUM_RESIDENT_BUILDING_AFFCTD | NUM_BUSINESS_BUILDING_AFFCTD | FACILITY_NAME | NPMS_LNG_ID | FACILITY_STATUS | FACILITY_LATITUDE | FACILITY_LONGITUDE | FACILITY_STATE | FACILITY_LIQUID_VAPOR_RATE | FACILITY_NUM_VAPORIZERS | FACILITY_TOTAL_CAPACITY | FACILITY_SOURCE_TRUCK_IND | FACILITY_SOURCE_RAILROAD_IND | FACILITY_SOURCE_MARINE_IND | FACILITY_SOURCE_LIQUEFY_IND | INTER_INTRA | FACILITY_NUMBER_TANKS | FACILITY_VOLUME_STORAGE | FACILITY_TYPE_BASE_LOAD_IND | FACILITY_TYPE_PEAK_SHAVE_IND | FACILITY_TYPE_SATELLITE_IND | FACILITY_TYPE_MOBILE_TEMP_IND | SUB_MOBILE_TEMP_INTRASTATE_IND | SUB_MOBILE_TEMP_INTERSTATE_IND | FACILITY_TYPE_OTHER_IND | FACILITY_TYPE_OTHER_DETAILS | FUNCTION_MARINE_TERMINAL_IND | SUB_MARINE_IMPORT_TERMINAL_IND | SUB_MARINE_EXPORT_TERMINAL_IND | FUNCTION_STORAGE_IND | SUB_STORAGE_WITH_LIQUEFY_IND | SUB_STORAGE_WO_LIQUEFY_IND | FUNCTION_STRANDED_UTILITY_IND | FUNCTION_VEHICULAR_FUEL_IND | FUNCTION_NITRO_SPECIAL_USE_IND | FUNCTION_SPECIAL_USE_DETAILS | ITEM_INVOLVED | ITEM_INVOLVED_DETAILS | EST_COST_OPER_PAID | EST_COST_OPER_PAID_CURRENT | EST_COST_PROP_DAMAGE | EST_COST_PROP_DAMAGE_CURRENT | EST_COST_EMERGENCY | EST_COST_EMERGENCY_CURRENT | EST_COST_OTHER | EST_COST_OTHER_CURRENT | EST_COST_OTHER_DETAILS | EST_COST_UNINTENTIONAL_RELEASE | EST_COST_UNINTENT_REL_CURRENT | EST_COST_INTENTIONAL_RELEASE | EST_COST_INTENT_REL_CURRENT | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | CCS_IN_PLACE_IND | CCS_OPERATING_IND | CCS_FUNCTIONAL_IND | ACCIDENT_IDENTIFIER | ACCIDENT_DETAILS | EMPLOYEE_DRUG_TEST_IND | NUM_EMPLOYEES_TESTED | NUM_EMPLOYEES_FAILED | CONTRACTOR_DRUG_TEST_IND | NUM_CONTRACTORS_TESTED | NUM_CONTRACTORS_FAILED | CAUSE | CAUSE_DETAILS | MAP_CAUSE | MAP_SUBCAUSE | INTERNAL_EXTERNAL | NATURAL_FORCE_TYPE | NF_OTHER_DETAILS | NF_EXTREME_WEATHER_IND | NF_HURRICANE_IND | NF_TROPICAL_STORM_IND | NF_TORNADO_IND | NF_OTHER_IND | NF_EXTREME_WEATHER_DETAILS | PARTY_TYPE | OUTSIDE_FORCE_TYPE | OSF_VEHICLE_SUBTYPE | OSF_HURRICANE_IND | OSF_TROPICAL_STORM_IND | OSF_TORNADO_IND | OSF_HEAVY_RAINS_IND | OSF_OTHER_WEATHER_IND | OSF_OTHER_WEATHER_DETAILS | OSF_INTENTIONAL_SUBTYPE | OSF_INTENTIONAL_DETAILS | OSF_INTENT_SECURITY_BREACH_IND | OSF_OTHER_DETAILS | PWJF_FIELD_EXAM_IND | PWJF_METALLURGICAL_IND | PWJF_OTHER_ANALYSIS_IND | PWJF_OTHER_ANALYSIS_DETAILS | PWJF_STILL_UNDER_INVEST_IND | PWJF_FAILURE_TYPE | PWJF_INSULATION_DEGRAD_IND | EQ_FAILURE_TYPE | EQ_FAILURE_DETAILS | EQ_LOW_TEMP_EMBRITTLEMENT_IND | EQ_INSULATION_DEGRADATION_IND | OPERATION_TYPE | OPERATION_DETAILS | RELATED_INADEQUATE_PROC_IND | RELATED_NO_PROC_IND | RELATED_FAILURE_FOLLOW_IND | RELATED_OTHER_IND | OPERATION_RELATED_DETAILS | OTHER_TYPE | MISC_DETAILS | UNKNOWN_SUBTYPE | EXTRNL_COR_GALVANIC_IND | EXTRNL_COR_ATMOSPHERIC_IND | EXTRNL_COR_STRAY_CURRENT_IND | EXTRNL_COR_MICROBIOLOGIC_IND | EXTRNL_COR_SELECTIVE_SEAM_IND | INTRNL_COR_CORROSIVE_CMDTY_IND | INTRNL_COR_WTR_DRPOUT_ACID_IND | INTRNL_COR_MICROBIOLOGIC_IND | INTRNL_COR_EROSION_IND | NF_EARTH_MOVEMENT_IND | NF_HEAVY_RAINS_IND | NF_LIGHTNING_IND | NF_TEMPERATURE_IND | NF_HIGH_WINDS_IND | NF_SNOW_ICE_IND | NF_VEGITATION_ROOT_IND | EXCVTN_DMG_OPERATOR_IND | EXCVTN_DMG_OP_CONTRACTOR_IND | EXCVTN_DMG_THIRD_PARTY_IND | EXCVTN_DMG_PREVIOUS_DAMAGE_IND | OSF_NEARBY_INDUSTRIAL_IND | OSF_VEHICLE_IND | OSF_BOAT_IND | OSF_OTHER_MARITIME_IND | OSF_ELECTRICAL_ARCING_IND | OSF_PREVIOUS_MECHANICAL_IND | OSF_INTENTIONAL_IND | OSF_OTHER_UNDERGROUND_IND | PWF_DESIGN_IND | PWF_CONSTRUCTION_IND | PWF_INSTALLATION_IND | PWF_FABRICATION_IND | PWF_MANUFACTURING_IND | EQF_CONTROL_RELEAF_IND | EQF_THREADED_COUPLING_IND | EQF_NON_THREADED_IND | EQF_VALVE_FAILURE_IND | IO_DAMAGE_BY_OPERATOR_IND | IO_VALVE_POSITION_IND | IO_EQUIPMENT_OVERPRESSURE_IND | IO_NOT_INSTALLED_PROPERLY_IND | IO_WRONG_EQUIPMENT_IND | IO_INADEQUATE_PROCEDURE_IND | IO_NO_PROCEDURE_IND | IO_FOLLOW_PROCEDURE_IND | PREPARER_NAME | PREPARER_TITLE | PREPARER_EMAIL | PREPARER_TELEPHONE | PREPARER_FAX | PREPARED_DATE | AUTHORIZER_NAME | AUTHORIZER_TITLE | AUTHORIZER_TELEPHONE | AUTHORIZER_EMAIL | NARRATIVE
2022-05-31 09:24 | NO | NO | 20120001 | 15002 | 2012-11-28 12:27 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2012-11-04 14:38 |  |  | 2012 | 1029623 | 2012-11-04 16:00 |  | NO | NO | YES | NO |  | OTHER COMMODITY | CO2 | 230 |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2012-11-04 14:38 | 2012-11-07 11:00 |  | NO |  | NO | 0 | 0 |  |  |  |  | NEWPORT LNG PLANT | NEWPORT | IN SERVICE | 44.62425232 | -124.0266953 | OR | 6 | 0 | 6 |  |  |  | YES | INTRASTATE | 1 | 165000 |  | YES | [9 empty] | YES | YES | [5 empty] | OTHER | PLANT CONTROL SYSTEM | 0 | 0 | 10000 | 11712 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 10000 | 5271 | 11712 | YES | YES | NO | OTHER | COMPUTERIZED CONTROL SYSTEM AND LOCAL OPERATING PERSONNEL. | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [29 empty] | OTHER EQUIPMENT FAILURE | PLANT CONTROL SYSTEM | NO | NO | [55 empty] | ANDREA SCOTT | COMPLIANCE SPECIALIST | a3s@nwnatural.com | 503-226-4211 |  | 2012-12-18 | KERRY SHAMPINE | MANAGER CODE COMPLIANCE | 503-226-4211 | kfs@nwnatural.com | ON SUNDAY NOVEMBER 4, 2012 AT APPROXIMATELY 2:30PM PST AN EVENT OCCURRED AT NW NATURAL'S NEWPORT LNG STORAGE PLANT LOCATED AT 1702 YAQUINA BAY RD IN NEWPORT, OREGON. THE PLANT WAS OPERATING IN LIQUEFACTION MODE AND EXPERIENCED AN UNPLANNED SHUTDOWN OF ITS LIQUEFACTION PROCESS. ON-SITE PERSONNEL RESPONDED APPROPRIATELY AND RETURNED THE PLANT TO HOLD MODE AND VERIFIED SAFE CONDITIONS. THERE WAS A SMALL CYCLING RELEASE OF CO2 FROM A VESSEL THROUGH ITS RELIEF VALVE FOR A PERIOD OF ABOUT 20 MINUTES. FURTHER RESEARCH OVER THE NEXT 24 HOURS CONFIRMED THE PRIMARY CAUSE OF THE EVENT AS THE FAILURE OF AN ALLEN-BRADLEY PLC-5/40E PROCESSOR BOARD. THIS PLC WAS PROGRAMMED AS THE CONTROL PLC FOR THE PLANT LIQUEFACTION PROCESS. A REPLACEMENT PLC WAS PROCURED AND DELIVERED TO THE PLANT ON WEDNESDAY NOVEMBER 7, 2012. THE LIQUEFACTION PLC PROGRAM WAS RELOADED INTO THE NEW PROCESSOR AND ITS FUNCTIONALITY WAS VERIFIED THAT SAME DAY. THE PLANT WAS DECLARED BACK IN SERVICE BY NOON WEDNESDAY NOVEMBER 7, 2012.
2022-05-31 09:24 | NO | NO | 20140001 | 15015 | 2014-01-29 16:28 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2013-12-31 07:00 |  |  | 2013 | 1069801 | 2013-12-31 09:37 |  | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 1 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2013-12-31 07:05 |  | YES | YES |  | NO | 0 | 0 |  |  |  |  | Portable tanker and vaporizer |  | IN SERVICE |  |  | MN | 1025 | 1 | 6000 | YES |  |  |  | INTERSTATE | 2 | 234 |  |  |  | YES |  | YES | [8 empty] | YES |  |  |  | RELIEF VALVE |  | 0 | 0 | 1000 | 1150.03927729772 | 0 | 0 | 0 | 0 |  | 500 | 351.4344 | 0 | 0 | 1500 | 922.289705484656 | 1501.47370352723 | NO |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [29 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | NO | NO | [55 empty] | JOHN GORMLEY | SR. CORROSION SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  | 2016-04-25 | THOMAS CORRELL | DIRECTOR OF PIPELINE SAFETY | 402-398-7715 | thomas.correll@nngco.com | ON TUESDAY, DECEMBER 31, 2013 AT APPROXIMATELY 0700 CST A FLASH FIRE OCCURRED DURING LIQUIFIED NATURAL GAS DELIVERY OPERATIONS AT THE BENSON, MINNESOTA TOWN BORDER STATION. INFORMATION INDICATES THE CAUSE OF THE FLASH FIRE WAS A CATASTROPHIC FAILURE OF A FUEL RUN REGULATOR LOCATED ON THE VAPORIZER TRAILER. THE REGULATOR FAILURE CAUSED MULTIPLE RELIEF VALVES TO EXHAUST GAS TO THE ATMOSPHERE WHICH WAS IGNITED BY THE WATER/GLYCOL HEATER BURNERS LOCATED ON THE VAPORIZER TRAILER. TWO EMPLOYEES WERE EXAMINED AT A NEARBY HOSPITAL AND RELEASED BACK TO FULL DUTY. THEY BOTH HAD SUNBURN LIKE INJURIES. NORTHERN HAD PLACED THIS TEMPORARY / PORTABLE LNG TANKER AND VAPORIZER TAILER AT THE BENSON, MINNESOTA TOWN BORDER STATION AS A CONTINGENCY WHILE WORK WAS BEING CONDUCTED UPSTREAM AT THE ALEXANDRIA, MINNESOTA COMPRESSOR STATION. THE TANKER AND VAPORIZER HAD BEEN CONNECTED TO THE BENSON TOWN BORDER STATION SINCE 12/27/2013 BUT WASN'T IN-SERVICE UNTIL THE MORNING OF 12/31/2013. THE WATER BATH HEATERS ON THE VAPORIZER TRAILER WERE LIT BUT LNG WAS NOT BEING DELIVERED. ON 12/31/2013, THE PIPELINE GAS PRESSURE WAS LOW ENOUGH TO TEST THE LNG DELIVERY. THE DELIVERY WAS JUST BEGINNING TO COME ON WHEN THE REGULATOR FAILED AND THE FLASH FIRE OCCURRED. THE TOWN OF BENSON, MINNESOTA WAS NEVER IN DANGER OF LOSING NATURAL GAS SERVICE.
2022-05-31 09:24 | YES | YES | 20140002 | 15014 | 2014-05-06 15:12 | SUPPLEMENTAL FINAL | 39054 | WILLIAMS PARTNERS OPERATING LLC | ONE WILLIAMS CENTER | TULSA | OK | 74172 | 2014-03-31 08:19 |  |  | 2014 | 1078325 | 2014-03-31 09:23 |  | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 14000 | 154200 | 0 | NO |  |  |  |  | 0 | YES | 1 | 0 | 0 | 0 | 1 | YES |  | 2014-03-31 08:19 | 2016-03-15 08:15 |  | YES |  | YES | 150 | 18 |  |  |  |  | Plymouth LNG Peak Shaving Plant |  | IN SERVICE |  |  | WA | 0 | 0 | 300 |  |  |  | YES | INTERSTATE | 2 | 344309 |  | YES | [9 empty] | YES | YES | [5 empty] | IN-PLANT PIPING |  | 71300 | 80441.730083807 | 40790000 | 46019890.18399 | 190000 | 214360.851555727 | 4698000 | 5300354.10846739 | PURIFICATION SYSTEM UPGRADE, CERTAIN MI INSPECTIONS AND ENVIRO MONITORING. | 80960 | 48632.7145 | 672800 | 404151.313485114 | 46503060 | 23750842.9775636 | 52067830.9021179 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | YES | 16 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [33 empty] | OTHER INCORRECT OPERATION | INADEQUATE PURGE FOLLOWING MAINTENANCE ACTIVITIES. | YES | [52 empty] | JARED ELLSWORTH | MANAGER PIPELINE SAFETY | jared.ellsworth@williams.com | 8015846539 |  | 2016-03-25 | JARED ELLSWORTH | MANAGER PIPELINE SAFETY | 8015846539 | jared.ellsworth@williams.com | AT APPROXIMATELY 08:19 PDT THE PLYMOUTH LNG FACILITY EXPERIENCED AN INTERNAL DETONATION RESULTING IN RAPID OVERPRESSURE AND SUBSEQUENT FAILURE OF PORTIONS OF THE LNG1 PURIFICATION AND REGENERATION SYSTEM, INCLUDING IN PLANT PIPING AND AN ADSORBER VESSEL, CAUSING DAMAGE TO ADJACENT BUILDINGS AND EQUIPMENT. DEBRIS FROM THE RUPTURE PENETRATED THE OUTER WALL OF ONE OF TWO LNG STORAGE TANKS. NATURAL GAS VENTED FROM THE VAPOR SPACE BETWEEN THE INNER AND OUTER WALLS OF THE STORAGE TANK BUT DID NOT IGNITE. STATION PERSONNEL IMMEDIATELY EXECUTED AN ESD OF THE FACILITY. OF 5 EMPLOYEES TAKEN TO THE HOSPITAL FOR EVALUATION, 4 EMPLOYEES WERE TREATED AND RELEASED AND 1 EMPLOYEE WAS ADMITTED FOR BURN INJURIES AND RELEASED SEVERAL DAYS LATER. A THIRD PARTY INVESTIGATION FIRM WAS CONTRACTED TO DOCUMENT THE INCIDENT LOCATION AND MANAGE ALL EVIDENCE. VARIOUS CONSULTANTS WERE ENGAGED IN THE COMPLETION OF AN INCIDENT INVESTIGATION. THE INVESTIGATION DETERMINED THE LEADING CAUSE WAS THE PRESENCE OF A FUEL/AIR MIXTURE REMAINING IN THE SYSTEM FOLLOWING MAINTENANCE ACTIVITIES. THE FUEL/AIR MIX THEN AUTO-IGNITED WITHIN THE SYSTEM PIPING UPON STARTUP WHEN THE FLAMMABLE MIXTURE ENTERED THE INLET OF A SALT BATH HEATER.
2022-05-31 09:24 | NO | NO | 20140003 | 15005 | 2014-08-19 08:14 | ORIGINAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS CO | 5400 WESTHEIMER COURT | HOUSTON | TX | 77056 | 2014-07-27 19:00 |  |  | 2014 | 1090405 | 2014-07-27 21:57 |  | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 1 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2014-07-27 19:00 | 2014-07-27 20:20 |  | NO |  | NO | 0 | 0 |  |  |  |  | Kingsport LNG Plant | Kingsport LNG | IN SERVICE | 36.44537113 | -82.52234253 | TN | 0 | 0 | 348000 |  |  |  | YES | INTERSTATE | 1 | 252000 |  | YES | [9 empty] | YES | YES | [5 empty] | RELIEF VALVE |  | 0 | 0 | 84500 | 95334.168191889 | 0 | 0 | 0 | 0 |  | 4 | 2.4028 | 0 | 0 | 84504 | 42908.0266842074 | 95336.5709939906 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS |  | HIGH WINDS |  | YES |  |  | YES | [81 empty] | DWAYNE TESCHENDORF | SENIOR TECHNICAL ADVISOR | deteschendorf@spectraenergy.com | 713-627-5573 | 713-386-4468 | 2014-08-19 | RICK KIVELA | DIRECTOR OPERATION COMPLIANCE | 713-627-6388 | rwkivela@spectraenergy.com | AFTER A TORNADO DISRUPTED ELECTRIC POWER TRANSMISSION TO THE EAST TENNESSEE LNG FACILITY IN KINGSPORT, TENNESSEE, THE GENERATOR AT THE FACILITY DID NOT IMMEDIATELY ACTIVATE. THE COMPRESSOR STOPPED WHICH CAUSED PRESSURE TO RISE IN THE LNG TANK AND NATURAL GAS VENTED THROUGH THE ASSOCIATED RELIEF VALVE UNTIL THE GENERATOR SWITCHED ON AND COMPRESSOR RETURNED TO SERVICE.
2022-05-31 09:24 | YES | NO | 20150001 | 15017 | 2015-02-13 18:32 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD (POB 7608, 83707) | BOISE | ID | 83709 | 2014-12-18 12:30 |  |  | 2014 | DO NOT KNOW NRC REPORT NUMBER |  |  | YES | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 185 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2014-12-18 01:30 |  | YES | NO |  | NO | 0 | 0 |  |  |  |  | NAMPA LNG FACILITY | NAMPA LNG | IN SERVICE |  |  | ID | 5 | 0 | 5 |  |  |  | YES | INTRASTATE | 1 | 94000 |  | YES | [9 empty] | YES | YES |  |  | YES |  |  | WELD |  | 0 | 0 | 100000 | 112821.500818804 | 300 | 338.464502456411 | 2000 | 2256.43001637607 | CRANE TO REMOVE ECONOMIZER AND COMPANY LABOR | 555 | 333.3888 | 0 | 0 | 102855 | 52327.2223258813 | 115749.78412923 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [22 empty] | YES |  |  |  |  | CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | [60 empty] | CRAIG CHAPIN | DIRECTOR - ENGINEERING SERVICES | craig.chapin@intgas.com | 208-377-6142 |  | 2016-09-21 | CRAIG CHAPIN | DIRECTOR - ENGINEERING SERVICES | 208-377-6142 | craig.chapin@intgas.com | A WELD ON ONE OF THE TUBES WITHIN THE ECONOMIZER FAILED (PULLED APART) LEAKING ~ 600 PSIG METHANE GAS INTO THE ENCLOSED AREA OF THE ECONOMIZER. BOXED AREA OF ECONOMIZER FILLED WITH GAS AND RUPTURED RESULTING IN DAMAGE TO THE TOP AND SIDE OF THE BOX. THE LEAKING GAS RESULTED IN A LOW PRESSURE ALARM ON THE CO2 PURIFICATION TOWER. OPERATORS ARRIVED ON SITE AND ACTIVATED THE LIQUEFACTION EMERGENCY SHUTDOWN. IT SHOULD BE NOTED A SRC REPORT WAS FILED ON 12-23-14 IN LIEU OF AN INCIDENT REPORT GIVEN THE INFORMATION AND SITUATION AT THAT TIME. THIS INCIDENT REPORT IS BEING SUBMITTED AT THIS TIME IN ADDITION TO THE SCR REPORT BASED ON THE RECOMMENDATION OF OUR IDAHO PUC REGULATOR. MONTHLY REPORTS ARE BEING SUBMITTED TO JERRY KENERSON AT JERRY.KENERSON@DOT.GOV PROVIDING UPDATED INFORMATION AS A NEW ECONOMIZER IS BEING BUILT AND INSTALLED.
2022-05-31 09:24 | NO | NO | 20150002 | 15008 | 2015-02-20 15:44 | SUPPLEMENTAL FINAL | 32206 | FREEPORT LNG DEVELOPMENT, L.P. | 333 CLAY STREET SUITE 5050 | HOUSTON | TX | 77002 | 2015-02-19 09:17 |  |  | 2015 | 1108577 | 2015-02-20 08:22 |  | YES | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 1711 |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2015-02-19 09:19 | 2015-02-19 11:51 |  | NO |  | NO | 0 | 50 |  |  |  |  | FREEPORT LNG DEVELOPMENT L.P. | 1 | IN SERVICE |  |  | TX | 0 | 0 | 1800 |  |  | YES |  | INTERSTATE | 2 | 160000 | YES | [7 empty] | YES | YES | YES | [7 empty] | FLANGE/GASKET |  | 0 | 0 | 25 | 27.8671361949177 | 0 | 0 | 0 | 0 |  | 4771 | 3841.439 | 0 | 0 | 4796 | 4436.35619289801 | 3869.30610333107 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [29 empty] | OTHER EQUIPMENT FAILURE | FLANGE GASKET ON A 4" PROCESS PIPELINE FAILED UNDER PRESSURE DURING MAINTENANCE / TESTING OF A VALVE UPSTREAM. | NO | NO | [55 empty] | MICHAEL STEPHENSON | REGULATORY COMPLIANCE SPECIALIST | mstephenson@freeportlng.com | 979-415-8728 | 979-415-8733 | 2015-02-20 | MICHAEL JOHNS | DIRECTOR REGUALTORY AFFAIRS | 979-415-8720 | mjohns@freeportlng.com | WHILE CONDUCTING VALVE TESTING / MAINTENANCE ON A PRESSURIZED NATURAL GAS LINE ~ 1100 PSI OF PRESSURE WAS RELEASED FROM A FAILED FLANGE GASKET THAT WAS POSITIONED BEHIND A BLIND FLANGE ON A PLANT NATURAL GAS HANDLING SYSTEM. THERE WERE NO PERSONNEL IN THE IMMEDIATE VICINITY OF THE RELEASE AND THE SYSTEM WAS SHUT DOWN IMMEDIATELY BY OPERATIONS BY UTILIZING AND ESD (EMERGENCY SHUT DOWN) BUTTON PULL STATION. NO INJURIES OCCURRED. THE IN-PLANT ALARM SYSTEM FUNCTIONED BY SOUNDING GAS RELEASE AND EVACUATION ALARMS AND ALL PERSONNEL LEFT THE AREA AND MUSTERED IN DESIGNATED LOCATIONS UNTIL THE SITUATION STABILIZED AND THE ALL-CLEAR HORN WAS SOUNDED. THE FLANGE WAS INSPECTED AND FOUND TO BE IN GOOD ORDER, THE GASKET WAS REPLACED AND THE SYSTEM WAS PUT BACK INTO SERVICE ON THE SAME DAY. REPORTS WERE FILED OR NOTIFICATIONS WERE MADE WITH FERC, NRC, PHMSA, BRAZORIA COUNTY COMMUNITY AWARENESS AND ENVIRONMENTAL RESPONSE AND THE CITY OF QUINTANA.
2022-05-31 09:24 | NO | NO | 20150004 | 15012 | 2015-12-30 12:39 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2015-12-13 08:45 |  |  | 2015 | 1135692 | 2015-12-13 11:08 |  | NO | NO | YES | NO |  | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2015-12-13 08:54 | 2015-12-13 10:12 |  | NO |  | NO | 0 | 0 |  |  |  |  | GASCO LNG PLANT | GASCO | IN SERVICE |  |  | OR | 120 | 3 | 120 |  |  |  | YES | INTRASTATE | 1 | 106750 |  | YES | [9 empty] | YES | YES | [5 empty] | EMERGENCY SHUT-OFF VALVE (ESV) |  | 0 | 0 | 22829 | 25447.154087751 | 5000 | 5573.42723898354 | 0 | 0 |  | 0 | 0 | 0 | 0 | 27829 | 13960.8507661559 | 31020.5813267346 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [10 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [76 empty] | SAMANTHA BURT | CODE COMPLIANCE SPECIALIST | s7b@nwnatural.com | 5032264211 |  | 2016-01-05 | JOE S. KARNEY | SENIOR MANAGER CODE COMPLIANCE | 5032264211 | jsk@nwnatural.com | AT APPROXIMATELY 8:49AM ON DECEMBER 13TH, 2015 NW NATURAL WAS NOTIFIED OF A SIGNIFICANT FIRE CLOSE TO THE PORTLAND LNG PLANT LOCATED AT 7900 NW SAINT HELENS RD., IN PORTLAND. A SEMI-TRUCK WITH A TANKER FULL OF FUEL TRAVELED OFF HIGHWAY 30 COLLIDING WITH A RAIL CAR CAUSING THE FIRE IMMEDIATELY ADJACENT TO THE PROPERTY. THE VEHICLE FIRE DISRUPTED THE PRIMARY POWER TO THE FACILITY WHICH RESULTED IN THE ACTIVATION OF THE ESD AT APPROXIMATELY 8:54AM. NWN FIRST RESPONDER ARRIVED ON SITE AT 10:12AM AND ACTIVATED BACK UP POWER. MINOR DAMAGE WAS EXPERIENCED AT THE CONTROL ROOM BUILDING DUE TO THE FIRE. NONE OF THE CRITICAL INFRASTRUCTURE OR OPERATIONAL SYSTEMS OF THE LNG PLANT WAS DAMAGED. PORTLAND GENERAL ELECTRIC REPAIRED THE PRIMARY POWER DECEMBER 15, 2015 AT 1:00PM. NW NATURAL IS REPORTING THE INCIDENT DUE TO LNG EMERGENCY SHUT DOWN.
2022-05-31 09:24 | NO | NO | 20160001 | 15016 | 2016-06-24 08:57 | ORIGINAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2016-04-20 11:59 |  |  | 2016 | 1145755 | 2016-04-20 12:45 |  | NO | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 325.2 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2016-04-20 11:59 | 2016-04-27 09:15 |  | NO |  | NO | 0 | 0 |  |  |  |  | LNG PLANT | 14 | IN SERVICE |  |  | IL | 10 | 0 | 10 |  |  |  | YES | INTRASTATE | 2 | 313358 |  | YES | [9 empty] | YES | YES | [5 empty] | IN-PLANT PIPING |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 823 | 760.8868 | 0 | 0 | 823 | 876.239892183288 | 760.88679245283 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN A TANK, VESSEL, OR SUMP/SEPARATOR OVERFLOW OR FACILITY OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [33 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN A TANK, VESSEL, OR SUMP/SEPARATOR OVERFLOW OR FACILITY OVERPRESSURE |  |  | YES | [51 empty] | SHAWN BARTELS | COMPLIANCE SPECIALIST | srbartels@peoplesgasdelivery.com | 312-240-5421 |  | 2016-06-24 | TOM WEBB | COMPLIANCE MANAGER | 312-240-4650 | tjwebb@peoplesgasdelivery.com | VALVE CONFIGURATION ON A TRANSMISSION LINE OUTSIDE OF THE LNG PLANT WAS CHANGED TO INCREASE FLOW IN THE PIPELINE WHICH THE LNG OUTLET ALSO FED INTO. AN INCREASE IN PRESSURE THAT ACCOMPANIED THE INCREASE IN FLOW IN THE PIPELINE CAUSED THE OUTLET OF THE LNG PLANT TO BACK UP, LIFTING RELIEF VALVES WITHIN THE LNG PLANT. TIMELINE: 11:30 AM: STATION VALVE RECONFIGURATION BEGINS IN AN ATTEMPT TO MITIGATE THE FROST HEAVING 11:55 AM: MAHOMET LINE #2 PRESSURE BEGINS TO INCREASE DUE TO VALVES 354 AND 471 BEING LEFT OPEN DURING THE RECONFIGURATION 11:59 AM: LNG FACILITY RELIEF VALVES BEGIN TO OPEN 11:59 AM: LNG FACILITY EMERGENCY SHUT DOWN SYSTEM ACTIVATED 12:06 PM: LNG ESD ALARM CLEARED 12:25 PM: PLANT MANAGER NOTIFIED OF INCIDENT 12:45 PM: NATIONAL RESPONSE CENTER NOTIFIED AND NRC REPORT #1145755 GENERATED 12:57 PM: ILLINOIS COMMERCE COMMISSION NOTIFIED 1:43 PM: ESTIMATED GAS RELEASE CALCULATED TO BE 325,200 SCF 3:10 PM: SHIFT OPERATOR AND ASSISTANT SHIFT OPERATOR SENT FOR POST-INCIDENT DRUG AND ALCOHOL TESTING 3:20 PM: RANDY STEWART WITH ICC ARRIVED AT MANLOVE FIELD FOR INVESTIGATION PGL CONSIDERS THIS INCIDENT CLOSED, BUT WILL REPORT QUARTERLY ON IT UNTIL ALL THE ICC AND PHMSA QUESTIONS HAVE BEEN ANSWERED.
2022-05-31 09:24 | NO | NO | 20170001 | 15020 | 2017-04-04 14:14 | SUPPLEMENTAL FINAL | 32561 | ECOELECTRICA L.P. | RD 337, KM 3.7 BO TALLABOA PONIENTE FIRM DELIVERY | PENUELAS | PR | 00624 | 2017-03-07 15:35 |  |  | 2017 | 1172670 | 2017-03-07 17:42 |  | NO | NO | YES | NO |  | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2017-03-07 15:35 | 2017-03-07 15:37 |  | YES |  | NO | 0 | 0 |  |  |  |  | ECOELECTRICA LNG TERMINAL | 1 | IN SERVICE |  |  | PR | 119 | 2 | 186 |  |  | YES |  | INTERSTATE | 1 | 776728 | YES | [10 empty] | YES |  | YES |  |  |  |  | PUMP |  | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 86.7876991478326 | ABC FIRE EXTINGUISHER REFILL | 0 | 0 | 0 | 0 | 80 | 39.0589107076695 | 86.7876991478326 | YES | YES | YES | FLAME DETECTORS |  | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [33 empty] | OTHER INCORRECT OPERATION | INADEQUATE TOOLS USED DURING MAINTENANCE TASK. | YES | [52 empty] | OSCAR CEDENO | LNG TERMINAL MANAGER | oscar.cedeno@ecoelectrica.com | 787-487-6042 | 787-836-2250 | 2017-12-06 | CARLOS REYES | CO-PRESIDENT - GENERAL MANAGER | 787-836-2840 | creyes@ecoelectrica.com | ON TUESDAY, MARCH 7TH, 2017 AT 15:35:58HRS, LNG TERMINAL EMERGENCY SHUTDOWN #1 WAS TRIGGERED DUE TO THE ACTIVATION OF FLAME DETECTOR 1LNG-AE-2016C AT THE TOP OF THE LNG TANK. THE EVENT HAPPENED WHILE O&M PERSONNEL WAS WORKING IN THE REPLACEMENT OF LNG PUMP P-101C. WHILE THE PUMP WAS BEING REMOVED FROM THE TANK COLUMN AND TRAVELING TO ITS TRANSPORTATION FRAME, SUPPORTED BY THE LNG TANK TOP CRANE, O&M PERSONNEL NOTICED A SMALL FIRE IN THE BOTTOM SUCTION NOTCH OF THE PUMP. IMMEDIATELY, ECOELECTRICA MAINTENANCE TECHNICIANS PROCEEDED TO EXTINGUISH THE FIRE USING PORTABLE ABC FIRE EXTINGUISHERS LOCATED AT THE LNG TANK TOP PLATFORM. NO PERSONNEL WAS INJURED OR EQUIPMENT DAMAGED DURING THE INCIDENT. AT 15:37HRS (TWO MINUTES LATER), A LNG SENDOUT PUMP WAS RETURNED TO OPERATION AND AT 15:41HRS LNG VAPORIZATION PROCESS WAS REESTABLISHED AND TERMINAL RECOVERED FOR NORMAL OPERATION. THE ROOT CAUSE OF THE IGNITION WAS A STATIC ELECTRICITY DISCHARGE. AFTER A NITROGEN PURGE OF MORE THAN 12 HOURS, THE PUMP WAS READY TO BE REMOVED FROM ITS WELL. DUE TO STRONG GUST OF WINDS, PRIOR TO LIFTING THE PUMP, A POLYPROPYLENE ROPE WAS TIED TO ONE OF THE STANDS OF THE BOTTOM SUCTION NOTCH AS AN AID TO CONTROL PUMP MOVEMENTS WHILE BEING TRANSFERRED FROM THE WELL TO THE TRANSPORTATION FRAME. DURING THIS MANEUVER THE TECHNICIAN ATTENDING THE PUMP WAS USING SKIN GLOVES WHILE THE PROPYLENE ROPE WAS BEING CONTROLLED WITH HIS HANDS CREATING FRICTION BETWEEN THE TWO MATERIALS. THE GLOVES' MATERIAL (LEATHER) IN CONTACT WITH THE ROPE (POLYPROPYLENE) GAVE RISE TO ACCUMULATIONS OF ELECTRIC CHARGE THAT WAS RELEASED SUDDENLY IN ELECTROSTATIC DISCHARGES WITH SUFFICIENT ENERGY TO IGNITE THE FLAMMABLE GAS MIX PRESENT AT THE PUMP NOTCH. THE FIRST STEP ON THE IGNITION IS THE PRODUCTION OF A SPARK THAT INSTANTLY GENERATES IR LIGHT (CORONA EFFECT) THAT WAS CAPTURED BY THE FLAME DETECTOR WHICH TRIGGERED THE ESD #1.
2022-05-31 09:24 | YES | NO | 20170002 | 31840 | 2017-09-21 11:30 | SUPPLEMENTAL FINAL | 3411 | DISTRIGAS OF MASSACHUSETTS LLC | 18 ROVER ST | EVERETT | MA | 02149 | 2017-09-20 16:47 |  |  | 2017 | 1191070 | 2017-09-21 11:10 |  | NO | NO | NO | YES | ARC FLASH | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | TWO SEPARATE ELECTRICAL FEEDS |  |  |  | NO |  | YES | 0 | 0 |  |  |  |  | Everett Marine LNG Terminal |  | IN SERVICE |  |  | MA | 91 | 2 | 715 |  |  | YES |  | INTERSTATE | 2 | 97000 | YES | [7 empty] | YES | YES | [8 empty] | OTHER | ELECTRICAL SUBSTATION | 0 | 0 | 150000 | 162726.935902186 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 150000 | 73235.4575768803 | 162726.935902186 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [40 empty] | MISCELLANEOUS | OVERHEATING OF NATIONAL GRID OVERHEAD CONDUCTOR THAT DROPPED ONTO THE SWITCHGEAR, AND THEN TO GROUND. | [46 empty] | MARK SKORDINSKI | MANAGER OF PORT OPERATIONS SAFETY AND SECURITY | mark.skordinski@exeloncorp.com | 617-381-8554 | 617-381-5654 | 2019-03-25 | MARK SKORDINSKI | MANAGER OF PORT OPERATIONS SAFETY AND SECURITY | 617-381-8554 | mark.skordinski@exeloncorp.com | FAILURE OF THE 23 KV UTILITY CONNECTION AT THE BUSBAR WITHIN SUBSTATION SS-1. A SECTION OF NATIONAL GRID OVERHEAD CONDUCTOR DEVELOPED A HOTSPOT, OVERHEATED, DROPPED ONTO THE SWITCHGEAR, AND THEN TO GROUND. THIS EVENT HAD THE POTENTIAL TO CREATE A VOLTAGE DIFFERENTIAL BETWEEN THE SWITCHGEAR ENCLOSURE AND THE LIVE SWITCHGEAR BUS LARGE ENOUGH TO INITIATE A FLASHOVER BETWEEN THE SWITCHGEAR BUS AND ENCLOSURE.
2022-05-31 09:24 | YES | NO | 20180001 | 33122 | 2018-02-21 19:35 | SUPPLEMENTAL FINAL | 32152 | SABINE PASS LNG, L.P. (CHENIERE) | 700 MILAM STREET SUITE 1900 | HOUSTON | TX | 77002 | 2018-01-22 21:20 |  |  | 2018 | 1202595 | 2018-01-22 22:33 |  | YES | NO | NO | NO |  | LNG (LIQUEFIED NATURAL GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 825 | 0 | 245 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | FACLITY UTILIZED THE UNAFFECTED LNG STORAGE TANKS |  |  |  | NO |  | NO | 0 | 0 |  |  |  |  | SABINE PASS LNG TERMINAL | 32152 | IN SERVICE |  |  | LA | 2527 | 0 | 2513 |  |  |  | YES | INTERSTATE | 5 | 333031 | YES | [7 empty] | YES | YES | YES | YES | YES | [5 empty] | STORAGE TANK/VESSEL |  | 0 | 0 | 34000000 | 36102266.5457842 | 9500 | 10087.3980054397 | 0 | 0 |  | 2775 | 2250.1773 | 0 | 0 | 34012275 | 16255000.6048945 | 36114604.1210946 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [33 empty] | OTHER INCORRECT OPERATION | SEE PART G FOR FULL DESCRIPTION. |  |  |  | YES | SEE PART G FOR FULL DESCRIPTION. | [48 empty] | MICHAEL MYERS | LEAD COMPLIANCE COORDINATOR | michael.myers2@cheniere.com | 337-569-7234 |  | 2019-12-20 | PAUL NIELSON | MANAGER REGULATORY COMPLIANCE | 7133755595 | paul.nielson@cheniere.com | ON MONDAY, JANUARY 22ND, 2018 A SMALL LNG RELEASE WAS OBSERVED AT THE BASE OF THE SOUTHEAST SIDE OF TANK S-103 BY OPERATING FIELD PERSONNEL. ALL LNG RELEASED FROM THE OUTER TANK SHELL WAS CONTAINED IN THE SECONDARY CONTAINMENT. THE LNG VAPORIZED AND DISPERSED. TANK S-103 WAS PROMPTLY REMOVED FROM OPERATIONAL LNG SERVICE. THIRD-PARTY EXPERTS PERFORMED A ROOT CAUSE FAILURE ANALYSIS (RCFA) OF THE EVENT. THE RCFA DETERMINED THAT TRANSIENT FLOW THOUGH THE BOTTOM FILL CONNECTION CAUSED LNG TO ENTER THE TANK ANNULAR SPACE (SPACE BETWEEN THE INNER TANK WALL AND OUTER TANK SHELL) ABOVE THE INNER TANK LIP DURING FILLING OF THE INNER TANK, WHICH RESULTED IN THE RELEASE OF LNG FROM TANK S-103 DURING THE INCIDENT. NONE OF THE TRANSIENT FLOWS EXCEEDED NORMAL OPERATING FLOW PARAMETERS OR TANK NAME PLATE SPECIFICATIONS. A DETAILED DISCUSSION OF CAUSES AND CONTRIBUTING FACTORS IS CONTAINED IN THE RCFA REPORT SUBMITTED TO PHMSA. TO ADDRESS THE DIRECT CAUSE OF THE INCIDENT, BOTTOM FILL RUNDOWN CAPABILITY TO ALL LNG STORAGE TANKS WAS PERMANENTLY AND PHYSICALLY DISABLED. SABINE PASS HAS ACTED TO ADDRESS BASIC/ROOT CAUSES ASSOCIATED WITH PREVENTION AND MITIGATION BARRIERS. TANK S-103 WAS REMOVED FROM SERVICE AND PERMANENT REPAIRS ARE UNDERWAY. ITEM A.5-NRC 48-HOUR REPORT # 1202757 ITEM B.1 NOMINAL
2022-05-31 09:24 | NO | NO | 20180002 | 30972 | 2018-09-24 15:50 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-09-04 23:00 |  |  | 2018 | 1223643 | 2018-09-05 06:10 |  | YES | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 0 | 10000 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2018-09-04 23:43 | 2018-09-05 08:00 |  | NO |  | NO | 0 | 0 |  |  |  |  | GARNER LNG PLANT | 1 | IN SERVICE |  |  | IA | 100 | 2 | 150 |  |  |  | YES | INTERSTATE | 1 | 100 |  | YES | [9 empty] | YES | YES | [5 empty] | VAPORIZER |  | 0 | 0 | 500 | 530.915684496827 | 0 | 0 | 0 | 0 |  | 0 | 0 | 42 | 34.0567375886525 | 542 | 278.159114729011 | 564.972422085479 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [29 empty] | OTHER EQUIPMENT FAILURE | VAPORIZER SHUT DOWN WHEN CONTROL SYSTEM SHUT DOWN UNEXPECTEDLY | NO | NO | [55 empty] | JOHN A GORMLEY | SR. CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 4023987494 | - | 2018-09-24 | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON SEPTEMBER 3, 2018, AT 2230 COMMUNICATIONS WAS LOST BETWEEN THE HMI AND NNG-GARN-CTRLS-SW-G, WHICH IS THE COMMUNICATION FOR THE VAPORIZERS AND LNG PUMPS. TWO VAPORIZERS WERE RUNNING AT THE TIME, 50 MMSCFD EACH, AND SHUT DOWN DUE TO THE LOSS OF COMMUNICATION. IT WAS FOUND THAT THE OUTLETS OF THE VAPORIZERS GOING INTO PIPELINE WERE GETTING EXTREMELY COLD. THE ESD VALVES DID NOT SHUT AUTOMATICALLY WHICH COULD HAVE ALLOWED LNG INTO THE PIPELINE. THE TEAM THEN SAW THAT THE LNG PUMPS DID NOT SHUT OFF AND WERE STILL RUNNING. THE MANUAL VALVES ON THE VAPORIZERS WERE SHUT IN TO ENSURE NO LNG WOULD GET INTO THE PIPELINE. AT 2250 THE A AND C LNG PUMP EMERGENCY-STOP BUTTONS WERE PUSHED. THE TEAM PROCEEDED TO BYPASS FIRE AND GAS AND START A BLOW DOWN OF THE VAPORIZERS, TO MINIMIZE THE RISK OF LNG GETTING INTO THE CARBON STEEL PIPING OF PIPELINE. THE FIRE AND GAS IS BYPASSED TO PREVENT AN UNEXPECTED ESD. WHILE THE VAPORIZERS WERE BLOWING DOWN A PILOT RELIEF VALVE BLEW INSIDE THE VAPORIZER BUILDING. THE PILOT RELIEF IS VERY NEAR A GAS DETECTOR HEAD. THE TEAM MEMBER IN THE CONTROL ROOM ANNOUNCED OVER RADIO THAT EVERYONE NEEDED TO GET IN THE CONTROL ROOM. THE ESD BUTTON WAS THEN MANUALLY PUSHED AT 2339. AFTER THE VAPORIZERS WERE BLOWN DOWN, THE PLC CABINET WAS OPENED AND THE ETHERNET SWITCH (NNG-GARN-CTRLS-SW-G) WAS FOUND TO BE COVERED IN WATER. MOST LIKELY FROM THE HUMIDITY IN THE VAPORIZER BUILDING. THE UNIT DID NOT APPEAR TO BE POWERED UP. AFTER SOMETIME OF ATTEMPTING TO GET CORPORATE ON THE PHONE THROUGH THE COMPANY'S CONFERENCE BRIDGE ANOTHER EMPLOYEE ARRIVED ON SITE TO INVESTIGATE THE SWITCH. THAT EMPLOYEE FOUND THAT THE SWITCH NOW HAD A COUPLE LIGHTS ILLUMINATED. HE PROCEEDED TO REMOVE POWER AND POWER BACK UP THE SWITCH. IT THEN BEGAN TO FUNCTION NORMALLY. INSPECTORS FROM THE IOWA UTILITIES BOARD VISITED THE PLANT ON SEPTEMBER 7, 2018 TO EXAMINE THE VAPORIZERS AND COMMUNICATIONS ENCLOSURE.
2022-05-31 09:24 | YES | NO | 20180003 | 32628 | 2018-12-22 11:27 | SUPPLEMENTAL FINAL | 32152 | SABINE PASS LNG, L.P. (CHENIERE) | 700 MILAM STREET SUITE 1900 | HOUSTON | TX | 77002 | 2018-11-23 07:55 |  |  | 2018 | 1232687 | 2018-12-11 18:18 |  | YES | NO | NO | NO |  | LNG (LIQUEFIED NATURAL GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 2.01 | 1500 | 0.6 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2018-11-23 08:00 | 2018-12-22 03:30 |  | NO |  | NO | 0 | 0 |  |  |  |  | SABINE PASS LNG TERMINAL | 32152 | IN SERVICE |  |  | LA | 749 | 0 | 750 |  |  |  | YES | INTERSTATE | 5 | 901707 | YES | [7 empty] | YES | YES | YES | YES | YES | [5 empty] | COLD BOX |  | 0 | 0 | 175000 | 185820.489573889 | 0 | 0 | 0 | 0 |  | 7 | 5.6761 | 4959 | 4021.12765957447 | 179966 | 88266.0211244211 | 189847.293356395 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [29 empty] | OTHER EQUIPMENT FAILURE | TRANSITION JOINT FAILURE | NO | NO | [55 empty] | MICHAEL J. MYERS | LEAD COMPLIANCE COORDINATOR | michael.myers2@cheniere.com | 8323122700 |  | 2019-08-29 | PAUL NIELSON | MANAGER REGULATORY COMPLIANCE | 7133755595 | paul.nielson@cheniere.com | DURING TRAIN 5 COMMISSIONING AT SABINE PASS LNG ON 23 NOVEMBER, 2018 AT 07:55AM, SITE PERSONNEL OBSERVED SMALL AMOUNTS OF LNG REACHING THE GROUND NEAR THE NORTHWEST CORNER OF THE METHANE COLD BOX. PERSONNEL IMMEDIATELY COMMUNICATED THIS OBSERVATION TO THE CONTROL BOARD OPERATOR AND AN ORDERLY SHUTDOWN OF TRAIN 5 WAS CONDUCTED VIA THE NORMAL SHUT DOWN PROCESS. INITIALLY, THIS EVENT WAS CONSIDERED TO BE A SAFETY-RELATED CONDITION (SRC) AND TIMELY REPORTED TO PHMSA ON NOVEMBER 30, 2018. AFTER REMOVAL OF PERLITE INSULATION FROM THE COLDBOX, IT WAS DETERMINED THAT A TRANSITION JOINT ON A HEAT EXCHANGER WAS THE SOURCE OF THE LEAK AND REPAIR COST WAS ESTIMATED TO LIKELY EXCEED $50,000, THEREFORE AN NRC TELEPHONIC INCIDENT REPORT WAS FILED (NRC REPORT # 1232687). THE HEAT EXCHANGER WHERE THE LEAK WAS IDENTIFIED WAS OPERATING AT NORMAL FLOWS, TEMPERATURES, AND PRESSURES AT THE TIME OF AND PRIOR TO THE DISCOVERY OF THE LEAK. AS A PRECAUTIONARY MEASURE, ALL 16 TRANSITION JOINTS ON THE ASSOCIATED HEAT EXCHANGER WERE REPLACED AND RETESTED DURING THE COLD BOX REPAIR PROCESS. A ROOT CAUSE FAILURE ANALYSIS (RCFA) WAS CONDUCTED BY THE COLD BOX EQUIPMENT MANUFACTURER, WITH PARTICIPATION FROM THE OPERATOR, THE TRANSITION JOINT MANUFACTURER, THE CONSTRUCTION CONTRACTOR, AND THE COLD BOX PROCESS LICENSER. THE RCFA REPORT HAS BEEN PROVIDED TO PHMSA SW REGION AND ADDRESSES FOUR TRANSITION JOINT FAILURES AT SABINE PASS.
2022-05-31 09:24 | NO | NO | 20190002 | 31782 | 2019-03-13 12:05 | ORIGINAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD (POB 7608, 83707) | BOISE | ID | 83709 | 2019-02-27 08:10 |  |  | 2019 | 1238769 | 2019-02-27 11:55 |  | NO | NO | YES | NO |  | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2019-02-27 08:10 | 2019-03-07 12:30 |  | NO |  | NO | 0 | 0 |  |  |  |  | NAMPA LNG FACILITY | NAMPA LNG | IN SERVICE |  |  | ID | 4 | 0 | 5 |  |  |  | YES | INTRASTATE | 1 | 60848 |  | YES | [9 empty] | YES | YES | [5 empty] | COMPRESSOR |  | 0 | 0 | 5000 | 5203.48320597121 | 0 | 0 | 5000 | 5203.48320597121 | OIL TESTING AND DISPOSAL BY 3RD PARTY. | 0 | 0 | 0 | 0 | 10000 | 4683.66802914519 | 10406.9664119424 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [29 empty] | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT |  | NO | NO | [55 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  | 2019-03-13 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@intgas.com | A LIQUEFACTION EMERGENCY SHUTDOWN (LES) WAS INITIATED THE MORNING OF FEBRUARY 27, 2019 AFTER THE LNG PLANT OPERATORS DISCOVERED A LEAK ON AN OIL HOSE GOING INTO THE DATUM CYCLE GAS COMPRESSOR.
2022-05-31 09:24 | NO | NO | 20190003 | 32515 | 2019-08-06 07:54 | ORIGINAL FINAL | 32214 | CAMERON LNG, LLC | 2925 BRIARPARK SUITE 1000 | HOUSTON | TX | 77042 | 2019-07-05 12:56 |  |  | 2019 | 1251069 | 2019-07-05 13:53 |  | NO | NO | YES | NO |  | LNG (LIQUEFIED NATURAL GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 0.86 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | ONLY LOADING OPERATIONS WERE AFFECTED |  |  |  | NO |  | NO | 0 | 0 |  |  |  |  | Cameron LNG |  | IN SERVICE |  |  | LA | 1 | 0 | 705 |  |  |  | YES | INTERSTATE | 3 | 1270000 | [6 empty] | YES | MARINE TERMINAL | YES |  | YES | YES | YES | [5 empty] | BREAK-AWAY COUPLING |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 6.3018 | 0 | 0 | 7 | 7.25721784776903 | 6.30183727034121 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [40 empty] | MISCELLANEOUS | FALSE SIGNAL FROM SWITCH | [46 empty] | CLAYTON MILLER | ENVIRONMENTAL MANAGER | cmiller@cameronlng.com | 3372461284 |  | 2019-08-05 | DAN CALLENS | CHIEF OPERATING OFFICER | 8327835575 | dcallens@cameronlng.com | ON JULY 5, 2019, AT 12:56 PM, LOADING NEAR 12,000M3/H, THE ESD 1.1A WAS ACTIVATED AT THE NORTH JETTY AND THE POWER EMERGENCY RELEASE COUPLER (PERC) ON THE LOADING ARMS WERE DISCONNECTED. ESD 1.1A WAS INITIATED BY THE PROXIMITY SWITCH FOR 2ND STAGE DRIFT/SLEW (XS-1041) ON LOADING ARM S-101B.
2022-05-31 09:24 | NO | NO | 20190004 | 32586 | 2019-08-13 21:42 | SUPPLEMENTAL FINAL | 32206 | FREEPORT LNG DEVELOPMENT, L.P. | 333 CLAY STREET SUITE 5050 | HOUSTON | TX | 77002 | 2019-08-13 02:00 |  |  | 2019 | 1254985 | 2019-08-13 06:51 |  | YES | NO | NO | NO |  | REFRIGERANT GAS |  | 62.3 | 1009 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2019-08-13 02:00 | 2019-08-15 19:00 |  | NO |  | NO | 0 | 0 |  |  |  |  | Freeport LNG Liquefaction Plant |  | IN SERVICE |  |  | TX | 0 | 0 | 724 |  |  |  | YES | INTERSTATE | 3 | 200000 | YES | [7 empty] | YES |  | YES | [7 empty] | FLANGE/GASKET |  | 0 | 0 | 10000 | 10406.9664119424 | 2500 | 2601.7416029856 | 50 | 52.0348320597121 | WATER USED FOR VAPOR DISPERSION. | 2000 | 1800.5249 | 31279 | 28159.3097112861 | 45829 | 40379.853770278 | 43020.577492657 | YES | YES | YES | GAS DETECTORS |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [29 empty] | NON-THREADED CONNECTION FAILURE |  | NO | NO | [55 empty] | MICHAEL STEPHENSON | REGULATORY COMPLIANCE SUPERINTENDENT | mstephenson@freeportlng.com | 979-415-8728 | 979-415-8733 | 2019-08-20 | MICHAEL STEPHENSON | REGULATORY COMPLIANCE SUPERINTENDENT | 979-415-8728 | mstephenson@freeportlng.com | DURING COMMISSIONING ACTIVITIES OF THE LIQUEFACTION PLANT TRAIN 1 FACILITIES, A FLANGE GASKET AT THE OUTLET OF THE LOW-PRESSURE MIXED-REFRIGERANT (LP MR) DRUM FAILED RESULTING IN A RELEASE OF MIXED REFRIGERANT TO THE ATMOSPHERE. THE DURATION OF THIS EVENT WAS APPROXIMATELY 41 MINUTES. UPON BECOMING AWARE OF THE RUPTURED FLANGE AND VENTING TO THE ATMOSPHERE, FREEPORT LNG OPERATORS TOOK IMMEDIATE STEPS TO ISOLATE THE RUPTURE DRUM, MINIMIZE AND EVENTUALLY STOP THE FLOW OF MIXED-REFRIGERANT TO THE DRUM, AND THUS, TO THE ATMOSPHERE. TO PROVIDE FOR THE SAFE DE-PRESSURIZATION AND EVACUATION OF MIXED REFRIGERANT, ALLOW FOR REPAIRS AND TO FURTHER MINIMIZE EMISSIONS, THE BALANCE OF MIXED REFRIGERANT IN THE BLOCKED OFF SECTION OF THE SYSTEM WAS VENTED TO THE LIQUEFACTION FLARE (LIQFLARE). CONTRIBUTING CAUSES FOR THE FAILURE INCLUDE AN ANTI SURGE VALVE UPSTREAM OF THE SUCTION DRUM CONTAINING METAL SHAVINGS IN THE VALVE POSITION INDICATOR MECHANISM FROM THE MANUFACTURING PROCESS CAUSING THE VALVE TO FAIL CLOSED DURING OPERATION. THIS CAUSED A RAPID TEMPERATURE FLUCTUATION IN THE SURGE DRUM FROM APPROX -40 DEGREES FAHRENHEIT TO 200 DEGREES FAHRENHEIT. THE GASKET SPACER ALSO CONTAINED WHAT APPEARED TO BE A VERTICAL SCRATCH POTENTIALLY CAUSED DURING INSTALLATION IN THE AREA OF THE FAILURE. ALL EQUIPMENT HAS BEEN REPAIRED AND TORQUED TO SPEC WITH A NEW GASKET INSTALLED. ALL VALVE ACTUATORS IN THIS APPLICATION AND ALL OTHERS IN THE FACILITY HAVE BEEN CHECKED FOR DEBRIS IN ORDER TO PREVENT POTENTIAL RECURRENCE.
2022-05-31 09:24 | NO | NO | 20190005 | 33040 | 2019-08-19 17:20 | SUPPLEMENTAL FINAL | 32206 | FREEPORT LNG DEVELOPMENT, L.P. | 333 CLAY STREET SUITE 5050 | HOUSTON | TX | 77002 | 2019-08-01 17:20 |  |  | 2019 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 315 | 905 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2019-08-01 17:20 | 2019-08-11 03:23 |  | NO |  | NO | 0 | 0 |  |  |  |  | Freeport LNG Liquefaction Plant |  | IN SERVICE |  |  | TX | 0 | 0 | 724 |  |  |  | YES | INTERSTATE | 3 | 200000 | YES | [7 empty] | YES |  | YES | [7 empty] | IN-PLANT PIPING |  | 0 | 0 | 39322 | 40922.27332504 | 4800 | 4995.34387773236 | 32100 | 33406.3621823352 | ENGINEERING - DESIGN ALTERATIONS / PROC. REVIEW - UPDATES / LAB TESTING / NDE | 870 | 783.2283 | 2500 | 2250.656167979 | 79592 | 39193.6864727478 | 82357.8638995432 | YES | YES | YES | GAS DETECTORS |  | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [33 empty] | OTHER INCORRECT OPERATION | USE OF A 2" PURGE LINE OUTSIDE OF ITS INTENDED PURPOSE. |  |  | YES | [50 empty] | MICHAEL STEPHENSON | REGULATORY COMPLIANCE SUPERINTENDENT | mstephenson@freeportlng.com | 9794158728 |  | 2019-12-09 | MICHAEL STEPHENSON | REGULATORY COMPLIANCE SUPERINTENDENT | 9794158728 | mstephenson@freeportlng.com | AT ~ 1720 HRS ON 8-1 AT THE FREEPORT LNG LQF FACILITY DURING THE STARTUP AND COOL DOWN OF LNG TRAIN 1 COOL DOWN OPERATIONS, FEED GAS WAS BEING VENTED TO 6" FLARE HEADER VIA A 2" PSV BYPASS LINE ON THE BACK END OF THE MCHE. AFTER APPROXIMATELY 1 HOUR OF VENTING,THE 6" FLARE HEADER PIPING FAILED AT THE JUNCTION TO THE 2" LINE AND VENTED NATURAL GAS TO THE ATMOSPHERE. THE LEAK WAS ISOLATED WITHIN 15 MINUTES BY CLOSING A VALVE NEAR THE MCHE UPSTREAM OF THE FAILURE. THE 6" FLARE HEADER WAS BLOCKED AND INERTED WITH NITROGEN. NO INJURIES OCCURRED AND THERE WAS NO FACILITY DAMAGE ASIDE FROM THE POINT OF FAILURE. CAUSE OF THE FAILURE HAS BEEN PRELIMINARY DETERMINED TO BE FIV AND AIV DUE TO NON ADHERENCE TO PROPER COOL-DOWN PROCEDURE AND THE USE OF THE 2" LINE OUTSIDE OF IT'S INTENDED PURPOSE. PROCEDURES HAVE BEEN MODIFIED, OPERATOR TRAINING HAS BEEN REVISITED, AND THE LINE CONNECTION HAS BEEN REPAIRED AND PHYSICALLY BLOCKED-IN ORDER TO PREVENT RE-OCCURRENCE.
2022-05-31 09:24 | YES | NO | 20190006 | 34836 | 2019-12-10 12:54 | SUPPLEMENTAL FINAL | 39053 | LNG INDY, LLC | 129 E. MARKET STREET SUITE 100 | INDIANAPOLIS | IN | 46204 | 2019-11-06 11:00 |  |  | 2019 | 1263307 | 2019-11-06 21:30 |  | NO | YES | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 2977 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2019-11-06 08:31 | 2019-11-07 19:54 |  | NO |  | NO | 0 | 0 |  |  |  |  | Kinetrex Energy LNG North |  | IN SERVICE |  |  | IN | 4470 | 0 | 0 |  |  |  | YES | INTRASTATE | 1 | 228520 | [6 empty] | YES | MERCHANT AND PEAK SHAVING |  |  |  | YES | YES | [5 empty] | STORAGE TANK/VESSEL |  | 0 | 0 | 300000 | 312208.992358273 | 15384 | 16010.0771281322 | 0 | 0 |  | 9467 | 8522.7848 | 0 | 0 | 324851 | 157530.264536797 | 336741.854263308 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT PUMP/COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [29 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT PUMP/COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL |  | YES | NO | [55 empty] | ANTHONY HOPWOOD | EXECUTIVE DIRECTOR OF OPERATIONS | ahopwood@kinetrexenergy.com | 3172520282 |  | 2021-02-10 | ANTHONY HOPWOOD | EXECUTIVE DIRECTOR OF OPERATIONS | 3172520282 | ahopwood@kinetrexenergy.com | ON NOVEMBER 6, 2019, KINETREX ENERGY'S LNG NORTH'S STORAGE TANK EXPERIENCED A CRACK IN THE CARBON STEEL EXTERIOR TANK SHELL. THE CRACK WAS IDENTIFIED DIRECTLY BELOW THE EXISTING LNG PUMP CATWALK/PLATFORM AND APPROXIMATELY 1 FOOT ABOVE THE DOME LIP/COMPRESSION EDGE. THE OPERATOR ON DUTY NOTIFIED MANAGEMENT OF A POTENTIAL LEAK ON TOP OF THE LNG STORAGE AS EVIDENCED BY A VAPOR CLOUD. PLANT MANAGEMENT INFORMED THE LNG PLANT MECHANIC OF THIS POTENTIAL ISSUE AND REQUESTED THAT HE INVESTIGATE IT IMMEDIATELY. THE LNG PLANT MECHANIC INVESTIGATED THE ISSUE AS REQUESTED AND INFORMED THE DIRECTOR OF OPERATIONS THAT IT APPEARED THERE WAS A CRACK IN THE EXTERIOR TANK SHELL. THE DIRECTOR OF OPERATIONS INSTRUCTED THE OPERATOR ON DUTY AND THE LNG PLANT MECHANIC TO SHUTDOWN THE LIQUEFACTION AND TRAILER LOADING ACTIVITIES UNTIL ADDITIONAL INVESTIGATIONS COULD TAKE PLACE. THE DIRECTOR OF OPERATIONS AND LNG PLANT ENGINEER VISITED THE SITE IMMEDIATELY FOLLOWING THE NOTIFICATION BY THE LNG PLANT MECHANIC TO CONFIRM THE FINDINGS. IT WAS CONFIRMED THAT A CRACK HAD OCCURRED IN THE CARBON STEEL OUTER TANK AT A LENGTH OF APPROXIMATELY 2.5 FEET. APPROXIMATELY 4 TO 5 YEARS AGO, WITH THE FACILITY UNDER PREVIOUS OWNERSHIP, A LEAK IN AN LNG LIQUID VALVE OCCURRED DIRECTLY ABOVE THE LOCATION OF FAILURE CAUSING DISCOLORATION IN THIS AREA. IN ADDITION, KINETREX ENERGY REPLACED THIS VALVE IN OCTOBER 2019 AS PART OF OUR ROUTINE MAINTENANCE PROGRAM TO ENSURE THE INTEGRITY OF OUR FACILITY. AFTER THE VALVE REPLACEMENT AND SUBSEQUENT COOLDOWN OF THE LINE, THE KINETREX ENERGY PLANT MECHANICS VERIFIED TIGHTNESS OF THE NEWLY INSTALLED VALVE AND NOTATED A SMALL LNG LEAK (A COUPLE OF DROPS/MINUTE) LANDING IN THE EXISTING LNG DRIP PAN PRIOR TO RECTIFYING THIS LEAK. THIS LEAK WAS STOPPED AT THIS TIME. WITH THE DISCOLORATION IT IS PRESUMED THE CARBON STEEL OUTER TANK'S INTEGRITY WAS PREVIOUSLY IMPACTED ULTIMATELY LEADING TO THE FAILURE IN 2019. KINETREX ENERGY BEGAN THE PROCESS OF CONTACTING VARIOUS ENGINEERING FIRMS WITH RELEVANT EXPERIENCE, AS WELL AS, MATRIX PDM, THE ORIGINAL TANK MANUFACTURER. MATRIX PDM RECOMMENDED THAT KINETREX ENERGY USE AN EPOXY (BELZONA PRODUCT) TO TEMPORARILY STOP THE LEAK. THE LEAK WAS STOPPED THE EVENING OF NOVEMBER 7, 2019 WITH BOIL-OFF GAS NORMAL OPERATION RESUMING. THE INDIANA UTILITY REGULATORY COMMISSION AND A PHMSA REPRESENTATIVE VISITED THE SITE ON NOVEMBER 14, 2019 TO DISCUSS THE INCIDENT. SINCE THIS LEAK WAS DISCOVERED, KINETREX ENERGY HAS CONTRACTED WITH MATRIX PDM TO CONDUCT A PHASE I ENGINEERING STUDY. THE ENGINEERING STUDY WILL INCLUDE RECOMMENDATION(S), COST(S), AND SCHEDULE TO TEST AND PERMANENTLY REPAIR THE CRACK. THIS REPORT IS EXPECTED TO BE PROVIDED BY MATRIX PDM WITHIN 4 WEEKS. MATRIX PDM HAS SINCE COMPLETED A PHASE I AND II ENGINEERING STUDY OUTLINING THE PROPOSED DESIGN TO PERMANENTLY REPAIR THE CRACK. MATERIAL HAS BEEN PROCURED FOR THIS REPAIR AND IS CURRENTLY ON STANDBY WHILE KINETREX ENERGY BOILS OFF THE REMAINING INVENTORY TO PURGE THE TANK OUT OF SERVICE WITH N2. THE TANK N2 AND AIR PURGE OUT OF SERVICE PROCESS COMPLETED ON OCTOBER 12, 2020 WITH CONSTRUCTION COMMENCING IMMEDIATELY AFTER ON OCTOBER 13, 2020 WITH A COMPLETION DATE OF OCTOBER 22, 2020. ALL QA/QC MEASURES WERE TAKEN TO ENSURE THE WELD OF THE TANK WAS SATISFACTORY INCLUDING A PRESSURE TEST OF THE AREA. THE N2 AND NATURAL GAS PURGE INTO SERVICE ACTIVITIES STARTED ON OCTOBER 23, 2020 AND WERE COMPLETE ON NOVEMBER 3, 2020. THE TANK COOLDOWN WAS COMPLETED ON NOVEMBER 15, 2020 CONCLUDING THE REPAIR PROJECT AND REINSTATING LNG SERVICE.
2022-05-31 09:24 | YES | NO | 20200001 | 34731 | 2020-06-10 09:49 | SUPPLEMENTAL FINAL | 18490 | SOUTHERN LNG, INC | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-05-11 13:37 |  |  | 2020 | 1277059 | 2020-05-11 15:03 |  | YES | NO | YES | NO |  | REFRIGERANT GAS |  | 10 | 74 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | ADJACENT UNITS WERE SHUTDOWN AS PRECAUTION |  |  |  | YES |  | NO | 0 | 0 |  |  |  |  | ELBA ISLAND LNG FACILITY | 5900LNG | IN SERVICE |  |  | GA | 28 | 0 | 210 |  |  |  | YES | INTERSTATE | 5 | 2379103 | YES | [7 empty] | YES | YES | YES | YES | YES | [5 empty] | COMPRESSOR |  | 0 | 0 | 1000000 | 1019942.52373073 | 0 | 0 | 0 | 0 |  | 600 | 600 | 4000 | 4000 | 1004600 | 464323.762926004 | 1024542.52373073 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [29 empty] | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT |  | NO | NO | [55 empty] | CARLA ROARK | COMPLIANCE MANAGER | carla_roark@kindermorgan.com | 912-944-3856 |  | 2021-01-15 | STEVE HEARD | LNG DIRECTOR | 912-944-3806 | steve_heard@kindermogan.com | ON MAY 11, 2020, AT 13:37, AT KINDER MORGAN'S SOUTHERN LNG ELBA ISLAND FACILITY (SLNG), A FIRE OCCURRED ON MIXED REFRIGERANT COMPRESSOR (MRC) UNIT B AT MOVEABLE MODULAR LIQUEFACTION SYSTEM (MMLS) UNIT 2 (US02-K-0501B). THE COMPRESSOR WAS OPERATING AT THE TIME OF THE FIRE. SLNG OPERATORS EXTINGUISHED THE FIRE WITHIN 10 MINUTES, USING ON-SITE FIREWATER MONITORS. SLNG CALLED 911; THE SAVANNAH FIRE DEPARTMENT ARRIVED ON-SCENE AFTER THE FIRE WAS EXTINGUISHED. UPON NOTIFICATION OF THE FIRE, THE CONTROL ROOM OPERATOR FOR MMLS US02 ACTIVATED THE EMERGENCY SHUTDOWN DEVICE (ESD) FOR MMLS US02 AT 13:38. AT 13:44, THE MIXED REFRIGERANT (MR) SYSTEM WAS DEPRESSURIZED AND ANY REMAINING MR WAS SENT TO THE GROUND FLARE. THE INCIDENT RESULTED IN NO EVACUATIONS, FROM EITHER THE FACILITY OR THE PUBLIC. THE PRODUCTS INVOLVED IN THE INCIDENT WERE MOBIL DTE 846 TURBINE OIL AND MR. THE MR IS A MIXTURE OF ISOPENTANE, NITROGEN, METHANE, PROPANE, AND ETHYLENE. THE REFRIGERANT MIXTURE EITHER WAS CONSUMED IN THE FIRE OR WAS SENT TO THE FLARE ONCE THE MR SYSTEM WAS DEPRESSURIZED. SLNG ESTIMATES THAT THE TOTAL AMOUNT OF MR RELEASE IS 6,750 POUNDS (APPROXIMATELY 84 MCF). IT IS ESTIMATED THAT 10 MCF OF MR WAS RELEASED AND BURNED IN THE FIRE AND AN ESTIMATED 74 MCF OF MR WAS SENT TO THE FLARE WHEN THE UNIT WAS DEPRESSURIZED. THE RELEASE OF MR CAUSED NO ACUTE CHRONIC EXPOSURES TO PERSONNEL OR TO THE ENVIRONMENT. SOME TURBINE OIL WAS RELEASED TO THE GROUND. THE MAXIMUM POSSIBLE AMOUNT OF TURBINE OIL RELEASED TO THE GROUND IS 150 GALLONS. NO WATERWAYS OR DRAINS WERE IMPACTED. THE FIREWATER AND OIL MIXTURE WAS CONTAINED WITHIN THE DESIGNED FACILITY IMPOUNDMENTS. MORAN ENVIRONMENTAL RESPONDED TO THE INCIDENT AND BEGAN CLEAN-UP ACTIVITIES OF THE OIL ON THE EVENING OF THE INCIDENT. SLNG HAS RETAINED EXPONENT ENGINEERING AND SCIENTIFIC CONSULTING TO ASSUME THE LEAD IN THE INCIDENT INVESTIGATION. EXPONENT WILL BE PROVIDING THE ROOT CAUSE ANALYSIS INVESTIGATION REPORT.
2022-05-31 09:24 | NO | NO | 20200002 | 34937 | 2020-09-27 00:35 | SUPPLEMENTAL FINAL | 32214 | CAMERON LNG, LLC | 2925 BRIARPARK SUITE 1000 | HOUSTON | TX | 77042 | 2020-08-27 08:05 |  |  | 2020 | 1285850 | 2020-08-28 12:12 |  | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 8243 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | NO; FACILITY WAS ALREADY OPERATING IN A SAFE SHUTDOWN MODE DUE TO HURRICANE. |  |  |  | NO |  | NO | 0 | 0 |  |  |  |  | Cameron LNG |  | IN SERVICE |  |  | LA | 0 | 0 | 3 |  |  |  | YES | INTERSTATE | 3 | 1840549 | YES | [7 empty] | YES |  | YES | [7 empty] | RELIEF VALVE |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20064 | 20064 | 0 | 0 | 20064 | 23105.7725947522 | 20064 | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE |  | OTHER NATURAL FORCE DAMAGE | THE FACILITY LOST POWER DURING A HURRICANE. BACK-UP GENERATORS FOR INSTRUMENT AIR COMPRESSORS EVENTUALLY RAN OUT OF FUEL BECAUSE PERSONNEL WERE UNABLE TO ACCESS THE SITE AS A DIRECT RESULT OF THE DAMAGE TO THE SURROUNDING AREA. LOSS OF INSTRUMENT AIR CAUSED CONTROL VALVES TO FAIL OPEN/CLOSED (PER DESIGN). THE VALVE ALLOWING BOIL-OFF GAS TO RUN TO THE MARINE FLARE FAILED CLOSED, ALLOWING STORAGE TANK PRESSURE TO INCREASE UNTIL THE PSV ON THE TANK LIFTED TO RELIEVE PRESSURE (PER DESIGN). | YES | YES | [83 empty] | MICHAEL WOLF | REGULATORY AND COMPLIANCE MANAGER | mwolf@cameronlng.com | 832-783-5513 |  | 2021-03-01 | DAN CALLENS | CHIEF OPERATING OFFICER | 832-783-5575 | dcallens@cameronlng.com | PRIOR TO HURRICANE LANDFALL, THE FACILITY WAS PLACED INTO A SAFE SHUTDOWN MODE AND EVACUATED. THE FLARE VALVE WAS LEFT IN AUTO WITH A SET-POINT OF 3.0 PSIG TO CONTINUE CONTROLLING TANK PRESSURES AS LONG AS POSSIBLE DURING THE STORM. DURING THE STORM, POWER WAS LOST TO THE FACILITY, CAUSING THE DIESEL STANDBY GENERATOR TO START. EVENTUALLY THE GENERATOR RAN OUT OF FUEL AND SHUT DOWN BECAUSE PERSONNEL WERE UNABLE TO ACCESS THE SITE AS A DIRECT RESULT OF DAMAGE TO THE SURROUNDING AREA CAUSED BY HURRICANE LAURA, WHICH CAUSED THE INSTRUMENT AIR COMPRESSORS TO SHUT DOWN, CAUSING LOSS OF INSTRUMENT AIR. THIS CAUSED THE CONTROL VALVES TO GO TO THEIR FAIL SAFE POSITION, WHICH IS FAIL CLOSE FOR THE FLARE VALVE. AT THAT POINT, TANK PRESSURES STARTED CLIMBING UNTIL THE PSV ON T-202 LIFTED PER DESIGN TO CONTROL THE TANK PRESSURES. BASED ON OUR INVESTIGATION, WE BELIEVE THE LIFT OCCURRED THE MORNING OF AUGUST 27. AN INITIAL INCIDENT NOTIFICATION WAS MADE TO THE NRC (#1285850) ON AUGUST 28 ONCE THE FACILITY WAS ASSESSED BY OUR DISASTER RECOVERY TEAM. THE MARINE FLARE WAS RESTORED IN THE EVENING ON AUGUST 29 AND THE PSV RE-SEATED ON ITS OWN. A 48-HR FOLLOW-UP NOTIFICATION WAS MADE TO THE NRC (#1285993) THE MORNING OF AUGUST 30.
2022-05-31 09:24 | YES | NO | 20200004 | 34779 | 2020-11-05 12:59 | SUPPLEMENTAL FINAL | 32206 | FREEPORT LNG DEVELOPMENT, L.P. | 333 CLAY STREET SUITE 5050 | HOUSTON | TX | 77002 | 2020-10-21 23:14 |  |  | 2020 | 1290377 | 2020-10-21 23:14 |  | NO | NO | NO | YES | SMALL FIRE INSIDE OF A COMPRESSOR ENCLOSURE DISCOVERED AFTER UNIT TRIP. | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | ONE UNIT OF THE LNG FACILITY IS DOWN - 2 OTHERS REMAIN IN OPERATION. |  |  |  | YES |  | NO | 0 | 0 |  |  |  |  | FREEPORT LNG DEVELOPMENT L.P. | 1 | IN SERVICE |  |  | TX | 713 | 0 | 2172 |  |  |  | YES | INTERSTATE | 3 | 1153340 | YES | [7 empty] | YES |  | YES | [7 empty] | OTHER | ELECTRICAL JUNCTION BOX | 0 | 0 | 80000 | 81595.4018984586 | 5000 | 5099.71261865366 | 365040 | 372319.818862666 | LABOR FOR CLEANUP AND REPAIR AND TESTING, FREIGHT, RCA CONTRACTOR SUPPORT, | 0 | 0 | 0 | 0 | 450040 | 206580.235130192 | 459014.933379779 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [29 empty] | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT |  | NO | NO | [55 empty] | MICHAEL STEPHENSON | REGULATORY COMPLIANCE MANAGER | mstephenson@freeportlng.com | 9794158728 | 979-415-8733 | 2021-01-28 | MICHAEL STEPHENSON | REGULATORY COMPLIANCE MANAGER | 9794158728 | mstephenson@freeportlng.com | ON OCTOBER 21 AT APPROXIMATELY 1030PM, FLNG EXPERIENCED A TRIP ON THE TRAIN 1 LP MR COMPRESSOR. UPON INVESTIGATION, THE OPS TEAM OPENED THE DOOR TO THE COMPRESSOR ENCLOSURE AND NOTICED SMOKE AND VISIBLE FLAME ON AN ELECTRICAL JUNCTION BOX. OPERATORS THEN MANUALLY ACTIVATED THE DELUGE SYSTEM INSIDE THE ENCLOSURE AND BEGAN TO ISOLATE BREAKERS TO THE VFD. OPS THEN CALLED THE LOCAL FIRE DEPARTMENT OUT TO ASSIST. THE FIRE DEPARTMENT WAS ABLE TO EXTINGUISH THE REMAINING FIRE USING HAND HELD FIRE EXTINGUISHERS AFTER THE POWER WAS ISOLATED. NOTE: A 48 HR NRC NUMBER WAS NOT PROVIDED UPON FLNG CALLING THE NRC WITHIN THE 48 HR TIMEFRAME. FLNG WAS INFORMED BY THE NRC THAT THERE WAS NO RELEASE AND THEREFORE NO NUMBER WAS TO BE PROVIDED.
2022-05-31 09:24 | YES | NO | 20200005 | 35309 | 2020-11-09 20:56 | SUPPLEMENTAL FINAL | 32152 | SABINE PASS LNG, L.P. (CHENIERE) | 700 MILAM STREET SUITE 1900 | HOUSTON | TX | 77002 | 2020-10-11 15:28 |  | NO | 2020 | 1289503 | 2020-10-11 16:03 |  | NO | NO | YES | NO |  | OTHER COMMODITY | TRIAZINE | 0.03 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2020-10-11 15:29 | 2020-10-23 19:30 |  | YES | 0.03 | NO | 0 | 0 | 0 | 0 | 0 | 0 | SABINE PASS LNG TERMINAL |  | IN SERVICE |  |  | LA | 2243 | 0 | 4100 |  |  |  | YES | INTERSTATE | 5 | 2525736 | YES | [7 empty] | YES | YES | YES | YES | YES | [5 empty] | OTHER | 11V-1904 THERMAL OXIDIZER KNOCKOUT DRUM | 0 | 0 | 1162461 | 1185643.40607855 | 0 | 0 | 0 | 0 |  | 7 | 7 | 0 | 0 | 1162468 | 533608.333888428 | 1185650.40607855 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [40 empty] | MISCELLANEOUS | SEE PART G NARRATIVE | [46 empty] | MICHAEL J. MYERS | LEAD COMPLIANCE COORDINATOR | michael.myers2@cheniere.com | 337-569-7234 |  | 2021-05-20 | PAUL NIELSON | MANAGER REGULATORY COMPLIANCE | 7133755595 | paul.nielson@cheniere.com | AT THE TIME OF THE INCIDENT, TRAIN 1 WAS IN STANDBY AWAITING COMPLETION OF FIN FAN REPAIRS. ON OCTOBER 11TH, AT APPROXIMATELY 1527 HRS, SMOKE WAS OBSERVED NEAR THE TRAIN 1 THERMAL OXIDIZER KO DRUM 11V-1904 BY A FIELD OPERATOR CONDUCTING OPERATOR ROUNDS. AT 1528 HRS, THE DCS OPERATOR INITIATED A MANUAL EMERGENCY SHUT DOWN (ESD) OF TRAIN 1. ON-SITE EMERGENCY RESPONSE PERSONNEL ARRIVED ON THE SCENE AT 1535 HRS WHERE A FLUCTUATING ORANGE FLAME WAS OBSERVED ON THE INLET FLANGE TO THE THERMAL OXIDIZER KNOCK OUT DRUM 11V-1904. AT 1539 HRS THE MUSTER ALARM WAS SOUNDED. THE FLAME WAS CONTAINED AND EXTINGUISHED UTILIZING WATER SPRAY FROM AREA FIRE MONITORS AT APPROXIMATELY 1550 HRS. AT THAT TIME, THERE WAS NO THREAT TO ADJACENT EQUIPMENT OR PIPING. NEARBY EQUIPMENT WAS KEPT COOL USING WATER SPRAY. THE SUBSEQUENT ALL CLEAR WAS PROVIDED AT 1557 HRS. AS AN ESD WAS INITIATED, AN IMMEDIATE NOTIFICATION TO THE NATIONAL RESPONSE CENTER (NRC) WAS MADE AT 1603 ON OCTOBER 11TH, 2020, NRC REPORT # 1289503. THROUGH COORDINATION WITH BOTH PHMSA AND FERC, SABINE PASS SUPPORTED MULTIPLE VISITS AND DATA REQUESTS AND RETURNED TRAIN 1 TO SERVICE ON OCTOBER 24, 2020 WITH THE THERMAL OXIDIZER ISOLATED UNDER A DOCUMENTED TEMPORARY MANAGEMENT OF CHANGE PROCESS. STATUS AS OF 4/28/2021: THE THERMAL OXIDIZER 11V-1904 REMAINS OUT OF SERVICE UNDER THAT TEMPORARY MOC PENDING A FITNESS FOR SERVICE REPORT AND AN OPERATIONAL WINDOW TO RETURN IT TO SERVICE DURING AN OUTAGE. INCIDENT INVESTIGATIONS WERE CONDUCTED BY AN INDEPENDENT 3RD PARTY AND CHENIERE. THESE INCIDENT INVESTIGATION REPORTS WERE PROVIDED TO PHMSA SW REGION ON APR 2, 2021. THE CAUSE WAS AN UNIDENTIFIED HAZARD, THE REVERSE FLOW OF HOT FLUE GAS FROM THE THERMAL OXIDIZER. HAZARD RECURRENCE WAS MITIGATED BY ADDING INTERLOCKS TO PREVENT BACK-FLOW FROM THE THERMAL OXIDIZER TO THE KNOCKOUT DRUM. A FITNESS-FOR-SERVICE EVALUATION WAS PERFORMED ON ALL AFFECTED COMPONENTS. WHERE APPROPRIATE, REPAIRS WERE MADE IN ACCORDANCE WITH INDUSTRY STANDARDS. IN ADDITION, CERTAIN PIPING AND VALVES WERE REBUILT OR REPLACED OUT OF AN ABUNDANCE OF CAUTION. NOTES ON IR PARTS: A5-OTHER NRC REPORT: 1289704 FOR 48HR UPDATE A14-TRAIN 1 OF THE FACILITY WAS SHUT DOWN ON MANUAL ESD. A14B-STARTUP DATE/TIME FOR TRAIN 1 C1B-VALUE ESTIMATED
2022-05-31 09:24 | NO | NO | 20210001 | 36230 | 2021-02-03 21:30 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2021-01-04 12:37 | CENTRAL | NO | 2021 | 1296801 | 2021-01-27 10:46 | 1296954 | YES | NO | NO | NO |  | LNG (LIQUEFIED NATURAL GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 26.25 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2021-01-04 12:37 | 2021-12-20 15:00 |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | WESCOTT | 2801 | IN SERVICE |  |  | MN | 0 | 0 | 0 |  |  |  | YES | INTRASTATE | 2 | 427950 |  | YES | [9 empty] | YES | YES | [5 empty] | RELIEF VALVE |  | 0 | 0 | 0 | 0 | 0 | 0 | 69175 | 69175 | ENGINEERING REVIEW, HAZOP STUDY | 68 | 68 | 0 | 0 | 69243 | 31210.6028391304 | 69243 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [29 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | NO | NO | [51 empty] | YES | YES |  |  | JEFF CREMIN | PRINCIPAL ENGINEER | jeffrey.j.cremin@xcelenergy.com | 612-817-2665 |  | 2022-01-11 | CHRISTOPHER AKINS | MANAGER PIPELINE COMPLIANCE AND STANDARDS | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON JANUARY 4, 2021, THERE WAS A RELEASE OF GAS DURING A VAPORIZATION TEST RUN AT THE WESCOTT LNG FACILITY. AFTER THE EVENT, THE COMPANY INVESTIGATION LED TO THE FOLLOWING TECHNICAL FINDINGS: *ONE OF THE TEMPERATURE CONTROL VALVES (TCV) ON THE WATER ETHELENE GLYCOL (WEG) SYSTEM DID NOT OPERATE AS COMMANDED BY THE PROGRAMABLE LOGIC CENTER (PLC). THE PLC WAS COMMANDING THE TCV CORRECTLY, IT WAS NOT PHYSICALLY MOVING TO THE COMMANDED POSITION. AS THE SYSTEM WAS RESTARTED TO RESOLVE THE ISSUES WITH THE APPLICABLE TCV, THE PLC LOGIC REVERTED TO INITIAL OPERATION AND LIMITED WEG FLOW FURTHER. *THE TCV CAUSED INSUFFICIENT WATER ETHYLENE GLYCOL (WEG) FLOW TO ONE OF THE LNG VAPORIZERS. THE OUTLET NATURAL GAS TEMPERATURE DROPPED AND THE VAPORIZER OUTLET VALVE CLOSED. *THE LNG PUMPS INSTALLED IN 2000 WERE ABLE TO EXCEED THE SET POINT OF THE PRESSURE SAFETY VALVES. *THE SPECIFIC LNG PUMP CONTINUED PUMPING AGAINST A CLOSED VALVE. THIS CAUSED THE PRESSURE IN THE PIPING TO INCREASE AND EVENTUALLY RESULTED IN PRESSURE SAFETY VALVES LIFTING ON THE NATURAL GAS LINE BETWEEN THE LNG PUMP AND THE CLOSED VAPORIZER OUTLET VALVE. *THIRD-PARTY TESTING HAS INDICATED THROUGH MECHANICAL ANALYSIS THAT THE TCV VALVE DID REQUIRE INCREASED TORQUE TO OPERATE. AS A RESULT OF THE INVESTIGATION, THE FOLLOWING ACTIONS WERE TAKEN TO MINIMIZE RECURRENCE: *VARIABLE FREQUENCY DRIVES WERE ADDED TO THE TWO (2) IN-SERVICE LNG PUMPS. *PRESSURE SAFETY VALVES WERE ADDED TO THE TWO (2) IN-SERVICE LNG PUMPS. *THE WESCOTT LNG PLANT OPERATING, MAINTENANCE, AND EMERGENCY MANUALS WERE REVISED. *THE TCVS ON FOR THE VAPORIZER INLET VALVES ON THE WEG SYSTEMS WERE REPLACED WITH EPDM SEATS. NSP EVALUATED THE OTHER WEG TCV VALVES AND FOUND THEY WERE INSTALLED WITH THE COMPATIBLE EPDM SEAT MATERIAL. *THE SCADA SYSTEM AND PLC CODE FOR THE FACILITY WERE REPLACED.
2022-05-31 09:24 | NO | NO | 20210002 | 36229 | 2021-02-23 14:17 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2020-12-31 07:30 |  | NO | 2020 | 1298162 | 2021-02-16 16:41 | 1298362 | YES | NO | NO | NO |  | LNG (LIQUEFIED NATURAL GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 27.31 |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | VAPRIZATION TEST RUN WAS STOPPED AND STARTED AGAIN ON JANUARY 4, 2021. |  |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | WESCOTT | 2801 | IN SERVICE |  |  | MN | 0 | 0 | 0 |  |  |  | YES | INTRASTATE | 2 | 427950 |  | YES | [9 empty] | YES | YES | [5 empty] | RELIEF VALVE |  | 0 | 0 | 0 | 0 | 0 | 0 | 69175 | 70554.5240790734 | ENGINEERING REVIEW, HAZOP STUDY | 68 | 68 | 0 | 0 | 69243 | 31831.4593470535 | 70622.5240790734 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [29 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | NO | NO | [51 empty] | YES | YES |  |  | JEFF CREMIN | PRINCIPAL ENGINEER | elisabeth.m.kallberg@xcelenergy.com | 612-817-2665 |  | 2022-01-11 | CHRISTOPHER AKINS | MANAGER PIPELINE COMPLIANCE AND STANDARDS | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON DECEMBER 31, 2020, THERE WAS A RELEASE OF GAS DURING A VAPORIZATION TEST RUN AT THE WESCOTT LNG FACILITY. AFTER THE EVENT, THE COMPANY INVESTIGATION LED TO THE FOLLOWING TECHNICAL FINDINGS: *ONE OF THE TEMPERATURE CONTROL VALVES (TCV) ON THE WATER ETHELENE GLYCOL (WEG) SYSTEM DID NOT OPERATE AS COMMANDED BY THE PROGRAMABLE LOGIC CENTER (PLC). THE PLC WAS COMMANDING THE TCV CORRECTLY, IT WAS NOT PHYSICALLY MOVING TO THE COMMANDED POSITION. AS THE SYSTEM WAS RESTARTED TO RESOLVE THE ISSUES WITH THE APPLICABLE TCV, THE PLC LOGIC REVERTED TO INITIAL OPERATION AND LIMITED WEG FLOW FURTHER. *THE TCV CAUSED INSUFFICIENT WATER ETHYLENE GLYCOL (WEG) FLOW TO ONE OF THE LNG VAPORIZERS. THE OUTLET NATURAL GAS TEMPERATURE DROPPED AND THE VAPORIZER OUTLET VALVE CLOSED. *THE LNG PUMPS INSTALLED IN 2000 WERE ABLE TO EXCEED THE SET POINT OF THE PRESSURE SAFETY VALVES. *THE SPECIFIC LNG PUMP CONTINUED PUMPING AGAINST A CLOSED VALVE. THIS CAUSED THE PRESSURE IN THE PIPING TO INCREASE AND EVENTUALLY RESULTED IN PRESSURE SAFETY VALVES LIFTING ON THE NATURAL GAS LINE BETWEEN THE LNG PUMP AND THE CLOSED VAPORIZER OUTLET VALVE. *THIRD-PARTY TESTING HAS INDICATED THROUGH MECHANICAL ANALYSIS THAT THE TCV VALVE DID REQUIRE INCREASED TORQUE TO OPERATE. AS A RESULT OF THE INVESTIGATION, THE FOLLOWING ACTIONS WERE TAKEN TO MINIMIZE RECURRENCE: *VARIABLE FREQUENCY DRIVES WERE ADDED TO THE TWO (2) IN-SERVICE LNG PUMPS. *PRESSURE SAFETY VALVES WERE ADDED TO THE TWO (2) IN-SERVICE LNG PUMPS. *THE WESCOTT LNG PLANT OPERATING, MAINTENANCE, AND EMERGENCY MANUALS WERE REVISED. *THE TCVS ON FOR THE VAPORIZER INLET VALVES ON THE WEG SYSTEMS WERE REPLACED WITH EPDM SEATS. NSP EVALUATED THE OTHER WEG TCV VALVES AND FOUND THEY WERE INSTALLED WITH THE COMPATIBLE EPDM SEAT MATERIAL. *THE SCADA SYSTEM AND PLC CODE FOR THE FACILITY WERE REPLACED.
2022-05-31 09:24 | YES | NO | 20210003 | 35429 | 2021-03-04 18:25 | SUPPLEMENTAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD (POB 7608, 83707) | BOISE | ID | 83709 | 2021-02-17 11:10 |  | NO | 2021 | 1298246 | 2021-02-17 11:43 |  | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 201.6 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | THE RELEASE IS A NON-HAZARDOUS LEAK. |  |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | NAMPA LNG FACILITY | NAMPA LNG | IN SERVICE |  |  | ID | 0 | 0 | 0 |  |  |  | YES | INTRASTATE | 1 | 73646 |  | YES | [9 empty] | YES | YES | [5 empty] | STORAGE TANK/VESSEL |  | 0 | 0 | 1989000 | 1989000 | 0 | 0 | 0 | 0 |  | 532 | 532 | 0 | 0 | 1989532 | 895764.548553028 | 1989532 | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS WORKING FOR THE OPERATOR |  | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | [87 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.coom | 208-377-6032 |  | 2021-06-24 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | ON THURSDAY, FEBRUARY 4, 2021 A PLANT OPERATOR WAS WORKING ON THE ROOF OF THE LNG TANK AND AUDIBLY AND VISUALLY DISCOVERED A NON-HAZARDOUS LEAK. THE NON-HAZARDOUS LEAK IS UNDER A STEEL BACKING PLATE THAT IS WELDED TO THE ROOF OF THE LNG TANK. THE BACKING PLATE IS PART OF THE SUPPORT SYSTEM FOR THE WALKING PLATFORM. BECAUSE THE BACKING PLATE IS NOT FULLY WELDED, WATER ACCUMULATED BETWEEN THE BACKING PLATE AND THE LNG TANK ROOF, ULTIMATELY LEADING TO A NON-HAZARDOUS CORROSION LEAK. AN ESTIMATED 300 CFH IS VENTING TO THE ATMOSPHERE. INTERMOUNTAIN GAS COMPANY (IGC) HIRED AN ENGINEERING CONSULTANT ON FEBRUARY 11, 2021 TO EVALUATE REPAIR OPTIONS. ON FEBRUARY 17, 2021 AT 11:10 A.M. MST, USING DATA PROVIDED BY THE ENGINEERING CONSULTANT, IGC DETERMINED THE LNG TANK WILL BE TAKEN OUT OF SERVICE TO MAKE REPAIRS, WHICH IS EXPECTED TO EXCEED $50,000, AT WHICH TIME IGC NOTIFIED THE NRC. AS OF FEBRUARY 17, 2021, THE LNG TANK HAD 3,093,114 GALLONS OF LNG. TO ALLOW FOR THE OFFLOAD AND VAPORIZATION OF THE LNG, THE LNG TANK WILL BE TAKEN OUT OF SERVICE IN JUNE 2021. THE ESTIMATED VOLUME OF COMMODITY RELEASED UNINTENTIONALLY (PART A, QUESTION 9) IS 201.6 MCF AS OF MARCH 4, 2021. THIS QUANTITY WILL BE REVISED FOR THE FINAL REPORT. ESTIMATED COST OF OPERATOR'S PROPERTY DAMAGE & REPAIRS (PART C, QUESTION 1.B.) IS $500,000. THIS COST WILL BE REVISED FOR THE FINAL REPORT. INTERMOUNTAIN GAS COMPANY RECEIVED A QUOTE FOR REPAIRS ON JUNE 23, 2021. THE OPERATOR'S PROPERTY DAMAGE & REPAIRS (PART C, QUESTION 1.B.) HAS BEEN REVISED FROM $500,000 TO $1,989,000.
2022-05-31 09:24 | NO | NO | 20210004 | 36447 | 2021-09-29 12:45 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-08-30 18:35 | CENTRAL | YES | 2021 | 1315189 | 2021-08-30 19:03 | 1315272 | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 528.8 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2021-08-30 18:35 | 2021-08-31 07:00 |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 1 | Ocheyedan LNG Plant |  | IN SERVICE |  |  | IA | 120 | 3 | 150000 | YES |  |  |  | INTRASTATE | 1 | 760 | YES | [13 empty] | YES |  |  |  | RELIEF VALVE |  | 0 | 0 | 3449 | 3449 | 4729 | 4729 | 4058 | 4058 | COST ASSOCIATED TO RESTORE SYSTEM. | 7724 | 7724 | 0 | 0 | 19960 | 14401.8122670028 | 19960 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | INCORRECT OPERATION | STORAGE TANK OR PRESSURE VESSEL ALLOWED OR CAUSED TO OVERFILL OR OVERPRESSURE | INCORRECT OPERATION | OVERFILL/OVERFLOW OF TANK/VESSEL/SUMP | [33 empty] | STORAGE TANK OR PRESSURE VESSEL ALLOWED OR CAUSED TO OVERFILL OR OVERPRESSURE |  |  |  | YES | [44 empty] | YES | [5 empty] | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 563-585-4014 | 563-583-0850 | 2022-03-10 | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | 15635854014 | tony.engling@blackhillscorp.com | ON AUGUST 30TH, 2021 THE OCHEYEDAN IOWA LNG PLANT, LOCATED AT 6383 RAILROAD STREET, OCHEYEDAN IOWA, WHICH FEEDS A SINGLE COMMERCIAL CUSTOMER, SHUT DOWN DUE TO OVER PRESSURIZATION AND RELEASE OF GAS INTO THE ATMOSPHERE. THIS OCCURRED DURING THE TRANSFER OF LNG FROM COAXIS TO BLACK HILLS ENERGY'S LNG TANK. INITIAL INVESTIGATION SHOWS THAT THE LNG TRANSFER PROCEDURE WAS NOT FOLLOWED BY COAXIS TO BLACK HILLS ENERGY'S LNG FACILITY. BLACK HILLS ENERGY SAFEGUARDS OPERATED AS DESIGNED. SERVICE WAS RESTORED AUGUST 31ST AT 7:00PM CENTRAL TIME.
2022-05-31 09:24 | NO | NO | 20210005 | 36641 | 2021-10-08 10:18 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-09-08 11:26 | CENTRAL | YES | 2021 | 1316155 | 2021-09-08 13:26 | 1316361 | YES | NO | YES | NO |  | LNG (LIQUEFIED NATURAL GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 0.05 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2021-09-08 11:00 | 2021-09-10 12:00 |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | Ocheyedan LNG Plant |  | IN SERVICE |  |  | IA | 120 | 3 | 50000 | YES |  |  |  | INTRASTATE | 1 | 760 | YES | [13 empty] | YES |  |  |  | RELIEF VALVE |  | 0 | 0 | 3450 | 3450 | 265 | 265 | 0 | 0 |  | 0 | 0 | 0 | 0 | 3715 | 1671.94031762295 | 3715 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [29 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | NO | NO | [43 empty] | YES | [11 empty] | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 563-585-4014 | 563-583-0850 | 2022-05-04 | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | 15635854014 | tony.engling@blackhillscorp.com | ON SEPTEMBER 8, 2021 THE OCHEYEDAN, IA LNG FACILITY WENT INTO EMERGENCY SHUT DOWN (ESD) AS A RESULT OF A METHANE MONITOR DETECTING THE PRESENCE OF METHANE. INVESTIGATION OF THE INCIDENT REVEALED THAT THE SOURCE OF METHANE WAS FROM A RUPTURE DISC WHICH WAS ALLOWING SEEPAGE TO BETWEEN THE RUPTURE DISC AND THE MOUNTING FRAMEWORK. THE AMOUNT OF METHANE PRESENT WAS NOT MEASURABLE. NEW RUPTURE DISCS WERE ORDERED AND INSTALLED RESOLVING THE ISSUE OF SEEPAGE. THE OLD DISCS THAT WERE REMOVED WERE SENT IN FOR TESTING BY AN INDEPENDENT LABORATORY. RESULTS OF THE LABORATORY TESTING REVEALED THAT THE TWO RUPTURE DISCS BLEW AT 115 AND 108 PSI WITH A STENCILED PRESSURE OF 148 PSI.
2022-05-31 09:24 | NO | NO | 20210007 | 36117 | 2021-12-10 20:50 | SUPPLEMENTAL FINAL | 32214 | CAMERON LNG, LLC | 2925 BRIARPARK SUITE 1000 | HOUSTON | TX | 77042 | 2021-11-12 05:46 | CENTRAL | NO | 2021 | 1321811 | 2021-11-12 07:41 | 1321860 | NO | NO | YES | NO |  | LPG (LIQUEFIED PETROLEUM GAS) WHILE BEING HANDLED IN LIQUID PHASE |  | 3.91 | 0 | 2.78 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | ONLY TRAIN 3 WAS SHUT DOWN; THE REST OF THE FACILITY CONTINUED OPERATIONS. |  |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | Cameron LNG |  | IN SERVICE |  |  | LA | 2232 | 0 | 2205 |  |  |  | YES | INTERSTATE | 3 | 1309916 | YES | [7 empty] | YES |  | YES | [7 empty] | PUMP |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 200 | 0 | 0 | 200 | 230.320699708455 | 200 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | EQUIPMENT FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [29 empty] | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT |  | NO | NO | [55 empty] | MICHAEL WOLF | REGULATORY AND COMPLIANCE MANAGER | mwolf@cameronlng.com | 832-783-5513 |  | 2021-12-10 | MICHAEL WOLF | REGULATORY AND COMPLIANCE MANAGER | 8327835513 | mwolf@cameronlng.com | ON NOVEMBER 10, 2021, P3-2505B (A BUTANE PUMP IN TRAIN 3) WAS PLACED IN STANDBY MODE, WITH P3-2505A IN SERVICE AND ONLINE. ROUTINE MAINTENANCE WORK TO ADD BARRIER FLUID TO THE PUMP WAS BEING PLANNED. BASED ON A REVIEW OF THE HISTORICAL SUCTION PRESSURE AND SEAL PRESSURE, CAMERON BELIEVES THAT A MINOR SEAL FAILURE (AROUND 1/8" IN SIZE) ON P3-2505B OCCURRED AROUND 5:05AM ON NOVEMBER 12, 2021. AT 5:46AM, TRAIN 3 EXPERIENCED A TRIP DUE TO ZONE 11 FIRE AND GAS DETECTION. TRAIN 3 WAS SHUT DOWN AND ISOLATION OF THE PROCESS WAS ACHIEVED AT THIS TIME. WITHIN TEN MINUTES, THE SUCTION AND DISCHARGE BLOCK VALVES FOR P3-2505B WERE CLOSED AND THE PUMP WAS DEPRESSURIZED TO THE FLARE SYSTEM. ALARMS AT THE DCS WERE CLEARED AT 6:07AM. BASED ON THIS TIMELINE, CAMERON ESTIMATES THE TOTAL DURATION OF THE RELEASE AT AROUND FIFTY (50) MINUTES. WE ESTIMATE THAT APPROXIMATELY 540 LBS. OF LIQUID PROPANE GASES ("LPGS") WERE RELEASED, BUT NO POOLING OCCURRED. THERE WERE NO INJURIES OR DEATHS ASSOCIATED WITH THIS EVENT AND NO EVACUATIONS WERE NEEDED. TRAINS 1 AND 2 CONTINUED OPERATIONS THROUGHOUT THE EVENT.
2022-05-31 09:24 | NO | NO | 20210008 | 36162 | 2021-12-20 20:17 | ORIGINAL FINAL | 39257 | INTERIOR GAS UTILITY | 2525 PHILLIPS FIELD ROAD | FAIRBANKS | AK | 99709 | 2021-11-21 17:10 | ALASKA | NO | 2021 | 1322689 | 2021-11-22 10:10 | 1322785 | NO | NO | YES | NO |  | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2021-11-21 18:09 | 2021-11-22 10:04 |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LNG STORAGE AND VAPORIZATION SITE3 |  | IN SERVICE |  |  | AK | 5 | 1 | 48 | YES |  |  |  | INTRASTATE | 1 | 71740 | YES |  | YES | [8 empty] | YES |  | YES | YES |  |  |  | VAPORIZER |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YES | YES | NO | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN A TANK, VESSEL, OR SUMP/SEPARATOR OVERFLOW OR FACILITY OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [33 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN A TANK, VESSEL, OR SUMP/SEPARATOR OVERFLOW OR FACILITY OVERPRESSURE |  | YES | [40 empty] | YES | [6 empty] | YES |  | YES |  |  | ERIK WEFLEN | MECHANICAL ENGINEER | eweflen@interiorgas.com | 9074527111 | 9074578111 | 2021-12-20 | DAN BRITTON | GENERAL MANAGER | 9074527111 | dwbritton@interiorgas.com | THE INTERIOR GAS UTILITY (IGU) LNG STORAGE AND VAPORIZATION SITE NUMBER 3 (SS3) IN FAIRBANKS, ALASKA SENT COLD GAS AND POSSIBLY LNG TO THE DISTRIBUTION SYSTEM. WHEN THE COLD GAS OR LNG ENTERED THE DISTRIBUTION SYSTEM, IT EMBRITTLED THE 8' UNDERGROUND HDPE PIPE, WHICH SUBSEQUENTLY RUPTURED IN A SECTION OF PIPING WITHIN IGU PROPERTY. THE HIGHEST RECORDED PRESSURE DOWNSTREAM OF THE DISTRIBUTION REGULATORS AT SS3 WAS 62PSIG. AT APPROXIMATELY 4:10PM ON 11/21/2021, A TEMPERATURE SWITCH ON THE OUTLET OF THE VAPORIZER MALFUNCTIONED AND CLOSED A VALVE TO STOP THE FLOW OF LNG THROUGH THE VAPORIZER. WITH NO LNG TO VAPORIZE, THE GLYCOL HEATER TURNED OFF DUE TO LOW DEMAND. AT ABOUT 4:55PM, AN OPERATOR NOTICED THAT THE FLOW OF LNG HAD STOPPED, AND THE DISTRIBUTION PRESSURE WAS DROPPING. THE OPERATOR OPENED THE CLOSED VAPORIZER VALVE VIA REMOTE CONTROL. THE OPERATOR DID NOT NOTICE THAT THE BOILER WAS NOT FIRING AND DID NOT MONITOR THE SITE LONG ENOUGH TO VERIFY THE SYSTEM WAS STABLE AND PROPER TEMPERATURES WHERE BEING MAINTAINED. DUE TO THE MALFUNCTIONING TEMPERATURE SWITCH AND A TEMPERATURE TRANSMITTER THAT HAD NOT BEEN PROGRAMMED TO ACT AS A BACKUP TO THE TEMPERATURE SWITCH, THE CONTROL SYSTEM DID NOT STOP THE FLOW OF LNG THROUGH THE VAPORIZER, UPON A LOW GAS TEMPERATURE ON THE OUTLET OF THE VAPORIZER. THE BOILER ATTEMPTED TO FIRE ABOUT THREE MINUTES AFTER THE LNG FLOW RESUMED BUT FAILED TO STAY RUNNING. THE SYSTEM ATTEMPTED TO START A BACK-UP BOILER ABOUT 10 MINUTES LATER, ABOUT WHEN THE DISTRIBUTION LINE RUPTURED. THE STANDARD OPERATING PROCEDURES WILL BE REVISED TO NO LONGER ALLOW CONTROL CHANGES FROM VIA REMOTE CONTROL (EXCEPT FOR EMERGENCY SHUT DOWNS AND SPECIFIED EXCEPTIONS) AND INSTEAD REQUIRE THE MONITORING OPERATOR TO TRAVEL TO THE SITE TO MAKE THE NECESSARY ADJUSTMENTS AND CHANGES. THE VAPORIZER TEMPERATURE SWITCHES WILL BE RECOMMISSIONED, AND THE TEMPERATURE TRANSMITTERS WILL BE ADDED INTO THE VAPORIZER SHUTDOWN PROGRAMMING LOGIC TO ADD REDUNDANCY. ADDITIONALLY, A DOWNSTREAM TEMPERATURE TRANSMITTER LOCATED ON THE METER SKID WILL BE USED TO SHUT DOWN THE LNG PUMPS IF LOW TEMPERATURE IS DETECTED INDICATING THE VAPORIZER SHUTDOWNS FAILED TO ACTIVATE AS A RESULT OF LOW OUTLET TEMPERATURE.
2022-05-31 09:24 | NO | NO | 20220001 | 36358 | 2022-01-04 14:49 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-12-27 07:25 |  | YES | 2021 | 1325314 | 2021-12-27 10:12 | 1325870 | NO | NO | YES | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 0 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2021-12-27 07:25 | 2021-12-27 08:35 |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | Ocheyedan LNG Plant |  | IN SERVICE |  |  | IA | 120 | 3 | 150000 | YES |  |  |  | INTRASTATE | 1 | 753 | YES | [13 empty] | YES |  |  |  | RELIEF VALVE |  | 0 | 0 | 0 | 0 | 40 | 40 | 0 | 0 |  | 0 | 0 | 0 | 0 | 40 | 18.0020491803279 | 40 | YES | YES | YES | COMPUTERIZED CONTROL SYSTEM (SUCH AS ALARM(S), ALERT(S), EVENT(S), LEAK DETECTION, TEMPERATURE, PRESSURE, ETC.) |  | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [40 empty] | MISCELLANEOUS | CUSTOMERS LOAD/ USAGE DRAMATICALLY CHANGED AND CAUSED THE RELIEF TO RELEASE AN UNMEASURABLE AMOUNT OF GAS THAT CAUSED THE METHANE SENSOR TO PUT THE LNG SYSTEM INTO EMERGENCY SHUT DOWN MODE. ALL EQUIPMENT WORKED AS DESIGNED. | [46 empty] | TONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 15635854014 | 563-583-0850 | 2022-02-18 | TONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | 15635854014 | tony.engling@blackhillscorp.com | CUSTOMERS GAS LOAD / USAGE DRAMATICALLY INCREASED ERODING THE LINE PACK IN THE SYSTEM. THE FACILITY BEGAN PRESSURIZING THE SYSTEM TO RESTORE LINE PACK PRESSURE. LINE PACK PRESSURE WAS RESTORED QUICKER THAN DEMAND, AND THE SET POINT FOR THE RELIEF VALVE WAS EXCEEDED. THE RELIEF VALVE RELEASED THE EXCESS PRESSURE AND RESEATED WITHOUT A MEASURABLE AMOUNT OF NATURAL GAS BEING VENTED TO ATMOSPHERE. DUE TO THE WEATHER PATTERN THE ONSITE METHANE DETECTOR RECOGNIZED THE RELEASE AND PLACED THE SYSTEM INTO EMERGENCY SHUT DOWN AS THE SYSTEM IS DESIGNED. WE REVIEWED THE SCADA SYSTEM DATA AS WELL AS PERFORMED AN ONSITE INVESTIGATION AND WERE ABLE TO CONCLUDE THAT THE DEMAND ON THE SYSTEM AND THE RECOVERY OF THE NATURAL GAS DEMAND IS WHAT TRIGGERED THE RELEASE. THE SYSTEM OPERATED AS DESIGNED AND NO EQUIPMENT DEFICIENCIES WERE NOTED.
2022-05-31 09:24 | NO | NO | 20220002 | 36404 | 2022-02-10 17:24 | SUPPLEMENTAL FINAL | 40021 | VENTURE GLOBAL CALCASIEU PASS, LLC | 1001 19TH STREET NORTH SUITE 1500 | ARLINGTON | VA | 22209 | 2022-01-17 02:00 | CENTRAL | YES | 2022 | 1326824 | 2022-01-18 17:50 | 1326987 | YES | NO | NO | NO |  | NATURAL GAS WHILE BEING HANDLED IN GASEOUS PHASE |  | 3609.2 | 0 | 0 | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | NO | THE VENTING OPERATION WAS SHUT DOWN BUT THE ENTIRE LNG FACILITY WAS NOT. |  |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | Venture Global Calcasieu Pass |  | IN SERVICE |  |  | LA | 0 | 0 | 1699 |  |  |  | YES | INTERSTATE | 2 | 0 | YES | [7 empty] | YES |  | YES | YES | YES |  |  |  | YES | AT THE TIME OF THE INCIDENT, THE FACILITY WAS STILL UNDER COMMISSIONING. | OTHER | TEMPORARY VENT ON LNG STORAGE TANK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17564 | 17564 | 0 | 0 | 17564 | 20226.7638483965 | 17564 | YES | YES | YES | REMOTE OPERATING PERSONNEL |  | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [33 empty] | OTHER INCORRECT OPERATION | AIR SPECIALIST NOT INCLUDED IN MANAGEMENT OF CHANGE (MOC) APPROVAL PROCESS | YES | [51 empty] | YES | CASSIE HARRISON | DIRECTOR REGULATORY COMPLIANCE | cassie.harrison@venturegloballng.com | 7134197783 |  | 2022-02-28 | FORY MUSSER | SENIOR VICE PRESIDENT DEVELOPMENT | 2027596738 | fmusser@venturegloballng.com | AN UNINTENTIONAL DISCHARGE OF NATURAL GAS OCCURRED DURING NITROGEN DISPLACEMENT ACTIVITIES ASSOCIATED WITH COMMISSIONING OF THE SOUTH LNG TANK. NITROGEN MUST BE REMOVED FROM THE TANK, PRIOR TO THE INITIAL START-UP, BY FLOWING NATURAL GAS INTO THE TANK IN ORDER TO DISPLACE THE NITROGEN. THE FACILITY AND ITS PRIMARY CONTRACTOR DEVELOPED A PROCEDURE FOR CARRYING OUT THE NITROGEN DISPLACEMENT ACTIVITIES THAT INITIALLY INCLUDED DIRECTING THE VENT STREAM TO THE LP FLARE. LATER, THE PROCEDURE WAS AMENDED TO PROVIDE FOR VENTING OF THE NITROGEN VIA A ROOF VENT ON THE LNG TANK. THE FACILITY COMPLETED A MANAGEMENT OF CHANGE ("MOC") EVALUATION FOR THE AMENDED PROCEDURE, WHICH WAS APPROVED BY OPERATIONS, COMMISSIONING, AND ENGINEERING. ACCORDING TO THE AMENDED PROCEDURE, THE VENTING WOULD BE MONITORED TO DETERMINE WHEN THE NITROGEN DISPLACEMENT WOULD BE COMPLETE AND THE REMAINDER OF THE TANK CONTENTS WOULD BE SWITCHED TO THE LP FLARE. VENTING OF NITROGEN FROM THE TANK BEGAN ON JANUARY 15, 2022 AT APPROXIMATELY 0300 AND ENDED ON JANUARY 17, 2022 AT APPROXIMATELY 1000 HOURS WHEN FACILITY ENVIRONMENTAL PERSONNEL BECAME AWARE OF THE VENTING AND POTENTIAL FOR NATURAL GAS TO BE PRESENT IN THE VENT STREAM. OPERATIONS WERE PROTECTIVELY CEASED PRIOR TO CONFIRMATION OF THE PRESENCE AND/OR QUANTITY OF ANY NATURAL GAS IN THE VENT. LATER, IT WAS DETERMINED THAT NATURAL GAS MIXED WITH NITROGEN WAS IN FACT EMITTED. THE PRIMARY ROOT CAUSE OF THE INCIDENT WAS THE EXCLUSION OF AN ENVIRONMENTAL SPECIALIST/ AIR PERMITTING SPECIALIST IN THE SIGN-OFF APPROVAL OF THE MOC. IF THAT INDIVIDUAL WAS INCLUDED IN THE MOC PROCESS, THE MOC WOULD HAVE NEVER BEEN EXECUTED SINCE THE LNG TANK IS NOT AN APPROVED EMISSION SOURCE. TO PREVENT ANY RECURRENCE, ANY NITROGEN DISPLACEMENT ACTIVITY USING NATURAL GAS WILL EITHER DIRECT ANY VENT STREAM PURGED FROM THE LNG STORAGE TANKS TO A FLARE OR SUCH ACTIVITY WILL BE PERMITTED PURSUANT TO THE REGULATORY PERMIT IN LAC 33:III.309 OR OTHER APPROPRIATE AUTHORIZATION FROM THE LOUISIANA DEPARTMENT OF ENVIRONMENTAL QUALITY. IN ADDITION, THE FACILITY WILL ENSURE THAT ANY VENTING PROCEDURE AND ANY CHANGES THERETO ARE THOROUGHLY REVIEWED DURING THE MOC PROCESS AND ARE APPROVED BY APPROPRIATE AND RELEVANT STAFF, INCLUDING ENVIRONMENTAL STAFF, IN ADDITION TO OPERATIONS AND ENGINEERING STAFF. FINALLY, ANY PERSONNEL INVOLVED IN NITROGEN PURGING OPERATIONS FOR THE LNG STORAGE TANKS WILL RECEIVE ADDITIONAL TRAINING ON THE PROCEDURES AND REGULATORY REQUIREMENTS PRIOR TO ANY FUTURE NITROGEN DISPLACEMENT OPERATIONS.
2022-05-31 09:24 | NO | NO | 20220003 | 36402 | 2022-02-28 08:24 | ORIGINAL | 40195 | EVERSOURCE GAS COMPANY OF MASSACHUSETTS | 247 STATION DRIVE | WESTWOOD | MA | 02090 | 2022-01-31 02:30 | EASTERN | YES | 2022 | 1327701 | 2022-01-31 08:19 | 1327821 | NO | NO | YES | NO |  | NO RELEASE OF COMMODITY INVOLVED |  |  |  |  | NO |  |  |  |  | 0 | NO |  |  |  |  | 0 | YES |  | 2022-01-31 02:05 | 2022-02-01 13:00 |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | Ludlow LNG |  | IN SERVICE |  |  | MA | 30 | 3 | 48 | YES |  |  | YES | INTRASTATE | 1 | 186522 |  | YES | [9 empty] | YES | YES | [5 empty] | OTHER | SEND OUT PUMP ELECTRICAL JUNCTION BOX | 0 | 0 | 10000 | 9802.47740207566 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 10000 | 4411.61700703047 | 9802.47740207566 | YES | YES | YES | FLAME DETECTORS |  | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [40 empty] | MISCELLANEOUS | ELECTRICAL INSULATION FAILURE CAUSED CLASS C FIRE IN JUNCTION BOX | [46 empty] | KATHERINE SILVER | SUPERVISOR COMPLIANCE | katherine.silver@eversource.com | 508-864-1836 |  | 2022-02-28 | KATHERINE SILVER | OPERATIONS COMPLIANCE SUPERVISOR | 5088641836 | katherine.silver@eversource.com | LNG FLAME MONITORING DEVICE ALERTED PLANT OPERATIONS PERSONNEL WHO WITNESSED A FLASH ON THE PLANT CCTV IN THE AREA OF THE LNG SEND OUT PUMPS. PLANT OPERATOR INITIATED THE ESD AND MADE NOTIFICATIONS TO GAS CONTROL AND MANAGEMENT. ELECTRIC ARCING HAD OCCURRED IN AN LNG PUMP JUNCTION BOX. THE ARCING CEASED IMMEDIATELY WHEN THE ESD WAS INITIATED.