2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20180126 | 31294 | 2018-12-07 16:49 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2018-11-08 10:25 | 2018 |  |  | 30.1763 | -92.6684 | 1229862 | 2018-11-08 12:05 |  | NATURAL GAS |  | 1 | 312 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-08 10:51 | 2018-11-17 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-08 10:25 | 2018-11-08 10:45 | ONSHORE | LA | 70546 | Not Within a Municipality | JEFFERSON DAVIS | SURVEY STATION NO. | 10+18 | ANR LATERAL 703 SOUTH JENNINGS | ROUTE ID: 8001703 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 12 |  | 0.25 | 42000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | LONESTAR | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1956 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 328 |  | NO | NO | NO |  |  |  |  | 12000 | 12998.730734360832 | 12000 | 12998.730734360832 | 1 | 1.42316784869976359338061465721040189125 | 138000 | 149485.403445149568 | 0 | 0 | 0 | 0 |  |  | 162001 | 77417.2529357930641040189125295508274232 | 175484.2880817199317635933806146572104019 | [8 empty] | 796 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 7387 | NO | [5 empty] | YES | PIPELINE WAS INSTALLED PRIOR TO DESIGN REQUIREMENTS FOR INTERNAL INSPECTION TOOLS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MINIMAL AMOUNT OF GAS LOSS WAS NOT DETECTABLE DUE TO THE SMALL SIZE OF THE LEAK. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CONSTRUCTION-RELATED | [13 empty] | YES | [62 empty] | NO | [63 empty] | YES | 1982 | 1638 | NO | [13 empty] | NO | [63 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ROGER STREET | COMPLIANCE SPECIALIST | 615-465-5123 | roger_street@transcanada.com | ON 8 NOVEMBER 2018 AT 10:25 CT, A CONTRACT EMPLOYEE, WHILE CONDUCTING A CLOSE INTERVAL SURVEY, OBSERVED BUBBLING FROM THE GROUND ABOVE THE ANR LATERAL 703 SOUTH JENNINGS LINE. UPON DISCOVERY OF THE CONDITION, THE EMPLOYEE CONTACTED THE AREA OFFICE, WHO DISPATCHED A QUALIFIED TECHNICIAN TO SHUT IN VALVES TO THE 703 LATERAL AND INVESTIGATE THE SOURCE OF THE LEAK. THE INITIAL FIELD INVESTIGATION DETERMINED THAT THE SOURCE OF THE BUBBLING WAS DUE TO LEAK ON THE PIPELINE. AT 12:05 CT, AN INCIDENT WAS REPORTED INTO THE NATIONAL RESPONSE CENTER (REPORT #1229862). A COURTESY CALL WAS ALSO PLACED THE PHMSA ACCIDENT INVESTIGATION DIVISION (AID) TO INFORM THE DIVISION OF THE INCIDENT. FOLLOWING THE DISCOVERY OF THE LEAK, ACTIONS INCLUDED THE REDUCTION OF PIPELINE PRESSURE FROM DISCOVERY PRESSURE OF 976PSIG TO 100PSIG, COMPLETED . ON 12 NOVEMBER 2018, REPAIR CREWS ARRIVED AT THE SITE TO REPAIR THE PIPELINE. ON NOVEMBER 13 PRIOR TO EXCAVATION, PIPELINE PRESSURE WAS REDUCED TO 20PSIG. ON 15 NOVEMBER THE PIPELINE WAS EXPOSED, THE COATING WAS EXAMINED, AND A DEFECT WAS FOUND ON THE GIRTH WELD. IT WAS DETERMINED TO REPAIR THE LEAK BY PLACING A TYPE-B PRESSURE CONTAIN SLEEVE ACROSS THE DEFECT. ON 16 NOVEMBER, THE TYPE-B SLEEVE WAS WELDED ONTO THE PIPELINE AND THE REPAIR WAS COMPLETED. THE DEFECT WAS LIMITED TO A SINGLE PIN HOLE LOCATED AT THE 06:00 POSITION ON THE WELD WITH NO ANOMALIES OBSERVED NEAR THE GIRTH WELD. THE PIPELINE WAS PURGED, LOADED, AND RETURNED TO SERVICE AT 14:00 ON NOVEMBER 17, 2018.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20180127 | 31545 | 2018-12-13 10:04 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-11-28 04:35 | 2018 |  |  | 35.0336 | -88.8904 | 1231460 | 2018-11-28 07:00 |  | NATURAL GAS |  | 7501 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | EVENT ONLY INVOLVED UNIT 1B | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-28 06:00 | 2018-11-28 06:00 | ONSHORE | TN | 38052 | Not Within a Municipality | HARDEMAN COUNTY | MILEPOST | MLV 71-1 | STATION 71 (MIDDLETON) (STA 71-1) | LINE 100-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2015 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING THROUGH UNIT 1B VENT VALVE (IN PROPER OPEN POSITION) BECAUSE OF ICE IN CONTROL SYSTEM OF UNIT 1B DISCHARGE VALVE. | CLASS 1 LOCATION | NO |  | 567 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 31580 | 44943.6406619385342789598108747044917258 | 1800 | 1949.8096101541248 | 1000 | 1083.227561196736 | 0 | 0 |  |  | 34380 | 30827.6579455557497172576832151300236407 | 47976.6778332893950789598108747044917258 | [8 empty] | 650 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION FOUND ICE IN THE CONTROL SYSTEM OF UNIT 1B DISCHARGE VALVE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205 325 3863 | 205 325 3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713 369 9443 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 06:00 HOURS, 11/28/2018, A TGP EMPLOYEE ARRIVED AT STATION 71 AND DISCOVERED NATURAL GAS BLOWING FROM THE 2-INCH UNIT VENT VALVE ON COMPRESSOR UNIT 1B. THE EMPLOYEE IMMEDIATELY CONTACTED THE STATION SUPERVISOR FOR EVENT NOTIFICATION. THE STATION SUPERVISOR IMMEDIATELY DISPATCHED ADDITIONAL EMPLOYEES TO ASSIST. THE STATION E&C TECHNICIAN ARRIVED AT STATION 71 AT 6:20 HOURS AND CONFIRMED NATURAL GAS BLOWING FROM THE 2-INCH UNIT VENT VALVE AND DISCOVERED THE UNIT DISCHARGE VALVE WAS OPEN. AT 6:25 HOURS, THE MANUAL LOCKING VALVE BENEATH THE 2-INCH UNIT VENT VALVE WAS CLOSED THEREBY TERMINATING THE NATURAL GAS RELEASE. THE 2-INCH UNIT VENT VALVE WAS ALSO CLOSED. THE UNIT HAD PREVIOUSLY BEEN BLOWN DOWN FROM AN EARLIER EMERGENCY SHUTDOWN (ESD) TEST AND WAS LEFT WITH THE 2-INCH VENT VALVE IN THE NORMAL OPEN POSITION. AS PART OF POST INCIDENT INVESTIGATION, PRESSURE TRENDING INFORMATION WAS ANALYZED AND IT WAS DETERMINED THE DISCHARGE VALVE OPENED AT 3:25 HOURS AND REPORTABLE VOLUME WAS MET AT 04:35 HOURS. INVESTIGATION ALSO IDENTIFIED ICE HAD FORMED IN THE CONTROL SYSTEM OF THE UNIT 1B DISCHARGE VALVE, IMPAIRING ITS OPERATION, ALLOWING THE DISCHARGE VALVE TO OPEN PREMATURELY THEREFORE ALLOWING NATURAL GAS TO VENT THROUGH THE OPEN 2-INCH UNIT VENT VALVE TO ATMOSPHERE. POST EVENT REPAIRS INCLUDED THE CONTROL SYSTEM OF THE UNIT DISCHARGE VALVE WAS BLOWN CLEAN, FREE OF MOISTURE, AND THE CONTROL SYSTEM FILTER WAS REPLACED. PRIOR TO RETURN TO SERVICE, THE 2-INCH UNIT VENT VALVE WAS CONFIRMED RETURNED TO THE OPEN POSITION, ALSO THE MANUAL LOCKING VALVE BENEATH THE 2-INCH UNIT VENT VALVE WAS CONFIRMED RETURNED TO THE OPEN POSITION. THE UNIT SUCTION AND THE UNIT DISCHARGE VALVES WERE CONFIRMED PROPERLY CLOSED. COMPRESSOR UNIT 1B WAS CONFIRMED SAFE AND READY TO RETURN TO SERVICE AS NEEDED ON 11/28/2018. SINCE 11/28/2018, OPERATIONS HAS REVISED THE WINTERIZATION PLAN FOR STATION 71 TO INCLUDE INSPECTION OF VALVE CONTROL SYSTEMS TO DISCOVER CONDENSATE ISSUES AND ELIMINATE THE ISSUES BEFORE FREEZING CONDITIONS BEGIN. PLEASE NOTE THE FOLLOWING REQUESTED INFORMATION: THE ORIGINAL NRC REPORT NUMBER IS 1231460. THE UPDATED INFORMATION NRC REPORT NUMBER IS 1231506. THE REQUIRED PHMSA 48-HOUR NRC REPORT NUMBER IS 1231637.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20180128 | 31323 | 2018-12-13 14:34 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2018-11-27 09:45 | 2018 |  |  | 42.0421 | -93.271 | 1231388 | 2018-11-27 10:43 |  | NATURAL GAS |  | 7000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-27 13:56 | 2018-11-29 10:18 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-27 09:49 | 2018-11-27 11:00 | ONSHORE | IA | 50056 | Not Within a Municipality | STORY | MILEPOST | 20.5 | MARSHALLTOWN 10-INCH | IAB66101 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.219 | 42000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COLD APPLIED TAPE | [28 empty] | 1950 | 1950 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 166 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 32410 | 46124.8699763593380614657210401891252955 | 90000 | 97490.48050770624 | 10000 | 10832.27561196736 | 0 | 0 |  |  | 132410 | 78052.50852499849125295508274231678487 | 154447.6260960329380614657210401891252955 | [8 empty] | 425 |  | 500 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 39000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE THIRD PARTY CONTACTED NORTHERN BEFORE THE CONTROLLERS COULD REACT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST | john.gormley@nngco.com | 4023987494 |  |  |  |  | THOMAS G CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON NOVEMBER 27, 2018, MUMM BACKHOE AND EXCAVATING, LLC, WAS INSTALLING DRAIN TILE IN FARMLAND LOCATED NEAR COLO, IOWA. COMPANY OWNER GREG MUMM ("MUMM") AND EMPLOYEE TIM ABEL ("ABEL") WERE HIRED BY LAND OWNER DAVE EGGER ("EGGER") TO INSTALL DRAIN TILE IN HIS FARM FIELD DUE TO DRAINAGE ISSUES ENCOUNTERED EARLIER IN THE YEAR. ABEL WAS OPERATING THE TILING MACHINE ON THE SOUTHEAST 1/4 SECTION, (S34, T48N, R21W) IN STORY COUNTY, IOWA, AND MUMM WAS ROUTING DRAIN TILE WITH HIS VEHICLE AND DRAIN TILE TRAILER. AT APPROXIMATELY 0945, ABEL WAS USING THE TILING MACHINE TO INSTALL DRAIN TILE IN THE NORTHWEST CORNER OF THE PROPERTY IN AN EASTERLY DIRECTION AND MADE CONTACT WITH AND DAMAGED NORTHERN NATURAL GAS ("NORTHERN") 10-INCH-DIAMETER IAB66101 BRANCH LINE CAUSING A RUPTURE AND GAS LEAK. NORTHERN ISOLATED AND BLEW DOWN BRANCH LINE IAB66101 AND COMPLETED REPAIRS TO RESTORE SERVICE NOVEMBER 29, 2018. THE INCIDENT RESULTED IN A GAS RELEASE OF APPROXIMATELY 7.0 MCF AND AN EMERGENCY WHICH WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NOTIFICATION #1231388 AND 1231571). THE ROOT CAUSE WAS FAILURE BY MUMM TO MAKE A ONE CALL NOTIFICATION PRIOR TO PERFORMING TRENCHING ACTIVITIES. HAD MUMM PROPERLY SUBMITTED A ONE CALL, THIS WOULD HAVE NOTIFIED NORTHERN TO PERFORM A LINE LOCATE, WHICH COULD HAVE PREVENTED THE LINE STRIKE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20180129 | 32591 | 2018-12-13 18:45 | SUPPLEMENTAL FINAL | 12874 | DOMINION ENERGY QUESTAR PIPELINE, LLC | 333 SOUTH STATE STREET P.O. BOX 45922 | SALT LAKE CITY | UT | 84145-0360 | 2018-11-17 18:26 | 2018 |  |  | 41.4259 | -111.1775 | 1230701 | 2018-11-17 20:53 |  | NATURAL GAS |  | 48855 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-17 19:47 | 2019-01-10 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-17 18:26 | 2018-11-17 20:12 | ONSHORE | UT | 84086 | Not Within a Municipality | RICH COUNTY | SURVEY STATION NO. | 1933+30.07 | ML048 | ML048/TL112 JUNCTION TO ML048/JL057 JUNCTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.312 | 42000 | API 5L X42 | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL NATIONAL DUQUESNE | COLD APPLIED TAPE | [28 empty] | 1980 | 1977 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 432 | 62.8 |  | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | NO |  |  |  |  | 20000 | 21664.55122393472 | 0 | 0 | 118923 | 169247.3900709219858156028368794326241135 | 462080 | 500537.79147778777088 | 21997 | 23827.756663644601792 | 0 | 0 | ESTIMATED MISCELLANEOUS OTHER COSTS. |  | 623000 | 351938.5956398734296231347517730496453901 | 715277.4894362890784876028368794326241135 | [8 empty] | 780 |  | 918 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 89232 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS CLEAR THAT CONTROLLER/CONTROL ROOM ISSUES WERE NOT THE CAUSE OR A CONTRIBUTING FACTOR | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  |  | YES |  | YES | KIEFNER ANALYSIS CONCLUDED THAT FAILURE OCCURRED DUE TO CORROSION CAUSED BY DISBONDED COATING AND CP SHIELDING |  |  |  | YES |  |  | YES | YES | 1980 | YES | YES | YES |  |  |  | 2018 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CALEB BENTLEY | ENGINEER II - PIPELINE COMPLIANCE | caleb.a.bentley@dominionenergy.com | 8013245117 |  |  |  |  | RON JORGENSEN | VP WESTERN PIPELINE OPERATIONS | 8013245145 | ron.jorgensen@dominionenergy.com | ON 11/17/2018 AT 18:26 LOCAL TIME, DOMINION ENERGY QUESTAR PIPELINE'S (DEQP) MAIN LINE 048 (ML048) RUPTURED IN RICH COUNTY, UT. OPERATORS WERE DISPATCHED AND SHUTDOWN THE ML048 TRANSMISSION PIPELINE VIA MANUAL BLOCK VALVES AT 19:47. AT 20:12, A DEQP OPERATOR ARRIVED ON-SITE OF THE INCIDENT AND DISCOVERED A RUPTURE OF THE 20" ML048 PIPELINE WHICH HAD RESULTED IN AN UNINTENDED NATURAL GAS LOSS OF APPROXIMATELY 48.9 MMSCF. ONCE IT WAS CONFIRMED AT 20:48 THAT THE INCIDENT WAS REPORTABLE, INCLUDING CONFIRMATION OF EXACT FAILURE LOCATION, DEQP NOTIFIED THE NATIONAL RESPONSE CENTER VIA TELEPHONIC REPORT ON 11/17/2018 AT 20:53. A 48-HOUR CONFIRMATION OF THE INCIDENT WAS REPORTED TO THE NRC ON 11/19/2018 AT 17:56. AN INCIDENT INVESTIGATION TEAM WAS DEPLOYED AND PROGRESSED AN INVESTIGATION OF THE FAILURE AND REPAIR OF THE PIPELINE. CAUSE OF THE FAILURE WAS EXTERNAL CORROSION AS A RESULT OF DISBONDED COATING AND CP SHIELDING AS DETERMINED BY A KIEFNER & ASSOCIATES METALLURGICAL ANALYSIS. NOTES ON PARTICULAR QUESTIONS PART A: Q 6-7. SECOND NRC NOTIFICATION NUMBER 1230856 ON 11/19/2018 AT 17:56 LOCAL TIME Q 15B. COMPANY REPAIRED THE PIPELINE SEGMENT DIRECTLY AFFECTED BY THE FAILURE AND PLACED THE SEGMENT BACK IN-SERVICE SUBJECT TO SEVERAL COMMITMENTS: 1) MAINTAIN A PIPELINE PRESSURE AT 80% OF OPERATING PRESSURE AT TIME OF FAILURE, 2) CONTRACT WITH INDEPENDENT PARTY AND COMPLETE A PIPE FAILURE ANALYSIS, 3) COMPLETE INLINE INSPECTION OF MAIN LINE 048 FROM YELLOW CREEK SITE TO THE MAIN LINE 048-MAIN LINE 060 JUNCTION, AND 4) PERFORM NECESSARY REMEDIATION. THE PIPE FAILURE ANALYSIS HAS BEEN COMPLETED BY KIEFNER AND ASSOCIATES. INLINE INSPECTION IS IN PROGRESS AT THE TIME/DATE OF THIS SUPPLEMENTAL REPORT, AND THE PIPELINE REMAINS UNDER THE OPERATING RESTRICTION COMMITMENT (80% OF OPERATING PRESSURE AT TIME OF FAILURE). Q 19A. TIME ENTERED REFERS TO TIME OPERATOR BECAME AWARE OF INCIDENT BUT HAD NOT CONFIRMED
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20180130 | 32377 | 2018-12-14 08:54 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2018-11-16 02:16 | 2018 |  |  | 37.5559 | -81.3697 | 1230533 | 2018-11-16 02:32 |  | NATURAL GAS |  | 3920 | 3.64 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-16 02:45 | 2019-06-10 09:00 |  |  |  |  | YES |  |  |  |  | NO | [6 empty] | 0 | 2018-11-16 02:16 | 2018-11-16 01:45 | ONSHORE | WV | 25826 | CORRINE | WYOMING | SURVEY STATION NO. | RS-807629 | LINE KA TO KA-14 | LINE KA-14 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FLANGE ASSEMBLY | [38 empty] | 1999 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 49 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 11 | 11.915503173164096 | 11564 | 16457.5130023640661938534278959810874704 | 525715 | 569468.97733454206624 | 2200 | 2383.1006346328192 | 0 | 0 | TEMPORARY REPAIRS, EQUIPMENT WILL BE REMOVED WHEN PERMANENT REPAIRS ARE COMPLETE |  | 539490 | 263083.026210057057390704491725768321513 | 588321.5064747121157298534278959810874704 | [8 empty] | 560 |  | 1000 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER WAS NOTIFIED OPERATING PERSONNEL ABOUT THE PRESSURE ALARM AND MADE OPERATIONS AWARE THERE WAS A CALL ALREADY FROM WYOMING 911. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | AGE AND CONDITIONS OF SOFT GOODS | [161 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST US REGULATORY COMPLIANCE | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | GEORGE HAMATY | MANAGER EAST US REGULATORY COMPLIANCE | 304-357-3728 | george_hamaty@transcanada.com | ALL TIMES RECORDED WERE IN EASTERN STANDARD TIME ON 11/15/18 AT 23:54, TRANSCANADA'S GAS CONTROL (GC) CENTER (COLUMBIA GAS TRANSMISSION OPID 2616) WAS NOTIFIED BY WEST VIRGINIA WYOMING COUNTY 911 OF A GAS RELEASE AND FIRE AT CAIRO HOLLOW IN THE TOWN OF BUD, WV. COMPANY PERSONNEL WAS DISPATCHED BY LOCAL OPERATIONS AT THAT TIME. AT 00:36 ON 11/16/18, GC RECEIVED A LOW-PRESSURE ALARM OF 0 AT MEASURING STATION (MS) 804927 CORRINE DELIVERY POINT (DP) AT THE END OF LINE KA-14. COMPANY PERSONNEL ARRIVED ONSITE AT 01:45 ON 11/16/2018 AND CONFIRMED A FIRE AT CORRINE REGULATOR STATION (RS) 807629 LOCATED AT PIPELINES KA TO KA-14. COMPANY PERSONNEL CLOSED THE VALVE TO PIPELINE KA-14 AT 02:45 ON 11/16/2018 ISOLATING RS-807629 AND PIPELINE KA-14. COMPANY PERSONNEL CONTACTED MOUNTAINEER GAS COMPANY (LOCAL DISTRIBUTION OPERATOR) TO ISOLATE THE FEED AT MS-804927 CORRINE DP TO PREVENT BACKFEED INTO PIPELINE KA-14. PRELIMINARY INVESTIGATION IDENTIFIED A FAILED 2" ANSI-600 FLANGED CONNECTION THAT WAS MISSING PART OF THE GARLOCK GASKET. THE MISSING GASKET ALIGNS WITH HEAT MAPS OF THE FACILITY TO INDICATE THE FIRE DAMAGE IS SOURCED FROM THIS FLANGE. IGNITION SOURCE FOR THE LEAK AT THE INLET FLANGE TO THE REGULATION COULD BE THE IN-DIRECT FIRED HEATER ONSITE. TEMPORARY SERVICE WILL BE RESTORED USING A 2" SKID MOUNTED REGULATION SKID AND 2" CONNECTION TO AND FROM BELOW GROUND PIPING TO PIPELINE KA-14. PERMANENT INSTALLATION OF FACILITY WILL COMMENCE IN 2019 WITH EXPECTED IN SERVICE OF MARCH 29, 2019. THE INITIAL NRC REPORT NO. 1230533 REPORTED ON NOVEMBER 16, 2016 @ 02:32 AND THE 48-HR UPDATE NRC REPORT NO. 1230594 WAS REPORTED ON NOVEMBER 16, 2018 @ 14:23. AN APPARENT GASKET FAILURE OCCURRED IN TOP WORKS OF THE PRESSURE REGULATOR AT CORRINE REGULATOR STATION (RS) 807629. REPAIRS WERE COMPLETED ON JUNE 10, 2019.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20180131 | 31342 | 2018-12-18 11:02 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2018-12-10 03:10 | 2018 |  |  | 39.9268 | -101.9388 | 1232489 | 2018-12-10 05:17 |  | NATURAL GAS |  | 25100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-10 03:10 | 2018-12-10 15:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-10 04:21 | 2018-12-10 05:02 | ONSHORE | KS | 67756 | Not Within a Municipality | CHEYENNE | SURVEY STATION NO. | 160 / 4594+62 | LINE W | ST FRANCIS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1980 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD OF THE ST FRANCIS COMPRESSOR STATION, THE STATION ISOLATION VALVE LITERALLY FROZE WHILE PARTIALLY OPEN ALLOWING MAINLINE GAS TO VENT DURING THE STATION BLOW-DOWN. | CLASS 1 LOCATION | NO |  | 128 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 100380 | 142857.588652482269503546099290780141844 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100380 | 93735.4609929078014184397163120567375887 | 142857.588652482269503546099290780141844 | [8 empty] | 621 |  | 960 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AUTOMATIC ESD WAS CAUSED BY GAS DETECTION AT THE STATION AND THE UNINTENTIONAL GAS RELEASE FROM THE FROZEN ISOLATION VALVE, THE CONTROLLER WAS NOT AT FAULT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | FROZEN ISOLATION VALVE | [161 empty] | JOHN ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | john.glahn@sscgp.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@sscgp.com | ON 12/10/2018 AT 3:10 AM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) RECEIVED A HIGH LEVEL GAS DETECTION ALARM WHICH TRIGGERED AN AUTOMATIC EMERGENCY SHUTDOWN (ESD) OF THE ST. FRANCIS COMPRESSOR STATION IN CHEYENNE COUNTY, KANSAS. OPERATIONS PERSONNEL WERE DISPATCHED TO THE STATION ARRIVING AT 5:02 AM. AS PART OF THE ESD, THE STATION IS AUTOMATICALLY ISOLATED AND BLOWN DOWN. THE SCADA OPERATOR RECEIVED ALARMS THAT SSCGP LINE W WAS EXPERIENCING A RAPID DROP IN PRESSURE UPSTREAM OF THE STATION. THE UPSTREAM STATION ISOLATION VALVE FAILED TO FULLY CLOSE DURING THE ESD CAUSING MAINLINE GAS TO ESCAPE ALSO. ALL GAS WAS RELEASED THROUGH THE STATION BLOW-OFF VALVES. THE PERSONNEL ON SITE WARMED THE FROZEN ISOLATION VALVE AND HAD IT FULLY CLOSED BY 5:40 AM. A SMALL FITTING INSIDE OF THE STATION WAS LEAKING WHICH PROPERLY CAUSED THE ORIGINAL ESD. THIS FITTING WAS REPAIRED AND THE STATION WAS BROUGHT BACK ON-LINE AT 3:30 PM ON 12/10/2018.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20180132 | 31694 | 2018-12-18 18:02 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2018-11-20 15:13 | 2018 |  |  | 39.6983 | -104.7007 | 1230933 | 2018-11-20 16:33 |  | NATURAL GAS |  | 5962 | 3045 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-20 16:14 | 2018-11-21 19:42 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-20 15:13 | 2018-11-20 15:43 | ONSHORE | CO | 80018 | AURORA | ARAPAHOE | MILEPOST | MP 105+4872 | 9A PIPELINE | PUEBLO/WATKINS MAINLINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 60000 | API 5L X-60 | DSAW |  | KAISER STEEL | COAL TAR | [28 empty] | 1966 | 1966 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 3.3 | [7 empty] | CLASS 3 LOCATION | NO |  | 395 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 12116 | 13124.385131459653376 | 23722 | 33760.3877068557919621749408983451536643 | 28414 | 30778.827923844056704 | 0 | 0 | 0 | 0 |  |  | 64252 | 41520.1655467894535166430260047281323877 | 77663.6007621595020421749408983451536643 | [8 empty] | 500 |  | 820 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | REMOTELY CONTROLLED | 38260 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A THIRD-PARTY LINE STRIKE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE BUSINESS | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | SITE DEVELOPMENT | YES | 830500140 |  | UTILITY OWNER | YES | YES | NO |  | OTHER |  |  |  | INEDEQUATE HEI CONSTRUCTION INSTRUCTION/PROCEDURE. INEDEQUATE HEI CONSTRUCTION COMMUNICATION/HARDWARE/SOFTWARE/PROCESS. INEDEQUATE VERTICAL COMMUNICATION BETWEEN HEI CONSTRUCTION SUPERVISOR AND OPERATOR. | [262 empty] | KRITI BHAYANI | PIPELINE ENGINEER - CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan,com | ON NOVEMBER 20, 2018 AT 3:13 PM MST COLORADO INTRASTATE GAS COMPANY (CIG) GAS CONTROL RECEIVED A CALL FROM A THIRD-PARTY CONTRACTOR INDICATING THAT WHILE GRADING THEY THE THIRD-PARTY CONTRACTOR HAD HIT AND PUNCTURED A NATURAL GAS PIPELINE. CIG PERSONNEL ARRIVED AT THE LOCATION OF THE LINE STRIKE AT 3:43 PM MST AND CONFIRMED THAT IT WAS ON THE CIG PIPELINE. THE THIRD-PARTY CONTRACTOR STRUCK THE CIG 9A PIPELINE WHILE GRADING THE AREA FOR A NEW HOUSING DEVELOPMENT. THERE WAS AN OPEN ONE CALL TICKET AND CIG DAMAGE PREVENTION PERSONNEL HAD MARKED THE LINE. THE CONTRACTOR HAD PREVIOUSLY AGREED ORALLY AND IN WRITING TO CIG'S REQUEST THAT A CIG REPRESENTATIVE BE ONSITE FOR ANY WORK WITHIN 25 FEET OF OUR PIPELINE ASSETS. FURTHER, THE CONTRACTOR TOLD CIG A FEW DAYS BEFORE THE INCIDENT THAT NO WORK WOULD BE PERFORMED WITHIN 25 FEET OF THE PIPELINE ON THE DAY OF THE LINE STRIKE. DESPITE THE PIPELINE MARKINGS AND THE PRIOR AGREEMENTS, THE THIRD-PARTY CONTRACTOR PROCEEDED WITH GRADING OVER THE PIPELINE WITHOUT NOTIFYING CIG. POST CONFIRMATION BY CIG FIELD PERSONNEL THAT OUR PIPELINE HAD BEEN STRUCK, THEY PROCEEDED TO ISOLATE THE PIPELINE BETWEEN MLV 11 AND 11.9. CIG THEN IMPLEMENTED A BLOW DOWN PROCESS FOR THIS SEGMENT. ONCE THE LEAK SITE WAS DECLARED SAFE AND FREE OF GAS VAPORS CIG PROCEEDED TO MAKE REPAIRS. THE REPAIRS CONSISTED OF REPLACING SIXTY FEET OF PRETESTED TWENTY INCH PIPE. THE REPAIRS WERE COMPLETED ON NOVEMBER 21, 2018. UPON COMPLETING THE REPAIRS CIG IMPLEMENTED A PURGE AND PACK PROCESS FOR THIS SEGMENT. ONCE THE PURGE PROCESS WAS CONFIRMED TO BE COMPLETED THE SEGMENT PRESSURE WAS ALLOWED TO EQUALIZE. THE SEGMENT WAS THEN RETURNED TO GAS CONTROL FOR NORMAL OPERATIONS AND WAS BACK IN SERVICE AT 7:42 PM MST ON NOVEMBER 21, 2018.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20180133 | 31532 | 2018-12-19 09:14 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2018-11-23 16:24 | 2018 |  |  | 40.438 | -78.5911 | 1231182 | 2018-11-24 16:15 |  | NATURAL GAS |  | 23240 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | GAS WAS ABLE TO BYPASS THE COMPRESSOR STATION. NOT REQUIRING PIPELINE SHUTDOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-23 16:24 | 2018-11-23 16:51 | ONSHORE | PA | 15938 | LILLY | CAMBRIA | MILEPOST | 54.76 | LINE 19 | ARMAGH-LILLY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | GATE |  | 30" X 24" NORDSTRUM PLUG VALVE |  |  |  | 1961 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUTDOWN. | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 100164 | 142550.1843971631205673758865248226950355 | 100 | 108.3227561196736 | 0 | 0 | 0 | 0 |  |  | 100264 | 93581.5467165628235503546099290780141844 | 142658.5071532827941673758865248226950355 | [8 empty] | 618 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM PERSONNEL COULD NOT HAVE CAUSED THE MALFUNCTION OF THE VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | EXTERNAL FREEZING IN THE SHAFER OPERATOR CONTROL PILOT | [161 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: ON FRIDAY, NOVEMBER 23, AT 4:24 PM EST LILLY STATION HAD A STATION EMERGENCY SHUT DOWN (ESD). THE ESD WAS CAUSED BY A COMMERCIAL POWER DISRUPTION. THE EMERGENCY GENERATOR STARTED THOUGH A CIRCUIT BREAKER TRIPPED CAUSING A LOSS OF ELECTRICAL POWER WHICH RESULTED IN FULL STATION ESD ACTIVATION. WHEN THE ESD OCCURRED, GAS VENTED THROUGH THE THREE STATION ESD BLOW DOWN VALVES BECAUSE 30"X 24" (VALVE 19-149) FAILED TO CLOSE AUTOMATICALLY. OPERATOR PERSONNEL MANUALLY CLOSED VALVE 19-149 AT 5:01 PM EST. TOTAL GAS LOSS THROUGH THE THREE ESD BLOW DOWN VALVES WAS CALCULATED TO BE 23.24 MMSCF. WHEN THE ESD SYSTEM ACTIVATED, THE CONTROL PILOT ASSEMBLY IN THE SHAFER ACTUATOR FOR VALVE 19-149 FROZE DUE TO THE PRESENCE OF WATER (EXTERNAL TO THE CONTROL) AND COLD AMBIENT TEMPERATURES WHICH CAUSED THE VALVE TO REMAIN OPEN. SUPPLEMENTAL REPORT: 48 HR NRC REPORT 1231234 PRIOR TO THE NOVEMBER 23, 2018 INCIDENT AT TETLP'S LILLY COMPRESSOR STATION, TETLP HAD CALCULATED THE ESTIMATED GAS LOSS FOR A NORMAL ESD EVENT AT LILLY STATION TO BE 1.23 MMSCF. BASED ON THIS CALCULATION, AN ESD OPERATING AS ANTICIPATED WOULD NOT BE REPORTABLE, SINCE THE GAS RELEASE WOULD BE WELL UNDER THE 3 MMSCF THRESHOLD FOR REPORTING. HOWEVER, ONE OF THE ESD ISOLATION VALVES UNEXPECTEDLY DID NOT CLOSE PROPERLY, SO THE ACTUAL GAS LOSS WAS GREATER THAN THE ESTIMATED 1.23 MMSCF, AND GREATER THAN THE 3 MMSCF REPORTING THRESHOLD. ON NOV. 24, THE ESTIMATED GAS LOSS WAS CALCULATED TO BE MORE THAN 3 MMSCF, AND THEN WAS REPORTED TO NRC. THIS EVENT HAS IDENTIFIED THE NEED FOR ADDITIONAL TRAINING AND AWARENESS OF THE REQUIREMENT TO IMMEDIATELY REPORT SUCH EVENTS TO INTERNAL PERSONNEL RESPONSIBLE FOR NRC NOTIFICATIONS. THE TRAINING WILL BE DEVELOPED AND IMPLEMENTED SYSTEM-WIDE IN 2019.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20180134 | 31360 | 2018-12-20 08:37 | ORIGINAL FINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2018-11-22 21:23 | 2018 |  |  | 42.6763 | -78.9443 | 1231490 | 2018-11-28 11:29 |  | NATURAL GAS |  | 5300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE REPAIR DID NOT REQUIRE SHUTDOWN OF THE PIPELINE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-22 21:47 | 2018-11-22 21:59 | ONSHORE | NY | 14006 | TOWN OF EVANS | ERIE | MILEPOST | RELIEF VALVE | LINE RM32/FERRIER RD. STATION | STATION EVE 47 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE CONTROLS | 2001 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | RELIEF VALVE RELEASE | CLASS 2 LOCATION | NO |  | 74 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 16000 | 22770.68557919621749408983451536643026 | 200 | 216.6455122393472 | 2100 | 2274.7778785131456 | 0 | 0 |  |  | 18300 | 16040.0189253893861026004728132387706856 | 25262.10896994871029408983451536643026 | [8 empty] | 317 |  | 320 | OTHER | SYSTEM MAXIMUM OPERATING PRESSURE |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY IS CONNECTED TO A PIPELINE THAT WAS MONITORED AND CONTROLLED THROUGH SCADA BY THE CONTROLLERS WITHIN PARAMETERS. THE CAUSE OF THE INCIDENT WAS NOT DUE TO CONTROLLER ACTION NOR WAS THE INCIDENT NEGATIVELY AFFECTED BY CONTROLLER ACTION OR LACK OF ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | RELIEF VALVE PILOT GAS CONTROL FLOW RESTRICTOR. | [22 empty] | YES | COMPONENT FAILURE | [161 empty] | JOHN SEAGER | PIPELINE INTEGRITY ENGINEER | seagerj@natfuel.com | 716-857-7899 | 716-857-7508 |  |  |  | WILLIAM SNYDER | OPERATIONS SUPERINTENDENT | 716-827-2327 | snyderw@natfuel.com | NATIONAL FUEL GAS SUPPLY CORPORATION HAS REPORTED A NATURAL GAS INCIDENT AS A RESULT OF AN UNINTENTIONAL RELEASE OF NATURAL GAS ESTIMATED AT GREATER THAN THREE (3) MILLION CUBIC FEET, THAT OCCURRED AT 7700 FERRIER RD. IN THE TOWN OF EVANS, ERIE COUNTY, NY. NATIONAL FUEL CONFIRMED DISCOVERY OF THE INCIDENT ON WEDNESDAY NOVEMBER 28, 2018 AFTER COMPLETING A COMPREHENSIVE FLOW ANALYSIS OF GAS LOST DURING A RELIEF VALVE RELEASE THAT OCCURRED FROM APPROXIMATELY 9:23 PM TO 11:33 PM ON THURSDAY NOVEMBER 22ND, 2018. THE PROBABLE CAUSE OF THE INCIDENT WAS EQUIPMENT FAILURE OF A RESTRICTOR VALVE FOR A RELIEF VALVE CONTROL THAT CAUSED THE DEVICE TO FAIL IN AN OPEN POSITION. THERE WERE NO INJURIES OR PROPERTY DAMAGE. THE UPDATED NRC REPORT NUMBER 1231680.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190001 | 31882 | 2019-01-07 18:29 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-12-08 20:50 | 2018 |  |  | 42.2057 | -83.9686 | 1232438 | 2018-12-09 11:02 |  | NATURAL GAS |  | 5264 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-08 21:40 | 2018-12-09 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-08 20:50 | 2018-12-08 21:30 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | MILEPOST | ENGINE 3-1 | FREEDOM COMPRESSOR STATION | ENGINE 3-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2016 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL TUBING - PILOT LINE | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 390 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 16358 | 23280.1796690307328605200945626477541371 | 1200 | 1299.8730734360832 | 400 | 433.2910244786944 | 645 | 698.68177697189472 | LABORATORY EXAMINATION |  | 18603 | 16348.0382076391712113711583924349881797 | 25712.0255439174051805200945626477541371 | [8 empty] | 659 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE NOTIFICATIONS/RESPONSE WERE COMPLETED ACCORDING TO PROCEDURE - IMMEDIATE NOTIFICATION TO GAS CONTROL WHEN THE FAILURE WAS IDENTIFIED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE PILOT TUBE FOR A PILOT OPERATED PRESSURE RELIEF VALVE ON A HIGH PRESSURE COMPRESSOR DISCHARGE LINE CRACKED. AFTER THE PILOT TUBE CRACKED AND LEAKED DOWN CONTROL PRESSURE TO THE RELIEF VALVE WAS LOST AND THE RELIEF VALVE WENT INTO AN OPEN CONDITION, RELEASING GAS TO THE ATMOSPHERE. | YES |  |  |  |  | YES | [6 empty] | YES | [165 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 8, 2018 AT APPROXIMATELY 20:50 HOURS CONSUMERS ENERGY GAS CONTROL RECEIVED A NOTIFICATION OF A POSSIBLE GAS RELEASE FROM A CONTRACTOR WORKING ONSITE AT CONSUMERS ENERGY FREEDOM COMPRESSOR STATION. FREEDOM COMPRESSOR STATION IS LOCATED IN MANCHESTER, MICHIGAN (WASHTENAW COUNTY) A STATION MECHANIC ARRIVED ONSITE AT APPROXIMATELY 21:30 HOURS AND IDENTIFIED A RELEASE AT RELIEF VALVE #171 (UNIT 3-1). THE MECHANIC CLOSED VALVE 171 TO ISOLATE THE GAS FROM ENGINE 3-1 WHICH STOPPED GAS FROM BLOWING. UPON FURTHER INVESTIGATION A CRACK (LEAK) ON THE RELIEF VALVE PILOT LINE WAS DISCOVERED. THE PILOT LINE LEAK CAUSED PRESSURE TO BLEED OFF WHICH ALLOWED THE RELIEF VALVE TO OPEN AND RELEASE GAS TO THE ATMOSPHERE. NEW PILOT LINE TUBING WAS INSTALLED AND A RELIEF VALVE INSPECTION PERFORMED TO VERIFY NO CHANGE IN SET PRESSURE OCCURRED AS A RESULT OF THE FAILURE. ADDITIONAL VALVE INSPECTIONS AND LEAK TESTS WERE PERFORMED ON THREE ADDITIONAL RELIEF VALVES LOCATED IN PLANT 3 AS A PRECAUTIONARY MEASURE. NO ADDITIONAL LEAKS WERE DISCOVERED. THE FAILED EQUIPMENT WAS SENT TO CONSUMERS ENERGY'S LABORATORY SERVICES FOR FURTHER ANALYSIS. A SUMMARY OF THE FINDINGS ARE DETAILED BELOW: THE LONGER LEG OF THE TUB FRACTURED IN HIGH CYCLE FATIGUE INITIATING AT MULTIPLE LOCATIONS ON THE TUB OD UNDER THE FERRULE, APPROXIMATELY 3/8" FROM THE END OF THE TUBE. THE FATIGUE CRACK HAD PROPAGATED APPROXIMATELY 300 DEGREES AROUND THE TUBE PRIOR TO THE TUBE BEING TAKEN OUT OF SERVICE. THE FRACTURE SURFACE EXHIBITED A TRANSITION AFTER APPROXIMATELY 150 DEGREES OF PROPAGATION INDICATING THE STATE OF STRESS CHANGED OR THE PROPAGATION RATE INCREASED. THE FERRULE AT THIS LOCATION WAS NOT SQUARE WITH THE TUBE ABOVE IT, INDICATING A SIDE LOAD MAY HAVE BEEN APPLIED AT SOME POINT. THERE WAS NO APPARENT DEFECTS AT THE CRACK ORIGIN LOCATION. THE TUBE, FERRULE AND NUT FROM THE FAILURE LOCATION WERE ALL MADE OF TYPE 316 STAINLESS STEEL. ALTHOUGH NO RELATED TO THE FAILURE, THE ID OF THE TUBING HAD AN INTER-GRANULAR TEXTURE CONSISTENT WITH HAVING BEEN IN CONTACT WITH A CORROSIVE MEDIA. THE CAUSE OF THIS IS NOT UNDERSTOOD, AND THIS CONDITION MAY HAVE BEEN PRESENT AS-RECEIVED FROM THE MANUFACTURER.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190002 | 31989 | 2019-01-09 17:33 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-12-10 19:00 | 2018 |  |  | 32.9133 | -97.5859 | 1232643 | 2018-12-11 12:01 |  | NATURAL GAS |  | 25 | 475 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-11 06:30 | 2018-12-11 20:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-10 19:00 | 2018-12-10 20:40 | ONSHORE | TX | 76020 | RENO | PARKER | SURVEY STATION NO. | 916+16 | LINE CA | NORTH FORT WORTH TO SPRINGTOWN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.25 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR | [28 empty] | 1950 | 1950 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 191 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 2463 | 2667.989483227560768 | 130 | 185.011820330969267139479905437352245863 | 75000 | 81242.0670897552 | 11685 | 12657.51405258386016 | 0 | 0 |  |  | 89278 | 42723.3084889909504904586288416075650118 | 96752.5824458975901951394799054373522459 | [8 empty] | 356 |  | 470 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26400 | NO | [5 empty] | YES | NO LAUNCHERS | YES |  |  |  |  | YES | NO LAUNCHERS | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO |  |  |  |  | YES | [6 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | 1884483868 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 14 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | SCOTT MCCRACKEN | OPERATIONS MANAGER | benjamine.mccracken@atmosenergy.com | 817-207-2803 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT # 1232875 ON DECEMBER 10, 2018 AT 19:00, A THIRD PARTY CONTRACTOR HIT ATMOS ENERGY'S LINE CA, PUNCTURING THE LINE AND CAUSING A LEAK. THE LINE SEGMENT WAS ISOLATED AT 06:30 ON DECEMBER 11, 2018, AND A CONTROLLED GAS RELEASE WAS PERFORMED UNTIL LINE PRESSURE WAS ELIMINATED. AT THAT POINT, A TEN FOOT PIPE SEGMENT WAS REMOVED BY ATMOS ENERGY, AND APPROPRIATE REPAIRS WERE MADE. CNG RESOURCES WERE UTILIZED TO HOLD UP A SMALL RESIDENTIAL AREA AND SEVEN FARM TAP CUSTOMERS ON THE SEGMENT WERE OUT OF SERVICE DURING THE SHUTDOWN. SERVICE WAS RESTORED AT 20:30 ON DECEMBER 11, 2018. AFTER INVESTIGATION OF THE INCIDENT, IT WAS DETERMINED THAT CONTRACT LOCATOR DID NOT APPROPRIATELY MARK THE LINE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190003 | 31462 | 2019-01-10 10:16 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2018-12-12 09:50 | 2018 |  |  | 35.8487 | -87.4505 | 1232747 | 2018-12-12 11:20 |  | NATURAL GAS |  | 4529 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE UNIT WAS ALREADY SHUTDOWN. RELEASED GAS WAS THROUGH AN OPEN VENT VALVE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-12 10:09 | 2018-12-12 10:09 | ONSHORE | TN | 37137 | NUNNELY | HICKMAN | MILEPOST | VENT VALVE 1B | COMPRESSOR STATION 860 - BUILDING B | UNIT 1B VENT VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING THROUGH UNIT 1B VENT VALVE (IN PROPER OPEN POSITION) BECAUSE OF OPEN LOAD VALVE. | CLASS 3 LOCATION | NO |  | 42 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 19784 | 28155.9527186761229314420803782505910165 | 350 | 379.1296464188576 | 0 | 0 | 0 | 0 |  |  | 20134 | 18641.6782833835940101654846335697399527 | 28535.0823650949805314420803782505910165 | [8 empty] | 799 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE STATION WAS OPERATING WITHIN NORMAL RANGE PRIOR TO FALLING OFFLINE. THE CONTROLLERS DID NOT MAKE ANY SETPOINT OR OTHER HP CHANGES THAT WOULD PROMPT AN INVESTIGATION INTO THEIR ACTIONS. WHEN THE STATION FELL OFFLINE CONTROLLERS IMMEDIATELY CONTACTED THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | A SOLENOID OPERATED VALVE ACTUATOR IN THE BUILDING B SOLENOID OPERATED CONTROLS FAILED, ALLOWING THE SUPPLY PRESSURE TO OPEN THE LOAD VALVE. | [22 empty] | YES | SOLENOID OPERATED VALVE ACTUATOR FAILURE | [161 empty] | KRISTIN VAN DER LAAN | MANAGER-ENGINEERING-COMPLIANCE CODES AND STANDARDS | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR-ENGINEERING-COMPLIANCE CODES AND STANDARD | 713-369-9443 | jaime_hernandez@kindermorgan.com | TUESDAY, DECEMBER 11 (DETERMINED WEDNESDAY, DECEMBER 12, THROUGH TRENDING): A SOLENOID OPERATED VALVE ACTUATOR IN THE TENNESSEE GAS PIPELINE COMPANY (TGP) STATION 860 BUILDING B FAILED, ALLOWING THE SUPPLY PRESSURE TO OPEN THE LOAD VALVE TO BUILDING B'S COMPRESSOR UNIT 1B (UNIT 1B) UNIT 1B WAS NOT RUNNING AND WAS IN A NORMAL AVAILABLE-DEPRESSURIZE STATE AT THE TIME OF THE ACTUATOR FAILURE, NO ONE HAD BEEN IN BUILDING B ON DECEMBER 11 OR 12 PRIOR TO THE EVENT, THEREFORE THE ACTUATOR FAILURE WAS NOT DISCOVERED UNTIL DECEMBER 12. WEDNESDAY, DECEMBER 12: MORNING OF DECEMBER 12 - TECHNICIAN WAS CALIBRATING PRESSURE TRANSMITTERS IN THE STATION 860 YARD. FOLLOWING COMPANY PROCESS AND PROCEDURES, HE BYPASSED THE PRESSURE TRANSMITTERS PRIOR TO PERFORMING CALIBRATION. THE CONTROL LOGIC FOR THE STATION 860 CONTROLS QUERIED EACH TRANSMITTER FOR PRESSURES. WHEN THE COMPUTER DID NOT RECEIVE PRESSURE INFORMATION FROM THE THREE DISABLED PRESSURE TRANSMITTERS, IT ISSUED A DEFAULT PRESSURE OF 1000PSIG IN ORDER TO INITIATE A STATION SHUTDOWN DUE TO HIGH-PRESSURE CONDITION. 08:29A - STATION 860 SHUT DOWN. ALL UNITS IN BOTH BUILDINGS A AND B SHUTDOWN. 10:09A - LOCAL FIELD OPERATIONS DISCOVERED THE UNIT 1B VENT VALVE OPEN AND RELEASING GAS TO ATMOSPHERE. THE VALVE WAS IMMEDIATELY SHUT IN AND MANAGEMENT WAS NOTIFIED. 10:58A - GAS LOSS CALCULATIONS FINALIZED RESULTING IN AN ESTIMATED 4,529 MCF TOTAL UNINTENTIONAL RELEASE OF GAS. POST EVENT REPAIRS/ACTIONS: THE BUILDING B LOAD VALVE WAS PLACED IN MANUAL MODE, AND THE VENT VALVE WAS PLACED BACK IN OPERATION AND CLOSED. A NEW VALVE ACTUATOR HAS BEEN ORDERED AND REPAIRS ARE SCHEDULED FOR COMPLETION BEFORE THE END OF JANUARY 2019. BUILDING A WAS PLACED BACK IN OPERATION. POST EVENT EVALUATION - GAS RELEASE: WHEN THE UNIT 1B PLC RECEIVES THE SHUTDOWN COMMAND, IT SHUTS THE UNIT DOWN AND OPENS THE 2-INCH VENT VALVE, RELEASING THE GAS FROM UNIT 1B. IN THIS INSTANCE, THERE SHOULD NOT HAVE BEEN ANY GAS TO RELEASE BECAUSE OF THE AVAILABLE-DEPRESSURIZE STATE OF THE UNIT BUT BECAUSE THE ACTUATOR FAILURE CAUSED THE LOAD VALVE TO OPEN, THE LOAD VALVE FED GAS TO THE VENT VALVE. NOTE THAT BUILDING A CONTROL PROGRAMMING VARIES FROM BUILDING B CONTROL PROGRAMMING IN THAT BUILDING A SHUTS DOWN THE UNITS WITHOUT VENTING GAS. POST EVENT EVALUATION - STATION 860 SHUT DOWN: THE EMPLOYEE WAS FOLLOWING ESTABLISHED PROCESS AND PROCEDURE FOR CALIBRATING THE STATION TRANSMITTERS. THE SITE-SPECIFIC PROCEDURES FOR CALIBRATING THE STATION PRESSURE TRANSMITTERS DID NOT ADDRESS CONTROL SYSTEM SETTINGS WHEN BYPASSING THE PRESSURE TRANSMITTERS. THE SITE-SPECIFIC JOB PROCEDURE HAS BEEN UPDATED TO REFLECT THE ADDITIONAL CALIBRATION REQUIREMENTS PRIOR TO ACTUAL TESTING OF PRESSURE TRANSMITTERS. ADDITIONAL NOTES: 48-HOUR UPDATE NRC 1232934 PART A4 ESTIMATED BASED ON 100 MINUTES RELEASE = 4529 MCF. 3000MCF MET IN APPROX. 1 HOUR 21 MIN.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190004 | 32646 | 2019-01-11 15:44 | SUPPLEMENTAL FINAL | 288 | ALGONQUIN GAS TRANSMISSION, L.L.C. (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2018-12-13 09:38 | 2018 |  |  | 41.6432 | -72.8743 | 1232901 | 2018-12-13 14:36 |  | NATURAL GAS |  | 9.975 | 100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-09 13:30 | 2019-01-10 15:09 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-13 09:38 | 2018-12-13 10:30 | ONSHORE | CT | 06489 | SOUTHINGTON | HARTFORD | MILEPOST | 4.229 | LINE M-2 | MSYS-EOLN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 74 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1" THREADED NIPPLE | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 63 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 302 | 327.134723481414272 | 31 | 44.11820330969267139479905437352245862884 | 198467 | 214984.924388032603712 | 0 | 0 | 0 | 0 |  |  | 198800 | 95016.3821700542510785862884160756501182 | 215356.1773148237106553947990543735224586 | [8 empty] | 165 |  | 189.5 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43571 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM PUBLIC |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES THAT WOULD HAVE BEEN WITNESSED BY SCADA WOULD NOT HAVE BEEN OUTSIDE ACCEPTABLE LIMITS THEREFORE NO ALARMS WOULD HAVE BEEN RECEIVED BY THE CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [6 empty] | YES | INADEQUATE TORQUING OF NIPPLE | CONSTRUCTION | NO | [150 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1233090 AT APPROXIMATELY 9:38 AM EST ON DECEMBER 13, 2018, A GAS UTILITY COMPANY NOTIFIED ENBRIDGE OF A POSSIBLE NATURAL GAS RELEASE DISCOVERED DURING A LEAK SURVEY IN CLOSE PROXIMITY TO ALGONQUIN GAS TRANSMISSION'S (AGT) NATURAL GAS PIPELINE AT SOUTHINGTON, CONNECTICUT. ENBRIDGE PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE SITE AT ABOUT 10:30 AM EST. AGT'S INITIAL LEAK SURVEYS WAS INCONCLUSIVE BECAUSE OF THE LOW GAS LEVELS. AGT PERFORMED FURTHER TESTS WITH AN ETHANE GAS DETECTOR AND CONCLUSIVELY DETERMINED THE ORIGIN OF THE GAS RELEASE WAS FROM AGT'S PIPELINE FACILITIES AT ABOUT 2:00 PM EST. AGT PROACTIVELY MADE THE NRC CALL AT 2:36 PM EST AFTER DETERMINING THE COST OF EXCAVATION ACTIVITIES TO REPAIR THE LEAK WOULD EXCEED THE $50,000. AGT MADE EMERGENCY ONE CALL TICKETS AND REQUESTS FROM THE CITY OF SOUTHINGTON WERE PUT IN FOR EXCAVATION ACTIVITIES. AGT MOBILIZED CONTRACTORS TO BEGIN EXCAVATION ACTIVITIES AT THE SITE ON DECEMBER 14 AT ABOUT 8:00 AM. AGT UPON EXCAVATION, ENBRIDGE DETERMINED THAT THE APPARENT CAUSE OF THE LEAK WAS FROM A 1INCH THREADED NIPPLE. THE PIPE WAS REPLACED ON JANUARY 9-10, 2019. THE CAUSE OF THE RELEASE IS UNDER INVESTIGATION. SUPPLEMENTAL REPORT: THE APPARENT CAUSE IS THE 1 INCH THREADED NIPPLE WAS NOT PROPERLY TORQUED INTO THE THREAD-O-LET, RESULTING IN THE NATURAL GAS LEAK.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190005 | 34310 | 2019-01-15 16:40 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2018-12-15 14:09 | 2018 | CENTRAL | NO | 36.3705 | -85.9609 | 1233110 | 2018-12-15 15:50 | 1233260 | NATURAL GAS |  | 46436 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2018-12-15 14:19 | 2018-12-29 19:00 |  | YES | OPERATOR | 2018-12-15 14:21 | NO | [5 empty] | VALVE CLOSURE |  | 2018-12-15 14:19 | VALVE CLOSURE |  | 2018-12-15 14:47 | 12 | 2018-12-15 14:09 | 2018-12-15 17:00 | ONSHORE | TN | 37145 | PLEASANT SHADE | SMITH | MILEPOST | MP 49.147 | DIXON SPRINGS - GAINESBORO | 3100-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.281 | 42000 | API 5L | OTHER | ERW - RESISTANCE WELDED USING A DC WELDING CURRENT | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1949 | 1949 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 805 | 42 |  | CLASS 2 LOCATION | NO |  | 422 |  | NO | NO | [5 empty] | 100000 | 108322.7561196736 | 0 | 0 | 187601 | 266987.7115839243498817966903073286052009 | 2865200 | 3103663.6083408879872 | 0 | 0 | 0 | 0 |  | 4.04 | 3152801 | 1592188.33408349166925200945626477541371 | 3478974.0760444859370817966903073286052 | 0 | 0 | 0 | 1 | NO |  |  |  | 756 | 193080 | 773 | 192.619(A)(1) |  | 1999-08-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 123922 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED MAOP PRIOR TO THE FAILURE, AND THUS CONTROLLER ERROR WAS NOT THE CAUSE OF THE FAILURE. WHEN THE PRESSURE LOSS WAS OBSERVED, THE CONTROLLER PROMPTLY NOTIFIED APPROPRIATE COMPANY PERSONNEL TO RESPOND TO THE FAILURE. | [12 empty] | YES | 6 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | OTHER | THE MOST LIKELY MECHANISM FOR THE REDUCTION IN TOUGHNESS WAS HYDROGEN EMBRITTLEMENT OF THE ERW SEAM HEAT AFFECTED ZONE (HAZ.) | [11 empty] | YES | THE MOST LIKELY MECHANISM FOR THE REDUCTION IN TOUGHNESS WAS HYDROGEN EMBRITTLEMENT OF THE ERW SEAM HEAT AFFECTED ZONE (HAZ.) | UNKNOWN | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | YES | 2013 | 1025 | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 2:09 P.M. CST ON DECEMBER 15, 2018, ETNG'S 22-INCH DIAMETER LINE 3100-1 TRANSPORTING NATURAL GAS FROM DIXON SPRINGS COMPRESSOR STATION TO GAINESBORO COMPRESSOR STATION IN TENNESSEE FAILED AT MP 49.147. THE FAILED PIPE IS 22 INCH DIAMETER BY 9/32 INCH WALL THICKNESS, X-42. THE FAILURE RESULTED IN A RUPTURE WITHOUT FIRE. THERE WERE NO INJURIES OR FATALITIES. APPROXIMATELY 12 RESIDENTS EVACUATED UNTIL LOCAL EMERGENCY RESPONDERS OPENED ACCESS TO THE AREA. THE COMPRESSOR UNITS AT THE DIXON SPRINGS COMPRESSOR STATION WERE SHUTDOWN REMOTELY BY THE CONTROL ROOM AT 2:19 PM CST. THE ESD AT THE DIXON SPRING COMPRESSOR STATION WAS ACTIVATED AT 2:56 PM CST. THE MLV AT GAINESBORO COMPRESSOR STATION WAS CLOSED AT 2:47 PM CST FOLLOWED BY ESD ACTIVATION, COMPLETING INITIAL ISOLATION OF THE FAILURE SITE. ETNG PERSONNEL WERE ALSO DISPATCHED TO CLOSE THE MAINLINE BLOCK VALVES IMMEDIATELY DOWNSTREAM OF THE FAILURE SITE WHICH WAS CLOSED AT APPROXIMATELY 4:30 PM CST. ETNG PERSONNEL ARRIVED AT THE FAILURE SITE AT APPROXIMATELY 5:00 PM CST. THE NRC WAS NOTIFIED AT 3:50 PM CST, AS SOON AS LOCATION INFORMATION FOR THE FAILURE SITE WAS AVAILABLE. THE LINE WAS REPLACED, TESTED, AND SUBSEQUENTLY PUT IN-SERVICE ON DECEMBER 29, 2018. A 3RD PARTY METALLURGICAL INVESTIGATION IS ONGOING. THE ROOT CAUSE IS PENDING. SUPPLEMENTAL REPORT 09/27/2020 THE FAILURE HAS BEEN DETERMINED TO BE DUE TO A RELATIVELY SMALL 0.09' DEEP X 0.44' LONG HYDROGEN INDUCED CRACK IN THE ERW SEAM HEAT AFFECTED ZONE AT A LOCATION WHERE HYDROGEN EMBRITTLEMENT HAD REDUCED THE MATERIAL TOUGHNESS TO A LEVEL SUCH THAT THE PIPE COULD NOT WITHSTAND RUPTURE AT MOP.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190006 | 31535 | 2019-01-23 14:43 | ORIGINAL FINAL | 15259 | UGI PENN NATURAL GAS | 1 UGI DRIVE | DENVER | PA | 17517 | 2018-12-23 08:06 | 2018 |  |  | 41.4739 | -75.5452 | 1233820 | 2018-12-23 17:12 |  | NATURAL GAS |  | 9200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-12-23 08:56 | 2018-12-23 11:49 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-23 08:06 | 2018-12-23 08:42 | ONSHORE | PA | 18434 | JESSUP | LACKAWANNA | MILEPOST | LEC METER | UGI METER AT LACKAWANNA ENERGY CENTER | UNIONDALE 16 PEI - MARSHWOOD | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2017 |  | CARBON STEEL |  | OTHER | [8 empty] | THE FACILITY INVOLVED WAS UGI'S OVER PRESSURE PROTECTION DEVICE WHICH WAS A 10"X12" RELIEF VALVE. THE RELIEF VALVE VENTED EXCESS GAS BUT DID NOT RE-SEAT ITSELF. | CLASS 3 LOCATION | YES | METHOD2 | 352 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 36000 | 51234.0425531914893617021276595744680851 | 3700 | 4007.9419764279232 | 2000 | 2166.455122393472 | 0 | 0 |  |  | 41700 | 36340.9288015277508808510638297872340426 | 57408.4396520128845617021276595744680851 | [8 empty] | 684 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIONS OF THE CONTROLLER(S) DID NOT LEAD TO THIS INCIDENT NOR COULD HAVE PREVENTED THIS INCIDENT FROM OCCURRING. CONTROLLERS TOOK PROPER ACTIONS IN REACTING TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | JOHN D. TOUMEH | SENIOR ENGINEER | jtoumeh@ugi.com | 717 675 4606 |  |  |  |  | HANS G. BELL | CHIEF OPERATIONS OFFFICIER | 610 796 3450 | hbell@ugi.com | UGI UTILITIES, INC. (UGI) PROVIDES NATURAL GAS SERVICE TO A LARGE END USE CUSTOMER, THE LACKAWANNA ENERGY CENTER IN JESSUP, PA. UGI OPERATES MEASUREMENT AND REGULATION FACILITIES WHICH ARE LOCATED ON CUSTOMER'S PREMISES. WHILE THE CUSTOMER WAS PERFORMING TESTING OF ITS UTILIZATION EQUIPMENT, THE CUSTOMER'S EMERGENCY SHUTDOWN SYSTEM ACTIVATED, WHICH TRIGGERED THE ABRUPT CLOSURE OF A CUSTOMER OWNED VALVE LOCATED JUST DOWNSTREAM FROM THE UGI REGULATION FACILITIES. THE ABRUPT SHUTDOWN CAUSED A PRESSURE SPIKE AND THE UGI OVER-PRESSURE PROTECTION RELIEF VALVE OPENED TO RELIEVE EXCESS NATURAL GAS. WHEN PRESSURE WAS REDUCED, THE RELIEF DEVICE FAILED TO RE-SEAT AND CONTINUED TO VENT NATURAL GAS UNTIL THE REGULATOR STATION WAS ISOLATED THROUGH AN UPSTREAM STATION VALVE. ONCE ISOLATED, THE RELIEF WAS INSPECTED AND DAMAGE TO THE INTERNAL WEARING PARTS WAS REPAIRED. UGI HAS WORKED WITH THE CUSTOMER TO IMPROVE EMERGENCY SHUT-DOWN PROTOCOLS TO MINIMIZE THE POTENTIAL OF OVER-PRESSURE PROTECTION ACTIVATION. ADDITIONALLY, UGI IS IMPLEMENTING FACILITY MODIFICATIONS TO IMPROVE OVER-PRESSURE PROTECTION SYSTEM PERFORMANCE. AFTER THE SITUATION WAS MADE SAFE AND IMMEDIATE HAZARDS WERE MITIGATED, UGI PROCEEDED TO CALCULATE THE AMOUNT OF GAS RELEASED. ONCE UGI DETERMINED THAT THE GAS RELEASED EXCEEDED 3,000 MCF, A CALL WAS MADE TO THE NRC.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190007 | 31556 | 2019-01-25 09:30 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2018-12-27 08:00 | 2018 |  |  | 34.004 | -93.8662 | 1234021 | 2018-12-27 11:51 |  | NATURAL GAS |  | 200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STOPPLES WERE INSTALLED WITH NEW PIPE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-27 08:00 | 2018-12-27 09:15 | ONSHORE | AR | 71852 | NASHVILLE | HOWARD | MILEPOST | ROAD CROSSING | AM-165 | AM-165 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.125 | 35000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | MILL WRAP | [27 empty] | 1963 | 1963 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 62 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 834 | 1186.921985815602836879432624113475177305 | 167000 | 180899.002719854912 | 3000 | 3249.682683590208 | 0 | 0 |  |  | 170834 | 82018.141561055354751773049645390070922 | 185335.6073892607228368794326241134751773 | [8 empty] | 120 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 53741 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 | 405 246 9273 |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 12-27-2018, A NATURAL GAS LEAK WAS REPORTED ON ENABLE GAS TRANSMISSION LINE AM-165. THE LEAK WAS REPORTED TO BE COMING FROM A CASING VENT ON MOUNT PLEASANT DRIVE NEAR NASHVILLE, AR IN HOWARD COUNTY. THE PIPELINE WAS EXCAVATED ON BOTH SIDES OF THE ROAD AND NO SOLUTIONS FOR REPAIR WERE FOUND AS THE LEAK APPEARED TO BE INSIDE THE CASING. PLANS WERE INITIATED TO COMPLETE A BORE ACROSS THE ROAD AND TIE IN WITH STOPPLE FITTINGS. THE ROAD WAS CLOSED AND MANNED DURING THE REPAIR EFFORTS. THE BORE AND TIE-IN WERE COMPLETED ON 12-29-2018. UPON COMPLETION OF THE CONSTRUCTION, PIPING WAS REMOVED FROM THE CASING AND EXAMINED TO DETERMINE A CAUSE OF THE LEAK. THE CASING AND PIPE HISTORY WERE EVALUATED AND DID NOT HAVE A HISTORY OF BEING SHORTED AND THE PIPELINE HAD MET THE ESTABLISHED -.850 V POLARIZED POTENTIAL CRITERIA. UPON EXAMINATION OF THE PIPE, THERE WAS EVIDENCE OF LIGHTNING DAMAGE. THIS WAS IDENTIFIED BY METAL PUDDLING AND SPLATTER AT THE SITE OF THE LEAK. THE SURROUNDING PIPELINE SYSTEM WAS EVALUATED FOR ANY ADDITIONAL EFFECTS OF THE LIGHTNING AND NO OTHER DAMAGE WAS FOUND. AN INITIAL CALL WAS PLACED TO THE NRC ON 12/27 (#1234021) AND A 48 HOUR FOLLOW UP WAS PROVIDED ON 12/29 (#1234159). DURING THE 48 HOUR FOLLOW UP 3.1 MMCF WAS PROVIDED AS THE ESTIMATED VOLUME OF COMMODITY RELEASED. THIS ESTIMATE WAS CALCULATED USING A 1/2" HOLE AT 120 PSIG FOR 96 HOURS (EXPECTED TIME FOR COMPLETION). AFTER COMPLETION OF THE NEW BORE THE OLD CARRIER PIPE AND CASING WERE REMOVED AND IT WAS DISCOVERED THAT THE SIZE OF THE HOLE TO BE 1/8". THE LENGTH OF THE TIME OF GAS LOSS WAS SHORTER THAN INITIALLIY CALCULATED (56 HOURS INSTEAD OF 96). WHEN REPLACING 1/2" WITH AN 1/8", AND 96 HOURS WITH 56 THE GAS LOSS WAS LOWERED FROM 3.1 MMCF TO 200 MCF 1/28/2019 SUPPLEMENTAL REPORT PART E. 1 CHANGED ESTIMATED PRESSURE AT THE POINT AND TIME OF THE INCIDENT FROM 400 PSIG TO 120 PSIG. PART H ADDITIONAL DETAIL AROUND GAS LOSS CALCULATION FOR INCIDENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190008 | 31567 | 2019-01-29 15:05 | ORIGINAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-01-10 14:30 | 2019 |  |  | 38.8486 | -79.3761 | 1234982 | 2019-01-10 14:40 |  | NATURAL GAS |  | 14230 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-10 13:05 | 2019-01-10 18:18 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-10 12:59 | 2019-01-10 12:59 | ONSHORE | WV | 26884 | SENECA ROCKS | PENDLETON | MILEPOST | 00+00 | SENECA ROCKS COMPRESSOR STATION | COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM (ESD) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUT SYSTEM (ESD) VALVE DID NOT CLOSE AS DESIGNED ALLOWING AN EXCESSIVE VOLUME OF GAS TO BE RELEASED OUT THE BLOW-OFF PIPE TO THE ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 891 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 48382 | 76446.0997375328083989501312335958005249 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 48382 | 50159.8162729658792650918635170603674541 | 76446.0997375328083989501312335958005249 | [8 empty] | 862 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PERSONNEL AT THE COMPRESSOR STATION WERE PRESENT WHEN THE STATION'S EMERGENCY SHUTDOWN SYSTEM ACTIVATED THUS THE CONTROL ROOM WAS NOT INVOLVED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | STATION ESD VALVE DID NOT PROPERLY CLOSE AFTER UNINTENTIONAL ESD ACTIVIATION | [161 empty] | CHRIS LEGG | US REGULATORY SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER TC-EAST | 304-357-3728 | george_hamaty@transcanada.com | ON JANUARY 10, 2019, AT 12:59 PM WHILE SETTING UP THE VALVE INDICATION, AN ELECTRICAL SHORT OCCURRED THAT CAUSED A RAPID DEGRADATION OF AN ELECTRICAL FUSE THAT WAS LINKED TO THE ESD SYSTEM. THIS NEW VALVE (NUMBER C7-273) WAS INSTALLED AS PART OF 2018-2019 WBX PROJECT. THE BLOWN FUSE CAUSED THE STATION TO ACTIVATE THE EMERGENCY SHUTDOWN SYSTEM (ESD). AFTER A PROLONGED BLOW DOWN, IT WAS DISCOVERED THAT VALVE 3029(STATION FIRE VALVE) DID NOT OPERATE/CLOSE. A PRELIMINARY INVESTIGATION INDICATED THE VALVE DID NOT CLOSE DUE TO ICE BUILDUP IN THE ACTIVATION SWITCH. BECAUSE VALVE 3029 DID NOT CLOSE DURING THE ESD, AN EXCESSIVE AMOUNT OF GAS WAS EVACUATED. GAS LOSS WAS APPROXIMATELY 14,230 MCF. NO FIRE OR EXPLOSIONS, DEATHS, INJURIES OR EVACUATIONS OCCURRED AS A RESULT OF THE RELEASE. GAS WAS RELEASE THROUGH DESIGNED ESD BLOW-OFF STACKS/PIPES TO THE ATMOSPHERE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190009 | 31641 | 2019-01-29 16:58 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-01-20 04:10 | 2019 |  |  | 38.4018 | -81.4172 | 1235614 | 2019-01-20 04:17 |  | NATURAL GAS |  | 5129 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE RELIEF VALVE WAS ISOLATED BUT THE STATION CONTINUED TO OPERATE/RUN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-20 03:19 | 2019-01-20 03:19 | ONSHORE | WV | 25071 | ELKVIEW | KANAWHA | MILEPOST | 00+00 | COCO COMPRESSOR STATION | STATION GAS SUCTION/WITHDRAW HEADER PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL ACTIVATION OF A RELIEF VALVE | CLASS 1 LOCATION | NO |  | 891 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 17439 | 27554.5354330708661417322834645669291339 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 17439 | 18079.8031496062992125984251968503937008 | 27554.5354330708661417322834645669291339 | [8 empty] | 781 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIVATION OF A RELIEF VALVE RESULTING IN A GAS RELEASE DID NOT INVOLVE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | ICE IN THE PILOT SENSING DEVICE | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER - US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@transcanada.com | ON 01/20/2019, AN 8" RELIEF VALVE AT COCO COMPRESSOR STATION UNINTENTIONALLY ACTIVATED AND RELEASED A REPORTABLE QUANTITY (5,129 MCF) OF NATURAL GAS TO THE ATMOSPHERE. THE RELIEF VALVE IS LOCATED ON THE 36" SUCTION HEADER OF THE STATION AND ACTS AS A TERTIARY OVERPRESSURE-PRESSURE PROTECTION (OPP) DEVICE. THE FIRST AND SECOND OPP DEVICES DID NOT ACTIVATE. THE CAUSE OF THE RELEASE WAS INVESTIGATED. ICE BUILD-UP IN THE PRESSURE SENSING LINES (PILOT)CREATED A DIFFERENTIAL IN PRESSURE CAUSING THE RELIEF VALVE TO OPEN. NO FIRE, EXPLOSION, DEATHS, INJURIES OR EVACUATIONS OCCURRED AS A RESULT OF THE RELEASE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190010 | 31640 | 2019-01-30 15:21 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-01-21 03:40 | 2019 |  |  | 38.4771 | -81.7106 | 1235670 | 2019-01-21 05:43 |  | NATURAL GAS |  | 5406 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE EMERGENCY SHUTDOWN VALVE WAS ISOLATED BUT THE STATION CONTINUED TO RUN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-21 03:43 | 2019-01-21 04:45 | ONSHORE | WV | 25159 | CHARLESTON | KANAWHA | MILEPOST | 00+00 | LANHAM COMPRESSOR STATION | CABOT EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | ESD VALVE (#C9-149) |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | EMERGENCY SHUTDOWN SYSTEM VALVE | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL/EQUIPMENT FAILURE OF AN EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE | CLASS 1 LOCATION | NO |  | 857 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 18380 | 29041.3648293963254593175853018372703412 | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | 18380 | 19055.3805774278215223097112860892388451 | 29041.3648293963254593175853018372703412 | [8 empty] | 742 |  | 920 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE ESD VALVE FAILURE DID NOT INVOLVE THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ICE BUILD-UP IN THE VALVE ACTUATOR/TRIGGER DEVICE | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@transcanada.com | 304-545-4350 |  |  |  |  | GEORGE HAMATY | MANAGER - US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@transcanada.com | ON 01/21/2019 AT 3:40 AM EST, AT LANHAM COMPRESSOR STATION, LOCATED IN CHARLESTON, WV, KANAWHA COUNTY, AN EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE (C9-149) MALFUNCTIONED AND OPENED RELEASING NATURAL GAS TO THE ATMOSPHERE. THE OPERATING PRESSURE OF THE PIPING AT THE TIME OF THE RELEASE WAS 742 PSIG (920 MAOP). THE GAS WAS RELEASED THROUGH A 4" ESD BLOWOFF STACK IN A DESIGNED/SAFE LOCATION. THE PUBLIC HEARD THE GAS RELEASE AND NOTIFIED THE MONITORING CENTER, PART OF THE CONTROL ROOM AT 3:43 AM. OPERATIONS PERSONNEL WERE CALLED TO THE SCENE, ARRIVING AT 4:45 AM AND MANUALLY ISOLATED THE VALVE AT APPROX. 5:00 AM, AS THE REST OF THE STATION CONTINUED TO RUN. THE GAS VOLUME THAT WAS RELEASED WAS CALCULATED AT 5,406 MCF. NO DEATHS, INJURIES, FIRE, EXPLOSION OR EVACUATIONS RESULTED FROM THE RELEASE. THE PRELIMINARY INVESTIGATION OF THE FAILURE DETERMINED ICE HAD ACCUMULATED IN THE VALVE CONTROLLER/TRIGGER DEVICE CAUSING THE VALVE TO ACTUATE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190011 | 32162 | 2019-01-31 16:22 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-01-03 18:13 | 2019 |  |  | 35.3966 | -110.3354 | 1234503 | 2019-01-03 20:04 |  | NATURAL GAS |  | 7663 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-03 18:13 | 2019-01-04 07:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-03 18:13 | 2019-01-03 19:06 | ONSHORE | AZ | 86047 | Not Within a Municipality | NAVAJO | MILEPOST | VALVE: 20 1/2 | DILKON COMPRESSOR STATION | DILKON COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | LOW POWER GAS PRESSURE | [5 empty] | CLASS 1 LOCATION | NO |  | 619 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 21529 | 34016.9501312335958005249343832020997375 | 4600 | 4883.6680291451946 | 50 | 53.08334814288255 | 0 | 0 |  |  | 26179 | 24497.997497069573717454068241469816273 | 38953.7015085216729505249343832020997375 | [8 empty] | 556 |  | 894 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | LOW POWER GAS PRESSURE TO POWER THE VALVE ACTUATOR. | [147 empty] | JORGE LOPEZ | ENGINEER COMPLIANCE CODES AND STANDARDS | jorge_lopez@kindermorga.com | 7016096218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JANUARY 3, 2019, A FIRE EYE ALARM AT DILKON COMPRESSOR STATION RESULTED IN A STATION ESD. A NORMAL ESD OPERATION AT THIS FACILITY WOULD NOT HAVE MET THE DOT/PHMSA REPORTABLE RELEASE VOLUME OF 3,000 MCF. AT THE TIME OF THE ESD NO UNITS AT THE STATION WERE RUNNING AND THE STATION VALVES WERE OPEN. DURING THE ESD OPERATION GAS VENTED THROUGH A 4" BRANCH CONNECTION THROUGH A VENT VALVE. AS PART OF OUR INVESTIGATION IT WAS DETERMINED THAT THE ACTUATOR ON THE STATION DISCHARGE VALVE DID NOT CLOSE COMPLETELY DUE TO LOW POWER GAS PRESSURE. THE INCOMPLETE VALVE CLOSURE IS WHAT CAUSED THE GAS TO VENT FOR A LONGER PERIOD OF TIME AND EVENTUALLY SURPASSED THE REPORTABLE QUANTITY OF 3,000 MCF. AT 18:13 KM TECHNICIAN WAS DISPATCHED TO THE SITE BY GAS CONTROL AND ARRIVED AT 19:06 WHERE HE VISUALLY DISCOVERED THE GAS VENTING AND CONFIRMED A FALSE FIRE ALARM. THE EMPLOYEE THEN PROCEEDED TO MANUALLY CLOSE THE DISCHARGE VALVE AT 19:20. AN ERL CALL WAS HELD AT 19:50 WHERE THE GAS LOSS WAS ESTIMATED TO EXCEED THE REPORTING THRESHOLD. CODES AND COMPLIANCE REPORTED THIS EVENT PRIOR TO THE 1 HOUR DEADLINE FROM CONFIRMED DISCOVERY. TOTAL GAS LOSS VOLUME WAS UNKNOWN AT THE TIME INCIDENT WAS INITIALLY REPORTED TO NRC, OPERATIONS CALCULATED THE GAS LOSS AT 10,404 MCF FOR THE 48HR NRC UPDATE. AS PART OF OUR INVESTIGATION AFTER FURTHER REVIEW BY KINDER MORGAN MEASUREMENT SME'S THE TOTAL GAS LOSS WAS CALCULATED AT 7,663 MCF. THE POWER GAS FOR THIS ACTUATOR COMES FROM A BURIED PRESSURE BOTTLE FED BY THE SUCTION SIDE OF THE PLANT DOWNSTREAM OF THE STATION SUCTION VALVE. NORMALLY THIS BURIED BOTTLE HAS PLENTY OF PRESSURE TO CLOSE ALL REQUIRED VALVES, BUT IN THE EVENING HOURS OF JANUARY 3RD THE MAINLINE HAD LOWER THAN NORMAL OPERATING PRESSURE. WHEN THE STATION EXPERIENCED AN ESD THE PRESSURE IN THE BOTTLE WAS NOT SUFFICIENT TO CLOSE THE STATION DISCHARGE VALVE. ON JANUARY 4TH EMPLOYEES RETURNED THE STATION TO SERVICE AT 07:22, INCLUDING RESTORING PRESSURE TO THE UNDERGROUND ESD STORAGE BOTTLE BY 07:45, CLEARED THE ESD ALARMS, AND TESTED THE VALVE ACTUATOR WHICH WORKED AS DESIGNED AND HAD APPROPRIATED GAS PRESSURE TO OPERATE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190012 | 32865 | 2019-02-05 15:27 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2018-12-30 00:22 | 2018 |  |  | 42.7645 | -83.903 | 1234214 | 2018-12-30 09:59 |  | NATURAL GAS |  | 14700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOCK VALVE FOR RELIEF SHUT-OFF | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-12-30 00:22 | 2018-12-30 01:15 | ONSHORE | MI | 48855 | DEERFIELD TOWNSHIP | LIVINGSTON COUNTY | MILEPOST | MLV 9 | C PIPELINE | 8,000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | SUSPECTED MECHANICAL FAILURE OF THE PILOT CONTROL FOR THE RELIEF VALVE | CLASS 1 LOCATION | NO |  | 645 |  | NO | NO | NO |  |  |  |  | 110 | 119.15503173164096 | 0 | 0 | 47775 | 67991.8439716312056737588652482269503546 | 15000 | 16248.41341795104 | 200 | 216.6455122393472 | 0 | 0 |  |  | 63085 | 51928.908688747008963546099290780141844 | 84576.0579335532338337588652482269503546 | [8 empty] | 722 |  | 844 | OTHER | 192.611(A)(1)(I) |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY BEING MONITORED WOULD NOT HAVE PROVIDED AN INDICATION THAT SOMETHING WAS WRONG. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | BREAK DOWN OF THE DIAPHRAGM GASKET | [161 empty] | FRENAE SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | DTE GAS DISPATCH RECEIVED A CALL FROM A CUSTOMER AT 00:22 OF AN ODOR IN AIR NEAR MAIN LINE VALVE 9 AT E. COHOCTAH RD. AND LUTZ RD. GAS DISPATCH CONTACTED GAS CONTROL AND THEY CONTACTED OPERATIONS. OPERATIONS SENT AN EMPLOYEE TO MLV 9 TO INVESTIGATE AND THE EMPLOYEE DISCOVERED THE RELIEF VALVE NORTH OF MLV 9 ON THE C LINE RELIEVING GAS TO ATMOSPHERE. THE TECHNICIAN CLOSED THE BLOCK VALVE UNDER THE RELIEF VALVE TO STOP THE BLOWING GAS. THE TECHNICIAN DID NOT OBSERVE ANY APPARENT PHYSICAL DAMAGE TO THE RELIEF. THE C LINE (MAOP 844) WAS MADE "COMMON" WITH THE A & B LINES (MAOP 811) AND THE ALARM POINT FOR THE C LINE WAS LOWERED TO 811 THUS PROTECTING THE C LINE UNTIL PERMANENT REPAIRS CAN BE MADE. THE CAUSE OF FAILURE (RELIEF VALVE) WAS DUE MATERIAL FAILURE. A NEW VALVE WAS INSTALLED ON 5/29/2019 AND THE C-LINE WAS RETURNED TO SERVICE WITH AN ALARM POINT AT 844 MAOP.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190013 | 32616 | 2019-02-07 15:06 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-01-08 14:34 | 2019 |  |  | 30.459 | -93.1459 | 1234847 | 2019-01-08 15:20 |  | NATURAL GAS |  | 112.8 | 41 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS STATION WAS CURRENTLY NOT RUNNING. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-08 14:34 | 2019-01-08 14:34 | ONSHORE | LA | 70657 | RAGLEY | BEAUREGARD PARISH | MILEPOST | 64.4 | GILLIS COMPRESSOR STATION | GILL-OPEL | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 2 |  | 0.218 | 35000 | ASTM A106 | SEAMLESS |  | VALLOUREC | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2017 | 2016 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 42 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 130 | 138.01670517149463 | 358 | 565.658792650918635170603674540682414698 | 250000 | 265416.74071441275 | 0 | 0 | 0 | 0 |  |  | 250488 | 117523.7432686516820894225721784776902887 | 266120.4162122351632651706036745406824147 | [8 empty] | 855 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF THE LEAK WAS MINIMAL TO BE DETERMINED BY CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | BASED ON THE METALLURGICAL TESTING, ASSESSMENT OF THE SITE AND REVIEW OF THE RADIOGRAPHIC REPORT IT WAS DETERMINED THAT THE TWO PIPES SETTLED IN DIFFERENT DIRECTIONS CAUSING A STRESS CONCENTRATION AT THIS POINT. | NO | [306 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1234963 AT APPROXIMATELY 2:34 PM CST ON JANUARY 8, 2019, AN ENBRIDGE EMPLOYEE DISCOVERED A NATURAL GAS RELEASE BELOW GROUND AT THE GILLIS COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN BEAUREGARD PARISH, LA. THE LEAK WAS LOCATED NEAR THE INLET OF A FILTER SEPARATOR. THE FILTER SEPARATOR WAS ISOLATED AND BLOWN DOWN ON JANUARY 8, 2019, AND IT REMAINED ISOLATED UNTIL REPAIR WAS COMPLETE. THE APPARENT CAUSE IS UNDER INVESTIGATION. THE 2 INCH PIPE WAS REPLACED AND ADDITIONAL PIPE SUPPORTS WERE INSTALLED. SUPPLEMENTAL REPORT (08/26/2019) TETLP PERFORMED METALLURGICAL TESTING OF THE PIPE AND THE RESULTS DID NOT IDENTIFY ANY ROOT CAUSE. IN ADDITION, THE RADIOGRAPH FILM WAS REVIEWED BY AN ASNT LEVEL III. THE RADIOGRAPH WAS FREE OF DEFECTS AND MET API 1104. BASED ON THE METALLURGICAL TESTING PERFORMED, ASSESSMENT OF THE SITE AND REVIEW OF THE RADIOGRAPHIC REPORT IT WAS DETERMINED THAT THE CAUSE OF THE LEAK WAS THE TWO PIPES SETTLING IN DIFFERENT DIRECTIONS CAUSING A STRESS CONCENTRATION AT THIS POINT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190014 | 31704 | 2019-02-13 14:31 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-01-18 13:45 | 2019 |  |  | 33.4618 | -94.3726 | 1235534 | 2019-01-18 15:50 |  | NATURAL GAS |  | 5 | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-18 14:20 | 2019-01-22 23:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-18 13:45 | 2019-01-18 13:45 | ONSHORE | TX | 75570 | NEW BOSTON | BOWIE | MILEPOST | CM-22 | CM-22 | CM-22 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  | YES | CASED | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.237 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1953 | 1953 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 44 |  | NO | NO | NO |  |  |  |  | 1000 | 1061.666962857651 | 40 | 42.46667851430604 | 20 | 31.60104986876640419947506561679790026247 | 170000 | 180483.38368580067 | 10000 | 10616.66962857651 | 0 | 0 |  |  | 181060 | 84813.8609077810026996325459317585301837 | 192235.7880056179034441994750656167979003 | [8 empty] | 220 |  | 250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1165 | NO |  | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | PINHOLE LEAK IN WELD | [13 empty] | YES | [62 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 1/18/2019 ENABLE MIDSTREAM O&M TECHNICIANS WERE IN THE NEW BOSTON, TEXAS AREA PERFORMING MAINTENANCE AND NOTICED A SLIGHT GAS ODOR WHILE TRAVELING DOWN TEXAS STATE HIGHWAY 82. DUE TO CM-22 (4') BEING IN THE AREA, THE TECHNICIANS PERFORMED AN INSPECTION OF THE AREA USING GAS DETECTION EQUIPMENT. IT WAS CONFIRMED THAT CM-22 WAS LEAKING WITHIN A CASED RAILROAD CROSSING PARALLEL TO US HWY 82 NEAR NEW BOSTON TEXAS. THE TEAM CLOSED THE HWY TEMPORARILY WHILE THE LINE WAS ISOLATED AND BLOWN DOWN. THE ROAD WAS CLOSED AT 2:20 PM AND REOPENED AT 4:30 PM. A NEW BORE WAS PERFORMED AND THE FINAL TIE-INS WERE COMPLETED 1/22/2019. WHEN THE CARRIER PIPE WAS REMOVED THE PIPE WAS THOROUGHLY CLEANED AND INSPECTED, AND NO CORROSION WAS OBSERVED ON THE PIPE. DUE TO THIS, IT IS ASSUMED THERE IS A SMALL PINHOLE LEAK IN A WELD SOMEWHERE ON THE PIPE. THE PIPE WILL HAVE END CAPS WELDED ON AND PRESSURED UP TO DETERMINE WHERE THE LEAK IS COMING FROM. AN INITIAL CALL WAS PLACE TO THE NRC ON 1/18/2019 @ 16:50 (NRC# 1235534) AND A 48 HOUR FOLLOW UP WAS PLACED ON 1/20/2019 @ 08:26 (NRC# 1235618). A SUPPLEMENTAL REPORT WILL BE PROVIDED WHEN TESTING AND FINAL CONSTRUCTION COSTS ARE COMPLETED. 2/26/2019 SUPPLEMENTAL D.7.B CHANGED FROM $85,000 TO $170,000 D.7.C CHANGED FROM $500 TO $10,000 NARRATIVE - A THOROUGH REVIEW OF THE PIPE WAS PERFORMED AND CORROSION DEFECTS WERE NOT FOUND. THERE IS HIGH CONFIDENCE THAT THE LEAK IS DUE TO A PINHOLE IN A WELD AND WE WILL NOT BE MOVING FORWARD WITH WELDING THE PIPE BACK TOGETHER AND HYDROTESTING.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190015 | 32062 | 2019-02-15 10:42 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-01-18 03:55 | 2019 |  |  | 40.1173 | -104.6089 | 1235460 | 2019-01-18 02:04 |  | NATURAL GAS |  | 3282 | 96.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-18 04:17 | 2019-01-18 15:06 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-17 23:55 | 2019-01-18 01:18 | ONSHORE | CO | 80642 | Not Within a Municipality | WELD | MILEPOST | MP 63 +563 | L0250A HIGH PLAINS MAIN LINE | STA 250-A HUDSON | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | OTHER BUTT WELD | [18 empty] | 2013 |  | CARBON STEEL |  | LEAK |  |  | OTHER | WELD FAILURE. | [5 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 337 | 357.781766483028387 | 11516 | 18195.8845144356955380577427821522309711 | 5000 | 5308.334814288255 | 500 | 530.8334814288255 | 700 | 743.1668740003557 | METALLURGICAL LABORATORY ANALYTICAL COST. |  | 18053 | 15000.87389563908734341994750656167979 | 25136.0014506361601250577427821522309711 | [8 empty] | 817 |  | 1200 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM A 3RD-PARTY OIL AND GAS OPERATOR WORKING NEAR THE LOCATION. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS OR CONTROL ROOM ISSUES WERE DETERMINED TO BE A CAUSE OR CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION | [23 empty] | YES | HIGH-CYCLE, LOW STRESS, UNIDIRECTIONAL BENDING FATIGUE. | [55 empty] | NO | [63 empty] | YES |  |  | NO | [13 empty] | NO | [63 empty] | STEPHEN R. DINES | ENGINEER - CODES AND STANDARDS | stephen_dines@kindermorgan.com | (719) 329-5633 |  |  |  |  | JAIME A. HERNANDEZ | DIRECTOR ENGINEERING - CODES AND STANDARDS | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON JANUARY 17, 2019 AT APPROXIMATELY 11:55 PM LOCAL TIME, COLORADO INTERSTATE GAS (CIG) GAS CONTROL RECEIVED A TELEPHONE CALL FROM A THIRD-PARTY OIL AND GAS OPERATOR REPORTING A SOUND OF GAS RELEASING FROM OUR PIPELINE FACILITY AT THE L250A PIG LAUNCHER AND PIG RECEIVING FACILITY IN WELD COUNTY, COLORADO. UPON RECEIVING THE THIRD-PARTY REPORT, GAS CONTROL CALLED THE CIG AREA SUPERVISOR AND DISPATCHED HIM TO THE LOCATION. HE ARRIVED ON SITE AT 1:18 AM LOCAL TIME ON JANUARY 18, 2019 AND VERIFIED THAT THE GAS LEAK WAS IN FACT ON THE CIG L250 PIPELINE PIG TRAP FACILITY. AT 1:50 AM LOCAL TIME ON JANUARY 18, 2019, CIG INITIATED AN INTERNAL EMERGENCY-RESPONSE-LINE (ERL) TELEPHONE CALL TO DISCUSS THE AVAILABLE INFORMATION REGARDING THE GAS LEAK TO DETERMINE WHETHER DISCOVERY OF A REPORTABLE EVENT OCCURRED. SINCE THE 250A SEGMENT IMPACTED BY THE LEAK COULD NOT BE IMMEDIATELY ISOLATED UNTIL ALTERNATIVE GAS SUPPLIES FOR CIG'S CUSTOMERS SERVED FROM THAT SEGMENT COULD BE ARRANGED, CIG DECIDED TO ASSUME THE RELEASE VOLUMES WOULD EXCEED THE REPORTABLE THRESHOLD AND DECIDED TO NOTIFY THE NATIONAL RESPONSE CENTER (NRC) OF THE EVENT PRIOR TO ESTABLISHING THE ACTUAL VOLUMES RELEASED. IT WAS NOT UNTIL THE AFFECTED SEGMENT CONTAINING THE LEAK COULD BE ISOLATED AT 4:17 AM ON JANUARY 18, 2019, THAT CIG WAS ABLE TO ESTIMATE THE ACTUAL RELEASE VOLUME. DURING THE INITIAL INVESTIGATION, CIG CALCULATED THE TOTAL RELEASE VOLUME (3,282 MCF) AND DETERMINED IT HAD MET THE REPORTING REQUIREMENT FOR THE EVENT AT 3:55 AM ON JANUARY 18, 2019. THE NRC WAS NOTIFIED AT 2:04 AM LOCAL TIME ON JANUARY 18, 2019 (NRC NO. 1235460) OF THE GAS RELEASE WITH AN ESTIMATE TO BE GREATER THAN 3,000 MCF AND RESULTING IN A REPORTABLE EVENT. THE NRC LOGGED RECEIPT OF THE REPORT AT 2:09 AM LOCAL TIME. A COURTESY NOTIFICATION TO THE PHMSA INCIDENT INVESTIGATION TEAM WAS PROVIDED AT 2:38 AM LOCAL TIME THAT DAY. AT 3:06 PM LOCAL TIME ON JANUARY 18, 2019, ALL REPAIRS TO THE FACILITIES WERE COMPLETE AND RETURNED TO SERVICE. AT 3:54 PM LOCAL TIME ON JANUARY 18, 2019, A 48-HOUR UPDATE REPORT WAS CALLED INTO THE NRC (REPORT NO. 1235523) PROVIDING THE TOTAL VOLUME OF THE RELEASE (3,282 MCF) WITH CONFIRMATION THAT THERE WERE NO CUSTOMER IMPACTS DUE TO THE INCIDENT. THE NRC LOGGED THE RECEIPT OF THE REPORT AT 14:02 LOCAL TIME. THE 1' BLOW-OFF VALVE ASSEMBLY THAT FAILED WAS SENT FOR A COMPLETE METALLURGICAL ANALYSIS TO DETERMINE THE ROOT CAUSE OF THE FAILURE. FROM THE METALLURGICAL ANALYSIS, IT WAS DETERMINED THE ROOT CAUSE OF THE BUTT WELD FAILURE WAS CAUSED BY HIGH-CYCLE, LOW NOMINAL STRESS, UNIDIRECTIONAL-BENDING FATIGUE. OPERATIONS FIELD PERSONNEL OBSERVED THAT THE 1' BLOW-OFF VALVE ASSEMBLY WAS FOUND APPROXIMATELY 25 FEET FROM THE WELDED COUPLING LOCATED ON THE 250A PIPELINE FOLLOWING THE EVENT. THE THREADED NIPPLE END OF THE ASSEMBLY WAS LOCATED APPROXIMATELY 6-12 INCHES FROM THE REST OF THE VENT VALVE ASSEMBLY. THE VALVE WAS FOUND IN THE CLOSED POSITION. BASED ON THESE OBSERVATIONS, IT WAS CONCLUDED THAT THE WELDED END FAILED FIRST AND THE THREADED NIPPLE SEPARATED FROM THE VENT VALVE AFTER THE ENTIRE 1' BLOW-OFF VALVE ASSEMBLY WAS EJECTED AND IMPACTED WITH THE GROUND. THE METALLURGICAL ANALYSIS DID NOT IDENTIFY ANY MATERIAL COMPOSITION DEFICIENCIES OF THE ASSEMBLY. IN ADDITION NO EVIDENCE OF EXCESSIVE TORQUE WAS IDENTIFIED. CIG CONCLUDED THE ROOT CAUSE OF THE THREADED-END OF THE NIPPLE BLOW-OFF VALVE ASSEMBLY FAILURE RESULTED FROM THE ASSEMBLY IMPACTING THE GROUND SURFACE. THE ROOT CAUSE OF THE WELD FAILURE IS ASSOCIATED WITH A VIBRATION CAUSED FROM AN 8-INCH FLOW CONTROL VALVE AT THE REGULATOR STATION AT GATE 6. CIG FINALIZED A VIBRATION STUDY ON APRIL 24, 2019. RESULTS OF THE STUDY IDENTIFIED FACILITY MODIFICATIONS WILL BE NECESSARY TO HELP REDUCE VIBRATION AND UNTIL THESE CHANGES CAN BE COMPLETED, CIG WILL IMPLEMENT OPERATING CHANGES AS NEEDED TO HELP LOWER VIBRATION LEVELS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190016 | 31668 | 2019-02-18 12:04 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2019-01-20 20:00 | 2019 |  |  | 40.4288 | -96.2181 | 1235664 | 2019-01-20 23:17 |  | NATURAL GAS |  | 5316 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-20 23:03 | 2019-01-26 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-20 20:00 | 2019-01-20 20:03 | ONSHORE | NE | 68450 | TECUMSEH | JOHNSON | MILEPOST | 18.45 | AUBURN BRANCH LINE | NEB46001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 |  | 0.25 | 24000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | NONE | [28 empty] | 1932 | 1931 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 113 | 2 |  | CLASS 1 LOCATION | NO |  | 102 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 13000 | 20540.6824146981627296587926509186351706 | 15000 | 15925.004442864765 | 20000 | 21233.33925715302 | 0 | 0 |  |  | 48000 | 29870.5283907220757611548556430446194226 | 57699.0261147159477296587926509186351706 | [8 empty] | 536 |  | 500 | 192.619(C) |  |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  |  |  | MANUAL | MANUAL | 50500 | NO |  |  |  | YES |  | YES | DRESSER COUPLINGS. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE INCIDENT AND NOTIFIED THE CORRECT PERSONNEL TO RESPOND. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [14 empty] | YES | HIGH PHOSPHORUS WAS DETECTED IN THE METAL EXAMINATION. | [13 empty] | YES | THERE WAS NOT PHYSICAL DAMAGE TO THE PIPE THAT FAILED. INITIALLY, IT APPEARS TO BE STEEL CHEMISTRY. | [55 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 4023987494 |  |  |  |  | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | 4023987494 | john.gormley@nngco.com | AT APPROXIMATELY, 20:00 ON 1/20/19 A RUPTURE OCCURRED ON THE AUBURN (NEB46001) BRANCH LINE. AT 20:48, THE RUPTURE AT MILEPOST 18.45 WAS REPORTED BY FIRST RESPONDERS TO THE OPERATIONS COMMUNICATION CENTER (OCC). THE RUPTURE IS LOCATED ON THE WEST SIDE OF 619TH AVENUE, NORTH OF HIGHWAY 41 IN SECTION 6, TOWNSHIP 5N, AND RANGE 11E IN JOHNSON COUNTY, NEBRASKA. AT THE INCIDENT LOCATION, INVESTIGATORS OBSERVED A HOLE 15 FEET IN LENGTH AND 10 FEET IN WIDTH EXPOSING THE PIPELINE RUPTURE AT A DEPTH 48" BELOW GRADE. A FAILURE MEASURING 113" IN LENGTH ALONG THE 5 O'CLOCK POSITION OF THE PIPELINE OCCURRED ON THE 6-INCH-DIAMETER SEGMENT OF PIPELINE WITH A WALL THICKNESS OF 0.250". THE PIPELINE IS VINTAGE 1932 DRESSER COUPLED PIPE WITH A SPECIFIED MINIMUM YIELD STRENGTH (SMYS) OF 24,000 PSI. THE PRESSURE AT THE POINT OF THE FAILURE WAS ESTIMATED 535 PSIG, PRODUCING A HOOP STRESS OF 29% SMYS. A DRESSER COUPLING WAS PRESENT, BUT REMAINED INTACT. NO EXTERNAL STRESSES WERE PRESENT THAT WOULD BE INDICATIVE OF THIRD PARTY DAMAGE. CALIPER MEASUREMENT OF THE PIPELINE WALL THICKNESS MEASURED CONSISTENTLY THROUGHOUT THE LENGTH OF THE FAILURE SO CORROSION IS NOT A FACTOR. THERE IS EVIDENCE OF A SEAM FOUND INTACT AT THE 10 O'CLOCK POSITION INDICATING THAT COMPOSITION OF CARBON, MAGNESIUM AND SULFUR ARE NOT EXCESSIVE AS CRACKING ALONG THE SEAM IS MORE COMMON WHEN COMPOSITION ISSUES EXIST. INITIAL INVESTIGATION REVEALED THAT A QUICK-CONNECT ON THE VALVE VRG CONTROLLER AT THE AUBURN TAKE-OFF SETTING SENSE LINE WAS LEAKING GAS. THIS SMALL LEAK CAUSED THE AUBURN TAKEOFF REGULATOR TO MALFUNCTION, RESULTING IN THE AUBURN BRANCH LINE REACHING A PRESSURE OF 535 PSIG PRIOR TO RUPTURE, WHEREAS THE TYPICAL OBSERVED LINE PRESSURE IS APPROXIMATELY 425 PSIG. LOCAL OPERATIONS EMPLOYEES WERE WORKING ON THE CONTROLLER WHEN THE RUPTURE OCCURRED ALLOWING A QUICK RESPONSE. THIS INCREASED PRESSURE IS CERTAINLY A CONTRIBUTING FACTOR TO THE PIPELINE FAILURE, BUT THE PIPELINE SHOULD NOT HAVE FAILED AT 525 PSIG, AS THIS IS LESS THAN THE MAOP PLUS ALLOWABLE BUILDUP. LABORATORY ANALYSIS OF THE PIPELINE WILL BE REQUIRED TO DETERMINE THE ROOT CAUSE OF THE PIPELINE FAILURE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190017 | 32014 | 2019-02-20 12:38 | SUPPLEMENTAL FINAL | 31604 | EQUITRANS MIDSTREAM CORPORATION | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2019-01-29 11:30 | 2019 |  |  | 39.39 | -80.3545 | 1236276 | 2019-01-29 16:25 |  | NATURAL GAS |  | 17812 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-29 13:49 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-29 14:51 | 2019-01-29 13:49 | ONSHORE | WV | 26366 | LUMBERPORT | HARRISON | SURVEY STATION NO. | 460+77 | H312 | H312 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 12 |  | 0.312 | 52000 | API 5L PSL 2 | LONGITUDINAL ERW - HIGH FREQUENCY |  | MAVERICK TUBE CORPORATION | EPOXY | [9 empty] | PIPE GIRTH WELD | [18 empty] | 2015 | 2014 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 3.6 |  | CLASS 1 LOCATION | NO |  | 287 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 71248 | 112575.580052493438320209973753280839895 | 15000 | 15925.004442864765 | 140 | 148.63337480007114 | 0 | 0 |  |  | 86388 | 80957.1101415326418069816272965879265092 | 128649.217870158274460209973753280839895 | [8 empty] | 701 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12904 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | CONTROLLER WAS NOT NOTIFIED BY SCADA THAT AN INCIDENT WAS HAPPENING DUE TO ALERT/ALARM SETTINGS. FATIGUE DID NOT PLAY A PART IN THIS FAILURE. | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | JACOB LYONS | MANAGER PIPELINE COMPLIANCE | jlyons@equitransmidstream.com | 4125537870 |  |  |  |  | GREGG WEST | VP ENVIRONMENTAL SAFETY AND COMPLIANCE | 4123952971 | gwest@equitransmidstream.com | ON 1/29/19 A RUPTURE OCCURRED ON THE MAINLINE OF H312 PIPELINE. THE FAILURE WAS LOCATED AT A GIRTHWELD OF AN ELBOW AND MAINLINE PIPE. THE PIPE AND COATING INFORMATION IS IN PART C OF THIS REPORT. THE FITTING INFORMATION IS 12.75", 0.375 WT, Y52. THE COATING FOR THE WELD WAS DENSO 7200. THE ROOT CAUSE INVESTIGATION FOUND THAT A LANDSLIDE ABOUT 150 YARDS FROM THE RUPTURE MOVED THE PIPELINE FROM IT'S ORIGINAL LOCATION APPROXIMATELY 10 FEET AND PLACED STRESSED ON THE WELD AT THE ELBOW. THE WELD WAS SENT OUT FOR ANALYSIS. THE NDT READER SHEET SHOWS THE X-RAY FOR THE WELD PASSED. THE HYDROTEST PERFORMED DURING CONSTRUCTION WAS SUCCESSFUL. TIMELINE DATE: 1/29/2019 1:03 PM CYBERTEL (ANSWERING SERVICE FOR EMERGENCY NUMBER) CALLED OPERATION FIELD TECH ABOUT POTENTIAL LEAK 1:36 PM XTO CALLED INTO EQUITRANS GAS CONTROL ABOUT POTENTIAL LEAK ON H312 1:49 PM H312 PIPELINE ISOLATED 2:30 PM EQUITRANS MIDSTREAM COMPLIANCE DEPARTMENT NOTIFIED OF POTENTIAL LINE RUPTURE 2:51 PM EQUITRANS OPERATIONS FIELD PERSONNEL PERFORMED A VISUAL CONFIRMATION OF INCIDENT 4:25 PM NATIONAL RESPONSE CENTER NOTIFIED OF INCIDENT METALLURGICAL ANALYSIS SHOWED HIGH APPLIED AXIAL STRESS (LAND/SOIL MOVEMENT) ACTING ON A GIRTHWELD. THE GIRTHWELD SHOWED SOME PRE-EXISTING HYDROGEN ASSISTED COLD CRACKS OR HYDROGEN EMBRITTLEMENT, WHICH FORMED OVER TIME AS A RESULT OF HYDROGEN IN THE WELD OR A COMBINATION OF THESE TWO PROCESSES. WITH CONSULTATION, THESE CRACKS WERE STABLE UNDER HOOP STRESS BUT BECAME UNSTABLE WITH THE ADDED AXIAL STRESS. A LANDSLIDE WAS OBSERVED APPROXIMATELY 100 YARDS FROM THE FAILURE LOCATION PERPENDICULAR TO THE PIPE ON A SIDE HILL.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190018 | 31880 | 2019-02-20 15:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-01-21 02:43 | 2019 |  |  | 42.2069 | -83.9693 | 1235668 | 2019-01-21 04:30 |  | NATURAL GAS |  | 32564 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-21 04:31 | 2019-01-21 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-21 02:43 | 2019-01-21 02:43 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | MILEPOST | PLANT II | PLANT II | FREEDOM COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | CATALYTIC HEATER | 2016 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | CATALYTIC HEATER FAILURE PREVENTED THE PILOT GAS REGULATOR FROM OPERATING RAPIDLY ENOUGH TO MAINTAIN PRESSURE FOR THE PILOT GAS SYSTEM. | CLASS 1 LOCATION | NO |  | 390 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 100623 | 158989.6220472440944881889763779527559055 | 1405 | 1491.642082814999655 | 1209 | 1283.555358094900059 | 0 | 0 |  |  | 103237 | 105544.7438936846943982834645669291338583 | 161764.8194881539942021889763779527559055 | [8 empty] | 668 |  | 800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE RESPONSE BY CONTROLLERS WAS PERFORMED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES |  |  |  | YES |  |  |  |  | YES | [25 empty] | YES | CATALYTIC HEATER FAILURE | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON JANUARY 21, 2019 AT APPROXIMATELY 02:43 HOURS, AN OPERATOR --ALREADY ONSITE RESPONDING TO A LOW PILOT PRESSURE ALARM AT CONSUMERS ENERGY'S FREEDOM COMPRESSOR STATION --OBSERVED GAS BLOWING AT OR NEAR THE PLANT II FIREGATE BLOW DOWN VALVES. DURING HIS INVESTIGATION THE OPERATOR DETERMINE THAT THREE (3) OF THE PLANT 2 FIREGATE BLOW DOWN VALVES WERE IN THE OPEN POSITION. THE OPERATOR WAS SUCCESSFUL AT CLOSING TWO OF THE THREE BLOW DOWN VALVES BUT UNABLE TO CLOSE THE THIRD VALVE (VALVE 614). THE OPERATOR PERFORMED A MANUAL EMERGENCY SHUT DOWN (ESD) OF PLANT 2 BY OPENING A PILOT GAS VENT VALVE TO STOP THE GAS FROM BLOWING. THE PLANT 2 ESD ISOLATION VALVE (VALVE 609) STUCK OPEN AND GAS CONTINUED TO ESCAPE. THE OPERATOR ATTEMPTED TO HAND PUMP VALVE 609 TO THE CLOSE POSITION WITH NO SUCCESS. THE OPERATOR WITH THE ASSISTANCE OF 2 STATION MECHANICS CLOSED VALVES 267 AND 268, WHICH ARE DOWNSTREAM OF VALVE 609. THIS OPERATION SUCCESSFULLY STOPPED THE GAS FROM BLOWING. AN INCIDENT INVESTIGATION IDENTIFIED A CATALYTIC HEATER FAILURE PREVENTED THE PILOT GAS REGULATOR FROM OPERATING RAPIDLY ENOUGH TO MAINTAIN PRESSURE FOR THE PILOT GAS SYSTEM CAUSING THE BLOW DOWN VALVES TO OPEN AND GAS TO BLOW. OPERATIONS PERSONNEL ARE EVALUATING ACTIONS TO IMPLEMENT THAT WILL MINIMIZE FUTURE OCCURRENCE.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20190019 | 33216 | 2019-02-20 17:59 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-01-21 10:37 | 2019 |  |  | 39.7659 | -81.346 | 1235682 | 2019-01-21 11:59 |  | NATURAL GAS |  | 74768 | 22051 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 |  | YES |  | 2019-01-21 10:48 | 2019-04-02 09:00 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 4 | 2019-01-21 10:43 | 2019-01-21 11:10 | ONSHORE | OH | 43788 | SUMMERFIELD | NOBLE | MILEPOST | 678.8 | LINE 10 | ATHE-BERN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API-5L | DSAW |  | CLAYMONT STEEL | COAL TAR | [28 empty] | 1952 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 624 | 30 |  | CLASS 1 LOCATION | NO |  | 634 |  | YES | NO | NO |  |  |  |  | 4000000 | 4246667.851430604 | 66153 | 70232.454593922186603 | 224304 | 354412.0944881889763779527559055118110236 | 14000000 | 14863337.480007114 | 1500000 | 1592500.4442864765 | 1500000 | 1592500.4442864765 | OTHER RESTORATION AND SETTLEMENTS |  | 21290457 | 10099232.87205038663997392913385826771654 | 22719650.76909278216298095275590551181102 | [8 empty] | 803 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 57300 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED MAOP PRIOR TO THE FAILURE, AND THUS CONTROLLER ERROR WAS NOT THE CAUSE OF THE FAILURE. WHEN THE PRESSURE LOSS WAS OBSERVED, THE CONTROLLER PROMPTLY NOTIFIED APPROPRIATE COMPANY PERSONNEL TO RESPOND TO THE FAILURE. | [12 empty] | YES | 11 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | MAYRA SALINAS |  | marya.salinas@enbridge.com | [5 empty] | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 7136275008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1235825 AT APPROXIMATELY 10:37 A.M. EST ON JANUARY 21, 2019, TETLP'S 30-INCH DIAMETER LINE 10 TRANSPORTING NATURAL GAS FROM BERNE COMPRESSOR STATION TO ATHENS COMPRESSOR STATION IN NOBLE COUNTY, OHIO FAILED AT MP 678.8, APPROXIMATELY 2.8 MILES SOUTH OF THE BERNE COMPRESSOR STATION. TETLP CONFIRMED THE RUPTURE AT 10:43 A.M. EST. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. THERE WERE TWO INJURIES AND NO FATALITIES. ONE INJURY REQUIRED INPATIENT HOSPITALIZATION. APPROXIMATELY 4 RESIDENTS WERE EVACUATED. THE ESD AT THE BERNE COMPRESSOR STATION WAS ACTIVATED AT 10:48 AM EST. THE MAINLINE VALVE AT M.P. 670.55 WAS CLOSED AT 11:00 AM EST AND THE BERNE COMPRESSOR STATION BY-PASS VALVE WAS CLOSED AT 11:14 AM EST, COMPLETING THE ISOLATION OF THE FAILURE SITE. TETLP PERSONNEL ARRIVED AT THE FAILURE SITE AT APPROXIMATELY 11:14 AM EST. A THIRD PARTY METALLURGICAL INVESTIGATION IS ONGOING. THE ROOT CAUSE IS PENDING. THE COST OF THE DAMAGE HAS NOT YET BEEN DETERMINED. THE PIPELINE REMAINS OUT OF SERVICE AT THIS TIME. SUPPLEMENTAL REPORT (10/04/2019) UPDATED PART D.7 TO INCLUDE COST OF DAMAGE SUPPLEMENTAL REPORT (10/24/2019) THE METALLURGICAL ROOT CAUSE OF THE INCIDENT WAS A RESULT OF DUCTILE OVERLOAD FROM A LONGITUDINAL TENSILE OR BENDING FORCE, LIKELY FROM LAND MOVEMENT THAT EXCEEDED THE LOAD CARRYING CAPACITY OF THE WELD. SUPPLEMENTAL REPORT (01/21/2020) THE METALLURGICAL ROOT CAUSE OF THE INCIDENT WAS A RESULT OF DUCTILE OVERLOAD FROM A LONGITUDINAL TENSILE OR BENDING FORCE FROM LAND MOVEMENT THAT EXCEEDED THE LOAD CARRYING CAPACITY OF THE WELD. - UPDATED RESTART TIME TO 04/02/2019 AT 9:00 AM CST - UPDATED NUMBER OF INJURIES FROM 1 TO 2 IN PART A AND UPDATED NARRATIVE TO REFLECT 1 INPATIENT HOSPITALIZATION - UPDATED APPARENT CAUSE IN PART G FROM LAND MOVEMENT TO LANDSLIDE
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190020 | 32068 | 2019-03-01 11:03 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-01-31 14:45 | 2019 |  |  | 30.5438 | -94.868 | 1236458 | 2019-01-31 15:40 |  | NATURAL GAS |  | 1269 | 4594 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 15:00 | 2019-02-11 13:23 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 13:52 | 2019-01-31 14:10 | ONSHORE | TX | 77371 | SHEPHERD | SAN JACINTO | SURVEY STATION NO. | 374 + 34.1 | TGP 100-1 | 100-1 25-1D TO 32-1S | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 24 |  | 0.25 | 50000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1944 | 1944 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO | NO |  |  |  |  | 10000 | 10616.66962857651 | 12311 | 13070.181979740541461 | 3400 | 5372.178477690288713910761154855643044619 | 87867 | 93285.491025413220417 | 2000 | 2123.333925715302 | 0 | 0 |  |  | 115578 | 56065.3856005470121195328083989501312336 | 124467.8550371358625919107611548556430446 | [8 empty] | 716 |  | 750 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37065 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | LACK OF FUSION DUE TO MISALIGNMENT | [12 empty] | YES | YES |  |  |  | YES | [58 empty] | YES | YES |  |  | YES |  |  |  | 2014 | [31 empty] | 2014 | [23 empty] | YES | 1984 | 1581 | NO | [13 empty] | NO | [63 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 1:52PM ON JANUARY 31, 2019, A LOCAL PUMPER NOTIFIED TENNESSEE GAS PIPELINE (TGP) OPERATIONS ABOUT A POTENTIAL LEAK SOUTH OF THE TRINITY RIVER IN SAN JACINTO COUNTY, TEXAS. TGP DISPATCHED OPERATIONS TO THE SITE TO INVESTIGATE. THEY ARRIVED AT 2:10PM AND AT 2:45PM CONFIRMED THAT THE 100-1 LINE WAS LEAKING. THE LINE WAS ISOLATED BY CLOSING MAINLINE VALVES MLV 27-1A AND MLV 27-1 AT 3:00PM. THE LINE WAS THEN BLOWN DOWN TO 0PSIG BY 8:00PM ON JANUARY 31, 2019. DUE TO WET GROUND CONDITIONS AND LOGISTICS, EXCAVATION OF THE LINE BEGAN ON FEBRUARY 2, 2019. THE LEAK WAS DETERMINED TO BE COMING FROM A CRACK IN THE PIPE GIRTH WELD. TO REPAIR THE CRACKED SECTION, THE LINE WAS CUT OUT AND REPLACED. REPAIRS WERE COMPLETED AND THE LINE WAS RETURNED TO SERVICE ON 1:23PM ON FEBRUARY 11, 2019. METALLURGICAL ANALYSIS DETERMINED THAT THE CAUSE OF THE CRACK WAS LACK OF FUSION IN THE PIPE GIRTH WELD DUE TO PIPE MISALIGNMENT DURING WELDING. A 48-HOUR PHONE UPDATE WAS PROVIDED TO THE NRC. THE 48-HOUR NRC REPORT NUMBER IS 1236609.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190021 | 33564 | 2019-03-01 13:47 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-01-30 10:25 | 2019 | EASTERN | NO | 42.8095 | -82.8675 | 1236339 | 2019-01-30 11:29 | 1236476 | NATURAL GAS |  | 2766 | 508 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-01-30 10:28 | 2019-12-30 15:30 |  | YES | OPERATOR | 2019-01-30 10:29 | YES | 2019-01-30 10:26 | ALLOWED TO BURN OUT |  | 2212 | NO | [6 empty] | 0 | 2019-01-30 10:25 | 2019-01-30 10:25 | ONSHORE | MI | 48005 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION | PLANT 3 THROUGHPUT PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2012 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | PLANT 3 EMERGENCY SHUT DOWN (ESD) ACTIVATION RESULTING IN A RELEASE OF GAS THROUGH THE BLOW DOWN SILENCERS DUE TO WIND CONDITIONS AND LOCATION OF THE BLOW DOWN SILENCERS, A GAS PLUME MADE CONTACT WITH THE PLANT 2 THERMAL OXIDIZER EXHAUST CAUSING GAS TO IGNITE AND SUBSEQUENT FIRE. | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO | [5 empty] | 0 | 0 | 2261 | 2400.429003021148911 | 12309 | 19448.8661417322834645669291338582677165 | 17500000 | 18579171.8500088925 | 2582 | 2741.224098098454882 | 0 | 0 |  | 4.45 | 17517152 | 8211448.65064319594071385039370078740157 | 18603762.36925174438725756692913385826772 | 0 | 0 | 0 | 0 | NO |  |  |  | 1170 | 800 | 1800 | 192.619(A)(2) |  | 2011-06-10 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 500 | NO | YES |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM REPRESENTATIVE RESPONDED APPROPRIATELY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [6 empty] | YES | [24 empty] | YES | VOLTAGE SPIKE IN THE GROUNDING SYSTEM OF THE DET-TRONIC PANEL | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JANUARY 30, 2019 AT APPROXIMATELY 10:23 A.M., CONSUMERS ENERGY'S (CE) RAY COMPRESSOR STATION PLANT 3 DETECTED AN ABNORMAL OPERATING CONDITION IN THE DET-TRONICS CONTROL SYSTEM. AS PART OF THE EMERGENCY SAFETY FIRE-GATE PROCESS, THE PLANT RELEASED NATURAL GAS INTO THE ATMOSPHERE THROUGH PLANT 3 BLOWDOWN SILENCERS. THE NATURAL GAS RELEASED FROM THE FIRE-GATE EVENT MIGRATED IN A NORTHEAST DIRECTION OVER THE PLANT 2 PROCESSING EQUIPMENT AS A RESULT OF THE WIND CONDITIONS OCCURRING AT THE TIME OF THE EVENT. AT APPROXIMATELY 10:25 A.M., A GAS PLUME IGNITED FROM THE PLANT 3 BLOWDOWN SILENCERS (SUCTION AND DISCHARGE). THE PLANT 2 THERMAL OXIDIZER'S 1506 DEGREES F EXHAUST STREAM AUTO-IGNITED THE PLANT 3 FIRE-GATE GAS PLUME. PERSONNEL AT THE RAY PLANT MANUALLY FIRE-GATED PLANT 1 AND PLANT 2, AS PART OF OUR STANDARD SAFETY PROTOCOLS, AT 10:27:58 A.M. AND 10:28:22 A.M., RESPECTIVELY. AT 10:28:48 A.M., THERE WAS A SECOND IGNITION AT THE PLANT 2 VENT STACK, WHICH IS LOCATED NEXT TO PLANT 3'S BLOWDOWN SILENCERS AND IS THE LOCATION WHERE THE NATURAL GAS IS RELEASED FOR PLANT 2. THE ARMANDA TOWNSHIP FIRE DEPARTMENT WAS NOTIFIED AT 10:29 A.M. AND ARRIVED ONSITE AT 10:38. THE EMERGENCY RESPONDERS REMAINED AT THE SITE UNTIL ALL THE NATURAL GAS WAS VENTED FROM THE PIPING TO ADDRESS REMAINING FIRE AND HOTSPOTS. A ROOT CAUSE ANALYSIS (RCA) TEAM WAS ASSEMBLED AND MET ON SITE FEBRUARY 2, 2019 TO IDENTIFY THE IGNITION SOURCE INITIATING THE FIRE AT THE RAY COMPRESSOR STATION PLANT 3 BLOW DOWN SILENCERS AND DEFINE HOW TO CONTROL AND PREVENT RE-OCCURRENCE. (REFER TO MPSC STAFF' INVESTIGATION REPORT APPENDIX A) FURTHER INVESTIGATION INTO THE DET-TRONICS FAILURE LEADING TO THE FIREGATE ACTIVATION REVEALED THAT A GROUNDING FAULT WAS THE UNDERLYING CAUSE OF THE INITIAL FIREGATE EVENT. WHEN THE STATION'S [DOMESTIC WATER] WELL PUMP STARTED UP, ITS VARIABLE FREQUENCY DRIVE CAUSED A VOLTAGE SPIKE IN THE GROUNDING SYSTEM OF THE DET-TRONICS PANEL LOCATED IN THE HEADQUARTERS BUILDING. THESE HIGH VOLTAGES CAUSED ENHANCED DISCRETE INPUT/OUTPUT (EDIO) AND ANALOG INPUT MODULE (AIM) TO LOSE COMMUNICATION WITH THE DET-TRONICS PILOT AIR SYSTEM, A FAULT WHICH TRIGGERED THE INITIAL FIREGATE. TO ELIMINATE THE GROUNDING VOLTAGE INTO THE DET-TRONICS SYSTEM, THE WELL PUMP PRESSURE SWITCH AND PRESSURE TRANSMITTER WERE RELOCATED TO THE EAST SIDE OF THE PLANT 3 AUXILIARY BUILDING. THE RISK OF A COMMUNICATIONS BREAK-DOWN BETWEEN THE PILOT AIR SYSTEM AND ITS MODULES HAS BEEN MITIGATED BY RELOCATING THE MODULES FROM THE HEADQUARTERS BUILDING TO THE PLANT 3 AUXILIARY BUILDING. RESTORATION AND RECOVERY ACTIVITIES HAVE BEEN OUTLINED THE CONSUMERS ENERGY COMPANY'S RAY NATURAL GAS COMPRESSOR STATION STORAGE FIELD INJECTION TIMELINE AND FACILITY REPAIR UPDATE TIMELINE & FACILITY REPAIR UPDATE (REFER TO MPSC STAFF INVESTIGATION REPORT APPENDIX M) FOLLOWING RESTORATION ACTIONS, NORMAL OPERATIONS TO THE CONSUMERS ENERGY RAY COMPRESSOR STATION WAS RESUMED ON DECEMBER 30, 2019.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190022 | 31750 | 2019-03-01 15:32 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-01-31 02:08 | 2019 |  |  | 39.9386 | -81.6847 | 1236402 | 2019-01-31 03:01 |  | NATURAL GAS |  | 55924 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 02:45 | 2019-01-31 10:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 02:08 | 2019-01-31 02:08 | ONSHORE | OH | 43732 | CUMBERLAND | GUERNSEY | MILEPOST | 12 | COMPRESSOR STATION 209 | 200 SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1950 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH OPEN VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 698 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 150000 | 237007.8740157480314960629921259842519685 | 300 | 318.5000888572953 | 500 | 530.8334814288255 | 0 | 0 |  |  | 150800 | 155886.5044659536624440944881889763779528 | 237857.2075860341522960629921259842519685 | [8 empty] | 669 |  | 790 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | SHELLEY BROMAN | PIPELINE ENGINEER CODES AND STANDARDS | shelley_broman@kindermorgan.com | 7134204417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JANUARY 31, 2019 AT 2:08AM, TENNESSEE GAS PIPELINE COMPRESSOR STATION 209 IN CUMBERLAND, OHIO EXPERIENCED AN EMERGENCY SHUTDOWN (ESD). THE ON DUTY OPERATOR NOTICED THAT THE STATION CONTINUED TO BLOW DOWN BEYOND DURATION OF A NORMAL SHUTDOWN AND CALLED THE OPERATIONS SUPERVISOR AND STATION PERSONNEL FOR ASSISTANCE IN LOCATING THE SOURCE OF THE CONTINUAL GAS RELEASE. THE OPERATIONS SUPERVISOR ARRIVED ON SITE AND TOGETHER WITH THE OPERATOR AND STATION PERSONNEL IDENTIFIED THAT THE STATION HEADER SUCTION VALVE, AS-1, AND DISCHARGE VALVE, AD-3, HAD NOT CLOSED AS DESIGNED. THE OPERATOR AND THE OPERATIONS PERSONNEL (OPERATIONS SPECIALIST) MANUALLY CLOSED THE SUCTION AND DISCHARGE VALVES AND STOPPED THE GAS RELEASE AT 2:45AM ON JANUARY 31, 2019. THE STATION VENTED FOR A TOTAL OF 37 MINUTES AND THE TOTAL GAS RELEASE WAS 55,924 MCF. THE INVESTIGATION REVEALED THAT ESD PUSH BUTTON 5 HAD HAD MOISTURE ENTER THE CASING AND CAUSED CORROSION ON THE BUTTON. ON THE DAY OF THIS EVENT, THE EXTREMELY COLD TEMPERATURES (-4 DEGREES FAHRENHEIT) CAUSED THE MOISTURE IN THE CASING TO FREEZE THEREFORE OPENING THE CIRCUIT ON THE BUTTON AND INITIATING THE ESD. IN ADDITION, MOISTURE HAD GOTTEN IN TO THE AS-1 SUCTION VALVE ACTUATOR AND AD-3 DISCHARGE VALVE ACTUATOR AND THE EXTREMELY COLD WEATHER CAUSED THE VALVE O-RINGS TO FREEZE, PREVENTING THEM FROM CLOSING. IN ORDER TO PREVENT A REOCCURRENCE OF THESE EVENTS THE PUSH BUTTON WAS REPLACED AND FRYQUEL 300 WAS ADDED TO THE VALVE ACTUATORS ON AS-1 AND AD-3 TO ENSURE THEY ARE SEALING TIGHTLY AND WATERTIGHT. A 48-HOUR PHONE CALL UPDATE WAS MADE TO THE NRC. THE 48-HOUR REPORT NUMBER IS 1236569. THE "ORIGINAL" REPORT WAS INTENDED TO BE MARKED AS "ORIGINAL/FINAL" BUT THE "FINAL" DESIGNATION WAS INADVERTENTLY NOT MARKED. NO NEW INFORMATION HAS BEEN ADDED TO THIS "SUPPLEMENTAL/FINAL" REPORT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190023 | 31812 | 2019-03-04 11:03 | SUPPLEMENTAL FINAL | 12498 | MIDWESTERN GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-02-08 23:05 | 2019 |  |  | 36.6199 | -86.5633 | 1237270 | 2019-02-09 11:00 |  | NATURAL GAS |  | 4650 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE COMPRESSOR VENT PERFORMED AS DESIGNED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-09 09:00 | 2019-02-09 09:00 | ONSHORE | TN | 37148-9737 | Not Within a Municipality | SUMNER | MILEPOST | 2101 | PORTLAND | COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | VALVE ACTUATOR | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELIEVED THROUGH A VENT VALVE AS DESIGNED UPON SHUTDOWN OF THE COMPRESSOR STATION. | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 12431 | 19641.6325459317585301837270341207349081 | 200 | 212.3333925715302 | 0 | 0 | 0 | 0 |  |  | 12631 | 12981.4555128138749286089238845144356955 | 19853.9659385032887301837270341207349081 | [8 empty] | 590 |  | 936 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A FAILURE OF A VALVE ACTUATOR. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | TERI ANDERSON | MANAGER REGULATORY COMPLIANCE | teri.anderson@oneok.com | 918-382-2073 |  |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPERATIONS | 918-588-7424 | wesley.dunbar@oneok.com | ON 02/08/2019 AT 23:05 HOURS, THE MGT-PORTLAND COMPRESSOR STATION EXPERIENCED A SHUTDOWN ON THE #1 COMPRESSOR. THE FIELD MECHANIC RESPONDED TO A CALLOUT AND STARTED THE #5 COMPRESSOR TO CONTINUE WITH THE GAS PROCESSING. UPON MAKING REPAIRS TO THE #1 COMPRESSOR AND STARTING THE UNIT BACK UP, THE FIELD MECHANIC ISSUED A SHUTDOWN COMMAND TO THE #5 COMPRESSOR. AS PER NORMAL OPERATIONS, WHEN A COMPRESSOR SHUTS DOWN, TELEMETRY CLOSES THE SUCTION VALVE AND BLOWS DOWN THE COMPRESSOR. UNKNOWN TO THE FIELD MECHANIC, THE VALVE ACTUATOR WHICH CLOSES THE #5 COMPRESSOR SUCTION VALVE WAS UNABLE TO PERFORM THE CLOSE FUNCTION. THE #5 COMPRESSOR SUCTION VALVE REMAINED OPEN. THE COMPRESSOR BEGAN TO BLOW DOWN AS PROGRAMMED, BUT WITH THE SUCTION VALVE REMAINING OPEN, NATURAL GAS CONTINUED TO RELIEVE OUT THE BLOW DOWN VENT. THE FIELD MECHANIC DID NOT SEE THE SUCTION VALVE HAD REMAINED OPEN AND THE CONTROLLER HAD A CLOSED VALVE INDICATOR ON HIS SCADA DISPLAY AS THE DISCONNECTED ACTUATOR HAD ACTIVATED THE LIMIT SWITCH DISPLAYING THE VALVE AS CLOSED IN SCADA. THE FIELD MECHANIC DID NOT HEAR THE GAS RELIEVING THROUGH THE VENT LINE AS THE BLOW DOWN HAS A SILENCER INSTALLED. DURING STATION ROUNDS ON 02/09/2019 AT 09:00, THE FIELD OPERATOR FOUND THE GAS RELIEVING THROUGH THE COMPRESSOR VENT LINE. THE GAS LOSS WAS CALCULATED AT 4.65 MMCF AND WAS REPORTED TO THE NRC ON 02/09/2019 AT 1100 HRS. THE ORIGINAL NRC REPORT NUMBER IS 1237270. THE 48 HOUR NRC REPORT NUMBER IS 1237760. ACTION TAKEN: AN LEL TRANSMITTER TO ALERT THE CONTROL CENTER OF VENTING GAS FROM THE BLOW DOWN HAS BEEN INSTALLED TO ASSIST THEM IN DETERMINING IF GAS IS VENTING TO ATMOSPHERE. THE SUCTION VALVE ACTUATOR WAS REPAIRED AND THE REMAINING STATION ACTUATORS WERE INSPECTED WITH NO ISSUES FOUND. SUPPLEMENTAL REPORT WAS CREATED DUE TO THE NRC REPORTING DATE IN PART A WAS INCORRECT IN THE FIRST REPORT. 3/18/2019 - SUPPLEMENTAL CREATED TO CORRECT NRC ORIGINAL REPORT NUMBER AND DESCRIPTION OF CONTROL VALVE BECOMING DISENGAGED FROM VALVE. THE MOUNTING NUTS HAD VIBRATED LOOSE ON THE MOUNTING STUDS OF THE VALVE ACTUATOR. WHEN THE NUTS VIBRATED LOOSE, THE ACTUATOR SLID OFF OF THE SHAFT WHICH DISENGAGED THE KEY ON THE SHAFT. WHEN A CLOSED COMMAND WAS SENT TO THE VALVE, THE ELECTRIC OPERATOR CLOSED AS IT SHOULD, BUT DID NOT MOVE THE VALVE. IT MADE THE CLOSED LIMIT SWITCH ON THE ELECTRIC OPERATOR, BUT BECAUSE IT WAS DISENGAGED FROM THE GEAR BOX SHAFT IT DID NOT OPERATE THE SUCTION VALVE. THE CONTROLS SAW THE CLOSED LIMIT ON THE SUCTION VALVE AND ALSO ON THE DISCHARGE VALVE AND IT THEN OPERATED AS IT SHOULD ALLOWING THE VENT VALVE TO OPEN TO BLOW DOWN THE COMPRESSORS. THE REPAIR WAS MADE BY INSTALLING THE ELECTRIC OPERATOR BACK ON THE SHAFT AND REPLACING THE NUTS. THE OPEN AND CLOSED LIMITS WERE THEN RESET AND TESTED AS PER PROCEDURE. INSTALLATION OF THE ACTUATOR WAS CONDUCTED BY A CONTRACTOR AND THE ACTUATOR HAD PERFORMED CORRECTLY POST INSTALLATION. MAINTENANCE HAD BEEN PERFORMED ON THE VALVE AND THERE WERE NO ISSUES FOUND DURING THE MAINTENANCE ACTIVITY. ALL ACTUATORS HAVE BEEN INSPECTED AT THE COMPRESSOR STATION TO VERIFY NUTS WERE TIGHT. 3/19/2019 SUPPLEMENTAL: UPDATED ROOT CAUSE TO INCORRECT OPERATION DURING INSTALLATION. THE BOLTS, IF TORQUED, SHOULD NOT HAVE VIBRATED LOOSE. THERE WAS NOT A FAILURE OF THE ACTUATOR, AS IT PERFORMED AS DESIGNED. THERE WERE NO BROKEN PARTS TO THE ACTUATOR.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190024 | 31734 | 2019-03-04 17:01 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-02-07 05:00 | 2019 |  |  | 35.2978 | -98.8337 | 1237058 | 2019-02-07 10:29 |  | NATURAL GAS |  | 8884 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS ALREADY SHUT DOWN. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-07 08:30 | 2019-02-07 08:30 | ONSHORE | OK | 73632 | CORDELL | WASHITA | MILEPOST | CORDELL | CORDELL COMPRESSOR STATION | CORDELL COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | FAILURE DUE TO ICING. | CLASS 1 LOCATION | NO |  | 50 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 28182 | 44529.0393700787401574803149606299212598 | 500 | 530.8334814288255 | 500 | 530.8334814288255 | 0 | 0 |  |  | 29182 | 29685.9258580326292362204724409448818898 | 45590.7063329363911574803149606299212598 | [8 empty] | 0 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VALVE WAS ICED OVER AND DID NOT CLOSE PROPERLY WHEN THE STATION WAS SHUT DOWN AT 01:00. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SURGE VALVE | [22 empty] | YES | ICING | [161 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | AT 2/7/19 AT 01:00 THE CORDELL COMPRESSOR STATION WAS SHUT DOWN BY SYSTEM CONTROL. WHEN THE STATION SHUT DOWN, A SURGE VALVE FOR THE FUEL GAS LINE HUNG OPEN DUE TO SEVERE ICING. DUE TO THE VALVE NOT CLOSING, NATURAL GAS WAS ALLOWED TO FLOW BY AND SINCE THE STATION WAS SHUT DOWN THIS GAS ESCAPED THROUGH A 2" VENT FOR 7.5 HOURS UNTIL IT WAS DISCOVERED BY AN OPERATOR EMPLOYEE AT 08:30 THE SAME DAY. THE VALVE WAS ISOLATED, DE-ICED, AND PUT BACK INTO SERVICE IMMEDIATELY. GAS LOSS FOR THE EVENT WAS CONFIRMED AT 09:30 AND A CALL WAS PLACED WITH THE NRC AT 10:28 (#1237058). A 48 HOUR FOLLOW UP CALL WAS PROVIDED ON 2/8/19 AT 07:34 (#1237159).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190025 | 31736 | 2019-03-04 21:22 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2019-01-31 15:02 | 2019 |  |  | 36.1335 | -95.8868 | 1236467 | 2019-01-31 17:27 |  | NATURAL GAS |  | 16800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 17:50 | 2019-02-03 11:28 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 15:05 | 2019-01-31 15:20 | ONSHORE | OK | 74129 | TULSA | TULSA | SURVEY STATION NO. | N/A | LINE C NORTH | LINE C NORTH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | BOLT-TYPE MECHANICAL COUPLING | 1959 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | BOLT-TYPE MECHANICAL COUPLING | OTHER | [8 empty] | MECHANICAL COUPLING SEPARATION | CLASS 3 LOCATION | YES | METHOD2 | 200 |  | NO | NO | NO |  |  |  |  | 25000 | 26541.674071441275 | 0 | 0 | 53978 | 85288.0734908136482939632545931758530184 | 265000 | 281341.745157277515 | 25000 | 26541.674071441275 | 0 | 0 |  |  | 368978 | 203496.9864876272907742782152230971128609 | 419713.1667909737132939632545931758530184 | [8 empty] | 230 |  | 300 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 26400 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PROJECT ENGINEERING DID NOT REFER TO THE CORRECT WORK ORDER OR MAP IN DESIGNING THE PROJECT AND FAILED TO IDENTIFY THE NEARBY COUPLING. |  |  |  | YES | PROJECT ENGINEERING DID NOT REFER TO THE CORRECT WORK ORDER OR MAP IN DESIGNING THE PROJECT AND FAILED TO IDENTIFY THE NEARBY COUPLING. | NORMAL OPERATING CONDITIONS | NO | [150 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 405-248-7018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 405-2390573 | meghan.booker@onegas.com | A RECENT PIPELINE CONSTRUCTION PROJECT REPLACED PART OF AN ORIGINALLY ALL-WELDED 16-INCH PIPELINE INSTALLED IN 1955. ALTHOUGH OPERATOR RECORDS EXISTED, THE PROJECT DESIGNERS AND REVIEWERS FAILED TO IDENTIFY THAT TWO COUPLINGS HAD LATER BEEN INSTALLED IN 1959. THE CURRENT REPLACEMENT PROJECT CREATED A 90-DEGREE OFFSET IN THE ORIGINAL PIPELINE ROUTE NEAR THE MOST PROXIMATE BURIED COUPLING, AND THE NEW PIPE CONFIGURATION INCREASED THE COUPLING'S AXIAL STRESS. BECAUSE THE EXISTENCE OF THE COUPLINGS WAS NOT NOTED, THE OPERATOR'S PRACTICE TO IMPROVE THE COUPLING'S RESTRAINT SYSTEM, NEAR THE NEWLY INSTALLED 90-DEGREE ELBOW, WERE NOT FOLLOWED AND THE BURIED COUPLING SEPARATED AT NORMAL OPERATING PRESSURE INTO THE PROXIMATE CONSTRUCTION TIE-IN POINT EXCAVATION WHICH WAS STILL OPEN. CORRECTIVE ACTIONS INCLUDE COMPLETING ADDITIONAL ENGINEERING REVIEW OF ACTIVE PROJECTS AND ADDITIONAL TRAINING.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190026 | 31772 | 2019-03-04 22:34 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-01-31 11:00 | 2019 |  |  | 40.0639 | -76.5762 | 1236976 | 2019-02-06 14:04 |  | NATURAL GAS |  | 1782 | 2417.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-01-31 11:00 | 2019-01-31 21:12 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-31 11:00 | 2019-01-31 11:00 | ONSHORE | PA | 17547 | MARIETTA | LANCASTER | MILEPOST | 169.92 | MARIETTA | HEID-MARI | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | TUBING FITTING | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STELL | LEAK |  |  | OTHER | TUBING FITTING | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 829 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 6914 | 7340.365381197799014 | 5096 | 8051.947506561679790026246719160104986877 | 200 | 212.3333925715302 | 0 | 0 | 0 | 0 |  |  | 12210 | 8615.216029109741184372703412073490813648 | 15604.6462803310090040262467191601049869 | [8 empty] | 709 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MARIETTA COMPRESSOR STATION IS LOCALLY MANNED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | MAYRA SALINAS | ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC 1237186 AT APPROXIMATELY 11:00 AM EST ON JANUARY 31, 2019, A NATURAL GAS RELEASE WAS DISCOVERED FROM A RELIEF VALVE AT MARIETTA COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN LANCASTER COUNTY, PA. THE INITIAL GAS LOSS WAS DETERMINED TO BE LESS THAN THE REPORTING THRESHOLD. THE APPARENT CAUSE WAS A TUBING FITTING UNDER A RELIEF VALVE SNAPPING OFF DUE TO VIBRATION, WHICH CAUSED THE RELIEF VALVE 305-10 TO ACTIVATE AND VENT GAS TO ATMOSPHERE. THE GAS LOSS WAS LATER REVISED ON FEBRUARY 6, 2019 AFTER IT WAS DETERMINED THAT DURING STATION ESD, THE MARIETTA STATION 36"X30" SUCTION VALVE #2-6290 DID NOT CLOSE AS INTENDED DUE TO FREEZING IN THE VALVE CONTROLS. THE REVISED GAS LOSS EXCEEDED THE REPORTING THRESHOLD. AFTER CONSULTATION WITH PHMSA ON FEBRUARY 6, 2019, PHMSA RECOMMENDED THAT ENBRIDGE MAKE THE NRC NOTIFICATION. THE AFFECTED PART OF MARIETTA STATION WAS RETURNED TO SERVICE BY 9:12 PM EST ON JANUARY 31, 2019. SUPPLEMENTAL REPORT: AT APPROXIMATELY 11:00 AM EST ON JANUARY 31, 2019, A NATURAL GAS RELEASE WAS DISCOVERED FROM A RELIEF VALVE AT MARIETTA COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN LANCASTER COUNTY, PA. THE ESD SYSTEM WAS ACTIVATED TO ISOLATE THE LEAK IMMEDIATELY AFTER THE LEAK WAS IDENTIFIED. THE INITIAL GAS LOSS WAS DETERMINED TO BE APPROXIMATELY 1,782 MCF, LESS THAN THE REPORTING THRESHOLD. THE APPARENT CAUSE WAS THE FAILURE OF A TUBING FITTING UNDER A RELIEF VALVE DUE TO VIBRATION, WHICH CAUSED THE RELIEF VALVE 305-10 TO ACTIVATE AND VENT GAS TO ATMOSPHERE. ON FEBRUARY 5, DURING THE INVESTIGATION OF THIS EVENT, IT WAS DETERMINED THE MARIETTA STATION 36"X30" SUCTION VALVE #2-6290 DID NOT CLOSE AS INTENDED DUE TO FREEZING IN THE VALVE CONTROLS, RESULTING IN A GAS LOSS VOLUME GREATER THAN ORIGINALLY ESTIMATED. THE GAS LOSS WAS REVISED TO APPROXIMATELY 4,200 MCF ON FEBRUARY 5, 2019. THE REVISED GAS LOSS EXCEEDED THE REPORTING THRESHOLD. AFTER CONSULTATION WITH PHMSA ON FEBRUARY 6, 2019, PHMSA RECOMMENDED THAT ENBRIDGE MAKE THE NRC NOTIFICATION. THE NRC NOTIFICATION WAS MADE ON FEB. 6, AS RECOMMENDED BY PHMSA. THE AFFECTED PART OF MARIETTA STATION WAS RETURNED TO SERVICE BY 9:12 PM EST ON JANUARY 31, 2019.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190027 | 31777 | 2019-03-12 14:54 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2019-02-14 15:26 | 2019 |  |  | 38.2286 | -122.5949 | 1237755 | 2019-02-15 08:12 |  | NATURAL GAS |  | 0.24 | 0.003 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-16 03:50 | 2019-02-16 03:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-14 15:26 | 2019-02-14 15:26 | ONSHORE | CA | 94954 | PETALUMA | SONOMA | MILEPOST | MP 1.9 | L21G | 34717 (ROUTE ID) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | WETLAND | 18 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | THREADED PLUG- LEAK FROM THREADS | 1961 |  | CARBON STEEL |  | LEAK |  |  | OTHER | THREADED PLUG- LEAK FROM THREA | [5 empty] | CLASS 3 LOCATION | NO |  | 116 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1.58005249343832020997375328083989501312 | 132987 | 141187.904389550433537 | 0 | 0 | 0 | 0 |  |  | 132988 | 62287.7327645999623999816272965879265092 | 141189.484442043871857209973753280839895 | [8 empty] | 308 |  | 450 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 4 | NO | [5 empty] | YES | SMALL DIAMETER- 3/4" | YES |  |  |  |  | YES | SMALL DIAMETER- 3/4" | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THESE LEAKS ARE UNIDENTIFIABLE ON SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | LEAK FROM THREADED PLUG | [161 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON THURSDAY, FEBRUARY 14, 2019 AT 1526 HOURS, PG&E WAS NOTIFIED OF A GRADE 1 LEAK AT 2100 S. MCDOWELL BLVD AT THE LOCATION WHERE THE PIPELINE ENTERS SHOLLENBERGER PARK (WETLAND) (L21G MP 1.9). PG&E LEAK SURVEYOR WAS ON SITE APPROXIMATELY AT 1526 HOURS. THE AREA WAS MADE SAFE AND A LEAK SURVEY STAYED ONSITE THROUGHOUT THE NIGHT TO MONITOR AND ENSURE SITE SAFETY. ON 2/15 PG&E CREWS ARRIVED ON-SITE AT APPROXIMATELY 800 HOURS. THE LEAK WAS REPAIRED BY 3:50 HOURS ON 2/16/19. THE GRADE 1 LEAK WAS IDENTIFIED ON A THREADED PLUG DOWNSTREAM OF A 3/4" VALVE. A VISUAL SOAP TEST CONFIRMED THAT THE LEAK WAS CAUSED BY IMPROPER SEALING OF THE THREADS. TOTAL GAS LOSS ESTIMATED AT 0.24 MCF. THERE WAS NO CUSTOMER IMPACT. THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA, POLICE, FIRE DEPARTMENT REPORTED . THERE WERE NO INJURIES OR FATALITIES. THERE WAS NO MEDIA, POLICE, FIRE DEPARTMENT REPORTED. THIS INCIDENT WAS REPORTED TO THE DOT (1237755) AND CPUC (190215-9105) DUE TO THE EXPECTED REPAIR COSTS BEING ESTIMATED AT OVER $50K ON 2/15/19 AT 0800 HOURS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190028 | 32542 | 2019-03-15 16:21 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2019-01-20 00:01 | 2019 |  |  | 39.8898 | -86.3837 | 1235638 | 2019-01-20 13:43 |  | NATURAL GAS |  | 15900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | BLOCKING VALVES AHEAD OF RELIEF VALVES WERE CLOSED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-20 00:01 | 2019-01-20 00:55 | ONSHORE | IN | 46112 | BROWNSBURG | HENDRICKS | MILEPOST | HCJ STATION | HENDRICKS COUNTY JUNCTION | RELIEF VALVES ON SOUTH AND EAST LINES | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 |  | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASED TO THE ATMOSPHERE AS A RESULT OF EQUIPMENT FAILURE | CLASS 1 LOCATION | NO |  | 541 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 51474 | 81331.6220472440944881889763779527559055 | 100 | 106.1666962857651 | 500 | 530.8334814288255 | 0 | 0 |  |  | 52074 | 53646.4531526148531322834645669291338583 | 81968.6222249586850881889763779527559055 | [8 empty] | 518 |  | 600 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ON SITE INVESTIGATION CONFIRMED CONTROLLERS ACTIONS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | CONTROL LINE TO PILOT REGULATORS FOR RELIEF VALVES OBSTRUCTED WITH ICE | [161 empty] | JERRY KNECHT | GAS COMPLIANCE SPECIALIST | jerry.knecht@centerpointenergy.com | 7653669496 |  |  |  |  | ADAM GILLES | REGIONAL OPERATIONS DIRECTOR | 8125688554 | adam.gilles@centerpointenergy.com | VECTREN'S HENDRICKS COUNTY JUNCTION (HCJ) IS A NATURAL GAS TRANSMISSION PIPELINE WITH A COMPRESSOR STATION. HCJ IS A CENTRAL STATION THAT DIRECTS THE FLOW OF GAS INTO VECTREN'S NORTH, SOUTH & EAST SYSTEMS. DURING THIS GAS RELEASE INCIDENT, VECTREN'S SCADA DATA SHOWS THAT NONE OF THE PIPELINES WERE OVER-PRESSURIZED. THE PRESSURES AT THE TIME OF THE INCIDENT WERE WELL WITHIN NORMAL OPERATING PRESSURE RANGES. THIS GAS RELEASE INCIDENT WAS CAUSED BY MOISTURE FREEZING IN THE CONTROL LINE TO THE RELIEF VALVES CAUSING THEM TO OPEN AND VENT NATURAL GAS TO ATMOSPHERE. LOW PRESSURE LIMITS ON SCADA SYSTEM ALERTED GAS CONTROLLERS TO POTENTIAL ISSUE, WHO IN TURN NOTIFIED SUPERVISION, WHICH DISPATCHED 1ST RESPONDER PERSONNEL, WHO ARRIVED AND INVESTIGATED AND RECTIFIED THE SITUATION. TEMPORARY HEAT TAPE, INSULATION AND COVERING OVER THE SECTIONS OF THE CONTROL LINES AND SYSTEM COMPONENTS THAT WERE INVOLVED IN THE FREEZE-OFF WERE PERFORMED THAT WEEK. VECTREN WILL BE MAKING THESE MORE PERMANENT SOLUTIONS LATER THIS SPRING/SUMMER. NOTE: THIS IS INTENDED TO REPLACE REPORT NUMBER 20190015 - 31671 WHICH WAS MISTAKENLY SUBMITTED VIA THE FORM PHMSA F 7100.1.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190029 | 31804 | 2019-03-18 13:56 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-02-18 18:09 | 2019 |  |  | 38.9563 | -77.3397 | 1238646 | 2019-02-26 10:26 |  | NATURAL GAS |  | 7.235 | 36591 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-18 18:42 | 2019-02-23 18:49 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-18 18:09 | 2019-02-18 18:09 | ONSHORE | VA | 20190 | RESTON | FAIRFAX | MILEPOST | 1597.19 | MAINLINE D / MLV 185D14 | MLV 185D0 (STATION 185) TO MLV R9 (POTOMAC RIVER) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 57 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | BALL |  | TIV |  |  |  | 2019 | 2016 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | CARBON STEEL WITH ASTM A182 F316 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 809 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 104559 | 111006.835969433130909 | 21 | 33.18110236220472440944881889763779527559 | 100041 | 106210.224631242263691 | 13335 | 14157.328949706776085 | 70337 | 74674.469166518598387 | NDT, INSPECTION, AND DOWN TIME COSTS |  | 288293 | 135038.8066633175282546141732283464566929 | 306082.0398192629737964094488188976377953 | [8 empty] | 485 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 107765 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS A MATERIAL DEFECT, NOT ASSOCIATED WITH A CONTROLLER PERFORMANCE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | WELD CONNECTION BETWEEN THE GREASE FITTING EXTENSION AND THE MAIN VALVE BODY. CRACKED WELD. |  |  |  |  | YES | [174 empty] | TIMOTHY HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 7132152889 |  |  |  |  | CLINT RATKE | MANAGER PIPELINE SAFETY | 9185736724 | clint.ratke@williams.com | ON 2/18/2019, DURING PURGE AND PACK OPERATIONS ON THE MAINLINE D VALVE SETTING OUTAGE FROM MLV 185D0 (STATION 185) TO R9 AT THE POTOMAC RIVER VALVE SITE (APPROX. 20.41 MILES OF 42" ML D), OPERATIONS PERSONNEL DETECTED A LEAK AT THE NEWLY INSTALLED MLV 185D14 VALVE SETTING AT 6:09 PM ET. THE SOURCE WAS THEN IDENTIFIED AS THE BACK WELD ON THE GREASE EXTENSION FITTING ON THE NEW 42" BALL VALVE. THE PACK STOPPED AT 6:42 PM ET AND PIPELINE SECTION WAS ISOLATED. THIS IS CONSIDERED AS THE SHUTDOWN TIME. IMMEDIATELY PERSONNEL BEGAN TO BLOWDOWN THE SECTION OF MAIN LINE D, AT ~7:00 PM. THE LINE WAS THEN ISOLATED, AND DRAWN DOWN THE NEXT DAY BY WASHINGTON GAS, AND BLOWDOWN RESUMED AGAIN AT 2:06 PM ON 2/19/2019. THE BLOWDOWN WAS COMPLETED TO 0 PSIG AT 8:40 PM ON 2/20/2019. THE LINE WAS THEN SWEPT WITH AIR AND THE CRACKED WELD CONNECTION BETWEEN THE GREASE FITTING EXTENSION AND THE MAIN VALVE BODY WAS POSITIVELY IDENTIFIED AS THE SOURCE OF THE LEAK. THE WELD WAS SAND BLASTED AND INSPECTED, AND REPAIRED USING TIG WELDING. THE CAUSE OF THE EQUIPMENT FAILURE WAS A CRACKED WELD CONNECTION AT THE FITTING. WELD REPAIR, INSPECTION, AND RE-COATING WAS COMPLETED BY 12:16 PM ON 2/23/2019 AND THE PIPELINE SECTION WAS RETURNED TO SERVICE (PURGE AND PACK) BY 6:49 PM ON 2/23/2019. NO FURTHER REVIEW OR ROOT CAUSE ANALYSIS (RCA) HAS BEEN PERFORMED. THE INITIAL TOTAL REPAIR COSTS WERE COLLECTED, REVIEWED, AND WERE DETERMINED TO EXCEED THE $50,000 LIMIT AT 10:15 AM ET ON 2/26/2019 DURING A PROJECT MEETING. THEREFORE, THIS LEAK EVENT IS A DOT REPORTABLE INCIDENT DUE TO THE REPAIR COSTS. THE NRC WAS CONTACTED AT 10:26 AM ET ON 2/26/2019 - INITIAL NRC# 1238646. A 48-HOUR UPDATE WAS SUBMITTED ON 2/28/2019 - NRC# 1238845, AND CORRECTED TO "WELD" CONNECTION, NOT "WELL" CONNECTION. A 30-DAY INCIDENT REPORT (F 7100.2) IS REQUIRED TO BE SUBMITTED TO PHMSA. FINAL REPAIR COSTS ARE INCLUDED IN THIS REPORT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190030 | 32951 | 2019-03-19 21:32 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-02-19 02:20 | 2019 |  |  | 42.8103 | -82.868 | 1238054 | 2019-02-19 10:23 |  | NATURAL GAS |  | 8367 | 1520 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-19 06:30 | 2019-10-15 11:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-19 02:43 | 2019-02-19 03:26 | ONSHORE | MI | 48005 | ARMADA | MACOMB | SURVEY STATION NO. | RELIEF VALVE | SLUG CATCHER VESSEL 3 - RELIEF VALVE PSV-00103 | SLUG CATCHER VESSEL 3 - RELIEF VALVE PSV-00103 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | SLUG CATCHER RELIEF VALVE PSV-00103 | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | VENTING GAS - SLUG CATCHER SAFETY RELIEF VALVE | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 4560 | 4841.20135063088856 | 25268 | 39924.7664041994750656167979002624671916 | 7700 | 8174.8356140039127 | 1000 | 1061.666962857651 | 0 | 0 |  |  | 38528 | 32407.0267462790678717585301837270341207 | 54002.4703316919273256167979002624671916 | [8 empty] | 1194.79 |  | 1800 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [18 empty] | YES | [172 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON FEBRUARY 19, 2019 AT APPROXIMATELY 02:43 HOURS CONSUMERS ENERGY GAS CONTROL WAS NOTIFIED OF VENTING GAS AT RAY COMPRESSOR STATION. RAY COMPRESSOR STATION IS LOCATED IN ARMADA, MICHIGAN (MACOMB COUNTY). THE ON-CALL STATION MECHANIC WAS DISPATCHED AT 02:47 HOURS AND ARRIVED AT THE SITE AT APPROXIMATELY 03:26 HOURS AND GAS WAS NO LONGER VENTING. SECURITY CAMERAS AT THE STATION WERE USED TO DETERMINE THE APPROXIMATE LOCATION OF THE BLOWING GAS. UPON FURTHER INVESTIGATION THE SOURCE OF THE BLOWING GAS WAS DETERMINE TO BE THE PRESSURE RELIEF VALVE (PSV-00103) ON THE SLUG CATCHER. SUBSEQUENT REVIEW OF PRESSURE DATA INDICATES GAS BEGAN VENTING AT APPROXIMATELY 02:20 HOURS AND BLEW FOR APPROXIMATELY 37 MINUTES BEFORE PRESSURE READINGS NORMALIZED. AT APPROXIMATELY 06:30 HOURS THE SLUG CATCHER WAS ISOLATED TO FURTHER INVESTIGATE THE POTENTIAL CAUSE OF THE GAS RELEASE. DURING THE VISUAL INSPECTION, ICE IN THE PILOT SENSING LINE WAS IDENTIFIED AS A POTENTIAL CAUSE. AFTER CONSULTING WITH ENGINEERING THE DECISION WAS MADE TO ISOLATE THE SLUG CATCHER PRESSURE RELIEF VALVE AND RESUME NORMAL OPERATION OF THE SLUG CATCHER. ON FEBRUARY 20, 2019 AFTER CONTINUED INVESTIGATION AND ADDITIONAL ENGINEERING CONSULTATION, THE SLUG CATCHER WAS BLOWN DOWN AND REMOVED FROM SERVICE PENDING A ROOT CAUSE REVIEW. A ROOT CAUSE ANALYSIS (RCA) WAS CONDUCTED BY THE EXPERITEC, THE PRESSURE RELIEF VALVE MANUFACTURE, ON FEBRUARY 25, 2019. A SUMMARY OF THE INVESTIGATION RESULTS ARE AS FOLLOWS: BASED ON THE MULTIPLE CONFERENCE CALLS HELD WITH TAYLOR FORGE (VESSEL MANUFACTURER), CONSUMER ENERGY, EXPERITEC AND EMERSON IT IS OUR OPINION THAT THE EXTERNAL LOW AMBIENT TEMPERATURES AND INTERNAL WET CONDITIONS OF THE NATURAL GAS CAUSED THE SUBJECT RELIEF VALVE TO FREEZE AT VARIOUS POINTS WITHIN THE VALVE. THE FREEZING CAUSED THE VALVE TO OPEN BELOW IT DESIGNATED SET PRESSURE. THE MANUFACTURER RECOMMENDED THAT ALL FOUR (4) RELIEF VALVES BE HEAT TRACED AND INSULATED TO PREVENT THE POTENTIAL OF POSSIBLE FREEZING IN THE FUTURE. CONSUMERS ENERGY'S OPERATIONS HAVE BEEN PERFORMING THE RECOMMENDED REQUIREMENTS TO RETURN THE VESSEL TO SERVICE. THE ANTICIPATED RETURN TO SERVICE DATE IS MARCH 20, 2019. THE FOUR (4) RELIEF VALVES WERE HEAT TRACED AND INSULATED PER MANUFACTURER'S RECOMMENDATION ON MARCH 18, 2019. THE EQUIPMENT WILL RESUME NORMAL OPERATION AS NEEDED DURING THE 2019-2020 WITHDRAWAL SEASON.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190031 | 32447 | 2019-03-21 17:05 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2019-02-21 15:45 | 2019 |  |  | 34.4746 | -84.9743 | 1238276 | 2019-02-21 16:08 |  | NATURAL GAS |  | 600.3 | 2138 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-02-21 18:39 | 2019-02-24 22:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2019-02-21 14:19 | 2019-02-21 15:20 | ONSHORE | GA | 30701 | CALHOUN | GORDON | MILEPOST | VALVE 10 | CHATTANOOGA ROME CALHOUN CROSSOVER | CHATTANOOGA ROME CALHOUN CROSSOVER VALVE 10 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1986 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 107 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 5644 | 5992.048338368582244 | 1585 | 2504.383202099737532808398950131233595801 | 128000 | 135893.371245779328 | 2000 | 2123.333925715302 | 1712 | 1817.573840412298512 | METALLURGICAL FAILURE ANALYSIS LAB COST |  | 138941 | 65976.2320509429447298792650918635170604 | 148330.7105523752482888083989501312335958 | [8 empty] | 1030 |  | 1190 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33137 | NO | [5 empty] | YES | SECTION IS NOT PIGGABLE BECAUSE IT DOES NOT HAVE LAUNCHERS OR RECEIVERS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATING NORMALLY AT THE TIME DUE TO THE DEMAND OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | FAILURE OF THE VALVE BOLTS WAS ATTRIBUTED TO HYDROGEN EMBRITTLEMENT, IN THE FORM OF HYDROGEN-STRESS CRACKING. | [16 empty] | YES | BOLTS DID NOT MEET THE ASTM A193 B7 HARDNESS SPECIFICATION. | [161 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | AT 14:19 EST ON 02/21/2019 SOUTHERN NATURAL GAS COMPANY (SNG) WAS NOTIFIED BY THE FIRE DEPARTMENT THAT THERE WAS AN ODOR AND PLUME OF GAS ABOVE A PIPELINE OPERATED BY SNG. AT 15:20 EST SNG PERSONNEL ARRIVED ON SITE. AT 18:39 EST THE SEGMENT WAS ISOLATED. AS A PRECAUTION THE HOME NEAR THE INCIDENT WAS EVACUATED AND THE OWNER STAYED WITH A RELATIVE FOR ONE NIGHT. THE FIRST VISUAL OBSERVATION OF THE RELEASE POINT IDENTIFIED THAT FOUR FACTORY INSTALLED BOLTS USED TO HOLD THE LOWER TRUNNION TO THE BALL VALVE WERE FOUND BROKEN OFF. THE UNINTENTIONAL AMOUNT OF GAS RELEASED WAS 600.3 MCF. TO REPAIR THE ISSUE THE DAMAGED VALVE WAS REMOVED AND BLIND FLANGES WERE INSTALLED ON BOTH ENDS OF THE PIPELINE. ON 02/24/2019 THE LINE WAS PURGED AND PUT BACK INTO SERVICE. THE ABNORMALLY HIGH REPAIR COSTS WERE DUE TO SNG CHOOSING TO MOBILIZE ITS CONTRACTOR AND WORK THROUGH THE WEEKEND TO MAKE THE REPAIRS SO THAT THE PIPELINE SYSTEM COULD BE RESTORED TO FULL CAPACITY AS SOON AS POSSIBLE, THUS MINIMIZING THE IMPACT TO DOWNSTREAM CUSTOMERS. THE ESTIMATED COST FOR REPAIRING THIS ISSUE UNDER NORMAL CIRCUMSTANCES IS $40,000. AFTER A METALLURGICAL ANALYSIS, THE FAILURE OF THE BOLTS WAS DETERMINED TO BE ATTRIBUTED TO HYDROGEN EMBRITTLEMENT, IN THE FORM OF HYDROGEN-STRESS CRACKING. THE TENSILE STRENGTH AND CHEMICAL COMPOSITION OF THE BOLTS CONFORM TO THE REQUIREMENTS OF ASTM A193 GRADE B7 MATERIAL. HOWEVER, THE BOLTS DID NOT MEET THE ASTM A193 B7 HARDNESS SPECIFICATION. THE BOLTS HAD A HARDNESS OF 40 HRC, WHICH EXCEEDS THE MAXIMUM ASTM A193 B7 HARDNESS REQUIREMENTS OF 35 HRC. THE HARDNESS CONDITION INCREASED THE MICROSTRUCTURE'S SUSCEPTIBILITY TO HYDROGEN CRACKING. NO EVIDENCE OF OVER-TORQUING, STRESS CORROSION CRACKING, OR OTHER METALLURGICAL IRREGULARITIES WAS FOUND. 48-HR NRC REPORT UPDATE NUMBER IS 1238409.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190033 | 32599 | 2019-03-27 16:34 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2019-02-28 14:47 | 2019 |  |  | 43.5285 | -116.3431 | 1238916 | 2019-02-28 19:17 |  | NATURAL GAS |  | 934.65 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-03 11:16 | 2019-03-03 19:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-02-28 14:47 | 2019-02-28 14:47 | ONSHORE | ID | 83642 | MERIDIAN | ADA | MILEPOST | 823.3 | ALBERTSON'S METER STATION | 1400 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FLANGE ASSEMBLY | [38 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 507 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 1020 | 1611.653543307086614173228346456692913386 | 50000 | 53083.34814288255 | 2000 | 2123.333925715302 | 0 | 0 |  |  | 53020 | 25412.5540665156179212598425196850393701 | 56818.3356119049386141732283464566929134 | [8 empty] | 700 |  | 809 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL UNDERGROUND LEAK NOT RELATED TO CONTROL ROOM ACTIVITY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [7 empty] | YES | [172 empty] | SHANE FRASIER | PIPELINE SAFETY ENGINEER | shane.frasier@williams.com | 8015846844 |  |  |  |  | SHANE FRASIER | PIPELINE SAFETY ENGINEER | 8015846844 | shane.frasier@williams.com | THURSDAY MARCH 28TH TWO WILLIAMS INTEGRITY SPECIALISTS DISCOVERED A GAS LEAK AROUND THE ALBERTSONS METER STATION LOOP LINE TAP VALVE. THIS OCCURRED JUST BEFORE 1400 MOUNTAIN TIME. DURING THIS CONVERSATION IT WAS COMMUNICATED THAT LEVELS GREATER THAN 10% LEL WERE BEING MEASURED ON THE COUNTY ROAD ADJACENT TO THE FACILITY. THE EMPLOYEES WERE DIRECTED TO SECURE THE ROAD AT A SAFE DISTANCE AND CONTINUE TO MONITOR LEL LEVELS. AT 1404 FROM THAT INITIAL PHONE CALL THE DISTRICT LEADERSHIP MADE NOTIFICATION TO GAS CONTROL AND INTERMOUNTAIN GAS (IMG) OUR LOCAL LDC. GAS CONTROL ALSO TOOK THE LEAD TO INTERFACE WITH THE SOC. DISTRICT LEADERSHIP DISPATCHED TO THE SITE TO ESTABLISH AN INCIDENT COMMAND IF NEEDED. SITE ASSESSMENTS DETERMINED THE LOOP LINE TAP VALVE WAS THE PROBABLE CAUSE. THIS IS A 4' WELD BY FLANGE VALVE BURIED BELOW GRADE AT OR ABOUT 6 FEET. WITH CLOSE COORDINATION AND COMMUNICATION WITH INTERMOUNTAIN GAS ON SITE, IT WAS DETERMINED NEITHER NWP NOR IMG COULD ISOLATE THE FACILITY WITH CURRENT SYSTEM DEMAND. THIS DECISION POINT OCCURRED LATE IN THE DAY WHICH DROVE FURTHER STEPS TO SECURE THE ROAD LONG TERM AND COMMUNICATE THE ACTIVITY TO LOCAL PROPERTY OWNERS. A 24 HOUR SCHEDULE WAS STAFFED FOR CONTINUES MONITORING AND ON SITE RESPONSE IF NEEDED, ALONG WITH DIRECT LINES OF COMMUNICATION WITH GAS CONTROL. FRIDAY MARCH 1ST WITH WORK PLANS AND SSMP'S IN PLACE EXCAVATION AND CONSTRUCTION COMMENCED WITH THE INSTALLATION OF A THREAD-O-RING FITTING TO FACILITATE A TEMPORARY BYPASS TO MAINTAIN SYSTEM THROUGHPUT FOR IMG. SATURDAY MARCH 2ND WITH THE SUPPORT OF POCATELLO DISTRICT, GAS CONTROL, OTS, AND MATERIALS MANAGEMENT A TEMPORARY BYPASS WAS FABRICATED AND TESTED. SUNDAY MARCH 3RD AT 1116 THE BYPASS WAS PLACED IN SERVICE WITH CONTINUOUS MONITORING BY BOTH NWP AND IMG OPERATIONS PERSONNEL. EXCAVATION THEN BEGAN ON THE LOOP LINE TO EXPOSE THE SUSPECTED LEAKING FITTING. IT WAS CONFIRMED THAT A BLOWN INSULATING GASKET WAS THE CAUSE. THE GASKET WAS REPLACED WITH A FLEXITALLIC GASKET IN PLACE OF THE INSULATING FLANGE GASKET. THE LINE WAS THEN CHECKED FOR LEAKS. AT 1930 ALBERTSONS METER STATION WAS RETURNED TO SERVICE, BYPASS LINE BLOWN DOWN AND SECURED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190034 | 32184 | 2019-03-28 09:44 | SUPPLEMENTAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-03-01 15:16 | 2019 |  |  | 35.822 | -83.9791 | 1239000 | 2019-03-01 16:29 |  | NATURAL GAS |  | 190 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-01 16:00 | 2019-03-01 16:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-01 15:16 | 2019-03-01 15:53 | ONSHORE | TN | 37701 | ALCOA | BLOUNT | MILEPOST | 0.713 | M&R 59048 | MARY-TOPS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | 1/2" NIPPLE AND ISOLATION VALVE | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | DAMAGE DURING MAINTENANCE | [5 empty] | CLASS 1 LOCATION | NO |  | 112 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 544 | 859.548556430446194225721784776902887139 | 50 | 53.08334814288255 | 0 | 0 | 0 | 0 |  |  | 594 | 587.407841458061908005249343832020997375 | 912.631904573328744225721784776902887139 | [8 empty] | 554 |  | 610 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF THE LEAK WAS MINIMAL TO BE DETERMINED BY CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1239112 AT APPROXIMATELY 3:16 PM EST ON MARCH 1, 2019, EAST TENNESSEE NATURAL GAS (ETNG) RECEIVED NOTIFICATION FROM A THIRD PARTY CONTRACTOR ABOUT DAMAGE TO ETNG'S PIPELINE FACILITIES (M&R 59048) IN BLOUNT COUNTY, TENNESSEE. EMERGENCY RESPONDERS ARRIVED ONSITE AND IMPLEMENTED A PARTIAL CLOSURE OF AN ADJACENT HIGHWAY UNTIL THE LEAK WAS ISOLATED. ETNG PERSONNEL ARRIVED ON SITE AT APPROXIMATELY, 3:53 PM EST ON MARCH 1, 2019 AND DETERMINED THAT A 1/2-INCH NIPPLE AND AN ISOLATION VALVE WAS DAMAGED CAUSING A RELEASE OF GAS. ETNG PERSONNEL SUBSEQUENTLY ISOLATED THE METER RUN AT APPROXIMATELY 4:00 PM EST AND REPLACED THE NIPPLE AND ISOLATION VALVE. THE METER RUN WAS RETURNED BACK TO SERVICE AT 4:10 PM EST. THE APPARENT CAUSE OF THE INCIDENT WAS A THIRD PARTY CONTRACTOR DAMAGING ETNG'S PIPELINE FACILITY WITH A FORKLIFT WHILE PREFORMING MAINTENANCE WORK FOR A THIRD PARTY PIPELINE UTILITY COMPANY. WHILE THIS INCIDENT DOES NOT MEET THE GAS LOSS OR COST CRITERIA OF A REPORTABLE INCIDENT, ETNG CLASSIFIED IT AS AN INCIDENT DUE TO THE PARTIAL CLOSURE OF THE HIGHWAY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190035 | 32003 | 2019-03-28 18:45 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-01-25 01:28 | 2019 |  |  | 41.2353 | -91.35 | 1239835 | 2019-03-11 17:46 |  | NATURAL GAS |  | 5679 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ONLY UNIT 9 AND UNIT 10 FOR 80 MINUTES | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-01-25 00:45 | 2019-01-24 18:00 | ONSHORE | IA | 52738 | Not Within a Municipality | LOUISA | MILEPOST | 9.7 | COMPRESSOR STATION 204 (CIARO COLUMBUS LATERAL) | COMPRESSOR STATION 204 UNIT 9 DISCHARGE PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2007 |  | CARBON STEEL |  | OTHER | [8 empty] | SUSPECTED LIQUIDS IN THE RELIEF VALVE SENSING LINE AND RELIEF VALVE PILOT FROZE CAUSING THE RELIEF VALVE TO PREMATURELY OPEN. | CLASS 1 LOCATION | NO |  | 510 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 13630 | 21536.1154855643044619422572178477690289 | 0 | 0 | 110 | 116.78336591434161 | 0 | 0 |  |  | 13740 | 14182.36024333372044958005249343832021 | 21652.8988514786460719422572178477690289 | [8 empty] | 210 |  | 712 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SEVERE COLD AND WIND CHILL EVENT; | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [306 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | WITH EXTREME COLD TEMPERATURE OF APPROXIMATELY -6 DEGREES F AND WIND CHILL OF APPROXIMATELY -21 DEGREE F, SUSPECTED LIQUIDS IN THE RELIEF VALVE SENSING LINE AND RELIEF VALVE PILOT FROZE CAUSING THE RELIEF VALVE TO PREMATURELY OPEN. SAID RELIEF VALVE IS LOCATED OUTSIDE THE COMPRESSOR BUILDING ON THE UNIT 9 DISCHARGE PIPE. LOCAL SOFTWARE RECOGNIZED THE RELIEF VALVE EVENT AND IMMEDIATELY SHUT DOWN UNIT 9 HOWEVER THE RELIEF VALVE CONTINUED TO RELEASE GAS. NIGHT SHIFT STAFF WERE ON SITE WORKING THE COLD WEATHER SHIFT AND INVESTIGATED THE GAS RELEASE WITH IMMEDIATE ATTEMPT TO RESET THE RELIEF VALVE. THE STAFF APPLIED HEAT TO THE RELIEF VALVE TO THAW ANY SUSPECTED ICE AND MANUALLY CLOSED THE LINE VALVE TO ISOLATE THE RELIEF VALVE; THE RELIEF VALVE THEN RESET. STAFF RETURNED THE ISOLATION VALVE TO THE OPEN POSITION AND RETURNED UNIT 9 TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190036 | 32539 | 2019-03-29 10:44 | SUPPLEMENTAL FINAL | 32005 | ENLINK LBU-GAS&LIQUIDS | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2019-03-04 15:20 | 2019 |  |  | 32.0077 | -93.7267 | 1239229 | 2019-03-04 16:16 |  | NATURAL GAS |  | 1 | 149 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-15 07:15 | 2019-03-17 15:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-04 15:20 | 2019-03-04 15:20 | ONSHORE | LA | 71052 | Not Within a Municipality | DESOTO | MILEPOST | MP16.43 | P1323-BAYOU PIERRE TO LOGANSPORT 6" | P1323-BAYOU PIERRE TO LOGANSPORT 6" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | YES |  |  | YES | CASED | [18 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.195 | 35000 | GRADE B | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | OTHER | TGF | [27 empty] | 1940 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 93 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 425 | 451.208459214501675 | 3 | 4.74015748031496062992125984251968503937 | 131536 | 139647.425626443981936 | 0 | 0 | 0 | 0 |  |  | 131964 | 61809.2619156233141999448818897637795276 | 140103.374243138798571629921259842519685 | [8 empty] | 410 |  | 500 | OTHER | 192.557 |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33528 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DURING THE ANNUAL CP SURVEY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A VERY SMALL LEAK INSIDE A CASING FOUND BY OPERATOR PERSONNEL DURING THE ANNUAL CP SURVEY. THE LEAK WAS NOT LARGE ENOUGH TO BE ABLE TO DISCOVER THE LEAK ON SCADA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | YES | NO |  | YES | YES | YES |  |  |  | 2019 |  |  |  | YES | [190 empty] | NO | [63 empty] | YES | 2003 | 500 | NO | [13 empty] | NO | [63 empty] | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | cordell.theriot@enlink.com | 3373226682 | 3379378524 |  |  |  | CORDELL THERIOT | SR. DOT COMPLIANCE SPECIALIST | 3373226682 | cordell.theriot@enlink.com | DURING THE ANNUAL CP SURVEY, OPERATIONS PERSONNEL FOUND AN APPARENT SMALL LEAK INSIDE A CASING AT A RAILROAD CROSSING. THE LEL ON THE VENT PIPE WAS FOUND TO BE 15%. IF THE REPAIR COST DID NOT EXCEED THE $50,000 THRESHOLD, THIS INCIDENT WOULD NOT HAVE BEEN REPORTABLE. THE ACTUAL LEAK WAS A MINOR PIN HOLE INSIDE THE CASING. IT APPEARS THE COATING WAS DAMAGED DURING THE INITIAL INSTALLATION OF THE CROSSING. THE CASING WAS NOT SHORTED. THE ESTIMATED GAS LOSS IS <1MCF.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190037 | 31886 | 2019-04-01 14:51 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-06 06:50 | 2019 |  |  | 33.0919 | -93.3964 | 1239400 | 2019-03-06 14:47 |  | NATURAL GAS |  | 8600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS SHUT DOWN | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-06 06:50 | 2019-03-06 08:55 | ONSHORE | AR | 71861 | TAYLOR | COLUMBIA | MILEPOST | 3146+22 | TAYLOR STATION | LINE S | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | MAUAL VALVE HAND PUMP | 2016 |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 421 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 24000 | 37921.259842519685039370078740157480315 | 2500 | 2654.1674071441275 | 2500 | 2654.1674071441275 | 0 | 0 |  |  | 29000 | 27223.7237783521225590551181102362204724 | 43229.594656807940039370078740157480315 | [8 empty] | 723 |  | 880 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [23 empty] | YES | [174 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 3/6/2019 AT 06:50 ENABLE GAS TRANSMISSION SYSTEM CONTROL NOTICED A DECREASE IN FLOW FOR LINE S AND DISPATCHED THE LOCAL OPERATIONS GROUP TO INVESTIGATE. UPON ARRIVING AT THE TAYLOR COMPRESSOR STATION, OPERATIONS DISCOVERED GAS BLOWING THROUGH THE UNIT 4 BLOWDOWN STACK. AFTER FURTHER INVESTIGATION, OPERATIONS DISCOVERED A DISCHARGE VALVE HAD OPENED CAUSING GAS FROM LINE S TO FILL THE STATION AND GAS WAS VENTING TO ATMOSPHERE THROUGH AN OPEN BLOWDOWN. USING GAS PRESSURE TO SHUT THE DISCHARGE VALVE, THE STATION WAS ISOLATED FROM LINE S. OPERATIONS WORKED WITH SYSTEM CONTROL TO CONFIRM THAT PRESSURE ON LINE S HAD INDEED STARTED TO BUILD. FURTHER INVESTIGATION DETERMINED THE DISCHARGE VALVE OPENED DUE TO HYDRAULIC PRESSURE LEAKING BACK THROUGH TO THE MANUAL HAND PUMP BY WAY OF A CUT O-RING. THIS ALLOWED GAS TO FLOW INTO THE STATION AND SINCE THE STATION BLOWDOWNS WERE OPEN (TO ELIMINATE ANY BUILDUP OF STATION GAS THAT MIGHT LEAK BY CLOSED VALVES WHILE THE STATION IS OFFLINE) GAS WAS ALLOWED TO VENT TO ATMOSPHERE. A PUMP OVERHAUL KIT WAS PURCHASED AND INSTALLED ON THE FAULTY MANUAL HAND PUMP. AFTER THE OVERHAUL KIT WAS INSTALLED AND TESTED IT WAS NOTICED THAT THE MACHINING INSIDE THE MANUAL HAND PUMP HAD AN ILL-MACHINED PORT THAT WAS CUTTING THE NEW O-RING SIMILAR TO THE FIRST O-RING. A NEW PUMP WAS INSTALLED. THE GAS LOSS WAS DETERMINED TO BE 8.6 MMCF AT 14:17 AND A CALL WAS PLACED TO THE NRC (#1239400) AT 14:28. A 48-HOUR FOLLOW UP WAS PROVIDED TO THE NRC (#1239553) ON 3/8/19 AT 07:47
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190038 | 32815 | 2019-04-01 23:10 | SUPPLEMENTAL FINAL | 39167 | SABAL TRAIL TRANSMISSION, LLC (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-03-06 02:05 | 2019 |  |  | 28.2614 | -81.5563 | 1239356 | 2019-03-06 09:24 |  | NATURAL GAS |  | 21700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-06 02:05 | 2019-03-06 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-06 02:05 | 2019-03-06 03:00 | ONSHORE | FL | 33869 | DAVENPORT | OSCEOLA | MILEPOST | 482.37 | COMPRESSOR STATION | DUMM-REUN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | SUCTION BLOCK VALVE | CLASS 1 LOCATION | NO |  | 948 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 59458 | 93946.7611548556430446194225721784776903 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 59458 | 61642.8083989501312335958005249343832021 | 93946.7611548556430446194225721784776903 | [8 empty] | 1200 |  | 1456 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE MALFUNCTION OF THE ISOLATION VALVE COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SUCTION VALVE | [22 empty] | YES | FAULTY LIMIT SWITCH | [161 empty] | NATHAN ATANU | SUPERVISOR | nathan.atanu@enbridge.com | 713-627-5008 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1239356 AT APPROXIMATELY 5:00 AM EST ON MARCH 6, 2019, AN ENBRIDGE TECHNICIAN DISCOVERED A NATURAL GAS RELEASE THROUGH A VENT VALVE ON UNIT 1 AT THE REUNION COMPRESSOR STATION ON THE SABAL TRAIL TRANSMISSION (STT) SYSTEM IN OSCEOLA COUNTY, FL. THE NATURAL GAS RELEASED OCCURRED DURING COMPRESSOR STATION UNIT OPERATIONS SWITCHOVER FROM UNIT 1 TO UNIT 2. AT APPROXIMATELY 2:05 AM EST, ENBRIDGE GAS CONTROL ISSUED A CALL ATTENDANT AND DISPATCHED AN ENBRIDGE TECHNICIAN HAVING DIFFICULTIES SWITCHING FROM UNIT 1 TO UNIT 2. AN ENBRIDGE TECHNICIAN ARRIVED ON SITE AT APPROXIMATELY 3:00 AM EST AND CLEARED ALARM ON UNIT 1. AT APPROXIMATELY, 5:00 AM EST THE ENBRIDGE TECHNICIAN DETERMINED THAT A SUCTION VALVE ON UNIT 1 HAD MALFUNCTIONED AND DID NOT COMPLETELY CLOSE RESULTING IN NATURAL GAS BEING VENTED TO THE STATION SOURCE CONTROL. THE ENBRIDGE TECHNICIAN SUBSEQUENTLY ISOLATED A MANUAL BLOCK VALVE DOWNSTREAM OF VENT VALVE TO STOP THE RELEASE OF NATURAL GAS TO ATMOSPHERE BAT 5:30AM EST. ENBRIDGE WAS UNABLE TO DETERMINE THE ESTIMATED GAS LOSS UNTIL APPROXIMATELY 9:00 AM EST. THE APPARENT CAUSE OF THE NATURAL GAS RELEASE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT: THE CAUSE OF THE NATURAL GAS RELEASE WAS A MALFUNCTION OF THE UNIT 1 SUCTION VALVE DUE TO A FAULTY LIMIT SWITCH.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190039 | 32446 | 2019-04-02 15:18 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-03 03:23 | 2019 |  |  | 39.1923 | -91.891 | 1239100 | 2019-03-03 04:47 |  | NATURAL GAS |  | 90006 | 1713 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-03 04:25 | 2019-04-16 19:03 |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | 2 | 2019-03-03 03:23 | 2019-03-03 03:45 | ONSHORE | MO | 65265 | MEXICO | AUDRAIN | SURVEY STATION NO. | 739+83 | CENTRALIA DISCHARGE | 400 LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.312 | 60000 | API-5LX | DSAW |  | KAISER | OTHER | PITTSBURGH ENAMEL | [27 empty] | 1962 | 1962 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | 6 O'CLOCK POSITION | 864 | 94 |  | CLASS 1 LOCATION | NO |  | 621 |  | YES | NO | NO |  |  |  |  | 993000 | 1054235.294117647443 | 5436 | 5771.221610094190836 | 285616 | 451288.2729658792650918635170603674540682 | 206000 | 218703.394348676106 | 12000 | 12740.003554291812 | 0 | 0 |  |  | 1502052 | 865849.316385611398588461942257217847769 | 1742738.18659658881692786351706036745407 | [8 empty] | 888 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 84069 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 4 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES |  |  | YES |  |  | YES | 2008 | [31 empty] | 2008 | [17 empty] | COMBINATION TOOL | 2015 |  |  |  |  | YES | 2019 | 1145 | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 3/3/19 3:28 CST COMPANY EMPLOYEE NOTIFIED GAS CONTROL OF LARGE FIRE NORTH OF MEXICO, MO NEAR 2 GATE. 3/3/19 3:36 CST EMPLOYEES DISPATCHED TO CENTRALIA STATION, 1 GATE AND 3 GATE. 3/3/19 3:45 CST EMPLOYEE ARRIVED ONSITE AND SPOKE TO MO STATE PATROL ONSITE. 3/3/19 4:17 CST DISCHARGE FIRE GATE CLOSED AT CENTRALIA STATION. 3/3/19 4:25 CST 403 GATE CLOSED. 3/3/19 4:35 CST 401 GATE CLOSED. 3/3/19 4:47 CST NRC TELEPHONIC NOTIFICATION MADE NRC#1239100. 3/3/19 4:54 CST FIRE DIMINISHED. 3/3/19 5:13 CST PHMSA AID NOTIFIED. 3/3/19 17:00 CST POWER RESTORED TO ELECTRIC CUSTOMERS. 3/4/19 22:11 CST 48-HOUR NRC NOTIFICATION MADE NRC#1239251. 3/4/19 22:43 CST PHMSA AID UPDATED. THE INITIAL SUPPLEMENTAL REPORT SUBMITTED ON 5/2/19 UPDATED THE FOLLOWING SECTIONS: PART A, QUESTION 15.B LOCAL TIME PIPELINE/FACILITY RESTARTED: 4/16/19 19:03 CST PART D, QUESTION 7.B ESTIMATED COST OF OPERATOR'S PROPERTY DAMAGE & REPAIRS: $206,000 THE SUPPLEMENTAL/FINAL DATED 7/19/19 UPDATED THE FOLLOWING SECTIONS: PART G, CONFIRMED CAUSE AS G5 ENVIRONMENTAL CRACKING RELATED BASED ON METALLURGICAL LAB ANALYSIS. PART G5, QUESTION 6, STRENGTH AND SPIKE PRESSURE TESTS WERE COMPLETED IN 2019, POST INCIDENT AND PRIOR TO RESTARTING THE LINE. STRENGTH TEST PRESSURE WAS 1145 PSIG. SPIKE TEST PRESSURE WAS 1264 PSIG.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20190040 | 33848 | 2019-04-02 17:36 | SUPPLEMENTAL FINAL | 32595 | HIGH POINT GAS GATHERING, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2019-01-14 13:15 | 2019 | CENTRAL | NO | 29.3875 | -89.4431 | 1235206 | 2019-01-14 14:47 |  | NATURAL GAS |  | 9094.533 | 10069 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-01-16 09:00 | 2019-12-03 08:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-01-14 14:00 | VALVE CLOSURE |  | 2019-01-15 15:00 | 0 | 2019-01-16 09:00 | 2019-01-15 07:00 | OFFSHORE | [28 empty] | 15 | IN STATE WATERS | LA | MARDI GRAS PASS | UNKNOWN | PLAQUEMINES |  |  |  | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 | NO | 0.344 | 60 | 52000 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | ENAMEL WRAP WITH 2" CONCRETE | UNKNOWN | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 20 | 0.5 |  | CLASS 1 LOCATION | NO |  | 400 |  | NO | NO | [5 empty] | 0 | 0 | 33832 | 35918.316687400048632 | 30558 | 48283.244094488188976377952755905511811 | 700000 | 743166.8740003557 | 25000 | 26541.674071441275 | 12000 | 12740.003554291812 | METALLURGICAL ANALYSIS | 3.36 | 801390 | 392712.9855659367932725669291338582677165 | 866650.112407977024608377952755905511811 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 20000 | 1072 | 192.619(A)(1) |  | 1953-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 79200 | YES | [7 empty] | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS DISCOVERED BY A PUBLIC FISHERMAN, AND WAS A CAUSE OF WHAT APPEARS TO BE WELD FAILURE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION | [14 empty] | YES | [10 empty] | 800 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 346-241-3585 |  |  |  |  | KEVIN STANLEY | SR. MANAGER EHS | 346-241-3585 | kstanley@3cmidstream.com | A FISHERMAN IN THE AREA SAW THE BUBBLING WATER AND REPORTED TO THE NRC AND THE LOCAL PARISH SHERIFF'S OFFICE. AMID OPERATIONS CONTROL CENTER WAS NOTIFIED BY THE US COAST GUARD. AFTER FLY-OVERS TO VIEW THE AREA, IT WAS CONFIRMED TO BE AN AMID 20" NATURAL GAS GATHERING PIPELINE. THE LINE WAS SHUT IN. UPON FURTHER INVESTIGATION BY A THIRD-PARTY CONTRACTOR, THE LINE HAD FAILED AT A WELD, WITH THE ENTIRE GIRTH COMING APART. THIRD PARTLY ANALYSIS ON THE PIPE DETERMINED THE ROOT CAUSE WAS FATIGUE FRACTURE IN GIRTH WELDMENT DUE TO MECHANICAL VIBRATION (OSCILLATION). INSTALLED MECHANICAL FLANGES AT EACH CUT WHERE THE DAMAGED SECTION OF THE PIPELINE WAS REMOVED. INSTALLED PRE-HYDROTESTED PIPE SECTION WITH 9 PALLETS OF 3:1 CEMENT/SAND BAGS FOR SUPPORT. LINE WAS LEAK TESTED AT OPERATING PRESSURE, DIVERS OBSERVED FOR 2 HOURS AND VERIFIED NO LEAKS AT THE FLANGES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190041 | 31960 | 2019-04-03 09:18 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-03-05 17:13 | 2019 |  |  | 29.7943 | -93.7481 | 1239330 | 2019-03-05 18:04 |  | NATURAL GAS |  | 66216.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-05 17:12 | 2019-03-06 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-05 17:13 | 2019-03-05 17:55 | ONSHORE | LA | 70631 | CAMERON | CAMERON | SURVEY STATION NO. | R-14-W,T-14-S | COMPRESSOR STATION 342 | VALVE #1342-5 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2006 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL GAS LOSS THROUGH A SIDE GATE VALVE. VALVE FAILED TO CLOSE ALL THE WAY DURING THE STATION ESD. | CLASS 1 LOCATION | NO |  | 589 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 203286 | 321202.5511811023622047244094488188976378 | 15750 | 16721.25466500800325 | 0 | 0 | 16532 | 17551.478229962686332 | COST TO MAN THE STATION UNTIL IT WAS BROUGHT BACK INTO SERVICE |  | 235568 | 225875.6439033400456650866141732283464567 | 355475.2840760730517867244094488188976378 | [8 empty] | 955 |  | 1100 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ACTIONS WERE BEING PERFORMED BY GAS CONTROL AT THE STATION AND THERE WERE NO INDICATIONS OF AN ABNORMAL OPERATION EVENT BEFORE THE ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [9 empty] | YES | [24 empty] | YES | DISCH. SIDE GATE VALVE PNEUMATIC INTERLOCKING DEVICES DIDN'T FUNCTION PROPERLY | [161 empty] | KRISTIN VAN DER LAAN | MANAGER-ENGINEERING-COMPLIANCE CODES AND STNDS | kristin_vanderlaan@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR-ENGINEERING-COMPLIANCE CODES AND STNDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 17:12 CST, THE STATION EMERGENCY SHUTDOWN (ESD) SYSTEM AT THE NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) STATION 342 IN JOHNSON BAYOU, LA (CAMERON PARISH) WAS ACTIVATED. NGPL GAS CONTROL IN HOUSTON, TX RECEIVED AN ABNORMAL SHUTDOWN ALARM AROUND 17:13. THE CONTROLLER DISPATCHED A TECHNICIAN TO THE SITE. PERSONNEL ARRIVED AT THE STATION AT 17:55. UPON ARRIVAL, THE TECHNICIAN ASSESSED THE SITUATION RECOGNIZING THAT THE DISCHARGE BLOWDOWN VALVE WAS VENTING GAS; THEREFORE, THE DISCHARGE SIDE GATE VALVE (1342-5) DID NOT CLOSE PROPERLY WHEN THE ESD WAS ACTIVATED. THE TECHNICIAN CLOSED THE VALVE STOPPING THE RELEASE OF GAS AT 17:58. NOTE THAT LOCAL EMERGENCY RESPONDERS HAD TEMPORARILY BLOCKED THE ACCESS ROAD TO THE STATION (DEEP BAYOU ROAD) UNTIL THE GAS RELEASE STOPPED. STATION PERSONNEL BEGAN INVESTIGATING THE CAUSE OF THE ESD AND IT WAS INITIALLY DETERMINED THAT THE PNEUMATIC FIRE PROTECTION PANEL TRIPPED INITIATING THE ESD. RETURN TO SERVICE WAS DELAYED DUE TO DETERMINING THE CAUSE OF THE ESD AS WELL AS OBTAINING REPLACEMENT COMPONENTS IN THE FIRE PROTECTION PANEL. ADDITIONALLY, LINE BREAK/PIPELINE RUPTURE DETECTION DEVICES HAD CLOSED THE UPSTREAM AND DOWNSTREAM MAINLINE BLOCK VALVES ADDING TO THE DELAY. THE DELAY IMPACTED ONE NGPL CUSTOMER, THE CHENIERE LNG FACILITY. THE INVESTIGATION DETERMINED THAT THE ESD WAS CAUSED BY COMPONENT FAILURE OF THE PNEUMATIC ESD RESET PALM BUTTON IN THE FIRE PROTECTION CONTROL PANEL. ADDITIONALLY, THE ESD DID NOT FUNCTION AS DESIGNED DUE TO THE DISCHARGE SIDE GATE VALVE NOT CLOSING FULLY DUE TO THE PNEUMATIC INTERLOCKING DEVICES NOT FUNCTIONING PROPERLY. NOTE: 48-HOUR NRC UPDATE #1239500
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190042 | 32017 | 2019-04-12 10:26 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2019-03-20 12:00 | 2019 |  |  | 42.3487 | -94.0408 | 1240413 | 2019-03-20 16:30 |  | NATURAL GAS |  | 62000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | SERVICE TO THE TOWN OF LEHIGH, IA COULD BE MAINTAINED WITH THE LEAK. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-20 12:00 | 2019-03-20 13:00 | ONSHORE | IA | 50557 | Not Within a Municipality | WEBSTER | MILEPOST | 20.88 | OGDEN TO VENTURA | M520A | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | OTHER BUTT WELD | [18 empty] | 1956 |  | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 70 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 142600 | 225315.4855643044619422572178477690288714 | 100000 | 106166.6962857651 | 10000 | 10616.66962857651 | 0 | 0 |  |  | 252600 | 199360.2433337204495800524934383202099738 | 342098.8514786460719422572178477690288714 | [8 empty] | 360 |  | 380 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10600 | NO | [5 empty] | YES | 2-INCH PIPELINE | YES |  |  |  |  | YES | 2-INCH PIPELINE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK IS SO SMALL THAT SCADA DID NOT REGISTER A PRESSURE DROP AND THERE WAS NO LOSS OF SERVICE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | FLOATING DEBRIS (WOOD OR ICE) STRUCK ABOVE GROUND APPURTENANCE THAT WAS SUBMERGED IN FLOOD WATERS AND CAUSED LEAKAGE. | NO | [306 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON MARCH 20, 2019, THE OGDEN (IOWA) FIELD OPERATIONS TEAM WAS NOTIFIED BY THE COUNTY SHERIFF OF GAS BLOWING UNDER THE FLOOD WATERS OF THE DES MOINES RIVER NEAR THE TOWN OF LEHIGH, IOWA. THE LEHIGH TAKE-OFF VALVE SETTING IS LOCATED IN THIS AREA AND WAS COMPLETELY SUBMERGED BY THE FLOOD WATERS OF THE DES MOINES, RIVER. THE LEAK WAS SMALL ENOUGH THAT NO LOSS OF SERVICE OCCURRED. THE FIELD OPERATIONS TEAM INSPECTED THE SITE DAILY TO MONITOR THE LEAK AND CHECK ON FLOOD WATER LEVELS. THE SITE WAS STILL UNDER WATER AS OF APRIL 12, 2019 BUT THE LEAK WAS VISIBLE FROM SHORE. THE BUTT WELD BELOW THE BLOW OFF VALVE BETWEEN THE WELD NECK FLANGE AND TEE IS CRACKED PROBABLY DUE TO BEING STRUCK BY FLOATING ICE. THE WELD QUALITY IS NOT SUSPECTED SO IT WON'T BE SENT TO A LABORATORY FOR ANY FURTHER ANALYSIS. THE TAKE-OFF SETTING WAS TOTALLY BYPASSED TO ELIMINATE THE LEAK. THE SECTION OF A-LINE WAS ISOLATED, BLOWN DOWN AND CAPPED. THE TOWN OF LEHIGH, IA IS BEING FED FROM THE B-LINE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190043 | 32171 | 2019-04-12 11:53 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-03-17 06:41 | 2019 |  |  | 29.9884 | -93.9327 | 1240289 | 2019-03-17 08:19 |  | NATURAL GAS |  | 5302 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-17 07:35 | 2019-03-17 14:37 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-17 05:44 | 2019-03-17 07:20 | ONSHORE | TX | 77651 | PORT NECHES | JEFFERSON | SURVEY STATION NO. | STATION 3+46 | SABINE COMPRESSOR STATION | TEXACO - SABINE CS TIE-IN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1996 |  | CARBON STEEL |  | OTHER | [8 empty] | AS DESIGNED, STATION ESD ACTIVATED FOLLOWING LOSS OF COMMERCIAL POWER AND LATER LOSS OF UPS POWER AND ESD ISOLATION VALVE FG-3 DID NOT CLOSE ALLOWING A NATURAL GAS TO CONTINUE FLOW INTO ESD SYSTEM; | CLASS 1 LOCATION | NO |  | 246 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 14845 | 23455.8792650918635170603674540682414698 | 7000 | 7431.668740003557 | 500 | 530.8334814288255 | 0 | 0 |  |  | 22345 | 18903.2365861633544422572178477690288714 | 31418.3814865242460170603674540682414698 | [8 empty] | 756 |  | 1100 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | OTHER | ADJACENT COMPANY MOTIVA CALLED GAS CONTROL; CUSTOMER ENLINK CALLED GAS CONTROL; |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AS DESIGNED, STATION ESD ACTIVATED FOLLOWING LOSS OF COMMERCIAL POWER AND LATER LOSS OF UPS POWER AND ESD ISOLATION VALVE FG-3 DID NOT CLOSE ALLOWING A NATURAL GAS TO CONTINUE FLOW INTO ESD SYSTEM; UPON THE COMPLETE LOSS OF POWER, THE COMPRESSOR STATION PLC SENT MISCELLANEOUS, INADVERTENT, AND INACCURATE STATUS AND SIGNALS THROUGH THE SCADA SYSTEM TO KM TEJAS GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | ESD ISOLATION VALVE FG-3 DID NOT CLOSE ALLOWING A NATURAL GAS TO CONTINUE FLOW INTO ESD SYSTEM; | [11 empty] | YES | [173 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | POST INCIDENT INVESTIGATION DETERMINED KM TEJAS SABINE COMPRESSOR STATION LOST COMMERCIAL AC POWER, 3/15/2019, AT 18:00 HOURS. FOLLOWING THE COMMERCIAL AC POWER FAILURE, THE COMPRESSOR STATION WAS PROVIDED ELECTRICAL POWER BY THE COMPRESSOR STATION UPS BATTERY SYSTEM. ONCE THE UPS BATTERY SYSTEM WAS DEPLETED, THE COMPRESSOR STATION WENT INTO ESD MODE AS COMPRESSOR STATION LOGIC IS PROGRAMMED FOR A COMPLETE POWER LOSS OCCURRENCE. 3/17/2019, 05:44-HOURS MOTIVA EMPLOYEE CALLED KM TEJAS GAS CONTROL CONCERNING A POSSIBLE EVENT AT THE COMPRESSOR STATION SITE. 05:45-HOURS, ENLINK EMPLOYEE CALLED KM TEJAS GAS CONTROL BELIEVING KM TEJAS WAS TAKING NATURAL GAS FROM ENLINK. UPON THE COMPLETE LOSS OF POWER, THE COMPRESSOR STATION PLC SENT MISCELLANEOUS, INADVERTENT, AND INACCURATE STATUS AND SIGNALS THROUGH THE SCADA SYSTEM TO KM TEJAS GAS CONTROL. BECAUSE THE PLC WAS BLACKED-OUT, ALL COMPRESSOR STATION ALARMS AND COMPRESSOR STATION VALVE STATUS SEEN THROUGH SCADA DID NOT REFLECT ACTUAL COMPRESSOR STATION VALVE CONFIGURATIONS. ALSO UPON THE COMPLETE LOSS OF POWER, A VALVE IDENTIFIED AS FIREGATE 3 (FG-3), ONE OF THE COMPRESSOR STATION ESD ISOLATION VALVES, DID NOT CLOSE. THE OPEN VALVE FG-3 ALLOWED NATURAL GAS TO FLOW FROM CUSTOMER ENLINK THROUGH KM TEJAS METERS AND INTO THE COMPRESSOR STATION ESD SYSTEM THEREBY RELEASING ADDITIONAL NATURAL GAS TO ATMOSPHERE. NATURAL GAS VENTED UNTIL THE KM TEJAS EMPLOYEE ACCESSED THE COMPRESSOR STATION SITE BY ENTRY THROUGH MOTIVA PROPERTY SECURITY AND ARRIVED AT THE COMPRESSOR STATION SITE AT 07:20-HOURS AND CONFIRMED NATURAL GAS WAS VENTING AND MANUALLY CLOSED TWO (2) UPSTREAM VALVES ON THE METER RUNS TO TERMINATE THE NATURAL GAS RELEASE AT 07:35-HOURS. COMMERCIAL AC POWER WAS RESTORED TO THE COMPRESSOR STATION AND THE COMPRESSOR STATION RETURNED TO SERVICE AT 14:37-HOURS ON 3/17/2019. FOLLOWING THIS INCIDENT, KM TEJAS REPLACED VALVE FG-3 TO ENSURE VALVE OPERATION RELIABILITY. ALSO BY ELECTIVE CHOICE, KM TEJAS HAS INSTALLED LOSS OF AC POWER INDICATOR ALARMS IN THE COMPRESSOR STATION PLC SYSTEM. THE TEXAS RAILROAD COMMISSION INCIDENT REPORT NUMBER FOR THIS INCIDENT IS #1958. THE NRC 48-HOUR UPDATE INCIDENT REPORT NUMBER FOR THIS INCIDENT IS #1240384. SUBMITTING AS FINAL WITH NO CHANGES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190044 | 33451 | 2019-04-12 12:16 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-02-07 03:00 | 2019 | CENTRAL | NO | 35.7474 | -97.6388 | 1237104 | 2019-03-07 15:56 |  | NATURAL GAS |  | 6736 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-02-07 03:00 | 2019-02-07 03:00 | ONSHORE | OK | 73003 | EDMOND | LOGAN | MILEPOST | EDMONDSTORAGE | EDMOND STORAGE | A-4002 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2008 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELEASED PRIOR TO SET POINT. | CLASS 1 LOCATION | NO |  | 500 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 19537 | 30869.4855643044619422572178477690288714 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.9004 | 19537 | 20254.8950131233595800524934383202099738 | 30869.4855643044619422572178477690288714 | 0 | 0 | 0 | 0 | NO |  |  |  | 729 | 97 | 740 | 192.619(A)(1) |  | 1979-05-15 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLS HAVE NO CONTROL OF THE MANUAL RELIEF VALVES | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE RELEASED PRIOR TO SET POINT. | [161 empty] | JACK CROW | COMPLIANCE SPECIALIST | jcrow@oneok.com | 4053232492 |  |  |  |  | JACK CROW | COMPLIANCE SPECIALIST | 4053232492 | jcrow@oneok.com | THURSDAY FEBRUARY 7TH AT 3:00 AM THE 8' RELIEF VALVE PROTECTING A-4002 FROM A-1129 WENT OFF AT 729 PSI WITH A 740 PSI SET POINT. MERCER VALVE HAD TESTED THE RELIEF VALVE WEDNESDAY FEBRUARY 4TH. THE EVENT LASTED FOR 15 MINUTES AT 729 PSI THROUGH A 8' RELIEF WITH AN APPROX. 6MMCF GAS LOSS. MERCER HAS RETESTED THE RELIEF VALVE AND FOUND TO BE SET AT 740 PSI SET POINT. THE FREEZING COLD TEMPERATURES AND PRESSURES WITHIN 11 PSI OF MAOP MAY HAVE BEEN THE LEADING CAUSE OF EVENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190045 | 34165 | 2019-04-12 16:05 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-02-22 15:00 | 2019 | CENTRAL | NO | 35.6828 | -97.1163 | 1238392 | 2019-02-22 17:06 |  | NATURAL GAS |  | 491 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-02-22 18:45 | 2019-02-23 15:15 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-02-22 18:45 | VALVE CLOSURE |  | 2019-02-22 18:45 | 0 | 2019-02-22 15:15 | 2019-02-22 15:15 | ONSHORE | OK | 74881 | WELLSTON | LINCOLN | MILEPOST | A-26 | A-26 | A-26 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 500 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1188 | 1877.102362204724409448818897637795275591 | 50000 | 53083.34814288255 | 5000 | 5308.334814288255 | 5000 | 5308.334814288255 | INSPECTION COST | 2.42 | 61188 | 29333.6617181782266141732283464566929134 | 65577.1201336637844094488188976377952756 | 0 | 0 | 0 | 0 | NO |  |  |  | 542 | 194 | 600 | 192.619(A)(1) |  | 1970-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 41184 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES |  |  | UTILITY OWNER | YES | YES | YES | 22 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO SUPPORT EXPOSED FACILITIES | [263 empty] | JACK CROW |  | jcrow@oneok.com | 4053232492 |  |  |  |  | JACK CROW |  | 4053232492 | jcrow@oneok.com | EXCAVATOR WORKING FOR OPERATOR FAILED TO PROTECT THE PIPE FROM EXCAVATION DAMAGE. DIRT SLOUGHED OFF BANK STRIKING A 1-INCH DRIP LINE AND BROKE A 1-INCH NIPPLE JUST ABOVE THE VALVE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190046 | 32035 | 2019-04-15 15:35 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 HIGHWAY 56; BOX 20010 | OWENSBORO | KY | 42301 | 2019-03-25 03:13 | 2019 |  |  | 38.1459 | -97.4542 | 1240963 | 2019-03-25 07:46 |  | NATURAL GAS |  | 9300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-25 03:13 | 2019-03-25 07:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-25 03:46 | 2019-03-25 03:46 | ONSHORE | KS | 67062 | Not Within a Municipality | HARVEY | MILEPOST | GATE 42 | HESSTON COMPRESSOR STATION | 171-01-001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1954 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD OF THE HESSTON COMPRESSOR STATION, THE STATION ISOLATION GATE VALVE #42 FAILED TO CLOSE ALLOWING MAINLINE GAS TO VENT DURING THE STATION BLOW-DOWN | CLASS 1 LOCATION | NO |  | 414 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 21155 | 33426.0104986876640419947506561679790026 | 1200 | 1274.0003554291812 | 0 | 0 | 0 | 0 |  |  | 22355 | 22494.3892448622521963254593175853018373 | 34700.0108541168452419947506561679790026 | [8 empty] | 580 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AUTOMATIC ESD WAS TRIGGERED AND THE UNINTENTIONAL GAS RELEASE BECAUSE THE ISOLATION VALVE FAILED TO CLOSE, THE CONTROLLER WAS NOT AT FAULT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ISOLATION VALVE FAILED TO AUTOMATICALLY CLOSE DURING ESD. | [161 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 270-852-4414 | 270-852-5016 |  |  |  | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 270-852-4670 | shawn.patterson@southernstar.com | ON 3/25/2019 AT 3:13 AM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) GAS CONTROL RECEIVED AN ALARM THAT AN AUTOMATIC EMERGENCY SHUTDOWN (ESD) WAS UNDERWAY AT THE HESSTON COMPRESSOR STATION IN HARVEY COUNTY, KANSAS. OPERATIONS PERSONNEL WERE DISPATCHED TO THE STATION ARRIVING AT 3:46 AM. UPON ARRIVAL IT WAS NOTICED THAT GAS WAS STILL VENTING OUT OF THE STATION BLOW-OFF STACK. IT WAS DETERMINED THAT VALVE #42 FAILED TO CLOSE AUTOMATICALLY AND IT WAS CLOSED MANUALLY USING GAS POWER AT 3:56 AM AND THE GAS RELEASE STOPPED. SINCE THE GAS RELEASE WAS PART OF AN ESD IT WAS NOT IMMEDIATELY DETERMINED THAT THIS WAS A REPORTABLE EVENT. A SOLENOID VALVE IN THE BASEMENT FOR THE ESD SYSTEM WAS REPLACED AND THE STATION WAS BROUGHT BACK INTO OPERATION AT 7:15 AM. THE INITIAL GAS LOSS ESTIMATE WAS MADE AT 7:30 AM AND IT WAS DETERMINED THAT THIS WOULD BE A REPORTABLE EVENT AND THE NRC WAS CALLED AT 7:46 AM (NRC#1240963). AFTER INVESTIGATING THE ISOLATION VALVE, THE CAUSE OF THE FAILURE OF THE VALVE TO CLOSE WAS BECAUSE SOME MATERIAL HAD BUILT UP IN THE OPERATOR OF THE VALVE. ALL COMPONENTS OF THE VALVE WERE CLEANED OUT. ALL OF THE ESD LINES WERE ISOLATED AND BLOWN OUT TO REMOVE ANY DEBRIS THAT MAY HAVE BEEN REMAINING IN THE LINE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190047 | 32549 | 2019-04-17 14:22 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-21 16:38 | 2019 |  |  | 25.6667 | -80.3185 | 1240712 | 2019-03-21 19:55 |  | NATURAL GAS |  | 5017 | 773 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-21 17:51 | 2019-03-23 20:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2019-03-21 16:38 | 2019-03-21 17:21 | ONSHORE | FL | 33156 | PINECREST | MIAMI DADE | SURVEY STATION NO. | 7235+24 | FGT | FLMEA-22 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 |  | 0.25 | 52000 | API 5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | YOUNGSTOWN SHEET AND TUBE | POLYOLEFIN | [28 empty] | 1959 | 1959 | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 211 |  | NO | NO | NO |  |  |  |  | 15500 | 16455.8379242935905 | 4191 | 4449.446241336415341 | 15923 | 25159.175853018372703412073490813648294 | 226912 | 240904.973875955303712 | 0 | 0 | 0 | 0 |  |  | 262526 | 132008.7558119900213454514435695538057743 | 286969.433894603682256412073490813648294 | [8 empty] | 269 |  | 288 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24288 | NO | [5 empty] | YES | THIS LINE DOES NOT HAVE A LAUNCHER OR RECEIVER INSTALLED. THE MAOP HAS BEEN REDUCED TO 288 PSI IN RECENT YEARS. MAOP 288 IS OPERATING AT 20% OF SMYS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION WAS NOT NECESSARY DUE TO PIPELINE OPERATING NORMALLY BEFORE BEING HIT BY 3RD PARTY DIGGING IN THE AREA. | [12 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 72915175 | N/A | UTILITY OWNER | YES | YES | YES | 50 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NOTIFICATION TO ONE-CALL CENTER MADE, BUT NOT SUFFICIENT | [265 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | (713)857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | (713)857-5479 | nathan.hlavaty@energytransfer.com | 3/21/19 17:41 EST OPERATIONS ARRIVED ON SITE AND CONFIRMED LINE HIT. 3/21/19 17:48 EST LINE SHUT IN AND ISOLATED. 3/21/19 19:55 EST NRC TELEPHONIC NOTIFICATION MADE NRC#1240712. 3/21/19 20:20 EST PHMSA AID NOTIFIED. 3/21/19 21:00 EST FPL POWER RESTORED TO CUSTOMERS AND EVACUEE RETURNED HOME. 3/23/19 16:09 EST REPLACEMENT COMPLETED AND LINE PUT BACK IN SERVICE. 3/23/19 17:54 EST 48-HOUR NRC NOTIFICATION MADE NRC#1240870. 3/23/19 18:23 EST PHMSA AID UPDATED. THE SUPPLEMENTAL REPORT SUBMITTED 8/13/19, CORRECTED PART A: 5 - LATITUDE/LONGITUDE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190048 | 32425 | 2019-04-19 10:14 | SUPPLEMENTAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2019-03-19 08:00 | 2019 |  |  | 38.6613 | -90.2896 | 1240527 | 2019-03-20 08:31 |  | NATURAL GAS |  | 4.56 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | LEAK WAS ON DRIP RISER, NOT ON THE LINE PIPE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-19 08:30 | 2019-03-19 08:43 | ONSHORE | MO | 63112 | ST. LOUIS | Not Within a County or Parish | SURVEY STATION NO. | STA 302+27 | LANSDOWNE TO STATION N | C-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 120 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 1951 |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 287 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 14 | 22.12073490813648293963254593175853018373 | 61272 | 65050.458148213992072 | 1500 | 1592.5004442864765 | 0 | 0 |  |  | 62786 | 29414.8353882457247257427821522309711286 | 66665.0793274086050549396325459317585302 | [8 empty] | 185 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 20 | NO |  | YES | YES | YES |  |  |  | YES |  | YES |  |  |  |  | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PARAMETERS WERE NOT EXCEEDED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | WHILE LIFTING A STREET COVER PLATE, THE PLATE STRUCK THE DRIP BOX AND CRACKED THE 2" DRIP RISER INSIDE THE BOX RESULTING IN A LEAK. | [251 empty] | LAURA KLECKLEY | MANAGER TIM CORROSION CONTROL PUBLIC AWARENESS | laura.kleckley@spireenergy.com | 205-326-2680 |  |  |  |  | CRAIG R. HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON MARCH 19, 2019 AT 8:00 AM CST, A SPIRE STREET REPAIR CREW DAMAGED A DRIP BOX WHILE LIFTING A STREET COVER PLATE. THE 2" DRIP RISER ATTACHED TO THE TRANSMISSION PIPELINE WAS CRACKED INSIDE THE DRIP BOX AND RESULTED IN A LEAK. THE TRANSMISSION PIPELINE WAS NOT DAMAGED. SPIRE INSTALLED A 2" STOPPER FITTING AND CAPPED THE RISER TO REPAIR THE LEAK, WHICH WAS COMPLETED AT APPROXIMATELY 12:00 AM CST ON MARCH 21, 2019. A 48 HR. UPDATE WAS CALLED INTO THE NRC AT 9:18 AM CST ON MARCH 22, 2019 THAT THE LEAK HAD BEEN PERMANENTLY REPAIRED AND THERE WAS NO MORE RELEASE OF GAS TO THE ENVIRONMENT; NRC REPORT NUMBER 1240741.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20190049 | 32882 | 2019-04-23 16:15 | SUPPLEMENTAL FINAL | 31130 | DCP MIDSTREAM | 6900 E. LAYTON AVE. SUITE 900 | DENVER | CO | 80237-3658 | 2019-04-02 10:00 | 2019 |  |  | 40.2921 | -104.9418 | 1242220 | 2019-04-08 16:22 |  | NATURAL GAS |  | 533 | 32 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-02 10:30 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 2 | 2019-04-02 10:00 | 2019-04-02 10:15 | ONSHORE | CO | 80534 | Not Within a Municipality | WELD | SURVEY STATION NO. | 6+176 | SOCO GATHERING SYSTEM | BZ-7-1-2-EXT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 |  | 0.125 |  | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 83 |  | NO | YES | NO |  |  |  |  | 59951 | 63647.996090279035101 | 71 | 75.378354362893221 | 1359 | 2147.291338582677165354330708661417322835 | 1000 | 1061.666962857651 | 159525 | 169362.422249866775775 | 159525 | 169362.422249866775775 | INVESTIGATION, ENVIRONMENTAL RESPONSE, ENVIRONMENTAL INVESTIGATION |  | 381431 | 179422.0445252010811160314960629921259843 | 405657.1772458158080373543307086614173228 | [8 empty] | 200 |  | 400 | 192.619(A)(4) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 12153 | YES | [7 empty] | YES |  | YES | YES |  |  |  | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THE CAUSE WAS CYCLIC STRESS RESULTING FROM INSTALLATION OF CONCRETE ROAD DRAINAGE STRUCTURES OVER THE PIPELINE. PLEASE SEE ADDITIONAL NARRATIVE IN SECTION H. | [251 empty] | MIKE PAVLAK | SR. COMPLIANCE SPECIALIST | mpavlak@dcpmidstream.com | 970-378-8241 |  |  |  |  | JOHN PONTIOUS | MANAGER PIPELINE COMPLIANCE | 405-605-3859 | jdpontious@dcpmidstream.com | DCP GAS CONTROL RECEIVED A CALL FROM A PROPERTY OWNER ON APRIL 2, 2019 AT APPROXIMATELY 10:00 AM MST REPORTING A SUSPECTED GAS RELEASE. DCP PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 10:15 AM MST AND CONFIRMED A GAS RELEASE AND ISOLATED THE LINE. DCP PERSONNEL BLEW DOWN REMAINING PRESSURE IN THE LINE. INITIAL INVESTIGATION INDICATED A CRACK IN THE PIPE AT APPROXIMATELY THE 6-O'CLOCK POSITION IMMEDIATELY ADJACENT TO A GIRTH WELD TO BE THE SOURCE OF THE RELEASE. BASED ON INVESTIGATION AND METALLURGICAL ANALYSIS, DCP HAS DETERMINED THAT THE BZ-7-1-2-EXT CLASS 2 GAS GATHERING PIPELINE FAILED DUE TO CYCLIC FATIGUE CAUSED BY EXTERNAL LOADING. THE BZ-7-1-2-EXT PIPELINE RUNS PARALLEL TO A COUNTY ROAD AND UNDERNEATH AN INTERSECTION WITH A SECOND COUNTY ROAD. AS PART OF A COUNTY ROAD EXPANSION PROJECT IN AUGUST 2015, A HEAVY CONCRETE PRE-FABRICATED DRAINAGE CULVERT AND SUPPORT BRACE WERE INSTALLED DIRECTLY OVER AND WITHIN A FEW INCHES OF THE TOP OF THE PIPELINE AT THE INTERSECTION. DCP HAD LOCATED AND MARKED THE PIPELINE IN JULY 2015 IN RESPONSE TO AN 811 NOTIFICATION FOR THE ROAD PROJECT, BUT DCP WAS NOT PROVIDED WITH THE COUNTY'S CONSTRUCTION PLANS PRIOR TO THE WORK BEING DONE, AND WAS NOT AWARE NOR MADE AWARE OF THE CONFLICT BETWEEN THE CULVERT INSTALLATION AND THE PIPELINE. FREQUENT HEAVY VEHICLE TRAFFIC AT THE INTERSECTION SUBSEQUENTLY APPLIED REGULAR CYCLIC LOADING TO THE CONCRETE CULVERT AND CONCRETE SUPPORT BRACE UNDER THE ROADWAY, WHICH CYCLIC LOADING CAUSED A BENDING FRACTURE AND THEN FINAL DUCTILE OVERLOAD TEAR OF THE GATHERING PIPELINE IMMEDIATELY BELOW, RESULTING IN THE FAILURE OF THE BZ-7-1-2-EXT PIPELINE ON OR IMMEDIATELY BEFORE APRIL 2, 2019. THE AFFECTED PIPELINE SEGMENT HAS BEEN PURGED OF ALL HYDROCARBONS, PHYSICALLY DISCONNECTED FROM ALL SOURCES OF GAS, AND CAPPED. DCP HAS FURTHER RESPONDED TO THE FAILURE BY CONDUCTING AN EXTENSIVE SOIL AND GROUNDWATER INVESTIGATION ON THE SURROUNDING PROPERTIES, AND IS PURSUING REMEDIATION OPTIONS WITH THE PROPERTY OWNERS UNDER THE OVERSIGHT OF THE COLORADO OIL AND GAS CONSERVATION COMMISSION.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20190050 | 32432 | 2019-04-23 21:42 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-03-24 10:30 | 2019 |  |  | 28.4313 | -91.0844 | 1240916 | 2019-03-24 11:44 |  | NATURAL GAS |  | 336 | 13500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-24 11:44 | 2019-03-26 09:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-24 10:30 | 2019-03-25 11:15 | OFFSHORE | [28 empty] | 150 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SHIP SHOAL | 242 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 |  | 0.5 | 52000 | AP5L | SEAMLESS |  | UNITED SATES STEEL CORPORATION | OTHER | CONCRETE | [27 empty] | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 34641 | 36777.205260351888291 | 862 | 1362.005249343832020997375328083989501312 | 36000 | 38220.010662875436 | 281000 | 298328.416562999931 | 0 | 0 | CLAMP |  | 352503 | 165590.6454843467903771627296587926509186 | 374687.6377355710873119973753280839895013 | [8 empty] | 660 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | AUTOMATIC | 197322 | NO | [5 empty] | YES | UPSTREAM END OF PIPELINE IS SUB-SEA WITH NO PIGGING FACILITIES | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | PRODUCER SAW BUBBLES |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHANIE ROSS | PIPEINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | CINT RATKE | MANAGER PIPELINE SAFETY | 918-573-6724 | clint.ratke@williams.com | WILLIAMS OPERATIONS RECEIVED A CALL ABOUT A SHEEN AND BUBBLES ONE MILE FROM THE SHIP SHOAL 229 PLATFORM. BOTH WILLIAMS AND ANCHOR SHUT-IN PRODUCTION AT SHIP SHOAL 229 & 243. WILLIAMS OPERATIONS SUPERVISOR AND TECHNICIAN FLEW OFFSHORE AND PLOTTED THE COORDINATES OF THE SHEEN TO BE LESS THAN 100 FT FROM OUR LINE. O'BRIENS WAS NOTIFIED AND PRODUCERS WERE SHUT IN ON 3/24/3019. WILLIAMS CONTACTED CHET MORRISON DIVERS TO REQUEST THEIR SERVICE FOR THE LEAK INVESTIGATION AND PETROQUIP TO INQUIRE ABOUT A 20" REPAIR CLAMP. DIVERS CONFIRMED THE LEAK ON 3/25/19 COMING FROM THE WILLIAMS 20" PIPELINE SEGMENT #1636 AND WAS FOUND AT THE 4 O CLOCK POSITION. ADDITIONAL NOTIFICATIONS OF THE CONFIRMED LEAK WERE MADE BY WITT O' BRIEN'S. WORK BEGAN TO REMOVE CONCRETE AND CLEARING AREA FOR REPAIR WORK. ON 3/26/2019, DIVERS REPORTED ALL CONCRETE REMOVED AND COMPLETED THE REPAIR CLAMP INSTALLATION ON 3/27/2019. LINE PRESSURE WAS RETURNED ON 3/28/19 AND NO LEAKS WERE DISCOVERED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190051 | 32191 | 2019-04-25 10:21 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-03-27 12:03 | 2019 |  |  | 27.4681 | -98.0503 | 1241224 | 2019-03-27 15:32 |  | NATURAL GAS |  | 8490 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-03-27 12:03 | 2019-03-29 01:31 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-03-27 12:03 | 2019-03-27 12:03 | ONSHORE | TX | 78363 | KINGSVILLE | KLEBERG | MILEPOST | 0.02 | LOBO 30" RESIDUE | #20150125 KR04 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 687 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 15000 | 23700.7874015748031496062992125984251969 | 5000 | 5308.334814288255 | 0 | 0 | 0 | 0 |  |  | 20000 | 17893.0151169347997244094488188976377953 | 29009.1222158630581496062992125984251969 | [8 empty] | 847 |  | 915 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | AUTOMATIC | MANUAL | 144500 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE RELEASED PREMATURELY . SYSTEM DID NOT EXCEED MAOP | [161 empty] | TIMOTHY BUNAG | ENGINEER | timothy.bunag@energytransfer.com | 832-294-5324 |  |  |  |  | CHRIS KRESTA | MANAGER- REGULATORY COMPLIANCE | 713-989-7077 | christopher.kresta@energytransfer.com | ON MARCH 27, 2019 AT APPROXIMATELY 12:03 PM, ENERGY TRANSFER HAD A RELIEF VALVE MALFUNCTION ON THE LOBO 30" RESIDUE PIPELINE. THIS PIPELINE SYSTEM IS A CLASS 1 TRANSMISSION LINE AND IS LOCATED ON THE KING RANCH IN KLEBERG COUNTY IN KINGSVILLE, TX. THE EVENT WAS REPORTABLE DUE TO THE UNINTENTIONAL RELEASE OF GAS AMOUNTED AT 8.49 MMCF. THE RELIEF VALVE MALFUNCTIONED AND RELEASED PREMATURELY. THE PRESSURE ON THIS SYSTEM DID NOT EXCEED MAOP. THE PIPELINE WAS SHUT IN FOR RELIEF VALVE REPAIR. THE RELIEF VALVE WAS REBUILT AND REPLACED AND THE LINE WAS RETURNED TO SERVICE AT 1:31 AM ON MARCH 29, 2019. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TX RRC AS INTRASTATE (SYSTEM ID #730067). THIS LEAK WAS TELEPHONICALLY REPORTED TO THE TX RRC ON MARCH 27, 2019. A 48 HR. NRC UPDATE WAS MADE ON MARCH 29, 2019 AT 08:51 AM. INCIDENT REPORT #1241355 5/24/19 TO PREVENT REOCCURRENCE OF THIS ISSUE, ENERGY TRANSFER WILL CONTINUE TO ENSURE OUR RELIEF VALVES ARE BEING TESTED AND INSPECTED ANNUALLY BY OUR QUALIFIED INDIVIDUALS IN ACCORDANCE WITH OUR SOP.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190052 | 34171 | 2019-04-26 10:49 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-03-25 14:35 | 2019 | EASTERN | NO | 37.5181 | -77.5396 | 1241015 | 2019-03-25 14:35 | 1241186 | NATURAL GAS |  | 33.49 | 492.74 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-03-30 12:53 | 2019-04-10 16:20 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-03-23 13:57 | VALVE CLOSURE |  | 2019-03-23 13:57 | 0 | 2019-03-22 16:30 | 2019-03-22 17:30 | ONSHORE | VA | 23225 | RICHMOND | RICHMOND | SURVEY STATION NO. | 3876+89 | VM-107 | VS-12017 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | ROAD CROSSING |  | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 | NO | 0.25 | 46000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 314 |  | NO | NO | [5 empty] | 0 | 0 | 1306 | 1386.537053492092206 | 89 | 140.624671916010498687664041994750656168 | 828825 | 879936.120490492590075 | 0 | 0 | 0 | 0 |  | 2.65 | 830220 | 388898.0728114399210703648293963254593176 | 881463.2822159006927796876640419947506562 | 0 | 0 | 0 | 0 | NO |  |  |  | 380 | 105000 | 639 | 192.619(A)(1) |  | 1988-08-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 11540 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONAL PERSONNEL DISCOVERED LEAK DURING ROUTINE LEAKAGE SURVEY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | LIGHTNING OR AC FAULT DAMAGE | [5 empty] | YES | LIGHTNING OR AC FAULT DAMAGE |  |  | YES | YES | YES | KNOWN HVAC CORRIDOR | YES | YES | 1952 | NO | YES | YES | YES | YES | 2006 ' AC MODELING PRIOR TO THE INSTALLATION OF THE AC MITIGATION THAT WAS INSTALLED IN 2007. | 2019 | 2010 | 2006 |  | YES | [190 empty] | YES | YES |  |  | YES |  |  |  | 2014 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2007 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2014 | FREE SWIMMING | STANDARD RESOLUTION |  | INSIDE ILI CUPS | 2007 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK NEWMAN | US REGULATORY COMPLIANCE SPECIALIST | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | GEORGE HAMATY | MANGER TC EAST | 304-357-3728 | george_hamaty@transcanada.com | ON MARCH 22, 2019 AT 07:38 AM WHILE CONDUCTING A LEAK SURVEY AT A CASING VENT A POSITIVE INDICATION OF THE PRESENCE OF NATURAL GAS WAS DISCOVERED AND REPORTED TO THE MONITORING CENTER. THE LEAK WAS DISCOVERED AT A VENT FROM A ROAD CASING AND A SAMPLE SENT TO DETERMINE THE GAS SOURCE. ON MARCH 25, 2019 AFTER THE DETERMINATION THAT THE GAS SOURCE WAS PIPELINE AND THE ESTIMATED COSTS TO REPAIR THE LEAK WOULD EXCEED $50,000 AT REPORT WAS FILED WITH THE NRC. THIS INCIDENT WAS NOT REPORTED DUE TO THE ESTIMATED AMOUNT OF GAS RELEASED EXCEEDING 3,000 MCF, BUT AN UNINTENDED RELEASE OF GAS WITH COSTS FOR REPAIRS EXCEEDING $50,000. THE AREA WAS ISOLATED, THE TRANSMISSION PIPELINE PRESSURE WAS REDUCED TO 185 PSIG (FROM 380 PSIG). CONSTRUCTION CREWS PULLED THE EXISTING PIPELINE SECTION FROM THE CURRENT ROAD CROSSING (CASED) AND REPLACE WITH NEW PRETESTED PIPE. WORK WAS COMPLETED ON 4/8/2019 AND LINE FULLY RESTORED TO SERVICE ON 4/10/2019. DNV CONCLUSION THAT IT WAS LIKELY A NEARBY LIGHTNING STRIKE THAT CAUSED THE LEAK. THE END SEAL EXHIBITED SIGNS THAT ITS CONFIGURATION AND COMPOSITION MAY HAVE FACILITATED THE ARCING BETWEEN THE PIPELINE AND CASING. CP ANNUAL SURVEY WAS CONDUCTED POST INCIDENT TESTING AND DURING THE PIPE INSPECTION. IF UPGRADE TO THE AC MITIGATION OCCURS, TC ENERGY MAY BE ABLE TO PROVIDE SUPPORTING DATA / MODELING TO BETTER DEFINE THE EXACT CAUSE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190053 | 32856 | 2019-05-02 09:21 | SUPPLEMENTAL FINAL | 31023 | CITGO REFINING & CHEMICAL CO. L.P. | 1293 ELDRIDGE PARKWAY | HOUSTON | TX | 77077 | 2018-11-12 03:00 | 2018 |  |  | 27.805 | -97.4784 | 1242400 | 2019-04-10 16:23 |  | HYDROGEN GAS |  | 1700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-11-13 06:48 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-11-13 00:55 | 2018-11-13 00:55 | ONSHORE | TX | 78407 | CORPUS CHRISTI | NUECES | MILEPOST | VS-C | N02 HYDROGEN PIPELINE | VS-C TO VS-E | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 216 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.25 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1983 | 1983 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD1 | 93 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 4000 | 5692.671394799054373522458628841607565012 | 1600000 | 1733164.0979147776 | 150000 | 162484.1341795104 | 350000 | 379129.6464188576 | UT ILI SMART PIGGING COSTS |  | 2104000 | 1007280.10219281701607565011820330969267 | 2280470.54990794465437352245862884160757 | [8 empty] | 260 |  | 390 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 17233 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM OTHER THIRD PARTY OPERATOR PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK OCCURRED WITHIN NORMAL OPERATING CONDITIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | ILI EXAMINATION IDENTIFIED INTERNAL CORROSION AS THE CAUSE OF FAILURE |  |  |  |  | YES | SATURATED LIQUID HYDROCARBON DROP-OUT |  |  | YES | UT ILI SMART PIGGING RESULTS | YES |  | YES |  |  |  | NO | NO | NO | YES | [168 empty] | YES | YES |  | YES |  |  |  |  | 2012 | [19 empty] | 2018 | [35 empty] | YES | 2016 | 663 | NO | [13 empty] | NO | [63 empty] | DAVID R. GARCIA | PROCESS SAFETY MANAGEMENT ADVISOR | dgarci2@citgo.com | 361-844-5479 |  |  |  |  | DAVID R. GARCIA | PROCESS SAFETY MANAGEMENT ADVISOR | 361-844-5479 | dgarci2@citgo.com | AT 3:00 AM ON NOVEMBER 12, 2018, LYONDELL PERSONNEL REPORTED A POTENTIAL PIPELINE LEAK JUST SOUTH OF LYONDELL VALVE STATION CLOSE TO CITGO VALVE STATION C (LATITUDE:27.80514; LONGITUDE: 097.47093). THE POTENTIAL LEAK WAS DISCOVERED DUE TO BUBBLING WATER IN THE DITCH. NO VISIBLE HYDROCARBON SHEEN WAS NOTED, INDICATING A PROBABLE NON-HYDROCARBON GAS LEAK. THE MORNING OF NOVEMBER 12TH, LYONDELL TESTED THEIR AREA GAS PIPELINES AND DETERMINED THAT LYONDELL WAS NOT THE SOURCE OF THE LEAK. LATER THAT DAY, CITGO TESTED THE N11 (PURCHASED H2) PIPELINE, NB7 (AIR LIQUIDE) PIPELINE, AND FINALLY THE N02 (#5 PLAT H2) PIPELINE. THE N02 PIPELINE WAS DETERMINED TO BE THE SOURCE OF THE LEAK. WHEN THE N02 LINE WAS DE-PRESSURED, THE BUBBLING IN THE DITCH SUBSIDED. THE SCADA SYSTEM WAS FUNCTIONAL AND OPERATING UNDER NORMAL CONDITIONS AT THE TIME OF THE INCIDENT. THE PIPELINE PRESSURE DROP DUE TO THE FAILURE WAS SO SMALL THAT IT DID NOT INDICATE ON THE CONTROL ROOM SCADA SCREEN AT THE PRESSURE POINT ADJACENT TO THE LEAK AREA. THE TEXAS RAILROAD COMMISSION WAS CALLED AND NOTIFIED OF THE LEAK AT 12:55 AM ON NOVEMBER 13, 2018. THE N02 LINE WAS DE-PRESSURED TO THE POINT WHERE THE BUBBLING STOPPED (NOON ON NOVEMBER 13TH) AND A PLAN WAS DEVELOPED TO ISOLATE THE LINE WHILE MINIMIZING EMISSIONS FROM THE WEST PLANT DUE TO H2 CONTAINMENT FROM THE #5 REFORMER. AN ADDITIONAL ISOLATION VALVE ON THE N02 LINE AT CITGO VALVE STATION C WAS INSTALLED IN ORDER TO ISOLATE THE N02 LINE FROM THE N11 LINE. HYDRO-EXCAVATION WAS ATTEMPTED TO UNCOVER THE LEAK LOCATION BUT, DUE TO SOIL INSTABILITY, THE DEPTH OF THE EXCAVATION (OVER 25 FOOT), AND ITS PROXIMITY TO I-37, THE DECISION WAS MADE TO ABANDON THIS ACTIVITY AND BACKFILL THE EXCAVATION. QUEST INTEGRITY WAS CONTRACTED TO SMART PIG THE N02 LINE. RESULTS FROM THE UT ILI SMART PIG IDENTIFIED 5 AREAS OF CONCERN. ALL LOCATIONS WERE AT THE BOTTOM OF THE PIPE AND AT LOW LYING AREAS. NO PROPERTY DAMAGE OCCURRED DUE TO THE INCIDENT, EITHER CITGO OR PROPERTY OF OTHERS. THE LEAK RESULTED IN 1.7 MMSCF OF GAS RELEASED TO ATMOSPHERE AN NRC CALL (REPORT #1242400) WAS MADE ON 4/10/19 AT 16:23 AN NCR 48-HOUR UPDATE (RENEWED REPORT #1242587) WAS MADE ON 4/12/19 AT 13:38 THE RE-ROUTE OF A PORTION OF THE N02 LINE IS NOW ALMOST COMPLETE. MAINTENANCE COSTS INCURRED DUE TO THE PARTIAL REPLACEMENT OF THE LINE ARE YET TO BE FINALIZED BUT COST ESTIMATES HAVE BEEN REPORTED HEREIN AS REQUESTED. ESTIMATED COMPLETION OF THE N02 PIPELINE REPAIR IS EXPECTED BY THE END OF NOVEMBER 2019; THE LINE CONTINUES TO BE ISOLATED AND DEPRESSURED AT THIS TIME.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190054 | 32063 | 2019-05-03 08:57 | ORIGINAL FINAL | 4070 | EAST TENNESSEE NATURAL GAS, LLC (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-04-04 21:17 | 2019 |  |  | 35.9798 | -84.2287 | 1241906 | 2019-04-04 22:31 |  | NATURAL GAS |  | 3138 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE NATURAL GAS RELEASE WAS ISOLATED TO THE RELEIF VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-04 21:58 | 2019-04-04 21:58 | ONSHORE | TN | 37830 | OAK RIDGE | ANDERSON | MILEPOST | 9.377 | MR 59021 | WART -TOPS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | RELEASE OF NATURAL GAS FROM RELIEF VALVE. | CLASS 3 LOCATION | NO |  | 236 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 7720 | 12198.0052493438320209973753280839895013 | 1000 | 1061.666962857651 | 0 | 0 | 0 | 0 |  |  | 8720 | 8472.041343596933698162729658792650918635 | 13259.6722122014830209973753280839895013 | [8 empty] | 130 |  | 720 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROLLER VIA SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | FILTER ELEMENT IN REGULATOR GAS SUPPLY WAS DISTORTED | [161 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1242022 AT APPROXIMATELY 9:17 PM EST ON APRIL 4, 2019, EAST TENNESSEE NATURAL GAS (ETNG) WAS NOTIFIED BY A UTILITY COMPANY EMPLOYEE ABOUT A NATURAL GAS RELEASE AT ETNG'S METER AND REGULATOR STATION (M&R 59021) IN ANDERSON COUNTY, TN. ETNG PERSONNEL ARRIVED AT M&R 59021 AT APPROXIMATELY 9:58 PM EST AND DISCOVERED NATURAL GAS RELEASE FROM A RELIEF VALVE. ETNG PERSONNEL SUBSEQUENTLY ISOLATED THE RELIEF VALVE. THE APPARENT CAUSE WAS A COLLAPSED SUPPLY GAS FILTER ON THE UPSTREAM REGULATOR THAT STOPPED THE SUPPLY GAS TO THE BOOT AND RESULTING IN THE REGULATOR TO FAIL OPEN.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190055 | 34303 | 2019-05-03 11:11 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2019-04-03 15:48 | 2019 | PACIFIC | NO | 38.4958 | -121.4295 | 1241929 | 2019-04-05 08:50 |  | NATURAL GAS |  | 25.2 | 23 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-04-05 00:20 | VALVE CLOSURE |  | 2019-04-05 00:20 | 0 | 2019-04-03 15:48 | 2019-04-03 15:48 | ONSHORE | CA | 95823 | SACRAMENTO | SACRAMENTO | MILEPOST | 2.45 | DFM 0609-02 | 35151 (ROUTE ID) | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 6 |  | 0.188 | 30000 | API 5L X-42 | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | ASPHALT |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1962 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | CONSTRUCTION RELATED DEFECT | [5 empty] | CLASS 3 LOCATION | NO |  | 56 |  | NO | NO | [5 empty] | 0 | 0 | 69 | 73.255020437177919 | 76 | 120.083989501312335958005249343832020997 | 201636 | 214070.279722765317036 | 0 | 0 | 0 | 0 |  | 3 | 201781 | 94550.7186327916900656036745406824146982 | 214263.618732703807290958005249343832021 | 0 | 0 | 0 | 0 | NO |  |  |  | 130 | 130 | 150 | 192.619(A)(2) |  | 1962-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 300 | NO | [5 empty] | YES | PIPELINE IS NOT CURRENTLY CONFIGURED TO ACCOMMODATE TRADITIONAL ILI TOOLS DUE TO THE LOW PRESSURE OF THE PIPELINE (150 MAOP). IT IS CATEGORIZED FOR A FUTURE NON-TRADITIONAL INSPECTION AND WILL BE EVALUATED AT THAT TIME FOR ANY TOOL PASSAGE CONSTRAINTS. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SYSTEM IMPACT OR ALARMS DETECTED ON SCADA | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | MATERIAL/WELD FAILURE | [13 empty] | YES | MATERIAL/WELD FAILURE | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER - REGULATORY COMPLIANCE | 925-328-5776 | susie.richmond@pge.com | ON APRIL 3, 2019 AT 1548 HOURS, PG&E IDENTIFIED A GRADE 1 LEAK ALONG DFM 0609-02 AT 6434 FLORIN RD, SACRAMENTO. PG&E CREWS WERE ONSITE AND FINISHED MAKING REPAIRS TO THE LEAKS DISCOVERED ON A SAVE-A-VALVE AND PCF ON APRIL 4, 2019 AT 0414 HOURS. A LEAK SURVEY WAS CONDUCTED FOLLOWING THE REPAIRS AND FOUND AN ADDITIONAL LEAK ON THE WELD OF DFM 0609-02. ON APRIL 6, 2019, PG&E CUT OUT THE FOLLOWING: LEAKING MITER ELBOW, PCF, SAVE-A-VALVE, 6IN ELBOW AND INSTALLED A NEW 6IN PCF AND MAIN. THE APPARENT CAUSE WAS DETERMINED AS METALLURGICAL FAILURE OF THE MITER WELD, LIKELY DUE A CONSTRUCTION-RELATED DEFECT. THERE ARE NO KNOWN INJURIES OR FATALITIES. CUSTOMER IMPACT IS UNKNOWN. NO POLICE OR FIRE DEPARTMENT REPORTED. ON APRIL 5, 2019, THIS INCIDENT WAS REPORTED TO DOT (1241929) AND CPUC (190405-9141) DUE TO MEDIA PRESENCE (FOX NEWS) AND THE EXPECTED REPAIR COSTS BEING ESTIMATED AT OVER $50K.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190056 | 37311 | 2019-05-06 16:15 | SUPPLEMENTAL FINAL | 17620 | ROCKY MOUNTAIN NATURAL GAS LLC | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2019-04-07 09:00 | 2019 | MOUNTAIN | NO | 39.3092 | -107.3962 | 1242079 | 2019-04-07 09:31 | 1242266 | NATURAL GAS |  | 800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-04-06 22:34 | 2019-10-21 08:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-04-07 00:30 | YES | 2019-04-06 22:30 | ALLOWED TO BURN OUT |  | 800 | YES | [6 empty] | 0 | 2019-04-06 22:34 | 2019-04-07 01:00 | ONSHORE | CO | 81623 | Not Within a Municipality | PITKIN | MILEPOST | WC71 PROCESS | GAS STORAGE WELL #71- PROCESSING BUILDING | WC71 PROCESSING BUILDING | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2012 | 2012 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | A 1-INCH THREADED NOZZLE RUPTURED. EXTRA HEAVY WALL THICKNESS 0.179. APPROXIMATE ID OF RUPTURED 0.957. | 1 | 1 |  | CLASS 1 LOCATION | NO |  | 179 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 842480 | 894433.18286831381448 | 2500 | 2654.1674071441275 | 0 | 0 |  | 0 | 844980 | 395760.58112671026462 | 897087.35027545794198 | 0 | 0 | 0 | 0 | NO |  |  |  | 930 | 0 | 1318 | 192.619(A)(1) |  | 2013-10-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING |  |  |  |  | YES |  | YES |  |  | YES | [6 empty] | YES |  |  | YES | GLYCOL CONTRIBUTED TO INTERNAL CORROSION | [161 empty] | JASON PRICE | PROGRAM MANAGER SIMP | jason.price@blackhillscorp.com | 3073157860 |  | THOM WARNES | thomas.warnes@blackhillscorp.com | 9709897053 | BILL STEPHENS | MANAGER CODES AND STANDARDS | 3039816474 | bill.stephens@blackhillscorp.com | 4/6/19 AT 10:30PM MT- DENVER GAS CONTOL RECEIVED A CHAIN OF ALARMS RESULTING IN AN EMEGENCY SHUT DOWN AND ISOLATION OF THE WOLF CREEK WELL #71. ON-CALL OPERATIONS PERSONNEL WERE NOTIFIED AND DISPATCHED TO THE SITE. GAS CONTROL UTILIZED AUTOMATIC ISOLATION VALVES AND SHUT IN THE ENTIRE STORAGE FIELD. COMPANY PERSONNEL SHUT MANUAL ISOLATION VALVES ALONG 3-INCH PIPELINE WHILE TRAVELING TO THE WELL LOCATION. UPON ARRIVAL (1:00 AM MT ON 4-7-19) TO WELL LOCATION COMPANY PERSONNEL OBSERVED A SMALL FIRE BURING FROM 1-INCH GLYCOL PIPING OFF OF THE GAS/GLYCOL HEAT EXCHANGER ON THE DEHYDRATION UNIT HOUSE WITHIN THE PROCESS BUILDING. A SMALL FIRE WAS OBSERVED FROM RESIDUAL GAS BURNING OFF FROM PROCESS PLUMBING. PERSONNEL ALSO WITNESSED EVIDENCE OF SMALL SECONDARY FIRES INSIDE THE PROCESS BUILDING THAT WERE STILL SMOLDERING. ALL TRIETHYLENE GLYCOL WAS CONTAINED WITHIN THE SECONDARY CONTAINMENT OF THE PROCESS BUILDING OR WAS CONSUMED DURING THE FIRE. PERSONNEL LEFT THE WELL SITE AND EVALUATED ALL OTHER WELL LOCATIONS WITHIN THE STORAGE FIELD. NO ISSUES WERE OBSERVED AT ANY OTHER LOCATIONS. PERSONNEL RETURNED BACK TO WELL #71 LOCATION TO EVALUATE OVERALL SITE CONDITIONS. THEY VERIFIED SLAM VALVES, VENT VALVE AND SUB-SURFACE SAFETY VALVE WERE IN THE CORRECT EMERGENCY SHUT POSITION AND ISOLATED MANUAL BLOCK VALVES ON THE FLOW LINE AND PIPELINE. PERSONNEL EVALUATED WELLHEAD HOUSED IN WELLHEAD BUILDING; NO ISSUES WERE OBSERVED, SHUT MASTER AND WING VALVES ON TREE ALL OK. COMPANY PERSONNEL LEFT SITE TO COMMUNICATE FINDINGS WITH MANAGEMENT. MANGEMENT WAS NOTIFIED AT 6:30 AM MT (4-7-19) OF SITE FINDINGS. NO INJURIES OCCURED DURING INCIDENT. NO BREACH OF SECONDARY CONTAINMENT OF ANY STORED OR RELEASED LIGUIDS (TRIETHYLENE GLYCOL). FOLLOW-UP 48 HOUR NRC #1242266. THROUGH INTERNAL AND EXTERNAL INVESTIGATION THE ROOT CAUSE WAS CAUSED BY A FAILED 1-INCH NIPPLE ON GLYCOL GAS HEAT EXCHANGER ON THE DEHYDRATION UNIT. IGNITION SOURCE WAS DETERMINED TO BE UNKNOWN AT THE TIME OF THE INCIDENT. IT IS KNOWN THAT THE PROCESS BUILDING CONTAINED AN ATOMIZED GLYCOL AND GAS MIXTURE RESULTING IN A EXPLOSION AND FIRE. LESSONS LEARNED: OPERATOR IS USING INTERNAL AND EXTERNAL ENGINEERING TO REVIEW THE USE OF HIGH PRESSURE THREADED CONNECTIONS ON AUXILIARY LINES ON DEHYDRATION UNITS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190057 | 32365 | 2019-05-14 13:03 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-04-23 08:10 | 2019 |  |  | 32.9787 | -91.8147 | 1243855 | 2019-04-26 14:40 |  | NATURAL GAS |  | 0.1 | 5006 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-23 16:29 | 2019-04-29 11:47 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-23 08:10 | 2019-04-23 08:10 | ONSHORE | LA | 71220 | BASTROP | MOREHOUSE | MILEPOST | 58+1674 | MAIN LINE SYSTEM | MLS 26-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 26 |  | 0.281 | 52000 | API 5L | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 560 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 13566 | 14402.574018126893466 | 0 | 0 | 61898 | 65715.061666962881598 | 0 | 0 | 0 | 0 |  |  | 75464 | 35344.832415141261816 | 80117.635685089775064 | [8 empty] | 660 |  | 840 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 43178 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK NOT DETECTABLE BY SCADA. INCIDENT REPORTABLE ONLY BECAUSE REPAIR COSTS MAY MEET THE REPORTING THRESHOLD OF $50,000. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | PINHOLE LEAK IN LONGITUDINAL SEAM | [7 empty] | YES | [62 empty] | YES | YES | [6 empty] | 2013 | [55 empty] | YES | 1963 | 1161 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | OQ PA AND EVENT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 |  |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | ON APRIL 21, 2019 AT APPROXIMATELY 4:00 PM, TEXAS GAS TRANSMISSION RECEIVED NOTIFICATION FROM AN INDIVIDUAL WHO WAS RIDING A FOUR WHEELER NEAR THE RIGHT-OF-WAY THAT HE OBSERVED SMALL BUBBLES IN A MUD HOLE. ON APRIL 22, METHANE WAS DETECTED IN THE AREA USING MULTIPLE LEAK DETECTORS BUT BECAUSE OF RECENT FLOODING, IT COULD NOT BE ASSUMED THAT THIS REPRESENTED A NATURAL GAS LEAK. ON APRIL 23 AT APPROXIMATELY 8:10, OPERATIONS PERSONNEL CONFIRMED A POSSIBLE LEAK WITH LEAK DETECTOR. OPERATIONS NOTIFIED PIPELINE SERVICES , THE LINE WAS ISOLATED AND PRESSURE WAS REDUCED FROM 660 PSIG TO 300 PSIG. ON APRIL 23, 2019 AT APPROXIMATELY 11:00 AM, PIPELINE SERVICES BEGAN AN INVESTIGATIVE DIG WHICH CONFIRMED A PINHOLE LEAK IN AN EXISTING WELD ON THE MLS 26-2. THE LINE WAS BLOWN DOWN TO 0 PSIG AT 4:29 PM ON APRIL 23. AFTER EVALUATION, IT WAS DETERMINED THAT ESTIMATED REPAIR COSTS MAY EXCEED $50,000, THUS, MEETING THE PHMSA INCIDENT DEFINITION AND THE NRC WAS CONTACTED. A SECTION OF PIPE WAS CUT OUT, THE LINE WAS PURGED AND PACKED AND PLACED BACK INTO SERVICE ON APRIL 29, 2019 AT 11:00. 6-28-19 UPDATE TO SUBMIT FINAL REPORT. UPDATED PART C TO INDICATE INCIDENT OCCURRED ON PIPE INSTEAD OF WELD AND SUB-CAUSE BASIS TO INCLUDE METALLURGICAL ANALYSIS AS REQUESTED BY PHMSA. ACTUAL COSTS ARE NOW REPRESENTED AND PIR WAS CONFIRMED AS REQUESTED BY PHMSA.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190058 | 32469 | 2019-05-16 18:53 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-04-19 05:31 | 2019 |  |  | 27.7595 | -97.7982 | 1243158 | 2019-04-19 06:09 |  | NATURAL GAS |  | 8802 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-19 05:18 | 2019-04-19 06:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-19 04:40 | 2019-04-19 05:23 | ONSHORE | TX | 78339 | BANQUETE | NUECES | MILEPOST | BANQUETE C/S | BANQUETE COMPRESSOR STATION | TRAILSTONE UNIT 5010 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2018 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 358 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 20114 | 31781.175853018372703412073490813648294 | 9000 | 9555.002665718859 | 250 | 265.41674071441275 | 0 | 0 |  |  | 29364 | 25185.4900398201931384514435695538057743 | 41601.595259451644453412073490813648294 | [8 empty] | 846 |  | 1050 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS DETERMINED INDEPENDENT FROM CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | AT 4:40 AM ON APRIL 19TH, 2019 NATURAL GAS PIPELINE CO. OF AMERICA, LLC (NGPL) RECEIVED A CALL FROM FIRST RESPONDERS IN BANQUETE, TX REPORTING A LOUD NOISE. NGPL NOTIFIED KINDER MORGAN TEJAS PIPELINE, LLC (TEJAS) WHO SHUT DOWN THE BANQUETE COMPRESSOR STATION AT 5:18 AM. A TEJAS OPERATOR ARRIVED ON SITE AT 5:23 AM. AT 5:31 AM IT HAD BEEN DETERMINED THAT THE 4" RELIEF VALVE CONNECTED TO TRAILSTONE UNIT 5010 HAD BEEN RELIEVING PRESSURE CAUSING THE LOUD NOISE. THE UNIT WHICH WAS RUNNING AT THE TIME OF THE EVENT WAS LOCKED OUT AND THE STATION WAS BROUGHT BACK ONLINE AT 6:45 AM. A UNIT DISCHARGE RELIEF VALVE WAS FOUND TO HAVE DRIFTED FROM ITS LAST KNOWN SET PRESSURE, OPENING PREMATURELY AT 846 PSIG RELEASING 8,802 MCF. THE INVESTIGATION FOUND THAT THE RELIEF VALVE'S DESIGNED SET POINT IS 1050 PSIG HOWEVER, THE INVESTIGATION ALSO FOUND THAT THE RELIEF VALVE WAS LAST SET AT 970 PSIG. IT IS BELIEVED THAT THE CAUSE FOR THE RELIEF VALVE DRIFT WAS DUE TO VIBRATION AND PRESSURE PULSATIONS FROM THE UNIT. ADDITIONAL CONTRIBUTING FACTORS TO THE AMOUNT OF UNINTENTIONAL RELEASED GAS WAS THAT THE RELIEF VALVE'S VENT LINE CONNECTING PIPE NIPPLE FOR THE PRESSURE SWITCH WAS FOUND TO HAVE BEEN BROKEN AT THE CONNECTING THREADS TO THE PRESSURE SWITCH. BY VISUAL EXAMINATION THE PIPE NIPPLE WAS DETERMINED NOT TO MEET TEJAS SCHEDULE 160 REQUIREMENTS. POST-INCIDENT IT WAS DISCOVERED THAT THE LADDER LOGIC ASSOCIATED WITH THE PRESSURE SWITCH HAD NOT BEEN ENABLED. HAD THE LADDER LOGIC BEEN ENABLED, WITH THE ACTIVATION OF THE PRESSURE SWITCH, IT WOULD HAVE STOPPED THE UNIT THEREFORE REDUCING THE AMOUNT OF UNINTENTIONAL RELEASED GAS. UPON RESTARTING THE UNIT AFTER THE EVENT, THE TECHNICIAN NOTICED THERE WAS BACKFLOW INTO THE UNIT COMING FROM THE DISCHARGE PIPING DOWNSTREAM OF THE CHECK VALVE. FURTHER INVESTIGATION OF THE CHECK VALVE DETERMINED THAT THE CHECK VALVE'S FLAPPER ON THE DISCHARGE PIPELINE FAILED DURING THIS EVENT. HOWEVER, IT IS NOT BELIEVED THAT THIS FAILURE WAS A CONTRIBUTING FACTOR TO THE AMOUNT OF GAS RELEASED RATHER IT WAS A RESULT OF THE DISCHARGE PULSATING EVENTS ASSOCIATED WITH THE CONTINUED COMPRESSOR OPERATIONS AND THE PRESSURE FLUCTUATIONS ASSOCIATED WITH THE ON/OFF ACTIVATION OF THE DISCHARGE RELIEF VALVE. THE 48-HR NRC INCIDENT REPORT NUMBER IS 1243256.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190059 | 32813 | 2019-05-22 10:06 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-04-23 13:04 | 2019 |  |  | 39.6392 | -79.3394 | 1243531 | 2019-04-23 16:23 |  | NATURAL GAS |  | 3136 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-23 13:04 | 2019-04-23 14:43 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-23 13:04 | 2019-04-23 13:04 | ONSHORE | MD | 21520 | KAESE MILL | GARRETT | MILEPOST | 0 | ACCIDENT COMPRESSOR STATION | ACCI-UNIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 8374 | 13231.3595800524934383202099737532808399 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8374 | 8681.706036745406824146981627296587926509 | 13231.3595800524934383202099737532808399 | [8 empty] | 2368 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS TRIGGERED BY A FIRE DETECTOR AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ESD WAS TRIGGERED AS A RESULT OF THE FIRE DETECTOR DETECTING A FLAME SIGNATURE NEAR THE SALT BATH HEATER. | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | NO | [150 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1243693 AT APPROXIMATELY 1:04 PM EDT ON APRIL 23, 2019, AN EMERGENCY SHUTDOWN (ESD) SYSTEM WAS ACTIVATED AT ACCIDENT COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN GARRETT COUNTY, MARYLAND. TETLP COMPLETED THE REPORT TO THE NATIONAL RESPONSE CENTER AT APPROXIMATELY 4:23 EDT ONCE IT WAS DETERMINED THE GAS LOSS VOLUME EXCEEDED 3 MMSCF. THE ESD OCCURRED WHILE RETURNING A SALT BATH HEATER (SBH) BACK TO NORMAL OPERATIONS. THIS PROCESS INVOLVES USING GAS FIRED AUXILIARY BURNERS TO HEAT THE SALT TO A LIQUID STATE AND USING THE MAIN BURNERS TO KEEP THE SALT AT A LIQUID STATE AFTER THE GAS FIRED AUXILIARY BURNER IS DEACTIVATED. THIS PROCESS WAS BEING PERFORMED IN ACCORDANCE WITH THE MANUFACTURER'S RECOMMENDED PROCEDURE. THE ESD WAS TRIGGERED BY THE FIRE DETECTOR NEAR THE GAS FIRED AUXILIARY HEATER THAT DETECTED THE FLAME SIGNATURE. TETLP'S INVESTIGATION DETERMINED THAT BOTH THE AUXILIARY HEATER AND THE FIRE DETECTOR WERE FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. AS PART OF THE MITIGATIVE PLAN, THE TEMPERATURE OF THE GAS POWERED AUXILIARY BURNER WAS LOWERED DURING STARTUP. SUPPLEMENTAL REPORT 10/14/19: CAUSE HAS BEEN UPDATED TO INCORRECT OPERATION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190060 | 32814 | 2019-05-22 14:38 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-04-27 07:03 | 2019 |  |  | 39.6392 | -79.3394 | 1243893 | 2019-04-27 08:02 |  | NATURAL GAS |  | 3324 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-27 07:03 | 2019-04-27 13:38 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-27 07:03 | 2019-04-27 07:03 | ONSHORE | MD | 21520 | KAESE MILL | GARRETT | MILEPOST | 0 | ACCIDENT COMPRESSOR STATION | ACCI-UNIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 8876 | 14024.5459317585301837270341207349081365 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8876 | 9202.152230971128608923884514435695538058 | 14024.5459317585301837270341207349081365 | [8 empty] | 2477 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS TRIGGERED BY A FIRE DETECTOR AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ESD WAS TRIGGERED AS RESULT OF THE FIRE DETECTOR DETECTING A FLAME SIGNATURE NEAR THE SALT BATH HEATER. | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | NO | [150 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1244152 AT APPROXIMATELY 7:03 AM EDT ON APRIL 27, 2019, AN EMERGENCY SHUTDOWN (ESD) SYSTEM WAS ACTIVATED AT ACCIDENT COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN GARRETT COUNTY, MARYLAND. THE ESD OCCURRED WHILE RETURNING A SALT BATH HEATER (SBH) BACK TO NORMAL OPERATIONS. THIS PROCESS INVOLVES USING GAS FIRED AUXILIARY BURNERS TO HEAT THE SALT TO A LIQUID STATE AND USING THE MAIN BURNERS TO KEEP THE SALT AT A LIQUID STATE AFTER THE GAS FIRED AUXILIARY BURNER IS DEACTIVATED. THIS PROCESS WAS BEING PERFORMED IN ACCORDANCE WITH THE MANUFACTURER'S RECOMMENDED PROCEDURE. THE ESD WAS TRIGGERED BY THE FIRE DETECTOR NEAR THE GAS FIRED AUXILIARY BURNER THAT DETECTED THE FLAME SIGNATURE. TETLP'S INVESTIGATION DETERMINED THAT BOTH THE AUXILIARY BURNER AND THE FIRE DETECTOR WERE FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. AS PART OF THE MITIGATIVE PLAN, THE TEMPERATURE OF THE GAS POWERED AUXILIARY BURNER WAS LOWERED DURING STARTUP. FOLLOWING THIS ESD AT THE STATION, REVISIONS WERE MADE TO THE MITIGATIVE PLAN THAT NOW REQUIRES THE FIRE DETECTOR TO BE DISABLED WHEN RETURNING THE SBH TO OPERATIONS AND THE STATION MANNED LOCALLY UNTIL THE FIRE DETECTOR IS ACTIVATED. SUPPLEMENTAL REPORT 10/14/19: CAUSE HAS BEEN UPDATED TO INCORRECT OPERATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190061 | 32178 | 2019-05-22 16:12 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-04-22 14:36 | 2019 |  |  | 33.2328 | -97.6756 | 1243544 | 2019-04-23 17:11 |  | NATURAL GAS |  | 62.4 | 73.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-22 19:50 | 2019-04-24 18:50 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-22 14:37 | 2019-04-22 15:08 | ONSHORE | TX | 76234 | DECATUR | WISE | SURVEY STATION NO. | 16972 | W 12-1 | DECATUR TO BRIDGEPORT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 198 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 |  | 0.156 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY | [28 empty] | 1991 | 1991 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.2 | 0.7 | [7 empty] | CLASS 1 LOCATION | NO |  | 54 |  | NO | NO | NO |  |  |  |  | 183000 | 194285.054202950133 | 236 | 250.553403234405636 | 200 | 316.010498687664041994750656167979002625 | 165000 | 175175.048871512415 | 0 | 0 | 676 | 717.686866891772076 | MEALS |  | 349112 | 163626.1470198754827243254593175853018373 | 370744.3538432763897539947506561679790026 | [8 empty] | 240 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 19008 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | AUGER | POLE | YES | 1960726723 | TEXAS811 | CONTRACT LOCATOR | NO | NO | YES | 47 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | RON WHITSON | FIELD SUPERVISOR | ronald.whitson@atmosenergy.com | 940-872-6151 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1243764 ON APRIL 22, 2019 AT 14:36, A THIRD-PARTY CONTRACTOR HIT ATMOS ENERGY'S LINE W 12-1 WHILE DRILLING TO INSTALL A BILLBOARD POLE, PUNCTURING THE LINE AND CAUSING A LEAK. THE LINE SEGMENT WAS ISOLATED AT 19:50 AND A CONTROLLED GAS RELEASE WAS PERFORMED UNTIL THE PRESSURE WAS ELIMINATED. CNG RESOURCES WERE UTILIZED TO SERVE 5 CUSTOMERS DURING THE SHUTDOWN. ON APRIL 23, 2019 AT 19:02, THE DAMAGED SECTION OF PIPE WAS REMOVED AND REPAIRS COMMENCED. SERVICE WAS RESTORED AT 18:50 ON APRIL 24, 2019. AFTER INVESTIGATION OF THE INCIDENT, IT WAS DETERMINED THAT THE CONTRACT LOCATOR DID NOT APPROPRIATELY MARK THE LINE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190062 | 32965 | 2019-05-24 17:24 | SUPPLEMENTAL FINAL | 32645 | HILCORP ALASKA, LLC | 3800 CENTERPOINT DR. SUITE 1400 | ANCHORAGE | AK | 99503 | 2019-04-27 19:30 | 2019 |  |  | 60.7764 | -151.4333 | 1243956 | 2019-04-27 22:27 |  | NATURAL GAS |  | 1.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-04-27 20:00 | 2019-05-27 14:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-04-27 19:30 | 2019-04-27 19:30 | ONSHORE | AK | 99635 | Not Within a Municipality | KENAI PENINSULA BOROUGH | MILEPOST | MILE 4.48 | MIDDLE GROUND SHOALS | MGS A PIPELINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | SUBMERGED, ON SEAFLOOR |  |  | YES | [6 empty] | YES | UNCASED | COOK INLET | 60 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 8 |  | 0.594 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR | [9 empty] | PIPE GIRTH WELD | [18 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | CORROSION / WELD DISCONTINUITY | [5 empty] | CLASS 1 LOCATION | NO |  | 123 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 50 | 79.00262467191601049868766404199475065617 | 1500000 | 1592500.4442864765 | 0 | 0 | 0 | 0 |  |  | 1500050 | 702602.0416421197073490813648293963254593 | 1592579.44691114841601049868766404199475 | [8 empty] | 195 |  | 499 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 37193 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | DIVERS NOTICED THE LEAK DURING SUBSEA INSPECTIONS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | YES |  |  | YES | [24 empty] | 2017 | [35 empty] | YES | 2017 | 750 | NO | [13 empty] | NO | [63 empty] | JUSTIN SELVIK | REGULATORY COMPLIANCE SPECIALIST | jselvik@hilcorp.com | (907) 777-8538 |  |  |  |  | BEN WASSON | INTEGRITY ENGINEER | (907) 777-8447 | bwasson@hilcorp.com | DIVERS WERE CONDUCTING TACTILE INSPECTIONS OF A METAL LOSS ANOMALY IDENTIFIED BY A 2017 ILI WHEN THE DIVE BOAT NOTICED SMALL BUBBLES AT THE WATER SURFACE. UPON INVESTIGATION, DIVERS FOUND BUBBLES EMANATING FROM THE TOP OF THE PIPELINE NEAR A GIRTH WELD, LOCATED APPROXIMATELY FIVE FEET AWAY FROM THE ILI ANOMALY. PRODUCTION ON THE PLATFORM WAS SHUT-IN AND PIPELINE PRESSURE WAS REDUCED TO LIMIT THE LEAK TO THE FULLEST EXTENT WHILE MAINTAINING POSITIVE PRESSURE INSIDE THE PIPELINE. DIVERS BEGAN REPAIR ACTIVITIES, AND COMPLETED INSTALLATION OF A TEMPORARY CLAMP TO STOP THE LEAK WITHIN 24 HOURS OF DISCOVERY. THE INSTALLATION OF THE PERMANENT CLAMP TO REPAIR THE PIPELINE WAS COMPLETED ON MAY 24. HILCORP ALASKA SELECTED THE ONSHORE PIPELINE CLASSIFICATION IN PART B OF THIS REPORT. HOWEVER, HILCORP ALASKA AND PHMSA ARE CURRENTLY IN DISCUSSIONS REGARDING THE APPROPRIATE STATUS OF THE PIPELINE (ONSHORE VERSUS OFFSHORE).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190063 | 33239 | 2019-05-28 11:19 | SUPPLEMENTAL FINAL | 20044 | LINDE | 10 RIVERVIEW DR. | DANBURY | CT | 06810 | 2019-05-05 17:30 | 2019 |  |  | 29.8269 | -94.9946 | 1244769 | 2019-05-06 09:22 |  | HYDROGEN GAS |  | 65.4 | 759 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-06 12:30 | 2019-05-12 09:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-05 17:30 | 2019-05-05 18:30 | ONSHORE | TX | 77521 | BAYTOWN | HARRIS | MILEPOST | 105+72.74 | GCPO | 232 - H2 BAYTOWN SEG 2 10IN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 |  | 0.228 | 52000 | API 5LX52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | AMERICAN STEEL PIPE | EPOXY | [28 empty] | 1992 | 1992 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 156 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 873 | 926.835258574729323 | 75 | 118.503937007874015748031496062992125984 | 400000 | 424666.7851430604 | 100000 | 106166.6962857651 | 0 | 0 |  |  | 500948 | 234670.041581715686110622047244094488189 | 531878.820624408103338748031496062992126 | [8 empty] | 800 |  | 1100 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 35646 | NO |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK INDICATIONS WERE NOT VISIBLE FROM THE SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [306 empty] | SEAN BINGHAM | PIPELINE REGULATORY SPECIALIST | sean_bingham@praxair.com | 6302079543 |  |  |  |  | SEAN BINGHAM | PIPELINE REGULATORY SPECIALIST | 6302079543 | sean_bingham@praxair.com | AT 1730 ON 5 MAY 2019, PRAXAIR WAS NOTIFIED BY A THIRD PARTY THAT THERE WAS A POSSIBLE LEAK ON ITS HYDROGEN PIPELINE, AS IDENTIFIED BY SOUND. PRAXAIR PERSONNEL ARRIVED ON THE SITE AT 1830 AND CONFIRMED THAT HYDROGEN WAS PRESENT IN THE AREA. THE LOCATION WAS IN AN ISOLATED AREA. MANUAL ISOLATION VALVES WERE SHUT TO CLOSE IN THE SEGMENT AND IT WAS MANUALLY BLOWN DOWN. AT 0852 ON 6 MAY 2019, PRAXAIR DETERMINED THAT THE INCIDENT MET REPORTABLE CRITERIA AND CALLED THE NATIONAL RESPONSE CENTER AT 0922. BLOWDOWN OF THE ISOLATED SEGMENT WAS COMPLETED AT 1230 ON 6 MAY 2019. THERE WAS NO IMMEDIATELY RECOGNIZABLE CAUSE OF THE INCIDENT. NO EXCAVATORS WERE OPERATING IN THE AREA, AND CP TESTING SHOWED NO ABNORMALITIES. THE SUSPECTED AREA OF THE LEAK WAS EXCAVATED, BUT THE PIPE WAS SHOWN TO BE IN EXCELLENT CONDITION. UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE LEAK WAS MOST LIKELY LOCATED UNDERNEATH A SMALL NON-NAVIGABLE DRAINAGE CANAL. UNABLE TO EXCAVATE UNDER THE WATER, A NEW SEGMENT OF PIPE WAS INSTALLED, REROUTING AROUND THE LEAK. THE PIPELINE WAS PUT BACK INTO SERVICE ON 12 MAY 2019 AT 0930. IN JUNE 2019, THE INACTIVE SEGMENT OF PIPE WAS FURTHER INVESTIGATED WITH A TETHERED INLINE INSPECTION (ILI) TOOL IN ORDER TO FURTHER INVESTIGATE THE CAUSE OF THE LEAK. RESULTS SHOWED AN ANOMALY IN THE VICINITY OF A GROUNDING ROD FOR A NEARBY ELECTRICAL TRANSMISSION TOWER. AN ADDITIONAL DCVG INSPECTION SHOWED A SIMILAR ANOMALY, CORRELATING THE RESULTS OF THE ILI. IT IS THEREFORE SUSPECTED THAT LIGHTNING STRUCK THE TOWER DURING A STORM, CREATING A SURGE OF ENERGY THAT RELEASED INTO THE GROUND THROUGH THE GROUNDING ROD. THIS ELECTRICAL ENERGY CREATED THE ANOMALY ON THE PIPE WHICH EVENTUALLY LED TO THE SMALL LEAK. THE NEWLY INSTALLED SEGMENT OF PIPE IS NOT LOCATED IN THE VICINITY OF THE GROUNDING ROD. AN EXTERNAL INSPECTION COMPANY WAS HIRED TO REVIEW PIPELINE LOCATIONS WITH SIMILAR ENVIRONMENTS THROUGHOUT THE PIPELINE SYSTEM. NO OTHER ANOMALIES WERE DISCOVERED AND A SIMILAR INCIDENT IS NOT SUSPECTED TO OCCUR AGAIN.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190064 | 33419 | 2019-05-31 08:41 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-05-02 22:39 | 2019 | CENTRAL | YES | 34.6253 | -93.0407 | 1244490 | 2019-05-03 02:03 | 1244649 | NATURAL GAS |  | 51886 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-05-03 01:20 | 2020-02-02 09:30 |  | YES | OPERATOR | 2019-05-02 | NO | [5 empty] | VALVE CLOSURE |  | 2019-05-03 01:00 | VALVE CLOSURE |  | 2019-05-03 01:00 | 350 | 2019-05-02 22:50 | 2019-05-03 01:00 | ONSHORE | AR | 71909 | HOT SPRINGS VILLAGE | GARLAND | MILEPOST | 4131+28 | BT-1 | BT-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.328 | 65000 | API 5LX | SINGLE SAW |  | REPUBLIC | ASPHALT |  | YES | [26 empty] | 1973 | 1973 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 120 | 60 |  | CLASS 1 LOCATION | NO |  | 655 |  | NO | NO | [5 empty] | 86421 | 91750.320597121057071 | 0 | 0 | 136979 | 216434.0104986876640419947506561679790026 | 4746798 | 5039518.615958772051498 | 25000 | 26541.674071441275 | 0 | 0 |  | 2.64 | 4995198 | 2417440.84996993641105732545931758530184 | 5374244.621126022047610994750656167979 | 0 | 0 | 10 | 0 | NO |  |  |  | 962 | 160000 | 1000 | 192.619(A)(1) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 88338 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | NEAR NEUTRAL PH SCC ACTING WITHIN AREA OF EXTERNAL CORROSION. | 1426 | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | NO | [13 empty] | NO | [45 empty] | YES | [17 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 5/2/2019 AT 22:39 ENABLE GAS TRANSMISSION LINE BT-1 EXPERIENCED A FAILURE NEAR HOT SPRINGS VILLAGE IN GARLAND COUNTY, ARKANSAS. THE FAILED SECTION OF BT-1 WAS SENT TO STRESS ENGINEERING SERVICES (SES) FOR METALLURGICAL ANALYSES. AS OF THE DUE DATE FOR THIS REPORT, THE LINE IS CURRENTLY OUT OF SERVICE AND THE RESULTS OF THE ANALYSIS HAVE NOT BEEN RECEIVED. PRELIMINARY FINDINGS FOR THE FAILURE ARE NEAR NEUTRAL STRESS CORROSION CRACKING ACTING WITHIN AREA OF EXTERNAL CORROSION. THE NRC WAS NOTIFIED ON 5/3/2019 AT 02:03 (NRC#1244490). A 48 HOUR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 5/4/2019 AT 14:54 (NRC# 1244649). THE FAILURE INVESTIGATION IS ON-GOING. ------UPDATE------ BASED ON EXAMINATIONS AND ANALYSIS BY STRESS ENGINEERING, IT WAS DETERMINED THE PIPE FAILED AS A RESULT OF NEAR-NEUTRAL PH STRESS CORROSION CRACKING (SCC) IN CONCERT WITH GENERAL EXTERNAL CORROSION THAT REDUCED THE WALL THICKNESS NEAR THE 6 O'CLOCK ORIENTATION OF THE PIPE. THE PIPELINE CONTINUES TO BE OUT OF SERVICE UNTIL ALL OF THE 30" IS HYDROTESTED. ------UPDATE------ THE LINE HAS BEEN FULLY HYDROTESTED AND WAS PLACED BACK INTO SERVICE ON FEBRUARY 2, 2020. 09/25/2019 SUPPLEMENTAL A.10 GAS LOSS VOLUME UPDATED. D.7 UPDATED CONSTRUCTION COSTS D.7.F GAS LOSS TOTAL UPDATED G.1 UPDATED TO DETERMINED BY METALLURGICAL ANALYSIS H. NARRATIVE UPDATED 2/3/2020 SUPPLEMENTAL A.15.B UPDATED TO 2/2/2020 AND 09:30 C.3.D UPDATED TO API-5L C.3.E UPDATED TO SUBMERGED ARC WELDING D.7 COSTS UPDATED E.5.C ENTERED 88,338 H. NARRATIVE UPDATED
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190065 | 32545 | 2019-05-31 11:38 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2019-05-02 23:54 | 2019 |  |  | 40.2277 | -103.8131 | 1244489 | 2019-05-03 00:57 |  | NATURAL GAS |  | 12626 | 166 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-08 19:00 | 2019-05-15 19:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-02 23:20 | 2019-05-02 23:54 | ONSHORE | CO | 80701 | FORT MORGAN | MORGAN | SURVEY STATION NO. | 11+2414 | FORT MORGAN LOOP | 4B | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | VALVE STEM/OPERATOR |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 1959 | 1959 | CARBON STEEL |  | OTHER | [8 empty] | VALVE FLANGE PULLED APART JUST ENOUGH TO ALLOW GAS RELEASE | CLASS 1 LOCATION | NO |  | 130 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 332 | 352.473431668740132 | 25252 | 39899.4855643044619422572178477690288714 | 80000 | 84933.35702861208 | 2500 | 2654.1674071441275 | 0 | 0 |  |  | 108084 | 64975.6540321387973880524934383202099738 | 127839.4834317294095742572178477690288714 | [8 empty] | 630 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 29357 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS COULD NOT HAVE CONTRIBUTED TO AN INCIDENT FROM 3RD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | KENNETH PETERS | SENIOR PIPELINE ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | LATE NIGHT MAY 2, 2019, A FARMER WAS RUNNING A TRACTOR PLANTER IN A CIRCULAR PATTERN, PLANTING A FIELD OF CORN. THE TRACTOR PLANTER RAN THROUGH A STEEL BARRICADE AND OVER COLORADO INTERSTATE GAS (CIG) TRANSMISSION'S LINE 4B ABOVEGROUND VALVE STEM/OPERATOR. THIS CAUSED THE VALVE FLANGE TO PULL APART BELOWGROUND AND RELEASE NATURAL GAS. THE FARMER SHUT DOWN THE TRACTOR AND REMOVED HIMSELF FROM THE SCENE. CIG OPERATIONS PERSONNEL SECURED THE SITE AND DETERMINED THAT THERE WAS NO THREAT TO THE GENERAL PUBLIC SINCE THE OCCURRENCE WAS IN THE MIDDLE OF A FIELD, AWAY FROM ANY POPULATED AREAS. THE NEED TO MAINTAIN SERVICE TO CUSTOMERS RESULTED IN ALLOWING THE GAS TO CONTINUE TO RELEASE UNTIL A BYPASS COULD BE CONSTRUCTED AND INSTALLED. FOLLOWING THIS, ISOLATION VALVES WERE CLOSED AND THE PIPELINE WAS BLOWN DOWN TO ALLOW REMOVAL OF THE TRACTOR PLANTER AND REPAIR OF THE FACILITY. THE FACILITY WAS RESTORED TO SERVICE MAY 15, 2019. THE NECESSARY 48-HOUR UPDATE WAS PROVIDED TO THE NRC MAY 4, 2019 AT 13:06 MDT AND WAS ASSIGNED REPORT NUMBER 1244639.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190066 | 32600 | 2019-06-05 11:21 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-05-15 15:50 | 2019 |  |  | 30.6397 | -93.9097 | 1246205 | 2019-05-20 10:45 |  | NATURAL GAS |  | 0.1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | MINOR LEAK ONLY REPORTED BECAUSE REPAIR COST MAY EXCEED $50,000 | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-15 15:50 | 2019-05-15 15:50 | ONSHORE | TX | 75956 | KIRBYVILLE | JASPER | MILEPOST | 120.33 | BEAUMONT-LATEX LINE | INDEX 64 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 30000 | API 5L | LAP WELDED |  | UNKNOWN | ASPHALT | [28 empty] | 1924 | 1924 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 196 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 55000 | 58391.682957170805 | 0 | 0 | 0 | 0 |  |  | 55000 | 25760.174160298545 | 58391.682957170805 | [8 empty] | 155 |  | 292 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 116160 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK NOT DETECTABLE BY SCADA | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpmlp.com | 2706886357 |  |  |  |  | DARRAL WARD | MANAGER PIPELINE SAFETY | 2706886356 | darral.ward@bwpmlp.com | GULF SOUTH'S PIPELINE TECH FOUND A MINOR LEAK DURING LINE PATROL OF ITS INDEX 64. THE LINE IS IN A CREEK EXPOSURE. INDEX 64 IS OPERATING AT 155 PSIG AND HAS A MAOP OF 292 PSIG. THE LEAK IS SMALL AND 700 FT. FROM THE NEAREST STRUCTURE AND HIGHWAY. THE AREA WAS FLAGGED OFF AND CONTACT AT THE NEAREST PROPERTY WAS MADE. GULF SOUTH WILL INVESTIGATE THE LEAK TO DETERMINE WHAT REPAIR METHOD IS NEEDED. A PIPE REPLACEMENT IS THE LIKELY THE BEST REPAIR WHICH WOULD CAUSE THE COST TO EXCEED $50,000, MEETING THE PHMSA DEFINITION FOR INCIDENT. FOR THIS REASON, THE NRC WAS CALLED. THE GAS LOSS REMAINS UNKNOWN, BUT MINIMAL, AT THIS TIME AND THEREFORE, A GAS LOSS COST IS NOT DOCUMENTED IN THIS REPORT. THE RESPONSES TO PART E QUESTIONS 5A, 5B, AND 5C REPRESENT THE ANSWERS THAT WILL BE TRUE WHEN THE SECTION IS ISOLATED AND BLOWN DOWN; THAT HAS NOT YET HAPPENED BUT THE ANSWERS ARE POPULATED BECAUSE THE PORTAL WILL NOT ALLOW SUBMISSION OF THIS REPORT WITHOUT POPULATING THESE FIELDS. 8-21-19 UPDATE TO SUBMIT FINAL REPORT. A PLIDCO BOLT-ON CLAMP WAS INSTALLED. UPDATED REPAIR COSTS ACCORDINGLY. IN RESPONSE TO PHMSA EMAIL DATED 6-18-19, THE DATE SHOWN IN PART A, ITEM 4 (5-15-2019) IS CORRECT. THIS WAS THE DATE THE "POTENTIAL" LEAK WAS FIRST DISCOVERED ALTHOUGH IT WAS NOT A CONFIRMED LEAK NOR YET CONFIRMED WHAT THE REPAIR WOULD BE, THEREFORE, REPAIR COSTS COULD NOT YET BE ESTIMATED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190067 | 32584 | 2019-06-05 11:24 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-05-10 18:45 | 2019 |  |  | 39.7902 | -88.3589 | 1245594 | 2019-05-14 10:53 |  | NATURAL GAS |  | 3121.014 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | ISOLATED UNIT 1215 | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-10 18:47 | 2019-05-10 19:03 | ONSHORE | IL | 61953 | TUSCOLA | DOUGLAS | MILEPOST | 0+00 | TUSCOLA COMPRESSOR STATION | UNIT 1215 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1963 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE SETPOINT WAS SET TOO LOW | CLASS 1 LOCATION | NO |  | 331 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 8239 | 13018.0524934383202099737532808398950131 | 0 | 0 | 0 | 0 | 157 | 166.681713168651207 | 4 MAN HOURS FOR CALL-OUT |  | 8396 | 8615.278994881726464627296587926509186352 | 13184.7342066069714169737532808398950131 | [8 empty] | 843 |  | 900 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DID NOT EXCEED MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | TEST STAND WORN CAUSING RELIEF VALVE ACTUAL SET PRESSURE TO BE LOW | [15 empty] | YES | TEST STAND WORN CAUSING RELIEF VALVE ACTUAL SET PRESSURE TO BE LOW | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 5/10/19 18:47 CST PROPERTY OWNER NOTIFIED OPERATIONS OF GAS BLOWING AT STATION. 5/10/19 18:49 CST YARD NOISE ALARM TO GAS CONTROL. 5/10/19 19:03 CST UNIT 1215 SHUTDOWN AND TAKEN OUT OF SERVICE. 5/14/19 10:53 CST NRC TELEPHONIC NOTIFICATION MADE NRC#1245594. 5/14/19 11:11 CST PHMSA AID UPDATED. 5/16/19 10:16 CST 48-HOUR NRC NOTIFICATION MADE NRC#1245848. 5/16/19 10:47 CST PHMSA AID UPDATED. THE SUPPLEMENTAL REPORT SUBMITTED 8/20/19, IS MADE TO UPDATE PART D: 7D AND TO FURTHER CLARIFY THE EVENT. - THERE WERE NO REPAIRS REQUIRED TO THE RELIEF VALVE AS IT FUNCTIONED PROPERLY. IT WAS A FAULTY TEST STAND USED DURING THE TEST AND INSPECT OF THE RELIEF VALVE THAT LED TO THE SET-POINT BEING SET BELOW WHERE IT SHOULD HAVE BEEN SET, RESULTING IN THE RELEASE OF GAS. - THE TEST STAND WAS COMPLETELY REBUILT AND THE ACCURACY CONFIRMED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190068 | 32512 | 2019-06-07 11:14 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-05-08 20:02 | 2019 |  |  | 37.5801 | -84.7499 | 1245076 | 2019-05-08 22:12 |  | NATURAL GAS |  | 19350 | 226 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-08 20:43 | 2019-05-10 17:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-08 20:02 | 2019-05-08 20:35 | ONSHORE | KY | 40422 | DANVILLE | LINCOLN | MILEPOST | 427.273 | DANVILLE COMPRESSOR STATION | DANV-OWSV | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1948 |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 590 | 626.38350808601409 | 50504 | 79798.9711286089238845144356955380577428 | 0 | 0 | 3000 | 3185.000888572953 | 0 | 0 |  |  | 54094 | 54041.2268487098423701049868766404199475 | 83610.3555252678909745144356955380577428 | [8 empty] | 800 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. AN ESD ISOLATION VALVE DID NOT CLOSE PROPERLY AND THE THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1245382 AT APPROXIMATELY 8:02 PM EDT ON MAY 8, 2019, A NATURAL GAS RELEASE FROM THE EMERGENCY SHUTDOWN (ESD) SYSTEM OCCURRED AT THE DANVILLE COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) IN LINCOLN COUNTY, KENTUCKY. TETLP PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 8:35 PM EDT AND DETERMINED THAT A VALVE (LINE 10 ESD ISOLATION VALVE) DID NOT CLOSE PROPERLY CAUSING THE GAS RELEASE AFTER THE ESD SYSTEM WAS ACTIVATED. THE TETLP PERSONNEL SUBSEQUENTLY ISOLATED THE ESD SYSTEM AT APPROXIMATELY 8:43 PM EDT, STOPPING THE GAS RELEASE. THE STATION WAS RETURNED TO NORMAL OPERATIONS ON MAY 10, 2019. THE APPARENT CAUSE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT: TETLP HAS COMPLETED ITS INVESTIGATION OF THE MAY 8, 2019 ESD EVENT AT DANVILLE COMPRESSOR STATION. THE EMERGENCY SHUTDOWN (ESD) SYSTEM ACTIVATION WAS CAUSED BY A TRIP IN THE BREAKER SUPPLYING ELECTRICITY TO THE ESD PANEL RESULTING FROM A SHORT IN THE WIRING THAT RUNS FROM THE ESD PANEL TO AN ESD PULL-BUTTON. THE ESD SYSTEM ACTIVATED, BUT ONE OF THE ESD BLOCK VALVES, VALVE# 10-296, DID NOT CLOSE AS INTENDED. THE BLOCK VALVE HAD BEEN DEACTIVATED DURING THE ROUTINE TESTING AND INSPECTION OF THE ESD AS REQUIRED BY COMPANY PROCEDURES, HOWEVER, THE BLOCK VALVE WAS NOT REACTIVATED AFTER THE ROUTINE TESTING AND INSPECTION HAD BEEN COMPLETED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190069 | 32353 | 2019-06-10 12:26 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-05-23 | 2019 |  |  | 31.989 | -102.484 | 1247712 | 2019-06-03 14:33 |  | NATURAL GAS |  | 5232 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | #3 COMPRESSOR SHUT DOWN, STATION CONTINUED TO OPERATE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-23 20:30 | 2019-05-24 07:00 | ONSHORE | TX | 79741 | Not Within a Municipality | ECTOR | MILEPOST | COMPRESSOR ST | ONEOK WESTEX TRANSMISSION ECTOR CO. COMPRESSOR STA | ONEOK INDEX NUMBER 4056-000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2016 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SUCTION VALVE | OTHER | [8 empty] | RELIEF OPENED WHEN SUCTION VALVE FAILED TO CLOSE | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 14269 | 22545.7690288713910761154855643044619423 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 14269 | 14793.3202099737532808398950131233595801 | 22545.7690288713910761154855643044619423 | [8 empty] | 957 |  | 1188 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | COMPRESSOR SUCTION ISOLATION VALVE | [22 empty] | YES | STATION PROGRAMING DID NOT INITIATE SUCTION VALVE CLOSURE DURING ENGINE SHUTDOWN | [161 empty] | BRACKEN HILL | COMPLIANCE SPECIALIST | bracken.hill@oneok.com | 806-324-9702 |  |  |  |  | BRACKEN HILL | COMPLIANCE SPECIALIST | 806-324-9702 | bracken.hill@oneok.com | AT APPROXIMATELY 20:30 ON 5/23/2019, THE HIGH TURBO TEMPERATURE ALARM INITIATED AN ENGINE SHUTDOWN FOR THE NUMBER 3 COMPRESSOR AT THE ONEOK WESTEX TRANSMISSION, ECTOR COUNTY COMPRESSOR STATION. AS THE COMPRESSOR SHUT DOWN THE STATION ALARM CONTROL LOGIC FAILED TO AUTOMATICALLY CLOSE THE SUCTION VALVE TO THE COMPRESSOR. FAILURE TO CLOSE THE SUCTION VALVE CAUSED 5232 MCF OF NATURAL GAS TO BE RELEASED THROUGH THE VENT VALVE.THE RELEASE WAS IDENTIFIED BY ONEOK OPERATIONS TEAM MEMBERS WHEN THEY ARRIVED ON SITE AT 07:00 ON 5/24 AND REVIEWED THE STATION CONTROL LOG. ONEOK TECHNICIANS REVIEWED THE PROGRAMMING LOGIC FOR THE CONTROLS OF THE COMPRESSOR. CORRECTIONS WERE MADE TO THE UNITS PROGRAMMING TO INSURE THE SUCTION VALVE CLOSES WHENEVER SHUT DOWN BY AN ALARM; TO PROHIBIT THIS EVENT FROM REOCCURRING.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190071 | 32325 | 2019-06-24 14:03 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-05-25 02:00 | 2019 |  |  | 39.9307 | -78.5767 | 1246785 | 2019-05-25 10:02 |  | NATURAL GAS |  | 5900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RELIEF VALVE WAS ISOLATED AND HAD NO IMPACT ON PIPELINE OPERATIONS. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-25 06:30 | 2019-05-25 07:00 | ONSHORE | PA | 15522 | BEDFORD | BEDFORD | MILEPOST | 59.617 | M&R 71144 | BEDF-CHAM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 103 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 15342 | 24241.1653543307086614173228346456692913 | 0 | 0 | 1000 | 1061.666962857651 | 0 | 0 |  |  | 16342 | 16374.114834410581992125984251968503937 | 25302.8323171883596614173228346456692913 | [8 empty] | 300 |  | 1389 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ACTIVATION OF THE RELIEF VALVE RELEASE COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF THE A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | PRESSURE REGULATOR LEAKAGE DUE TO CUSTOMER DEMAND DROPPING TO ZERO FLOW | [161 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1246924 AT APPROXIMATELY 6:30 AM EDT ON MAY 25, 2019, TEXAS EASTERN TRANSMISSION (TETLP) RECEIVED NOTIFICATION FROM A LAND OWNER ABOUT A RELEASE OF NATURAL GAS AT TETLP'S METER AND REGULATOR STATION (M&R 71144) IN BEDFORD COUNTY, PA. TETLP'S EMPLOYEE ARRIVED AT M&R 71144 AT APPROXIMATELY 7:00 AM EDT AND DISCOVERED A NATURAL GAS RELEASE THROUGH A RELIEF VALVE. THE EMPLOYEE STOPPED THE RELEASE BY CLOSING AN ISOLATION VALVE. THE RELIEF VALVE ACTIVATED BECAUSE THE CUSTOMER DEMAND HAD DROPPED TO ZERO FLOW (NOT UNUSUAL WITH WARM WEATHER) AND THE PRIMARY PRESSURE REGULATOR (SET AT 285 PSIG) SHUT OFF (AS INTENDED) THOUGH IT LEAKED A SMALL QUANTITY OF GAS THROUGH IT. THE SMALL LEAKAGE CAUSED THE PRESSURE TO BUILD UP UNTIL THE RELIEF VALVE ACTIVATED AT 300 PSIG. TETLP'S EMPLOYEE SUBSEQUENTLY INSPECTED THE RELIEF VALVE AND PRESSURE REGULATOR AND DETERMINED THAT THERE WERE NO MECHANICAL FAILURES (OTHER THAN THE SMALL LEAKAGE THROUGH THE REGULATOR WHEN THE CUSTOMER DEMAND WAS ZERO). THERE WAS NO OTHER IMPACT DUE TO THE RELEASE. THE PRESSURE REGULATOR SETTING AND RELIEF VALVE SETTINGS WERE ADJUSTED TO ACCOMMODATE FOR LOW DEMAND SUMMER CONDITIONS. TETLP REVIEWED THE SCADA DATA AT APPROXIMATELY 9:45 AM EDT ON MAY 25, 2019 AND DETERMINED THAT THE RELIEF VALVE BEGAN VENTING AT APPROXIMATELY 2 AM EDT ON MAY 25, 2019. TETLP WAS ABLE TO CALCULATE THE GAS LOSS BY CALCULATING THE RELIEF VALVE CAPACITY FLOW RATE AND OVER A 5-HOUR DURATION. TETLP SUBSEQUENTLY NOTIFIED THE NRC AT APPROXIMATELY 10:02 EDT.
2023-02-28 09:42 | YES | YES | GG (Gas Gathering) | 20190072 | 33829 | 2019-06-27 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-05-28 22:55 | 2019 | EASTERN | NO | 41.072 | -79.241 | 1247157 | 2019-05-29 14:04 | 1247379 | NATURAL GAS |  | 2400 | 7.78 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-05-29 13:55 | 2019-09-20 13:00 |  | NO |  |  | YES | 2019-05-29 13:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2400 | YES | VALVE CLOSURE |  | 2019-05-29 12:15 | VALVE CLOSURE |  | 2019-05-29 12:17 | 2 | 2019-05-29 13:55 | 2019-05-28 23:55 | ONSHORE | PA | 16240 | MAYPORT | CLARION | MILEPOST | 682+07 | LINE 4010 | 4010-015 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.156 | 42000 | X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EXTRUDED POLYEHYLENE |  | NO | [26 empty] | 1982 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 93 |  | YES | YES | NO |  |  |  |  | 1000000 | 1061666.962857651 | 18 | 19.110005331437718 | 5520 | 8721.889763779527559055118110236220472441 | 250000 | 265416.74071441275 | 250000 | 265416.74071441275 | 300000 | 318500.0888572953 | ROOT CAUSE FAILURE ANALYSIS AND OTHER ENGINEERING COSTS | 2.3 | 1805538 | 848791.5104942559526805826771653543307087 | 1919741.53291288276527705511811023622047 | 0 | 1 | 2 | 2 | NO |  |  |  | 32 | 1000 | 50 | 192.619(A)(2) |  | 1982-08-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1076 | NO | YES | YES | [5 empty] | YES |  | YES |  |  |  |  | TYPE B GATHERING | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE 4010 IS NOT COVERED UNDER THE SCADA SYSTEM. NO ACTIVITIES BY THE GAS CONTROLLER | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES |  | YES |  |  |  |  | DIRECT CURRENT | CATHODIC PROTECTION CURRENT FROM NEARBY PROTECTED PIPELINE | YES | YES |  |  | YES | NO |  | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | (304)357-3596 |  |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | (304)357-2245 | paul_shaffer@tcenergy.com | ON MAY 28, 2019, AT APPROXIMATELY 10:55 P.M., COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) RECEIVED NOTICE OF A POTENTIAL INCIDENT AT 2464 PINE RUN ROAD NEAR MAYPORT, PENNSYLVANIA. THE INCIDENT LOCATION WAS ADJACENT TO A COLUMBIA PIPELINE, LINE 4010, WHICH IS PART OF A 13.88-MILE GATHERING SYSTEM THAT TRANSPORTS GAS FROM PRODUCTION FACILITIES IN JEFFERSON AND CLARION COUNTIES, PENNSYLVANIA, TO A COMPRESSOR STATION IN RIMERSBURG, PENNSYLVANIA. THE FEDERAL POWER COMMISSION ORIGINALLY APPROVED COLUMBIA'S ACQUISITION OF LINE 4010 IN 1971, AND THE PIPELINE REMAINS SUBJECT TO THE JURISDICTION OF THE FEDERAL ENERGY REGULATORY COMMISSION UNDER THE NATURAL GAS ACT. COLUMBIA'S RECORDS INDICATE THAT THE SECTION ADJACENT TO THE INCIDENT LOCATION WAS REPLACED IN 1982 USING 0.156-INCH WALL THICKNESS, 6-INCH NPS CARBON STEEL PIPE WITH AN EXTRUDED POLYETHYLENE COATING. COLUMBIA'S RECORDS ALSO INDICATE THAT AT THE TIME OF THE INCIDENT THE MAXIMUM ALLOWABLE OPERATING PRESSURE OF LINE 4010 WAS 50 PSIG, PRODUCING A HOOP STRESS THAT IS LESS THAN 20 PERCENT OF SPECIFIED MINIMUM YIELD STRENGTH OF THE LINE PIPE, AND THAT THE OPERATING PRESSURE WAS 32 PSIG. COLUMBIA'S RECORDS FURTHER INDICATE THAT THE SECTION ADJACENT TO THE INCIDENT LOCATION WAS NOT PART OF A REGULATED GATHERING LINE, ALTHOUGH PHMSA AND COLUMBIA ARE CURRENTLY REVIEWING THAT DETERMINATION. COLUMBIA OPERATIONS PERSONNEL ARRIVED AT THE INCIDENT LOCATION AT APPROXIMATELY 11:10 P.M. A RESIDENCE AT THE LOCATION SUSTAINED FIRE-RELATED DAMAGE, AND AN OCCUPANT SUSTAINED INJURIES NECESSITATING IN-PATIENT HOSPITALIZATION. ANOTHER SINGLE-FAMILY DWELLING IN THE VICINITY WAS EVACUATED AS A PRECAUTIONARY MEASURE. AS PART OF ITS INITIAL RESPONSE TO THE INCIDENT, COLUMBIA SURVEYED THE AREA TO IDENTIFY POTENTIAL LEAK SOURCES, ISOLATED THE AFFECTED SECTION, AND TOOK OTHER REMEDIAL ACTIONS IN COOPERATION WITH STATE AND LOCAL AUTHORITIES. COLUMBIA ALSO SUBMITTED INCIDENT REPORTS TO THE NATIONAL RESPONSE CENTER (NRC) ON MAY 29, 2019 (NRC REPORT NO. 1247157), AND MAY 31, 2019 (NRC. REPORT NO. 1247379). A THIRD PARTY, ECHELON- APPLIED GEOSCIENCES CONSULTING, CONDUCTED A STRAY GAS ORIGIN STUDY AS PART OF COLUMBIA'S INCIDENT INVESTIGATION. THE STUDY REVEALED THAT THE STRAY GAS IN THE SOILS IN THE VICINITY OF THE INCIDENT LOCATION WAS OF THE SAME GENETIC ORIGIN AS THE GAS IN LINE 4010, AND THAT THERE WAS A FEASIBLE PATHWAY FOR LEAKING GAS TO MIGRATE FROM LINE 4010 TO THE RESIDENCE. HOWEVER, THE STUDY ALSO INDICATED THAT STRAY GAS DETECTED IN THE SOILS WAS OF THE SAME GENETIC ORIGIN AS GAS FROM A NEARBY WELL (API # 37-031-00978), WHICH IS THE SUBJECT OF AN ONGOING INVESTIGATION BY THE PENNSYLVANIA DEPARTMENT OF ENVIRONMENTAL PROTECTION (PADEP). ANOTHER THIRD PARTY, KIEFNER AND ASSOCIATES (KIEFNER), PREPARED A ROOT CAUSE FAILURE ANALYSIS (RFCA) FOR COLUMBIA. IN THE RCFA, KIEFNER CONCLUDED THAT A LEAK IN LINE 4010 BENEATH PINE RUN ROAD WAS THE SIGNIFICANT CONTRIBUTOR OF FUEL TO THE FIRE AT THE RESIDENCE, AND THAT THE LEAK WAS CAUSED BY EXTERNAL CORROSION. HOWEVER, KIEFNER ALSO NOTED THAT TWO OTHER POTENTIAL COMBUSTIBLE GAS SOURCES WERE PRESENT IN THE AREA: (1) A THIRD-PARTY METER STATION LOCATED TO THE SOUTH OF THE RESIDENCE, WHICH WAS LEAKING AT THE TIME OF THE INCIDENT, AND (2) A THIRD-PARTY WELL LOCATED ON A NEIGHBORING PROPERTY WITH GAS GEOCHEMISTRY THAT WAS INDISTINGUISHABLE FROM THE GAS IN LINE 4010. KIEFNER COULD NOT OFFER A CONCLUSIVE DETERMINATION ABOUT THE POSSIBLE INFLUENCE OF THESE OTHER GAS SOURCES ON THE INCIDENT. COLUMBIA IS IN THE PROCESS OF IMPLEMENTING THE RECOMMENDATIONS THAT KIEFNER INCLUDED IN THE RCFA TO PREVENT THE POTENTIAL RECURRENCE OF A SIMILAR INCIDENT. COLUMBIA HAS COOPERATED WITH THE VARIOUS AUTHORITIES INVOLVED IN THE INCIDENT INVESTIGATION AND WILL UPDATE THE INFORMATION PROVIDED IN THIS REPORT IF ADDITIONAL RELEVANT MATERIAL BECOMES AVAILABLE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190073 | 32346 | 2019-06-27 15:08 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-05-30 09:45 | 2019 |  |  | 35.8487 | -87.4505 | 1247267 | 2019-05-30 10:54 |  | NATURAL GAS |  | 48698 | 1956 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE INCIDENT OCURRED WHEN THE STATION WAS ALREADY OFF-LINE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-30 09:45 | 2019-05-30 09:45 | ONSHORE | TN | 37137 | NUNNELLY | HICKMAN | MILEPOST | CS 860 | COMPRESSOR STATION 860 | 500 LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1962 |  | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH BLOWDOWN STACK | [5 empty] | CLASS 3 LOCATION | NO |  | 633 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 5086 | 5399.638173094012986 | 126615 | 200058.3464566929133858267716535433070866 | 4400 | 4671.3346365736644 | 1280 | 1358.93371245779328 | 0 | 0 |  |  | 137381 | 136309.9566852170816327401574803149606299 | 211488.2529788183840518267716535433070866 | [8 empty] | 702 |  | 936 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | YES | ISOLATION VALVE | [22 empty] | YES | INTERNAL WORN VANES IN VALVE ACTUATOR MOTOR | [161 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 9:42AM ON MAY 30, 2019, THE ESD SYSTEM AT TENNESSEE GAS PIPELINE COMPANY (TGP) STATION 860 WAS ACTIVATED FOR A SCHEDULED ESD TEST. AFTER 3 MINUTES, AT 9:45AM, STATION PERSONNEL NOTICED THAT THE SUCTION SIDE OF THE STATION WAS EVACUATED AS DESIGNED; HOWEVER, THE DISCHARGE SIDE CONTINUED TO BLOW DOWN. AT THIS POINT, STATION PERSONNEL BEGAN TO LOCATE THE SOURCE OF THE RELEASE. STATION PERSONNEL DETERMINED THAT BD 500-1, A 30" ISOLATION VALVE, DID NOT CLOSE AS INTENDED DURING THE ESD. THIS ALLOWED GAS TO BLOW THROUGH FOUR 8" AND ONE 10" BLOWDOWN STACKS. STATION PERSONNEL CLOSED THE BLOWDOWN VALVES TO STOP THE RELEASE. THE TOTAL VENT TIME WAS 16 MINUTES AND THE TOTAL UNINTENTIONAL GAS LOSS WAS 48,698 MCF. INCIDENT INVESTIGATION REVEALED THAT VALVE BD 500-1 FAILED TO CLOSE AS THE VALVE ACTUATOR MOTOR DID NOT OPERATE. A 3RD PARTY CONTRACTOR EXAMINED THE MOTOR AND DETERMINED THAT INTERNAL WORN VANES CAUSED THE FAILURE TO OPERATE. TO PREVENT A REOCCURRENCE, THE VALVE ACTUATOR MOTOR WAS REPLACED. A 48-HR UPDATE CALL WAS MADE TO THE NRC. THE NRC REPORT NUMBER FOR THIS CALL IS #1247459.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190074 | 33883 | 2019-06-28 16:53 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-06-01 10:12 | 2019 | CENTRAL | NO | 34.4636 | -97.5309 | 1247500 | 2019-06-01 11:02 | 1247648 | NATURAL GAS |  | 150 | 250 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-06-01 10:30 | YES | 2019-06-01 10:12 | ALLOWED TO BURN OUT |  | 150 | NO | [6 empty] | 0 | 2019-06-01 10:12 | 2019-06-01 10:12 | ONSHORE | OK | 73481 | RATLIFF CITY | CARTER | SURVEY STATION NO. | CS 801 | RATLIFF CITY COMPRESSOR STATION 801 | AG TEXOMA SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 1999 | 1999 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | [5 empty] | 0 | 0 | 650 | 690.08352585747315 | 390 | 616.220472440944881889763779527559055118 | 450588 | 478374.393460103248788 | 3500 | 3715.8343700017785 | 156097 | 165723.027901190748147 | MATERIALS FOR TEMPORARY SETUP | 2.6 | 611225 | 286499.1667669516306878346456692913385827 | 649119.5597295941934668897637795275590551 | 0 | 0 | 0 | 0 | NO |  |  |  | 652 | 0 | 1050 | 192.619(A)(1) |  | 1989-12-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INADEQUATE PROCEDURE. FURTHER EXPLANATION PROVIDED IN PART H: NARRATIVE. | YES |  |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [146 empty] | YES | YES |  | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 10:12AM ON JUNE 1, 2019, OPERATIONS PERSONNEL WORKING AT THE NATURAL GAS PIPELINE COMPANY OF AMERICA (NGPL) RATLIFF CITY COMPRESSOR STATION 801 HEARD A LOUD NOISE FROM THE OTHER SIDE OF THE YARD. EMPLOYEES SAW FLAMES ORIGINATE FROM AND ENGULF FILTER/SEPARATOR #3. OPERATIONS PERSONNEL IMMEDIATELY CALLED THEIR SUPERVISOR AND MUSTERED AT THE FRONT GATE. THERE WERE NO INJURIES. THE RATLIFF CITY FIRE DEPARTMENT ARRIVED ON SITE AFTER RECEIVING A CALL FROM A CONCERNED CITIZEN. HOWEVER, THEY DID NOT APPROACH OR FIGHT THE FIRE. AT THE TIME OF THE NRC CALL, 11:02AM, THE FIRE HAD DIED OUT. PRIOR TO THE EVENT, THE STATION WAS OFF-LINE AND ISOLATED FOR MAINTENANCE. THIS THEREFORE MINIMIZED THE AMOUNT OF GAS LOSS. THE INVESTIGATION IN TO THE INCIDENT WAS INCONCLUSIVE ON THE EXACT CAUSE OF THE INCIDENT. CONTRIBUTING FACTORS TO THE INCIDENT WERE DETERMINED TO INCLUDE THE PRESENCE OF A FLAMMABLE ATMOSPHERE AND IRON SULFIDE IN THE FILTER SEPARATOR AND INADEQUATE PROCEDURES. THE INVESTIGATION REVEALED THAT THERE WAS NEITHER A MANUFACTURERS NOR A SITE-SPECIFIC PROCEDURE FOR PURGING AND PACKING THE FILTER SEPARATOR UNITS. IN ADDITION, THERE WAS NOT A MAINTENANCE PROCEDURE FOR CLEANING OUT OF THE ACCESSIBLE SECTIONS OF THE FILTER SEPARATORS, LEADING TO AN EXCESSIVE AMOUNT OF SOLID BUILD UP, INCLUDING IRON SULFIDE. IN ORDER TO PREVENT A REOCCURRENCE, A PURGE VALVE WAS ADDED TO THE DOWNSTREAM SECTION OF FILTER SEPARATORS #1 AND #3 (ONE ALREADY EXISTED ON #2) TO MAKE THE PURGING SEQUENCE REQUIRED ON EACH SEPARATOR SIMILAR. THE EMPLOYEES HAVE BEEN RETRAINED ON PURGING AND PACKING, AND A SITE-SPECIFIC PROCEDURE TO ENSURE AN EFFECTIVE PURGE THROUGH THE ENTIRE FILTER SEPARATOR VESSEL WAS CREATED. IN ADDITION, NGPL EMPLOYEES ALSO REVISED THE SITE-SPECIFIC MAINTENANCE PROCEDURE TO INCREASE THE FREQUENCY OF FILTER ELEMENT REPLACEMENT AND CLEANING PARTICULATES OUT OF THE SUMP VESSEL.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20190075 | 32926 | 2019-06-28 17:24 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2019-05-30 06:09 | 2019 |  |  | 40.886 | -81.5428 | 1247272 | 2019-05-30 12:08 |  | NATURAL GAS |  | 1.2 | 4.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-05-30 06:48 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-05-30 06:09 | 2019-05-30 06:45 | ONSHORE | OH | 44614 | Not Within a Municipality | STARK | MILEPOST | WELL # 1944 | WELL # 1944 MORELLI REALTY #1 | WELL # 1944 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | RING GASKET | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 47 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 9 | 9.555002665718859 | 2 | 3.16010498687664041994750656167979002625 | 250000 | 265416.74071441275 | 1000 | 1061.666962857651 | 0 | 0 |  |  | 251011 | 117566.3563235841479649632545931758530184 | 266491.12278492299649941994750656167979 | [8 empty] | 315 |  | 2000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | JEFFERY BURDETTE | ENGINEERING TECHNICAL CONSULTANT | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | TERRY GLIDDEN | MANAGER GAS OPERATIONS OHIO PIPELINE SAFETY | 3303514326 | terry.l.glidden@dominionenergy.com | AT APPROXIMATELY 6:00 AM ON MAY 30, 2019, STORAGE WELL #1944 WAS STRUCK WITH A TRACTOR AND MANURE SPREADER. THE CONTRACTED MANURE SPREADER WAS NOT THE NORMAL FARMER DOING THE WORK, AND NOT FAMILIAR WITH THE PROPERTY. THE WORK WAS PERFORMED DURING EARLY HOURS WITH LESS DAY LIGHT FOR VISIBILITY. DOMINION ENERGY OHIO FIELD PERSONNEL WERE NOTIFIED BY THE FARMER AND ARRIVED ON LOCATION AT 06:45 AM. THE GAS LEAK WAS FOUND TO BE COMING FROM BELOW THE MASTERVALVE (GATE VALVE), ON THE FLANGE BETWEEN THE MASTERVALVE AND THE WELLHEAD ADAPTER FLANGE (INTERNAL WELLHEAD SEALS). WELLHEAD CASING PRESSURE (3.50" OD CASING) WAS MEASURED AT 315 PSIG. ANNULAR PRESSURE WAS MEASURED AT 0.5 PSIG. AT 06:48 HRS, THE WELL WAS BLOWN TO THE STOCK TANK AND BLEW DOWN COMPLETELY IN 5 MINUTES. THE WELL IS STILL BLOWN DOWN AND REPAIR COSTS ARE ESTIMATED. ADDITIONAL PROTECTION AROUND THE WELL IS BEING CONSIDERED TO MINIMIZE THE POSSIBILITY OF A RECURRENCE. ALSO, ADDITIONAL ENHANCEMENTS TO PUBLIC AWARENESS IS BEING CONSIDERED TO INCLUDE MANURE SPREADER CONTRACTORS. THE WELL IS STILL SHUT IN AND IS ANTICIPATED TO BE REPAIRED/REPLACED SOMETIME IN NOVEMBER 2019. UPDATES WILL CONTINUE TO BE PROVIDED VIA EMAIL TO THE LEAD PHMSA STORAGE INSPECTOR. THE OCTOBER 2019 UPDATE REQUEST AND GUIDANCE PROVIDED BY PHMSA FOR UPDATES ALSO SUGGESTED THAT NO FURTHER SUPPLEMENTAL REPORTING WAS REQUIRED FOR THIS INCIDENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190076 | 32742 | 2019-07-02 16:47 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2018-04-16 08:00 | 2018 |  |  | 41.8105 | -81.0946 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 2119 | 215 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2018-03-29 17:43 | 2018-03-31 18:10 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2018-03-29 13:01 | 2018-03-29 13:32 | ONSHORE | OH | 44057 | MADISON | LAKE | MILEPOST | L#298 | LAKESHORE LINE | L#298 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR | [28 empty] | 1969 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 0.6 | [7 empty] | CLASS 3 LOCATION | NO |  | 223 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 426 | 461.454941069809536 | 4195 | 5970.189125295508274231678486997635933806 | 56130 | 60801.56300997279168 | 4974 | 5387.973889392564864 | 0 | 0 |  |  | 65725 | 33321.1816987412643393380614657210401891 | 72621.1809657306743542316784869976359338 | [8 empty] | 144 |  | 260 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 27984 | YES | [7 empty] | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 807200681 | OHIO ONE-CALL (OUPS) | CONTRACT LOCATOR | YES | YES | YES | 48 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | JEFFERY BURDETTE | TECHNICAL CONSULTANT | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | TERRY GLIDDEN | MANAGER GAS OPERATIONS OHIO PIPELINE SAFETY | 3303514326 | terry.l.glidden@dominionenergy.com | A CONTRACTOR INSTALLING A WATER MAIN DROVE A TRENCH BOX INTO A DOMINION ENERGY OHIO TRANSMISSION LINE L#298. THE CONTRACTOR WAS INFORMED OF THE SAFE DIGGING REQUIREMENTS, BUT FAILED TO CONTACT THE COMPANY OR CONTRACTED LOCATING SERVICE WHEN EXCAVATING WITHIN 10 FEET OF THE TRANSMISSION LINE. AN RCA WAS CONDUCTED AND FOUND THE ROOT CAUSE TO BE A FAILURE TO MAINTAIN CLEARANCE BETWEEN POWERED EQUIPMENT AND UNDERGROUND FACILITIES. THIS INCIDENT WAS FOUND UNREPORTED DURING A PUCO PIPELINE SAFETY INSPECTION. THE REASON WAS DUE TO THE $50,000 THRESHOLD EXCEEDANCE FROM CONTRACTOR REPAIR COSTS INCURRED AFTER THE EVENT, BUT NOT CORRECTLY TRACKED FOR REPORTING REQUIREMENTS. DOMINION ENERGY OHIO HELD AN INTERNAL MEETING TO ADDRESS THIS ISSUE AND IMPLEMENTED MEASURES TO ENSURE FUTURE REPORTING IS NOT MISSED AGAIN.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190077 | 33514 | 2019-07-03 11:22 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-06-18 15:18 | 2019 | CENTRAL | YES | 34.4532 | -90.5873 | 1249387 | 2019-06-19 10:20 | 1249482 | NATURAL GAS |  | 19105 | 601 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-06-19 11:33 |  | YES | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | FLOW CONTROL UPSTREAM FED PARALLEL LINE. |  | OPERATIONAL CONTROL | FLOW CONTROL UPSTREAM FED PARALLEL LINE. |  | 0 | 2019-06-18 15:18 | 2019-06-19 09:10 | ONSHORE | AR | 72342 | HELENA | PHILLIPS | MILEPOST | 9+1382 | HELENA 12" LINE #1 | HEL 12-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDERWATER IN MS RIVER | 240 | NO | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 192 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.5 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1950 | 1950 | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN; UNSAFE FOR DIVING OPS | [5 empty] | CLASS 1 LOCATION | NO |  | 290 |  | NO | NO | [5 empty] | 0 | 0 | 1581 | 1678.495468277946231 | 50246 | 79391.3175853018372703412073490813648294 | 1400000 | 1486333.7480007114 | 1500 | 1592.5004442864765 | 0 | 0 |  | 2.63 | 1453327 | 709248.8719113923222778451443569553805774 | 1568996.06149857766000134120734908136483 | 0 | 0 | 0 | 0 | NO |  |  |  | 683 | 40000 | 914 | 192.619(A)(1) |  | 1949-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 15097 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | LINE HAS BEEN ABANDONED; FINAL DETERMINATION WILL NOT BE COMPLETED. | [145 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | ON JUNE 18, 2019, TEXAS GAS TRANSMISSION'S GAS CONTROL RECEIVED A CALL ABOUT A POSSIBLE UNDERWATER PIPELINE LEAK IN THE MISSISSIPPI RIVER. AREA PERSONNEL ARRANGED FOR HELICOPTER, FLEW OVER AREA, AND CONFIRMED BUBBLES ON JUNE 19 AT APPROXIMATELY 09:10. NRC NOTIFICATION WAS MADE AND LINE WAS ISOLATED AND PRESSURED DOWN TO 0 PSIG. ON JUNE 21, A SONAR INSPECTION WAS DONE BUT WATER WAS AT A HIGH LEVEL WITH THE EAST BANK RIGHT-OF-WAY FLOODED AND INACCESSIBLE. DUE TO THE WATER MOVEMENT AND FLOODING IT WAS UNSAFE FOR DIVING OPERATIONS; INCIDENT SITE IS APPROXIMATELY 80 FEET BELOW WATER. MULTIPLE SONAR PASSES WERE RECORDED FROM APPROXIMATELY THE MIDDLE OF THE RIVER TOWARD THE WEST BANK WHERE THE SUSPECTED LEAK IS LOCATED. SONAR INDICATES THERE MAY BE A POSSIBLE EXPOSURE ON THE HELENA 12" #1 LINE (HEL 12-1). IT IS LIKELY THAT THIS SECTION OF THIS LINE WILL BE ABANDONED. 9-6-19 EMAIL RECEIVED FROM PHMSA INDICATED THAT THE LATITUDE AND LONGITUDE INDICATED ON THIS REPORT DOES NOT FALL ON THE REFERENCED MAPPED PIPELINE. THIS PIPELINE IS UNDER THE MISSISSIPPI RIVER AND THE LOCATION PROVIDED IS WHERE BUBBLES WERE FOUND IN THE WATER; THIS IS THE MOST ACCURATE LATITUDE AND LONGITUDE AVAILABLE AT THIS TIME. THE LINE IS STILL SHUT IN. ALTHOUGH IT IS NOT KNOWN WHETHER THE INCIDENT OCCURRED ON THE PIPE OR A WELD, TO ACCOMMODATE PHMSA'S REQUEST FOR PIPE DATA, THE ANSWERS PROVIDED IN PART C HAVE CHANGED FROM "ITEM INVOLVED IN INCIDENT = UNKNOWN," TO "ITEM INVOLVED IN INCIDENT = PIPE." REGARDING THE COSTS AND ABANDONMENT, COST HAS BEEN REDUCED FROM $5,000,000 TO $1,400,000 BECAUSE TEXAS GAS ORIGINALLY EXPECTED TO REPAIR THE LINE BUT INSTEAD WILL CHECK THE INTEGRITY OF THE HEL 12-2 (PARALLEL LINE) AND CONSIDER ABANDONING THE HEL 12-1; IF THIS APPROACH IS USED, PIG TRAPS MAY ALSO BE INSTALLED. CAUSE HAS NOT BEEN DETERMINED. THIS LINE IS OUT OF SERVICE AND THE LOCATION IS UNDER THE MISSISSIPPI RIVER. NO ADDITIONAL INVESTIGATION INTO CAUSE IS PLANNED. 11-14-19 UPDATE: TEXAS GAS WILL INVESTIGATE USING A DIVING TEAM. AT THIS TIME, THE CAUSE REMAINS UNKNOWN. ADDITIONALLY, TEXAS GAS PLANS TO PERFORM AN INLINE INSPECTION ON THE PARALLEL LINE. 3-25-2020 DIVERS WERE UNABLE TO IDENTIFY THE CAUSE OF THIS INCIDENT. THE PIPELINE INVOLVED IN THIS INCIDENT HAS NOW BEEN ABANDONED IN PLACE. A SECOND REDUNDANT PIPELINE IN THE SAME RIGHT-OF-WAY WAS MODIFIED AND INLINE INSPECTED TO ENSURE ITS INTEGRITY. INLINE INSPECTION SHOWED THIS PIPELINE IS FIT FOR SERVICE. SUBSEQUENTLY, GAS WAS RE-ROUTED TO THIS PIPELINE TO PROVIDE SERVICE. TO FURTHER INVESTIGATE THE CAUSE OF THIS INCIDENT WOULD REQUIRE PHYSICAL INSPECTION OF THE ABANDONED PIPELINE. DOING SO WOULD REQUIRE DIVERS TO JET OUT APPROXIMATELY 20 FEET OF SILT FROM THE RIVER BOTTOM. THIS ACTION WOULD NOT ONLY POSE SIGNIFICANT RISK TO PERSONNEL BUT COULD POSSIBLY JEOPARDIZE THE INTEGRITY OF THE SECOND PIPELINE NOW IN SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190078 | 32463 | 2019-07-05 10:25 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2019-06-07 04:14 | 2019 |  |  | 32.4671 | -91.5975 | 1248110 | 2019-06-07 06:35 |  | NATURAL GAS |  | 28400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-07 05:38 | 2019-06-07 13:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-07 04:14 | 2019-06-07 05:30 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | MLV 13 | DELHI COMPRESSOR STATION | 8012501 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF THE EMERGENCY SHUTDOWN SYSTEM (ISOLATION VALVE FAILED TO CLOSE) | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 69000 | 109023.6220472440944881889763779527559055 | 0 | 0 | 0 | 0 | 350 | 371.58343700017785 | LABOR COSTS |  | 69350 | 71699.3614518862233822834645669291338583 | 109395.2054842442723381889763779527559055 | [8 empty] | 670 |  | 858 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE ISSUE VIA SCADA ALARMS AND INITIATED A CALL-OUT OF FIELD OPERATIONAL PERSONNEL, WHO IDENTIFIED THE INCIDENT AND TOOK CORRECTIVE ACTIONS. GAS CONTROL DOES NOT HAVE THE CAPABILITY TO REMOTELY CLOSE VALVES AND THEREFORE COULD PREVENT THE INCIDENT THROUGH THEIR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [12 empty] | YES | [11 empty] | YES | VALVE FAILED TO CLOSE COMPLETELY | [161 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ERIK HUGHES | US REGUALTORY COMPLIANCE MANAGER - WEST | 402-492-7447 | erik_hughes@transcanada.com | ON JUNE 7 AT 04:14 CT, ANR PIPELINE GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) ALARM AT DELHI COMPRESSOR STATION LOCATED AT 1984 HWY 80 W, DELHI, LA 71232 (32.46620, -91.59704). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 05:30 CT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED THROUGH THE STATION BLOWDOWN STACKS. IMMEDIATE ACTION WAS TAKEN BY CLOSING THE VALVES OPEN TO ATMOSPHERE, WHICH ENDED THE RELEASE AT 05:38 CT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 28.4 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED AND NO EVACUATIONS WERE REQUIRED. INVESTIGATION INTO THE CAUSE OF THE UNINTENTIONAL RELEASE WAS ATTRIBUTED TO A FIRE DETECTION EQUIPMENT (FIRE EYE) FAULT THAT INITIATED THE ACTIVATION OF THE ESD SYSTEM. WHEN THE SYSTEM ACTIVATED, A STATION ISOLATION VALVE FAILED TO FULLY CLOSE RESULTING IN THE RELEASE GAS ABOVE 3 MILLION CUBIC FEET THROUGH THE STATION'S BLOWDOWN PIPING. NO EVIDENCE OF FIRE WAS DISCOVERED WITHIN THE COMPRESSOR STATION BUILDING. THUNDERSTORMS WITH LIGHTNING MAY HAVE ALSO CONTRIBUTED TO THE ACTIVATION OF THE FIRE DETECTION EQUIPMENT. PRIOR TO PLACING THE STATION BACK INTO SERVICE, THE FIRE DETECTOR WAS TESTED AND FOUND TO OPERATE CORRECTLY. ADDITIONALLY, THE ISOLATION VALVE WAS INSPECTED AND MAINTENANCE PERFORMED, WHICH INCLUDED GREASING, TESTING, CHECKING HYDRAULIC FLUIDS, A SIMULATED ACTIVATION, FOLLOWING PROCEDURES FOR INSPECTION, AND ENSURING COMPLETE OPERATION OF VALVE. ON JUNE 7, 2019 AT 11:45 CT, DELHI COMPRESSOR STATION WAS RETURNED TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190079 | 32461 | 2019-07-10 13:01 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-06-07 13:00 | 2019 |  |  | 39.9854 | -83.9189 | 1248488 | 2019-06-11 08:22 |  | NATURAL GAS |  | 361 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-11 16:45 | 2019-06-19 10:22 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-07 13:00 | 2019-06-07 13:00 | ONSHORE | OH | 45502 | SPRINGFIELD | CLARK | SURVEY STATION NO. | 00+50 | LINE Z-228 | Z-228-001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 |  | 0.154 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE | [28 empty] | 1955 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 72 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 840 | 1327.244094488188976377952755905511811024 | 300000 | 318500.0888572953 | 0 | 0 | 0 | 0 |  |  | 300840 | 141380.9070160879834645669291338582677165 | 319827.332951783488976377952755905511811 | [8 empty] | 167 |  | 175 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 164 | NO | [5 empty] | YES | LINE Z-228 IS A 2.375- INCH DIAMETER PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1959 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@transcanada.com | (304)357-2351 |  |  |  |  | GEORGE HAMATY | US REGULATORY COMPLIANCE MANAGER EAST | (304) 357-3728 | george_hamaty@transcanada.com | ON JUNE 7, 2019, AT APPROXIMATELY 13:00 EASTERN STANDARD TIME (EST), A COLUMBIA GAS TRANSMISSION, LLC. (COLUMBIA) OPERATIONS PERSONNEL WAS PERFORMING NORMAL ROUTINE MAINTENANCE TASKS ON LINE Z-215 AND ASSOCIATED SIDE LINES. AT THE LAWRENCEVILLE MEASURING STATION, THE OPERATIONS PERSONNEL NOTICED A WEAK SMELL OF ODOR OF GAS. BASED ON THE LOCATION AND THE AMOUNT OF GAS, THE LEAK WAS GRADED AS A GRADE 2 LEAK. ON JUNE 10, 2019, OPERATIONS PERSONNEL CONDUCTED ADDITIONAL SURVEYS FOR FURTHER INVESTIGATIONS. AFTER EXPOSING THE PIPE, IT WAS DISCOVERED THAT NATURAL GAS WAS LEAKING FROM AN UNMAPPED CASING ON LINE Z-228 UNDER SHRINE ROAD. AT APPROXIMATELY 14:00 EST OPERATIONS TEAM DECIDED TO UPGRADE THE LEAK TO A GRADE 1 AND CONTINUED MONITORING THE LEAK THROUGH THE NIGHT. ON JUNE 11, 2019 AT APPROXIMATELY 08:00 EST AFTER ESTIMATING THE COST OF THE PIPELINE REPAIR, IT WAS DECIDED TO REPORT THIS EVENT TO THE NATIONAL RESPONSE CENTER AS AN INCIDENT DUE TO COST OF THE REPAIRS. PIPELINE Z-228 IS A 2.375-INCH IN DIAMETER WITH0.154-INCH WALL THICKNESS. IT IS 164-FEET LATERAL PIPELINE FROM LINE Z-215 LOCATED IN CLARK COUNTY ON 3735 SHRINE RD, SPRINGFIELD, OHIO. ON JUNE 11, 2019, AT 16:35 EST A COMPRESSED NATURAL GAS TANKER WAS CONNECTED AND STARTED FEEDING THROUGH LAWRENCEVILLE POINT OF DELIVERY TO CONTINUE DELIVERABILITY TO THE DOWNSTREAM TOWN. AT 16:45 LINE Z-228 WAS BLOWN DOWN. ON JUNE 13, 2019, THE CONSTRUCTION CREW WAS DISPATCHED TO THE SITE AND ON JUNE 14, 2019 THE CASING AND PIPE WERE REMOVED AND SENT TO A COLUMBIA STORAGE FACILITY. AFTER INVESTIGATION, IT WAS IDENTIFIED THE INCIDENT WAS CAUSED DUE TO EXTERNAL CORROSION PITTING. THE INITIAL NRC REPORT NO.1248488 AND THE NRC 48-HOUR REPORT NO. 1248650 HAVE BEEN CALLED-IN ON JUNE 11TH AND JUNE 12TH RESPECTIVELY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190080 | 33002 | 2019-07-10 17:41 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2019-06-10 12:29 | 2019 |  |  | 32.4671 | -91.5975 | 1248420 | 2019-06-10 13:44 |  | NATURAL GAS |  | 5700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-10 12:45 | 2019-06-14 15:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-10 12:29 | 2019-06-10 12:40 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | MLV 13 | DELHI COMPRESSOR STATION | 8012501 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | MALFUNCTION OF EMERGENCY SHUTDOWN SYSTEM (ISOLATION VALVE FAILED TO CLOSE) | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 13800 | 21804.7244094488188976377952755905511811 | 2500 | 2654.1674071441275 | 0 | 0 | 0 | 0 | NONE |  | 16300 | 15478.0036214595258464566929133858267717 | 24458.8918165929463976377952755905511811 | [8 empty] | 835 |  | 858 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE ISSUE VIA SCADA ALARMS AND INITIATED A CALL-OUT OF FIELD OPERATIONAL PERSONNEL, WHO IDENTIFIED THE INCIDENT AND TOOK CORRECTIVE ACTIONS. GAS CONTROL DOES NOT HAVE THE CAPABILITY TO REMOTELY CLOSE VALVES AND THEREFORE COULD NOT PREVENT THE INCIDENT THROUGH THEIR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [14 empty] | YES | [9 empty] | YES | VALVE FAILED TO CLOSE COMPLETELY | [161 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ERIK HUGHES | US REGUALTORY COMPLIANCE MANAGER - WEST | 402-492-7447 | erik_hughes@transcanada.com | ON JUNE 10 AT 12:29 CT, ANR PIPELINE'S GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) ALARM AT DELHI COMPRESSOR STATION LOCATED AT 1984 HWY 80 W, DELHI, LA 71232 (32.46707, -91.59751). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 12:40 CT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED THROUGH THE STATION'S BLOWDOWN STACKS. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO EMERGENCY EXISTED AND CLOSING THE VALVES, WHICH ENDED THE RELEASE AT 12:45 CT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 5.7 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED AND NO EVACUATIONS WERE REQUIRED. THE CAUSE OF THE UNINTENTIONAL RELEASE WAS ATTRIBUTED TO A FLAME DETECTION EQUIPMENT (FIRE EYE) THAT INITIATED THE ACTIVATION OF THE ESD SYSTEM. WHEN THE SYSTEM ACTIVATED, STATION ISOLATION VALVE 501-14-16 FAILED TO FULLY CLOSE RESULTING IN THE RELEASE GAS. FOLLOWING THE INCIDENT, DELHI COMPRESSOR STATION WAS TAKEN OUT OF SERVICE DURING THE INVESTIGATION. VALVE 501-14-16 WAS LOCKED OUT OF SERVICE AND BY-PASSED TO ANOTHER ESD VALVE CAPABLE OF ISOLATING THE STATION. THE FLAME DETECTION EQUIPMENT WAS REMOVED FROM THE BUILDING AND REPLACED. DELHI COMPRESSOR STATION WAS PLACED BACK INTO SERVICE ON JUNE 10, 2019. THE COMPRESSOR ENGINE BUILDING WHERE THE SHUTDOWN WAS INITIATED REMAINED OUT OF SERVICE UNTIL JUNE 14 AT 15:45 CT. DURING THE SHUTDOWN PERIOD, NO ADDITIONAL FLAME DETECTION ACTIVATIONS WERE DETECTED. THE FLAME DETECTOR UNIT WAS SENT TO THE ORIGINAL MANUFACTURER FOR EVALUATION. THE MANUFACTURER REPORTED THAT THE UNIT MET ALL MANUFACTURING SPECIFICATIONS AND OPERATED AS INTENDED. THE MANUFACTURER RECOMMENDED THAT THE UNIT'S SENSITIVITY BE REDUCED FROM "HIGH" TO "MEDIUM". THIS RECOMMENDED CHANGE IS DUE TO THE OPERATIONAL AND ENVIRONMENTAL CONDITION IN THE RECIPROCATING ENGINE COMPRESSOR BUILDING. THE CHANGE IN SENSITIVITY DOES NOT AFFECT THE SAFETY OF THE PIPELINE FACILITY AND THE SYSTEM HAS BEEN TESTED ACCORDING TO PROCEDURES. THIS ACTION WAS COMPLETED ON JULY 26, 2019. ON 19 NOVEMBER 2019 INVESTIGATION AND REMEDIAL ACTION WAS TAKEN TO REPAIR VALVE 501-14-16, WHICH FAILED TO OPERATE FULLY CLOSED DURING A STATION ESD. THE 3-WAY PILOT VALVE, WHICH SENDS POWER GAS TO OPERATE THE VALVE WHEN PILOT PRESSURE DROPS OUT, WAS REPLACED. AN EXTRA POWER GAS BOTTLE WAS ALSO INSTALLED IN LINE WITH THE POWER GAS SUPPLY LINE TO ENSURE WE HAVE AN AMPLE AMOUNT OF POWER GAS TO FULLY STROKE THE VALVE. AN FULL EMERGENCY SHUTDOWN SYSTEM WAS CONDUCTED ON 11/19/2019 TO TEST REPAIRS ON VALVE 501-14-16. DURING THIS TEST, IT WAS DISCOVERED THAT PRESSURE TO THE POWER GAS SUPPLY ON THE ACTUATOR DROPPED OUT CAUSING THE VALVE TO NOT OPERATE. FURTHER INVESTIGATION REVEALED THAT THE PILOT GAS SUPPLY WAS INSTALLED INTO THE POWER GAS PORT AND THE POWER GAS SUPPLY WAS INSTALLED INTO THE PILOT GAS PORT ON THE OPERATOR. THE SWITCHING OF THESE SUPPLIES CAUSED AN INCOMPLETE OPERATION OF THE VALVE DUE TO RELIEVING PRESSURE OF THE PILOT GAS DURING AN ESD INITIATION. THESE LINES WERE SWITCHED TO THE CORRECT PORTS ON THE ACTUATOR AND PROPER OPERATION FOR VALVE CLOSURE WAS DOCUMENTED. VALVE 501-14-16 WAS PLACED BACK INTO SERVICE ON 22 NOVEMBER 2019.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190081 | 32413 | 2019-07-11 14:20 | ORIGINAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2019-06-14 03:00 | 2019 |  |  | 32.27 | -95.2413 | 1248878 | 2019-06-14 09:50 |  | NATURAL GAS |  | 49 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-14 07:40 | 2019-06-19 21:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-14 07:20 | 2019-06-14 07:20 | ONSHORE | TX | 75791 | WHITEHOUSE | SMITH | MILEPOST | MLR-38 | S2-3-1 | MLR-38 BARBEE RD. | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2009 |  | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE RAN OVER 2-INCH VALVE CAUSING FLANGE LEAK | CLASS 2 LOCATION | NO |  | 29 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 161 | 254.388451443569553805774278215223097113 | 90000 | 95550.02665718859 | 2000 | 2123.333925715302 | 3500 | 3715.8343700017785 | CNG |  | 95661 | 44895.945688835252164041994750656167979 | 101643.5834043492400538057742782152230971 | [8 empty] | 240 |  | 300 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [260 empty] | BRUCE CAUGHRON | OPERATIONS SUPERVISOR | bruce.caughron@atmosenergy.com | 903-738-8122 | 903-242-4826 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT # 1249008 A VEHICLE WAS TRAVELING SOUTHBOUND ON HWY 110 TOWARD WHITEHOUSE, TEXAS. THE DRIVER LEFT THE ROADWAY ONTO THE EAST SIDE OF HWY 110 WHILE STILL TRAVELING SOUTH. THE VEHICLE THEN TRAVELED THROUGH THE STATION FENCE DAMAGING A 2-INCH ABOVEGROUND VALVE. THE INCIDENT OCCURRED ON 6/14/19 AT APPROXIMATELY 03:00. ATMOS ENERGY WAS FIRST NOTIFIED BY THE FIRE DEPARTMENT AT 06:18. THE FIRE DEPARTMENT INITIALLY NOTIFIED CENTERPOINT ENERGY, WHO DETERMINED THAT THEY DID NOT OPERATE THE FACILITY. AN ATMOS ENERGY TECHNICIAN WAS THE FIRST RESPONDER AND ARRIVED AT APPROXIMATELY 07:20. THE EMERGENCY VALVE AT THE STATION WAS TURNED OFF AT APPROXIMATELY 07:40. AT APPROXIMATELY 09:30 ON 6/14/19, IT WAS DETERMINED THAT REPAIRS WOULD LIKELY EXCEED THE $50,000 THRESHOLD, AND THE TELEPHONIC REPORT TO THE NRC WAS MADE AT 09:50. CNG WAS UTILIZED TO MAINTAIN SERVICE UNTIL NECESSARY REPAIRS COULD BE MADE. THE LINE WAS PLACED BACK IN SERVICE AT 21:15 ON 06/19/19. POLICE ADVISED THERE WERE NO INJURIES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190082 | 32430 | 2019-07-16 14:57 | SUPPLEMENTAL FINAL | 31613 | MIDCOAST PIPELINES (EAST TEXAS), L.P. | 600 TRAVIS SUITE 5500 | HOUSTON | TX | 77002 | 2019-06-20 20:30 | 2019 |  |  | 30.6062 | -94.9401 | 1249587 | 2019-06-20 22:45 |  | NATURAL GAS |  | 17468 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-20 20:30 | 2019-06-21 18:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-20 20:30 | 2019-06-20 20:30 | ONSHORE | TX | 77335 | GOODRICH | POLK | MILEPOST | GOODRICH STA. | GOODRICH COMPRESSOR STATION | TXCG-36 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2007 |  | CARBON STEEL |  | LEAK |  |  | OTHER | COMPRESSOR BLOW DOWN | [5 empty] | CLASS 1 LOCATION | NO |  | 830 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 42500 | 67152.2309711286089238845144356955380577 | 1795 | 1905.692198329483545 | 682 | 724.056868668917982 | 0 | 0 |  |  | 44977 | 45221.8243608455102821601049868766404199 | 69781.9800381270104508845144356955380577 | [8 empty] | 867 |  | 1050 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO MECHANICAL MALFUNCTION. NO CONTROLLER INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES |  |  | YES | [13 empty] | YES | [5 empty] | YES | [167 empty] | BENITA KALKA | GIS ANALYST | benita.kalka@midcoastenergy.com | 713-627-5723 |  |  |  |  | BENITA KALKA | GIS ANALYST | 713-627-5723 | benita.kalka@midcoastenergy.com | * INADEQUATE WARNING SYSTEM * TEMPERATURE EXTREMES AIR CONDITIONING FAILED WHICH CAUSED ELEVATED TEMPERATURES IN THE MCC. THE ELEVATED TEMPERATURES LEAD THE SHUTDOWN OF THE UPS. THE SHUTDOWN OF THE UPS (LOSS OF POWER) TRIGGERED THE ESD OF THE FACILITY. THE ELEVATED TEMPERATURES DID TRIGGER AN ALARM, BUT THIS ALARM WAS INACCURATELY LABELED IN THE MOST PROMINENT LOCATION. THE ALARM TAG WAS CORRECT BUT THE DESCRIPTION OF ALARM WAS WRONG. THIS GAVE OPERATIONS THE FALSE IMPRESSION OF A GENERATOR ISSUE WHICH WAS FOLLOWED UP ON AN NO ISSUES WERE FOUND. * INADEQUATE ENGINEERING * INADEQUATE OR IMPROPER CONTROLS DUE THE ESD VALVE SEQUENCE DESIGN, THE INLET AND STATION VALVES ACTUATED CLOSED AND THE BLOWDOWN VALVES ACTUATED OPEN. HOWEVER, THE OUTLET OUTLET VALVE (0201) FAILED TO SEAL CLOSED ALLOWING THE BLOWDOWN VALVES TO NOT ONLY DE-PRESSURE THE STATION BUT CONTINUE TO BLOWDOWN THE PIPELINE SYSTEM THAT SHOULD HAVE BEEN ISOLATED BY DESIGN. ACTIONS TAKEN TO DATE: 1) VALVE CONTRACTOR CHANGED OUT HYDRAULIC FLUID, ADJUSTED PRESSURES IN VALVE CHAMBERS, 2) CHANGED DESCRIPTION ON THE ALARM TAG IN SOFTWARE, 3) AS MENTION ABOVE THE ESD VALVE CLOSURE SEQUENCE HAS BEEN MODIFIED TO PRESENT BLOW DOWN VALVE FROM OPENING UNTIL INLET AND OUTLET VALVES ARE COMPLETELY CLOSED ON STATION. THIS SETUP WAS TESTED AND DOCUMENTED AS WORKING PROPERLY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190083 | 32434 | 2019-07-18 10:51 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-06-29 22:31 | 2019 |  |  | 39.6392 | -79.3394 | 1250551 | 2019-06-29 23:29 |  | NATURAL GAS |  | 3642 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-29 22:31 | 2019-06-30 07:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-29 22:31 | 2019-06-29 23:31 | ONSHORE | MD | 21520 | KAESE MILL | GARRETT | MILEPOST | 0 | ACCIDENT COMPRESSOR STATION | ACCI-UNIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 8413 | 13292.9816272965879265091863517060367454 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8413 | 8722.139107611548556430446194225721784777 | 13292.9816272965879265091863517060367454 | [8 empty] | 2657 |  | 3550 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS TRIGGERED BY A FIRE DETECTOR AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | YES, THERE WAS A SEVERE STORM WITH AN EXTREME AMOUNT OF LIGHTNING ACTIVITY. | [301 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1250679 AT APPROXIMATELY 10:31 PM EDT ON JUNE 29, 2019, AN EMERGENCY SHUTDOWN (ESD) WAS INADVERTENTLY ACTIVATED AT ACCIDENT COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN GARRETT COUNTY, MARYLAND. THE ESD OCCURRED DURING A SEVERE LIGHTENING STORM IN THE AREA. THE ESD WAS TRIGGERED BY A FIRE DETECTOR THAT DETECTED A FLAME SIGNATURE AS A RESULT OF THE SEVERE LIGHTING STORM. TETLP'S INVESTIGATION DETERMINED THAT THE ESD SYSTEM AND FIRE DETECTOR WERE FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. THE COMPRESSOR STATION WAS RETURNED TO NORMAL OPERATIONS AT APPROXIMATELY 7:30 AM EDT ON JUNE 30, 2019.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190084 | 33154 | 2019-07-19 12:53 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-06-21 09:28 | 2019 |  |  | 35.5553 | -109.7275 | 1249637 | 2019-06-21 11:22 |  | NATURAL GAS |  | 11628.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | RESPONDING OPERATIONS PERSONNEL WERE ABLE TO MANUALLY CLOSE THE ESD VALVE | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-21 09:28 | 2019-06-21 10:30 | ONSHORE | AZ | 86505 | Not Within a Municipality | APACHE | MILEPOST | C DISCHARGE | NAVAJO C/S DISCHARGE PIPING, C PLANT TO 1201 LINE | POWER GAS VALVE TO 1201 DISCHARGE VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1993 |  | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH VENT VALVE | CLASS 1 LOCATION | NO |  | 602 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 18839 | 29766.6089238845144356955380577427821522 | 0 | 0 | 180 | 191.10005331437718 | 0 | 0 |  |  | 19019 | 19615.5527436847184068766404199475065617 | 29957.7089771988916156955380577427821522 | [8 empty] | 758 |  | 845 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DEEMED THE INCIDENT WAS INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | AT 9:28 AM (MST) EL PASO NATURAL GAS COMPANY, LLC (EPNG) NAVAJO COMPRESSOR STATION C PLANT EXPERIENCED AN EMERGENCY SHUTDOWN (ESD). EPNG GAS CONTROL DISPATCHED A TECHNICIAN TO THE NAVAJO COMPRESSOR STATION WHO ARRIVED AT 10:30 AM (MST). UPON ARRIVAL THE TECHNICIAN DISCOVERED GAS VENTING THROUGH A VENT VALVE. AT 10:32 AM (MST) THE TECHNICIAN PROCEEDED TO MANUALLY CLOSE THE DISCHARGE VALVE WHICH STOPPED THE UNINTENTIONAL RELEASE OF GAS. THE ACTIVATION OF THE ESD WAS DUE TO A FIRE EYE MALFUNCTION. UPON ACTIVATION OF THE ESD THE INLET AND DISCHARGE VALVES ARE DESIGNED TO TURN TO THE CLOSED POSITION AND THE GAS REMAINING IN THE PLANT IS VENTED TO ATMOSPHERE, HOWEVER IN THIS EVENT THE DISCHARGE VALVE DID NOT CLOSE. THE DISCHARGE VALVE IN THIS SYSTEM HAD UNDERGONE AN ESD MAINTENANCE TEST ON MARCH 6TH, 2019 AND THE VALVE HAD CLOSED AS DESIGNED. THE DISCHARGE VALVE IS ACTUATED WITH POWER GAS BUT DURING THE INVESTIGATION IT WAS FOUND THAT THE ASSOCIATED POWER GAS SUPPLY VALVE WAS IN THE CLOSED POSITION. CONSEQUENTLY, WHEN THE ESD SYSTEM WAS ACTIVATED THERE WAS NO POWER GAS FEEDING THE DISCHARGE VALVE ENABLING IT TO TURN TO THE CLOSED POSITION. THIS RESULTED IN THE DISCHARGE VALVE REMAINING OPEN ALLOWING GAS FROM THE DISCHARGE SIDE OF THE PLANT TO CONTINUE TO VENT. THE DISCHARGE VALVE REMAINED OPEN UNTIL IT WAS MANUALLY SHUT BY THE TECHNICIAN. THE 48-HR NRC INCIDENT REPORT NUMBER IS 1249752. THE CONFIRMED DISCOVERY TIME OF THE INCIDENT WAS 10:30 AM (MST).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190085 | 32977 | 2019-07-25 10:29 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2019-06-30 10:20 | 2019 |  |  | 43.9578 | -86.1865 | 1250615 | 2019-07-01 12:28 |  | NATURAL GAS |  | 2186 | 2227 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-01 12:18 | 2019-07-04 12:25 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-30 10:20 | 2019-06-30 10:20 | ONSHORE | MI | 49405 | CUSTER | MASON | MILEPOST | MLV 4-5 | LOREED-LUDINGTON PIPELINE (16 INCH) | LOREED-LUDINGTON PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | YES |  |  |  |  | YES | UNCASED | YES | UNCASED | HATTING CREEK | 6 | SHORELINE/BANK/MARSH CROSSING | [11 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 |  | 0.25 | 1625 | X52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP | OTHER | TRENTON WAX COATING | [27 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 334 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 13362 | 14185.993957703932662 | 13116 | 20723.9685039370078740157480314960629921 | 97218 | 103213.138795095114918 | 37985 | 40327.419584147873235 | 27914 | 29635.371601208470014 | SEE PART H FOR DESCRIPTION |  | 189595 | 96254.8577674569104120236220472440944882 | 208085.8924420923987030157480314960629921 | [8 empty] | 495 |  | 913 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 13 | NO | [5 empty] | YES | PIG TRAPS WERE NOT USABLE AS CONFIGURED. | YES |  |  |  |  | YES | DESIGN OF PIG TRAPS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME WAS NOT SIGNIFICANT ENOUGH TO SHOW ANY NOTICEABLE PRESSURE DECREASES OR FLOW INCREASES IN GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | KIEFNER PERFORMED AN INVESTIGATION OF THE CAUSE OF THE LEAK. SEE PART H FOR THE SUMMARY AND CONCLUSIONS. |  |  | YES | YES |  |  | YES | YES | 1968 | YES | YES | YES |  |  |  | 2018 |  |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CORRIE J. TOWNS | SUPERVISOR OF CODES AND STANDARDS | corrie.towns@dteenergy.com | 313-346-2896 |  |  |  |  | CORRIE TOWNS | SUPERVISOR OF CODES AND STANDARDS | 313-346-2896 | corrie.towns@dtenergy.com | A VERBAL NOTIFICATION REGARDING A LEAK ON THE 16' LOREED-LUDINGTON TRANSMISSION LINE FOR DTE GAS WAS MADE TO THE MPSC AND NRC. THE LEAK WAS FOUND BY A LANDOWNER AND THE DTE CREW WAS DISPATCHED AT 10:20 PM ON 6/30/2019. DTE GAS LOWERED THE PRESSURE OF THE LINE AS OF 12:18 AM ON 7/1/2019 AND PRESSURE CONTROL PROCEDURE AND A REPAIR PLAN ARE BEING DEVELOPED. APPROXIMATELY 5.5 FEET SECTION WAS REPLACED AND THE PIPE SECTION IS UNDERGOING A FAILURE INVESTIGATION BY A THIRD PARTY LABORATORY. MPSC, JIM JOHNSON, WAS NOTIFIED AT 12:30 AM AND WE HAD A FOLLOW-UP DISCUSSION AT APPROXIMATELY 12:53 AM. THE NRC WAS NOTIFIED AT 12:28 AM AND THE INCIDENT NUMBER IS 1250615. THE LINE WAS RETURNED TO SERVICE ON 7/4/2019. KIEFNER PERFORMED AN INVESTIGATION OF THE CAUSE OF THE LEAK. THE REPORT WAS DATED AUGUST 29, 2019. THE SUMMARY AND CONCLUSION OF THE REPORT STATED "THE LEAK THAT OCCURRED ON THE LOREED-LUDINGTON PIPELINE IN THE MLV 4-5 VALVE SECTION ON JUNE 30, 2019 WAS LIKELY CAUSED BY CORROSION WHICH THINNED THE PIPE WALL THICKNESS TO THE POINT THAT THE REMAINING LIGAMENT WAS UNABLE TO SUPPORT THE STRESS INDUCED BY THE INTERNAL PRESSURE. THE FAILURE OF THE PIPE WALL WAS BY DUCTILE TEARING AND THE APPEARANCE OF A CRACK-LIKE FEATURE WAS CAUSED BY THE LOCALIZED NECKING OF THE MATERIAL JUST PRIOR TO TEARING. AN AREA OF COATING DAMAGE AND DISBONDMENT, WHICH CAUSED CATHODIC SHIELDING OF THE PIPE MATERIAL, LIKELY ENABLED THE CORROSION TO OCCUR. THE PRESENCE OF A TWO PART FULL-ENCIRCLEMENT SWAMP WEIGHT OVER THE LEAK LOCATION LIKELY CONTRIBUTED TO THE CONDITIONS WHICH WOULD BE NECESSARY FOR DISBANDED COATING TO SHIELD THE PIPE MATERIAL. THE TYPE OF CORROSION THAT OCCURRED AT THIS LOCATION CAN BE DESCRIBED AS 'UNDER DEPOSIT ACID ATTACK.' HOWEVER, THE EXACT CAUSE OF THE CORROSION WAS NOT IDENTIFIED. AN ANALYSIS OF THE CORROSION PRODUCTS FOR THE PRESENCE OF BACTERIA FOUND A LOW PRESENCE OF COMMON BACTERIA ASSOCIATED WITH PIPELINE CORROSION. PART D7.D ESTIMATED OTHER COSTS DESCIPTION: LUMPED COST OF FLEET, FACILITY, TRAVEL/MILEAGE, AND HOTEL COSTS FOR EVERYONE THAT WAS DEPLOYED ON SITE FOR THE WEEK OF THE INCIDENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190086 | 32476 | 2019-07-26 11:33 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-06-28 00:22 | 2019 |  |  | 30.3202 | -95.1591 | 1250361 | 2019-06-28 01:25 |  | NATURAL GAS |  | 137143 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-28 00:49 | 2019-06-28 03:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-28 00:49 | 2019-06-28 00:49 | ONSHORE | TX | 77328 | Not Within a Municipality | MONTGOMERY | SURVEY STATION NO. | 485 | LINE 100-1 | VALVE SEGMENT 100-25-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2016 |  | CARBON STEEL |  | OTHER | [8 empty] | DURING STATION ESD, VALVE BS-2 DID NOT CLOSE PROPERLY BECAUSE OF MALFUNCTION OF REGULATOR ON POWER GAS SUPPLY TO THE VALVE OPERATOR; | CLASS 1 LOCATION | NO |  | 496 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 338524 | 534885.6902887139107611548556430446194226 | 1000 | 1061.666962857651 | 2800 | 2972.6674960014228 | 5050 | 5361.41816243113755 | INVESTIGATION; |  | 347374 | 355108.2483055310259583989501312335958005 | 544281.4429100041221111548556430446194226 | [8 empty] | 735 |  | 750 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DURING STATION ESD, VALVE BS-2 DID NOT CLOSE PROPERLY BECAUSE OF MALFUNCTION OF REGULATOR ON POWER GAS SUPPLY TO THE VALVE OPERATOR; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | TRASH IN REGULATOR OF POWER SUPPLY GAS TO VALVE OPERATOR; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martiin_muller@kindermorgan.com | 205-325-3863 | 205-325-3508 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 00:22-HOUR AN EMERGENCY SHUTDOWN (ESD) OCCURRED AT STATION 25. PROPER NOTIFICATIONS WERE MADE AND ON-CALL EMPLOYEES ARRIVED ON SITE AT 00:49-HOUR AND FOUND GAS VENTING THEREBY CONFIRMING THE EVENT. EMPLOYEES CLOSED THE NECESSARY VALVES TERMINATING THE RELEASE OF NATURAL GAS. AN INVESTIGATION OF THE EVENT PROMPTLY BEGAN. A FAULTY MODULE IN THE PLC WAS DISCOVERED WHICH INITIATED THE ESD. THE MODULE WAS REPLACED POST-INCIDENT. ALSO IT WAS ALSO DETERMINED THE POWER GAS REGULATOR TO THE OPERATOR OF VALVE BS-2 HAD MALFUNCTIONED CAUSING THE VALVE TO REMAIN OPEN INSTEAD OF CLOSING PROPERLY FOR THE ESD. TRASH WAS FOUND IN THE POWER GAS REGULATOR CAUSING IT TO MALFUNCTION. THE POWER GAS REGULATOR WAS REPLACED POST-INCIDENT. ALL REGULATORS INVOLVING POWER GAS TO VALVE OPERATORS IN THE ESD SYSTEM AND THE ESD VALVES WERE INSPECTED POST-INCIDENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190087 | 32863 | 2019-07-29 12:54 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-06-29 11:40 | 2019 |  |  | 36.3459 | -86.8682 | 1250516 | 2019-06-29 13:34 |  | NATURAL GAS |  | 3588 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-05 14:40 | 2019-07-10 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-29 11:40 | 2019-06-29 12:20 | ONSHORE | TN | 37080 | Not Within a Municipality | DAVIDSON | SURVEY STATION NO. | 1322 | LINE 500-1 | VALVE SEGMENT 563-1-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM; | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD ACTIVATION; | CLASS 2 LOCATION | NO |  | 760 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 8857 | 13994.5249343832020997375328083989501312 | 21320 | 22634.73964812511932 | 3000 | 3185.000888572953 | 5000 | 5308.334814288255 | INVESTIGATION; |  | 38177 | 22914.9687296951668962729658792650918635 | 45122.6002853695294197375328083989501312 | [8 empty] | 814 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL CONTROL ROOM MANAGEMENT PROCESSES WERE FOLLOWED; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [10 empty] | YES | UPS SYSTEM BATTERIES; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON 06/29/2019 AT 11:40-HOURS, THE TGP ON-CALL EMPLOYEE RESPONDED TO A GAS CONTROL CALL OUT CONCERNING A POSSIBLE ESD AT TGP STATION #563, JOELTON, TN. THE EMPLOYEE ARRIVED ON SITE AT APPROXIMATELY 12:20-HOURS AND PROCEEDED TO VERIFY SYSTEM STATUS. AT 12:45-HOURS, THE EMPLOYEE DISCUSSED WITH SUPERVISION AND CONFIRMED THE FACILITY ESD HAD OCCURRED WITH ALL VALVES WORKING AS DESIGNED. AT 13:00 HOURS, OPERATIONS ESTIMATED THE GAS LOSS FOR THE EVENT TO BE 4,005 MCF AND WAS REPORTED AS NRC #1250516 ON 06/29/2019 AT 13:34-HOURS. ENGINEERING PROVIDED REVISED ESTIMATED GAS LOSS ON 07/12/2019 AS 3,588 MCF. INVESTIGATION FOUND THERE WAS A MOMENTARY LOSS OF COMMERCIAL POWER AND THE STATION UPS SYSTEM DID NOT HOLD THE REQUIRED COMPRESSOR STATION VOLTAGE (120 VDC) IN THE INTERIM WHILE THE EMERGENCY GENERATOR WAS RAMPING UP TO COME ON-LINE. THIS INTERIM LACK OF VOLTAGE TRIGGERED THE COMPRESSOR STATION ESD. THE INVESTIGATION IDENTIFIED TWO BATTERIES IN THE UPS SYSTEM HAD IMPROPERLY DRAINED POWER. FURTHER INVESTIGATION FOUND SAID BATTERIES HAD NOT BEEN STORED AND MAINTAINED CORRECTLY DURING COMPRESSOR STATION CONSTRUCTION PRIOR TO OCTOBER, 2018. THE FAULTY BATTERIES WERE REPLACED. THE REPAIRS ALSO INCLUDED REPLACING SOME WIRING, FUSES, BREAKERS AND BATTERY CHARGERS. THE INVESTIGATION ALSO FOUND PREVIOUS AUTOMATION PROGRAMMING IN MAY, 2019 HAD INADVERTENTLY DISABLED AN ALARM CONCERNING ELECTRICAL POWER STATUS; SAID ALARM HAS BEEN REESTABLISHED. DURING THE INVESTIGATION AND REPAIR TIME PERIOD, THE STATION WAS IN MANNED OPERATION WITH THE EXCEPTION OF JULY 5, 2019, 14:40-HOURS TO JULY 10, 2019, 11:00-HOURS. JULY 5, 2019, INCLEMENT WEATHER IN THE AREA CAUSED ANOTHER LOSS OF COMMERCIAL POWER AND STATION ESD INCIDENT. (REFERENCE DOT REPORT #2019092) OPERATIONS KEPT THE STATION OFF LINE FOLLOWING THE JULY 5, 2019 INCIDENT UNTIL JULY 10, 2019 FOR CERTAIN TASKS RELATED TO BOTH INCIDENTS TO OCCUR. THE STATION THEN RESUMED MANNED OPERATION UNTIL OCTOBER 3, 2019, AT APPROXIMATELY 18:00-HOURS WHEN ALL REPAIRS FOR THE JUNE 29, 2019 INCIDENT WERE COMPLETED AND THE STATION RETURNED TO AUTOMATED OPERATION. THE 48-HOUR UPDATE IS NRC REPORT #1250639.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190088 | 32480 | 2019-07-30 10:25 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-07-10 07:00 | 2019 |  |  | 35.7699 | -91.6 | 1251484 | 2019-07-10 07:12 |  | NATURAL GAS |  | 3667 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | STOPPLES WERE INSTALLED. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-04 10:30 | 2019-07-04 07:00 | ONSHORE | AR | 72501 | BATESVILLE | INDEPENDENCE | MILEPOST | 1408+92 | JM-7 | JM-7 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | FILLET WELD | [18 empty] | 1977 |  | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 148 |  | NO | NO | NO |  |  |  |  | 2000 | 2123.333925715302 | 0 | 0 | 9000 | 14220.4724409448818897637795275590551181 | 137200 | 145660.7073040697172 | 0 | 0 | 14000 | 14863.337480007114 | MISCELLANEOUS, FUEL, OVERHEAD |  | 162200 | 81084.5028679216336346456692913385826772 | 176867.8511507370150897637795275590551181 | [8 empty] | 606 |  | 720 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL |  | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS DISCOVERED DURING A DIRECT ASSESSMENT DIG. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | LEAKING WELD | [13 empty] | YES | [62 empty] | NO | [63 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2019 | [12 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | DURING AN IM ECDA DIG ON 7/4/2019, TWO SMALL PIN HOLE LEAKS WERE FOUND IN A FILLET WELD ON LINE JM-7 AT THE BATESVILLE TB #2 TAP. A 20% PRESSURE REDUCTION WAS IMPLEMENTED, AND THIS LEAK WAS TREATED AS A SAFETY RELATED CONDITION. THE MAOP OF JM-7 IS 720 PSIG AND THE DISCOVERY PRESSURE WAS 606 PSIG. THE LINE WAS RESTRICTED IN THIS AREA TO 485 PSIG UNTIL REPAIRS WERE COMPLETED. JM-7 IS A PREDOMINANTLY 8" PIPELINE AND OPERATES AT 40% SMYS AT THIS LOCATION. THIS IS A CLASS 3 SEGMENT, AND THE LEAK WAS LOCATED ON COMPANY PROPERTY IN INDEPENDENCE COUNTY, AR. THE LEAKS WERE TREATED AS AN SRC UNTIL THE MORNING OF 7/10/2019 WHEN IT WAS DETERMINED THE PLAN OF REPAIR WOULD EXCEED $50,000. A CALL WAS PLACED TO THE NRC (NRC# 1251484) ON 7/10/2019 @ 07:12. A 48 HR. FOLLOW UP TO THE NRC (NRC# 1251686) WAS PLACED ON 7/12/2019 @ 06:52. THE LINE WAS REPAIRED WITHOUT INTERRUPTING SERVICE BY INSTALLING TWO STOPPLES AND A BYPASS. IN BETWEEN THE STOPPLES, AROUND 20 FEET OF PIPE WAS REPLACED ELIMINATING THE LEAK. THE REPAIR JOB WAS COMPLETED ON 7/18/19 AND THE LINE WAS RETURNED TO REGULAR SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190089 | 32762 | 2019-07-30 17:20 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2019-06-30 08:58 | 2019 |  |  | 30.466 | -92.5223 | 1250564 | 2019-06-30 10:31 |  | NATURAL GAS |  | 99000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-06-30 09:43 | 2019-06-30 11:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-06-30 08:58 | 2019-06-30 09:35 | ONSHORE | LA | 70535 | EUNICE | ACADIA | MILEPOST | 501 MP 0 | EUNICE COMPRESSOR STATION | 8001501 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | EMERGENCY SHUTDOWN SYSTEM | 1973 |  | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN SYSTEM MALFUNCTION | CLASS 1 LOCATION | NO |  | 788 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 230000 | 363412.0734908136482939632545931758530184 | 75000 | 79625.022214323825 | 1000 | 1061.666962857651 | 0 | 0 | NONE |  | 306000 | 274047.3205910572497742782152230971128609 | 444098.7626679951242939632545931758530184 | [8 empty] | 602 |  | 975 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR IDENTIFIED THE ALARM AND FOLLOWED THE PROCEDURES TO INITIATE AN INVESTIGATION. FIELD PERSONNEL WAS DISPATCHED TO THE SITE AND RESPONDED TO THE LOCATION OF THE ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  |  | YES | [5 empty] | YES | [19 empty] | YES | [167 empty] | ROGER STREET | COMPLIANCE SPECIALIST | roger_street@transcanada.com | 615-465-5123 |  |  |  |  | ERIK HUGHES | US REGUALTORY COMPLIANCE MANAGER - WEST | 402-492-7447 | erik_hughes@transcanada.com | ON JUNE 30 AT 08:58 CDT, ANR PIPELINE'S GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) FIRE ALARM AT EUNICE COMPRESSOR STATION LOCATED AT 4202 FOURNERAT ROAD, EUNICE, LA 70535 (30.465980, - 92.522270). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 09:35 CDT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED TO THE ATMOSPHERE THROUGH THE VENT STACKS. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO FIRE EXISTED AND CLOSING THE VALVES OPEN TO ATMOSPHERE, WHICH ENDED THE RELEASE AT 09:43 CDT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 99 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED, AND NO MANDATORY EVACUATIONS WERE REQUIRED. THE CAUSE OF THE UNINTENTIONAL RELEASE HAS BEEN ATTRIBUTED TO A FLAME DETECTION EQUIPMENT (FIRE EYE) ACTIVATION THAT INITIATED THE EMERGENCY SHUTDOWN (ESD) SYSTEM. WHEN THE SYSTEM INITIATED, SEVEN ESD VALVES DID NOT FULLY OPERATE ALLOWING GAS TO CONTINUE TO VENT UNTIL PERSONNEL ARRIVED ON SITE AND ISOLATED THE SYSTEM. NO INDICATION OF FIRE WAS OBSERVED IN THE COMPRESSOR BUILDING. THE FLAME DETECTOR UNIT WAS SENT TO THE ORIGINAL MANUFACTURER FOR EVALUATION. THE MANUFACTURER REPORTED THAT THE DETECTION UNIT MET ALL MANUFACTURING SPECIFICATIONS AND OPERATED AS INTENDED. THE MANUFACTURER ALSO RECOMMENDED THAT THE UNIT'S SENSITIVITY BE REDUCED FROM "HIGH" TO "MEDIUM" AND INCREASE THE ACTIVATION DELAY FROM 8 SECONDS TO 10 SECONDS. THESE RECOMMENDED CHANGES ARE DUE TO THE OPERATIONAL AND ENVIRONMENTAL CONDITION IN THE RECIPROCATING ENGINE COMPRESSOR BUILDING. THE CHANGE IN SENSITIVITY AND TIMING DOES NOT AFFECT THE SAFETY OF THE PIPELINE FACILITY AND THE SYSTEM HAS BEEN TESTED ACCORDING TO PROCEDURES. THE CHANGES TO THE FLAME DETECTION EQUIPMENT WAS COMPLETED ON 26 JULY 2019. INVESTIGATION INTO ESD VALVES DETERMINED THAT PILOT GAS WAS NOT VENTED COMPLETELY UPON AUTOMATIC ACTIVATION. EVEN THOUGH THE ESD SYSTEM HAD ACTIVATED AND STARTED TO VENT PILOT GAS, PRESSURES THROUGH THE SUPPLY LINE MAINTAINED ENOUGH PRESSURE TO PREVENT THE VALVES FROM FULLY MOVING TO THE CLOSED POSITION. TO REDUCE THE PILOT GAS SUPPLY, A SMALLER 1/32" ORIFICE PLATE WAS INSTALLED INTO THE SUPPLY LINE ON AUGUST 14, 2019, REDUCING THE FLOW OF GAS AND RECHARGE TIME INTO THE SUPPLY SYSTEM. THE PURPOSE OF THE ORIFICE IS TO MAINTAIN PILOT GAS PRESSURE IN THE EVENT OF A MINOR LEAK TO PREVENT AN UNINTENDED ESD. THE ESD SYSTEM HAS BEEN INSPECTED AND TESTED ACCORDING TO PROCEDURES SINCE THE ORIFICE REPLACEMENT AND OPERATED CORRECTLY. THE SYSTEM HAS BEEN PLACED BACK INTO FULL SERVICE. IN ADDITION TO THE ORIFICE CHANGE, FIVE EMERGENCY VALVES WILL BE UPGRADED WITH NEW THREE-WAY PILOT VALVE ASSEMBLIES AND THE END-OF-STROKE VALVE ON TWO OTHER VALVES WILL BE REPLACED, WHICH WILL ENSURE PROPER OPERATION OF THE VALVES. THE ADDITIONAL UPGRADES TO THE VALVES ARE ANTICIPATED TO BE COMPLETED WITHIN 120 DAYS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190090 | 33322 | 2019-07-31 13:50 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-07-09 12:43 | 2019 | EASTERN | NO | 38.5762 | -83.4674 | 1251442 | 2019-07-09 16:23 | 1251614 | NATURAL GAS |  | 10969.5 | 59 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | COMPRESSED NATURAL GAS WAS USED TO MAINTAIN SERVICE TO CUSTOMERS |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-07-11 15:30 | VALVE CLOSURE |  | 2019-07-11 19:15 | 0 | 2019-07-09 12:42 | 2019-07-09 15:58 | ONSHORE | KY | 41179 | VANCEBURG | LEWIS | SURVEY STATION NO. | 3876+89 | EM122 | FLOC NUMBER 026298 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.188 | 42000 | X42 | OTHER | UNKNOWN | UNKNOWN | EXTRUDED POLYEHYLENE |  | NO | [26 empty] | 1995 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 123 |  | NO | NO | [5 empty] | 0 | 0 | 137 | 145.448373911498187 | 25449 | 40210.755905511811023622047244094488189 | 286740 | 304422.38492980284774 | 1000 | 1061.666962857651 | 0 | 0 |  | 2.32 | 313326 | 161216.1639808907026984330708661417322835 | 345840.256172083807950622047244094488189 | 0 | 0 | 0 | 0 | NO |  |  |  | 450 | 336 | 720 | 192.619(A)(1) |  | 1986-05-16 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | NO | YES | MANUAL | MANUAL | 64200 | NO | YES |  |  | YES |  |  |  | YES |  |  | YES |  | YES | SINGLE GAS SUPPLY | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | OUR OPERATING PERSONNEL WAS FIRST NOTIFIED BY LOCAL DISTRIBUTION PERSONEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO THE INCIDENT DID NOT OCCUR DUE TO CONTROL ROOM OR SUPERVISORY PERSONNEL ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | NO | [7 empty] | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | MARK NEWMAN | REGIONAL COMPLIANCE SPECIALIST | mark_newman@transcanada.com | 304-722-8475 | 304-722-8420 |  |  |  | GEORGE HAMATY | MANAGER EAST US REGULATORY COMPLIANCE | 304-357-3782 | george_hamaty@transcanada.com | ON 7/9/2019 A CONTRACTOR WAS WORKING FOR THE LANDOWNER TO INSTALL A NEW CULVERT AT THE SAME LOCATION AS AN EXISTING CULVERT. DURING THE EXCAVATION THE CONTRACTOR CAME IN CONTACT WITH PIPELINE OPERATOR COLUMBIA GAS TRANSMISSION, LLC (OPID 2616), COLUMBIA, PIPELINE EM-122. PRESSURE ON EM-122 WAS REDUCED FROM 450 PSIG TO ABOUT 100 PSIG IN ORDER TO MAINTAIN MARKET REQUIREMENTS UNTIL COMPRESSED NATURAL GAS (CNG) TRUCKS COULD BE USED AS AN ALTERNATE SUPPLY WHILE REPAIRS WERE MADE. APPROXIMATELY 9 COMPRESSED TANKERS MAINTAINED THE VANCEBURG MARKET THROUGHOUT THE PIPELINE REPAIR. THE CONTRACTOR WAS USING AN EXCAVATOR (KOBELCO 135SR) TO INSTALL THE NEW CULVERT. THE LANDOWNER ACKNOWLEDGE THAT A CALL WAS NOT MADE TO KY811. COLUMBIA HAS VERIFIED THAT A LOCATE REQUEST FOR THIS LOCATION WAS NOT MADE FOR THE DATE OF THIS INCIDENT. ON 7/9/2019 COLUMBIA LOWERED THE PIPELINE PRESSURE TO 100 PSIG, AND PROVIDE ONSITE MONITORING A CONTROLLED LEAK 24/7 UNTIL MATERIALS AND EQUIPMENT WERE AVAILABLE TO MAKE REPAIRS. LINE EM-122 IS LOCATED IN A CLASS 1 LOCATION. THE CLOSEST HABITABLE RESIDENTS ARE APPROXIMATELY 500 FEET AWAY AND WERE MADE AWARE OF THE INCIDENT AND MAINTAINED COMMUNICATION DURING REPAIR OPERATIONS. ON 7/11/2019 CNG WAS PLACED INTO SERVICE TO VANCEBURG MARKET. LINE EM-122 WAS SHUT IN AND BLOWDOWN. NO MARKET CUSTOMERS WERE AFFECTED, BUT APPROXIMATELY 14 FARM TAPS WERE SHUT IN DURING PIPELINE REPAIRS. ON 7/13/2019, FINAL REPAIRS WERE MADE USING PRETESTED 6.625' OD, 0.188 WALL, MAOP OF 720 PSIG PIPE. CNG HAS DISCONNECTED FROM THE VANCEBURG MARKET. THE PIPELINE WAS PURGED AND PLACE INTO SERVICE ON 7/11/2019. COLUMBIA DID INVESTIGATE PUBLIC AWARENESS RECORDS AND DETERMINED THAT THE LANDOWNER HAS RECEIVED PAST INFORMATION FROM ITS MAILING PROGRAM THAT INCLUDED A REMINDER TO CALL BEFORE YOU DIG.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20190091 | 32652 | 2019-08-01 22:30 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 811 LOUISIANA ST. SUITE 1200 | HOUSTON | TX | 77002 | 2019-07-05 15:30 | 2019 |  |  | 27.9428 | -94.3892 | 1251095 | 2019-07-05 17:55 |  | NATURAL GAS |  | 5225 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-05 18:00 | 2019-08-22 12:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-05 17:13 | 2019-07-05 18:00 | OFFSHORE | [28 empty] | 350 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | HIA | 582 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 |  | 0.5 | 60000 | 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | ITALSIDER | ASPHALT | [28 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 143 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 12018 | 18989.0708661417322834645669291338582677 | 750000 | 796250.22214323825 | 250000 | 265416.74071441275 | 0 | 0 |  |  | 1012018 | 480826.4092137315984251968503937007874016 | 1080656.03372379273228346456692913385827 | [8 empty] | 745 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SUB-SEA AND NO CONTROLLER'S ACTIONS WERE RELATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 7137251663 |  |  |  |  | JOHN JEWETT | DOT COMPLIANCE AND FACILITY SECURITY MANAGER | 7138602605 | john.jewett@genlp.com | ON 7/5/19, A GENESIS EMPLOYEE RECEIVED A CALL AT 15:30 HOURS OF A SUSPECTED LEAK IN THE HIA 582 AREA. DURING A HELICOPTER OVERFLIGHT, THE GENESIS EMPLOYEE OBSERVED SOME BUBBLING IN THE WATER AND A BARELY VISIBLE SHEEN (500 FT. BY 20FT.) AT THE REPORTED COORDINATES. THE LEGS OF THE PIPELINE WERE SHUT IN AS GENESIS CONTINUED TO MONITOR. A DIVE BOAT AND CREW WAS CALLED IN TO INVESTIGATE. WHEN THE DIVE CREW ARRIVED TO INSPECT THE PIPELINE, THEY NOTICED HOLE WITH AN APPROXIMATE DIAMETER OF 1/8 IN.. AT THE TIME, HOWEVER, VISIBILITY ON THE SEA FLOOR WAS VERY POOR MAKING ANY FURTHER DETERMINATION OF THE EXACT CAUSE DIFFICULT TO COMPLETE. THE PIPELINE WILL CONTINUE TO BE SHUT IN UNTIL A SEPARATE DIVE BOAT ARRIVES MID TO LATE AUGUST TO FURTHER ASSESS THE CAUSE OF THE LEAK AND THEN REPAIR THE PIPELINE. SUPPLEMENTAL REPORT (9/03/2019): ON 8/22/19 A DIVE TEAM REPAIRED PIPE WITH 30" PLEDCO CLAMP. THE PIPELINE WAS PRESSURED TO 1000 PSI WITH NO LEAKAGE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190092 | 32862 | 2019-08-02 12:25 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-07-05 14:40 | 2019 |  |  | 36.3459 | -86.8682 | 1251077 | 2019-07-05 15:25 |  | NATURAL GAS |  | 3506 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-05 14:40 | 2019-07-10 11:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-05 14:40 | 2019-07-05 14:40 | ONSHORE | TN | 37080 | Not Within a Municipality | DAVIDSON | SURVEY STATION NO. | 1322 | LINE 500-1 | VALVE SEGMENT 563-1-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | ESD SYSTEM; | 2018 |  | CARBON STEEL |  | OTHER | [8 empty] | ESD ACTIVATION; | CLASS 2 LOCATION | NO |  | 760 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 8655 | 13675.3543307086614173228346456692913386 | 0 | 0 | 600 | 637.0001777145906 | 0 | 0 |  |  | 9255 | 9254.051577811703525984251968503937007874 | 14312.3545084232520173228346456692913386 | [8 empty] | 848 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL CONTROL ROOM MANAGEMENT PROCESSES WERE FOLLOWED; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [16 empty] | YES | [10 empty] | YES | UPS SYSTEM BATTERIES; | [161 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | THE STATION WAS IN MANNED OPERATION AS INVESTIGATION CONTINUED FROM AN ESD EVENT ON JUNE 29, 2019. (REFERENCE DOT REPORT #2019087) INCLEMENT WEATHER INCLUDING LIGHTNING ACTIVITY IN THE AREA CAUSED A MOMENTARY LOSS OF COMMERCIAL POWER. A COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) WAS INITIATED. THE INTERLOCKING COMPRESSOR STATION ESD FUNCTIONED AS DESIGNED RESULTING IN A PHMSA REPORTABLE GAS LOSS OF 3,506 MCF. OPERATIONS PERSONNEL WERE ON SITE DURING THE EVENT AND CONFIRMED A LOUD POP DUE TO LIGHTNING ACTIVITY. INVESTIGATION RESOURCES INCLUDING DIVISION CONTROLS SUPPORT, HOUSTON AUTOMATION AND OPERATIONS CONFIRMED LOCAL INCLEMENT WEATHER CAUSED THE LOSS OF COMMERCIAL POWER, AND THE STATION UPS SYSTEM DID NOT HOLD THE REQUIRED COMPRESSOR STATION VOLTAGE (120 VDC) IN THE INTERIM WHILE THE EMERGENCY GENERATOR WAS RAMPING UP TO COME ON-LINE. THIS INTERIM LACK OF VOLTAGE TRIGGERED THE COMPRESSOR STATION ESD. INVESTIGATION OF THIS EVENT AND INVESTIGATION AND REPAIRS CONCERNING THE JUNE 29, 2019 INCIDENT CONTINUED WITH THE STATION HELD OFF LINE BY OPERATIONS TO ALLOW CERTAIN TASKS TO OCCUR UNTIL JULY 10, 2019 AT 11:00-HOURS WHEN THE STATION RESUMED MANNED OPERATION. ON-SITE PERSONNEL WERE UNABLE TO LOCATE ANY DIRECT LIGHTNING STRIKE TO THE FACILITIES. NO DAMAGE BY THIS LIGHTNING EVENT AND INCLEMENT WEATHER WAS IDENTIFIED. THE STATION REMAINED IN MANNED OPERATION UNTIL OCTOBER 3, 2019, AT APPROXIMATELY 18:00-HOURS WHEN ALL REPAIRS FOR THE JUNE 29, 2019 INCIDENT WERE COMPLETED AND THE STATION RETURNED TO AUTOMATED OPERATION. NRC 48-HOUR UPDATE IS REPORT #1251213.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190093 | 32525 | 2019-08-07 16:34 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-07-08 15:35 | 2019 |  |  | 28.3781 | -92.7564 | 1251360 | 2019-07-08 19:24 |  | NATURAL GAS |  | 571 | 22638 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-08 19:00 |  | YES |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-20 19:10 | 2019-07-20 19:10 | OFFSHORE | [28 empty] | 180 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EAST CAMERON | 286 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 |  | 0.375 | 52000 | API-5LX | SEAMLESS |  | U.S. STEEL | OTHER | CONCRETE AND SOMASTIC | [27 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 55690 | 59124.23316154258419 | 1405 | 2219.973753280839895013123359580052493438 | 468000 | 496860.138617380668 | 0 | 0 | 0 | 0 |  |  | 525095 | 246735.6383148923816191863517060367454068 | 558204.3455322040920850131233595800524934 | [8 empty] | 670 |  | 1440 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 48734 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | SUPERVISOR | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1251483 AT APPROXIMATELY 3:35 PM CDT ON JULY 8, 2019, SURFACE BUBBLES WERE DISCOVERED BY A THIRD PARTY FLYING OVER LINE ON THE TEXAS EASTERN TRANSMISSION (TETLP) IN EAST CAMERON BLOCK 286. TETLP TOOK PROACTIVE MEASURES AND SHUT DOWN TETLP'S 16-INCH, LINE 41-A-5 NATURAL GAS PIPELINE ON JULY 8, 2019 AT APPROXIMATELY 7:00 PM CDT. DUE TO HURRICANE ACTIVITIES, TETLP WAS UNABLE TO INVESTIGATE AND DETERMINE THE SOURCE OF THE LEAK UNTIL JULY 20, 2019. THE LINE REMAINS SHUT DOWN AND HAS NOT BEEN RETURNED TO SERVICE. THIS LINE IS SCHEDULED FOR ABANDONMENT IN 2019. THE FERC APPROVAL FOR ABANDONMENT WAS RECEIVED ON JULY 18, 2019. THE APPARENT CAUSE IS INTERNAL CORROSION.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20190094 | 32985 | 2019-08-13 12:39 | SUPPLEMENTAL FINAL | 31943 | MIDCOAST GATHERING (NORTH TEXAS) L.P. | 2950 NORTH LOOP WEST SUITE 1150 | HOUSTON | TX | 77092 | 2019-07-19 03:30 | 2019 |  |  | 32.9857 | -97.6849 | 1252461 | 2019-07-19 05:40 |  | NATURAL GAS |  | 5135 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-19 03:30 | 2019-07-19 04:45 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-19 03:15 | 2019-07-19 04:23 | ONSHORE | TX | 76082 | SPRINGTOWN | PARKER | MILEPOST | SPRINGTOWN YA | SPRINGTOWN PIPE YARD | CAG 2ND | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2011 |  | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE | CLASS 3 LOCATION | NO |  | 1 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 15706 | 24816.3044619422572178477690288713910761 | 0 | 0 | 405 | 429.975119957348655 | 0 | 0 |  |  | 16111 | 16472.8119147604326884383202099737532808 | 25246.2795818996058728477690288713910761 | [8 empty] | 490 |  | 500 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 1500 | NO | [5 empty] | YES | GATHERING LINE | YES |  |  |  |  | YES | GATHERING LINE | TYPE A GATHERING | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | CONTROL ROOM OPERATOR FAILED TO NOTIFY FIELD PERSONNEL OF LOSS IF COMMUNICATIONS |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | BENITA KALKA | GIS ANALYST | benita.kalka@midcoastenergy.com | 7138212072 |  |  |  |  | MELANIE HOSEY | DIRECTOR OF INTEGRITY | 7138212063 | melanie.hosey@midcoastenergy.com | THE COMPRESSION AT THE MIDCOAST SPRINGTOWN PLANT SHUT DOWN DUE TO A POWER FAILURE. THE PLANT IS APPROXIMATELY 350 YARDS FROM THE SPRINGTOWN PIPE YARD WHERE THE RELIEF VALVE ON 2ND CAG WENT OFF AT SET PRESSURE (490 PSIG). GAS CONTROL RECEIVED AN ALARM THAT THE DECATUR COMPRESSOR SHUT IN AND WEATHERFORD PLANT CALLED GAS CONTROL THAT THEY WERE LOSING INLET VOLUME. GAS CONTROL CALLED PLANT OPERATOR TO GO TO SPRINGTOWN PLANT TO CHECK ON COMPRESSION AT 3:00 AM. AT 3:15 AM POLICE CALLED GAS CONTROL THAT THERE WAS GAS RELIEVING AT THE SPRINGTOWN PIPE YARD. MIDCOAST EMPLOYEE ARRIVED AT THE SPRINGTOWN PLANT AND HEARD RELIEF VALVE GOING OFF AT 3:30 AM (CONFIRMATION BY THE OPERATOR). MIDCOAST OPERATIONS TECH WAS CALLED TO INVESTIGATE THE RELIEF VALVE AND VERIFIED THE RELIEF VALVE ON 2ND CAG WAS RELIEVING AT 4:23 AM. OPERATION TECH OPEN BLOCK VALVE TO SWITCH 2ND CAG GAS INTO SM-12 PIPELINE AND THE RELIEF VALVE CLOSED AT 4:45 AM. THE RELIEF VALVE HAD RELIEVED AT 490 PSIG AT SET PRESSURE. RELIEF VALVE INFORMATION: MAKE: CONSOLIDATED, MODEL # 3910R-4-CC-V-65 SIZE 6' X 8' X8' MIDCOAST PERSONNEL (OPERATIONS, GAS CONTROL, IT,) PERFORMED A IN HOUSE INVESTIGATION AND HAS IDENTIFIED THAT WE WILL INSTALL A LOW LOW ALARM AT THE 4TH CAG TO SM-12 PIPELINE TO GIVE AN ALARM AT 30,000N MCF TO INFORM GAS CONTROL TO CALL OUT PERSONNEL TO THE SPRINGTOWN PLANT (ONLY MANNED DAYLIGHT HOURS) TO CALL SOMEONE OUT. THIS SHOULD PREVENT TISE FROM OCCURRING AGAIN. PREVENTION OF RECURRENCE TO PREVENT THIS FROM HAPPENING AGAIN A COMMITTEE REVIEWED THE INCIDENT AND DETERMINED THE FOLLOWING WILL BE IMPLEMENTED. AUTOMATE THE BYPASS VALVE TO OPEN AND COMMON UP THE SUCTION AND DISCHARGE HEADERS. SETTING PRESSURE TO OPERATE BELOW RELIEF VALVE SETTING. INSTALL A CHECK VALVE DOWNSTREAM OF THE PSV TO PREVENT ANY BACKFLOW IN THE EVENT SPRINGTOWN'S DISCHARGE LINE PRESSURE IS HIGHER THAN SPRINGTOWN'S SUCTION LINE PRESSURE. CHANGE THE METER RUN COMMUNICATION TO ALLOW GAS CONTROL THROUGH SCADA TO SEE NO FLOW ON THE SUCTION LINE TO SPRING TOWN. AFE HAS BEEN APPROVED, ENGINEERING HAS ORDERED PARTS AND SET UP A WORK ORDER. GAS CONTROL'S INCIDENT REVIEW CONTROLLER DIDN'T RECOGNIZE COMPRESSOR UNITS WERE DOWN DUE TO THE COMMUNICATIONS OUTAGE. REVIEWED THE GAS CONTROL AND OPERATIONS MEETING MINUTES AND SCADA CHANGES MADE. REVIEWED GAS CONTROL'S COMMUNICATION OUTAGE PROCEDURE. REVIEWED CORRECTIVE ACTIONS: GAS CONTROL WILL NOTIFY ON-CALL OPERATOR IF COMMUNICATION OUTAGE OCCURS AT SPRINGTOWN PLANT. CORRECTIVE ACTIONS 11/13/2019 GAS CONTROL CHANGE THE COMMUNICATION OUTAGE SETPOINT TO 30 MINUTES FROM 60 MINUTES. MOVE THE 4TH CAG OUTLET METER TO A SEPARATE COMMUNICATIONS PATH SO EITHER INLET OR OUTLET OF COMPRESSOR STATION CAN BE SEEN IF FUTURE COMMUNICATION OUTAGE OCCURS. CONTROLLER WILL NOTIFY FIELD PERSONAL IF COMMUNICATION OUTAGE OCCURS. FIELD INSTALLED A PRESSURE CONTROL VALVE TO SHUT GAS IN AT A PRESSURE SET POINT. INSTALLED A CONTROL VALVE TO RE-ROUTE GAS TO A DIFFERENT PIPELINE AT A PRESSURE SET POINT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190095 | 33137 | 2019-08-16 08:59 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-07-18 13:53 | 2019 |  |  | 34.7475 | -87.8178 | 1252409 | 2019-07-18 14:57 |  | NATURAL GAS |  | 15.5 | 27097 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-18 14:00 | 2019-07-24 20:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-18 13:53 | 2019-07-18 13:53 | ONSHORE | AL | 35633 | FLORENCE | LAUDERDALE | MILEPOST | 160.05 | LINE 10 | BART-MTPL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [20 empty] | WELD SADDLE | [17 empty] | UNKNOWN |  | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 62595 | 66455.043540074664345 | 36 | 56.88188976377952755905511811023622047244 | 484915 | 514818.235294117834665 | 0 | 0 | 0 | 0 |  |  | 547546 | 256472.8310983739669813385826771653543307 | 581330.1607239562785375590551181102362205 | [8 empty] | 810 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 87490 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [6 empty] | YES | YES | HYDROGEN INDUCED CRACKING AT ORGINAL CONSTRUCTION WELD REPAIR | [12 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2019 | [55 empty] | YES | 1996 | 1310 | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT 1252608 AT APPROXIMATELY 1:53 PM CDT ON JULY 18, 2019, AN ENBRIDGE EMPLOYEE DISCOVERED A NATURAL GAS RELEASE DURING A HYDO-VAC EXCAVATION ACTIVITIES ON TEXAS EASTERN TRANSMISSION'S (TETLP) LINE 10 PIPELINE SYSTEM IN LAUDERDALE COUNTY, AL. THE LEAK LOCATION WAS SUBSEQUENTLY ISOLATED AT APPROXIMATELY 2:35 PM CDT, STOPPING THE GAS RELEASE. THE LEAK WAS ON THE WELD SADDLE CONNECTING LINE 10 TO A 16 INCH PIPE. THE AFFECTED PIPE WAS REPLACED AND RETURNED TO SERVICE AT APPROXIMATELY 8:30 PM CDT ON JULY 24, 2019. THE APPARENT CAUSE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL-FINAL REPORT 01/02/2020 METALLURGICAL ANALYSIS REPORT DETERMINED CAUSE OF THE LEAK WAS BENDING LOAD AND HYDROGEN INDUCED CRACKING AT ORIGINAL CONSTRUCTION WELD REPAIR.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190097 | 33434 | 2019-08-22 17:22 | SUPPLEMENTAL FINAL | 1217 | BEAR CREEK STORAGE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-07-25 08:18 | 2019 | CENTRAL | YES | 32.3886 | -92.9297 | 1253115 | 2019-07-25 09:07 | 1253288 | NATURAL GAS |  | 154.08 | 98.29 | 0.3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-07-25 08:35 | 2019-12-13 17:30 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-07-25 08:23 | VALVE CLOSURE |  | 2019-07-25 08:30 | 0 | 2019-07-25 07:50 | 2019-07-25 08:18 | ONSHORE | LA | 71008 | Not Within a Municipality | BIENVILLE | SURVEY STATION NO. | 959 | BCS-5.7-4 LINE | BCS-5.7-4 LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.375 | 52000 | API 5L | SEAMLESS |  | ARMCO STEEL | COAL TAR |  | YES | [26 empty] | 1981 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 331 |  | NO | NO | [5 empty] | 0 | 0 | 208 | 220.826728274391408 | 327 | 516.677165354330708661417322834645669291 | 43172 | 45834.286120490508972 | 50 | 53.08334814288255 | 48108 | 51074.674249155874308 | LAB COST & FREIGHT - $2,000; ENVIRONMENTAL TESTING & SOIL REMEDIATION - $46, 108 | 2.12 | 91865 | 43212.3761532207362849921259842519685039 | 97699.5476114179879466614173228346456693 | 0 | 0 | 0 | 0 | NO |  |  |  | 2267 | 1815 | 3100 | 192.619(A)(1) |  | 1981-11-13 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1712 | YES | [7 empty] | YES |  |  |  |  | YES | PIG TRAPS ARE NOT INSTALLED | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [5 empty] | YES |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [20 empty] | YES | [42 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 25TH, 2019 AT 7:50 AM A BIENVILLE SHERIFF NOTICED A POTENTIAL LEAK COMING FROM THE BEAR CREEK STORAGE COMPANY, LLC (BCSC) 5.7-4 LINE. THE SHERIFF'S DEPARTMENT THEN NOTIFIED BCSC GAS CONTROL. AT 8:18 AM BCSC PERSONNEL ARRIVED ON SITE TO CONFIRM THE LEAK. AT 8:30 AM THE LINE WAS ISOLATED, AND AT 8:35 AM THE BLOWDOWN PROCESS COMMENCED. THE UNINTENTIONAL GAS LOSS WAS ESTIMATED TO BE 154.08 MCF. THE SECTION OF PIPE THAT HAD A LEAK WAS CUTOUT AND SENT IN FOR METALLURGICAL ANALYSIS. AFTER A NEW SECTION OF PIPE WAS INSTALLED, THE PIPELINE WAS RESTARTED ON DECEMBER 13TH, 2019. BCSC HAS DETERMINED THAT THE CAUSE OF THE LEAK WAS INTERNAL PITTING CORROSION. BCSC BELIEVES THE CAUSE MAY BE MIC, BUT THE METALLURGICAL REPORT IS NOT DEFINITIVE. AFTER THE INCIDENT, BCSC BATCH TREATED ALL LINES WITH BIOCIDE. BCSC WILL EVALUATE THE CURRENT INTERNAL CORROSION MITIGATION PROGRAM AND MAKE CHANGES TO THE PROGRAM BASED ON FINDINGS FROM THE EVALUATION. BECAUSE LIQUIDS HAD BEEN RELEASED DURING THE INCIDENT, BCSC COMPLETED ENVIRONMENTAL TESTING AND REMOVED, DISPOSED OF, AND REPLACED, THE CONTAMINATED SOIL AT THE LEAK SITE. THE ACTIONS TAKEN TO REMEDIATE THE SITE LED TO THE ABNORMALLY HIGH COSTS ASSOCIATED WITH THE INCIDENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190098 | 32770 | 2019-08-23 09:18 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-07-26 06:10 | 2019 |  |  | 36.4408 | -96.4953 | 1253231 | 2019-07-26 07:47 |  | NATURAL GAS |  | 23516 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-26 07:57 | 2019-08-01 17:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-26 06:10 | 2019-07-26 07:30 | ONSHORE | OK | 74035 | HOMINY | OSAGE | MILEPOST | 5239+72 | LINE 7 | LINE 7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 |  | 0.25 | 52000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | US STEEL | COAL TAR | [28 empty] | 1970 | 1970 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 81 | 20 |  | CLASS 1 LOCATION | NO |  | 388 |  | NO | NO | NO |  |  |  |  | 5000 | 5308.334814288255 | 0 | 0 | 55750 | 88087.9265091863517060367454068241469816 | 250000 | 265416.74071441275 | 10000 | 10616.66962857651 | 6000 | 6370.001777145906 | MISCELLANEOUS |  | 326750 | 184725.9600202808432257217847769028871391 | 375799.6734436097727060367454068241469816 | [8 empty] | 750 |  | 780 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 101100 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [63 empty] | YES | YES | [6 empty] | 2015 | [55 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON 7/26/2019 AT 06:10 RATE OF CHANGE ALARMS ALERTED THE SYSTEM CONTROLLER OF A POSSIBLE SITUATION WITH LINE 7. THE CONTROLLER STARTED TO DISPATCH O&M TECHS TO INVESTIGATE THE CAUSE OF THE ALARMS. AT 6:20 A LANDOWNER CALLED SYSTEM CONTROL TO NOTIFY OF A JET ENGINE NOISE ON HIS PROPERTY. O&M TECHNICIANS DISCOVERED THE RUPTURE SITE TO BE ON A LARGE RANCH NEAR HOMINY, OKLAHOMA. THE AREA IS A CLASS 1 LOCATION AND THERE WERE NO INJURIES, EVACUATIONS, FIRES, OR FATALITIES. VALVES WERE SHUT AND THE LINE WAS ISOLATED AT 07:57. THE NRC WAS NOTIFIED ON 7/26/19 AT 07:47 (NRC# 1253231). A 48 HOUR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 7/27/19 AT 15:57 (NRC# 1253370). THE FAILED SECTION OF PIPE WAS REMOVED AND SENT TO A LAB FOR METALLURGICAL ANALYSIS. THE RESULTS OF THE METALLURGICAL FAILURE EXAMINATION INDICATED: -THE PIPE FAILED DUE TO NEAR NEUTRAL STRESS CORROSION CRACKING FROM A BREAK IN THE OD SURFACE COATING THAT ALLOWED THE PIPE TO BE EXPOSED TO THE ELEMENTS. -STRAIGHT, WIDE CRACKS WERE OBSERVED WITH VERY LITTLE BRANCHING. THESE ARE A HALLMARK FEATURE OF NEAR-NEUTRAL STRESS CORROSION CRACKING. -EXPOSURE TO THE ELEMENTS CAUSED PITTING CORROSION, WHICH ACTED AS NUCLEATION SITES FOR STRESS CORROSION CRACKING. -THE FAILURE INITIATION REGION EXHIBITED A PRE-EXISTING CRACK THAT HAD PROPAGATED APPROXIMATELY 80% OF THE PIPE WALL THICKNESS AT THE TIME OF FAILURE. -IN ADDITION, THE OD SURFACE OF THE PIPE EXHIBITED A COLONY OF CRACKS PROPAGATING PARALLEL TO THE FRACTURE SURFACE. THE REGIONS OF THE PIPE IMMEDIATELY ADJACENT TO THE FAILURE INITIATION REGION DID NOT EXHIBIT PITTING CORROSION, INDICATING THAT THE INITIAL REGION OF COATING DAMAGE WAS SMALL AND LOCALIZED. 10/1/2019 SUPPLEMENTAL REPORT PART G.5.1 UPDATED TO DETERMINED BY METALLURGICAL ANALYSIS PART G.5.3 UPDATED TO STRESS CORROSION CRACKING PART H NARRATIVE UPDATED TO INCLUDE METALLURGICAL RESULTS
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190099 | 32606 | 2019-08-23 10:19 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-08-20 08:44 | 2019 |  |  | 33.1525 | -85.5113 | 1255737 | 2019-08-20 09:03 |  | NATURAL GAS |  | 23800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-20 05:20 | 2019-08-20 09:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-08-20 05:20 | 2019-08-20 05:15 | ONSHORE | AL | 36276 | WADLEY | RANDOLPH | MILEPOST | MP 969.48 | COMPRESSOR STATION 110 - MAIN UNIT (MU) #04 | MU 04 RELIEF VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | 3/8" PILOT TUBING TO THE RELIEF VALVE |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [38 empty] | 2018 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL (SS) TUBING | OTHER | [8 empty] | SS TUBING CONNECTION FAILURE | CLASS 1 LOCATION | NO |  | 7 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 52836 | 83483.6535433070866141732283464566929134 | 400 | 424.6667851430604 | 100 | 106.1666962857651 | 0 | 0 |  |  | 53336 | 55011.6637164178894212598425196850393701 | 84014.4870247359121141732283464566929134 | [8 empty] | 753 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | LOCAL LANDOWNER CALLED THE SHERIFF ABOUT NOISE. DEPUTY CALLED, SEE PART H. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA AND ESD SYSTEMS WERE OPERATING NORMALLY. PIPELINE CONTROL DISPATCHED THE OPERATION TECHNICIAN AFTER NOTIFICATION CALL RECEIVED FROM THE SHERIFF DEPUTY. THE RESPONSE PROCESSES AND PROCEDURES WERE EFFECTIVE TO IDENTIFY THE TUBING CONNECTION FAILURE AND SHUT-DOWN THE COMPRESSOR UNIT TO STOP THE GAS RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | 3/8" PILOT TUBING CONNECTION FAILED AT THE PRESSURE RELIEF VALVE PILOT CAUSING THE RELIEF VALVE TO VENT OPEN (LOSS OF PILOT PRESSURE). | [7 empty] | YES | [177 empty] | TIM HUGGINS | PRINCIPAL ENGINEER | timothy.n.huggins@williams.com | 7132152889 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | COMPRESSOR STATION 110 MAIN UNIT 04 RELIEF VALVE RELEASE TUBING CONNECTION FAILURE EVENT TIMELINE 08/20/2019 4:47 AM PIPELINE CONTROL (HOUSTON) CONTACTED LOCAL OPERATION TECHNICIAN. CONTROLLER HAD RECEIVED A CALL FROM THE LOCAL DEPUTY THAT WAS ON-SITE OUTSIDE AT THE STATION GATE. LOCAL LANDOWNER NEAR STATION HAD CALLED THE SHERIFF ABOUT THE STATION NOISE AND DEPUTY WAS DISPATCHED TO THE SITE. 5:15 AM OPERATION TECHNICIAN ARRIVED AND HEARD GAS RELEASE, ACCESS WAS HELD-UP BY THE DEPUTY UNTIL IDENTIFIED. 5:20 AM OP TECH MANUALLY SHUT-DOWN THE UNIT AND IDENTIFIED THE PILOT TUBING CONNECTION FAILURE AT THE PRESSURE RELIEF VALVE. THE 3/8-INCH STAINLESS STEEL TUBING CONNECTION FAILED AT THE PRESSURE RELIEF VALVE PILOT AND CAUSED THE RELIEF VALVE TO VENT OPEN (LOSS OF PILOT PRESSURE TO THE RELIEF VALVE). NO OTHER OPERATING ISSUES WERE IDENTIFIED. 6:15 AM OPERATIONS PERSONNEL REVIEWED THE STATION HMI AND TRENDED THE OPERATION DATA BACK TO APPROXIMATELY 2:40 AM FOR NORMAL OPERATION. A 9 PSIG PRESSURE DROP WAS NOTED ON MU04 WITH NO CHANGES IN HORSEPOWER COMMANDS. THERE WERE NO SHUT-DOWN ALARMS. MU04 WAS RUNNING UNTIL MANUALLY SHUT-DOWN AT 5:20 AM. THE REASONABLE GAS RELEASE DURATION IS APPROXIMATELY 2-HOURS AND 40-MINUTES. 7:33 AM OPERATIONS NOTIFIED DIVISION ENGINEER TO DETERMINE THE APPROXIMATE GAS RELEASE VOLUME ASSOCIATED WITH THIS DURATION. 8:41 AM ENGINEER CALCULATED 23,800 MSCF FOR THE GAS RELEASE DURATION. 8:44 AM SECURITY OPERATIONS CENTER WAS CONTACTED AND THE GAS RELEASE VOLUME WAS CONFIRMED WITH PIPELINE SAFETY. THIS GAS RELEASE EVENT WAS DETERMINED TO BE A REPORTABLE INCIDENT DUE TO EQUIPMENT FAILURE AND THE RELEASE VOLUME EXCEEDING 3 MMSCF. 9:00 AM THE PILOT TUBING WAS REPLACED, PILOT RE-SET, CHECKED, AND COMPRESSOR UNIT AND RELIEF VALVE WERE RETURNED BACK TO SERVICE. THE TUBING CONNECTION FAILURE WAS LIKELY DUE TO VIBRATION (RECIPROCATING COMPRESSOR UNIT) AND FATIGUE ON THE MOUNTED TUBING. THE NEW PILOT TUBING INSTALLATION WAS MODIFIED. 9:03 AM/10:03 AM NRC REPORT TIME SOC CONTACTED THE NRC, INCIDENT REPORT # 1255737. 9:17 AM PHMSA AID CONTACTED PIPELINE SAFETY TO DISCUSS THE INCIDENT. THE GENERAL LOCATION AND RELEASE INFORMATION, WAS AN INCIDENT DUE TO EQUIPMENT FAILURE (TUBING) AND THE GAS RELEASE VOLUME EXCEEDING 3 MMSCF, AND WAS NOT AN EMERGENCY. NO SPECIFIC EVENT DETAILS WERE KNOWN AT THIS TIME, OTHER THAN A TUBING FAILURE HAD OCCURRED CAUSING THE MAIN UNIT RELIEF VALVE TO VENT OPEN. 10:00 AM OPERATIONS DISCUSS THE RELEASE EVENT SUMMARY AND TIMELINE WITH PIPELINE SAFETY, GATHERED SITE INFORMATION, AND THE INCIDENT REVIEW PROCESS BEGINS. 08/22/2019 7:57 AM NRC CONTACTED FOR PHMSA 48-HOUR UPDATE, NRC INCIDENT REPORT # 1256000 AND PROVIDED UPDATED INFORMATION. PLEASE NOTE, THE NRC CONTACT REVISED THE INCIDENT DISCOVER DATE AND TIME TO 22-AUG-2019 AT 08:00 LOCAL INCIDENT TIME, WHICH WAS THE APPROXIMATE TIME FOR THE 48-HOUR UPDATE? THE NRC CONTACT MAY HAVE MISUNDERSTOOD THE COMMUNICATION. THE ORIGINAL INCIDENT DATE AND TIME IS STILL 20-AUG-2019 AT 08:44 LOCAL INCIDENT TIME AS NOTED ON NRC INCIDENT REPORT # 1255737. 08/23/2019 THE INCIDENT REVIEW AND CAUSE WERE COMPLETED. INCIDENT REPORT SUBMITTED. ROOT CAUSE ANALYSIS AND REMEDIATION THE NEW PRESSURE RELIEF/SAFETY VALVE (PSV) WAS INSTALLED ON 10/25/2018 WITH THE ORIGINAL VENDOR PILOT FILTER AND TUBING ATTACHED TO THE PSV. THE VENDORS PSV DESIGN HAD THE PILOT FILTER SUPPORTED SOLELY BY THE TUBING CONNECTING THE FILTER TO THE RELIEF VALVE PILOT. THE TUBING FAILED AT THE CONNECTION TO THE PSV PILOT. THIS FAILURE APPEARS TO BE DUE TO VIBRATION INDUCED FATIGUE FROM THE UNSUPPORTED WEIGHT OF THE PILOT FILTER AND THE FAILURE EVENT WAS REVIEWED WITH THE VENDOR. WILLIAMS-TRANSCO HAS REPLACED THE PILOT TUBING AND REMOTE MOUNTED THE PILOT FILTER FOR BETTER SUPPORT WHICH SHOULD PREVENT ANY FUTURE FAILURE FROM OCCURRING. THE TUBING AND PILOT FILTER INSTALLATION WILL BE MONITORED FOR NORMAL OPERATION AND VIBRATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190100 | 33138 | 2019-08-26 12:57 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-07-29 20:28 | 2019 |  |  | 39.6108 | -81.6289 | 1253581 | 2019-07-29 23:41 |  | NATURAL GAS |  | 45 | 26520.63 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-29 22:33 | 2019-08-19 18:35 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-29 21:59 | 2019-07-30 21:59 | ONSHORE | OH | 45715 | BEVERELY | MORGAN | MILEPOST | 658.85 | LINE 10 | ATHE-BERN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 |  | 0.375 | 52000 | API-5L X-52 | DSAW |  | NATIONAL TUBE | COAL TAR | [28 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 59406 | 93864.5984251968503937007874015748031496 | 454762 | 482805.791363071084062 | 0 | 0 | 0 | 0 |  |  | 514168 | 274584.3216648077650685511811023622047244 | 576670.3897882679344557007874015748031496 | [8 empty] | 806 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 79728 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE VOLUME OF THE LEAK WAS TOO SMALL TO BE DETECTED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | PIPE DURING ORIGINAL CONSTRUCTION INSTALLED ON SHARP ROCK | [8 empty] | YES |  |  |  | YES | [63 empty] | YES | YES |  |  | YES |  |  |  | 2019 | [31 empty] | 2019 | [23 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 713-627-4726 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: 48 HR NRC REPORT # 1253798 AT APPROXIMATELY 8:28 PM EDT ON JULY 29, 2019, ENBRIDGE'S GAS CONTROL RECEIVED A NOTIFICATION OF A NATURAL GAS RELEASE FROM THE PUBLIC ON TEXAS EASTERN TRANSMISSION'S (TETLP) LINE 10 PIPELINE SYSTEM AT MP 658.85 IN LAUDERDALE COUNTY, OH. TETLP DISPATCHED EMPLOYEES TO THE LOCATION AND DISCOVERED A LEAK AT APPROXIMATELY 9:59 PM EDT. TETLP MADE THE NRC NOTIFICATION AT 11:41 PM EDT FOLLOWING CONFIRMED DISCOVERY OF THE LEAK. THE PIPELINE WAS SUBSEQUENTLY ISOLATED AT 10:33 PM EDT, STOPPING THE RELEASE OF GAS. THE AFFECTED PIPE WAS REPLACED AND RETURNED TO SERVICE AT APPROXIMATELY 6:35 PM EDT ON AUGUST 19, 2019. THE APPARENT CAUSE IS STILL UNDER INVESTIGATION. SUPPLEMENTAL REPORT: 01/02/2020 THE APPARENT CAUSE IS A CRACK ASSOCIATED WITH PIPE LAID ON SHARP ROCK DURING ORIGINAL CONSTRUCTION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190101 | 32621 | 2019-08-28 13:59 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-07-29 09:15 | 2019 |  |  | 27.6982 | -97.9708 | 1253535 | 2019-07-29 13:55 |  | NATURAL GAS |  | 340 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-07-29 09:15 | 2019-07-30 05:39 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-29 09:15 | 2019-07-29 09:45 | ONSHORE | TX | 78332 | ALICE | JIM WELLS | MILEPOST | 327+31 | ALICE TO DRISCOLL 8" | 3054 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 |  | 0.25 |  | UNKNOWN | SEAMLESS |  | UNKNOWN | COLD APPLIED TAPE | [28 empty] | 1964 | 1964 | CARBON STEEL |  | MECHANICAL PUNCTURE | 9 | 5 | [7 empty] | CLASS 1 LOCATION | NO |  | 134 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 800 | 1264.041994750656167979002624671916010499 | 45000 | 47775.013328594295 | 1500 | 1592.5004442864765 | 0 | 0 |  |  | 47300 | 22608.4526609844510853018372703412073491 | 50631.5557676314276679790026246719160105 | [8 empty] | 260 |  | 300 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 24148 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | ENTERPRISE EMPLOYEE WORKING NEARBY NOTIFIED GAS CONTROL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS ACTIONS WERE CONSISTENT WITH EXPECTATIONS AND FOLLOWED ESTABLISHED OPERATING PROCEDURES. INVESTIGATION WAS NOT WARRANTED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 9 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHRISTOPHER KRESTA | REGULATORY MANAGER | chris.kresta@energytransfer.com | 713-989-7077 |  |  |  |  | CHRISTOPHER KRESTA | REGULATORY MANAGER | 713-989-7077 | chris.kresta@energytransfer.com | AT APPROXIMATELY 09:15 HOURS ON JULY 29, 2019, ENERGY TRANSFER SUSTAINED A PIPELINE STRIKE FROM A FARMER PLOWING ACROSS IT'S EASEMENT ON ITS ALICE TO DRISCOL 8" TRANSMISSION LINE, ACCOUNT #3054. (RRC SYSTEM ID: 962481). THIS EVENT OCCURRED IN A RURAL CLASS 1 LOCATION IN SOUTH TEXAS OUTSIDE THE CITY OF ALICE IN JIM WELLS COUNTY. THERE WERE NO FIRES, INJURIES, OR EVACUATIONS. NOTIFICATIONS WERE MADE TO THE NRC AT 13:55 HOURS ON JULY 29, 2019 (NRC INCIDENT # 1253535) AND TX RRC (INCIDENT # 2036) AT APPROXIMATELY 14:07 HOURS. THE LINE WAS MECHANICALLY PUNCTURED BY THE LINE STRIKE. IT WAS ISOLATED, BLOWN DOWN, AND THE DAMAGED SECTION WAS REMOVED AND REPLACED. THE LINE WAS RETURNED TO SERVICE ON JULY 30, 2019 AT APPROXIMATELY 05:39 HOURS. THIS REPORT IS BEING SUBMITTED AS A "SIGNIFICANT EVENT" UNDER CFR 191.3 (3) AND DOES NOT MEET OTHER REPORTING CRITERIA. THIS EVENT OCCURRED ON AN INTRASTATE GAS TRANSMISSION PIPELINE UNDER JURISDICTION OF THE TEXAS RAILROAD COMMISSION. TO PREVENT REOCCURRENCE, ENERGY TRANSFER MET WITH THE EXCAVATOR AND EXPLAINED ONE CALL PROCEDURES AND SPECIFICS OF OUR PIPELINE THROUGH THE PROPERTY. ENERGY TRANSFER ALSO LOWERED A PORTION THE AFFECTED PIPELINE IN THE AREA OF THE INCIDENT. ** PHMSA 48 HR. NRC UPDATE MADE ON JULY 30, 2019 AT 16:03 HOURS. ( #1253688)
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190102 | 32795 | 2019-08-29 20:19 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-07-30 20:55 | 2019 |  |  | 31.9497 | -103.1073 | 1253714 | 2019-07-30 21:52 |  | NATURAL GAS |  | 5628 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE FACILITY WAS DOWN BEFORE THE INCIDENT OCCURED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-07-30 20:29 | 2019-07-30 20:30 | ONSHORE | TX | 79745 | KERMIT | WINKLER | MILEPOST | KEYSTONE CS | KEYSTONE CS | B-PLANT SUCTION PIPING | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | URETHANE SEAT | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 85 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 6529 | 10316.1627296587926509186351706036745407 | 3565 | 3784.842722587525815 | 100 | 106.1666962857651 | 0 | 0 |  |  | 10194 | 8485.47509383656777804461942257217847769 | 14207.1721485320835659186351706036745407 | [8 empty] | 581 |  | 585 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE INCIDENT OCCURRED DUE TO A POWER FAILURE WHICH CAUSE THE COMPRESSOR STATION TO STOP WORKING WHICH CAUSED BACK PRESSURE AND THUS GAS RELEASE THROUGH RELIEF VALVE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DUE TO PARTIAL SEAT FAILURE. | [161 empty] | KRITI BHAYANI | PIPELINE ENGINEER - CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 30, 2019, KEYSTONE COMPRESSOR STATION IN KERMIT CITY, WINKLER COUNTY, TEXAS LOST POWER AT 7:50 PM (CST). THE COMPRESSOR STATION SHUTDOWN DUE TO LOSS OF COMMERCIAL POWER. APPROXIMATELY 39 MINUTES AFTER THE LOSS OF POWER, THE PLANT B INLET SUCTION PIPING RELIEF VALVE, SET AT 585 PSIG, BEGAN RELIEVING PRESSURE INTERMITTENTLY UNTIL 8:55 PM DUE TO PRESSURE BUILD UP FROM UPSTREAM NATURAL GAS FLOW. GAS CONTROL NOTIFIED LOCAL OPERATIONS ABOUT THE RELIEF VALVE RELEASE AT 8:29 PM AND AT 8:30 PM PERSONNEL STARTED TO INVESTIGATE THE CAUSE OF THE RELIEF VALVE'S INTERMITTENT ACTIVATION. AT APPROXIMATELY 8:55 PM THE RELIEF VALVE SEAT MATERIAL PARTIALLY FAILED DUE TO THE INTERMITTENT ACTIVITY, ALLOWING THE VALVE TO LEAK GAS UNTIL 10:12 PM. DURING THIS EVENT FIELD PERSONNEL WERE IN CONTACT WITH THE CONTROL CENTER AND BOTH WERE TRYING TO DETERMINE IF THE RELIEF VALVE WAS TRULY ACTIVATING DUE TO AN OVERPRESSURE EVENT AND WERE TRYING TO DETERMINE HOW TO ELIMINATE OR DIVERT THE PRESSURE SOURCE. ONCE THEY DETERMINED WE DID NOT HAVE AN OVERPRESSURE EVENT LOCAL PERSONNEL OPENED A BYPASS VALVE AT 10:00 PM BETWEEN PLANT-B SUCTION AND DISCHARGE PIPING. THIS ACTION DIVERTED THE INCOMING FLOW OF GAS. ONCE THIS WAS ACCOMPLISHED FIELD PERSONNEL THEN ISOLATED THE RELIEF VALVE BY CLOSING ITS ISOLATION VALVE AT APPROXIMATELY 10:12 PM. THE POST INCIDENT INVESTIGATION DETERMINED THAT THE RELIEF VALVE SEAT WAS WEATHERED AND PARTIALLY TORN. THE RELIEF VALVE'S SEAT MATERIAL WAS REPLACED AND TESTED BEFORE B-PLANT WAS PUT BACK IN SERVICE.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20190103 | 37372 | 2019-08-30 10:24 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2019-08-01 01:23 | 2019 | CENTRAL | YES | 37.5445 | -84.8078 | 1253844 | 2019-08-01 03:14 | 1254075 | NATURAL GAS |  | 101485 | 25918 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 6 | 6 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-08-01 02:19 | 2020-03-25 12:00 |  | NO |  |  | YES | 2019-08-01 01:25 | ALLOWED TO BURN OUT |  | 101485 | YES | VALVE CLOSURE |  | 2019-08-01 01:39 | VALVE CLOSURE |  | 2019-08-01 02:19 | 75 | 2019-08-01 01:25 | 2019-08-01 01:29 | ONSHORE | KY | 40484 | STANFORD | LINCOLN | MILEPOST | MP 423.4 | LINE 15 | DANV - TOMP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 43 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.375 | 52000 | API-5L | FLASH WELDED |  | A. O. SMITH | COAL TAR |  | YES | [26 empty] | 1958 | 1957 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 33.2 | 94 |  | CLASS 2 LOCATION | NO |  | 633 |  | YES | YES | YES | SOME PERSONS HAVE COMPLAINED OF RESPIRATORY DISTRESS AND EMOTIONAL DISTRESS. |  |  |  | 4200000 | 4459001.2440021342 | 58056 | 61636.137195663786456 | 227326 | 359187.0131233595800524934383202099737533 | 9700000 | 10298169.5397192147 | 1800000 | 1911000.5331437718 | 3500000 | 3715834.3700017785 | ENVIRONMENTAL MITIGATION -INCIDENT INVESTIGATION -MISCELLANEOUS COSTS | 2.24 | 19485382 | 9255513.3054204761518094068241469816273 | 20804828.83718592256650849343832020997375 | 5 | 0 | 19 | 0 | NO |  |  |  | 925 | 452751 | 936 | 192.619(A)(1) |  | 2014-10-17 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 100742 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 7 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | HYDROGEN-INDUCED CRACKING AT THE OUTER SURFACE | [6 empty] | YES | [8 empty] | 1417 | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | HARD SPOTS | [23 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2010 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | IMU | 2018 | FREE SWIMMING |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | [5 empty] | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 17136275008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: ORIGINAL NRC # 1253844 48 HOUR REPORT NRC # 1254075 AT APPROXIMATELY 1:23 A.M. EDT ON AUGUST 1, 2019, TETLP'S 30-INCH DIAMETER LINE 15 TRANSPORTING NATURAL GAS FROM DANVILLE COMPRESSOR STATION TO TOMPKINSVILLE COMPRESSOR STATION IN KENTUCKY FAILED AT MP 423.4. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. TETLP GAS CONTROL RECEIVED A RATE OF CHANGE ALARM ON LINE 15 ON THE SOUTH SIDE OF DANVILLE COMPRESSOR STATION AT APPROXIMATELY 1:25 AM EDT. DURING THE ENSUING MINUTES, TETLP BEGAN RECEIVING REPORTS FROM THE PUBLIC AND A TETLP OPERATOR OF A FIRE SOUTH OF THE DANVILLE COMPRESSOR STATION. TETLP PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE MAINLINE BLOCK VALVES, MLV 15-382 AT MP 408.48 AND MLV 15-393 AT THE DANVILLE COMPRESSOR STATION, THUS ISOLATING THE FAILED SEGMENT. FIRST RESPONDERS EVACUATED APPROXIMATELY 75 MEMBERS OF THE PUBLIC. THE INCIDENT RESULTED IN 1 FATALITY AND 6 KNOWN INJURIES. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB. THE INCIDENT CAUSE IS BEING REPORTED AS OTHER INCIDENT CAUSE UNTIL THE NTSB RELEASES INFORMATION ABOUT THE INCIDENT CAUSE. THE APPARENT CAUSE WILL BE UPDATED WHEN IT BECOMES AVAILABLE FROM THE NTSB. ALSO NOTE THE PIPE INVOLVED IN THE INCIDENT WAS MANUFACTURED IN 1957 AND INSTALLED IN 1958, AS REFLECTED IN PART C, ITEM 3G OF THIS REPORT. THE PHMSA CORRECTIVE ACTION ORDER INCORRECTLY STATED THE PIPE WAS INSTALLED IN 1942. SUPPLEMENTAL REPORT - 7/21/2020 UPDATED PART A.7 ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY TO 101,485 MCF UPDATED PART A.8 ESTIMATED VOLUME OF INTENTIONAL AND CONTROLLED RELEASE/BLOWDOWN TO 25,918 MCF UPDATED ADDITIONAL PARTS AS A RESULT OF CHANGES TO THE PHMSA PORTAL SUPPLEMENTAL FINAL REPORT -11/20/2022 UPDATED PART A 16.B DATE AND TIME THE LINE RESTARTED UPDATED PART G 5. POST-CONSTRUCTION PRESSURE TEST VALUE. THE NTSB DETERMINED THE PROBABLE CAUSE OF THE AUGUST 1, 2019, ENBRIDGE INC. PIPELINE RUPTURE AND RESULTING FIRE WAS THE COMBINATION OF A PRE-EXISTING HARD SPOT (A MANUFACTURING DEFECT), DEGRADED COATING, AND INEFFECTIVE CATHODIC PROTECTION APPLIED FOLLOWING A 2014 GAS FLOW REVERSAL PROJECT, WHICH RESULTED IN HYDROGEN INDUCED CRACKING AT THE OUTER SURFACE OF LINE 15 AND THE SUBSEQUENT FAILURE OF THE PIPELINE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190104 | 32722 | 2019-08-30 11:56 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-08-03 16:25 | 2019 |  |  | 34.5372 | -106.679 | 1254143 | 2019-08-03 18:02 |  | NATURAL GAS |  | 9268 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-03 16:10 | 2019-08-03 19:16 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-08-03 17:10 | 2019-08-03 17:10 | ONSHORE | NM | 87002 | BODEGA | VALENCIA | SURVEY STATION NO. | COMPRESSOR ST | BELEN COMPRESSOR STATION | WEST FLOW VENT VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1956 |  | CARBON STEEL |  | OTHER | [8 empty] | EQUIPMENT MALFUNCTION: SUCTION VALVE'S ACTUATOR PILOT MALFUNCTIONED. | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 21099 | 33337.5275590551181102362204724409448819 | 50 | 53.08334814288255 | 150 | 159.25004442864765 | 0 | 0 |  |  | 21299 | 21967.9646991655809653543307086614173228 | 33549.8609516266483102362204724409448819 | [8 empty] | 689 |  | 836 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | NO | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE INCIDENT WAS CAUSED DUE TO EQUIPMENT FAILURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | DEBRIS FOUND IN THE PILOT VALVE OF THE ACTUATOR VALVE CAUSED MALFUNCTION | [161 empty] | KRITI BHAYANI | PIPELINE ENGINEER - CODES AND STANDARDS | kriti_bhayani@kindermorgan.com | 7134206633 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON 8/3/2019, BELEN COMPRESSOR STATION, VALENCIA COUNTY, NEW MEXICO EXPERIENCED A FIRE EYE DETECTION EVENT WHICH RESULTED IN AN ESD AT 4:10PM (MST). THE MAINLINE 1300 WEST FLOW SUCTION VALVE'S ACTUATOR PILOT MALFUNCTIONED RESULTING IN THE SUCTION VALVE NOT CLOSING UPON INITIATION OF THE ESD. THIS MALFUNCTION KEPT THE STATION PIPING FROM BEING ISOLATED WHICH RESULTED IN A CONTINUOUS RELEASE OF GAS THROUGH 6" ESD VENT VALVE. UPON RECEIPT OF THE ORIGINAL FIRE DETECTION SYSTEM ALARM GAS CONTROL DISPATCHED AN EPNG TECHNICIAN TO THE COMPRESSOR STATION AND UPON ARRIVAL AT 5:10 PM THE TECHNICIAN DISCOVERED AND CONFIRMED THE ESD VENT VALVE WAS VENTING GAS. THE EMPLOYEE PROCEEDED TO MANUALLY CLOSE THE SUCTION VALVE AND COMPLETED THE TASK BY 5:14 PM. HE IMMEDIATELY NOTIFIED HIS SUPERVISOR AT 5:15 PM. AN ERL CALL WAS INITIATED AT WHICH TIME WE CONFIRMED DISCOVERY AND AN NRC REPORT WAS MADE AT 6:02 PM. THE NATURAL GAS LOSS WAS ESTIMATED TO BE 9,268 MCF. THE ACTUATOR PILOT VALVE WAS REPAIRED AND TESTED THEN PLACED BACK IN SERVICE. THE ORIGINAL FIRE DETECTION EVENT WAS DETERMINED TO HAVE BEEN A FALSE EVENT INITIATED BY LIGHTING IN CLOSE PROXIMITY TO THE STATION AS THERE WERE LIGHTING STORMS IN THE AREA AND THERE WAS NO EVIDENCE OF FIRE AT THE STATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190105 | 32818 | 2019-09-08 15:12 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2019-08-12 15:33 | 2019 |  |  | 40.9135 | -90.9504 | 1254968 | 2019-08-12 20:25 |  | NATURAL GAS |  | 8125 | 435 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-12 22:00 | 2019-08-14 09:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 1 | 2019-08-12 15:49 | 2019-08-12 16:00 | ONSHORE | IL | 61469 | OQUAWKA | HENDERSON | SURVEY STATION NO. | 1852+19 | CARTHAGE LINE - STATION 323 TO STA. 950 | N/A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 |  | 0.203 | 35000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | AMERICAN STEEL PIPE (ACIPCO) | COAL TAR | [28 empty] | 1966 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 6 | [7 empty] | CLASS 2 LOCATION | NO |  | 263 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 1464 | 1554.280433623601064 | 27349 | 43212.8556430446194225721784776902887139 | 389521 | 413541.577039275075171 | 2300 | 2441.8340145725973 | 28800 | 30576.0085303003488 | FOOD AND LODGING. |  | 449434 | 226044.5521394083479155249343832020997375 | 491326.5556608162417575721784776902887139 | [8 empty] | 375 |  | 600 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 45900 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY THIRD PARTY EXCAVATION DAMAGE. THE STATION FEEDING THE SYSTEM FROM ABOUT 60 MILES TO THE NORTH IS MONITORED BY GAS CONTROL BUT THEY DO NOT HAVE REMOTE CONTROL CAPABILITIES FOR THE STATION. THE CONTROLLER DID OBSERVE A LOW-LOW ALARM AND NOTIFIED THE OPERATING DEPARTMENT, WHO WAS ALREADY AWARE OF THE EXCAVATION DAMAGE AND TOOK OVER MANUAL CONTROL OF VALVES TO ISOLATE THE SYSTEM. | [12 empty] | YES | 2 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [9 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 2170416 | J.U.L.I.E. | UTILITY OWNER | NO | NO | YES | 36 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [264 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 6303882316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6303882316 | lquezad@southernco.com | SUPPLEMENTAL REPORT WAS CREATED AND FILED AT PHMSA STAFF REQUEST. CHANGED LOCAL TIME OF INCIDENT FROM 15:49 TO 15:33. ++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++++ THIRD PARTY EXCAVATOR WAS PERFORMING INSTALLATION OF TELECOMMUNICATIONS FACILITIES VIA TRENCHING WHEN THEY STRUCK AN UNMARKED 10" NATURAL GAS TRANSMISSION LINE THAT IS OPERATED AS PART OF A DISTRIBUTION SYSTEM. THE TRANSMISSION LINE WAS PURGED INTO SERVICE ON 8/14/19 AT 09:15. THE TRANSMISSION LINE FEEDS A 60-PSIG DISTRIBUTION SYSTEM WITH 788 MOSTLY RESIDENTIAL CUSTOMERS THAT WERE INTERRUPTED. THE 60-PSIG SYSTEM WAS ENERGIZED IN MULTIPLE PHASES, WITH THE MAINS IN THE LAST PHASE ENERGIZED AT 17:00 ON 8/15/19. THE COST OF DAMAGE AND REPAIRS INCLUDES THE REACTIVATION OF THE 60-PSIG DISTRIBUTION SYSTEM AND TURN-ON/RELIGHTS FOR THE CUSTOMERS INTERRUPTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190106 | 34095 | 2019-09-18 16:41 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-08-21 17:50 | 2019 | MOUNTAIN | YES | 32.7896 | -104.2383 | 1255973 | 2019-08-21 18:55 | 1255979, 1256183 | NATURAL GAS |  | 30663 | 66.5 | 70 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-08-21 19:16 | 2020-02-17 08:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-08-21 19:17 | NO | [5 empty] | VALVE CLOSURE |  | 2019-08-21 19:16 | VALVE CLOSURE |  | 2019-08-21 17:41 | 0 | 2019-08-21 19:35 | 2019-08-21 19:35 | ONSHORE | NM | 88210 | Not Within a Municipality | EDDY | MILEPOST | MP 37 | INDIAN BASIN | LAUNCHER SITE TO CS 167 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.235 | 60000 | API 5L GRADE X60 | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET AND TUBE | ASPHALT |  | YES | [26 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 687.6 | 60 |  | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO | [5 empty] | 25279 | 26837.879154078559629 | 133 | 141.201706060067583 | 61203 | 96703.9527559055118110236220472440944882 | 166800 | 177086.0494046561868 | 608 | 645.493513417451808 | 36493 | 38743.412475564257943 | REPL. PIPE XPORT, MET. RPT, CONTAINMENT SOAKERS (RAIN-PREV. MEAS), M. PHONE CHGS | 1.996 | 290516 | 170854.5258105953631635354330708661417323 | 340157.9890096820355740236220472440944882 | 0 | 0 | 0 | 0 | NO |  |  |  | 879 | 6000 | 1000 | 192.619(A)(1) |  | 1965-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING UNDER MAOP AND CONTROLLERS WERE NOT MAKING ANY CHANGES TO PIPELINE CONDITIONS. NO CHANGES WERE MADE TO EITHER SETPOINT OR HORSEPOWER. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | LOCALIZED PITTING AND GENERAL CORROSION |  |  |  |  | YES | YES | ELECTROCHEMICAL |  |  |  | YES |  |  | YES | YES | 1966 |  | YES | YES | YES |  |  | 2019 | 2016 |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2002 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | ENGINEERING DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON AUGUST 21, 2019 THE NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) 20-INCH INDIAN BASIN PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE AND LIQUID SPRAY (A MIXTURE OF CONDENSATE AND USED OIL), BUT NO FIRE. AUGUST 21, 2019: 17:41 - RIVERSIDE FIRE DEPARTMENT (NM) DISPATCHED 17:51 - A MEMBER OF THE PUBLIC WORKING IN THE LOCO HILLS NEW MEXICO AREA CONTACTED NGPL GAS CONTROL AND REPORTED AN EVENT IN THE AREA OF THE PIPELINE. 17:55 - RIVERSIDE FIRE DEPARTMENT (NM) ARRIVES ON SCENE. ON ARRIVAL, UNITS STAGED UPWIND AND SECURED ALL ROADS GOING TOWARDS THE PIPELINE. 17:57 TO 18:04 - CALLS MADE TO DEPLOY NGPL PERSONNEL TO THE REPORTED EVENT LOCATION (NGPL TECHNICIAN 3) AND TO CLOSE THE UPSTREAM AND DOWNSTREAM VALVES (NGPL TECHNICIANS 1 AND 2). 18:32 - INTERNAL EMERGENCY RESPONSE LINE (ERL+) CALL NOTIFICATIONS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. DURING THE CALL, IT WAS COMMUNICATED THAT THE LOCAL FIRE DEPARTMENT ON-SITE HAD CLOSED HILLTOP ROAD AND HIGHWAY 82. 18:51 - CALL TO NRC INITIATED (#1255973) 19:15 - NGPL TECHNICIAN 1 ARRIVES AT MLV IB-3, AUTOMATIC VALVE FOUND FULLY OPEN. 19:16 - NGPL TECHNICIAN 1 CLOSES MLV IB-3 AND IN ROUTE TO MLV IB-4. 19:20 - NGPL TECHNICIAN 2 ARRIVES AT MLV IB-2 AND VERIFIES THAT THE VALVE IS CLOSED AND IN ROUTE TO MLV IB-1. MLV IB-2 TO MLV IB-3 ISOLATED. 19:29 - NGPL TECHNICIAN 3 ARRIVES AT THE GENERAL INCIDENT LOCATION. 19:35 - NGPL TECHNICIAN 3 ON THE FAILURE SITE, VERIFIES FAILURE, REPORTED NO GAS BLOWING. 19:45 - NGPL TECHNICIAN 1 VERIFIES MLV IB-4 CLOSED AND STANDING BY AT SITE. 20:05 - NGPL TECHNICIAN 2 ARRIVES AT MLV IB-1 AND CLOSES THE VALVE. 20:20 - RIVERSIDE FIRE DEPARTMENT (NM) LEAVES THE SCENE. AUGUST 29, 2019: 12:00 - PIPE REPLACED AND COVERED. METALLURGICAL REPORT COMPLETED NOVEMBER 13, 2019. THE RESULTS OF THE METALLURGICAL ANALYSIS INDICATE THAT THE FAILURE OCCURRED AT AN AREA OF WALL THINNING IN THE LONGITUDINAL SEAM WELD DUE TO EXTERNAL CORROSION. THE WALL THINNING LED TO A BRITTLE FRACTURE INDUCED BY THE OPERATING PRESSURE. THE BRITTLE RUPTURE BEHAVIOR OF THE LONGITUDINAL SEAM WAS DUE IN PART TO THE LOW TOUGHNESS AND ALSO THE STRAIN RATE OF THE RUPTURE EVENT. MULTIPLE CORROSION MECHANISMS WERE OBSERVED AT THE RUPTURE INITIATION SITE, INCLUDING LOCALIZED CORROSION IN THE FORM OF SELECTIVE SEAM WELD CORROSION (SSWC), PITTING CORROSION AND GENERAL CORROSION. UPDATE NRC REPORT 1255979 AND 48-HOUR NRC REPORT 1256183. NOTE THAT FORM PHMSA F 7100.2 (REV 09-2019) PART J, Q1 WHEN A POSITIVE RESPONSE IS ENTERED FOR AN INTERNAL INSPECTION TOOL THEN BOTH A MOST RECENT AND A PREVIOUS ENTRY IS REQUIRED. NGPL RAN A GEOMETRY/DEFORMATION TOOL IN 2017 BUT DID NOT HAVE A PRIOR TOOL RUN OF THIS TYPE. IN ORDER TO SUBMIT THIS FORM THE 2017 RUN HAS BEEN ENTERED TWICE IN THAT SECTION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190107 | 33229 | 2019-09-19 18:31 | SUPPLEMENTAL FINAL | 32005 | ENLINK LBU-GAS&LIQUIDS | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2019-08-20 20:25 | 2019 |  |  | 29.7706 | -91.717 | 1255844 | 2019-08-20 20:53 |  | NATURAL GAS |  | 4688 | 3060 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-08-20 | 2019-10-10 12:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-08-20 | 2019-08-20 19:30 | ONSHORE | LA | 70538 | Not Within a Municipality | ST. MARY | MILEPOST | WEST OF BV-2 | P1566 - WEEKS ISLAND TO ST. JAMES 36" | P1566 - WEEKS ISLAND TO ST. JAMES 36" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER WATER | 77 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 36 |  | 0.438 | 60000 | 5LX60 | DSAW |  | ARMCO | OTHER | THIN FILM EPOXY (TFE) | [27 empty] | 1979 | 1979 | CARBON STEEL |  | LEAK |  |  | OTHER | INTERNAL CORROSION | [5 empty] | CLASS 1 LOCATION | NO |  | 786 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 7650 | 8121.75226586103015 | 11720 | 18518.2152230971128608923884514435695538 | 360000 | 382200.10662875436 | 0 | 0 | 0 | 0 |  |  | 379370 | 184345.711259501912974671916010498687664 | 408840.0741177125030108923884514435695538 | [8 empty] | 811 |  | 1001 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 38016 | NO | [5 empty] | YES | SEGMENT IS CAPPED ON ONE END. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE LEAK WAS INTERNAL CORROSION. THE LEAK WAS NOT LARGE ENOUGH FOR PIPELINE CONTROL TO DETECT A LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | GENERAL CORROSION | [14 empty] | NO |  |  |  | NO | [9 empty] | GENERAL CORROSION |  |  |  | YES |  |  |  | YES | YES |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CORDELL THERIOT | SR. DOT SPECIALIST | cordell.theriot@enlink.com | 3373226682 |  |  |  |  | CORDELL THERIOT | SR. DOT SPECIALIST | 3373226682 | cordell.theriot@enlink.com | ON 8/20/2019 ENLINK WAS NOTIFIED BY A LOCAL FISHERMAN OF A POSSIBLE LEAK. OPERATIONS IMMEDIATELY BEGAN TO DETERMINE IF THE LEAK WAS ON OUR ENLINK PIPELINE. AFTER CONFIRMING THE LEAK WAS ON AN ENLINK PIPELINE, OPERATIONS SHUT DOWN THE PIPELINE AND ALLOWED THE LINE TO CONTINUE LEAKING UNTIL THE PRESSURE WAS AT A SAFE ENOUGH LEVEL TO MAKE THE NECESSARY REPAIRS. THE LEAK WAS IN AN AREA COMPLETELY UNDERWATER. REPAIR WAS MADE BY CUTTING OUT A SECTION OF PIPE AND REPLACING WITH NEW PIPE. THE CUTOUT WAS SENT TO A METALLURGICAL LAB AND THE CONCLUSIONS ARE THAT BACTERIA WAS FOUND IN THE CORROSION DEPOSITS BUT WAS NOT THE MAIN CAUSE OF THE CORROSION, RATHER TUBERCLE FORMATIONS WERE THE MAIN CAUSE. THE 48-HOUR NOTIFICATION TO THE NRC WAS MADE ON 8/22/2019 @ 23:02, INCIDENT # 1256107.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190108 | 34607 | 2019-09-20 08:18 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-08-21 02:25 | 2019 | EASTERN | YES | 41.0258 | -79.6328 | 1255871 | 2019-08-21 09:05 | 1256125 | NATURAL GAS |  | 29311 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-08-21 07:58 | VALVE CLOSURE |  | 2019-08-21 07:58 | 0 | 2019-08-21 02:09 | 2019-08-21 07:31 | ONSHORE | PA | 16028 | Not Within a Municipality | ARMSTRONG | MILEPOST | VS-5016 | PIPELINE 134 | VS-5016 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL PIPE COUPLER | 1929 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | ONE JOINT OF PIPE BECAME DISCONNECTED FROM THE PIPELINE AT MECHANICAL PIPE COUPLER. | CLASS 1 LOCATION | NO |  | 109 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 54812 | 86605.8372703412073490813648293963254593 | 314517 | 333912.308157099819567 | 3000 | 3185.000888572953 | 0 | 0 |  | 1.87 | 372329 | 205540.5113998544736799553805774278215223 | 423703.1463160139799160813648293963254593 | 0 | 0 | 0 | 0 | NO |  |  |  | 229 | 7000 | 250 | 192.619(A)(3) |  | 1929-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 10824 | NO |  | YES |  | YES |  |  |  | YES |  | YES |  |  | YES | MECHANICALLY COUPLED PIPE | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | MECHANICAL COUPLING -DRESSER STYLE |  |  |  | YES | [12 empty] | YES | CONSTRUCTION ACTIVITIES ON THE PIPELINE | [161 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 304-357-3596 | 304-357-3522 |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | 304-357-2245 | paul_shaffer@tcenergy.com | PIPELINE 134 IS A 10-INCH BARE CARBON-STEEL PIPELINE OWNED AND OPERATED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616), A TC ENERGY ENTITY. THIS SEGMENT OF LINE 134 IS MECHANICALLY COUPLED, PLACED INTO SERVICE IN 1929 WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 250 PSIG. ON AUGUST 21, 2019 LINE 134 WAS SUBJECT TO A MECHANICAL COUPLING FAILURE OCCURRING IN ARMSTRONG COUNTY, PENNSYLVANIA. THE MORNING OF AUGUST 21ST, GAS CONTROL RECEIVED AN ALARM FROM THE IOWA COMPRESSOR STATION INDICATING THAT UNIT 1 HAD HIGH DISCHARGE PRESSURE. STATION PERSONNEL WERE DISPATCHED AND RESPONDED TO THIS CALL. LATER THAT HOUR GAS CONTROL RECEIVED A SECOND ALARM FROM THE IOWA COMPRESSOR STATION INDICATING THAT UNIT 2 HAD LOW SUCTION PRESSURE. THIS CALL WAS ALSO RESPONDED TO AND EVALUATED. PIPELINE PRESSURE CONTINUED TO DROP. OPERATIONS MANAGERS WERE NOTIFIED, AND ADDITIONAL SUPPORTING COMPANY PERSONNEL WERE DISPATCHED. THE PIPELINE LEAK WAS LOCATED AND ISOLATED BY 7:58 AM. THE PIPELINE IN THIS AREA IS PART OF A MODERNIZATION PROJECT. AT THE TIME OF THE INCIDENT, THE EFFECTED SEGMENT OF LINE 134 IN THIS PROJECT HAD BEEN EXPOSED, STOPPLES INSTALLED, PIPELINE SECTIONS REMOVED, AND END CAPS WERE INSTALLED. THE CONSTRUCTION ACTIVITIES DURING THIS CONSTRUCTION WORK APPEAR TO HAVE CONTRIBUTED TO THE DISCONNECTION OF THIS SECTION OF PIPE. INITIAL NRC REPORT NUMBER IS 1255871 REPORTED AUGUST 21, 2019 AND THE 48-HOUR NRC REPORT NUMBER IS 1256125 REPORTED ON AUGUST 23, 2019. THE INTERNAL INVESTIGATION INTO THIS INCIDENT HAS DETERMINED THE FOLLOWING CAUSAL FACTORS: -GUIDELINES FOR THE USE OF MECHANICAL COUPLINGS RESIDED WITHIN CPG INTEGRATED DOCUMENTS LISTING BUT NOT WITHIN THE TC ENERGY CONTROLLED DOCUMENT LIBRARY; THE SINGLE REFERENCE SOURCE FOR US NATURAL GAS PIPELINES PROJECTS. -DURING PROJECT PLANNING THE RISKS OF EXCAVATION ON 1929 VINTAGE PIPELINE SYSTEM WITH PROBABILITY FOR MECHANICAL COUPLINGS WAS NOT DOCUMENTED AS A POTENTIAL HAZARD FOR EXCAVATION/CONSTRUCTION ACTIVITIES. -WHEN A MECHANICAL COUPLING WAS EXPOSED DURING EXCAVATION, THE RISK WAS NOT ADEQUATELY ESCALATED BY THE CONTRACTOR TO THE PROJECT MANAGER. ADDITIONALLY, THE DECISION TO MOVE THE STOPPLE INSTALLATION POINT DUE TO MECHANICAL COUPLING DISCOVERY AT THAT POINT DID NOT GENERATE DISCUSSION ON THE RISK OF THE EXPOSED MECHANICAL COUPLING OR THE POTENTIAL OF ADDITIONAL MECHANICAL COUPLINGS NEAR THE EXCAVATION SITE. CORRECTIVE ACTIONS COMPLETED TO DATE INCLUDE: -ESTABLISHED US NATURAL GAS PROJECTS INITIATIVE TO IDENTIFY GAPS IN EXISTING ENGINEERING DESIGN STANDARDS -REQUIRE ALL PROJECTS TO DEVELOP A PRE-JOB SAFETY MANAGEMENT PLAN -THE DISTRIBUTION OF THE "MECHANICAL PIPELINE REPAIR TAPPING AND JOINING" PROCEDURE TO US NATURAL GAS PROJECT, US CONSTRUCTION SERVICES STAFF, US GAS OPERATIONS FIELD OPERATIONS MANAGERS AND TEAM LEADERS -PUBLICATION OF THE "MECHANICAL PIPELINE REPAIR TAPPING AND JOINING" PROCEDURE TO THE CONTROLLED DOCUMENT LIBRARY -ESTABLISHED REQUIRED TRAINING FOR US NATURAL GAS PROJECT CONSTRUCTION MANAGERS AND US GAS OPERATIONS FIELD OPERATIONS STAFF ON "MECHANICAL PIPELINE REPAIR TAPPING AND JOINING" PROCEDURES. -DISTRIBUTED LESSONS LEARNED SAFETY SHARE TO US NATURAL GAS PIPELINES PROJECTS, CONSTRUCTION SERVICES AND US GAS OPERATIONS FIELD OPERATIONS. -ADDITIONAL TRAINING PLANNED IN 2021
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190109 | 32765 | 2019-09-27 17:16 | ORIGINAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2019-09-04 04:16 | 2019 |  |  | 47.6374 | -117.6689 | 1257199 | 2019-09-04 09:31 |  | NATURAL GAS |  | 4623 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION CONTINUED TO OPERATE SAFELY DURING THE CONTROLLED REALEASE. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-04 04:04 | 2019-09-04 04:55 | ONSHORE | WA | 99022 | AIRWAY HEIGHTS | SPOKANE | MILEPOST | MP 146.1 | 2435 SPOKANE LINE | 2435 SPOKANE LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2019 |  | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | REGULATOR PILOR FILTERS, REGULATOR PILOT | OTHER | [8 empty] | REGULATOR VALVE EQUIPMENT FAILURE | CLASS 1 LOCATION | NO |  | 138 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 9492 | 14997.8582677165354330708661417322834646 | 300 | 318.5000888572953 | 400 | 424.6667851430604 | 0 | 0 |  |  | 10192 | 10168.6441636149664496062992125984251969 | 15741.0251417168911330708661417322834646 | [8 empty] | 372 |  | 625 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE WILLIAMS CONTROLLER PROMPTLY NOTIFIED AND DISPATCHED THE WILLIAMS ON-CALL TECHNICIAN TO INVESTIGATE THE ISSUE AT THE FACILITY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [19 empty] | YES | [168 empty] | JASON LAMBERT | MGR. PIPELINE SAFETY - WEST | jason.lambert@williams.com | 801-584-6657 |  |  |  |  | JASON LAMBERT | MGR. PIPELINE SAFETY - WEST | 801-584-6657 | jason.lambert@williams.com | ON 9/4/19, WILLIAMS NORTHWEST PIPELINE (NWP) CUSTOMER (AVISTA) GAS CONTROL REPORTED HIGH PRESSURE ALARM TO THE NWP CONTROL ROOM AT 04:04 PT. THE NWP PIPELINE CONTROLLER CONTACTED THE ON-CALL TECHNICIAN AND DISPATCHED HIM TO THE SITE AT 04:14 PT TO INVESTIGATE. THE TECHNICIAN ARRIVED ONSITE AT 04:55 PT TO FIND THE NWP RELIEF VALVE VENTING. THE TECHNICIAN MOVED FLOW FROM PRIMARY RUN TO SECONDARY RUN. THIS LOWERED PRESSURE TO 340 PSIG AND THE RELIEF VALVE RE-SEATED AND STOPPED BLOWING. THE TECHNICIAN ISOLATED, LOCKED OUT AND DEPRESSURIZED THE PRIMARY METER RUN AT 05:10 PT. THE TECHNICIAN DISASSEMBLED THE MOONEY REGULATOR PILOT AND BOOT TO INVESTIGATE. THE TECHNICIAN FOUND A LARGE AMOUNT OF ICE BUILT UP ON PILOT STEM. THE RESULTS OF THE INVESTIGATION WERE: THE REGULATOR PILOT FAILURED DUE TO ICE IN PILOT, CAUSING RISE IN PRESSURE AND THE RELIEF VALVE TO OPERATE. THE ICE IN THE PILOT WAS DETERMINED TO BE CASUED BY DITHIAZINE BUILD UP IN PILOT FILTER AND FILTERS FAILURE TO CONTAIN THE HYDRATES CREATED BY THE THE REACTION OF THE FILTER MEDIA REMOVING THE DITHIAZINE. PROPER REPAIRS WERE MADE ON 9/4/19 INCLUDING: 1) A NEW SULFUR FILTER WAS INSTALLED; AND 2) AN ADDITIONAL DESICANT FILTER IN SERIES AFTER THE SULFUR FILTER TO CAPTURE HYDRATES. NRC REPORTING: AT 08:45, WILLIAMS ENGINEERING PERSONNEL DISCOVERED THE ESTIMATED VOLUME OF GAS RELEASED EXCEEDED THE 3,000 MCF REPORTING THRESHOLD. AS A RESULT, THE WILLIAMS SECURITY OPERATION CENTER NOTIFIED THE NRC AT 09:31 (INCIDENT REPORT # 1257199). A 48-HOUR UPDATE REPORT (INCIDENT REPORT # 1257382) WAS MADE TO THE NRC ON 9/5/19 AT 16:06. AT THE TIME OF THE INCIDENT, THE NWP SCADA MONITORING WAS TEMPORARILY DISABLED DUE TO SCHEDULED MAINTENANCE. PREARRANGED PLANS WERE CONFIRMED BEFORE BEING DISABLED THAT AVISTA WOULD MONITOR AND NOTIFY NWP CONTROL ROOM AS APPROPRIATE. AFTER SCHEDULED MAINTENANCE CONCLUDED, THE NWP SCADA RETURNED TO FULL SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190110 | 32872 | 2019-10-04 11:35 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-09-05 12:30 | 2019 |  |  | 34.3043 | -97.4476 | 1257346 | 2019-09-05 13:05 |  | NATURAL GAS |  | 11683 | 1130 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-09-05 14:30 | 2019-09-06 02:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-05 12:30 | 2019-09-05 13:00 | ONSHORE | OK | 73438 | HEALDTON | CARTER | MILEPOST | LINE Q | LINE Q | Q | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 |  | 0.203 | 42000 | CARBON STEEL | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LONE STAR STEEL COMPANY | COAL TAR | [28 empty] | 1961 | 1961 | CARBON STEEL |  | MECHANICAL PUNCTURE | 8 | 8 | [7 empty] | CLASS 1 LOCATION | NO |  | 330 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 1673 | 1776.168828860850123 | 29209 | 46151.7532808398950131233595800524934383 | 57000 | 60515.016882886107 | 8000 | 8493.335702861208 | 0 | 0 |  |  | 95882 | 61509.7164386462344733517060367454068241 | 116936.2746954480601361233595800524934383 | [8 empty] | 535 |  | 565 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 36960 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS A THIRD PARTY DAMAGE AND NOT A DIRECT RESULT OF A CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | GRADING | NO | [5 empty] | YES | 14 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JACK CROW | COMPLIANCE SPECIALIST | jcrow@oneok.com | 4053232492 |  |  |  |  | JACK CROW | COMPLIANCE SPECIALIST | 4053232492 | jcrow@oneok.com | AT APPROXIMATELY 12:30 PM ON 9/5/2019 A LANDOWNER'S EMPLOYEE OPERATING A DOZER WITHOUT A ONE CALL TICKET STRUCK A 12 INCH NATURAL GAS PIPELINE NEAR THE TOWN OF HEALDTON IN CARTER COUNTY. ONEOK WAS NOTIFIED BY A THIRD PARTY CALL TO OUR CONTROL CENTER AT APPROXIMATELY 12:15 PM WHICH MATCHED WHAT THEY WERE SEEING IN SCADA. ONEOK PIPELINE CONTROL CENTER DISPATCHED LOCAL FIELD OPERATORS TO THE LOCATION AND SET UP AN EMERGENCY BRIDGE CALL FOR THE INCIDENT. FIELD OPERATIONS PERSONNEL ARRIVE ON LOCATION AT APPROXIMATELY 13:00 HOURS AND CONFIRMED THE RELEASE WAS ON THE ONEOK PIPELINE. FIELD PERSONNEL BEGAN TO ISOLATED THE DAMAGED AREA AND WORKED TO REROUTE GAS TO MAINTAIN SERVICE TO LOCAL COMMUNITIES. AT APPROXIMATELY 14:30 HOURS THE DAMAGE SECTION OF THE ONEOK Q PIPELINE WAS ISOLATED. ONCE GAS WAS REMOVED FROM THE PIPELINE FIELD PERSONNEL REMOVED THE DAMAGED SECTION OF PIPE AND NEW PRE-TESTED PIPE WAS INSTALLED. THE PIPELINE WAS RETURNED TO NORMAL OPERATIONS AT APPROXIMATELY 02:00 ON 9/06/2019. LOCAL ONEOK OPERATIONS MANAGEMENT MET WITH THE LANDOWNER'S EMPLOYEE TO DISCUSS THE IMPORTANCE OF CALLING OKLAHOMA ONE-CALL WHENEVER CONDUCTING ANY EXCAVATIONS. ONEOK ALSO VERIFIED THE LANDOWNER IS IN THE CURRENT ONEOK PUBLIC AWARENESS DATABASE. ONEOK HAS ALSO VERIFIED THE PIPELINE IS CLEARLY IDENTIFIED WITH PIPELINE MARKER SIGNS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190111 | 32799 | 2019-10-10 16:30 | ORIGINAL FINAL | 12576 | ENABLE MISSISSIPPI RIVER TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-09-13 16:05 | 2019 |  |  | 38.2619 | -90.4097 | 1258179 | 2019-09-13 18:02 |  | NATURAL GAS |  | 0 | 1 | 3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE PIPELINE REMIANED IN SERVICE DURING CLEANUP. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-13 16:05 | 2019-09-13 15:00 | ONSHORE | MO | 63048 | HERCULANEUM | JEFFERSON | MILEPOST | NA | ML1 | ML1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 2019 |  | CARBON STEEL |  | OTHER | [8 empty] | WHILE BLOWING DOWN A PIG TRAP, A SLUG OF HYDROCARBON LIQUID ATOMIZED AND BLEW INTO THE AIR. | CLASS 3 LOCATION | NO |  | 371 |  | NO | YES | NO |  |  |  |  | 400000 | 424666.7851430604 | 5 | 5.308334814288255 | 0 | 0 | 0 | 0 | 60000 | 63700.01777145906 | 40000 | 42466.67851430604 | MISCELLANEOUS, VEHICLE, OVERHEAD |  | 500005 | 234185.743291274072595 | 530838.789763639788255 | [8 empty] | 450 |  | 595 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 546 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | UNEXPECCTED LIQUID IN TRANSMISSION LINE. | [147 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | IN PREPARATION FOR AN ILI RUN, TEMPORARY PIG TRAPS WERE INSTALLED ON ML1 AT VARIOUS LOCATIONS THROUGHOUT THE LINE. AFTER INSTALLATION OF PIG TRAPS, THE LOCAL OPERATION TEAMS BEGAN PIGGING THE LINE IN PREPARATION FOR THE ILI RUN. AFTER RECEIVING THE "DRY" PIGS IN JEFFERSON COUNTY, MISSOURI THE OPERATIONS GROUP BLEW DOWN THE JOACHIM CREEK RECEIVER BARREL. LIQUIDS WERE NOT ANTICIPATED TO BE IN THE LINE. GAS FOLLOWED BY A BROWN MIST WAS RELEASED FROM A 3" BLOWDOWN ON THE PIG TRAP. THE MIST WAS BLOWN HIGH IN THE AIR INTO TREES, A NEARBY TRIBUTARY, AND SPREAD ACROSS 2.5 ACRES INTO A HOUSING DEVELOPMENT. THE AFFECTED AREA WAS REMEDIATED, AND THE RECOVERED HYDROCARBON LIQUID WILL BE RECYCLED AS USED OIL. A CALL WAS PLACED TO THE NRC(#1258179) ON 9/13/2019 AT 18:02 AND A 48 HR. FOLLOW UP (#1258293) WAS PLACED ON 9/15/2019 AT 12:36.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190112 | 32833 | 2019-10-16 15:00 | ORIGINAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-09-19 16:24 | 2019 |  |  | 28.701 | -91.6775 | 1258724 | 2019-09-19 16:32 |  | NATURAL GAS |  | 0 | 48609 | 3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-09-19 16:27 | 2019-09-29 18:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-19 16:24 | 2019-09-23 16:30 | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | EUGENE ISLAND | 197 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 |  | 0.5 | 60000 | UNKNOWN | DSAW |  | UNKNOWN | OTHER | MASTIC AND CONCRETE | [27 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 108000 | 114660.031988626308 | 0 | 0 | 360000 | 382200.10662875436 | 0 | 0 | 0 | 0 |  |  | 468000 | 219195.663763994892 | 496860.138617380668 | [8 empty] | 850 |  | 1250 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 247653 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [7 empty] | YES | SAMPLE ANALYSIS WAS UTILIZED | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 9/19/19 RECEIVED NOTIFICATION OF A POSSIBLE LEAK. NRC TELEPHONIC NOTIFICATION MADE AT 16:32 NRC#1258724. 9/20/19 PHMSA AID NOTIFIED 07:53 9/21/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 13:38 NRC# 1258902. PHMSA AID UPDATED AT 15:10 9/23/19 PHMSA AID UPDATED AT 9:47. 9/29/19 REPAIR COMPLETED. 9/30/19 LINE WAS RETURNED TO SERVICE. PART A, QUESTION 10: THE ESTIMATED VOLUME OF UNINTENTIONAL GAS RELEASED WAS 0. THE LEAK WAS INTERMITTENT FROM A PINHOLE AND THERE WERE NO BUBBLES, ONLY SHEEN FROM THE CONDENSATE.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20190113 | 33008 | 2019-10-18 22:43 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 811 LOUISIANA ST. SUITE 1200 | HOUSTON | TX | 77002 | 2019-09-20 11:30 | 2019 |  |  | 27.9432 | -94.3886 | 1258971 | 2019-09-20 12:00 |  | NATURAL GAS |  | 5500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-09-20 12:00 | 2019-10-10 16:15 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-09-20 11:30 | 2019-10-02 23:15 | OFFSHORE | [28 empty] | 350 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | HIA | 582 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 |  | 0.5 | 60000 | 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | ITALSIDER | ASPHALT | [28 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 143 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 12000 | 18960.6299212598425196850393700787401575 | 700000 | 743166.8740003557 | 0 | 0 | 0 | 0 |  |  | 712000 | 340297.7069220530637795275590551181102362 | 762127.5039216155425196850393700787401575 | [8 empty] | 840 |  | 1440 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 77088 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK OCCURRED SUB-SEA AND NO CONTROLLER'S ACTIONS WERE RELATED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | THE CAUSE IS LIKELY INTERNAL CORROSION HOWEVER FURTHER CAUSE-ANALYSIS CANNOT BE PERFORMED DUE TO THE LOCATION OF THE PIPE. |  |  | YES | THE CAUSE IS LIKELY INTERNAL CORROSION HOWEVER FURTHER CAUSE-ANALYSIS CANNOT BE PERFORMED DUE TO THE LOCATION OF THE PIPE. |  |  |  |  | YES | STRAIGHT PIPE NOT ON A LOW POINT. | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 7137251663 |  |  |  |  | JOHN JEWETT | DOT COMPLIANCE MANAGER | 7138602605 | john.jewett@genlp.com | WHILE PERFORMING A ROUTINE VISIT TO HIA 582 MANIFOLD PLATFORM, GENESIS PERSONNEL NOTICED AN AREA OF DISTURBED WATER TO THE SOUTH OF THE FACILITY. PERSONNEL INVESTIGATED THE AREA WITH A HELICOPTER AND FOUND THAT THERE WERE GAS BUBBLES COMING TO THE SURFACE OVER GENESIS 30" GAS PIPELINE. PERSONNEL MADE NOTIFICATIONS AND ISOLATED THE PIPELINE SEGMENT. THERE WAS NO SHEEN ASSOCIATED WITH THIS EVENT. DIVE CREW ARRIVED ON THE SCENE FOR REPAIRS WITH A CLAMP. THE DIVERS DESCRIBED THE ENVIRONMENT AS HAVING POOR VISIBILITY BUT DESCRIBED RELEASE POINT AS A THIN "SPLIT." UT MEASUREMENTS TAKEN NEAR THE RELEASE SITE INDICATED LITTLE TO NO METAL LOSS ON THE PIPE EXCEPT IMMEDIATELY ADJACENT TO THE SPLIT. AFTER THE TEST, THE PIPE WAS PRESSURED UP AGAIN WITHOUT ANY LEAKAGE. PART E, QUESTION 5C - THIS SEGMENT IS ISOLATED BY CLOSING 3 UPSTREAM VALVES AND ONE DOWNSTREAM VALVE. THE DISTANCE REPORTED IN THIS QUESTION IS THE LONGEST DISTANCE BETWEEN VALVES USED. PART G: EARLY ANALYSIS APPEARS TO POTENTIALLY POINT TO SOME TYPE OF CORROSION EVENT HOWEVER, DUE TO THE DEPTH OF THE PIPE AND THE POOR VISIBILITY ON THE SEA FLOOR, THE DATA AVAILABLE MAKES IT DIFFICULT TO DETERMINE WITH HIGH CONFIDENCE WHETHER IT IS INTERNAL OR EXTERNAL AT THIS TIME. GENESIS WILL COLLABORATE WITH A THIRD PARTY SME TO AID IN THE DETERMINATION. SUPPLEMENTAL (11/18/2020) - AFTER CONSULTING WITH A THIRD PARTY CORROSION EXPERT, GENESIS BELIEVES THE LEAK WAS PROBABLY CAUSED BY INTERNAL CORROSION, HOWEVER IT IS NOT POSSIBLE TO DETERMINE WHAT TYPE OF INTERNAL CORROSION IS RESPONSIBLE WITH A HIGH DEGREE OF CONFIDENCE. PRIOR TO REPAIRING THE LEAK SITE, DIVERS CONDUCTED SEVERAL UT SCANS OF THE RELEASE AREA, BOTH CIRCUMFERENTIALLY AND UPSTREAM/DOWNSTREAM FROM THE RELEASE SPOT. THE TESTS SHOWED METAL LOSS ONLY AT THE SPOT OF THE SPLIT BUT NOWHERE ELSE THAT WAS SCANNED. FURTHER ASSESSMENT IS NOT POSSIBLE SINCE VISIBILITY ON THE SEA FLOOR IS VERY POOR AT THIS SIGHT AND ALSO, THE SEGMENT IS NOT ILI PIGGABLE DUE TO THE DIFFERING PIPE DIAMETERS OF THE CONNECTING UPSTREAM PIPELINES. SINCE AT THIS TIME IT IS DIFFICULT TO DEFINITIVELY DETERMINE WHETHER THE EVENT WAS CAUSED BY INTERNAL OR EXTERNAL CORROSION, GENESIS HAS COMPLETED SEVERAL MITIGATING TECHNIQUES TO ENHANCE THE CATHODIC PROTECTION OF THIS SEGMENT. FIRST, GENESIS HAS INSTALLED AN ADDITIONAL SACRIFICIAL ANODE ON THIS SECTION OF PIPE. SECOND, AN ADDITIONAL WATER TRAP AND CORROSION COUPON HAVE BEEN INSTALLED ON HIA 582. FINALLY, GENESIS INTENDS TO RECOMMEND TREATMENT MEASURES FOR THE UPSTREAM OPERATOR TO FURTHER PROTECT THE DOWNSTREAM SEGMENTS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190114 | 33487 | 2019-10-21 14:19 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-10-04 15:45 | 2019 | EASTERN | YES | 39.9246 | -81.6915 | 1260273 | 2019-10-04 16:37 | 1260341 | NATURAL GAS |  | 897 | 23595 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-10-04 17:15 | 2019-10-08 05:40 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-10-04 17:15 | VALVE CLOSURE |  | 2019-10-04 17:15 | 0 | 2019-10-04 15:57 | 2019-10-04 15:57 | ONSHORE | OH | 43732 | Not Within a Municipality | MUSKINGUM | MILEPOST | 208-4+11.53 | LINE 200-4 | 204-4 TO 209-4 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 45 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | FILLET WELD | [18 empty] | 2009 | 2008 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 698 |  | NO | NO | [5 empty] | 0 | 0 | 56628 | 60120.076772703060828 | 2153 | 3401.853018372703412073490813648293963255 | 105000 | 111475.031100053355 | 1300 | 1380.1670517149463 | 5825 | 6184.210058645817075 | LAB ANALYSIS; | 2.4 | 170906 | 81270.4159531262132584435695538057742782 | 182561.3380014898826150734908136482939633 | 0 | 0 | 0 | 0 | NO |  |  |  | 730 | 746000 | 790 | 192.619(A)(1) |  | 1968-11-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 68957 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IMMEDIATE EXCAVATION AT SITE FOUND CRACK IN THE NECK OF THE HOT TAP FITTING; NOT CONTROL ROOM DETECTABLE LEAK; | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | MECHANICAL VIBRATION |  | YES | [14 empty] | YES | [8 empty] | 2220 | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | NO | [13 empty] | YES | 2009 | [6 empty] | YES | [55 empty] | WM. MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 205-325-3863 | 205-325-3592 | CARL BAYER | carl_bayer@kindermorgan.com | 740-638-2101 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | NRC #1260273; NRC #1260341 (48-HOUR); 36-INCH TENNESSEE GAS PIPELINE COMPANY, L.L.C. (TGP); LINE 200-4 WITH HOT TAP RECEIVING NATURAL GAS FROM TALLGRASS BIG MUSKINGUM METER STATION: AT 15:45-HOURS, THE LANDOWNER OBSERVED DIRT BLOWING AT THE HOT TAP RISER AND NOTIFIED A GRANDSON WHO NOTIFIED HIS BROTHER, A TGP COMPANY EMPLOYEE. AT 15:57-HOURS, EMPLOYEE ARRIVED ON SITE AND CONFIRMED A LEAK AT THE HOT TAP RISER. AT 16:15-HOURS, ALTHOUGH THE LANDOWNER'S HOME WAS OUTSIDE OF THE PIR (MORE THAN 1,900 FEET FROM THE LEAK SITE) THE LANDOWNER'S GRANDSON CHOSE TO RELOCATE THE LANDOWNER TO A RELATIVE'S HOME. THE DOWNSTREAM AND THE UPSTREAM PIPELINE MAIN LINE VALVES WERE CLOSED AT 17:15-HOURS. FOLLOWING NOTIFICATION TO APPLICABLE EMERGENCY RESPONDERS, AT 19:22-HOURS, BLOW-DOWN OF THE PIPELINE VALVE SECTION BEGAN. ON OCTOBER 5, 2019, AT 00:05-HOUR, BLOW-DOWN OF THE VALVE SECTION WAS COMPLETE. EXCAVATION AT THE HOT TAP SITE FOUND THE NECK OF THE HOT TAP FITTING CONTAINED A CRACK. THE HOT TAP WAS CUT OUT OF THE PIPELINE AND THE PIPELINE WAS REPAIRED WITH REPLACEMENT PIPE. DUE TO CHANGES IN BUSINESS NEEDS, THE HOT TAP CONNECTION WILL NOT BE REPLACED. THE HOT TAP FITTING WENT THROUGH LABORATORY ANALYSIS FOR CAUSE OF THE NECK FILLET WELD CRACK. THE JANUARY 17, 2020 METALLURGICAL REPORT CONCLUDES THE HOT TAP NECK FILLET WELD CRACK OCCURRED FROM FATIGUE. SAID REPORT FINDS FATIGUE CAUSE WAS STRESS AND / OR VIBRATION FROM PULSATION OF THE COMPONENT AND INSUFFICIENT SUPPORT OF A NEARBY BLOW OFF VALVE ASSEMBLY. NO MATERIAL DEFICIENCIES WERE FOUND WHICH WOULD HAVE CONTRIBUTED TO THE COMPONENT FAILURE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190115 | 33452 | 2019-10-25 16:04 | SUPPLEMENTAL FINAL | 1217 | BEAR CREEK STORAGE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-09-26 18:50 | 2019 | CENTRAL | YES | 32.3894 | -92.939 | 1259488 | 2019-09-26 21:01 | 1259665 | NATURAL GAS |  | 28779 | 2225 | 0.9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-09-26 20:10 | 2020-02-04 11:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-09-26 19:09 | VALVE CLOSURE |  | 2019-09-26 18:50 | 0 | 2019-09-26 19:03 | 2019-09-26 19:31 | ONSHORE | LA | 71008 | BIENVILLE | BIENVILLE | MILEPOST | WELLHEAD 12-3 | LINE #4 | LATERAL 12-3 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 | NO | 0.3 | 52000 | X52 | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1979 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | THE FAILURE OCCURRED IN AN ELBOW. THE ORIENTATION OF THE RUPTURE WAS AT THE EXTRADOS OF THE ELBOW. THE ELBOW CHANGES DIRECTION 90-DEGREES. | 9 | 4.5 |  | CLASS 1 LOCATION | NO |  | 115 |  | NO | NO | [5 empty] | 0 | 0 | 5514 | 5854.031633197087614 | 71323 | 112694.083989501312335958005249343832021 | 128048 | 135944.331259996495248 | 1688 | 1792.093833303714888 | 14396 | 15283.757597298743796 | $12,090 - ENVIRONMENTAL REMEDIATION $2,306 - METALLURGICAL EVALUATION/REPORT | 2.4783 | 220969 | 144033.0112398647454446036745406824146982 | 271568.298313297353881958005249343832021 | 0 | 0 | 0 | 0 | NO |  |  |  | 2449 | 4968.7 | 3100 | 192.619(A)(1) |  | 1981-11-13 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | AUTOMATIC | 12338 | NO | [5 empty] | YES | THE PIPE DIAMETER FOR THIS SEGMENT IS 3-INCHES AND GOES FROM THE WELL VALVE TO THE METER RUN, APPROXIMATELY 22FT. OF PIPE. | YES |  |  |  |  | YES | DIAMETER, BENDS, AND SEGMENT LENGTH | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | EROSION |  |  |  | YES |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES |  |  | 2004 | [6 empty] | YES | [53 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | ENGINEERING DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON SEPTEMBER 26, 2019 THE BEAR CREEK STORAGE COMPANY (BCSC) LINE 4 LATERAL 12-3 RUPTURED RELEASING NATURAL GAS TO ATMOSPHERE. THE LEAK WAS DETERMINED TO BE ON BCSC LINE 4 FROM AN ABOVEGROUND 3-INCH PIPELINE CONNECTING A METER STATION IN THE AREA TO STORAGE WELL 12-3 (OFTEN REFERRED TO AS A "WELL LEAD"). FOLLOWING AN INVESTIGATION, PRELIMINARY FINDINGS POINTED TO LOSS OF INTERNAL PIPE WALL THICKNESS IN THE 3-INCH PIPE CAUSED THE PIPE TO RUPTURE AND BREAK APART. SAMPLES OF THE PIPE WERE SUBMITTED FOR METALLURGICAL TESTING AND IT WAS DETERMINED THAT THE RUPTURE WAS DUE TO EROSION (AS INDICATED IN PART G1). DURING THE NATURAL GAS RELEASE BETWEEN 0.7 AND 0.9 BARRELS OF LIQUIDS, CONSISTING OF A MIXTURE OF WATER AND DISTILLATE, WERE ALSO RELEASED UNDER HIGH PRESSURE. DUE TO THE HIGH PRESSURE OF THE RELEASE, THE LIQUIDS WERE RELEASED IN A BROAD AREA ADJACENT TO THE WELL SITE. THE SURFACE OF THIS ENTIRE AREA WAS TREATED WITH BIO-AMENDMENTS. THE FOLLOWING TIMELINE IS BASED ON BEAR CREEK STORAGE COMPANY (BCSC) INVESTIGATION: SEPTEMBER 26, 2019 (ALL TIMES CST) 18:50 (APPROX.) - DURING INJECTION LINE 4 PIPELINE RUPTURES RELEASING NATURAL GAS TO ATMOSPHERE. STORAGE WELL 12-3 SURFACE SAFETY VALVE SHUTS IN AUTOMATICALLY. 19:03 - BCSC PERSONNEL (EMPLOYEE A) NOTIFIED OF NATURAL GAS RELEASE NEAR STORAGE WELL 12-3 BY MOWING CONTRACTORS. 19:09 - EMPLOYEE A NOTIFIED THE BCSC OPERATOR TO SHUT-IN (CLOSE) UPSTREAM VALVE, LINE 4 FIELD HEADER ISOLATION VALVE. 19:31 - EMPLOYEE A ARRIVED ON-SITE, CONFIRMED GAS VENTING WAS AT WELL 12-3 AND ITS ASSOCIATED METER STATION BUT DID NOT HAVE ENOUGH INFORMATION TO QUANTIFY THE EXTENT OF THE RELEASE DUE TO LOW VISIBILITY AT DUSK AND BECAUSE HE STAYED AT A SAFE DISTANCE BASED ON COMPANY'S PROCEDURES. SUBSEQUENTLY, HE CONTINUED WITH HIS EMERGENCY RESPONSE ACTIONS, PROCEEDING TO SHUT-IN THE REMAINING WELLS ON LINE 4. 19:45 - INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATIONS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. INITIAL ASSESSMENT OF THE INCIDENT GAVE NO INDICATIONS OF NRC REPORTABLITY. NOTE THAT EMPLOYEE A WAS UNABLE TO ATTEND THE CALL DUE TO EMERGENCY RESPONSE ACTIVITIES. 20:10 - LEAK SITE ISOLATED AND EMPLOYEE A WAS ALLOWING THE PIPE SEGMENT TO BLOWDOWN. 20:40 (APPROX.) - ONCE THE SEGMENT WAS BLOWN DOWN TO A SAFE LEVEL, EMPLOYEE A WAS ABLE TO ACCESS THE LOCATION AND ASSESS THE INCIDENT. 20:43 - DETERMINED THAT THE INCIDENT WOULD LIKELY MEET THE NRC REPORTABLE CRITERIA. 20:57 - CALL TO NRC INITIATED (#1259488). BY 21:00 - THE GAS RELEASE HAD COMPLETELY STOPPED. ADDITIONAL NOTES: 48-HOUR NRC UPDATE = 1259665, REPORT TAKEN AT 14:20C ON SEPTEMBER 28, 2019.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190116 | 32923 | 2019-11-05 14:51 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-10-06 13:13 | 2019 |  |  | 28.3858 | -90.1448 | 1260388 | 2019-10-06 14:51 |  | NATURAL GAS |  | 1000 | 1661 | 4.8 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-10-06 14:51 | 2019-10-13 06:00 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-10-06 13:13 | 2019-10-07 14:30 | OFFSHORE | [28 empty] | 236 | ON THE OUTER CONTINENTAL SHELF (OCS) | [5 empty] | SOUTH TIMBALIER | 229 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 |  | 0.5 | 42000 | API 5L | SEAMLESS |  | US STEEL | EPOXY | [28 empty] | 1996 | 1995 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 239 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 3577 | 3797.582726141817627 | 2149 | 3395.532808398950131233595800524934383202 | 236954 | 251566.233516971835054 | 0 | 0 | 0 | 0 |  |  | 242680 | 114884.7013510972614525170603674540682415 | 258759.3490515126028122335958005249343832 | [8 empty] | 939 |  | 1200 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 59664 | NO | YES | YES | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK |  |  |  |  | YES | LOW FLOW | YES | [7 empty] | YES | PINHOLE AT THE 6:00 OCLOCK POSITION | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 10/6/19 RECEIVED NOTIFICATION OF A POSSIBLE LEAK. NRC TELEPHONIC NOTIFICATION MADE AT 14:51 NRC#1260388. PHMSA AID NOTIFIED 15:29. 10/8/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 9:24 NRC#1260544. PHMSA AID UPDATED AT 13:51. CLAMP INSTALLED AT 18:00. 10/11/19 PHMSA AID UPDATED AT 11:25. 10/13/2019 LINE PRESSURED UP TO OPERATING PRESSURE AT 06:00. 10/14/19 PHMSA AID UPDATED AT 08:38. REPAIR COMPLETED. FLY OVER CONFIRMED NO BUBBLES OR SHEEN PRESENT. 11/12/19 SUPPLEMENTAL-FINAL SUBMITTED TO CORRECT NOMINAL DIAMETER (PART C - 3A) TO 10" AND PART G QUESTION #8 TO "FIELD EXAMINATION."
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190117 | 37135 | 2019-11-12 19:08 | SUPPLEMENTAL FINAL | 31531 | ONEOK WESTEX TRANSMISSION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2019-10-20 04:05 | 2019 | CENTRAL | NO | 32.7206 | -102.1715 | 1261647 | 2019-10-20 04:50 | 1261723 | NATURAL GAS |  | 0 | 122 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STATION WAS SHUTDOWN AND ISOLATED, PIPELINE CONTINUED TO FLOW. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-10-20 04:05 | 2019-10-20 04:07 | ONSHORE | TX | 79331 | Not Within a Municipality | DAWSON | MILEPOST | COMPRESSOR | LAMESA COMPRESSOR STATION | 500 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1982 | 1982 | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR FIRE. | CLASS 2 LOCATION | NO |  | 476 |  | NO | NO | [5 empty] | 0 | 0 | 361 | 383.261773591612011 | 0 | 0 | 10401206 | 11042616.784076776727106 | 1500 | 1592.5004442864765 | 2500 | 2654.1674071441275 | 0 | 2.96 | 10405567 | 4873622.148302822727273 | 11047246.713701798943117 | 0 | 0 | 0 | 0 | NO |  |  |  | 1134.75 | 180 | 1188 | 192.619(A)(1) |  | 1982-09-29 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS HAVE TAKEN PLACE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | LUBE OIL TUBING LEAK. SEE NARRATIVE. | [5 empty] | YES |  |  | YES | [174 empty] | BRENT THEEDE | COMPLIANCE SPECIALIST | brent.theede@oneok.com | 620-820-3047 |  |  |  |  | BRENT THEEDE | COMPLIANCE SPECIALIST | 620-820-3047 | brent.theede@oneok.com | ON OCTOBER 20, 2019 AT 2:27 A.M. A CONTROL ROOM EMPLOYEE RECEIVED AN ACTIVE LOW OIL ALARM AND COMPRESSOR MALFUNCTION ALARM ON UNIT 6307 AT THE LAMESA STATION. A FIELD EMPLOYEE WAS DISPATCHED TO VERIFY THE PROBLEM. AT 4:05 A.M. THE FIELD EMPLOYEE DISCOVERED THE UNIT TO BE ON FIRE. EMERGENCY SERVICES WAS NOTIFIED AND DISPATCHED TO THE STATION. AT 4:07 A.M. A STATION ESD WAS ACTIVATED BY THE FIELD EMPLOYEE, AT 4:46 A.M. THE FIRE WAS CONTAINED, AND NOTIFICATIONS WERE MADE. THE INITIAL CAUSE IS STILL UNDER INVESTIGATION. ONEOK HAS CONTRACTED WITH BAKER RISK OUT OF SAN ANTONIO, TX TO FURTHER INVESTIGATE AS TO THE ROOT CAUSE OF THE INCIDENT. MORE INFORMATION WILL BE UPDATED AS IT BECOMES KNOWN. UPDATE - APRIL 22, 2020 - UPDATED D7B - ESTIMATED COST OF OPERATORS PROPERTY DAMAGE AND REPAIR. COMPLETION OF REPAIRS EXPECTED TO BE COMPLETE EARLY 4TH QUARTER 2020. INVESTIGATION OF FAILURE IS CURRENTLY ON HOLD DUE TO COVID-19 RESTRICTIONS. INVESTIGATION IS EXPECTED TO RESUME LATE MAY 2020. UPDATE - FEBRUARY 17, 2021 - INVESTIGATION IS ONGOING SEVERAL POSSIBLE SCENARIOS ARE BEING LOOKED AT THIS TIME. NOTHING CONCLUSIVE HAS BEEN FOUND THAT WOULD HAVE INITIATED OR FUELED THE FIRE. ADDITIONAL TESTING AND INVESTIGATION IS CONTINUING PENDING COVID-19 RESTRICTIONS AND GUIDELINES. SUBMITTED BY BH. UPDATE - AUGUST 25, 2022 - FURTHER REVIEW OF THIS INCIDENT IS THE LUBE OIL PUMP TUBING ASSOCIATED WITH THE TURBINE AND COMPRESSOR SKID BEGAN TO LEAK RESULTING IN THE LUBE OIL BEING RELEASED THAT CAUSED THE LOW OIL ALARM NOTICE TO OUR CONTROL CENTER. AT SOME POINT IN TIME BETWEEN THE ALARM AT 2:27 AM AND OUR EMPLOYEE ARRIVING ON SITE AT 4:05 AM, THE OIL CAUGHT FIRE DUE TO THE CLOSE PROXIMITY TO THE HOT ENGINE EXHAUST SYSTEM. THERE IS NO EVIDENCE THERE WAS A RELEASE OF GAS OR FAILURE OF A GAS COMPONENT WHICH INITIATED THE EVENT. SUBMITTED BY BRENT THEEDE
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190118 | 33061 | 2019-11-14 11:18 | SUPPLEMENTAL FINAL | 19730 | TRUNKLINE GAS CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-10-17 18:16 | 2019 |  |  | 32.6211 | -91.5767 | 1261451 | 2019-10-17 19:58 |  | NATURAL GAS |  | 41238 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE ESD SYSTEM TRIPPED THE STATION SHUTDOWN TEMPORARILY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-10-17 18:16 | 2019-10-17 18:35 | ONSHORE | LA | 71237 | EPPS | WEST CARROLL | MILEPOST | VALVE SITE 66 | EPPS COMPRESSOR STATION | EPPS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1960 | 1960 | CARBON STEEL |  | OTHER | [8 empty] | POWER BREAKER THAT SUPPLIES THE TURBINE CONTROL BUILDING WAS TRIPPED. WHEN THIS BREAKER TRIPPED THE UPS BATTERIES RAN DOWN WHICH ACTIVATED THE ESD SYSTEM. | CLASS 1 LOCATION | NO |  | 745 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 83095 | 131294.4619422572178477690288713910761155 | 0 | 0 | 3000 | 3185.000888572953 | 0 | 0 |  |  | 86095 | 87553.4599887960504383202099737532808399 | 134479.4628308301708477690288713910761155 | [8 empty] | 785 |  | 900 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [13 empty] | YES | [173 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 10/17/19 NRC TELEPHONIC NOTIFICATION MADE AT 19:58 NRC#1261451. PHMSA AID NOTIFIED 20:13. 10/18/19 PHMSA AID UPDATED AT 14:00. 10/19/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 15:19 NRC#1261620. PHMSA AID UPDATED AT 15:39. THE SUPPLEMENTAL/FINAL REPORT DATED 12/11/19, PROVIDES FURTHER CLARIFICATION/CORRECTIONS FOR THE FOLLOWING SECTIONS: PART A, QUESTION 10. THE ESD SYSTEMS OPERATED AS DESIGNED. THERE WAS A STATION YARD BLOCK VALVE OUTSIDE THE ESD SYSTEM THAT WAS INADVERTENTLY OPEN THAT CONTRIBUTED TO THE AMOUNT RELEASED. PART E, QUESTION 7. RECEIVED AN ESD SAFETY STATUS ALARM FOR THE FUEL METER AT EPPS STATION THAT THE CONTROLLER ACKNOWLEDGED IMMEDIATELY. THE COMMUNICATIONS AT EPPS STATION WENT DOWN THE SAME TIME AS THE ESD TRIPPED. GAS CONTROL COULD NOT SEE A PROBLEM UNTIL THERE WAS A PRESSURE DROP AT THE UPSTREAM AND DOWNSTREAM LOCATIONS. COMMUNICATIONS WERE OUT AT THE STATION SO THE CONTROLLERS WERE NOT ABLE TO CONFIRM AN ACTUAL ESD. CONTROLLERS REVIEWED UPSTREAM AND DOWNSTREAM PRESSURES AND THERE WERE NO NEGATIVE RATE OF CHANGE ALARMS PRESENT. UPSTREAM PRESSURE STARTED TO SHOW A SLOW DECLINE IN PRESSURE. LOCAL SHERIFF'S DEPT CALLED IN A FEW MINUTES LATER AND REPORTED THERE WAS GAS BLOWING AT THE STATION. THE CONTROLLERS IMMEDIATELY DISPATCHED FIELD PERSONNEL TO THE SCENE AND STARTED AN EVERBRIDGE CONFERENCE BRIDGE TO ALERT MANAGEMENT AND FIELD PERSONNEL IN THE AREA. PART E, QUESTION 8. UPDATED YES, BASED ON THE INVESTIGATION NO CONTROLLER ISSUES WERE IDENTIFIED. PART H, THE UPS FOR THE ESD SYSTEM AND COMMUNICATION EQUIPMENT IS SIZED TO MAINTAIN POWER FOR A MINIMUM OF 4 HOURS AND WE HAVE A BACK-UP GENERATOR THAT WILL COME ON-LINE WHEN THERE IS A LOSS OF COMMERCIAL POWER ACROSS THE WHOLE STATION. THE BREAKER THAT TRIPPED WAS SUPPLING POWER TO THE CONTROL BUILDING ONLY, WHERE THE ESD CONTROLS AND COMMUNICATION EQUIPMENT IS LOCATED. IF THERE WOULD HAVE BEEN A LOSS OF COMMERCIAL POWER OF THE WHOLE STATION THE GENERATOR WOULD HAVE STARTED AUTOMATICALLY AND GAS CONTROL WOULD HAVE RECEIVED AN ALARM. THE UPS BATTERIES WOULD NOT HAVE RUN DOWN. THE STATION YARD BLOCK VALVE WAS IDENTIFIED AND LOCKED CLOSED. AN ALARM HAS BEEN INSTALLED TO NOTIFY GAS CONTROL IF THERE IS A FUTURE POWER LOSS AT THIS CONTROL BUILDING TO PREVENT RECURRENCE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190119 | 32938 | 2019-11-14 15:19 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LP | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-11-05 06:00 | 2019 |  |  | 29.9338 | -91.7436 | 1263095 | 2019-11-05 06:41 |  | NATURAL GAS |  | 15 | 97 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-11-10 14:30 | 2019-11-11 21:30 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-02 10:35 | 2019-11-02 11:25 | ONSHORE | LA | 70544 | JEANERETTE | IBERIA | MILEPOST | 7407+97 | INDEX 205 | IOWA CS TO FRANKLIN, LA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 58 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1931 |  | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING MECHANICAL COUPLING | [5 empty] | CLASS 1 LOCATION | NO |  | 128 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 271 | 287.711746934423421 | 42 | 66.36220472440944881889763779527559055118 | 132000 | 140140.039097209932 | 500 | 530.8334814288255 | 0 | 0 |  |  | 132813 | 62229.0720968502163222283464566929133858 | 141024.9465302975903698188976377952755906 | [8 empty] | 267 |  | 480 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 18469 | NO | [5 empty] | YES | MECHANICAL COUPLINGS AND ACETYLENE WELDS PREVENT INLINE INSPECTION | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK NOT DETECTABLE ON SCADA SYSTEM. NRC WAS CALLED ONLY BECAUSE THE REPAIR COSTS ARE EXPECTED TO EXCEED $50,000. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | [29 empty] | YES | MECHANICAL COUPLING LEAK | [200 empty] | SHANNON MATTINGLY | OQ PA AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipeline.com | 270-6886357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2706886497 | tina.baker@bwpipelines.com | ON 11-2-19 AT APPROXIMATELY 10:35 AM, GULF SOUTH RECEIVED A CALL FROM AN ATMOS TECHNICIAN ABOUT A POTENTIAL LEAK ON A GULF SOUTH PIPELINE. GULF SOUTH INVESTIGATED AND DETERMINED THERE WAS A MECHANICAL COUPLING LEAK ON ITS INDEX 205 (8" LINE) IN IBERIA PARISH, LOUISIANA. AFTER LOWERING THE PRESSURE BY 20% (270 PSI TO 215 PSI) AND MONITORING THE AREA NEAR THE LEAK WITH LEL EQUIPMENT, IT WAS DETERMINED THAT THE LEAK COULD BE MONITORED UNTIL A REPAIR PLAN WAS FORMULATED. BECAUSE IT WAS A COUPLING, A PRESSURIZED WELD OVER SLEEVE WOULD HAVE TO BE INSTALLED TO CORRECT THE LEAK. FOR BUSINESS REASONS, THE LINE WOULD NEED TO BE ISOLATED WITH STOPPLE FITTINGS AND DE-PRESSURED AND THE CUSTOMERS LOCATED WITHIN THE AFFECTED AREA SERVED BY A TEMPORARY BYPASS INSTALLED ON AN ADJACENT GULF SOUTH PIPELINE. ONCE THE LINE WAS DE-PRESSURED, THE WELD OVER SLEEVE COULD BE SAFELY INSTALLED. ON 11-5-19, WHEN THAT DECISION WAS MADE, THE REPAIR COSTS WERE THEN EXPECTED TO EXCEED THE $50,000 INCIDENT REPORTING CRITERIA AND THE NRC WAS CALLED. THE NRC NOTIFICATION FOR THIS INCIDENT WAS ONLY MADE BECAUSE OF ESTIMATED REPAIR COSTS. THE RESPONSES TO PART E QUESTIONS 5A AND 5B STATE THAT MANUAL VALVES UPSTREAM AND DOWNSTREAM WERE USED TO ISOLATE THE SEGMENT. ALTHOUGH THE NEAREST UPSTREAM AND DOWNSTREAM VALVES ARE MANUAL, STOPPLES WERE USED TO ISOLATE THE SECTION. THAT IS NOT AN OPTION IN THE SELECTIONS FOR THIS REPORT. ON 11-11-19 REPAIRS WERE COMPLETED AND LINE WAS RETURNED TO SERVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190120 | 35568 | 2019-11-22 10:13 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-10-23 13:00 | 2019 | EASTERN | NO | 39.8734 | -75.7419 | 1261975 | 2019-10-23 14:40 |  | NATURAL GAS |  | 730 | 730 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-10-23 13:00 | VALVE CLOSURE |  | 2019-10-23 13:00 | 0 | 2019-10-23 12:30 | 2019-10-23 13:30 | ONSHORE | PA | 19348 | KENNETT SQUARE | CHESTER | MILEPOST | 9.78/516+26 | DELAWARE POWER & LIGHT LATERAL | DELAWARE POWER & LIGHT LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 16 |  | 0.25 | 52000 | APL 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR |  | YES | [26 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 1300 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 69008.352585747315 | 150 | 159.25004442864765 | 0 | 0 |  | 0 | 65150 | 30514.09720988091285 | 69167.60263017596265 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 0 | 780 | 192.619(A)(4) |  | 1990-06-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE LEAK WAS DISCOVERED DURING A DIG | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | PIN-HOLE LEAK ON LONG SEAM. | [7 empty] | YES | [7 empty] | 1257 | [54 empty] | YES | YES | YES |  | YES | YES |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2018 | FREE SWIMMING | STANDARD RESOLUTION | [17 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2010 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | 2018 | FREE SWIMMING | [12 empty] | YES | 1990 | 1257.35 | NO | [13 empty] | YES |  |  | 2019 | 2019 | [5 empty] | YES | YES | [52 empty] | DIKA ONYEDIRIM | PIPELINE SAFETY ENGINEER | dika.onyedirim@williams.com | 2816608503 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | DURING ANOMALY INVESTIGATION OF FEATURE ID 1160 (DPLL A-4I_156_2019) THE FINDING REVEALED POSSIBLE LACK OF FUSION IN THE LONG SEAM CREATING A SMALL THROUGH WALL DEFECT LOCATED AT 11:30 POSITION ON THE DP&L LATERAL LOCATED AT APPROXIMATE MP 9.78. THE DEFECT PRODUCED A LOSS OF CONTAINMENT (GAS LEAK). THE REPAIRS WERE COMPLETED ON OCTOBER 26, 2019 DURING THE INSPECTION OF THE PIPE, (6) ID CONNECTED LACK OF FUSION INDICATIONS WERE FOUND IN THE INSPECTION AREA WITH A MAXIMUM DEPTH OF 0.192'-75.6% WALL LOSS. ALSO, IN THE INSPECTION AREA, (4) MID-WALL INCLUSIONS WERE FOUND WITH A MAXIMUM HEIGHT OF 0.168'-66.1% WALL LOSS. IN THE AREA OF MID-WALL INCLUSION #4 (FID #1160), A PINHOLE LEAK WAS FOUND WITH A SOAPY SOLUTION AFTER GAS WAS DETECTED DURING THE INSPECTION. A MAGNETIC PARTICLE INSPECTION WAS PERFORMED REVEALING NO RELEVANT INDICATIONS. PREDICTED ILI TOOL DATA AND ACTUAL LOCATION OF ANOMALY WERE FOUND TO BE IN THE SAME LOCATION. PER WILLIAMS PROCEDURES, A PIPE REPLACEMENT WAS PERFORMED TO COMPLETE THE MITIGATION FOR THIS DIG SITE. MAGNETIC PARTICLE, PAUT AND STRAIGHT BEAM ULTRASOUND INSPECTIONS WERE PERFORMED AT THE UPSTREAM AND DOWNSTREAM TIE-IN LOCATIONS FINDING NO RELEVANT INDICATIONS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190121 | 35567 | 2019-11-26 13:46 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-11-01 14:00 | 2019 | EASTERN | NO | 39.9887 | -75.7666 | 1262859 | 2019-11-01 15:57 |  | NATURAL GAS |  | 50 | 1047 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-01 14:50 | VALVE CLOSURE |  | 2019-11-01 14:50 | 0 | 2019-11-01 14:00 | 2019-11-01 14:30 | ONSHORE | PA | 19335 | DOWNINGTOWN | CHESTER | SURVEY STATION NO. | 81+84 | DELAWARE POWER & LIGHT LATERAL | DELAWARE POWER & LIGHT LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 52000 | APL 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR |  | YES | [26 empty] | 1964 | 1964 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 1300 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 65000 | 69008.352585747315 | 150 | 159.25004442864765 | 0 | 0 |  | 0 | 65150 | 30514.09720988091285 | 69167.60263017596265 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 0 | 780 | 192.619(A)(3) |  | 1990-06-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS EXPOSED | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | PINHOLE LEAK IN LONGSEAM | [7 empty] | YES | [7 empty] | 1257 | [54 empty] | YES | YES | YES |  | YES | YES |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2018 | FREE SWIMMING | STANDARD RESOLUTION | [17 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [5 empty] | 2018 | FREE SWIMMING | [12 empty] | YES | 1990 | 1257.35 | NO | [13 empty] | YES |  |  | 2019 | 2019 | [5 empty] | YES | YES | [52 empty] | DIKA ONYEDIRIM | PIPELINE SAFETY ENGINEER | dika.onyedirim@williams.com | 2816608503 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | DURING ANOMALY INSPECTION OF THE PIPE, ONE ID CONNECTED LACK OF FUSION AND TWO ID PLANAR DEFECTS WERE FOUND IN THE ILI CALL AREAS. PLANAR DEFECT #1 WAS FOUND TO BE 100.0% THRU-WALL AND WAS LEAKING AFTER ABRASIVE SANDBLASTING OPERATIONS WERE COMPLETED. PREDICTED ILI TOOL DATA AND ACTUAL LOCATION OF ANOMALY WERE FOUND TO BE IN THE SAME LOCATION. PER WILLIAMS PROCEDURES, A PIPE REPLACEMENT WAS PERFORMED TO COMPLETE THE MITIGATION FOR THIS DIG SITE. MAGNETIC PARTICLE, PAUT AND STRAIGHT BEAM ULTRASOUND INSPECTIONS WERE PERFORMED AT THE UPSTREAM AND DOWNSTREAM TIE-IN LOCATIONS FINDING NO RELEVANT INDICATIONS. LABORATORY FINDINGS: SCANNING ELECTRON MICROSCOPIC (SEM) EXAMINATIONS ITEM - A PORTION OF THE CRACK SURFACE, DETECTED DURING ULTRASONIC EXAMINATIONS REVEALED AFTER SECTIONING. FINDINGS - RUST COLORED DEPOSITS ORIGINATING ON THE INTERNAL SURFACE COVERED A PORTION OF THE FRACTURE SURFACE IN THE AREAS IDENTIFIED IN UT EXAMINATION. THESE AREAS WERE CONFIRMED TO BE CORRODED AND PITTED UNFUSED WELD METAL. METALLOGRAPHIC EXAMINATIONS SPECIMEN - A TRANSVERSE SECTION ACROSS THE REVEALED CRACKS. FINDINGS - THE CRACKS WERE CONFIRMED TO BE LONGITUDINAL, FOLLOWING A VIRTUALLY STRAIGHT PATH ALONG WHAT APPEARS TO BE THE ORIGINAL WELD LINE OF FUSION WITH A REPAIR WELD PRESENT ON THE EXTERNAL SURFACE OF THE SAMPLE. COMMENTS THE CRACK INDICATIONS WERE FOUND TO BE CORRODED AND PITTED AREAS OF THE UNFUSED WELD METAL ORIGINATING ON THE INTERNAL SURFACE OF THE PIPE FOLLOWING THE WELD LINE OF FUSION WITH A REPAIR WELD PRESENT ON THE EXTERNAL SURFACE OF THE PIPE. THE CRACKS APPEAR TO HAVE BEEN INTRODUCED DURING MANUFACTURING
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190122 | 33474 | 2019-11-26 17:19 | SUPPLEMENTAL FINAL | 15033 | PAIUTE PIPELINE CO | P.O. BOX 94197 | LAS VEGAS | NV | 89193 | 2019-10-29 07:34 | 2019 | PACIFIC | NO | 39.2914 | -118.5236 | 1262507 | 2019-10-29 09:23 | 1262689 | NATURAL GAS |  | 169 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-10-29 09:44 | 2019-11-02 11:53 |  | NO |  |  | YES | 2019-10-29 07:34 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 169 | NO | [6 empty] | 0 | 2019-10-29 08:19 | 2019-10-29 08:19 | ONSHORE | NV | 89406 | FALLON | CHURCHILL | MILEPOST | GA-19.73 | GABBS LATERAL | FALLON CITY GATE #3 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.154 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1992 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | OTHER OUTSIDE FORCE STRUCK FACILITY | 2 | 2 |  | CLASS 3 LOCATION | NO |  | 64 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1390 | 2196.272965879265091863517060367454068241 | 69102 | 73363.310467389399402 | 31115 | 33033.767549315810865 | 0 | 0 |  | 8.2249 | 101607 | 48379.392003169914927461942257217847769 | 108593.3509825844753588635170603674540682 | 0 | 0 | 0 | 0 | NO |  |  |  | 358 | 909.31 | 531 | 192.619(A)(2) |  | 2005-10-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 90 | NO | [5 empty] | YES | THIS WAS A CITY GATE. | YES |  |  |  |  | YES | CITY GATE | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | COMPANY SCADA NETWORK TRENDS ALERTED GAS CONTROL PERSONNEL TO A POTENTIAL ISSUE AT THE FACILITY. COMPANY EMPLOYEES WERE DISPATCHED TO THE FACILITY TO INVESTIGATE AND CONFIRMED THE SCADA INFORMATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | ROADWAY | 50 | YES | YES | YES | [236 empty] | WILLIAM PARRY | MANAGER - ENGINEERING STAFF | william.parry@swgas.com | 702-218-9781 | 702-876-4238 | CHRIS ANDERSON | chris.anderson@swgas.com | 775-887-2805 | CHRIS ANDERSON | DIRECTOR OF OPERATIONS PAIUTE PIPELINE | 775-887-2805 | chris.anderson@swgas.com | ON OCTOBER 29, 2019, A SEMI-TRUCK INVOLVED IN A THREE-VEHICLE COLLISION, VEERED OFF THE ROADWAY STRIKING A PAIUTE PIPELINE ABOVE GROUND METER AND PRESSURE REGULATION FACILITY, (FALLON CITY GATE #3) LOCATED AT THE INTERSECTION OF US HIGHWAY 50 AND SHECKLER ROAD IN FALLON, NV. THE DAMAGE TO THE FACILITY RESULTED IN AN UNINTENTIONAL RELEASE OF NATURAL GAS AND IGNITION. SUBSEQUENT TO STRIKING THE PAIUTE FACILITY THE SEMI-TRUCK IMPACTED AN EARTHEN BERM. THE DRIVER WAS EJECTED FROM THE VEHICLE AND PRONOUNCED DEAD AT THE SCENE. THE OCCUPANT OF ANOTHER VEHICLE WHICH COLLIDED WITH THE SEMI-TRUCK IN THE ROADWAY SUSTAINED INJURIES REQUIRING INPATIENT HOSPITALIZATION. COMPANY SCADA NETWORK TRENDS ALERTED GAS CONTROL PERSONNEL TO A POTENTIAL ISSUE AT THE FACILITY. COMPANY EMPLOYEES WERE DISPATCHED TO THE FACILITY TO INVESTIGATE AND CONFIRMED THE SCADA INFORMATION. THE INLET VALVE TO FALLON CITY GATE #3 WAS OPERATED TO CONTROL THE FLOW OF GAS AND DOWNSTREAM SERVICE WAS MAINTAINED THROUGH ADJACENT FACILITIES. SERVICE WAS TEMPORARILY RESTORED THROUGH THE EXISTING FACILITIES ON THE SAME DATE. NEW PERMANENT FACILITIES WERE PLACED IN SERVICE ON 11/02/2019. SUPPLEMENTAL: AN INVESTIGATION, LED BY LOCAL AUTHORITIES, DETERMINED THAT THE NATURAL GAS OF PAIUTE PIPELINE COMPANY'S FACILITIES WAS NOT RELATED TO THE CAUSE OF DEATH OR HOSPITALIZATION OF THOSE INVOLVED IN THIS INCIDENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190123 | 34314 | 2019-11-27 16:51 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-10-28 13:15 | 2019 | EASTERN | NO | 31.5828 | -89.4962 | 1262447 | 2019-10-28 16:58 |  | NATURAL GAS |  | 125 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | CROSSOVER HEADER WAS SHUT IN. MAINLINE WAS LEFT IN SERVICE |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-10-28 14:15 | VALVE CLOSURE |  | 2019-10-28 14:15 | 0 | 2019-10-28 13:15 | 2019-10-28 14:15 | ONSHORE | MS | 39401 | SEMINARY | COVINGTON | MILEPOST | 70-30VALVE YD | MAINLINE A | 70-30 VALVE YARD | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 2017 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 304 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 500 | 790.026246719160104986876640419947506562 | 80000 | 84933.35702861208 | 1000 | 1061.666962857651 | 0 | 0 |  | 4 | 81500 | 38456.0837394881124908136482939632545932 | 86785.0502381888911049868766404199475066 | 0 | 0 | 0 | 0 | NO |  |  |  | 645 | 48000 | 760 | 192.619(A)(2) |  | 2017-11-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 50 | NO | [5 empty] | YES | DOWNSTREAM CROSSOVER HEADER. MULTIPLE BENDS BETWEEN PIPELINE SEGMENTS. NO LAUNCHER/RECEIVERS INSTALLED. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | N/A | [161 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 832-215-4163 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | ON 10/28/2019 AT APPROXIMATELY 1:15 PM, GAS WAS HEARD RELEASING FROM THE 70-30 VALVE YARD. THE RELEASE WAS DETERMINED TO BE IN THE VICINITY OF THE MAINLINE A BLOCK VALVE IN THE 70-30 VALVE YARD. THE AREA NEAR THE CO2 CROSSOVER VALVE WAS HAND EXCAVATED AND BUBBLING WAS OBSERVED IN RAIN/WATER PUDDLE NEAR THE CO2 CROSSOVER VALVE AND 16 INCH INSULATING FLANGE. THE WILLIAMS' SECURITY OPERATIONS CENTER WAS CONTACTED AND NRC NOTIFICATION 1262447 WAS MADE AS IT WAS DETERMINED REPAIR COSTS WOULD BE EXPECTED EXCEED $50,000. THE DOWNSTREAM CROSSOVER HEADER WAS ISOLATED, BLOWN DOWN, AND LEAKING CEASED. THE AREA NEAR THE CO2 CROSSOVER VALVE AND 16 INCH INSULATING FLANGE WAS EXCAVATED. THE GASKET WAS REPLACED AND THE 16 INCH FLANGE WAS TIGHTENED TO SPECIFICATIONS. THE DOWNSTREAM CROSSOVER HEADER WAS PRESSURED UP AND LEAK TESTED. NO FURTHER RELEASE OF GAS WAS IDENTIFIED. THE EXCAVATED AREA WAS PROPERLY BACK-FILLED AND DOWNSTREAM CROSSOVER HEADER WAS BROUGHT BACK ON LINE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190124 | 34387 | 2019-12-03 12:01 | SUPPLEMENTAL FINAL | 14435 | OZARK GAS TRANSMISSION, L.L.C. (SPECTRA ENERGY PARTNERS, LP) | 1501 MCKINNEY SUITE 800 | HOUSTON | TX | 77010 | 2019-11-05 17:36 | 2019 | CENTRAL | NO | 36.2305 | -90.2749 | 1263191 | 2019-11-05 20:28 |  | NATURAL GAS |  | 10792 | 714 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-05 17:46 | 2019-12-19 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-05 17:46 | VALVE CLOSURE |  | 2019-11-05 20:07 | 0 | 2019-11-05 17:36 | 2019-11-05 19:15 | ONSHORE | AR | 72461 | RECTOR | CLAY | MILEPOST | 251.402 | LINE 2 | SROC-EOLN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 6 | NO | YES | [6 empty] | YES | UNCASED | UNKNOWN | 5 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | NO | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.188 | 60000 | API-5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL | EPOXY |  | NO | [26 empty] | 1993 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  |  |  | CLASS 1 LOCATION | NO |  | 285 |  | NO | NO | [5 empty] | 0 | 0 | 2756 | 2925.954149635686156 | 41657 | 65820.2467191601049868766404199475065617 | 3800000 | 4034334.4588590738 | 60000 | 63700.01777145906 | 0 | 0 |  | 3.86 | 3904413 | 1852374.38157094924517764829396325459318 | 4166780.67749932865114287664041994750656 | 0 | 0 | 0 | 0 | NO |  |  |  | 1164 | 3650 | 1480 | 192.619(A)(1) |  | 1993-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 52483 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE DID NOT EXCEED MAOP, BUT RATHER A PRESSURE LOSS WAS OBSERVED BY THE CONTROLLER. WHEN THE PRESSURE LOSS WAS OBSERVED, THE CONTROLLER PROMPTLY NOTIFIED APPROPRIATE COMPANY PERSONNEL TO RESPOND TO THE FAILURE. | [12 empty] | YES | 7 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [7 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [5 empty] | NO |  | PREVIOUS DAMAGE | [266 empty] | MAYRA SALINAS |  | mayra.salinas@enbridge.com | [5 empty] | RONDA LOUDERMAN | DIRECTOR EHSR | 361-960-5671 | rlouderman@blackbearllc.com | ORIGINAL REPORT: 48 HR NRC REPORT 1263227 AT APPROXIMATELY 5:36 P.M. CST ON NOVEMBER 5, 2019, OZARK GAS TRANSMISSION'S (OGT) 10-INCH DIAMETER LINE 2 TRANSPORTING NATURAL GAS FROM STANDING ROCK COMPRESSOR STATION TO THE END OF LINE IN CLAY COUNTY ARKANSAS FAILED AT MP 251.402. THE FAILURE RESULTED IN A RUPTURE WITHOUT FIRE. THERE WERE NO INJURIES OR FATALITIES OR EVACUATIONS. OGT'S GAS CONTROL RECEIVED A LOW LOW ALARM AT 5:36 PM CST AND SUBSEQUENTLY DISPATCHED OGT PERSONNEL TO THE FAILURE SITE. OGT'S GAS CONTROL REMOTELY CLOSED UPSTREAM AND DOWNSTREAM VALVES AT 5:48 PM CST, AND FURTHER ISOLATED THE RUPTURED SECTION OF PIPELINE BY MANUALLY CLOSING A VALVE NEARER TO THE RUPTURE SITE AT 8:07 PM CST. OGT PERSONNEL ARRIVED AT THE FAILURE SITE AT 7:15 PM CST AND BELIEVED THAT THE PIPELINE WAS LEAKING BUT NOT RUPTURED. THE NRC WAS NOTIFIED AT 8:28 PM CST OF AN APPARENT LEAK, AS SOON AS LOCATION INFORMATION FOR THE SITE WAS AVAILABLE. THE NRC WAS UPDATED THE FOLLOWING MORNING WITH INFORMATION CONFIRMING THERE HAD BEEN A RUPTURE WITH NO FIRE, CONFIRMED IN THE FIELD AFTER DAYLIGHT. THE SECTION OF THE LINE IS STILL ISOLATED AND SHUTDOWN. A 3RD PARTY METALLURGICAL INVESTIGATION IS ONGOING. THE APPARENT CAUSE IS PENDING. SUPPLEMENTAL REPORT 05/04/2020 THE CAUSE OF THIS INCIDENT IS THIRD PARTY DAMAGE. NOTE THAT THE PIPE ENDS DOWNSTREAM OF THE INCIDENT SITE AND DOES NOT HAVE A SOURCE OF GAS TO CONTINUOUSLY FEED FROM THAT SIDE. AS SUCH, THE LOCAL TIME OF FINAL UPSTREAM AND DOWNSTREAM IS UPDATED ON PART A.22.C AND PART A.22.F
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190125 | 33088 | 2019-12-04 12:53 | SUPPLEMENTAL FINAL | 207 | ALASKA PIPELINE CO | 3000 SPENARD ROAD P.O. BOX 190288 | ANCHORAGE | AK | 99519 | 2019-11-09 08:52 | 2019 |  |  | 61.1393 | -149.8729 | 1263538 | 2019-11-09 10:36 |  | NATURAL GAS |  | 348 | 172 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-11-09 11:03 | 2019-11-11 17:20 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-09 08:52 | 2019-11-09 09:09 | ONSHORE | AK | 99515 | ANCHORAGE | ANCHORAGE | MILEPOST | MILE POST 7 | WEST SIDE FEEDER | A8 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 |  | 0.188 | 42000 | 5L-X42 | SEAMLESS |  | UNDETERMINED | COLD APPLIED TAPE | [28 empty] | 1976 | 1975 | CARBON STEEL |  | MECHANICAL PUNCTURE | 11 | 1 | [7 empty] | CLASS 3 LOCATION | NO |  | 159 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 17204 | 18264.918429003027804 | 34807 | 54996.8871391076115485564304461942257218 | 894 | 949.130264794739994 | 50280 | 53380.61489248269228 | 0 | 0 |  |  | 103185 | 68111.9826250170641715013123359580052493 | 127591.5507253880716265564304461942257218 | [8 empty] | 582 |  | 685 | 192.619(A)(2) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 10853 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | YES | YES |  |  |  |  | CONTRACTOR | UNKNOWN/OTHER | POLE | NO | [5 empty] | NO |  | OTHER |  |  |  | CONTRACTOR WAS WORKING OUTSIDE OF THEIR LOCATE REQUEST SCOPE. | [262 empty] | RUSTY ALLEN | COMPLIANCE ENGINEER | rusty.allen@enstarnaturalgas.com | 907-334-7765 |  |  |  |  | STEVE COOPER | DIRECTOR OF OPERATIONS | 907-334-7730 | steve.cooper@enstarnaturalgas.com | ON NOVEMBER 9, 2019 A THIRD PARTY CONTRACTOR RUPTURED THE PIPELINE WHILE DRIVING PILE INTO THE GROUND. THE CONTRACTOR HAD BEEN NOTIFIED OF THE 8 INCH TRANSMISSION PIPELINE IN THE EASEMENT AND IGNORED THE OPERATORS REQUEST FOR A SAFETY WATCH. THE CONTRACTOR WAS PERFORMING WORK OUTSIDE OF THEIR LOCATE TICKET REQUEST AT THE TIME OF THE DAMAGE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190126 | 33025 | 2019-12-05 13:46 | ORIGINAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-11-07 21:48 | 2019 |  |  | 28.521 | -81.4889 | 1263440 | 2019-11-08 10:25 |  | NATURAL GAS |  | 3900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE ESD SYSTEM TRIPPED THE STATION SHUTDOWN TEMPORARILY | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-07 21:48 | 2019-11-07 22:43 | ONSHORE | FL | 32835 | ORLANDO | ORANGE | MILEPOST | 668.8 | ORLANDO COMPRESSOR STATION 18 | STATION YARD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2003 |  | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE. THE ESD SEQUENCE PROCESS FAILED, THE FIRE GATE VALVE DID NOT CLOSE COMPLETELY DUE TO A FAILED PILOT. AS A RESULT OF THE OPEN VALVE A REPORTABLE VOLUME OF GAS WAS RELEASED. | CLASS 3 LOCATION | YES | METHOD2 | 646 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 12051 | 19041.2125984251968503937007874015748031 | 550 | 583.91682957170805 | 1200 | 1274.0003554291812 | 0 | 0 |  |  | 13801 | 13313.4608027382035255905511811023622047 | 20899.1297834260861003937007874015748031 | [8 empty] | 867 |  | 973 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE IN THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | YES | COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE. THE ESD SEQUENCE PROCESS FAILED, THE FIRE GATE VALVE DID NOT CLOSE COMPLETELY DUE TO A FAILED PILOT. AS A RESULT OF THE OPEN VALVE A REPORTABLE VOLUME OF GAS WAS RELEASED. | [22 empty] | YES | SOFT GOODS INSIDE THE PILOT REGULATOR FAILED | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | 11/7/19 COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE AT 21:48. 11/8/19 NRC TELEPHONIC NOTIFICATION MADE AT 10:25 NRC#1263440. PHMSA AID NOTIFIED 10:39. 11/9/19 48-HOUR UPDATE NRC NOTIFICATION MADE AT 18:42 NRC#1263560. PHMSA AID UPDATED AT 19:25. 11/11/19 PHMSA AID UPDATED AT 11:34. THE COMPRESSOR STATION ESD SYSTEM WAS INITIATED AS A RESULT OF A FAILED FIBER OPTICS COMMUNICATION CABLE. THE ESD SEQUENCE PROCESS FAILED, THE FIRE GATE VALVE DID NOT CLOSE COMPLETELY DUE TO A FAILED PILOT. SOFT GOODS INSIDE THE PILOT REGULATOR FAILED. AS A RESULT OF THE OPEN VALVE A REPORTABLE VOLUME OF GAS WAS RELEASED. THE SOFT GOODS INSIDE THE PILOT REGULATOR WERE REPLACED TO PREVENT RECURRENCE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190127 | 34462 | 2019-12-08 22:54 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2019-11-08 14:05 | 2019 | EASTERN | NO | 35.1707 | -81.4091 | 1263466 | 2019-11-08 14:38 |  | NATURAL GAS |  | 1226 | 263 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-06 15:00 | 2019-12-30 08:13 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-06 15:00 | VALVE CLOSURE |  | 2019-11-06 15:00 | 0 | 2019-11-08 14:05 | 2019-11-06 15:00 | ONSHORE | NC | 28073 | GROVER | CLEVELAND | MILEPOST | STATION 145 | MAINLINE D, STA. 145 | 145D0 TO 145D1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 42 |  | 0.625 | 60200 | API 5L, X60 | LONGITUDINAL ERW - LOW FREQUENCY |  | NA | EPOXY |  | YES | [26 empty] | 2017 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 809 |  | NO | NO | [5 empty] | 0 | 0 | 6838 | 7259.678692020617538 | 31876 | 50365.7532808398950131233595800524934383 | 475000 | 504291.807357384225 | 45000 | 47775.013328594295 | 0 | 0 |  | 26 | 558714 | 279800.7263018058701083517060367454068241 | 609692.2526588390325511233595800524934383 | 0 | 0 | 0 | 0 | NO |  |  |  | 635 | 0 | 780 | 192.619(A)(2) |  | 2017-07-09 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | AUTOMATIC | 490 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DOES NOT PERTAIN TO CONTROL ROOM OPERATORS | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | CONSTRUCTION INSTALLATION | [12 empty] | YES | [8 empty] | 1351 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES | 2019 | [6 empty] | YES | [55 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | DURING THE SEMI-ANNUAL LEAK SURVEY FLIGHT, AN ELEVATED CH4 LEVEL WAS INDICATED. A LOCAL OPERATIONS TECH USED HANDHELD RMLD TO VERIFY THE PRESENCE OF NATURAL GAS. IT WAS INITIALLY BELIEVED A BURIED THREADED CONNECTION IN THE BODY VENT PIPING OF VALVE WAS LEAKING. POTHOLING, VACUUM EXCAVATION, AND PROBING WERE USED TO DETERMINE THE LEAK LOCATION UPSTREAM OF MAINLINE BLOCK VALVE 145D1 WHERE INCREASED LEVELS OF NATURAL GAS WERE NOTED ONCE THE PROBE BAR WAS REMOVED. THE PIPELINE SEGMENT WAS ISOLATED AND BLOWN DOWN TO ALLOW FOR FURTHER EXCAVATION. ONCE PIPELINE WAS EXCAVATED, THE SOURCE OF LEAK WAS IDENTIFIED USING LEAK DETECTION LIQUID AT A WELD FITTING. X-RAYS OF THE SUBJECT WELD WERE TAKEN. A PLAN HAS BEEN FORMULATED AND APPROVED TO CUT OUT THE WELD THAT WAS LEAKING AND ALSO THE FITTING JUST DOWNSTREAM OF THE SUSPECT WELD. NEW PIPE AND FITTING WILL BE INSTALLED. ONCE THE SUSPECT WELD AND FITTING ARE REMOVED, IT WILL BE SENT TO LAB FOR A FULL METALLURGICAL ANALYSIS. THE WORK IS SET TO BEGIN THE WEEK OF 12/9/2019. UPDATE: CRACKING CONFINED TO WELD METAL. CRACKING MOST LIKELY OCCURRED BY A HYDROGEN ASSISTED CRACKING (HAC) MECHANISM. THE HAC CRACKING WAS MOST LIKELY FACILITATED BY THE HI-LOW OF THE JOINT FIT-UP, AND QUALITY OF APPLICATION OF THE ROOT PASS DURING CONSTRUCTION INSTALLATION. ANY UNDUE STRESSES ASSOCIATED WITH THE FINAL TIE IN WELD MAY HAVE CONTRIBUTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190128 | 34078 | 2019-12-11 10:59 | SUPPLEMENTAL FINAL | 12576 | ENABLE MISSISSIPPI RIVER TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-11-14 13:00 | 2019 | CENTRAL | NO | 32.6784 | -92.3239 | 1263945 | 2019-11-14 14:23 | 1264007 | NATURAL GAS |  | 22213 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-14 13:45 | VALVE CLOSURE |  | 2019-11-14 14:00 | 0 | 2019-11-14 13:12 | 2019-11-14 13:30 | ONSHORE | LA | 71234 | Not Within a Municipality | UNION | MILEPOST | 1052+39 | WESTLINE | WESTLINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 18 |  | 0.281 | 52000 | API 5LX | OTHER | SMITH WELD | AO SMITH | COAL TAR |  | NO | [7 empty] | PIPE GIRTH WELD |  | YES | 0.375 | 52000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | SEAH STEEL COMPANY | FUSION BONDED EPOXY(FBE) |  | NO | [7 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 9 | 2 |  | CLASS 1 LOCATION | NO |  | 363 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 58864 | 93008.2099737532808398950131233595800525 | 75000 | 79625.022214323825 | 1000 | 1061.666962857651 | 0 | 0 |  | 2.65 | 134864 | 96622.8586488000319265091863517060367454 | 173694.8991509347568398950131233595800525 | 0 | 0 | 0 | 0 | NO |  |  |  | 649 | 12000 | 855 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 96901 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | WELDER PERFORMANCE | [13 empty] | YES | [7 empty] | UNKNOWN | [54 empty] | YES | YES | YES |  | YES |  |  |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2005 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | 2019 | FREE SWIMMING | HIGH RESOLUTION | [13 empty] | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2012 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | 11/14/19, 13:00 EMRT'S WESTLINE EXPERIENCED A FAILURE IN UNION PARISH LOUISIANA. THE FAILURE OCCURRED NEAR THE GIRTH WELD AREA OF A REPAIRED SECTION OF PIPE. THE PIPE WAS INSTALLED THE PREVIOUS DAY TO REMOVE AN ANOMALY DISCOVERED BY AN ILI TOOL RUN. THE FAILED SECTION WAS REMOVED AND SENT TO PRECISION ENGINEERING FOR ANALYSIS. NRC INITIAL 11/14/2019 (NRC # 1263945). 48 HR FOLLOW UP 1/15/2019 (NRC# 1264007). 07.10.2020 SUPPLEMENTAL. PRECISION ENGINEERING SOLUTIONS, LLC WAS CONTRACTED TO PERFORM A FAILURE INVESTIGATION FOR ENABLE ON CRACKING AND LEAKING ASSOCIATED WITH A GIRTH WELD IN THE WESTLINE SYSTEM THAT JOINED TWO PIPE MATERIALS: 18" .281" (OLD PIPE) AND 18" .375" (NEW PIPE). THE OLD PIPE WAS INSTALLED IN 1950, WHILE THE NEW PIPE WAS INSTALLED IN 2019. THE DIMENSIONAL EXAMINATION SHOWED THAT THE PIPE ON EITHER SIDE OF THE GIRTH WELD MET THE DIMENSIONAL REQUIREMENTS OF THE APPLICABLE API 5L AND 5LX SPECIFICATIONS FOR THEIR RESPECTIVE DATES OF MANUFACTURE AND SIZES. THE CHEMICAL ANALYSIS SHOWED THAT THE NEW PIPE MET THE CHEMICAL COMPOSITION REQUIREMENTS API 5L, BUT THAT THE OLD PIPE DID NOT, DUE TO HIGH CARBON, PHOSPHOROUS, AND CARBON EQUIVALENCY. IT IS TO BE NOTED THAT THERE WERE NO CHEMICAL COMPOSITION REQUIREMENTS FOR X52 LINE PIPE AT THE TIME OF THE MANUFACTURE OF THE OLD PIPE (1950). THE HARDNESS TESTING CONDUCTED DID NOT SHOW ANY ABNORMALITIES IN THE HARDNESS OF THE PIPES, HEAT AFFECTED ZONES, OR WELD METAL. THE MAGNETIC PARTICLE INSPECTION OF THE I.D. SURFACE SHOWED CRACK INDICATIONS ON THE OLD PIPE SIDE OF THE GIRTH WELD AROUND THE ENTIRE CIRCUMFERENCE. THE MICROSCOPIC EXAMINATION SHOWED LACK OF FUSION ORIGINATING AT THE I.D. BETWEEN THE OLD PIPE AND THE ROOT PASS WELD METAL. DUCTILE OVERLOAD FRACTURE WAS FOUND NEAR THE O.D. AND THROUGH-WALL IN SOME REGIONS. A VISUAL EXAMINATION OF THE FRACTURE SURFACE OF THE THROUGH WALL CRACK SHOWED LACK OF FUSION PRESENT AROUND MOST OF THE I.D. SURFACE WITH THE REMAINDER OF THE FRACTURE SURFACE BEING DUCTILE OVERLOAD. THE LACK OF FUSION IS THOUGHT TO BE ASSOCIATED WITH WELDING PARAMETERS AND WELDING TECHNIQUE. ALTHOUGH THE CARBON CONTENT AND CARBON EQUIVALENCE OF THE OLD PIPE WAS HIGH AND IN EXCESS OF CURRENT API 5L REQUIREMENTS, IT IS NOT THOUGHT TO BE THE PRIMARY CAUSE OF THE FAILURE. ADDITIONALLY, THE PRESENCE OF ELEVATED STRESSES GENERATED DURING THE TIE-IN PROCESS CANNOT BE DISCOUNTED, ALTHOUGH IT IS DIFFICULT TO QUANTIFY WHAT MAGNITUDE OF STRESS MIGHT HAVE EXISTED AT THE TIME OF CONSTRUCTION. ALL TIE IN WELDS ON THE WESTLINE REMEDIATION PROJECT WERE NON-DESTRUCTIVELY TESTED WHEN COMPLETED. WELDS TI-9 AND TI-10 (NEW PIPE) WERE TESTED AND PASSED BY A LEVEL II TECHNICIAN. THE TECHNICIAN'S PAPERWORK STATED THEY WERE FOLLOWING THE MINIMUM GUIDELINES SET FORTH IN API 1104. AFTER THE INCIDENT, THE X-RAY FILM FOR TI-9 AND TI-10 WAS SENT TO A 3RD PARTY X-RAY COMPANY FOR A QUALITY CONTROL CHECK. THE 3RD PARTY FOUND THE FILM DENSITY TO BE LESS THAN THE REQUIRED RANGE OF 1.8 - 4.0 THAT API 1104 AND ENABLE MIDSTREAM CONSTRUCTION SPEC CS-095 REQUIRE. FIVE OF THE SIX X-RAY SHOTS FOR TI-9 AND TI-10 WERE BELOW THE MINIMUM DENSITY REQUIREMENT OF 1.8. DENSITY BELOW 1.8 COULD POSSIBLY CAMOUFLAGE A FEATURE, IF PRESENT. DUE TO FILM DENSITY BEING OUT OF SPEC, ENABLE DISQUALIFIED THE X-RAY TECH. 7/30/20 SUPPLEMENTAL. BOTH WELDERS THAT PERFORMED THE WELDS WERE QUALIFIED AT THE TIME OF THE TIE-IN. BOTH HAD BEEN OBSERVED FOLLOWING THE WELDING PROCEDURE PRIOR TO THE FAILURE. AFTER THE FAILURE, A WELDER REVIEW WAS CONDUCTED AND THEY WERE NOT DISQUALIFIED. OF THE THREE X-RAY REVIEWS AFTER THE INCIDENT, ONLY ONE WELD WAS FOUND TO BE OUT OF SPEC (TI-10) FOR WHICH IT WAS REPAIRED IMMEDIATELY, X-RAYED, AND FOUND PASSING. WELD TESTING WAS PERFORMED AND CONFIRMED THE WELDING PROC. USED WAS ADEQUATE. ALONG WITH WELD TESTING, AND LEVEL III TECH REVIEWS, ENABLE WILL PERFORM AN ASSESSMENT APPROPRIATE FOR CRACK-LIKE DEFECTS ON THE WESTLINE HCAS, MCAS AND CLASS 3 LOCATIONS DURING THE NEXT REASSESSMENT CYCLE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190129 | 33944 | 2019-12-12 16:14 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2019-11-13 11:04 | 2019 | CENTRAL | NO | 31.949 | -103.1069 | 1263831 | 2019-11-13 12:00 | 1263966 | NATURAL GAS |  | 11048 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIGGING OPERATIONS CONTINUED AS SCHEDULED AFTER RELEASE WAS STOPPED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-11-13 11:04 | 2019-11-13 11:04 | ONSHORE | TX | 79745 | KERMIT | WINKLER | SURVEY STATION NO. | 10 +52 | LINE 3026 | 0010- MILEPOST 10 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH RELIEF VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 528 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 30272 | 47831.3490813648293963254593175853018373 | 0 | 0 | 250 | 265.41674071441275 | 0 | 0 |  | 2.74 | 30522 | 31501.4486561092071778215223097112860892 | 48096.7658220792421463254593175853018373 | 0 | 0 | 0 | 0 | NO |  |  |  | 605 | 140 | 651 | 192.619(C) |  | 1952-06-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PSSR NOT EFFECTIVELY COMPLETED. |  |  | YES |  |  | COMMISSIONING | NO | [150 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON NOVEMBER 13, 2019 AT 11:04AM, KINDER MORGAN EMPLOYEES AT THE EL PASO NATURAL GAS (EPNG) KEYSTONE COMPRESSOR STATION HEARD GAS VENTING IN THE STATION YARD AND NOTICED TWO RELIEF VALVES ON LINE 3026 WERE RELIEVING. SMART-PIGGING ACTIVITIES WERE BEING PERFORMED AND OPERATIONS DETERMINED THAT THE PIG WAS STUCK RESULTING IN AN INCREASE IN PRESSURE ON THE LINE. OPERATIONS DETERMINED THAT THE PIG WAS STOPPED AT BLOCK VALVE 1, WHICH WAS CLOSED. THEY OPENED THE VALVE MANUALLY WHICH ALLOWED THE PIG TO RESUME ITS RUN AND THE GAS RELEASE WAS STOPPED. A TOTAL OF 11,048 MCF OF GAS WAS RELEASED. THE INVESTIGATION REVEALED THAT BLOCK VALVE 1 WAS INCORRECTLY LEFT IN THE CLOSED POSITION FOR THIS PIG RUN DUE TO A MISUNDERSTANDING OF ITS FUNCTIONALITY. A RECENT PROJECT HAD REPLACED THE VALVE ACTUATOR TO MAKE THE VALVE CAPABLE OF REMOTE OPERATION. THIS VALVE IS ON THE BOUNDARY OF THE HOBBS AND ODESSA OPERATIONS AREA. THE PSSR FOR THE PROJECT HAD ONLY BEEN PERFORMED WITH THE HOBBS AREA, BUT THE ODESSA AREA WAS USING THE VALVE IN THEIR PIGGING OPERATIONS. THE PSSR HAD NOT SUCCESSFULLY COMMUNICATED HOW THIS VALVE FUNCTIONS TO THE ODESSA AREA AT THE COMPLETION OF THE PROJECT. THIS RESULTED IN THE ODESSA AREA INCORRECTLY BELIEVING THIS VALVE WOULD OPEN AS THE PIG APPROACHED AND ULTIMATELY CAUSING THE OVERPRESSURE AND RELEASE OF GAS. IN ORDER TO PREVENT A REOCCURRENCE, BOTH HOBBS AND ODESSA AREA OPERATIONS PERSONNEL HAVE BEEN RETRAINED ON THE CORRECT OPERATION OF THIS VALVE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190130 | 34391 | 2019-12-16 14:19 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-11-17 08:23 | 2019 | EASTERN | NO | 41.173 | -82.2132 | 1264138 | 2019-11-17 10:27 |  | NATURAL GAS |  | 1467 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-17 09:26 | 2019-11-17 17:15 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-17 09:26 | VALVE CLOSURE |  | 2019-11-17 09:26 | 12 | 2019-11-17 08:23 | 2019-11-17 09:01 | ONSHORE | OH | 44090 | WELLINGTON | LORAIN | SURVEY STATION NO. | 260+73 | L-722 | L722-055 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | COUPLING | 2014 | UNKNOWN | PLASTIC |  | OTHER | [8 empty] | SEPARATION | CLASS 3 LOCATION | YES | METHOD2 | 92 |  | NO | NO | [5 empty] | 257000 | 272848.409454416307 | 0 | 0 | 3257 | 5146.230971128608923884514435695538057743 | 10000 | 10616.66962857651 | 0 | 0 | 0 | 0 | 0 | 2.22 | 270257 | 128430.6161682028197191601049868766404199 | 288611.3100541214259238845144356955380577 | 0 | 0 | 1740 | 236 | NO |  |  |  | 76 | 1224 | 100 | 192.619(A)(1) |  | 2016-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 5300 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DOWNSTREAM CUSTOMER- COLUMBLIA GAS OF OHIO |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | OTHER | COUPLING- DRESSER STYLE |  |  |  | YES | [175 empty] | KAMRANROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | PAUL SHAFFER | PAUL SHAFFER | 304-550-4866 | paul_shaffer@tcenergy.com | OPERATIONS TEAM LEADER RECEIVED A CALL FROM COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY REGARDING LOW PRESSURE ALARMS AT WELLINGTON MEASURING STATION 706948 . COLUMBIA OPERATIONS PERSONNEL WERE ON THE SITE AT 09:00 EST AND CONFIRMED THAT THE LOW-PRESSURE ALARM WAS DUE TO A PLASTIC COUPLING SEPARATION ON LINE L-722. LINE L-722, IS CLASSIFIED AS TRANSMISSION THAT IS OPERATED AND MAINTAINED BY COLUMBIA. AT 09:36 EST, THE LEAK WAS ISOLATED, AND THE PIPELINE WAS REMOVED FROM SERVICE. PIPELINE L-722 IS A 4-INCH IN DIAMETER PLASTIC PIPELINE AT THE SITE OF THE INCIDENT WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF XXX PSIG, LOCATED IN LORAIN COUNTY, VILLAGE OF WELLINGTON, OHIO. THE REPAIR WAS COMPLETED BY REPLACING THE FAILED COUPLING AND LINE L-722 WAS RETURNED INTO SERVICE ON NOVEMBER 17, 2019 AT 15:15 EST. APPROXIMATELY 2,000 COH CUSTOMERS LOST NATURAL GAS SERVICE IN LIEU OF THIS INCIDENT AND DURING THE REPAIR INTERVAL OF THE AFFECTED SEGMENT OF LINE L-722. THE FAILED COUPLING WAS PRESERVED AND PROTECTED AS EVIDENCE, THEN SENT TO A LOCAL COLUMBIA OFFICE FOR FURTHER INVESTIGATION. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO. 1264138 AND THE NRC 48-HOUR REPORT NO. 1264285 HAVE BEEN CALLED-IN ON NOVEMBER 17TH AND NOVEMBER 19TH RESPECTIVELY. AFTER COMPLETION OF ROOT CAUSE ANALYSIS, IT WAS DETERMINED THAT THE CAUSAL AND ROOT CAUSE FACTORS OF PIPELINE SEPARATION INDICATE FIRST A LACK OF AWARENESS BY PROJECT TEAM AND FIELD OPERATIONS PERSONNEL TO THE PUBLISHED GUIDELINES FOR THE USE OF MECHANICAL COUPLINGS AS ESTABLISHED BY AND SECOND PRIOR TO THE EXCAVATION, POTENTIAL HAZARDS, HAZARDOUS WORK, OR WORK HAZARDOUS TO THE ENVIRONMENT OR FACILITIES WERE NOT ADEQUATELY IDENTIFIED FOR THE PLANNED PIPELINE REPLACEMENT. IN ORDER TO PREVENT SIMILAR FUTURE EVENTS, MECHANICAL PIPELINE REPAIR TAPPING AND JOINING PROCEDURE SHOULD BE DISTRIBUTED TO PROJECT TEAM AND TO ADEQUATELY IDENTIFY ALL POTENTIAL HAZARDS IN EACH PROJECT TO THE ENVIRONMENT OR FACILITIES , INCORPORATE PRE-JOB PLANNING PROCEDURE AND CHECKLIST PER PROJECT BY PROJECT TEAM.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190131 | 33083 | 2019-12-16 16:36 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2019-11-15 13:26 | 2019 |  |  | 43.1654 | -96.0445 | 1264146 | 2019-11-15 14:12 |  | NATURAL GAS |  | 154 | 38 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | YES |  | 2019-11-15 14:30 | 2019-11-16 00:56 |  |  |  |  | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-15 13:26 | 2019-11-15 14:20 | ONSHORE | IA | 51234 | Not Within a Municipality | SIOUX | MILEPOST | 5.24 | BOYDEN BRANCH LINE | IAB66701 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 |  | 0.154 | 35000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | REPUBLIC | COAL TAR | [28 empty] | 1954 | 1954 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 46 |  | NO | NO | NO |  |  |  |  | 10 | 10.61666962857651 | 100 | 106.1666962857651 | 385 | 608.320209973753280839895013123359580052 | 2000 | 2123.333925715302 | 40000 | 42466.67851430604 | 0 | 0 |  |  | 42495 | 20122.0730523576916779265091863517060367 | 45315.1160159094368908398950131233595801 | [8 empty] | 655 |  | 800 | 192.619(C) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO |  |  |  |  | MANUAL | MANUAL | 33000 | NO | [5 empty] | YES | 2-INCH PIPELINE | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LOCAL SHERIFF CALLED TO REPORT THE INCIDENT AT THE SAME TIME THE CONTROL ROOM DETECTED THE DROP IN PRESSURE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | AGRICULTURE | NO | [5 empty] | YES | 12 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JOHN A GORMLEY | SR CORROSION SPECIALIST - PIPELINE SAFETY | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON NOVEMBER 15, 2019, AT 1326 HOURS, THE SIOUX COUNTY, IOWA, SHERRIFF'S DEPARTMENT REPORTED KNOWN PIPELINE DAMAGE ABOUT 2 MILES SOUTHWEST OF BOYDEN, IOWA (POP ~700). THE EXACT LOCATION IS ON THE BOYDEN 2-INCH BRANCH LINE (IAB66701) AT MILEPOST 5.24. IT IS ASSUMED A FARMER WAS LAYING DRAINAGE TILE IN HIS FIELD WHEN HE PUNCTURED AND COMPLETELY SEVERED THE PIPELINE. PAULLINA SENIOR OPERATIONS AND MAINTENANCE TECHNICIANS ISOLATED THE LEAK AT 1430 HOURS. WHEN ARRIVING AT THE LEAK LOCATION AT 1448 HOURS, NO EQUIPMENT OR PERSONNEL WERE PRESENT. LOCAL LAW ENFORCEMENT FOUND THE EXCAVATOR LATER THAT DAY AFTER INTERVIEWING THE LANDOWNER AND NEIGHBORS. NO ONE CALL FOR THE WORK HAD BEEN MADE. THE BOYDEN, IOWA, #1 TOWN BORDER STATION (737111) LOST SERVICE IMMEDIATELY AFTER THE LINE HIT. TWO FARM TAPS ALSO LOST SERVICE. REPAIR SERVICES WERE MOBILIZED AT 1500 HOURS AND ARRIVED ON SITE AT 1600 HOURS. THE PIPELINE WAS REPAIRED BY REPLACING A CYLINDER OF PIPE USING PRE-TESTED PIPE 43-FEET LONG. SERVICE TO THE TOWN OF BOYDEN WAS RESTORED ON NOVEMBER 16, 2019, AT 0056 HOURS. THE INITIAL NRC REPORT NUMBER IS 1264042 AND THE 48-HOUR FOLLOW-UP IS 1264147.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190132 | 33258 | 2019-12-17 17:02 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-11-18 13:14 | 2019 |  |  | 35.1591 | -88.2205 | 1264245 | 2019-11-18 14:46 |  | NATURAL GAS |  | 116172 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THE STATION WAS OFFLINE AND BEING BYPASSED BY MAINLINE AT TIME OF INCIDENT. | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-11-18 13:14 | 2019-11-18 13:14 | ONSHORE | TN | 38372 | MADDOX | HARDIN | MILEPOST | VENT VALVE | TGP SAVANNAH CS 856 | UNIT #2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1999 |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VENTING THROUGH THE UNIT #2 VENT VALVE (IN PROPER OPEN POSITION) BECAUSE OF COMPRESSOR LOADING VALVE BEING OPENED. | CLASS 2 LOCATION | NO |  | 633 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 232925 | 368033.7270341207349081364829396325459318 | 0 | 0 | 500 | 530.8334814288255 | 1000 | 1061.666962857651 | ESTIMATED COST OF THE INVESTIGATION |  | 234425 | 242186.474088886214195538057742782152231 | 369626.2274784072114081364829396325459318 | [8 empty] | 135 |  | 936 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | COLD FRONT CAUSED SOME INSTRUMENTATION COMPONENTS TO FREEZE. TEMPERATURE WAS APPROXIMATELY 22 DEGREES FAHRENHEIT ON 11/12/19 WHEN THE COMPRESSOR LOADING VALVE OPENED. | [301 empty] | CLAYTON THEDINGER | PIPELINE ENGINEER - CODES AND COMPLIANCE | clayton_thedinger@kindermorgan.com | 713-420-5629 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | DAY OF DISCOVERY: ON 11/18/19, A KM MEASUREMENT TECH ARRIVED AT THE UNMANNED TGP STATION 856 FOR THE PURPOSE OF READING FUEL METER INDEXES. HE NOTICED A GAS RELEASE SOUND UPON EXITING HIS VEHICLE NEAR THE COMPRESSOR BUILDING. THE TECH REPORTED THE ISSUE TO THE OPERATIONS SUPERVISOR AND WAS INSTRUCTED TO TRY TO IDENTIFY THE LEAK. HE IDENTIFIED IT WAS COMING FROM THE BLOWDOWN SILENCER AS THE TECH COULD VISUALLY SEE THE GAS VENTING AND ALSO OBSERVED FROSTING ON THE SILENCER. THE TECH THEN PROCEEDED TO THE CONTROL ROOM AND ULTIMATELY IDENTIFIED THAT THE NORMALLY CLOSED REMOTED OPERATED 4IN COMPRESSOR LOADING VALVE WAS OPEN ON THE UNIT #2 LOAD LINE ALLOWING GAS TO VENT THROUGH THE NORMALLY OPEN COMPRESSOR VENT VALVE. THE TECH PROCEEDED TO CLOSE THE MANUAL BLOCK VALVE ON THE LOAD LINE ASSEMBLY AT 1:36PM TO STOP THE LEAK. THE LEAK STOPPAGE WAS REPORTED TO KM MANAGEMENT AT 1:40PM. AT THE TIME OF THE INCIDENT, IT WAS UNKNOWN THE QUANTITY OF GAS RELEASED BUT ON THE 2:35PM ERL CALL IT WAS DETERMINED TO REPORT TO THE NRC AS A PRECAUTION. IT WAS REPORTED TO THE NRC AT 2:46PM LOCAL TIME WITH THE UNKNOWN AMOUNT. THE REPORT NUMBER WAS 1264245. 48 HOUR UPDATE: DURING INVESTIGATION, IT WAS DETERMINED THAT THE GAS HAD BEEN VENTING THROUGH THE BLOWDOWN SILENCER FOR ABOUT 6 DAYS. THIS WAS REPORTED TO THE NRC (#1264366) ON THE 48 HR UPDATE AT 4:54PM LOCAL TIME ON 11/19/19. INVESTIGATION: DURING INVESTIGATION, IT WAS IDENTIFIED THAT THE UNIT #2 LOAD LINE VALVE OPENED ON 11/12/19 AT 11:43PM. THE LOAD LINE VALVE OPENED AS A RESULT OF FREEZING UP OF MOISTURE IN THE SOLENOID CONTROL BOX. AT STA 856, THE TEMPERATURE ON 11/12/19 WENT BELOW FREEZING AT 4PM AND WAS APPROXIMATELY 22 °F AT THE TIME OF THE EVENT. THIS AREA DOES HAVE WINTERIZATION PROCEDURES AND PLANS IN PLACE AND IS SCHEDULED IN MAXIMO TO BE PERFORMED MONTHLY NOVEMBER THROUGH MARCH. HOWEVER, SINCE THIS OCCURRED MID-MONTH, THE PLAN WAS NOT COMPLETED AT THE TIME OF THE INCIDENT. THE TIMING OF THE EVENT IS VALIDATED BY THE VALVE EVENT LOGS, THE ALARMS, AND THE PRESSURE RISE IN THE UNIT #2 PIPING AT THAT TIME OF THE EVENT. THE PRESSURE ON THE DISCHARGE OF UNIT #2 WHERE THE VENT VALVE IS LOCATED AVERAGED 135 PSI. THIS BACKPRESSURE FLUCTUATED WITH THE MAINLINE LINE PRESSURE AND WAS CREATED BY THE RESTRICTION OF AN ORIFICE PLATE ON THE INLET TO THE SILENCER. THE ORIFICE PLATE ON THE SILENCER IS A DESIGNED PLATE WITH 4 X 1.25" HOLES FOR CUTTING THE PRESSURE GOING INTO THE SILENCER. WHEN CALCULATING GAS LOSS IT WAS ASSUMED THAT THE ORIFICE PLATE ACTED AS 4 INDEPENDENT HOLES. THE TOTAL GAS LOSS CALCULATED WAS 116,172 MCF. THE GAS THAT PRESSURIZED THE UNIT #2 COMPRESSOR CASE ALSO PRESSURIZED THE UNIT #1 CASE. WHEN THE PLC SAW THE CASE PRESSURE ELEVATED ON UNIT #2, IT TRIGGERED THE UNIT TO TRY TO MAINTAIN SEAL OIL PRESSURE TRIGGERING ALARMS AND EVENT STATUSES. OVER THE COURSE OF THE EVENT THERE WERE 3 STATION WARNING CALLOUTS THAT WERE TRIGGERED THROUGH ALARMS ORIGINATING FROM THE LOAD LINE VALVE OPERATING. THESE ALARMS INDICATED ISSUES WITH UNIT 1 AND UNIT 2 IN RELATION TO THE SEAL OIL SYSTEMS. THE TECH RESPONDING TO THE CALLOUTS LOGGED IN REMOTELY TO ASSESS THE SCADA ALARMS. THE TECH VIEWED ONLY THE STATION LEVEL ALARM SCREEN AND UNIT 1A ALARM SCREEN, AND EITHER DIDN'T LOOK AT OR DIDN'T RECOGNIZE THE SIGNIFICANCE OF THE EVENTS. THE TECH ALSO DIDN'T LOG INTO THE UNIT 2A LEVEL MACHINES TO VIEW THE UNIT SPECIFIC ALARM SCREEN. IN ADDITION TO THE 2 EVENTS ON THE NIGHT THE INCIDENT ORIGINATED THERE WAS ALSO A CALLOUT 3 DAYS LATER AGAIN AS A RESULT OF A UNIT 2A ALARM THAT WAS NOT FOLLOWED UP ON. FOLLOW-UP ACTION ITEMS: OPERATIONS HAS CHANGED THE MAXIMO WORK ORDER TO BEGIN WINTERIZATION PLANS IN OCTOBER INSTEAD OF NOVEMBER. ALSO, THE TECH WAS PREVIOUSLY TRAINED ON SCADA AND HOW TO MANAGE ALARMS; HOWEVER AFTER THIS INCIDENT, OPERATIONS HELD RE-TRAINING FOCUSING ON ALARM LOG REVIEW AND ACKNOWLEDGEMENT RESPONSES. THE TECH IN QUESTION HAD OQ REVOKED AND WAS REQUIRED TO RETEST FOR THE OQ TASK.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20190133 | 34260 | 2019-12-18 17:11 | SUPPLEMENTAL FINAL | 31424 | AMERICAN MIDSTREAM (SIGCO INTRASTATE), LLC | BLACK BEAR TRANSMISSION, LLC 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2019-11-04 15:35 | 2019 | CENTRAL | NO | 29.8768 | -89.7604 | 1263070 | 2019-11-04 17:02 | 1263279 | NATURAL GAS |  | 10000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-11-04 17:25 | 2019-12-15 09:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2019-11-04 17:18 | VALVE CLOSURE |  | 2019-11-04 17:25 | 0 | 2019-11-03 15:45 | 2019-11-04 15:35 | ONSHORE | LA | 70085 | Not Within a Municipality | SAINT BERNARD | SURVEY STATION NO. | VERETTE LEVY | 8" CHALMETTE PIPELINE | MARSH TO LEVY SECTION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 78 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.25 | 52000 | API 5L X52M | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1962 | 1962 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 188 |  | NO | NO | [5 empty] | 1800 | 1911.0005331437718 | 0 | 0 | 25000 | 39501.3123359580052493438320209973753281 | 75000 | 79625.022214323825 | 500 | 530.8334814288255 | 0 | 0 |  | 2.5 | 102300 | 62123.3890358959932406824146981627296588 | 121568.1685648544275493438320209973753281 | 0 | 0 | 0 | 0 | NO |  |  |  | 750 | 0.75 | 998 | 192.619(A)(1) |  | 1963-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 26400 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS FOLLOWED THE OPERATIONS AND MAINTENANCE PLAN, AS WELL AS THE CRM UPON SEEING THE CHANGE IN PRESSURE FROM SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  | ,,, | NO | [306 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 346-241-3585 |  | ROBIN ASEVADO | rasevado@3cmidstream.com | 504-681-6925 | KEVIN STANLEY | SR. MANAGER EHS | 346-241-3585 | kstanley@3cmidstream.com | OPERATIONS CONTROL CENTER NOTICED THROUGH SCADA ON SUNDAY, NOVEMBER 3 AT 15:45 THAT THE CHALMETTE PIPELINE WAS EXPERIENCING A DROP IN PRESSURE, ALONG WITH THE VOLUME OF GAS BEING DELIVERED. THEY IMMEDIATELY NOTIFIED THE OPERATIONS MANAGER FOR THE PIPELINE ASSET AND AERIAL PATROL WAS DISPATCHED TO DETERMINE IF THERE WERE VISIBLE SIGNS OF A LEAK. WITH NONE FOUND AND DUE TO THE LATE TIME, OCC CONTINUED TO MONITOR THE LINE THROUGH THE NIGHT. ON MONDAY, NOVEMBER 4, 2019, A HELICOPTER AND BOAT WERE BOTH DISPATCHED AT 0800 TO MADE ADDITIONAL PATROLS SINCE OCC CONTINUED TO SEE THE SAME INDICATIONS WITH THEIR SYSTEM. NO LEAKS WERE FOUND. AT 15:12, AN OFF DUTY OFFICER FOR THE SAINT BERNARD PARISH NOTICED DIRT AND MUD BEING SPRAYED FROM THE GROUND AND CONTACTED THIRD COAST MIDSTREAM OCC. OCC MADE NOTIFICATIONS PER THE CRM AND OPERATIONS RESPONDED TO THE VERETTE LEVY TO SHUT VALVES AND ENSURE THE BYPASS PORTION OF THE PIPELINE WAS NOT UTILIZED UNTIL REPAIRS COULD BE MADE. REPAIRS BEGAN ON DECEMBER 9, 2019 AND WERE COMPLETED ON MONDAY, DECEMBER 16, 2019 BY REPLACING A 24' SECTION OF CARBON STEEL PIPE. THE PIPE WAS DISCOVERED TO HAVE BEEN INSTALLED IN 1963 CROSSING A CONCRETE PIER BEAM (SIMILAR TO A CURB STOP) AND DUE TO THE PIPE BEING IN A MARSH AREA, APPEARED TO HAVE SETTLED, CAUSING THE PIPE TO FAIL. ANALYSIS PERFORMED BY A THIRD PARTY INDICATED SAMPLE MOST LIKELY FAILED BY CRACKING FROM THE OUTSIDE IN DUE TO COMBINATION OF EXTERNAL WALL THINNING FROM CORROSION, CORROSION FATIGUE AND SHEAR OVERLOAD FROM BENDING.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190134 | 33111 | 2019-12-19 12:18 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2019-12-11 03:22 | 2019 |  |  | 32.4742 | -93.5086 | 1266121 | 2019-12-11 12:43 |  | NATURAL GAS |  | 6468 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | VALVE WAS OPENED; NO FURTHER ACTION REQUIRED | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-12-11 03:22 | 2019-12-11 04:00 | ONSHORE | LA | 71037 | HAUGHTON | BOSSIER | MILEPOST | 47+4499 | HAUGHTON COMPRESSOR STATION | SHC 20-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | ESD CONTROL VALVE ACTIVATED PREMATURELY | CLASS 2 LOCATION | NO |  | 383 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 16280 | 25723.2545931758530183727034120734908136 | 70 | 74.31668740003557 | 300 | 318.5000888572953 | 0 | 0 |  |  | 16650 | 17051.5109401754848908923884514435695538 | 26116.0713694331838883727034120734908136 | [8 empty] | 630 |  | 770 | 192.619(A)(3) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [34 empty] | YES | COLD AND OLD O-RINGS | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | DECEMBER 11, 2019 AT 03:22, GAS CONTROL RECEIVED AN ALARM FOR A VENT VALVE OPEN ON ITS SHC 4-6 ESD CONTROL VALVE ACCOMPANIED BY PRESSURE LOSS. WHILE AN OPERATIONS REPRESENTATIVE WAS EN ROUTE TO THE SITE, GAS CONTROL CALLED HIM STATING THAT NEIGHBORS HAD CALLED AND THAT THE POLICE AND FIRE DEPARTMENT WERE RESPONDING. ADDITIONALLY, THE GAS PRESSURE CONTINUED TO FALL. OPERATIONS REPRESENTATIVE CALLED 911 TO LET THEM KNOW HE WAS ON THE WAY TO THE SITE. OPERATIONS REPRESENTATIVE ARRIVED AT APPROXIMATELY 04:00, CLOSED THE POWER GAS THAT CONTROLS THE VALVE, AND MANUALLY CLOSED THE VALVE WHICH HAD OPENED PREMATURELY. HE INFORMED POLICE THAT THE SITE WAS SECURE. THE VALVE WAS SECURE AT 04:15. OPERATIONS REPRESENTATIVE ALSO CONTACTED GAS CONTROL TO VERIFY THE STATION PRESSURE WAS RETURNING TO NORMAL PRESSURE. A NEW REPAIR KIT WAS INSTALLED ON THE ESD CONTROL VALVE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20190136 | 33135 | 2019-12-26 10:24 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-12-11 21:52 | 2019 |  |  | 38.4953 | -81.3122 | 1266172 | 2019-12-11 21:54 |  | NATURAL GAS |  | 7890 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 |  | NO | THIS WAS AN ACTIVATION OF A COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM (ESD). | [6 empty] | NO |  |  |  |  | NO | [6 empty] | 0 | 2019-12-11 14:05 | 2019-12-11 14:05 | ONSHORE | WV | 25045 | CLENDENIN | KANAWHA | MILEPOST | CLENDENIN CS | CLENDENIN COMPRESSOR STATION | CLENDENIN COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN |  | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL ACTIVATION OF THE COMPRESSOR STATION EMERGENCY SHUTDOWN SYSTEM (ESD). | CLASS 1 LOCATION | NO |  | 785 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 0 | 0 | 18857 | 29795.0498687664041994750656167979002625 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 18857 | 19549.908136482939632545931758530183727 | 29795.0498687664041994750656167979002625 | [8 empty] | 673 |  | 1000 | 192.619(A)(1) |  |  |  | PRESSURE DID NOT EXCEED MAOP | NO | [22 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM DID NOT CONTRIBUTE TO THE CAUSE OF THE INCIDENT. THE KNOWN CAUSE WAS THE ACTIVATION OF THE ESD SYSTEM. THE CONTROL ROOM WAS IN COMMUNICATION WITH THE COMPRESSOR STATION DURING THE INCIDENT AND WAS ABLE TO ASSIST IN PROVIDING DATA/INFORMATION, FUNCTIONING NORMALLY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | A TRIGGER VALVE ON AN AIR SUPPLY WAS FROZEN WHICH CAUSED THE ESD TO ACTIVATE. | [161 empty] | CHRIS LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@tcenergy.com | 304-545-4350 | 304-722-8530 |  |  |  | GEORGE HAMATY | MANAGER - US REGULATORY COMPLIANCE - EAST | 304-357-3728 | george_hamaty@tcenergy.com | AN UNINTENTIONAL RELEASE OF NATURAL GAS OCCURRED WHEN THE EMERGENCY SHUTDOWN SYSTEM (ESD) AT CLENDENIN CS ACTIVATED. THE EVENT RELEASED A CALCULATED VOLUME OF 7890 MCF OF NATURAL GAS, EXCEEDING PHMSA'S REPORTABLE QUANTITY OF 3000 MCF. THE ESD SYSTEM RELEASED GAS, AS DESIGNED, THROUGH VARIOUS BLOW-OFF STACKS AROUND THE STATION. ONE OF THE BLOCK VALVES (24") ON THE ESD SYSTEM FAILED TO CLOSE AND REMAINED OPEN FOR APPROXIMATELY 21 MINUTES. THE STATION WAS MANNED AT THE TIME OF THE INCIDENT. NO FIRES, DEATHS, INJURIES, EVACUATIONS, OR ROAD CLOSURES OCCURRED AS RESULT OF THE INCIDENT. AN INVESTIGATION OF THE PROBABLE CAUSE OF THE ESD REVEALED A TRIGGER VALVE, ON AN AIR SUPPLY, WHICH CONTROLS THE SYSTEM, WAS FROZEN WHICH CAUSING THE ESD TO ACTIVATE. IT WAS DETERMINED A PROGRAMMING ERROR CAUSED THE BLOCK VALVE TO REMAIN OPEN FOR THE ADDITIONAL TIME. LOGIC WAS ADDED TO THE PROGRAMMABLE LOGIC CONTROLLER (PLC) TO ALLOW THE VALVE TO CLOSE CORRECTLY FOR FUTURE ESD ACTIVATIONS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200001 | 34196 | 2020-01-03 13:18 | SUPPLEMENTAL FINAL | 1007 | TALLGRASS INTERSTATE GAS TRANSMISSION, LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2019-11-30 13:05 | 2019 | CENTRAL | NO | 41.0755 | -103.6199 | 1265633 | 2019-12-05 15:19 | 1265936 | NATURAL GAS |  | 4034 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2019-12-01 10:55 | 2019-12-01 10:55 | ONSHORE | NE | 69145 | Not Within a Municipality | KIMBALL COUNTY | MILEPOST | COMPRESSOR | KIMBALL COMPRESSOR STATION | KIMBALL COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | PNEUMATIC ACTUATOR | 2004 | 2004 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER O-RING | OTHER | [8 empty] | RELEASE OF NATURAL GAS. | CLASS 1 LOCATION | NO |  | 418 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 9669 | 15277.5275590551181102362204724409448819 | 0 | 0 | 410 | 435.28345477163691 | 215 | 228.258397014394965 | LABOR AND MATERIALS. | 2.397 | 10294 | 10317.0205904042515403543307086614173228 | 15941.0694108411499852362204724409448819 | 0 | 0 | 0 | 0 | NO |  |  |  | 633 | 35000 | 1170 | 192.619(A)(1) |  | 1997-07-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES |  |  | YES | [16 empty] | YES | [136 empty] | YES | [36 empty] | KAYLA ROBINSON | COMPLIANCE COORDINATOR | kayla.robinson@tallgrassenergylp.com | 303-763-3464 |  |  |  |  | KAYLA ROBINSON | COMPLIANCE COORDINATOR | 303-763-3464 | kayla.robinson@tallgrassenergylp.com | ON 11/30/2019 KIMBALL COMPRESSOR STATION HAD A RELEASE OF NATURAL GAS DUE TO HIGH WINDS AND HEAVY BLOWING SNOW. THERE WAS A LOSS OF COMMERCIAL POWER, FOLLOWED BY LOSS OF THE BACKUP UPS, RESULTING IN AN ESD AT THE STATION. AS THE ESD OCCURRED, A PNEUMATIC VALVE DID NOT TRANSFER TO THE CLOSED POSITION AND VENTED GAS THROUGH A 2 INCH ESD LINE. THE VALVE WAS CLOSED AT 10:55 AM MST ON SUNDAY DECEMBER 1, 2019. SECOND NRC REPORT (48 HOUR UPDATE) FILED ON 12/9/2019, NRC# 1265936
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200002 | 34741 | 2020-01-08 11:34 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2019-12-10 13:39 | 2019 | EASTERN | NO | 40.5078 | -83.8219 | 1266049 | 2019-12-10 17:49 | 1266185 | NATURAL GAS |  | 2064 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-12 18:45 | 2020-12-08 10:00 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-10 14:23 | 2019-12-10 15:45 | ONSHORE | OH | 43310 | BELL CENTER | LOGAN | MILEPOST | 704+97 | DAYTON LAKE | MS704997 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 4 | NO | 0.236 |  | UNKNOWN | SINGLE SAW |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 110 |  | NO | NO | [5 empty] | 10000 | 10616.66962857651 | 0 | 0 | 4396 | 6945.91076115485564304461942257217847769 | 1780000 | 1889767.19388661878 | 0 | 0 | 0 | 0 |  | 2.13 | 1794396 | 842934.1100253879601312335958005249343832 | 1907329.77427635014564304461942257217848 | 1 | 0 | 1 | 1 | NO |  |  |  | 220 | 1690 | 300 | OTHER | 192.557 | 1973-04-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | DOWNSTREAM CUSTOMER- VECTERAN |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | YES | 60 |  | PASSENGER CAR | ROADWAY | 18 | YES |  |  |  | YES | INSIDE A BULDING | [233 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | [5 empty] | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON DECEMBER 10, 2019, AT 14:23 EASTERN STANDARD TIME (EST), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) GAS CONTROLLER RECEIVED A CALL FROM VECTREN, THE LOCAL DISTRIBUTION COMPANY (LDC), REGARDING LOW PRESSURE INDICATIONS AT DAYTON LAKE DELIVERY MEASURING STATION (MS) 704997. AN OPERATIONS PERSONNEL WAS DISPATCHED AND ARRIVED ON SITE AT 15:45 EST WHERE HE CONFIRMED THAT THE LOW-PRESSURE ALARM WAS DUE TO A CAR ACCIDENT. A CAR DAMAGED THE MS BUILDING AND INITIATED AN UNINTENTIONAL NATURAL GAS RELEASE FROM COLUMBIA FACILITY (MS704997). THE DRIVER WAS SENT TO A NEARBY HOSPITAL JUST FOR ROUTINE CHECK-UP AND WAS RELEASED FROM HOSPITAL ON THE SAME DAY. AT 18:45 EST, THE LEAK WAS ISOLATED, AND THE FACILITY WAS REMOVED FROM SERVICE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1266049 AND THE NRC 48-HOUR REPORT NO. 1266185 HAVE BEEN CALLED-IN ON DECEMBER 10TH AND DECEMBER12TH RESPECTIVELY . THE CONSTRUCTION OF THE NEW MS FACILITY HAS BEEN COMPETED, COMMISSIONED AND WAS READY TO START THE FLOW AS OF DECEMBER 8TH, 2020. THIS FLOW WILL START ONCE THE DOWNSTREAM LDC COMPLETES THEIR TIE-IN TO THE MS. TO AVOID ANY FUTURE SIMILAR VEHICULAR DAMAGE TO THE NEWLY FACILITY FROM RE-OCCURRING , THE NEW MS WAS CONSTRUCTED ABOUT 100 FEET OFF OF THE ROAD.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200003 | 33358 | 2020-01-09 12:54 | SUPPLEMENTAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-12-12 12:15 | 2019 | CENTRAL | NO | 29.7477 | -94.9133 | 1266544 | 2019-12-16 10:35 | 1266704 | NATURAL GAS |  | 30 | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-12 14:00 | 2020-02-05 07:45 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-12 12:15 | 2019-12-12 12:15 | ONSHORE | TX | 77523 | Not Within a Municipality | CHAMBERS | MILEPOST | MP 4.20 | INDEX 128-18 | CEDAR BAYOU TANK SITE REGULATOR | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 | YES | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 193 |  | NO | NO | [5 empty] | 0 | 0 | 2 | 2.123333925715302 | 66 | 104.283464566929133858267716535433070866 | 126165 | 133945.212368935538415 | 904 | 959.746934423316504 | 0 | 0 |  | 2.1935 | 127137 | 59584.2632100012375497874015748031496063 | 135011.3661018514993548582677165354330709 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 930 | 780 | 192.619(A)(1) |  | 1970-08-11 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | NO | [5 empty] | YES | THE FAILURE WAS ON A REGULATOR VALVE | YES |  |  |  |  | YES | THE FAILURE WAS ON A REGULATOR VALVE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING UNDER MAOP AND CONTROLLERS WERE NOT MAKING ANY CHANGES TO PIPELINE CONDITIONS. NO CHANGES WERE MADE TO EITHER SETPOINT OR HORSEPOWER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [17 empty] | YES | AGE OF THE STEM SEALS | [161 empty] | KRISTIN VAN DER LAAN | MANAGER - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODE AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 12:00 PM ON DECEMBER 12, 2019, A KINDER MORGAN TEXAS PIPELINE LLC (KMTP) EMPLOYEE ARRIVED AT THE KMTP CEDAR BAYOU TANK SITE TO PERFORM REGULARLY SCHEDULED OPERATIONS AND MAINTENANCE WORK. AT APPROXIMATELY 12:15 PM, THE EMPLOYEE NOTICED NATURAL GAS LEAKING OUT OF A BREATHER FITTING ON A COMPONENT OF THE ACTUATOR ON THE 10-INCH PRIMARY REGULATOR. THE EMPLOYEE CALLED HIS SUPERVISOR WHO THEN INITIATED THE INTERNAL EMERGENCY RESPONSE LINE (ERL) NOTIFICATIONS PER COMPANY PROCEDURES TO DISCUSS THE NATURAL GAS RELEASE EVENT. DURING THE CALL IT WAS DETERMINED THAT THE AMOUNT OF GAS LOSS DID NOT MEET THE INCIDENT REPORTING CRITERIA AND REPAIR COSTS WERE NOT EXPECTED TO REACH THE $50,000 REPORTING THRESHOLD. THERE WERE NO INJURIES OR PROPERTY DAMAGE ASSOCIATED WITH THE LEAK. IN ORDER TO SECURE THE LOCATION, THE EMPLOYEE CHANGED PRIMARY REGULATION FROM THE LEAKING REGULATOR TO A SECONDARY REGULATOR IN ORDER TO CONTINUE SUPPLYING GAS TO DOWNSTREAM CUSTOMERS. ONCE THE SECONDARY REGULATOR PICKED UP THE LOAD, THE UPSTREAM MONITOR VALVE AND DOWNSTREAM ISOLATION VALVES ON THE LEAKING PRIMARY REGULATOR RUN WERE SHUT AND SECURED USING COMPANY LOCKOUT/TAGOUT (LOTO) PROCEDURES ISOLATING THE PRIMARY REGULATOR RUN. THE PRIMARY REGULATOR RUN WAS THEN ALLOWED TO BLEED OUT TO ATMOSPHERE THROUGH THE BREATHER FITTING AND BODY BLEED ON THE PRIMARY REGULATOR. ON DECEMBER 16 AT APPROXIMATELY 10:00 AM, AFTER FURTHER INVESTIGATION AND REPAIR EVALUATION, FIELD OPERATIONS DETERMINED THAT THE COSTS OF REPAIR WOULD LIKELY EXCEED THE $50,000 REPORTABLE THRESHOLD. THE COSTS OF ESTIMATED REPAIRS HAD INCREASED BECAUSE THE EXCAVATION COSTS TO EXCAVATE THE BELOWGROUND REGULATOR EXCEEDED THE ORIGINAL ESTIMATE. A FOLLOW-UP ERL NOTIFICATION WAS INITIATED AND DURING THE CALL IT WAS DETERMINED THAT NOTIFICATION TO THE NRC AND RAILROAD COMMISSION OF TEXAS SAFETY DIVISION WAS REQUIRED. TRRC INCIDENT REPORT 2105 48 HOUR NRC REPORT 1266704 INITIALLY IT WAS DETERMINED THAT THE LEAKAGE WAS CAUSED BY BROKEN STEM SEALS ON THE PRIMARY REGULATOR. AFTER REPLACING THE STEM SEALS THERE WAS STILL SOME SMALL LEAKAGE DETECTED. AFTER CONSULTING WITH THE VALVE SERVICE COMPANY AND FURTHER INSPECTING THE VALVE STEM, IT WAS DETERMINED THAT THE VALVE STEM NEEDED TO BE REPLACED. THE NEW VALVE STEM WAS REPLACED ON FEBRUARY 3, 2020 AND AFTER PURGING, PACKING, AND OPERATING THE REGULATOR IT WAS CONFIRMED THAT NO LEAKAGE REMAINED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200004 | 33431 | 2020-01-09 13:30 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2019-12-17 16:05 | 2019 | CENTRAL | NO | 27.2561 | -98.9003 | 1266709 | 2019-12-17 21:22 | 1266770 | NATURAL GAS |  | 6156 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-17 16:05 | 2019-12-17 16:40 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-17 16:40 | 2019-12-17 16:40 | ONSHORE | TX | 78361 | Not Within a Municipality | JIM HOGG | MILEPOST | 0.0 + 0.0 | THOMPSONVILLE TO PRAIRIE LEA SYSTEM | 3017 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2007 | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 581 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 14159 | 22371.9632545931758530183727034120734908 | 1400 | 1486.3337480007114 | 0 | 0 | 0 | 0 |  | 2.3 | 15559 | 15334.9917393034237128608923884514435696 | 23858.2970025938872530183727034120734908 | 0 | 0 | 0 | 0 | NO |  |  |  | 674.24 | 0 | 1100 | 192.619(A)(1) |  | 1991-11-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOLS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [23 empty] | YES | [167 empty] | CHRISTOPHER PALAFOX | REGULATORY COMPLIANCE SPECIALIST | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER-INTRASTATE REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON DECEMBER 17, 2019 AT APPROXIMATELY 16:05 HRS., ENERGY TRANSFER EXPERIENCED A GAS RELEASE ON THE ESD SYSTEM ON A REGULATED CLASS 1 TRANSMISSION LINE, THE 3017 THOMPSONVILLE TO PRAIRIE LEA SYSTEM 24 INCH PIPELINE INSIDE THE THOMPSONVILLE COMPRESSOR STATION. THE COMPRESSOR STATION IS LOCATED IN JIM HOGG COUNTY 14 MILES SOUTHWEST OF HEBBRONVILLE, TX. GAS CONTROL OBSERVED AN ESD VALVE POSITION FAULT AND NOTIFIED OPERATIONS. OPERATIONS PERSONNEL WERE DISPATCHED TO INVESTIGATE AND WHEN THEY ARRIVED ON LOCATION THEY FOUND THE BLOW DOWN VALVE WAS OPENED, RELEASING GAS. AT APPROXIMATELY 16:40 HRS., THE MANUAL VALVE UNDERNEATH THE AUTOMATED BLOW DOWN VALVE WAS CLOSED, SECURING THE GAS RELEASE. ONCE THE ESD WAS RESET, OPERATIONS PERSONNEL NOTICED A 1/4 INCH RELIEF VALVE FOR THE SUPPLY TO THE BETTIS ESD ACTUATOR WAS LEAKING. THE LEAK, OVER TIME, DID NOT PROVIDE AMPLE POWER GAS TO THE ACTUATOR WHICH TRIGGERED THE ESD WHICH THEN CAUSED THE BLOW DOWN VALVE TO OPEN. OPERATIONS PERSONNEL REPLACED THE 1/4 INCH RELIEF VALVE. AT APPROXIMATELY 16:40 HRS. ON DECEMBER 17, 2019 THE SYSTEM WAS BACK IN OPERATION. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON DECEMBER 17, 2019, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1266709) AT 21:22 HRS. AND TO THE TXRRC (INCIDENT#2106) AT 21:45 HRS. A 48 HOUR NRC UPDATE WAS MADE ON DECEMBER 18, 2019 AT 13:40 HRS. (NRC#1266770). AFTER CLOSER INSPECTION AND REACHING OUT TO GENERANT VALVE MANUFACTURE FOR FAILURE ANALYSIS, IT WAS FOUND THAT SMALL PAINT CHIPS WERE ON THE SEATING AREA OF THE VALVE DUE TO PAINT OVER SPRAYING ON THE HEADER PIPING. THE VALVE WAS NOT COMPLETELY COVERED WITH PLASTIC WRAP AND TAPED OFF, ALLOWING PAINT PARTICLES TO BE SPRAYED ONTO THE BACKSIDE OF THE RELIEF VALVE NOZZLE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200005 | 33574 | 2020-01-17 22:23 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2019-12-20 05:30 | 2019 | EASTERN | NO | 42.7869 | -82.531 | 1266902 | 2019-12-20 10:21 |  | NATURAL GAS |  | 0 | 67 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2019-12-20 05:30 | 2019-12-28 20:00 |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-20 05:30 | 2019-12-20 05:30 | ONSHORE | MI | 48054 | EAST CHINA | ST. CLAIR | MILEPOST | DEHY | BELLE RIVER COMPRESSOR STATION | BELLE RIVER DEHY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2001 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | REBOILER BURNER TUBE HAD A WELD DEFECT. THE REBOILER BURNER TUBE ALLOWS THE GLYCOL TO BE HEATED FOR DEHYDRATION. WHEN THE REBOILER TUBE FAILED IT RELEASED GLYCOL AND THE GLYCOL CAUGHT FIRE. | CLASS 1 LOCATION | NO |  | 478 |  | NO | NO | [5 empty] | 0 | 0 | 177 | 187.915052425804227 | 0 | 0 | 150000 | 159250.04442864765 | 5000 | 5308.334814288255 | 0 | 0 |  | 2.6418 | 155177 | 72679.755375866314863 | 164746.294295361709227 | 0 | 0 | 0 | 0 | NO |  |  |  | 1000 | 76.08 | 1200 | 192.619(A)(2) |  | 2001-11-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 80 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM RESPONDED APPROPRIATE AND TIMELY TO THE ALARMS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | REBOILER BURNER TUBE HAD A WELD DEFECT. THE REBOILER BURNER TUBE ALLOWS THE GLYCOL TO BE HEATED FOR DEHYDRATION. WHEN THE REBOILER TUBE FAILED IT RELEASED GLYCOL AND THE GLYCOL CAUGHT FIRE. |  |  |  | YES | [174 empty] | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | ON DECEMBER 20, 2019 AT 05:30, THE LOCAL ONSITE PERSONNEL IDENTIFIED A FIRE IN THE REBOILER UNIT OF THE DEHY AND SHORTLY AFTER IT WAS CONFIRMED BY GAS CONTROL. GAS CONTROL MADE THE APPROPRIATE NOTIFICATIONS. THE NATIONAL RESPONSE CENTER AND THE MICHIGAN PUBLIC SERVICE COMMISSION WERE NOTIFIED. THE UNIT WAS SHUT DOWN AND FIRE WAS EXTINGUISHED. THERE WAS NO IMPACT TO GAS SUPPLY TO CUSTOMERS. THE EXTENT OF THE DAMAGE WAS ASSESSED. THE DEHY ALARM HISTORY AND OPERATIONAL DATA WAS EVALUATED FOR THE INITIAL ROOT CAUSE ANALYSIS. ON DECEMBER 21, 2019, THE TUBE BUNDLE WAS REMOVED, AND AN INSPECTION WAS COMPLETED. IT WAS DETERMINED THAT THE REBOILER BURNER TUBE HAD A WELD DEFECT. THE REBOILER BURNER TUBE ALLOWS THE GLYCOL TO BE HEATED FOR DEHYDRATION. WHEN THE REBOILER TUBE FAILED IT RELEASED GLYCOL AND THE GLYCOL CAUGHT FIRE. IT WAS DETERMINED THAT THE BUNDLE NEEDED TO BE REPLACED. ON DECEMBER 26, 2019, THE BURNER ASSEMBLY WAS INSTALLED AND ALIGNED INSIDE OF FIRE TUBES. THE FIRE TUBES WERE LEAK CHECKED OVERNIGHT. ON DECEMBER 26, 2019, THE VESSEL HEAD WAS INSTALLED AND LEAK CHECKED. ADDITIONALLY, THE BURNER ASSEMBLY, EXHAUST STACK, BURNER BOX, FUEL LINE AND TEG WERE INSTALLED AND REFILLED. ON DECEMBER 27, 2019, THE REBOILER WAS REFILLED WITH GLYCOL. ON DECEMBER 28, 2019, ALL REPAIR WORK WAS COMPLETED ON THE BELLE RIVER DEHY. THE UNIT WAS BROUGHT ONLINE AT 16:30 AND WAS RUNNING CONTINUOUSLY. THE REBOILER TEMPERATURE WAS INITIAL HELD AT 300 DEGREES F AND BEING RAISED BY 25 DEGREES PER 1/2 HOUR. WE WERE FLOWING 3 MMCF/HR OF GAS THROUGH IT. ONCE IT REACHED FULL OPERATING TEMPERATURE OF 360 DEGREES F (AT APPROXIMATELY 20:00), IT RAN FOR A 24-HOUR TEST PERIOD. TEST PERIOD OF 24-HOURS WAS SUCCESSFULLY AND WAS AVAILABLE FOR GAS CONTROL FOR FULL USE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200006 | 34797 | 2020-01-21 19:26 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2019-12-22 23:49 | 2019 | CENTRAL | NO | 41.3572 | -92.0577 | 1267113 | 2019-12-23 01:19 | 1267191 | NATURAL GAS |  | 22510 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY UNIT #14 WAS SHUTDOWN TEMPORARILY |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2019-12-23 00:38 | 2019-12-23 00:38 | ONSHORE | IA | 52231 | Not Within a Municipality | KEOKUK | SURVEY STATION NO. | 3612943 | COMPRESSOR STATION 109 HARPER | AMARILLO #4 LINE (108 TO 109) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1984 | 1984 | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS RELEASED TO ATMOSPHERE THROUGH UNIT #14 8-INCH VENT VALVE ONCE THERE WAS NO CONTROL SIGNAL FROM PLC TO COMMAND THE VENT VALVE TO REMAIN CLOSED; | CLASS 1 LOCATION | NO |  | 663 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 52899 | 83583.1968503937007874015748031496062992 | 1520 | 1613.73378354362952 | 585 | 621.075173271725835 | 0 | 0 |  | 2.35 | 55004 | 55828.7073957256136761023622047244094488 | 85818.0058072090561424015748031496062992 | 0 | 0 | 0 | 0 | NO |  |  |  | 647 | 220000 | 712 | 192.619(C) |  | 1960-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NEARBY PUBLIC NOTIFIED NGPL GAS CONTROL OF LOUD NOISE (NATURAL GAS RELEASE); | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [27 empty] | YES | [159 empty] | YES | [6 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253592 | MICHAEL BOHANNAN | mike_bohannan@kindermorgan.com | 3197282208 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | NRC REPORT #1267113 AND NRC 48-HOUR UPDATE REPORT #1267191: 23:49-HOUR, 12/22/2019, RESIDENTS LIVING NEAR NGPL STATION 109 CALLED NGPL GAS CONTROL REPORTING A LOUD NOISE. 23:56-HOUR, 12/22/2019, NGPL GAS CONTROL STAFF CONTACTED NGPL ON-CALL STAFF. 00:38-HOUR, 12/23/2019, NGPL STAFF ARRIVED AT STATION 109, SAFELY ENTERED THE AREA AND FOUND NATURAL GAS RELEASING TO ATMOSPHERE FROM THE 8-INCH VENT VALVE ASSOCIATED WITH UNIT #14 THEREBY CONFIRMING THE INCIDENT. NGPL STAFF IMMEDIATELY CLOSED TWO MANIFOLD VALVES SERVING UNIT #14 TO TERMINATE THE NATURAL GAS RELEASE. 01:30-HOUR NGPL STAFF SPECIALIST ARRIVED ON SITE TO BEGIN INVESTIGATION OF THE INCIDENT AND BEGIN SUBSEQUENT REPAIRS AS NEEDED. INVESTIGATION OF THE INCIDENT FOUND THE UNIT #14 PLC ELECTRONIC CARD CONTROLLING SIGNAL OUT DISTRIBUTION HAD FAILED. WHEN THE PLC ELECTRONIC CARD SIGNAL OUT WAS NO LONGER AVAILABLE; THERE WAS NO SIGNAL COMMANDING THE VENT VALVE TO REMAIN IN THE CLOSED POSITION THEREFORE THIS VALVE OPENED AND RELEASED NATURAL GAS. BY DESIGN, WITH NO SIGNAL RECEIVED FROM THE PCL ELECTRONIC SIGNAL OUT DISTRIBUTION CARD, UNIT #14 CEASED RUNNING. HOWEVER THE MANIFOLD VALVES REMAINED OPEN IN THEIR RESPECTIVE POSITION AS LAST COMMANDED BY THE PLC. WITH FAILURE OF THE PLC ELECTRONIC SIGNAL OUT DISTRIBUTION CARD, THE PLC WAS UNABLE TO COMMAND THE MANIFOLD VALVES TO PROPER CLOSED POSITION WHICH WOULD HAVE RETAINED THE UNIT BLOW DOWN TO A TYPICAL NON-REPORTABLE VOLUME. 2:45-HOUR, NECESSARY REPAIRS WERE COMPLETED WHICH INCLUDED REPLACING THE PLC ELECTRONIC SIGNAL OUT DISTRIBUTION CARD AND FOLLOWING GENERAL INTEGRITY INSPECTION, UNIT #14 WAS AVAILABLE FOR SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200007 | 35106 | 2020-01-30 13:00 | SUPPLEMENTAL FINAL | 2731 | CHEVRON PIPE LINE CO | 1400 SMITH STREET | HOUSTON | TX | 77002 | 2019-12-31 14:50 | 2019 | CENTRAL | NO | 29.6655 | -91.2547 | 1267695 | 2019-12-31 16:11 |  | NATURAL GAS |  | 173.3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-01-01 | VALVE CLOSURE |  | 2020-01-01 | 0 | 2019-12-31 15:50 | 2019-12-31 15:50 | ONSHORE | LA | 77563 | BAYOU VISTA | ST. MARY | MILEPOST | MP 1.3 | FLOODWAY SYSTEM | LAL13321A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.562 | 52000 | X60 ERW | OTHER | THIS IS A DEAD LEG SCHEDULED FOR ABANDONMENT. | UNKNOWN | OTHER | CEMENT | NO | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 330 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1603 | 2532.824146981627296587926509186351706037 | 320000 | 339733.42811444832 | 0 | 0 | 307035 | 325968.915940998874785 | ENLINK INVOICE TO CHEVRON | 9.25 | 628638 | 295344.2811526445287765485564304461942257 | 668235.168202428822081587926509186351706 | 0 | 0 | 0 | 0 | NO |  |  |  | 850 | 0 | 1404 | OTHER | THIS IS A DEAD LEG THAT IS SCHEDULED FOR ABANDONMENT | 2001-05-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1500 | NO | [5 empty] | YES | THIS IS 1500 FT. OF PIPE THAT IS A DEAD LEG AND SCHEDULED FOR ABANDONMENT. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | LOCALIZED PITTING |  |  |  |  | YES | [5 empty] | YES |  |  |  | YES | YES | [12 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [20 empty] | YES | [42 empty] | GARRETT PARKER | SENIOR REGULATORY SPECIALIST | parkerg@chevron.com | 8328544596 |  |  |  |  | GARRETT S. PARKER | SENIOR REGULATORY SPECIALIST | 8328544596 | parkerg@chevron.com | AT APPROXIMATELY 1450 CDT A PROPERTY OWNER NOTIFIED CHEVRON PIPE LINE CONTROL CENTER OF BUBBLES IN A SHALLOW DITCH. CHEVRON PIPE LINE ROUTED AN EMPLOYEE TO INVESTIGATE WHERE THEY FOUND A LEAK HAD OCCURRED ON THE 30" FLOODWAY TRUNKLINE. THIS IS DEAD LEG LINE THAT THE LEAK OCCURRED ON THAT WAS SCHEDULED FOR ABANDONMENT IN 2021 AND CHEVRON PIPE LINE IS EVALUATING HOW TO MOVE SCHEDULE UP TO ABANDON. AFTER DIGGING UP THE LINE TO EVALUATE AND REPAIR IT WAS FOUND THAT INTERNAL CORROSION WAS A CONTRIBUTING FACTOR TO THE RELEASE. IN DECEMBER 2020 THIS LINE WAS FLUSHED AND WASHED TO PROPERLY ABANDON THIS ASSET PER REGULATIONS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200008 | 33339 | 2020-02-03 15:32 | SUPPLEMENTAL FINAL | 32166 | SEMGAS, L.P. | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-01-08 11:40 | 2020 | CENTRAL | NO | 36.658 | -98.7529 | 1268323 | 2020-01-09 17:06 | 1268361 | NATURAL GAS |  | 1078 | 1004 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-01-08 11:40 | 2020-01-14 17:38 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-01-08 11:40 | VALVE CLOSURE |  | 2020-01-08 11:40 | 0 | 2020-01-08 11:40 | 2020-01-08 11:40 | ONSHORE | OK | 73746 | HOPETON | WOODS | SURVEY STATION NO. | 3657.5-3706.8 | ENABLE RESIDUE 16 INCH | ROSE VALLEY ENABLE RESIDUE SALES LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 16 |  | 0.25 | 65000 | API-5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | PARAGON | EPOXY |  | YES | [26 empty] | 2014 | 2014 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 385 |  | NO | NO | [5 empty] | 5000 | 5202.473221283635 | 2149 | 2236.022990507706323 | 2307 | 4049.020408163265306122448979591836734694 | 53650 | 55822.53766437340355 | 0 | 0 | 0 | 0 |  | 2.14 | 63106 | 30565.0945641789007300670553935860058309 | 67310.0542843280101791224489795918367347 | 0 | 0 | 0 | 0 | NO |  |  |  | 880 | 0 | 1216 | 192.619(A)(1) |  | 2014-06-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 11035 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | YES | YES | [13 empty] | YES | MANUFACTURE SEAM DEFECT | [13 empty] | YES | MANUFACTURE SEAM DEFECT | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [44 empty] | YES | [18 empty] | CHRIS PALAFOX | SPECIALIST REGULATORY COMPLIANCE | christopher.palafox@energytransfer.com | 7138984464 |  |  |  |  | CHRIS KRESTA | MANAGER - INTRASTATE REGULATORY COMPLIANCE | 7139897077 | chris.kresta@energytransfer.com | ON JANUARY 7, 2020, AT APPROXIMATELY 11:30 HRS, SEMGAS EXPERIENCED A GAS LEAK ON A REGULATED CLASS 1 TRANSMISSION LINE, THE ENABLE RESIDUE 16 INCH ON THE ROSE VALLEY PLANT SALES PIPELINE. THIS PIPELINE IS LOCATED IN WOODS COUNTY, 11 MILES SOUTHWEST OF ALVA, OKLAHOMA. OPERATIONS PERSONNEL WAS CONDUCTING A PIPELINE LEAK DETECTION SURVEY IN THE AREA AND DETECTED A HIGH HYDROCARBON LEL READING AND NOTICED BARE VEGETATION IN THE AREA. OPERATIONS PERSONNEL NOTIFIED THEIR SUPERVISOR OF A POTENTIAL LEAK. AT APPROXIMATELY 11:40 HRS, OPERATIONS PERSONNEL CLOSED THE UPSTREAM AND DOWNSTREAM BLOCK VALVES TO ISOLATED THE POTENTIAL LEAK AND BEGAN TO REDUCE THE PRESSURE. ON JANUARY 8, 2020 A CONTRACT CREW BEGAN EXCAVATION OF THE PIPELINE. ONCE THE PIPELINE WAS EXPOSED, OPERATIONS PERSONNEL DISCOVERED A PINHOLE LEAK ON THE PIPELINE'S LONGITUDINAL SEAM. A TOTAL OF 51 FEET OF PIPE WAS REMOVED AND THE AFFECTED PIPE SEGMENT WAS SENT TO THE LAB FOR ANALYSIS. THE 51 FEET OF PIPE WAS REPLACED WITH NEW PIPE TO PREVENT OTHER LEAKS FROM OCCURRING. ON JANUARY 14, 2020 AT APPROXIMATELY 17:38 HRS, THE PIPELINE WAS PUT BACK INTO SERVICE. THIS PIPELINE IS UNDER THE JURISDICTION OF THE OKLAHOMA CORPORATION COMMISSION. ON JANUARY 9, 2020, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1268323) AT 17:06 HRS. AND TO THE OCC AT 17:10 HRS. THIS INCIDENT BECAME A REPORTABLE INCIDENT ONCE THE ESTIMATED REPAIR COST WENT OVER THE $50,000.00 LIMIT. A 48 HOUR NRC UPDATE WAS MADE ON JANUARY 10, 2020 AT 11:21 HRS. (NRC#1268361) ON FEBRUARY 7, 2020, LAB RESULTS CONFIRMED THE LEAK WAS DUE TO MANUFACTURER'S DEFECT IN THE PIPELINE'S LONGITUDINAL SEAM WELD. FURTHER CONSIDERATIONS WILL BE MADE FOR FUTURE ILI ASSESSMENTS IN ORDER TO DETERMINE THE OVERALL CONDITION OF THE REMAINING PIPE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200009 | 36777 | 2020-02-12 13:30 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2020-01-17 10:39 | 2020 | CENTRAL | NO | 29.4821 | -91.0514 | 1268930 | 2020-01-17 10:58 | 1269061 | NATURAL GAS |  | 668 | 2791.87 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK SUSPECTED ON TAP VALVE, CLASS 1, NO NEARBY STRUCTURES, NON-HAZARDOUS |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | MINOR LEAK ON TAP VALVE |  | OPERATIONAL CONTROL | MINOR LEAK ON TAP VALVE |  | 0 | 2020-01-09 10:00 | 2020-01-09 11:00 | ONSHORE | LA | 70380-1000 | Not Within a Municipality | TERREBONNE PARISH | SURVEY STATION NO. | STA 5222+30 | EL300 | MS4185 CABOT TAP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN SOIL UNDER WATER | 102 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | TAP | 2006 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 765 |  | NO | NO | [5 empty] | 0 | 0 | 6673 | 6943.220761125139271 | 1597 | 2802.897959183673469387755102040816326531 | 1927000 | 2005033.179482712929 | 545000 | 567069.581119916215 | 0 | 0 |  | 2.39 | 2480270 | 1139615.4221169633268188075801749271137 | 2581848.87932293795674038775510204081633 | 0 | 0 | 0 | 0 | NO |  |  |  | 828 | 8450 | 1037 | 192.619(A)(1) |  | 1964-10-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 166516 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA IS IN PLACE FOR EL300, BUT DUE TO THE NATURE OF THE MINOR LEAK, NO INDICATIONS WERE SEEN ON THE SCADA SYSTEM AND THEREFORE THE CONTROLLER WAS NOT INVESTIGATED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE PRESSURE SAFETY VALVE IN THE BODY BLEED PORT OF THE TAP VALVE DEVELOPED A SMALL PARASITIC LEAK FROM YEARS OF UNDERWATER/SUBSURFACE SERVICE. | [15 empty] | YES | NO ADDITIONAL FACTORS SELECTED | [161 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304.539.9311 |  |  |  |  | CHRIS LEGG | MANAGER | 304.722.8530 | chris_legg@tcenergy.com | DURING NORMAL ROUNDS MADE BY A LANDOWNER IN THE RIGHT-OF-WAY (ROW) OF EAST LATERAL 300 (EL300) PIPELINE, OWNED AND OPERATED BY COLUMBIA GULF TRANSMISSION LLC (CGT), A TC ENERGY COMPANY (COMPANY), IN SOUTH LOUISIANA, A CONTINENTAL LAND AND FUR REPRESENTATIVE (LAND OWNER) NOTICED BUBBLES DEVELOPING RIGHT OFF THE CGT ROW. THE LAND OWNER INFORMED LOCAL CGT TEAM MEMBERS, PERFORMING MAINTENANCE ON NEARBY COMPANY ASSETS, AND THEY CONDUCTED A PRELIMINARY INVESTIGATION INTO THE AREA IN QUESTION. THE LEAK LOCATION WAS GRADED AS NON-HAZARDOUS TO ANYONE IN THE LOCAL VICINITY AS THIS IS LOCATED IN A REMOTE AREA. PLANS WERE MADE TO FURTHER INVESTIGATE THE FOLLOWING DAY. GAS SAMPLES WERE TAKEN TO DETERMINE IF THIS WAS MARSH GAS OR PIPELINE GAS. AFTER TWO SEPARATE GAS SAMPLES WERE PULLED AND BROUGHT IN TO A LOCAL LABORATORY, THE CGT INTEGRITY TEAM MADE A DETERMINATION BY COMPARING PIPELINE QUALITY GAS TO THE SAMPLES THAT THE CHARACTERISTICS OF THE GAS WERE SIMILAR ENOUGH TO MERIT NAMING THIS A LEAK ON THE EL 300 SYSTEM. THIS LEAK IS SUSPECTED TO BE ON AN ISOLATED 4-INCH TAP VALVE THAT USED TO BE A CABOT GAS FEED. INTEGRITY ENGINEERING ALONG WITH THE INVESTIGATING DIVE PARTY WILL WORK TO ANALYZE THE LEAK AND DEVELOP PLANS TO DETERMINE HOW TO ADDRESS AND MITIGATE. ON MARCH 26, 2021 AN ATTEMPT WAS MADE TO REPAIR THE LEAKING VALVE BY ENCAPSULATION; HOWEVER, THIS EFFORT WAS NOT SUCCESSFUL. ON MARCH 7, 2022 THE COMPANY MOBILIZED TO THE SITE OF THE LEAK TO BEGIN LOCATING THE TAP VALVE IDENTIFIED FOR CUTOFF AND REPAIR. THE REPAIR CONSISTED OF CUTTING THE DAMAGED VALVE ON THE FOUR INCH RISER OFF OF EL300 AND BLIND FLANGING THE RISER. AS OF APRIL 8, 2022, TC ENERGY HAS DEMOBILIZED FROM THE SITE OF THE LEAK LOCATED ON EAST LATERAL 300 LINE (EL300).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200010 | 33373 | 2020-02-18 15:07 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-01-19 06:21 | 2020 | CENTRAL | NO | 38.8448 | -93.3656 | 1269064 | 2020-01-19 11:46 | 1269170 | NATURAL GAS |  | 25882 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY UNIT 816 |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-01-19 06:21 | 2020-01-19 07:00 | ONSHORE | MO | 65337 | LA MONTE | PETTIS | SURVEY STATION NO. | 0+00 | HOUSTONIA COMPRESSOR STATION | HOUSTONIA 300/400 DISCHARGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2016 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 137 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 48658 | 85399.7551020408163265306122448979591837 | 1465 | 1524.324653836105055 | 497 | 517.125838195593319 | 0 | 0 |  | 1.88 | 50620 | 56935.3328030357459034810495626822157434 | 87441.2055940725147005306122448979591837 | 0 | 0 | 0 | 0 | NO |  |  |  | 815 | 220 | 898 | 192.619(A)(1) |  | 1965-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | NO | [5 empty] | YES | COMPRESSOR STATION PIPING. | YES |  |  |  |  | YES | COMPRESSOR STATION PIPING. | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SOLENOID VALVE MALFUNCTIONED. | [22 empty] | YES | SOLENOID VALVE FROZE. | [161 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 713-857-5479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 713-857-5479 | nathan.hlavaty@energytransfer.com | AFTER PLACING UNIT 816 ONLINE AT 06:21, GAS CONTROL NOTICED THE SUCTION AND DISCHARGE PRESSURES DROPPING. GAS CONTROL NOTIFIED ON CALL PERSONNEL. WHEN ON-CALL PERSONNEL ARRIVED AT THE PLANT, THE UNIT WAS SHUT DOWN BECAUSE THE UNIT BLOWDOWN VALVE WAS OPEN. THE UNIT WAS SHUT DOWN AT 07:13. UPON INVESTIGATION, IT WAS DISCOVERED THAT THE SOLENOID VALVE FROZE UP WHICH PREVENTED PRESSURE FROM BEING APPLIED TO THE DOME OF THE UNIT BLOWDOWN/RELIEF VALVE. AIR OPERATED SOLENOID WAS REPLACED WITH AN ELECTRONIC SOLENOID.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200011 | 33353 | 2020-02-20 13:48 | ORIGINAL FINAL | 39193 | ROVER PIPELINE, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-01-25 04:33 | 2020 | EASTERN | NO | 41.3578 | -84.3636 | 1269538 | 2020-01-25 09:36 | 1269646 | NATURAL GAS |  | 15620 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | UNIT 4204 WAS SHUT DOWN. DEFIANCE FACILITY WAS NOT SHUT DOWN. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-01-25 04:33 | 2020-01-25 05:50 | ONSHORE | OH | 43512 | DEFIANCE | DEFIANCE | NOT APPLICABLE |  | DEFIANCE CS | DEFIANCE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2017 | 2015 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 107 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 27491 | 48249.5102040816326530612244897959183673 | 1874 | 1949.886963337106398 | 240 | 249.71871462161448 | 0 | 0 |  | 1.76 | 29605 | 32629.1135601900028026763848396501457726 | 50449.1158820403535310612244897959183673 | 0 | 0 | 0 | 0 | NO |  |  |  | 1172 | 264 | 1500 | 192.619(A)(1) |  | 2017-10-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 60 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | nathan.hlavaty@energytransfer.com | 7138575479 |  |  |  |  | NATHAN HLAVATY | DIRECTOR - INTERSTATE REGULATORY COMPLIANCE | 7138575479 | nathan.hlavaty@energytransfer.com | AT APPROXIMATELY 04:33 EST ON SATURDAY, JANUARY 25TH, 2020, THE DISCHARGE PSV FOR UNIT 4204 OPENED WHILE THE UNIT WAS RUNNING. A LOCAL SHERIFF WAS CONTACTED DUE TO A HIGH NOISE COMPLAINT, HE THEN CONTACTED AN ANR EMPLOYEE. AFTER ANR VERIFIED IT WAS NOT AN ISSUE WITH THEIR STATION, THE ANR EMPLOYEE CONTACTED A ROVER EMPLOYEE AT 05:15 EST. THE ROVER EMPLOYEE RESPONDED BY DRIVING TO THE STATION, DETERMINING THE ISSUE WAS UNIT 4204, AND SHUTDOWN UNIT 4204 AT 05:55 EST. FITTINGS WERE REPLACED AND TIGHTENED AND THE VALVE WAS MODIFIED (PULLED APART, INSPECTED, SOFT PARTS REPLACED) BEFORE RETURNING TO SERVICE, NO FURTHER ISSUES IDENTIFIED. ONCE IT WAS DETERMINED THAT ESTIMATES OF POTENTIAL GAS LOSS WERE GREATER THAN 3 MMCF, THE DIRECTOR OF REGULATORY COMPLIANCE WAS NOTIFIED TO MAKE A TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200012 | 33659 | 2020-02-20 14:14 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2020-01-20 08:57 | 2020 | EASTERN | NO | 34.0932 | -78.0428 | 1269165 | 2020-01-21 08:40 | 1269881 | NATURAL GAS |  | 0.5 | 0.025 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | BEING MONITORED DAILY. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | BEING MONITORED |  | OPERATIONAL CONTROL | BEING MONITORED |  | 0 | 2020-01-20 08:42 | 2020-01-20 08:42 | ONSHORE | NC | 28479 | WINNABOW | BRUNSWICK | SURVEY STATION NO. | 34 5' 33.8" N | LINE 99 | 1181913 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | IN A WETLAND AREA | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.199 | 60000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | EPOXY |  | UNKNOWN | [26 empty] | 1992 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | PREVIOUS LEAK CLAMP | [5 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO | [5 empty] | 0 | 0 | 2 | 2.080989288513454 | 45 | 78.97959183673469387755102040816326530612 | 626000 | 651349.647304711102 | 210 | 218.50387529391267 | 0 | 0 |  | 89 | 626257 | 287499.6539087187706403615160349854227405 | 651649.2117611302628178775510204081632653 | 0 | 0 | 0 | 0 | NO |  |  |  | 477 | 477 | 477 | 192.619(A)(2) |  | 1992-08-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 36960 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A GRADE 2 LEAK. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | NO | [145 empty] | YES |  |  |  |  | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | SUPERVISOR WAS CALLED TO A LEAK ON LINE 99 1/2 MILE SOUTH OF FUNSTON FARM. THE LEAK WAS INVESTIGATED ON THE RIGHT OF WAY. THE LEAK IS NOT BLOWING ABOVE GROUND BUT THERE ARE BUBBLES RISING FROM THE GROUND WATER AND CANNOT OBTAIN A % READING. THE LEAK HAS BEEN MONITORED DAILY WITH NO CHANGE IN STATE OR GRADE. THE AREA IS WET WITH STANDING WATER. CHECKED THE SURROUNDING AREA WITH NO MIGRATION DETECTED. THE GRADE 2 LEAK WAS A RESULT OF AN IMPROPERLY INSTALLED LEAK CLAMP FROM 1992. ONE SECTION OF PIPE WAS CUT OUT AND REPLACED TO REPAIR.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200013 | 34076 | 2020-02-23 20:17 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-01-24 15:52 | 2020 | EASTERN | NO | 42.7532 | -84.5611 | 1269701 | 2020-01-27 16:08 | 1269774 | NATURAL GAS |  | 2220 | 28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-01-27 | 2020-02-01 13:47 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-01-24 20:20 | VALVE CLOSURE |  | 2020-01-24 20:41 | 0 | 2020-01-24 15:52 | 2020-01-24 15:53 | ONSHORE | MI | 48906 | LANSING | INGHAM | NOT APPLICABLE |  | LINE 1027 | BTW GRAND RIVER AND MLK BLVD. | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.25 | 35000 | API 5L | OTHER | UNKNOWN | UNKNOWN | OTHER | WAX | UNKNOWN | [26 empty] | 1956 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 165 |  | NO | NO | [5 empty] | 0 | 0 | 81 | 84.280066184794887 | 6416 | 11260.734693877551020408163265306122449 | 55651 | 57904.567447531114277 | 996 | 1036.332665679700092 | 0 | 0 |  | 2.89 | 63144 | 33428.3369188931464726997084548104956268 | 70285.914873273160276408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 382 | 7716 | 400 | 192.619(A)(2) |  | 1971-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 4843 | NO | YES |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1971 | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON FRIDAY, JANUARY 24, 2020 AT APPROXIMATELY 15:53 HOURS A LEAK WAS IDENTIFIED ON A 12" HP PIPELINE OWNED AND OPERATED BY CONSUMERS ENERGY (CE). THE PIPELINE WAS INSTALLED IN 1956 AND IS LOCATED ALONG THE NE CORNER OF THE PROPERTY AT THE CE LANSING SERVICE CENTER, 530 W WILLOW ST, LANSING. A SECTION OF THE PIPELINE WAS ISOLATED BETWEEN N. GRAND RIVER AND N. MARTIN LUTHER KING BLVD ON FRIDAY, JANUARY 24 AT APPROXIMATELY 20:41 HOURS. FURTHER LEAK INVESTIGATION ACTIVITIES WERE PERFORMED ON SATURDAY, JANUARY 25, 2020 AND THE SITE WAS CONTINUOUSLY MONITORED THROUGHOUT THE WEEKEND. THERE WERE NO FATALITIES OR INJURIES THAT OCCURRED AS A RESULT OF THE INCIDENT. REMEDIATION WORK BEGAN ON THURSDAY, JANUARY 30, 2020. A VISUAL INSPECTION PERFORMED AT THE LEAK LOCATION, IDENTIFIED THE LEAK SOURCE AS LOCALIZE PITTING. A TEMPORARY REPAIR, BY INSTALLING A BOLTED PLIDCO FITTING WAS COMPLETED ON FEBRUARY 1, 2020 AND NORMAL OPERATIONS RESUMED IMMEDIATELY FOLLOWING REPAIRS AT APPROXIMATELY 13:47 HOURS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200014 | 36339 | 2020-02-28 12:44 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-01-29 14:45 | 2020 | EASTERN | NO | 40.1366 | -77.0425 | 1269937 | 2020-01-30 09:26 | 1270051 | NATURAL GAS |  | 232.6 | 8.45 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STOPPLE BYPASS INSTALLED TO ALLOW PIPELINE TO REMAIN IN SERVICE. |  |  |  | YES | OPERATOR | 2020-01-30 13:15 | NO | [5 empty] | OPERATIONAL CONTROL | MANUAL OPERATION OF MAINLINE VALVE UPSTREAM |  | OPERATIONAL CONTROL | MANUAL OPERATION OF MAINLINE VALVE DOWNSTREAM |  | 0 | 2020-01-29 14:45 | 2020-01-29 14:45 | ONSHORE | PA | 17019 | DILLSBURG | YORK COUNTY | SURVEY STATION NO. | 1380+40 | 1655 NORTH | 1655-050 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 45 | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.188 | 60000 | X60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | US STEEL- NATIONAL TUBE | COAL TAR |  | UNKNOWN | [26 empty] | 1972 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 227 |  | NO | NO | [5 empty] | 0 | 0 | 20 | 20.80989288513454 | 556 | 975.836734693877551020408163265306122449 | 1492283 | 1552712.469215361337741 | 0 | 0 | 0 | 0 |  | 2.39 | 1492859 | 685646.7456948016432001778425655976676385 | 1553709.11584294034983202040816326530612 | 0 | 0 | 0 | 0 | NO |  |  |  | 702 | 29.14 | 936 | 192.619(A)(2) |  | 1972-01-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 36651 | NO |  | YES |  | YES |  | YES | MODIFICATIONS ARE CURRENTLY PLANNED TO CONFIGURE THIS SECTION OF PIPELINE TO ACCEPT FREE SWIMMING INSTRUMENTED INLINE INSPECTION TOOLS. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS IS A LEAK IN A ROAD CROSSING, REPORTED DUE TO COST. AN INVESTIGATION WAS NOT NECESSARY DUE TO THE FACT THAT CONTROLLERS DO NOT HAVE CONTROL OF ANY DEVICES AT THIS SITE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  | YES |  |  |  |  | ALTERNATING CURRENT | NEARBY POWER TRANSMISSION ELECTRICAL LINES | YES | YES |  |  | YES | YES | 1972 | NO | YES | YES | YES |  |  | 2021 | 2016 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 13043573596 |  | WILLIAM YOUSE | william_youse@tcenergy.com | 13043573596 | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | 13043572245 | paul_shaffer@tcenergy.com | ON JANUARY 29, 2020 WHILE CONDUCTING ROUTINE PIPELINE LEAK SURVEY, COMPANY PERSONNEL DETECTED THE PRESENCE OF NATURAL GAS IN A VENT ALONG A CASED ROAD-CROSSING ON LINE 1655 NEAR DILLSBURG, YORK COUNTY, PENNSYLVANIA. LINE 1655 IS A 10-INCH COATED CARBON STEEL TRANSMISSION PIPELINE WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 936 PSIG. THIS PIPELINE IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COMPANY) A TC ENERGY ENTITY WITH THE OPERATOR ID 2616. NATURAL GAS SAMPLES WERE TAKEN FROM THE VENT PIPE AND A NEARBY METERING STATION ON LINE 1655, THEN SENT TO AN INDEPENDENT LABORATORY FOR ANALYSIS. RESULTS CONFIRMED THAT THE SOURCE OF NATURAL GAS WAS FROM PIPELINE 1655. A PRESSURE REDUCTION FROM 702 PSIG DOWN TO 600 PSIG WAS PUT IN PLACE TO MAINTAIN UNINTERRUPTED FLOW TO APPROXIMATELY 42,000 DOWNSTREAM CUSTOMERS THAT WERE SERVICED BY THE LOCAL DISTRIBUTION COMPANY. THE NATIONAL RESPONSE CENTER (NRC) AND PHMSA ACCIDENT INVESTIGATION DIVISION WERE NOTIFIED OF THE INCIDENT (NRC# 1269937). PIPELINE STOPPLES AND BYPASS PIPING WERE INSTALLED AROUND THE LEAK AREA TO MAINTAIN NATURAL GAS FLOW DOWNSTREAM WHILE REPLACING THE PIPELINE THROUGHOUT THE ROAD CROSSING AREA. THIS WORK REQUIRED THE CLOSURE OF STATE ROUTE (SR) 74 AND TRAFFIC MANAGEMENT AROUND THE AREA. EVIDENCE SECTION OF PIPE WAS SENT FOR METALLURGICAL ANALYSIS BY AN INDEPENDENT LABORATORY. ANALYSIS INDICATED STRAY CURRENT INDUCED EXTERNAL CORROSION AS A PROBABLE CAUSE. AFTER COMPLETING PERMANENT REPAIRS, LINE 1655 WAS RETURNED TO SERVICE ON FEBRUARY 19, 2020. ANTICIPATING ALTERNATING CURRENT (AC) STRAY CURRENT AS A PROBABLE CAUSE, A TEMPORARY SOLID-STATE DE-COUPLER WAS INSTALLED BETWEEN LINE 1655 AND THE SR 74 CASING. AN ADDITIONAL FIVE CASINGS WERE CONNECTED TO THE PIPELINE THROUGH SOLID STATE DE-COUPLERS TO PROVIDE ADDITIONAL MITIGATION AGAINST AC DENSITY ON LINE 1655. IN JANUARY 2021, THE COMPANY RECEIVED AN AC STUDY REPORT AND MITIGATION RECOMMENDATIONS FROM A THIRD-PARTY CONTRACTOR. AFTER REVIEWING THE REPORT, THE COMPANY REQUESTED ADDITIONAL MODELING TO BE COMPLETED USING A MORE STRINGENT AC DENSITY THRESHOLD DUE TO COMPANY PROCEDURES THAT HAVE BEEN UPDATED SUBJECT TO THE ADDITIONAL STRINGENT STANDARD. AS OF MARCH 31, 2021, THE NEWLY INTRODUCED MODELING IS ONGOING. ONCE COMPLETED, A PROJECT WILL BE IMPLEMENTED TO INSTALL THE ADDITIONAL MITIGATION MEASURES. AS PREVIOUSLY NOTED, TEMPORARY MITIGATION IS CURRENTLY IN PLACE ON 1655 TO HELP MITIGATE AC CONCERNS. MODELING WAS RECENTLY COMPLETED FOR 1655. THE MODELING INDICATED UNMITIGATED (WITHOUT THE TEMPORARY MITIGATION MEASURES IN PLACE) STEADY STATE VOLTAGES OVER 15 VAC AS WELL AS CURRENT DENSITIES OVER 30 A/M2. JANUARY 2022, THE AC VOLTAGE STUDY WAS COMPLETED, A NEW MITIGATION PROJECT IS IN PROCESS AND WE ARE CURRENTLY IN THE PERMITTING STAGES TO INSTALL APPROXIMATELY 4,500 FEET OF MITIGATION RIBBON ALONG THE PIPELINE, SIX FAULT MITIGATION ELECTRODES, ADDITIONAL COUPON TEST STATIONS, CONVERSIONS OF ALL TEST STATIONS IN THE AREA TO "DEAD FRONT" TEST STATIONS, AND APPROXIMATELY 15 GRADIENT CONTROL MATS AT EXISTING TEST STATIONS. THE PIPELINE HAS BEEN TEMPORARILY GROUNDED THROUGH SOLID STATE DECOUPLERS TO EXISTING CASINGS TO MITIGATE RISKS ASSOCIATED WITH HIGH AC CURRENT DENSITY AND INDUCED AC POTENTIALS. THESE TEMPORARY MEASURES WILL BE DISCONNECTED UPON COMPLETION OF THE PROJECT. THE TEMPORARY MEASURES DO NOT AFFECT THE CATHODIC PROTECTION OF THE PIPELINE. PROJECT COMPLETION IS CURRENTLY SCHEDULED FOR Q3 2022. PLEASE NOTE QUESTION E1A. WOULD NOT ACCEPT 12140 (MSCF/D) AS AN ENTRY FOR FLOW RATE. THE FLOW RATE AT THE TIME OF THE INCIDENT HAS BEEN ENTERED AS 12.14 (MMCF/D).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200015 | 33953 | 2020-03-03 19:21 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION CO | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2020-02-02 10:00 | 2020 | EASTERN | NO | 43.9401 | -84.9411 | 1270167 | 2020-02-02 11:06 | 1270344 | NATURAL GAS |  | 672 | 852 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-02 10:13 | 2020-02-12 11:43 |  | NO |  |  | NO | [11 empty] | 0 | 2020-02-02 10:12 | 2020-02-02 10:12 | ONSHORE | MI | 48633 | LAKE GEORGE | CLARE | MILEPOST | 815.7 | GREAT LAKES GAS TRANSMISSION COMPANY | CS 12 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 2.375 |  | 0.218 | 35000 | UNKNOWN | SEAMLESS |  | US STEEL | COAL TAR |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1990 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 52 |  | NO | NO | [5 empty] | 0 | 0 | 2130 | 2216.25359226682851 | 1680 | 2948.571428571428571428571428571428571429 | 549327 | 571571.801445615072729 | 0 | 0 | 14000 | 14566.925019594178 | METALLURGICAL | 2.5 | 567137 | 261494.3774968141534211632653061224489796 | 591303.5514860475078104285714285714285714 | 0 | 0 | 0 | 0 | NO |  |  |  | 826 | 0 | 974 | 192.619(A)(1) |  | 1990-06-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UPON REVIEW, IT WAS DETERMINED CONTROLLERS' ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES |  |  |  | YES | OTHER | REVERSE BENDING FATIGUE RELATED TO THERMAL EXPANSION AND CONTRACTION. | [15 empty] | YES | [8 empty] | 974 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ROBERTA PRIMERA | COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 248-561-7803 |  |  |  |  | ERIK HUGHES | SENIOR MANAGER - US REGULATORY COMPLIANCE | 402-490-7253 | erik_hughes@tcenergy.com | ON FEBRUARY 2, 2020, AT 1000 (ALL TIMES ARE EASTERN STANDARD TIME), A FARWELL CS TECHNICIAN RESPONDED TO THE SOUND OF AN APPARENT NATURAL GAS RELEASE WITHIN THE COMPRESSOR STATION YARD. AT 1012, THE TECHNICIAN CONFIRMED THE RELEASE ASSOCIATED WITH THE 36 INCH HEADER INLET TO A GAS COOLER. AT 1013, THE TECHNICIAN ACTIVATED AN EMERGENCY SHUT DOWN (ESD) AND THE STATION WAS ISOLATED FROM ANY GAS SOURCES WITH THE BLOW DOWN SUCCESSFULLY COMPLETED. AT 1025 THE STATION WAS CONFIRMED ISOLATED. AT 1106, THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC); REPORT # 1270167. THE INCIDENT WAS REPORTED DUE TO ANTICIPATED REPAIR COSTS EXCEEDING THE REPORTABLE THRESHOLD OF $50,000. FIELD INVESTIGATION INDICATED THE SOURCE WAS DUE TO A FAILED WELD ASSOCIATED WITH THE WELD-O-LET 2 INCH SIPHON DRAIN LINE CONNECTED TO THE 36 INCH HEADER. THE FAILED SIPHON DRAIN LINE WAS REMOVED AND PLUGGED. THE 2 INCH SIPHON DRAIN LINE ASSEMBLY WAS SENT FOR METALLURGICAL ANALYSIS TO DETERMINE THE CAUSE OF THE FAILURE. 20200514 UPDATE: RCFA RECEIVED ON 1 MAY 2020; WILL INCLUDE FINAL SUMMARY AFTER PAGE-TURN MEETING WITH MPSC ON 21 MAY 2020. 20200609 UPDATE: RCFA WAS RECEIVED AND RESULTS REVIEWED WITH THE MPSC ON 5/21. ADDITIONAL QUESTIONS WERE ASKED AND RESPONSES WERE PROVIDED ON 6/8. 20200625 UPDATE: METALLURGICAL ANALYSIS DETERMINED THE PIPE CRACKED DUE TO REVERSED BENDING FATIGUE, WHICH WAS A RESULT OF THERMAL LATERAL, AND THERMAL EXPANSION AND CONTRACTION OF THE FIXED (IN CONCRETE) 2" DRAIN LINE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200016 | 33413 | 2020-03-04 15:19 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2020-02-07 17:19 | 2020 | CENTRAL | NO | 30.3544 | -93.7063 | 1270705 | 2020-02-07 17:19 | 1270824 | NATURAL GAS |  | 10.368 | 1861 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ATTEMPTED REPAIR BEFORE ISOLATION |  |  |  | YES | OPERATOR | 2020-02-07 17:19 | NO | [5 empty] | OPERATIONAL CONTROL | MONITORED LEAK AND REDUCED PRESSURE |  | OPERATIONAL CONTROL | MONITORED LEAK AND REDUCED PRESSURE |  | 0 | 2020-02-05 17:00 | 2020-02-05 | ONSHORE | LA | 70661 | STARKS | CALCASIEU | MILEPOST | 438.84 | VALVE 40A40 | MAINLINE A | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | GROVE |  |  |  | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 578 |  | NO | NO | [5 empty] | 0 | 0 | 3860 | 4016.30932683096622 | 22 | 38.61224489795918367346938775510204081633 | 59172 | 61568.149089959050044 | 0 | 0 | 0 | 0 |  | 2.074 | 63054 | 28958.6864918072437171545189504373177843 | 65623.0706616879754476734693877551020408 | 0 | 0 | 0 | 0 | NO |  |  |  | 640 | 48000 | 780 | 192.619(A)(3) |  | 1970-06-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 111144 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | EXCAVATION FOR PREPARATION OF REMOVAL OF VALVE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VISIBLE CRACK ON 1/4" NIPPLE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | VALVE NIPPLE | [8 empty] | YES | [172 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 7132152846 |  | JOHN BELL | john.bell@williams.com | 3375697670 | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | FEBRUARY 5TH 2020: THE 40A40 MAINLINE BLOCK VALVE IS A REDUCED PORT VALVE THAT IS SCHEDULED FOR REPLACEMENT IN JUNE. IN PREPARATION FOR THAT PROJECT A CREW WAS HAND EXCAVATING THE VALVE ON FEBRUARY 5TH TO LOCATE THE WELD AND CONCRETE SUPPORTS. WHILE BACKFILLING THE EXCAVATION BY HAND, A SMALL GAS LEAK WAS HEARD AND A STOP WORK WAS CALLED. INVESTIGATION OF THE GAS LEAK IDENTIFIED THAT THE LEAK WAS COMING FROM A SMALL CRACK ON A FITTING CONNECTED TO THE BODY DRAIN VALVE. IT WAS KNOWN THAT IF THE PRESSURE COULD BE RELIEVED FROM THE VALVE BODY, THE LEAK WOULD BE STOPPED. FEBRUARY 5TH - 6TH: SEVERAL EFFORTS WERE MADE TO STOP THE LEAK BUT THOSE EFFORTS WERE UNSUCCESSFUL. FEBRUARY 7TH: DUE TO THE INABILITY TO STOP THE LEAK BY BLOWING DOWN THE VALVE BODY, THE ONLY OTHER OPTION TO STOP THE LEAK WAS TO REMOVE THE PRESSURE FROM THE PIPELINE. DUE TO THE LEAK BEING LOCATED ON A MAINLINE BLOCK VALVE, ONE SECTION OF THE PIPELINE UPSTREAM AND DOWNSTREAM HAD TO BE ISOLATED TO RELIEVE PRESSURE. OPERATIONS AND PROJECT PERSONNEL INVESTIGATED OPTIONS TO ACCELERATE VALVE REPLACEMENT OR REPAIRS. AFTER CONSIDERING ALL ALTERNATIVES THE $50,000 THRESHOLD WAS GOING TO BE EXCEEDED AND THE NRC WAS NOTIFIED. FEBRUARY 10TH: THE PIPELINE WAS ISOLATED AND DECOMPRESSION STARTED TO AVOID BLOWING DOWN ~26MMSCF IN GAS. THE LEAK WAS FREQUENTLY CHECKED BY OPERATIONS TO ENSURE THAT THE LEAK RATE DID NOT INCREASE. RECOMPRESSION WAS COMPLETE AND THE REMAINING PRESSURE (44 PSIG) WAS BLOWN DOWN TO ATMOSPHERE. 2/28/2020 - UPDATE - AFTER FURTHER INVESTIGATION, THE LEAK WAS NOT DUE TO CORROSION. THE 1/4 INCH NIPPLE HAS A VISIBLE CRACK INSIDE WHERE THE THREADS STOPPED ENTERING THE 1/2 INCH X 1/4 INCH REDUCER. IT APPEARS THAT THE 1/4 INCH NIPPLE WAS BENT AT SOME POINT IN TIME CAUSING THE CRACK SINCE THE CRACK AREA ITSELF IS CLEAN AND SHINY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200018 | 33427 | 2020-03-06 11:26 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-02-06 14:50 | 2020 | CENTRAL | NO | 29.974 | -91.8093 | 1270587 | 2020-02-06 17:03 | 1270666 | NATURAL GAS |  | 1 | 80 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-19 09:00 | 2020-02-19 18:00 |  | YES | OPERATOR | 2020-02-06 16:35 | NO | [5 empty] | OPERATIONAL CONTROL | ADJUSTED PRESSURE CONTROL VALVE 20 PERCENT LOWER THAN OPERATING PRESSURE |  | OPERATIONAL CONTROL | ADJUSTED PRESSURE CONTROL REGULATOR TO LOWER PIPELINE PRESSURE |  | 0 | 2020-02-06 14:50 | 2020-02-06 16:05 | ONSHORE | LA | 70562 | NEW IBERIA | IBERIA | MILEPOST | 136.6 | LAFAYETTE TO FRANKLIN 8" LINE | INDEX 205 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 137 |  | NO | NO | [5 empty] | 1500 | 1560.7419663850905 | 150 | 156.07419663850905 | 2 | 3.51020408163265306122448979591836734694 | 90000 | 93644.51798310543 | 1200 | 1248.5935731080724 | 0 | 0 |  | 1.88 | 92852 | 42622.903224414115198104956268221574344 | 96613.4379233187346030612244897959183673 | 0 | 0 | 0 | 0 | NO |  |  |  | 275 | 11000 | 480 | 192.619(C) |  | 2018-03-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 20064 | NO |  | YES | YES | YES |  | YES | DRESSER COUPLED PIPE SEGMENTS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [7 empty] | YES | [174 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | ON 2-6-2020 AT 14:50, GULF SOUTH PIPELINE RECEIVED A PHONE CALL THAT THERE WAS A GAS SMELL NEAR ITS FACILITY. GULF SOUTH TECHNICIANS ARRIVED AT THE LOCATION AT APPROXIMATELY 16:05, SMELLED ODORANT, AND LOCATED A LEAK USING A GAS DETECTOR. TECHNICIANS CONTACTED AREA MANAGER AT 16:10, PROVIDED LEAK LOCATION DETAILS, AND A CONTRACTOR WAS CONTACTED TO EXCAVATE THE LEAK LOCATION. PRESSURE CONTROL VALVE SET POINT WAS LOWERED BY 20% OF THE OPERATING PRESSURE AT THE TIME OF DISCOVERY (FROM 275 PSIG TO 225 PSIG). AREA MANAGER NOTIFIED LAHAZMAT TO REPORT THE LEAK AT 16:35 AND MADE ADDITIONAL INTERNAL NOTIFICATIONS. AT APPROXIMATELY 18:00, CONTRACTOR ARRIVED ONSITE, HAND EXCAVATED THE LEAK LOCATION, AND DISCOVERED A LEAKING MECHANICAL COUPLING. CONTRACTOR BACK-FILLED HOLE AND TECHNICIANS MONITORED AREA. THE LEAK COULD ONLY BE DETECTED BY MONITOR WITHIN INCHES OF THE GROUND AND WAS DETERMINED TO BE LOW GRADE. THE LEAK LOCATION WAS MONITORED UNTIL THE BLOW DOWN AND REPAIR OCCURRED ON 2-19-2020. LEAK STOPPED AFTER LINE WAS DEPRESSURIZED AT 10:45 ON 2-19-2020. WELD OVER WAS INSTALLED AND LINE RETURNED TO SERVICE AT APPROXIMATELY 18:00 ON 2-19-2020.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200019 | 33453 | 2020-03-12 16:30 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-02-17 11:54 | 2020 | CENTRAL | NO | 35.9051 | -97.0448 | 1271412 | 2020-02-17 12:46 | 1271569 | NATURAL GAS |  | 430 | 3343 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-17 15:45 | 2020-02-19 19:46 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-02-17 15:45 | VALVE CLOSURE |  | 2020-02-17 15:45 | 0 | 2020-02-17 11:54 | 2020-02-17 11:54 | ONSHORE | OK | 74832 | Not Within a Municipality | LINCOLN | SURVEY STATION NO. | 120/180506 | EDMUND-DRUMRIGHT 12" | LINE XD | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | CREEK EXPOSURE |  |  | YES | [6 empty] | YES | UNCASED | UNNAMED CREEK | 1 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | NO | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1946 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 282 |  | NO | NO | [5 empty] | 0 | 0 | 5416 | 5635.318993294433432 | 697 | 1223.306122448979591836734693877551020408 | 232000 | 241394.757467560664 | 0 | 0 | 0 | 0 |  | 1.62 | 238113 | 109782.8762947584049585772594752186588921 | 248253.3825833040770238367346938775510204 | 0 | 0 | 0 | 0 | NO |  |  |  | 446 | 11000 | 498 | 192.619(C) |  | 1967-06-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 93750 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS SMALL ENOUGH THAT IT WAS NOT DETECTABLE BY THE GAS CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | CREEK BANK EROSION EXPOSED A 1 INCH TAP AT THIS LOCATION. DEBRIS CAUGHT ON THE 1 INCH LINE AND CRACKED THE TAP VALVE. | NO | [306 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON FEBRUARY 17, 2020 SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) WAS NOTIFIED BY AIR LEAK PATROL OF A POSSIBLE LEAK AT A CREEK CROSSING ON A SSCGP PIPELINE. BY 11:54 AM SSCGP OPERATIONS WAS ON SITE AND VERIFIED THE LEAK WAS ON A COMPANY PIPELINE, LINE XD. THE LEAK ITSELF WAS IDENTIFIED AS A 1 INCH TAP VALVE THAT HAD BEEN EXPOSED DUE TO BANK EROSION AND CRACKED DUE TO DEBRIS BUILD UP. THE LEAK ITSELF WAS MINOR BUT DUE TO THE REMOTE LOCATION THE NRC WAS NOTIFIED AT 12:46 AM BECAUSE THE ESTIMATED REPAIR WOULD BE IN EXCESS OF $50,000. THE FOLLOW UP CALL TO THE NRC WAS MADE ON 2/19/2020 AT 10:53 AM TO CONFIRM THERE WERE NO FIRE OR INJURIES AS A RESULT OF THIS LEAK. THE SEGMENT OF PIPELINE WAS ISOLATED BY 3:45 PM ON 2/17/2020 AND ALLOWED TO BLOW DOWN. THE 1 INCH LINE FOR THIS TAP WAS NO LONGER IN USE SO IT WAS DETERMINED THAT THE 1 INCH LINE COULD BE ABANDONED AND A PERMANENT REPAIR SLEEVE COULD BE INSTALLED. THE REPAIR SLEEVE WAS INSTALLED AND LINE XD WAS PLACED BACK IN SERVICE BY 7:46 PM ON 2/19/2020.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200020 | 33454 | 2020-03-12 16:34 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-02-14 09:49 | 2020 | CENTRAL | NO | 38.1728 | -95.3002 | 1271229 | 2020-02-14 10:32 | 1271254 | NATURAL GAS |  | 7164 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED AND OVERHAULED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-02-14 00:26 | 2020-02-14 00:26 | ONSHORE | KS | 66091 | WELDA | ANDERSON | SURVEY STATION NO. | 100/0 | WELDA COMPRESSOR STATION | LINE DS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | 1996 | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 363 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 11606 | 20369.7142857142857142857142857142857143 | 500 | 520.2473221283635 | 0 | 0 | 0 | 0 |  | 1.62 | 12106 | 13595.0233974979871530612244897959183673 | 20889.9616078426492142857142857142857143 | 0 | 0 | 0 | 0 | NO |  |  |  | 585 | 142000 | 690 | 192.619(A)(2) |  | 1970-10-29 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 48623 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE WELDA OPERATOR IMMEDIATELY NOTIFIED GAS CONTROL OF POSSIBLE RELIEF VALVE ACTIVATION. GAS CONTROL CONFIRMED A PRESSURE DROP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DUE TO DEBRIS IN THE PILOT, THE RELIEF VALVE MALFUNCTIONED | [147 empty] | YES | [13 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 2/14/2020 AT 12:26 AM LOCAL TIME, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) GAS CONTROL RECEIVED A CALL FROM THE OPERATOR AT THE WELDA COMPRESSOR STATION OF A POSSIBLE RELIEF VALVE ACTIVATION. GAS CONTROL CONFIRMED A PRESSURE DROP BUT THERE WAS NO MAOP EXCEEDANCE. GAS CONTROL RECEIVED ANOTHER CALL FROM THE ANDERSON COUNTY SHERIFF'S DEPARTMENT AT 12:31 AM DUE TO THE SOUND OF HISSING GAS. AT 12:34 AM THE WELDA OPERATOR IDENTIFIED THE LOCATION OF THE ACTIVATED RELIEF VALVE. SINCE THIS WAS NOT AN OVERPRESSURE EVENT, THE RELIEF VALVE WAS ISOLATED BY 12:48 AM. INITIAL GAS LOSS CALCULATIONS INDICATED THAT THIS WAS NOT A REPORTABLE EVENT. THE RELIEF VALVE WAS REMOVED, REBUILT AND PLACED BACK IN SERVICE AT APPROXIMATELY 10:00 AM ON 2/14/2020. THE GAS LOSS WAS RECALCULATED AT 9:49 AM AND IT WAS DETERMINED THAT ACTUAL GAS LOSS WAS APPROXIMATELY 7.1 MMCF. THE CALL TO THE NRC WAS PLACED AT 10:32 AM TO MAKE THE NOTIFICATION OF THE GAS LOSS AT THE RELIEF VALVE. THE NRC WAS ALSO NOTIFIED THAT THERE WERE NO INJURIES, FIRE OR PROPERTY DAMAGE AS A RESULT OF THIS RELEASE. THE FOLLOW UP CALL TO THE NRC WAS MADE ON 2/14/2020 AT 2:34 PM TO CONFIRM THAT THE EVENT WAS OVER AND THERE WERE NO INJURIES OR PROPERTY DAMAGE. THE TEMPERATURE AT THE TIME OF THE RELIEF VALVE MALFUNCTION WAS 2 DEGREES F. WHEN THE RELIEF VALVE WAS REMOVED FOR REBUILD, DEBRIS WAS PRESENT IN THE PILOT. SSCGP DETERMINED THAT DEBRIS IN THE PILOT CAUSED THE RELIEF VALVE TO MALFUNCTION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200021 | 33480 | 2020-03-13 15:37 | SUPPLEMENTAL FINAL | 32163 | ROCKIES EXPRESS PIPELINE LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2020-02-27 17:21 | 2020 | EASTERN | NO | 39.714 | -82.8717 | 1272273 | 2020-02-27 17:21 | 1272373 | NATURAL GAS |  | 5748.15 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ICE BUILDUP CAUSED INSTRUMENT AIR TO OPEN VALVE AND ALLOW UNINTENTIONAL VENTING. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-02-27 06:20 | 2020-02-27 06:20 | ONSHORE | OH | 43103 | Not Within a Municipality | PICKAWAY | NOT APPLICABLE |  | COLUMBUS COMPRESSOR STATION | COLUMBUS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2016 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | WHEN OPERATIONS PERSONNEL ARRIVED TO THE COLUMBUS COMPRESSOR STATION A RELEASE OF GAS WAS DISCOVERED ESTIMATED AT 6483 MCF. A REPAIR WAS MADE (DE-ICED). DUE TO DROPPING TEMPERATURE, IT IS SUSPECTED THAT ICE BUILDUP INSIDE A PNEUMATIC SOLENOID HAD ALLOWED INSTRUMENT AIR TO SLOWLY PRESSURIZE THE ACTUATOR AND SUBSEQUENTLY OPEN THE VALVE IN TURN ALLOWING THE COMPRESSOR TO BE PRESSURIZED WHILE STILL VENTING AT ROUGHLY 730 PSI. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 10059 | 17654.5714285714285714285714285714285714 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.75 | 10059 | 11583.9795918367346938775510204081632653 | 17654.5714285714285714285714285714285714 | 0 | 0 | 0 | 0 | NO |  |  |  | 730 | 0 | 1480 | OTHER | 0.8 DESIGN FACTOR. | 2016-07-21 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 3 | NO | [5 empty] | YES | IN STATION PIPING. | YES |  |  |  |  | YES | IN STATION PIPING. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS SPECIFIC COMPONENT IS NOT MONITORED BY GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | ICE BUILDUP CAUSED INSTRUMENT AIR TO OPEN VALVE AND ALLOW UNINTENTIONAL VENTING. | [20 empty] | YES | WEATHER REALTED - ICE BUILDUP. | [123 empty] | YES | [24 empty] | YES | [12 empty] | LAURA ARELLANO-BRIOT | SR. COMPLIANCE COORDINATOR | laura.arellano-briot@tallgrassenergylp.com | 3072424493 |  | LAURA ARELLANO-BRIOT | laura.arellano-briot@tallgrassenergylp.com | 3072424493 | LAURA ARELLANO-BRIOT | SR. COMPLIANCE COORDINATOR | 3072424493 | laura.arellano-briot@tallgrassenergylp.com | WHEN OPERATIONS PERSONNEL ARRIVED TO THE COLUMBUS COMPRESSOR STATION A RELEASE OF GAS WAS DISCOVERED THAT WAS ESTIMATED TO BE 6483 MCF. A REPAIR WAS MADE (DE-ICED). DUE TO DROPPING TEMPERATURE, IT IS SUSPECTED THAT ICE BUILDUP INSIDE A PNEUMATIC SOLENOID HAD ALLOWED INSTRUMENT AIR TO SLOWLY PRESSURIZE THE ACTUATOR AND SUBSEQUENTLY OPEN THE VALVE IN TURN ALLOWING THE COMPRESSOR TO BE PRESSURIZED WHILE STILL VENTING AT ROUGHLY 730 PSI. THE FINAL DETERMINATION OF THE GAS VOLUME RELEASED IS 5748.15 MCF.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200022 | 33807 | 2020-03-16 16:09 | SUPPLEMENTAL FINAL | 9171 | MARKWEST JAVELINA PIPELINE COMPANY, L.L.C. | 1515 ARAPAHOE STREET TOWER 1, SUITE 1600 | DENVER | CO | 80202 | 2020-02-17 10:09 | 2020 | CENTRAL | NO | 27.803 | -97.4305 | 1271395 | 2020-02-17 09:21 |  | OTHER GAS | REFINERY OFF GAS (RAW GAS) | 2598 | 161 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-17 10:03 | 2020-04-25 11:00 |  | YES | OPERATOR | 2020-02-17 08:37 | YES | 2020-02-17 08:35 | OTHER | ONCE WE ISOLATED THE GAS TO THE PIPELINE THE FIRED BURNED OUT | 2280 | YES | VALVE CLOSURE |  | 2020-02-17 09:55 | VALVE CLOSURE |  | 2020-02-17 10:02 | 10 | 2020-02-17 10:09 | 2020-02-17 08:45 | ONSHORE | TX | 78408 | CORPUS CHRISTI | NUECES | MILEPOST | I37 EXIT 1E | JAVELINA | RG-800 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.25 | 35000 | GRADE B | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 1990 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 74.5 | 3.7 |  | CLASS 3 LOCATION | NO |  | 226 |  | NO | NO | [5 empty] | 320000 | 332958.28616215264 | 402 | 418.278846991204254 | 6482 | 11376.5714285714285714285714285714285714 | 260000 | 270528.60750674902 | 75000 | 78037.098319254525 | 2650000 | 2757310.80728032655 | 7.D - PIPELINE CLEANING, ILI ATTEMPTS, HYDRO-TESTING | 2.495 | 3311884 | 1524731.43096716101442616326530612244898 | 3450629.64954404536782542857142857142857 | 0 | 0 | 0 | 1 | NO |  |  |  | 55 | 11100 | 240 | 192.619(A)(2) |  | 1990-08-21 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | YES | MANUAL | MANUAL | 1062 | NO |  |  | YES | YES |  | YES | LINE WAS DESIGNED TO RUN MAINTENANCE PIGS FROM THE 20" TO A 24", NOT SMART TOOLS. THERE ARE TIGHT BACK TO BACK 90'S AS WELL AS NO RECEIVER ON THE 20" (RG-800). | YES | YES | YES | YES |  | YES | TIGHT RADIUS BENDS | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | MARKWEST IDENTIFIED THAT ADDITIONAL ALARMS OR PRESSURE INDICATORS WOULD HELP IN IDENTIFYING PRESSURE INCREASES OR DECREASES AT OFF-SITES. | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  | YES | DIFFERENTIAL AERATION PRODUCED BY THE DEPOSITS WHICH COLLECTED ON THE BOTTOM OF THE PIPE. THE COLLECTION OF THESE DEPOSITS WAS LIKELY EXACERBATED BY THE LOW VOLUME AND/OR FLOW RATES. |  | YES |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | YES | 2019 | 172 | NO | [13 empty] | NO | [20 empty] | YES | [42 empty] | TONY MINUTILLO | PIPELINE COMPLIANCE SUPERVISOR | tminutillo@mplx.com | 303-489-3275 |  | KEVIN THOMPSON | krthompson@mplx.com | (361) 289-4755 | DENNIS THEBEAU | ENGINEERING MGR | (303) 531-9089 | dthebeau@mplx.com | A FIRE IGNITED AT THE INTERSECTION OF BUDDY LAWRENCE AND I37 FRONTAGE ROAD AT MILE MARKER 1E. WITH THE AMOUNT OF PIPELINES IN THE AREA AND CONGESTION IT WAS DIFFICULT AT FIRST TO IDENTIFY WHO'S PIPELINE WAS LEAKING. WITH SUCH LOW PRESSURES ON OUR RG PIPELINES IT CAN BE DIFFICULT TO SEE DRASTIC PRESSURE INTERRUPTIONS. IN THE PROCESS OF ISOLATION WE WERE ABLE TO 100% COMMIT TO THE LEAK BEING OUR PIPELINE. IN THE INVESTIGATION THE CAUSE OF THE INCIDENT HAS BEEN DETERMINED TO BE INTERNAL CORROSION. UPON A VISUAL EXAMINATION, LOCALIZED PITTING WAS DISCOVERED THAT HAS BEEN ATTRIBUTED TO DIFFERENTIAL AERATION PRODUCED BY THE DEPOSITS WHICH COLLECTED ON THE BOTTOM OF THE PIPELINE. THE COLLECTION OF THESE DEPOSITS LIKELY EXACERBATED BY THE LOW VOLUME AND/OR FLOW RATES. THE ENTIRE EAST SIDE SYSTEM OF THE SYSTEM INCLUDING THE RG-800 HAS BEEN PUT THROUGH A RIGOROUS CLEANING REGIME, AND PRESSURE TESTED TO SHOW THE INTEGRITY OF THE LINE TO 433 PSIG. THIS WAS ONLY DONE AFTER MULTIPLE FAILED ATTEMPTS TO SMART TOOL THE LINE, DUE TO THE LINE NOT BEING PEGGABLE ALTHOUGH WE DID SPEND COUNTLESS RESOURCES ON TRYING TO MAKE THE SYSTEM SMART PIGGABLE. THIS PIPELINE CONTAINS MULTIPLE TIGHT BENDS THAT DID NOT ALLOW THE PASSING OF THE SMART TOOLS. INVESTIGATION HAS NOT SHOWN ANY INDICATION OF GENERAL CORROSION ALONG THE ENTIRE SYSTEM, BUT SHOWED TO BE LOCALIZED TO THE AREA THAT FAILED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200023 | 33723 | 2020-03-18 12:39 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2020-02-18 03:35 | 2020 | CENTRAL | NO | 28.6779 | -96.9382 | 1271457 | 2020-02-18 04:24 | 1271623 | NATURAL GAS |  | 22240 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-02-18 03:35 | 2020-04-21 13:45 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-02-18 03:30 | NO | [5 empty] | VALVE CLOSURE |  | 2020-02-18 03:35 | VALVE CLOSURE |  | 2020-02-18 03:35 | 0 | 2020-02-18 02:54 | 2020-02-18 03:30 | ONSHORE | TX | 77951 | BLOOMINGTON | VICTORIA | SURVEY STATION NO. | 7876 | DUPONT LATERAL | INDEX 127-9 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8.625 |  | 0.188 | 46000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 61 | 15 |  | CLASS 1 LOCATION | NO |  | 168 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 45370 | 79628.9795918367346938775510204081632653 | 50000 | 52024.73221283635 | 1500 | 1560.7419663850905 | 0 | 0 |  | 2.04 | 96870 | 75888.1096507474872609329446064139941691 | 133214.4537710581751938775510204081632653 | 0 | 0 | 0 | 0 | NO |  |  |  | 744 | 3401 | 795 | 192.619(A)(1) |  | 1950-03-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 18321 | NO |  |  |  | YES |  | YES | NO PIG LAUNCHER AND RECEIVER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT OCCURRED INDEPENDENT OF THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | LACK OF FUSION | [7 empty] | YES | [7 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [44 empty] | YES | [18 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 7134204417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 2:54AM ON FEBRUARY 18, 2020, KINDER MORGAN TEJAS PIPELINE COMPANY, LLC (TEJAS) GAS CONTROL RECEIVED A PHONE CALL FROM THE INVISTA PLANT IN BLOOMINGTON, TEXAS NOTIFYING TEJAS OF A GAS RELEASE COMING FROM THE TEJAS RIGHT OF WAY. TEJAS EMPLOYEES ARRIVED ON SITE AT 3:30AM AND AT 3:35AM CONFIRMED DISCOVERY OF A REPORTABLE RELEASE OF NATURAL GAS. AT 3:35, TEJAS ISOLATED THE PIPE SEGMENT BY CLOSING THE UPSTREAM AND DOWNSTREAM ISOLATION VALVES. TO REPAIR THE PIPELINE, THE RUPTURED SEGMENT OF PIPE WAS CUT OUT, REPLACED, AND HYDROTESTED. THE LINE WAS RETURNED TO SERVICE AT 13:45 ON APRIL 21, 2020. THE FAILED PIPE SEGMENT WAS CUT OUT AND SENT TO A KINDER MORGAN DESIGNATED METALLURGICAL LABORATORY FOR TESTING. THE METALLURGICAL REPORT REVEALED THAT THE GAS RELEASE WAS CAUSED BY A RUPTURE THAT ORIGINATED IN THE ERW LONG SEAM. AREAS OF LACK OF FUSION IN THE WELD BOND LINE DECREASED THE WELD STRENGTH AND CAUSED THE FAILURE. THE LACK OF FUSION OCCURRED DURING THE ORIGINAL MANUFACTURING OF THE ERW PIPE.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20200025 | 33534 | 2020-03-25 13:02 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 811 LOUISIANA ST. SUITE 1200 | HOUSTON | TX | 77002 | 2020-02-28 07:00 | 2020 | CENTRAL | YES | 28.259 | -94.013 | 1274191 | 2020-03-25 11:10 | 1274270 | NATURAL GAS |  | 2860 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-01 09:00 | 2020-03-18 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-01 09:00 | VALVE CLOSURE |  | 2020-03-01 12:00 | 0 | 2020-02-28 07:00 | 2020-02-28 07:00 | OFFSHORE | [6 empty] | HIOS | HI582 TO HI 264 | [20 empty] | 203 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HIGH ISLAND | 470 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1978 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 1138 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 5434 | 9537.224489795918367346938775510204081633 | 778000 | 809504.833231733606 | 0 | 0 | 0 | 0 |  | 1.9 | 783434 | 363380.3423669263192011661807580174927114 | 819042.0577215295243673469387755102040816 | 0 | 0 | 0 | 0 | NO |  |  |  | 875 | 1200 | 1440 | 192.619(A)(1) |  | 1978-07-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 283574 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK TOO LOW TO BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [29 empty] | YES | [153 empty] | YES | [9 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALIST | jorge.morice@genlp.com | 713-725-1663 |  | NORMAN GIBSON | norman.gibson@genlp.com |  | JOHN JEWETT | MANAGER DOT COMPLIANCE AND SECURITY | 713-860-2605 | john.jewett@genlp.com | DURING A ROUTINE HELICOPTER FLYOVER ON FEBRUARY 22ND, A RELATIVELY LOW LEVEL OF GAS BUBBLES WERE SEEN NEAR THE HIGH ISLAND OFFSHORE SYSTEM (HIOS) 30" GAS PIPELINE IN THE HI-470 BLOCK. THE PERSONNEL DID NOT OBSERVE ANY SHEEN ON THE WATER. DIVERS ARRIVED ON LOCATION AND DISCOVERED A LEAK OF THE VALVE #1 GREASE FITTING AT A SUBSEA ASSEMBLY. PLANS WERE MADE TO REPLACE REMAINING GREASE FITTINGS ON THE SSTI ASSEMBLY TO PREVENT THEM FROM LEAKING AT A LATER DATE. ON MARCH 18, 2020 DIVERS COMPLETED THE REPLACEMENT OF FITTINGS, THE PIPELINE WAS RE-PRESSURED AND REMAINED WITHOUT ANY SIGNS OF LEAKAGE AFTERWARDS. UPON CLOSE INSPECTION OF THE LEAKING FITTING, IT WAS DETERMINED THAT THE FITTING'S INTERNAL SEAL PROVIDED BY THE CHECK BALL WAS BROKEN DUE TO CORROSION INSIDE THE FITTING. SUPPLEMENTAL (03/30/20) - 48 HOUR NRC CONFIRMATION RECORDED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200026 | 33515 | 2020-03-26 08:16 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-03-18 19:06 | 2020 | CENTRAL | YES | 32.144 | -94.2666 | 1273779 | 2020-03-18 20:32 | 1273816 | NATURAL GAS |  | 13532 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY THE UNIT (T6) WAS TAKEN OFFLINE. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-03-18 19:06 | 2020-03-18 19:56 | ONSHORE | TX | 75633 | CARTHAGE | PANOLA | MILEPOST | 0 | CARTHAGE JUNCTION COMPRESSOR STATION | INDEX 816-1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 13 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | TURBINE NO. 6 BYPASS VALVE FAILED OPEN. | CLASS 1 LOCATION | NO |  | 115 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 24628 | 43224.6530612244897959183673469387755102 | 2500 | 2601.2366106418175 | 200 | 208.0989288513454 | 0 | 0 |  | 1.82 | 27328 | 29601.0622065474396644314868804664723032 | 46033.9886007176526959183673469387755102 | 0 | 0 | 0 | 0 | NO |  |  |  | 694 | 600000 | 1202 | 192.619(A)(1) |  | 2012-03-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | NO | [5 empty] | YES | COMPRESSOR STATION | YES |  |  |  |  | YES | COMPRESSOR STATION | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | POWER SUPPLY WAS BAD | [20 empty] | YES | POWER SUPPLY WAS BAD | [161 empty] | SHANNON M MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | GULF SOUTH GAS CONTROL NOTICED A LOSS OF COMMUNICATION ALARM AND SOME UNUSUAL PRESSURE DIFFERENCES BETWEEN THE RUNNING UNITS AT THE CARTHAGE JUNCTION COMPRESSOR STATION ON 03/18/2020 AT 19:06. GAS CONTROL CONTACTED LOCAL OPERATIONS PERSONNEL TO INVESTIGATE. UPON ARRIVAL, AT 19:56, OPERATIONS PERSONNEL DISCOVERED THE NO. 6 TURBINE (T6) RECYCLE VALVE WAS OPEN AND VENTING GAS TO THE 4" BLOW DOWN. HE MANUALLY CLOSED THE VALVE WHICH STOPPED THE BLOW DOWN. FROM THE TIME GAS CONTROL RECEIVED THE ALARMS AND OPERATIONS PERSONNEL WERE ABLE TO RESPOND, ASSESS AND CORRECT THE ISSUE, T6 VENTED GAS FOR APPROXIMATELY 1 HOUR AT 694 PSIG. IT WAS DETERMINED THAT THE POWER SUPPLY FOR T6 WAS BAD. THIS POWER LOSS CAUSED BOTH THE LOSS OF COMMUNICATION AND THE RECYCLE VALVE TO REMAIN OPEN. POWER SUPPLY WAS REPLACED AND ISSUE WAS RESOLVED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200027 | 33861 | 2020-04-02 19:57 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2020-03-05 03:20 | 2020 | EASTERN | NO | 32.7875 | -84.2545 | 1272740 | 2020-03-05 04:24 | 1272876 | NATURAL GAS |  | 55527 | 911 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-05 04:13 | 2020-03-05 08:13 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-03-05 03:45 | NO | [11 empty] | 0 | 2020-03-05 03:17 | 2020-03-05 03:45 | ONSHORE | GA | 30286 | THOMASTON | UPSON | MILEPOST | 346.9 | THOMASTON COMPRESSOR STATION | 8" EMERGENCY RELIEF VALVE - 001, SOUTH MAIN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2003 | 2002 | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH VENT STACK | CLASS 1 LOCATION | NO |  | 191 |  | NO | NO | [5 empty] | 0 | 0 | 1567 | 1630.455107550291209 | 95506 | 167622.7755102040816326530612244897959184 | 3000 | 3121.483932770181 | 250 | 260.12366106418175 | 0 | 0 |  | 1.72 | 100323 | 112196.1738371515849089766763848396501458 | 172634.8382115887355916530612244897959184 | 0 | 0 | 0 | 0 | NO |  |  |  | 1076 | 0 | 1200 | 192.619(A)(1) |  | 1951-07-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE STATION WAS OFFLINE WITH NO CHANGES TO HORSEPOWER OR SETPOINTS BEING MADE | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | INCORRECT ASSESSMENT OF TIMEFRAME FOR REPAIR |  |  |  | YES | UNAWARENESS OF VALVE OPERATORS FAIL SAFE MODE | ROUTINE MAINTENANCE | NO | [136 empty] | YES |  |  | YES | [10 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 2545483437 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | AT 3:17 AM SOUTHERN NATURAL GAS COMPANY, L.L.C. (SNG) GAS CONTROL RECEIVED A PHONE CALL FROM THE PUBLIC REGARDING A LOUD NOISE COMING FROM A PIPELINE FACILITY. A SNG TECHNICIAN WAS CALLED OUT TO THE SITE AND ARRIVED AT 3:45 AM. UPON ARRIVAL THE TECHNICIAN MET WITH EMERGENCY RESPONDER PERSONNEL WHO PROCEEDED TO BLOCK THE ACCESS ROAD TO THE COMPRESSOR STATION. THE TECHNICIAN ATTEMPTED TO CLOSE THE EMERGENCY BLOWDOWN VALVE AND WAS UNABLE TO, SO THE DECISION WAS MADE TO ESD THE STATION, THUS ENDING THE GAS RELEASE. AN ERL (EMERGENCY RESPONSE LINE) CONFERENCE CALL WAS HELD AT 4:10 AM ABOUT THE EVENT. ON THE CALL IT WAS FORECASTED THAT THE GAS LOSS FROM THE EVENT WOULD EXCEED THE REPORTABLE THRESHOLD OF 3,000 MCF. AT THIS TIME (4:10 AM) SNG HAD CONFIRMED DISCOVERY OF THE INCIDENT. THE PILOT IN THE EMERGENCY BLOWDOWN VALVE WAS REPLACED. AFTER INVESTIGATING, IT WAS DETERMINED THAT THE PILOT ACTUATOR OF THE EMERGENCY BLOWDOWN VALVE HAD A LEAKING SEAL ON THE POWER GAS SIDE. IT IS BELIEVED THAT THE ESCAPING GAS FROM THE SEAL MADE ITS WAY TO THE VENT WHERE IT FROZE OVER THE EXHAUST PORT, PREVENTING THE LEAKING GAS FROM REACHING ATMOSPHERE. THE PRESSURE FROM THE LEAKING GAS CONTINUED TO BUILD, AND UPON REACHING 150 PSI THE VALVE OPERATOR ACTIVATED TO ITS "SAFE STATE" AS IT IS DESIGNED TO DO, AND IN THIS CONFIGURATION THE SAFE STATE HAS THE VALVE IN THE OPEN POSITION. THE VALVE OPERATOR'S SAFE STATE CONFIGURATION RESULTED IN THE EMERGENCY BLOWDOWN VALVE OPENING WITHOUT SNG'S COMMAND. BEFORE THE EVENT, SNG HAD IDENTIFIED THE VALVE OPERATOR AS LEAKING AND MADE PLANS TO ADDRESS THE LEAK, BUT DUE TO NOT BEING AWARE OF THIS OPERATOR'S FAIL SAFE MODE AN INCORRECT ASSESSMENT OF THE TIMEFRAME FOR REPAIR WAS MADE. AT THOMASTON COMPRESSOR STATION, SNG HAS MODIFIED ITS LEAK SURVEY WORK ORDERS ON ESD VENT VALVES WITH THIS TYPE OF OPERATOR SO THAT THE TECHNICIANS WHO COMPLETE THE WORK ORDER ARE INSTRUCTED TO PROMPTLY REPAIR ANY FOUND LEAK ON THE OPERATOR.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200028 | 33573 | 2020-04-06 11:01 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-03-21 14:52 | 2020 | CENTRAL | YES | 32.3106 | -93.9672 | 1273980 | 2020-03-21 17:06 | 1274038 | NATURAL GAS |  | 1 | 2709 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-21 21:00 | 2020-03-25 15:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-21 21:00 | VALVE CLOSURE |  | 2020-03-21 20:30 | 0 | 2020-03-21 14:52 | 2020-03-21 16:30 | ONSHORE | LA | 71129 | KEITHVILLE | CADDO | MILEPOST | 77+2014 | SHARON CARTHAGE 20" NO. 1 | SHC 20-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 20 |  | 0.25 | 52000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR |  | UNKNOWN | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1949 | 1949 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 461 |  | NO | NO | [5 empty] | 0 | 0 | 4930 | 5129.63859618566411 | 2 | 3.51020408163265306122448979591836734694 | 85000 | 88442.044761821795 | 1500 | 1560.7419663850905 | 0 | 0 |  | 1.82 | 91432 | 41971.085755111668418104956268221574344 | 95135.9355284741822630612244897959183673 | 0 | 0 | 0 | 0 | NO |  |  |  | 690 | 165000 | 931 | 192.619(A)(1) |  | 1949-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 52800 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CONSTRUCTION-RELATED CAUSES WHICH RESULTED IN THE GIRTH WELD PIN HOLE LEAK | [13 empty] | YES | [5 empty] | YES | LEAK WAS CAUSED BY A PIN HOLE DEFECT IN GIRTH WELD. | 1219 | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2010 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | MAPPING | 2017 | FREE SWIMMING | 2010 | FREE SWIMMING |  | YES | 1967 | 1219 | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | AT APPROXIMATELY 6:15 PM ON SATURDAY, MARCH 21, 2020 A LANDOWNER NOTIFIED A LOCAL FIRE DEPARTMENT WHO, IN TURN, NOTIFIED TEXAS GAS' CONTROL ROOM OF A POTENTIAL NATURAL GAS LEAK ON THE SHARON CARTHAGE LINE, (SHC 20-1) NEAR BLOCK VALVE #5. THE CADDO PARISH FIRE DEPARTMENT STATED THAT THE LANDOWNER REPORTED BUBBLING FROM THE PIPELINE AND EXPRESSED CONCERN. THE CONTROL ROOM CONTACTED OPERATIONS PERSONNEL WHO TOOK IMMEDIATE STEPS TO ISOLATE THE LEAK AND CLOSE BOTH BLOCK VALVE #5 AND BLOCK VALVE #6. WITH THE LEAK ISOLATED, PLANS WERE MADE TO INVESTIGATE ON MONDAY, MARCH 23. UPON EXCAVATION, IT WAS DISCOVERED THAT THERE WAS A VERY SMALL PINHOLE LEAK ON THE OUTSIDE EDGE OF A GIRTH WELD. A LEAK CLAMP WAS INSTALLED AND THE LEAK WAS STOPPED. ON TUESDAY, MARCH 24, A DRESSER STYLE 220 SLEEVE WAS INSTALLED OVER THE LEAK. THIS REPORT IS REQUIRED BASED ON THE COST OF REPAIR EXCEEDING $50,000. THE RESPONSE TO QUESTION A7 IS SHOWN AS 1 MCF BUT THE ACTUAL ANSWER IS UNKNOWN; TEXAS GAS DOES NOT KNOW HOW LONG THIS LEAK OCCURRED NOR DO WE KNOW THE ORIFICE SIZE SINCE THE REPAIR HAS BEEN COMPLETED. 4-9-2020 UPDATE PER PHMSA'S REQUEST. A LACK OF FUSION DURING CONSTRUCTION RESULTED IN A PIN HOLE DEFECT LEAK IN THE GIRTH WELD. PHMSA ALSO ASKED FOR CONFIRMATION THAT THE OPID RESPONSIBLE FOR THIS INCIDENT IS 19270; THAT IS CORRECT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200029 | 33570 | 2020-04-08 11:11 | ORIGINAL FINAL | 39597 | VALLEY CROSSING PIPELINE, LLC | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-03-12 13:44 | 2020 | CENTRAL | YES | 27.7474 | -97.8141 | 1273364 | 2020-03-12 17:08 | 1273633 | NATURAL GAS |  | 3538 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-12 13:44 | 2020-03-12 16:45 |  | NO |  |  | NO | [11 empty] | 0 | 2020-03-12 13:44 | 2020-03-12 13:44 | ONSHORE | TX | 78380 | ROBSTOWN | NUECES | MILEPOST | 2.91 | AGUA DULCE COMPRESSOR STATION | AGUA-BROW | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2018 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN OF COMPRESSOR STATION | CLASS 1 LOCATION | NO |  | 1386 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 6651 | 11673.1836734693877551020408163265306122 | 1007 | 1047.778106766524089 | 0 | 0 | 0 | 0 |  | 1.88 | 7658 | 8121.554440345202686032069970845481049563 | 12720.9617802359118441020408163265306122 | 0 | 0 | 0 | 0 | NO |  |  |  | 1572 | 0 | 1750 | 192.619(A)(1) |  | 2018-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  |  | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL AND THIS EVENT COULD NOT BE ASSOCIATED WITH THE ROLES AND RESPONSIBILITIES OF A CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL. | [22 empty] | YES | THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL. | [148 empty] | YES | [12 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 832-748-0908 |  | NATHAN ATANU | nathan.atanu@enbridge.com | 713-627-5008 | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 1:45 PM CDT ON MARCH 12, 2020 AN EMERGENCY SHUTDOWN (ESD) SYSTEM WAS ACTIVATED AT AGUA DULCE COMPRESSOR STATION ON THE VALLEY CROSSING PIPELINE (VCP) SYSTEM IN NUECES COUNTY, TEXAS. VCP COMPLETED THE REPORT TO THE NATIONAL RESPONSE CENTER AT APPROXIMATELY 5:08 PM CDT ONCE IT WAS DETERMINED THE GAS VOLUME EXCEEDED 3 MMSCF. THE ESD WAS ACTIVATED BY A FAULTY FUSE IN THE ESD MASTER X22-16 PANEL. TETLP'S INVESTIGATION DETERMINED THAT THE ESD WAS FUNCTIONING AS DESIGNED AT THE TIME OF THE ESD. AS PART OF THE MITIGATIVE PLAN, THE FAULTY FUSE WAS REPLACED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200030 | 33740 | 2020-04-10 12:52 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2020-03-14 13:40 | 2020 | CENTRAL | NO | 32.4106 | -91.4874 | 1273519 | 2020-03-14 17:16 | 1273598 | NATURAL GAS |  | 7313 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE INCIDENT INVOLVED ONLY A SINGLE UNIT BLOW DOWN. |  |  |  | YES | OPERATOR | 2020-03-14 21:06 | NO | [11 empty] | 0 | 2020-03-14 13:02 | 2020-03-14 13:38 | ONSHORE | LA | 71232-6405 | Not Within a Municipality | RICHLAND | NOT APPLICABLE |  | DELHI COMPRESSOR STATION | UNIT 811 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2006 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | UNIT 811 FAULTED AND WAS SHUTDOWN DUE TO A PROGRAMMABLE LOGIC CONTROLLER INPUT/OUTPUT CARD PROGRAM FAILURE. THIS RESULTED IN THE UNIT SUCTION AND DISCHARGE VALVES FAILING TO CLOSE, RESULTING IN AN UNINTENDED RELEASE OF NATURAL GAS INTO ATMOSPHERE. | CLASS 1 LOCATION | NO |  | 152 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 12725 | 22333.6734693877551020408163265306122449 | 0 | 0 | 0 | 0 | 1000 | 1040.494644256727 | THE FAULT OCCURRED BECAUSE OF AN I/O CARD ERROR; REPLACED CARD. | 1.74 | 13725 | 15113.1809057831463177842565597667638484 | 23374.1681136444821020408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 725 | 278061 | 1007 | 192.619(A)(2) |  | 2006-09-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL WERE NOT INPUTTING ANY OPERATIONAL MODE CHANGES TO THE PIPELINE SYSTEM TO BE CONSIDERED AS A CONTRIBUTING FACTOR THAT LED TO THIS INCIDENT. (PLC I/O CARD FAILURE WAS IDENTIFIED AS PROBABLE CAUSE) | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | I/O CARD FAILURE | [148 empty] | YES | [12 empty] | BENSON HUNLEY | REGULATORY COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | (304) 539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER US REGIONAL COMPLIANCE EAST | (304) 550-4866 | paul_shaffer@tcenergy.com | ON MARCH 14, 2020, AN ALARM WAS ACKNOWLEDGED BY THE US NATURAL GAS CONTROL, EAST TEAM, SUBJECT TO AN EMERGENCY SHUTDOWN (ESD) AT DELHI COMPRESSOR STATION (CS) UNIT 811 FAULT SIGNAL. COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) OPERATES AND MAINTAINS DELHI CS WHICH IS CLASSIFIED AS A TRANSMISSION CS, IS LOCATED IN RICHLAND PARISH, LOUISIANA AND NEAR THE CITY OF DELHI. AFTER RECEIVING THE NOTIFICATION FROM COLUMBIA MONITORING CENTER, CS PERSONNEL RESPONDED TO THIS ESD EVENT AT DELHI CS AND ADDRESSED THE UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) THAT WAS VENTING INTO ATMOSPHERE FROM THE BLOW DOWN DISCHARGE STACKS. THE CS PERSONNEL INSPECTED AND SECURED THE AREA TO ENSURE THAT IT WAS SAFE TO OPERATE DISCHARGE VALVES BEFORE MANUALLY CLOSING THEM. PRELIMINARY INVESTIGATION IDENTIFIED THE PROBABLE CAUSE THAT LED TO THIS UNINTENDED RELEASE AT UNIT 811 WAS DUE TO A FAULT SIGNAL ISSUED BY THE PROGRAMMABLE LOGIC CONTROLLER (PLC) AT THE INPUT/OUTPUT (I/O) BLOCK. THE ISSUED COMMAND INITIATED THE ACTIVATION OF THE BLOW DOWN VALVE TO OPEN (AS IT WAS DESIGNED TO) HOWEVER, THE SEQUENCING HAD FAILED TO CLOSE THESE VALVES TO STOP THE FLOW AND REMAINED OPEN FOR APPROXIMATELY 38 MINUTES. THE FAULTY PLC I/O CARD AS INDICATED AT THE UNIT CONTROL PANEL WAS REPLACED. ALL ALARMS WERE CLEARED AT THE PLC CONTROL PANEL, REQUIRED FUNCTIONAL TESTS WERE CONDUCTED WITH NO NEW ERRORS GENERATED (TO ENSURE NORMAL OPERATION OF THE UNIT), THEN THE UNIT WAS RETURNED BACK TO SERVICE. ROUTINE SAFETY CHECKS WERE CONDUCTED WHERE THE UNIT WAS MONITORED FOR A WHILE, VERIFIED THAT ALL SYSTEMS ARE RUNNING IN NORMAL MODE WITH NO NEW ERRORS WERE GENERATED THEREAFTER. A CALCULATED VOLUME OF UNINTENDED RELEASED MATERIAL WAS 7,313 MCF INTO ATMOSPHERE WHERE THE RELEASED MATERIAL DID NEITHER IGNITE NOR CAUSE ANY DAMAGE TO ANY OF THE CS DEVICES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200031 | 33704 | 2020-04-15 11:36 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-03-20 22:11 | 2020 | MOUNTAIN | YES | 40.7438 | -104.217 | 1273946 | 2020-03-20 22:47 | 1273996 | NATURAL GAS |  | 3924 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED, INSPECTED AND RESET |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-03-20 20:02 | 2020-03-20 21:33 | ONSHORE | CO | 80611 | Not Within a Municipality | WELD | SURVEY STATION NO. | 120/8 | NOBLE KEOTA INTERCONNECT | W-040 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2015 | 2014 | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE RELIEF VALVE MALFUNCTION | CLASS 1 LOCATION | NO |  | 428 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 6357 | 11157.1836734693877551020408163265306122 | 500 | 520.2473221283635 | 0 | 0 | 0 | 0 |  | 1.62 | 6857 | 7550.256633649590651603498542274052478134 | 11677.4309955977512551020408163265306122 | 0 | 0 | 0 | 0 | NO |  |  |  | 954 | 20438 | 960 | 192.619(A)(2) |  | 2016-05-19 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE FLUCTUATIONS DID NOT EXCEED OR DROP BELOW ALARM LIMITS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE CALIBRATION | [147 empty] | YES | [13 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 3/20/2020 AT 8:02 PM MDT, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) GAS CONTROL RECEIVED A CALL FROM A NOBLE KEOTA EMPLOYEE ABOUT NOISE COMING FROM THE INTERCONNECT METER FACILITY. SSCGP EMPLOYEE ARRIVED ON SITE AT 9:33 PM AND CONFIRMED THE RELIEF VALVE WAS VENTING. AFTER CONFIRMING THERE WAS NO OVERPRESSURE EVENT THE RELIEF VALVE WAS ISOLATED AT 9:42 PM. THE RELIEF VALVE WAS INSPECTED AND TESTED, IT WAS FOUND THAT THE SET POINT HAD DRIFTED TO 954 PSIG. THE TEMPERATURE AT THE TIME OF THE RELEASE WAS 16 DEGREES F. THE SET POINT WAS ADJUSTED BACK TO 988 PSIG. GAS LOSS WAS CALCULATED AT 10:11 PM AT 3.9 MMCF. THE NRC WAS NOTIFIED AT 10:47 PM. THE RELIEF VALVE WAS PLACED BACK IN SERVICE BY 11:00 PM. IN RESPONSE TO QUESTIONS SUBMITTED BY PHMSA, THE FOLLOWING RESPONSES ARE INCLUDED IN THIS SUPPLEMENTAL REPORT: Q: DID DEBRIS CONTRIBUTE TO THE FAILURE? A: WHEN THE PRESSURE RELIEF VALVE (PRV) WAS INSPECTED AFTER THE RELEASE NO DEBRIS WAS FOUND INSIDE OF THE PRV. THE AS FOUND SET POINT MATCHED THE PRESSURE ACHIEVED (954 PSI) SO THE PRV RELEASED AS SET. Q: HAS THE SET POINT DRIFTED BEFORE? A: THIS PRV RECEIVED ITS LAST ANNUAL INSPECTION ON 8/27/2019 AND THE AS FOUND SET POINT WAS 986 PSI. THE SET POINT WAS READJUSTED TO 988 AT THAT TIME. AT THE TIME, THE 2 PSI DRIFT WAS NOT CONSIDERED ENOUGH FOR CONCERN. Q: WHAT PREVENTATIVE MEASURES ARE BEING TAKEN TO PREVENT THIS IN THE FUTURE? A: THE PRV AT THIS RECEIPT POINT IS SPRING CONTROLLED. THROUGH OUR RESEARCH OF MANUFACTURE INFORMATION AND DISCUSSION WITH OPERATIONS, THE SPRING CONTROLLED PRVS SEEM TO BE MORE SUBJECT TO DRIFTING OF SET POINT AND RESEATING PRESSURES DURING RAPID PRESSURE FLUCTUATIONS AND LOW TEMPERATURES. IN THIS CASE THE VALVE DID NOT RESEAT UNTIL ALL PRESSURE WAS RELIEVED WHEN IT WAS ISOLATED. WE ARE SCOPING A PROJECT TO REPLACE THIS SPRING CONTROLLED PRV WITH A PILOT CONTROLLED PRV. WE ARE LOOKING AT ALL OF OUR RECEIPT POINTS WITH SIMILAR CONFIGURATIONS AND PRIORITIZING REPLACEMENT PROJECTS FOR THOSE ALSO.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200034 | 33892 | 2020-04-22 13:49 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-03-26 13:15 | 2020 | CENTRAL | YES | 32.3738 | -93.9437 | 1274308 | 2020-03-26 16:23 | 1274411 | NATURAL GAS |  | 157000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-26 19:25 | 2020-03-27 14:25 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-03-26 15:00 | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-26 19:25 | VALVE CLOSURE |  | 2020-03-26 19:25 | 0 | 2020-03-26 13:15 | 2020-03-26 15:11 | ONSHORE | LA | 71129 | GREENWOOD | CADDO | NOT APPLICABLE |  | LINE N | LINE N | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 42000 | UNKNOWN | DSAW |  | UNKNOWN | OTHER | PARTIALLY WRAPPED IN TAPE WITH A TAR LIKE SUBSTANCE BETWEEN TAPE AND PIPE OD. | YES | [26 empty] | 1950 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 30 | 24 |  | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 274750 | 482214.2857142857142857142857142857142857 | 165000 | 171681.616302359955 | 10000 | 10404.94644256727 | 0 | 0 |  | 1.75 | 449750 | 396732.6789202138709183673469387755102041 | 664300.8484592129392857142857142857142857 | 0 | 0 | 0 | 0 | NO |  |  |  | 225 | 4000 | 250 | 192.619(C) |  | 2012-11-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 32105 | NO | [5 empty] | YES | LACK OF PIG TRAPS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 1951 | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [14 empty] | YES | [48 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MARCH 26TH, 2020 AT 13:15 ENABLE GAS TRANSMISSION LINE N EXPERIENCED A FAILURE IN CADDO PARISH LOUISIANA. THE FAILED SECTION WAS LOCATED IN A SEASONAL CREEK 12" UNDERGROUND AND THE FAILURE OCCURRED NEAR THE 12 O'CLOCK AREA OF THE PIPE. THE FAILED SECTION WAS REMOVED AND SENT TO PRECISION ENGINEERING FOR METALLURGICAL ANALYSIS. THE NRC WAS NOTIFIED ON 3/26/2020 (NRC # 1274308). A 48 HR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 3/28/2020 (NRC # 1274411). ENABLE MIDSTREAM PARTNERS HAS NOT RECEIVED THE RESULTS OF THE LAB ANALYSIS. THE FAILURE INVESTIGATION IS ON-GOING. _______________________________________________________________________________________________________________________THE LAB ANALYSIS PERFORMED ON THE RUPTURED LINE PIPE INDICATE THAT THE INITIATION OF THE FRACTURE WAS DUE TO DUCTILE OVERLOAD. THE WALL THICKNESS OF THE LINE PIPE IN THE REGION OF THE FACTURE WAS FOUND TO HAVE BEEN REDUCED DUE TO HEAVY O.D. CORROSION AT THE 12 O'CLOCK POSITION (TOP OF LINE). THE WALL IN THIS REGION WAS REDUCED (WALL THICKNESS RANGING FROM 0.013 INCH TO 0.088 INCH MEASURED NEAR RUPTURE) TO THE POINT WHERE IT COULD NO LONGER SUPPORT THE HOOP STRESS GENERATED BY THE INTERNAL LINE PRESSURE (225 PSIG). BY USING THE BARLOW'S FORMULA AND THE TENSILE STRENGTH OBTAINED IN THE MECHANICAL TESTING, IT IS CALCULATED THAT WITH AN INTERNAL PRESSURE OF 225 PSIG AND A TENSILE STRENGTH OF 66,542 PSI, RUPTURE WOULD BE EXPECTED TO OCCUR AT A WALL THICKNESS OF APPROXIMATELY 0.027. THE ANALYSIS PERFORMED ON THE FAILED SECTION OF LINE N SHOW EXTENSIVE O.D. CORROSION OF THE TOP PORTION OF THE PIPE. WALL THICKNESS MEASUREMENTS CONFIRMED THE WALL LOSS WAS CONFINED TO THE 12 O'CLOCK POSITION OF THE PIPE. THIS SECTION OF LINE N WAS LOCATED IN A SEASONAL CREEK AREA WHERE THE PIPE IS BELIEVED TO HAVE BEEN 8-12 INCHES BELOW THE SURFACE PRIOR TO FAILURE. WHEN FULLY EVACUATED, STANDING WATER COULD BE SEEN INSIDE THE FAILED PIPE SEGMENT. THE GAS IN LINE N IS TARIFF QUALITY GAS INDICATING WATER WAS PRESENT ABOVE THE PIPE PRIOR TO RUPTURE. IT IS DETERMINED THAT 70 YEARS OF SEASONAL EXPOSURE TO WATER AND ATMOSPHERE, WITH COATING DETERIORATION AT THE 12 O'CLOCK POSITION, REDUCED THIS SECTION OF PIPE TO WHERE IT COULD NO LONGER SUPPORT THE HOOP STRESS GENERATED BY THE INTERNAL LINE PRESSURE (225 PSIG). ______________________________________________________________________________________________________________________ THE FAILED SECTION OF LINE HAS NEVER BEEN EXPOSED. ALONG WITH ANNUAL PATROLS THERE HAVE BEEN ADDITIONAL EXPOSURE INSPECTIONS ON THIS LINE. A CLOSE INTERVAL SURVEY WAS PERFORMED IN 2016 AND THE CREW DID NOT SEE ANY PIPE EXPOSED AND IN 2018 THE OPS SOUTHERN DIVISION LAUNCHED AN EXPOSED PIPE INITIATIVE. DURING THIS INITIATIVE THE FAILED SECTION WAS NOT SEEN OR DETERMINED TO BE EXPOSED. THERE WAS AN EXPOSURE ROUGHLY 700 FEET TO THE NORTH OF THE FAILURE SITE THAT WAS DISCOVERED IN 2006. THE EXPOSURE WAS ENTERED INTO MAXIMO, WORK ORDERS FOR INSPECTION WERE REGENERATED, AND THE COATING WAS REPAIRED IN 2013. THE SITE CONTINUES TO BE INSPECTED TODAY WITH WORK ORDERS BEING GENERATED FOR FOLLOW UP. IF THE FAILED SECTION WAS ABOVEGROUND, OR VISIBLE, WE WOULD HAVE SEEN IT. THE EXPOSURE WOULD HAVE FOLLOWED THE SAME INSPECTION PROCESS AS THE EXPOSURE 700 FEET DOWNSTREAM. MOST LIKELY THE FAILURE SITE HAS ALWAYS BEEN COVERED BY WATER AND A SMALL AMOUNT OF SOIL. WHEN THE FAILED SECTION WAS REPLACED TAPE COULD BE SEEN ON THE PIPE THROUGH THE ENTIRE EXCAVATION (ROUGHLY 90'). ALSO, IN LOOKING AT EXPOSED SECTIONS OF ORIGINAL LINE N PIPE, THE TAPE HAS BEEN PRESENT AT OTHER LOCATIONS AS WELL. TAPE WAS NOTED ON DOCUMENTATION FOR THE EXPOSURE MENTIONED ABOVE, AS WELL AS, SEEN ON A DIRECT ASSESSMENT DIG NEAR THE SHREVEPORT AREA. DUE TO THE ABOVE EXAMPLES THE TEAM BELIEVES THE TAPE IS PART OF ORIGINAL CONSTRUCTION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200035 | 33698 | 2020-04-22 14:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-03-24 13:32 | 2020 | EASTERN | NO | 37.6055 | -83.9246 | 1274209 | 2020-03-25 14:02 | 1274329 | NATURAL GAS |  | 15900 | 528 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-24 18:03 | 2020-04-06 11:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-24 17:09 | VALVE CLOSURE |  | 2020-03-24 18:03 | 0 | 2020-03-24 13:32 | 2020-03-24 13:32 | ONSHORE | KY | 40336 | IRVINE | ESTILL | SURVEY STATION NO. | 761+46 | KA1S | STATION CAMP | NO | OPERATOR-CONTROLLED PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.322 | 35000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | OTHER | CANUSA TAPE WRAP | YES | [26 empty] | 1990 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 189 |  | NO | NO | [5 empty] | 0 | 0 | 818 | 851.124619002002686 | 24645 | 43254.4897959183673469387755102040816327 | 270900 | 281869.9991291473443 | 0 | 0 | 0 | 0 |  | 1.55 | 296363 | 153106.9999989843680853236151603498542274 | 325975.6135440677143329387755102040816327 | 0 | 0 | 13 | 0 | NO |  |  |  | 600 | 5830 | 1000 | 192.619(A)(2) |  | 1990-03-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | YES | MANUAL | MANUAL | 42240 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER WAS NOTIFIED BY OPERATING PERSONNEL ABOUT THE LEAK AND OTHER MEMBERS OF OPERATIONS WAS ALSO MADE AWARE. CONTROLLER WAS NOT A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | YES | YES | 1991 | YES | YES |  | YES |  |  |  | 2010 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK NEWMAN | REGIONAL COMPLIANCE SPECIALIST | mark_newman@tcenergy.com | 304-549-0532 | 304-722-8420 | TRAVIS ROBERTS | travis_roberts@tcenergy.com | 859-595-3154 | PAUL SHAFFER | COMPLIANCE MANAGER EAST | 304-550-4866 | paul_shaffer@tcenergy.com | ON MARCH 24, 2020 AT 1:32 PM EASTERN STANDARD TIME (EST), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA), OPID 2616 COMPANY PERSONNEL WHILE PERFORMING MAINTENANCE TASKS AT STATION CAMP COMPRESSOR DISCOVERED A PINHOLE LEAK DUE AT THE SOIL-TO-AIR INTERFACE AT THE LAUNCHER ON LINE KA-1S, CLASSIFIED AS TRANSMISSION CARBON STEEL PIPELINE WITH 8.625-INCH IN DIAMETER, 0.322-INCH OF WALL THICKNESS AND GRADE B PIPELINE NEAR STATION CAMP COMPRESSOR. THE LEAK WAS EXPOSED BY HYDROVAC. APPROXIMATELY FIFTEEN FEET OF PRE-TESTED 8.625-INCH, 0.322 WALL, GRADE B, REPLACED THE CORRODED SECTION, WAS COATED, THEN THE EXPOSED PIPE WAS INSPECTED AND RECOATED, AND THE AREA WAS BACK-FILLED WITH FLOWABLE FILL AND OTHER MATERIAL. THIRTEEN CONSUMER TAPS SERVED BY COLUMBIA GAS OF KENTUCKY (CKY) THE LOCAL DISTRIBUTION OPERATOR WERE AFFECTED DURING REPAIRS AND CONVERTED TO BOTTLE GAS AND MONITORED AND MANAGED BY CKY. THE PIPELINE WAS RETURNED TO SERVICE ON APRIL 6, 2020 AT 09:12 EST. LINE KA-1S HAS A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 1,000 PSIG, AND OPERATES AT APPROXIMATELY 650 PSIG.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20200036 | 34060 | 2020-04-22 17:59 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-03-26 14:00 | 2020 | CENTRAL | YES | 37.2104 | -100.3536 | 1274304 | 2020-03-26 16:04 | 1274395 | NATURAL GAS |  | 0.3 | 285 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-27 07:00 | 2020-07-15 13:00 |  | YES | OPERATOR | 2020-03-26 14:09 | NO | [5 empty] | OPERATIONAL CONTROL | NO FAILURE THEREFORE NO ACTION TAKEN. |  | OPERATIONAL CONTROL | NO FAILURE THEREFORE NO ACTION TAKEN. |  | 0 | 2020-03-26 14:00 | 2020-03-26 14:00 | ONSHORE | KS | 67864 | MEADE | MEADE | NOT APPLICABLE |  | BORCHERS STORAGE FIELD | EAST 10" LATERAL - RECEIVER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 1981 | 1981 | CARBON STEEL |  | OTHER | [8 empty] | INCIDENT WAS RESULT OF RELEASE OF STORED ENERGY DURING PIGGING RECEIPT OPERATIONS | CLASS 1 LOCATION | NO |  | 381 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 194 | 201.855960985805038 | 0 | 0 | 0 | 0 | 305 | 317.350866498301735 | 20640 | 21475.80945745884528 | INCIDENT INVESTIGATION. | 0.68 | 21139 | 9703.358791256635551 | 21995.016284942952053 | 0 | 1 | 0 | 0 | NO |  |  |  | 936 | 50000 | 1875 | 192.619(A)(2) |  | 1981-11-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 14 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIGGING OPERATION IS A MANUAL OPERATION; THEREFORE, IT WOULD NOT GENERATE AN ACTIONABLE RESPONSE FROM THE CONTROL CENTER. NOTHING WOULD BE OBSERVABLE WITHIN SCADA FOR THE CONTROL CENTER TO SEE AS IT PERTAINS TO PULLING THE PIG CLEANER FROM THE PIG RECEIVER. | [12 empty] | YES | 6 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ALTHOUGH THE TRAP DOOR WAS OPEN, EMPLOYEE POSITIONED HIMSELF IN FRONT OF THE OPEN RECEIVER IN THE PROJECTED PATH OF THE PIG WITHOUT VERIFYING THAT THE PRESSURE BEHIND THE PIG HAD BEEN RELIEVED. SOP I.13 PIGGING AND PIG TRAP OPERATION WARNS OF THE DANGERS OF STANDING IN FRONT OF THE RECEIVER DOOR AND INSTRUCTS EMPLOYEES TO ENSURE THAT THE TRAP IS DEPRESSURIZED. AS PART OF ON THE JOB TRAINING, EMPLOYEES ARE TAUGHT THE DANGERS OF STANDING IN FRONT OF THE RECEIVER. |  |  | YES |  |  | ROUTINE MAINTENANCE | NO | [149 empty] | YES | KATHRYN HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 832-660-5977 |  |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | ON MARCH 26, 2020, EMPLOYEE WAS RECEIVING A CLEANING PIG ON THE TEN-INCH EAST LINE AT BORCHERS STATION WHEN THE PIG BECAME LODGED IN THE RECEIVER. THE DOOR TO THE RECEIVER WAS OPENED, AND EMPLOYEE HAD POSITIONED HIMSELF IN FRONT OF THE PIG RECEIVER IN AN ATTEMPT TO DISLODGE THE STUCK PIG. SUDDENLY, THE PIG BECAME DISLODGED AND DISCHARGED OUT OF THE BARREL, STRIKING EMPLOYEE. ANOTHER EMPLOYEE CALLED 911 AND ASSISTED INJURED EMPLOYEE UNTIL MEDICAL ASSISTANCE ARRIVED. HIGHWAY PATROL ARRIVED AND ASSISTED WITH FIRST AID UNTIL THE AMBULANCE ARRIVED. EMPLOYEE WAS TRANSPORTED TO MEADE COUNTY HOSPITAL WHERE THE EMPLOYEE PASSED AWAY. PLEASE REFER TO PART G (APPARENT CAUSE). AS IT APPLIES TO PART K (CONTRIBUTING FACTORS), SOP I.13 PIGGING AND PIG TRAP OPERATION REQUIRES A SITE SPECIFIC PIGGING PROCEDURE. HOWEVER, AT THE TIME OF THE INCIDENT, A SITE SPECIFIC PIGGING PROCEDURE WAS NOT LOCATED. IT HAS NOT BEEN DETERMINED THAT THE PRESENCE OF A SITE SPECIFIC PIGGING PROCEDURE AT BORCHERS STATION WOULD HAVE PREVENTED THIS INCIDENT. IN TERMS OF PROCESS IMPROVEMENT, WE HAVE CREATED A SITE SPECIFIC PIGGING PLAN FOR BORCHERS EAST 10" TRAP. A SAFETY ALERT HAS BEEN DISTRIBUTED COMPANY-WIDE IN ORDER TO REINFORCE OUR CURRENT PIGGING PROCEDURES AND STRESS THE IMPORTANCE OF PROPER SAFETY PROTOCOLS WHEN ENGAGING IN PIGGING ACTIVITIES. WE HAVE WORKED WITH LOCAL FIELD PERSONNEL TO REINFORCE OUR PIGGING PROCEDURES. ALSO, WE HAVE DEVELOPED A TEAM TO REVIEW AND ASSESS CURRENT PIGGING PROCEDURES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200037 | 34851 | 2020-04-23 14:54 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-03-26 08:45 | 2020 | EASTERN | YES | 40.2731 | -81.5744 | 1274263 | 2020-03-26 11:17 | 1274397 | NATURAL GAS |  | 8538 | 84.7 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-28 18:55 | 2020-04-24 12:00 |  | YES | OPERATOR | 2020-03-26 10:21 | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-28 14:09 | VALVE CLOSURE |  | 2020-03-28 18:50 | 0 | 2020-03-26 08:45 | 2020-03-26 09:58 | ONSHORE | OH | 43832 | NEWCOMERSTOWN | TUSCARAWAS | SURVEY STATION NO. | 62+61 | O-1460 | O-1460-100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER THE RIVER |  | NO | YES | [6 empty] | YES | UNCASED | TUSCARAWAS RIVER | 7 | BELOW WATER, PIPE ON OR ABOVE BOTTOM | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.25 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1954 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 140 |  | NO | NO | [5 empty] | 0 | 0 | 131 | 136.304798397631237 | 3966 | 6960.73469387755102040816326530612244898 | 2268855 | 2360731.476095096337585 | 0 | 0 | 0 | 0 |  | 1.55 | 2272952 | 1046091.7048292197219661282798833819242 | 2367828.51558737151984240816326530612245 | 0 | 0 | 0 | 0 | NO |  |  |  | 185 | 328 | 280 | 192.619(C) |  | 1976-05-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 32594 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | EROSION |  |  | YES | YES |  |  | YES | YES | 1954 | NO | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON MARCH 26, 2020 AT 08:45 EASTERN DAYLIGHT TIME (EDT), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) MONITORING CENTER RECEIVED A CALL FROM A PASSER-BY REGARDING THE OBSERVATION OF GAS BUBBLING IN TUSCARAWAS RIVER. COLUMBIA OPERATIONS PERSONNEL WERE ON SITE AT 09:58 EDT AND CONFIRMED THAT THE UNINTENDED NATURAL GAS (MATERIAL) RELEASE WAS FROM LINE O-1460. THE INVOLVED SECTION OF LINE O-1460 IN THIS EVENT CROSSED AT THE BOTTOM A RIVER. LINE O-1460 IS CARBON STEEL TRANSMISSION PIPELINE WITH 6 INCH IN DIAMETER AND MAXIMUM ALLOWABLE OPERATING PRESSURE OF 280 PSIG OPERATED AND MAINTAINED BY COLUMBIA. ON MARCH 28, 2020 AT APPROXIMATELY 18:55 EDT, THE AFFECTED SECTION OF LINE O-1460 WAS ISOLATED AND EMERGENCY BLOWDOWN OF THE AFFECTED SECTION WAS INITIATED. THE BLOWDOWN WAS COMPLETED AT 19:28 EDT. THE LEAK WAS ISOLATED AND THE AFFECTED SECTION OF THE LINE O-1460 WAS ISOLATED AND REMOVED FROM SERVICE. A COMPRESSED NATURAL GAS TANKER WAS CONNECTED AND STARTED FEEDING THE DOWNSTREAM CUSTOMERS WHOSE SERVICE IS PROVIDED BY THE LOCAL DISTRIBUTION OPERATOR. THE RIVER-CROSSING SECTION OF LINE O-1460 WAS CUT AND CAPPED ON BOTH ENDS. THE INITIAL NATIONAL RESPONSE CENTER REPORT NO.1278263 AND THE NRC 48-HOUR REPORT NO. 1274397 HAVE BEEN CALLED-IN ON MARCH 26TH AND MARCH 28TH RESPECTIVELY. THE INVOLVED SEGMENTS OF LINE O-1460 IN THIS INCIDENT WERE SENT TO A METALLURGICAL FAILURE ANALYSIS LABORATORY TO ESTABLISH THE ROOT CAUSE BEHIND THIS RIVER-CROSSING PIPELINE FAILURE. THE METALLURGICAL FAILURE ANALYSIS REPORT OF LINE O-1460 IDENTIFIED THAT THE CAUSE OF THE LEAK IS EROSION-CORROSION. THE CONSTRUCTION OF THE REPLACEMENT SECTION FOR LINE O-1460 WAS COMPLETED BY USING HORIZONTAL DIRECTIONAL DRILLING (HDD) METHOD FOR INSTALLING PIPE UNDER THE TUSCARAWAS RIVER. THE HDD METHOD WILL HELP PROTECT THE PIPE TO AVOID FUTURE EVENTS FROM RE-OCCURRING.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200038 | 33730 | 2020-04-24 16:21 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-04-24 00:39 | 2020 | CENTRAL | YES | 42.0471 | -94.046 | 1275984 | 2020-04-24 10:00 |  | NATURAL GAS |  | 3508 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REGULATOR FAILED OPEN, RELIEF VALVE KEPT MAOP WHILE STILL SERVING |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-24 00:09 | 2020-04-24 00:30 | ONSHORE | IA | 50212 | Not Within a Municipality | BOONE | MILEPOST | 0 | NORTHERN NATURAL GAS | 179IAB66001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED AFTER A REGULATOR FAILURE. | CLASS 1 LOCATION | YES | METHOD2 | 166 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 6314 | 11081.7142857142857142857142857142857143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.8 | 6314 | 7271.224489795918367346938775510204081633 | 11081.7142857142857142857142857142857143 | 0 | 0 | 0 | 0 | NO |  |  |  | 465 | 8400 | 500 | 192.619(A)(3) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS NOT DRIVEN BY A CONTROL ROOM FACTOR | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [267 empty] | YES | [38 empty] | JEFFREY CULLISON |  | j.cullison@nngco.com | 402-398-7439 |  |  |  |  | TOM CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | AT 0009 THE OCC RECEIVED A CALL FROM LOCAL POLICE THAT A NOISE WAS HEARD AT THE OGDEN COMPRESSOR STATION THAT SOUNDED LIKE A JET. TECHNICIANS ARRIVED AND COULD HEAR VENTING GAS AND WENT TO HMI TO SEE WHERE THE GAS COULD BE VENTING FROM. ONCE DETECTED, TECHNICIANS WENT TO THE REGULATOR LOCATION AND STARTED TO BRING PRESSURE DOWN BY CLOSING THE ISOLATION VALVE UPSTREAM OF THE REGULATOR. ONCE THE PRESSURE CAME DOWN, THE RELIEF VALVE SET AND THE GAS WAS NO LONGER VENTING. IT WAS FOUND THAT THE CIRCUIT CARD THAT CONTROLS THE READINGS FOR THE REGULATOR WAS DAMAGED BY A LIGHTNING STRIKE. THE CARD WAS REPLACED, AND THE SYSTEM TESTED AND RETURNED TO NORMAL OPERATION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200039 | 34134 | 2020-04-28 12:48 | SUPPLEMENTAL FINAL | 11248 | LAS VEGAS NATURAL GAS SYSTEM | 905 12TH ST. P.O. BOX 179 | LAS VEGAS | NM | 87701 | 2020-04-01 13:40 | 2020 | MOUNTAIN | YES | 35.8677 | -104.8773 | 1274991 | 2020-04-07 15:04 | 1275182 | NATURAL GAS |  | 156.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | NORMAL OPERATION |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-04-01 13:40 | NO | [5 empty] | OPERATIONAL CONTROL | LOWERED PRESSURE |  | OPERATIONAL CONTROL | LOWERED PRESSURE |  | 0 | 2020-04-01 13:40 | 2020-04-01 14:20 | ONSHORE | NM | 87701 | WATROUS NM | MORA COUNTY | MILEPOST | 371 | LAS VEGAS NATURAL GAS SYSTEM | 11248 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.322 | 42000 | UNKNOWN | CONTINUOUS WELDED |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | [9 empty] | CLASS 1 LOCATION | NO |  | 96 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 12824 | 22507.4285714285714285714285714285714286 | 63594 | 66169.216406862296838 | 2000 | 2080.989288513454 | 1000 | 1040.494644256727 | LABOR | 82.1 | 79418 | 45336.5664700435455949795918367346938776 | 91798.1289110610492665714285714285714286 | 0 | 0 | 0 | 0 | NO |  |  |  | 295 | 4489 | 300 | 192.619(A)(1) |  | 2008-04-10 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | STATE | NO |  |  |  | 158840 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | GAS LINE HIT BY DOZER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | GRADING | NO | [5 empty] | NO |  | OTHER |  |  |  | NO LOCATES WERE CALLED IN TO 811 | [262 empty] | KENNY LUCERO | GAS MANAGER | klucero@lasvegasnm.gov | 505-429-3202 |  | KENNY LUCERO | klucero@lasvegasnm.gov | 505-429-3202 | KENNY LUCERO | GAS MANAGER | 505-429-3202 | klucero@lasvegasnm.gov | ZACH BARLETT RANCH HAND WAS OPERATING DOZER WHEN HE HIT THE TRANSMISSION GAS LINE AT MILE MARKER 371 NORTH OF WATROUS, NM, OPERATOR DID NOT CALL 811 FOR LOCATES. 8'' BOLTED WRAP AROUND CLAMP WAS TEMPORARY INSTALLED AND WAS MONITORED DAILY . UNTIL CONTRACTOR PERMANENTLY REPAIRED IT . WORK STARTED ON 4/15/2020 AND COMPLETED ON 4/17/2020. REPAIRED BY INSTALLING TWO 8" STOPPLE FITTINGS, PLUGGED LINE AND INSTALLED 3"FEET OF 8'' PIPE . ALSO INSTALLED ONE 2'' BY-PASS . ALL FITTINGS WERE PRESSURE TESTED AT 500LBS. PIPE WAS PIPE WRAPPED. LEAK IS COMPLETELY REPAIRED AND FINISHED BY THE CONTRACTOR.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200040 | 34016 | 2020-04-28 16:08 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-07 19:53 | 2020 | CENTRAL | YES | 28.686 | -96.8194 | 1275005 | 2020-04-07 21:30 | 1275048 | NATURAL GAS |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-04-07 19:00 | 2020-04-07 19:53 | ONSHORE | TX | 77977 | PLACEDO | VICTORIA | MILEPOST | PLACEDO CG | PLACEDO CITY GATE STATION | 4793 PLACEDO CGSTA AND 2IN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1991 | 1989 | CARBON STEEL |  | OTHER | [8 empty] | DISRUPTION ONLY | CLASS 1 LOCATION | NO |  | 45 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  | 117 | 0.01 | 668 | 192.619(A)(1) |  | 1990-12-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | OTHER | CENTER POINT PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE DISRUPTION DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [142 empty] | YES | [5 empty] | YES | CHRIS PALAFOX | REGULATORY COMPLIANCE SPECIALIST | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER-INTRASTATE REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON APRIL 7, 2020 AT APPROXIMATELY 19:53, A DISRUPTION OF GAS FLOW TO THE PLACEDO, TX CITY GATE STATION OCCURRED. THE PLACEDO CITY GATE STATION IS LOCATED HALF A MILE SOUTHEAST FROM THE CITY OF PLACEDO, TX IN VICTORIA COUNTY. AT APPROXIMATELY 19:00, CENTERPOINT NOTIFIED COMPANY PERSONNEL THAT THERE WAS A DISRUPTION OF GAS FLOW AT THE PLACEDO CITY GATE STATION. AT APPROXIMATELY 19:53, COMPANY PERSONNEL ARRIVED AT THE PLACEDO CITY GATE STATION AND CONFIRMED THAT THE PRIMARY RUN VALVE WAS CLOSED. THE VALVE WAS OPENED RESUMING GAS FLOW BACK TO THE CITY GATE. COMPANY MEASUREMENT TECHNICIAN WAS DOING SOME ROUTINE TESTING ON THE METER/REGULATOR ON THE CITY GATE STATION. THE TECHNICIAN OPENED UP THE BYPASS ON THE STATION AND CLOSED THE PRIMARY RUN ON THE METER TO ALLOW HIM TO COMPLETE HIS TESTING. ONCE HE COMPLETED HIS TESTING, HE CLOSED THE STATION BYPASS AND DID NOT OPEN THE VALVE TO PLACE THE PRIMARY RUN ON THE METER/REGULATOR BACK INTO SERVICE. THIS SHUT IN/STOPPED THE GAS SUPPLY FOR THE STATION. THE TECHNICIANS' OPERATOR QUALIFICATION FOR THE TASK WERE PULLED AND THE INDIVIDUAL WILL BE RE-TRAINED TO PREVENT FURTHER DISRUPTIONS. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON APRIL 7, 2020, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1275005) AT 21:30 AND TO THE TXRRC (INCIDENT#2178) AT 21:40. A 48 HOUR NRC UPDATE WAS MADE ON APRIL 8, 2020 AT 11:35 (NRC#1275048)
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200041 | 34111 | 2020-05-01 13:20 | SUPPLEMENTAL FINAL | 32626 | THIRD COAST ALABAMA, LLC | BLACK BEAR TRANSMISSION 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2020-03-28 09:14 | 2020 | CENTRAL | YES | 33.3506 | -87.6798 | 1274435 | 2020-03-29 02:27 | 1274549 | NATURAL GAS |  | 148.129 | 1025 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-03-28 11:41 | 2020-05-15 08:25 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-03-28 09:55 | VALVE CLOSURE |  | 2020-03-28 10:00 | 0 | 2020-03-28 09:14 | 2020-03-28 09:55 | ONSHORE | AL | 35452 | MONTGOMERY | TUSCALOOSA | MILEPOST | 6.045 | MONTGOMERY | COLUMBUS | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.25 | 36 | X-42 | SEAMLESS |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1949 | 1948 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 185 |  | NO | NO | [5 empty] | 0 | 0 | 2076 | 2160.066881476965252 | 300 | 526.530612244897959183673469387755102041 | 225000 | 234111.294957763575 | 5000 | 5202.473221283635 | 0 | 0 | OPERATOR'S COST - UNKNOWN, STILL UNDER INVESTIGATION | 2.025 | 232376 | 106874.4888001504560997434402332361516035 | 242000.365672769073211183673469387755102 | 0 | 0 | 0 | 0 | NO |  |  |  | 460 | 20000 | 500 | 192.619(A)(1) |  | 1948-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 5280 | NO | [5 empty] | YES | NO LAUNCHERS / RECEIVERS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DROP IS PRESSURE WAS NOT ENOUGH TO TRIGGER AN ALARM AND THE EVENT WAS DUE TO CORROSION NOT A CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1971 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 3462413585 |  | KEVIN STANLEY | kstanley@3cmidstream.com | 3462413585 | KEVIN STANLEY | SR. MANAGER EHS | 3462413585 | kstanley@3cmidstream.com | THE LEAK OCCURRED ON THE THIRD COAST ALABAMA, LLC., 12 INCH MONTGOMERY COLUMBUS PIPELINE DUE TO EXTERNAL CORROSION (LOCALIZED PITTING). A COUPON HAS BEEN CUT OUT AND SENT TO A THIRD PARTY FOR METALLURGICAL ANALYSIS AT THE POINT OF FAILURE AS A PART OF THE INVESTIGATION INTO THE ROOT CAUSE. A NEW PIECE OF PIPE WAS PRE-HYDROTESTED AND WELDED INTO PLACE AND THE LINE WAS PLACED BACK INTO SERVICE. CORROSION CONTROL-CORROSION MONITORING SUBPART I REQUIREMENTS FOR CORROSION CONTROL IN ACCORDANCE WITH SCOPE 192.451 IT IS THE INTENT OF THIRD COAST ALABAMA, LLC TO CONTINUE TO MAINTAIN REQUIREMENTS FOR THE PROTECTION OF METALLIC PIPELINES FROM EXTERNAL, INTERNAL, AND ATMOSPHERIC CORROSION PROGRAMS ESTABLISHED. IT IS ALSO A CRITICAL REQUIREMENT THAT THIRD COAST ALABAMA, LLC WILL MAINTAIN AND SUPPORT UNDER 195.453 AND UNDER THE CORROSION CONTROL PROCEDURES REQUIRED BY 192.605(B)(2), INCLUDING THOSE FOR DESIGN, INSTALLATION, OPERATION, AND MAINTENANCE OF CATHODIC PROTECTION SYSTEMS, MUST BE CARRIED OUT BY, OR UNDER THE DIRECTION OF , A PERSON QUALIFIED IN PIPELINE CORROSION CONTROL METHODS. I. EXTERNAL CORROSION CONTROL PROGRAM THE CURRENT EXTERNAL CATHODIC PROTECTION PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.457, 192.459, 192.461, 192.463, 192.467, 192.469, 192.471, 192.473 THE CURRENT EXTERNAL CORROSION CONTROL: MONITORING PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.465 (A-E). II. INTERNAL CORROSION CONTROL PROGRAM THE CURRENT INTERNAL CORROSION CONTROL PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.475, 192.476, 192.461, 192.463, 192.467, 192.469, 192.471, 192.473 THE CURRENT INTERNAL CORROSION CONTROL: MONITORING PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.477. III. ATMOSPHERIC CORROSION CONTROL PROGRAM THE CURRENT ATMOSPHERIC CORROSION CONTROL PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.479 THE CURRENT ATMOSPHERIC CORROSION CONTROL: MONITORING PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.481. IV. CORROSION CONTROL PROGRAM REMEDIAL MEASURES THE CURRENT REMEDIAL CORROSION CONTROL PROGRAM AND GOING FORWARD WILL ADHERE TO THE STRINGENT REQUIREMENTS OF 192.483, 192.485. THIRD COAST ALABAMA, LLC RESERVES THE RIGHT TO CONDUCT DIRECT ASSESSMENT UNDER 192.490 AS DEFINED IN 192.903. FURTHERMORE, THIRD COAST ALABAMA, LLC WILL CONTINUE TO MAINTAIN A STRICT GUIDELINE TO CORROSION CONTROL RECORDS AS MANDATED BY STATUTE UNDER 192.491. 8-5-2020 UPDATE AN ANALYSES PERFORMED BY A THIRD PARTY INDICATED THAT THE SAMPLE PERFORATED FROM WALL LOSS DUE TO UNDERGROUND EXTERNAL CORROSION IN THE LOCATIONS WITH INADEQUATE COATING OR COATING DISBONDMENT AND INSUFFICIENT CATHODIC PROTECTION. SIDERITE IN THE OUTSIDE SURFACE DEPOSITS AND THE GHOST PEARLITE OBSERVED IN THE CORROSION SCALE INDICATED CONTRIBUTION FROM CARBONIC ACID CORROSION, WHICH REQUIRES PRESENCE OF CO2 AND WATER. THE SOURCE OF THE C02 IS LIKELY FROM THE GEOCHEMICAL REACTIONS IN THE SOIL.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200042 | 34242 | 2020-05-01 15:59 | SUPPLEMENTAL FINAL | 13769 | NORTHERN BORDER PIPELINE COMPANY | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2020-04-02 00:58 | 2020 | CENTRAL | YES | 45.5331 | -98.7855 | 1274697 | 2020-04-02 11:43 | 1274807 | NATURAL GAS |  | 35490 | 700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-02 01:40 | 2020-04-02 07:45 |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-02 01:30 | 2020-04-02 02:17 | ONSHORE | SD | 57481 | WETONKA | EDMUNDS | MILEPOST | 505.95 | NORTHERN BORDER PIPELINE | WETONKA COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | VARIOUS MATERIALS IN THE VALVE OPERATOR. | OTHER | [8 empty] | MALFUNCTION OF STATION VENT VALVE OPERATOR. | CLASS 1 LOCATION | NO |  | 1221 |  | NO | NO | [5 empty] | 0 | 0 | 1218 | 1267.322476704693486 | 61753 | 108382.8163265306122448979591836734693878 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.74 | 62971 | 71674.0649846432891246822157434402332362 | 109650.1388032353057308979591836734693878 | 0 | 0 | 0 | 0 | NO |  |  |  | 1020 | 200900 | 1435 | 192.619(A)(1) |  | 1992-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALARMS PRESENTED TO THE CONTROLLER DID NOT INDICATE A GAS RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | MALFUNCTION OF STATION VENT VALVE OPERATOR. | [15 empty] | YES | COMPONENTS OF THE VENT VALVE OPERATOR FAILED. | [161 empty] | ARTHUR GRELL | MANAGER US REGULATORY COMPLIANCE WEST | art_grell@tcenergy.com | 509-413-7603 |  |  |  |  | LEE ROMACK | DIRECTOR PIPELINE REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | AUGUST 31, 2020 - THE STATION VENT/BLOWDOWN VALVE OPERATOR WAS INSPECTED AND COMPONENTS OF THE ELEMENTARY CONTROL SENSOR (ECS) WERE DIRTY, WORN, AND DEGRADED. THE ECS MONITORS GAS PRESSURE ON THE PIPING AND WHEN THE PRESSURE LOWERS TO A SPECIFIED VALUE THE ECS WILL SIGNAL THE REVERSE RELAY TO ACTIVATE AND SEND SIGNAL TO SOLENOID TO OPEN VALVE. THE ECS, REVERSE RELAY AND TWO SOLENOIDS WERE REPLACED AT THIS LOCATION AND TESTED. THE SYSTEM IS NOW FUNCTIONING CORRECTLY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200043 | 34275 | 2020-05-01 16:18 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2020-04-05 18:00 | 2020 | EASTERN | YES | 40.0499 | -80.9638 | 1274863 | 2020-04-05 19:33 | 1274988 | NATURAL GAS |  | 4780 | 8998 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-05 21:18 | 2020-04-17 11:38 |  | YES | OPERATOR | 2020-04-05 19:08 | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-05 20:35 | VALVE CLOSURE |  | 2020-04-05 21:18 | 0 | 2020-04-05 19:00 | 2020-04-05 19:00 | ONSHORE | OH | 43950 | Not Within a Municipality | BELMONT | SURVEY STATION NO. | 87529 | TPL 15 | L#268 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 216 | NO | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.375 | 60000 | API 5L | SINGLE SAW |  | REPUBLIC/BETHLEHEM STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1965 | 1965 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | YES | METHOD2 | 633 |  | NO | NO | [5 empty] | 66919 | 69628.861099015914113 | 16871 | 17554.185143255241217 | 8963 | 15730.9795918367346938775510204081632653 | 807905 | 840620.825568231026935 | 56144 | 58417.531307149680688 | 0 | 0 |  | 1.875 | 956802 | 445404.9336265624681833615160349854227405 | 1001952.38270948859764687755102040816327 | 0 | 0 | 0 | 0 | NO |  |  |  | 733 | 489000 | 820 | 192.619(A)(2) |  | 1965-09-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 35376 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS CAUSED BY DAMAGE TO THE PIPE. THE LEAKING AREA WAS TOO SMALL TO HAVE TRIGGERED ANY PRESSURE OR FLOW ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO | YES | COUNTY ROAD | [9 empty] | CONTRACTOR | AUGER | ROAD WORK | YES | A93110237200AEOB |  | UTILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [118 empty] | YES | YES | YES |  | YES |  |  |  | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2018 | FREE SWIMMING | HIGH RESOLUTION | [17 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2011 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [13 empty] | YES | NO |  |  | NO | [13 empty] | NO | [63 empty] | JEFFERY BURDETTE | SUPERVISOR - PIPELINE COMPLIANCE | jeffery.l.burdette@dominionenergy.com | 3307545524 |  | JEFFERY BURDETTE | jeffery.l.burdette@dominionenergy.com | 3307545524 | REID HESS | MANAGER GAS PIPELINE COMPLIANCE | 8013243374 | reid.hess@dominionenergy.com | TPL-15 WAS TAKEN OUT OF SERVICE FOR A REPAIR RESULTING FROM AN ILI INSPECTION. A SECOND PARTY CONTRACTOR WAS HIRED TO INSTALL A RETAINING WALL AS PART OF THE REPAIR PROJECT. THE CONTRACTOR HIT THE PIPELINE WHILE AUGURING TO INSTALL SUPPORT BEAMS FOR THE RETAINING WALL BUT THE DAMAGE WAS NOT SEEN OR DETECTED AT THE TIME. THE LINE WAS PLACED BACK IN SERVICE ON DECEMBER 19TH, 2019 WITH NO APPARENT ISSUES. ON APRIL 5, 2020, DOMINION RECEIVED THE NOTICE OF A POTENTIAL GAS LEAK ON AIRPORT ROAD NEAR ST. CLAIRSVILLE, OHIO. DOMINION REPRESENTATIVES REPORTED TO THE AREA AND VERIFIED THE LEAK. THE LINE WAS TAKEN OUT OF SERVICE AND THE AREA MADE SAFE BY APPROXIMATELY 22:54 ON THE SAME DAY. EXCAVATION BEGAN ON APRIL 6, 2020, THE LEAK AREA WAS CONFIRMED ON APRIL 10, 2020, AND EXCAVATION WAS COMPLETED ON APRIL 13, 2020. THE REPLACEMENT OF THE DAMAGED PIPELINE SEGMENT WAS COMPLETED ON APRIL 16, 2020.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200044 | 33970 | 2020-05-01 21:41 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-04-03 13:40 | 2020 | CENTRAL | YES | 32.9086 | -96.916 | 1274764 | 2020-04-03 13:53 | 1274837 | NATURAL GAS |  | 258 | 308 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-03 18:19 | 2020-04-04 04:58 |  |  |  |  | NO | [11 empty] | 0 | 2020-04-03 11:38 | 2020-04-03 11:56 | ONSHORE | TX | 75234 | DALLAS | DALLAS | SURVEY STATION NO. | 4599+15 | LINE D | 119313489 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | SKIDSTEER SCRAPER/GRADER CAME IN CONTACT WITH ABOVEGROUND TAP CAUSING IT TO BEND AND BREAK | CLASS 4 LOCATION | YES | METHOD1 | 276 |  | NO | NO | [5 empty] | 0 | 0 | 1186 | 1234.026648088478222 | 994 | 1744.571428571428571428571428571428571429 | 73275 | 76242.245057911670925 | 9351 | 9729.665418444654177 | 0 | 0 |  | 3.852 | 84806 | 39616.6134107740271161632653061224489796 | 88950.5085530162318954285714285714285714 | 0 | 0 | 0 | 1 | NO |  |  |  | 311 | 48000 | 400 | 192.619(A)(1) |  | 1974-12-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE OF PIPELINE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO | YES | INTERSTATE HIGHWAY | [9 empty] | CONTRACTOR | GRADER/SCRAPER | LANDSCAPING | NO | [5 empty] | YES | 11 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | JEFF BROWN | OPERATIONS SUPERVISOR | jeffrey.brown@atmosenergy.com | 972-360-4404 |  |  |  |  | MARLO SUTTON | VP TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | AT APPROXIMATELY 11:00 AM ON APRIL 3, 2020 , A THIRD PARTY CONTRACTOR WAS LEVELING GROUND AND INSTALLING UNDERGROUND IRRIGATION NEAR THE INTERSECTION OF COMMERCE RD. AND I-635 SERVICE ROAD IN DALLAS, TX. ATMOS ENERGY DID NOT RECEIVE PRIOR NOTIFICATION OF THE EXCAVATION ACTIVITY, AND NO NOTIFICATION WAS MADE BY THE CONTRACTOR TO THE ONE-CALL CENTER. THE CONTRACTOR STRUCK A TAP ON ATMOS' LINE D, CAUSING A RELEASE OF GAS. ATMOS ENERGY WAS NOTIFIED OF THE INCIDENT BY THE FARMERS BRANCH FIRE DEPARTMENT AT 11:11 AM. THE RELEASE WAS SECURED AT 6:19 PM WHEN LINE D WAS TAKEN OUT OF SERVICE TO MAKE REPAIRS. LINE D WAS PLACED BACK IN SERVICE AT 4:58 AM ON APRIL 4, 2020. 48 HOUR NRC # 1274837
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200045 | 33724 | 2020-05-01 22:10 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-07 07:00 | 2020 | CENTRAL | YES | 32.8015 | -103.8025 | 1274969 | 2020-04-07 14:03 | 1275108 | NATURAL GAS |  | 13266 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ISOLATED VENTING RELIEF VALVE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-07 07:00 | 2020-04-07 07:00 | ONSHORE | NM | 88220 | CARLSBAD | LEE | SURVEY STATION NO. | 511+54.7 | MALJAMAR COMPRESSOR STATION | NMBW119G | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN | 1997 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED AT A LOWER PRESSURE THAN DESIRED AND FAILED TO RESET. | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 15389 | 27009.265306122448979591836734693877551 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.16 | 15389 | 17722.0262390670553935860058309037900875 | 27009.265306122448979591836734693877551 | 0 | 0 | 0 | 0 | NO |  |  |  | 978 | 26.9 | 1172 | 192.619(A)(2) |  | 1995-06-22 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO SAFETY RELATED ALARMS FOR THE CONTROL ROOM PERSONNEL TO RESPOND TO. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PRV OPERATED UNEXPECTEDLY AT LOWER THAN SET PRESSURE. | [161 empty] | KATHRYN HARRYMAN | REGULATORY COMPLIANCE SENIOR SPECIALIST | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR REGULATORY COMPLIANCE | 713-823-3795 | danny.nichols@energytransfer.com | AT 0700 NOTIFIED BY DURANGO PLANT EMPLOYEE THAT THE RELIEF VALVE WAS VENTING AT THE MALJAMAR CS. UPON INVESTIGATION ET OPERATIONS PERSONNEL VERIFIED THAT THE RELIEF VALVE WAS VENTING AND BLOCKED IT IN. THE RELIEF VALVE WAS REPAIRED AND TESTED BY COMPANY EMPLOYEES PRIOR TO BEING PUT BACK IN SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200046 | 34427 | 2020-05-05 14:36 | SUPPLEMENTAL FINAL | 32005 | ENLINK PROCESSING SERVICES, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2020-04-06 02:04 | 2020 | CENTRAL | YES | 31.9111 | -93.2461 | 1274875 | 2020-04-06 07:53 | 1274998 | NATURAL GAS |  | 11600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-06 07:58 | 2020-05-23 14:00 |  | YES | OPERATOR | 2020-04-06 08:08 | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-06 09:00 | VALVE CLOSURE |  | 2020-04-06 07:58 | 0 | 2020-04-06 07:30 | 2020-04-06 07:30 | ONSHORE | LA | 71019 | Not Within a Municipality | NATCHITOCHES PARISH | MILEPOST | MP1.16 | CAMPTI 8" LATERAL-P1330 | CAMPTI 8" LATERAL - RED RIVER CROSSING/P1330 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO LOSS OF COVER |  |  | NO | YES | [6 empty] | YES | UNCASED | RED RIVER | 60 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | YES | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8 |  | 0.5 | 35000 | 5L GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | REPUBLIC STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1974 | 1973 | CARBON STEEL |  | OTHER | [8 empty] | UNKNOWN DUE TO NOT BEING ABLE TO INSPECT THE PIPE DUE TO SAFETY REASONS. DECISION WAS MADE TO REPLACE THE CROSSING. WATER DEPTH AND VELOCITY IN THE RED RIVER WAS CONSIDERED TO DANGEROUS FOR DIVERS. | CLASS 1 LOCATION | NO |  | 160 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 20080 | 35242.4489795918367346938775510204081633 | 960360 | 999249.43655839034172 | 0 | 0 | 0 | 0 |  | 1.731 | 980440 | 463954.7791093892782137609329446064139942 | 1034491.88553798217845469387755102040816 | 0 | 0 | 0 | 0 | NO |  |  |  | 347 | 11600 | 720 | 192.619(A)(2) |  | 1974-03-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 5 | NO | [5 empty] | YES | LINE DOES NOT HAVE LAUNCHERS OR RECEIVERS INSTALLED. | YES |  |  |  |  | YES | CUSTOMER CONCERNED WITH LOSING SUPPLY | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | CAUSE OF THE INCIDENT IS UNKNOWN. INCIDENT IS LOCATED AT A MAJOR RIVER CROSSING. THE CROSSING WILL BE REPLACED AND ABANDONED IN PLACE. SEE PART C COMMENTS. | [145 empty] | CORDELL THERIOT | SR. DOT SPECIALIST | cordell.theriot@enlink.com | 3373226682 |  | CORDELL THERIOT | cordell.theriot@enlink.com | 3373226682 | CORDELL THERIOT | SR. DOT SPECIALIST | 3373226682 | cordell.theriot@enlink.com | PIPELINE CONTROL DETERMINED LOSS OF VOLUMES OF GAS AND LOSS OF PRESSURE THROUGH THE SCADA SYSTEM. AT 02:04 AM, OPERATIONS PERSONNEL WERE IMMEDIATELY CALLED OUT TO INVESTIGATE. AFTER CONFIRMED DISCOVERY WAS MADE, AT 07:30 AM, ON WHICH PIPELINE THE INCIDENT WAS LOCATED ON, OPERATIONS IMMEDIATELY ISOLATED THE AFFECTED PORTION OF THE PIPELINE AND ALLOWED THE LINE TO DEPRESSURIZE COMPLETELY. TO ADD MORE COMMENTS FOR PART E8. THE SINGLE CUSTOMER IS SOMEWHAT ADVERSE TO ONSTREAM PIGGING AS ENLINK IS THEIR SOLE SUPPLIER AND THEY ARE CONCERNED ABOUT SUPPLY INTERRUPTION. PART C QUESTION 3 IS UNKNOWN IF PIPE BODY OR PIPE SEAM. CHOSE PIPE SEAM DUE TO QUESTION REQUIRES AND ANSWER TO SUBMIT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200047 | 34015 | 2020-05-06 14:20 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2020-04-09 18:35 | 2020 | CENTRAL | YES | 29.3668 | -98.2089 | 1275138 | 2020-04-09 20:44 | 1275231 | NATURAL GAS |  | 30300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-09 18:37 | 2020-04-11 22:05 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-04-09 18:50 | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-09 18:37 | VALVE CLOSURE |  | 2020-04-09 18:37 | 3 | 2020-04-09 18:35 | 2020-04-09 20:25 | ONSHORE | TX | 78101 | ST. HEWDIG | BEXAR | SURVEY STATION NO. | 2956+80 | BURNELL TO ADKINS | 9122 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.25 | 46000 | API-5L-X-46-46000 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1949 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 16 | 28 |  | CLASS 2 LOCATION | NO |  | 342 |  | NO | NO | [5 empty] | 50000 | 52024.73221283635 | 0 | 0 | 46965 | 82428.3673469387755102040816326530612245 | 46965 | 48866.830967517183555 | 10000 | 10404.94644256727 | 2000 | 2080.989288513454 | EVACUATION EXPENSES | 1.55 | 155930 | 104102.8685502640370596355685131195335277 | 195805.8662583730330652040816326530612245 | 0 | 0 | 0 | 0 | NO |  |  |  | 505 | 0 | 612 | 192.619(A)(2) |  | 2011-11-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 79200 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO EMPLOYEES WERE FOUND TO BE HAVING CONTRIBUTED TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | BRITTLE FRACTURE INITIATING IN THE CONTACT MARKS AT THE EDGE OF THE HAZ | [13 empty] | YES | BRITTLE FRACTURE INITIATING IN THE CONTACT MARKS AT THE EDGE OF THE HAZ | UNKNOWN | [54 empty] | YES | YES |  |  | YES |  |  | YES | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2011 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | TDW SPIRAL MFL | 2018 | FREE SWIMMING |  |  |  | YES | 2011 | 888 | NO | [13 empty] | YES |  |  | 2018 | 2018 | [5 empty] | YES | YES | [33 empty] | YES | [18 empty] | AMIT SHAMGAR | SR. PIPELINE COMPLIANCE SPECIALIST | ashamgar@eprod.com | 713-381-6741 |  |  |  |  | NHAN TRUONG | PIPELINE COMPLIANCE MANAGER | 713-381-2493 | nvtruong@eprod.com | AT 18:35, HOUSTON CONTROL CENTER (HCC) RECEIVED A LOW PRESSURE ALARM AND NOTICED PRESSURES DROPPING ON THE PIPELINE. THE CONTROLLER IMMEDIATELY BLOCKED IN TWO REGULATORS AND DISPATCHED FIELD PERSONNEL TO INVESTIGATE. AT 18:50, HCC WAS NOTIFIED BY THE LOCAL FIRE DEPARTMENT THERE WAS GAS BLOWING FROM A PIPELINE. AT THE TIME, IT WAS NOT KNOWN IF THE SOURCE OF THE FAILURE WAS ENTERPRISE'S OR A 3RD PARTY CONNECTING PIPELINE. LOCAL TECHNICIANS CLOSED MANUAL VALVES TO FURTHER ISOLATE THE SEGMENT. AT 20:25, ENTERPRISE PERSONNEL WERE PERMITTED TO INSPECT THE SITE OF THE LEAK AND CONFIRMED THAT IT WAS ENTERPRISE'S PIPELINE. CONCERNING QUESTION E1A. - THE VALUE ENTERED .00 IS CORRECT AS PRODUCT WAS NOT FLOWING IN THE LINE AT THE POINT AND TIME OF THE INCIDENT. CONCERNING QUESTION E.11 - NO EMPLOYEES WERE FOUND TO BE HAVING CONTRIBUTED TO THIS INCIDENT. CONTROL ROOM SYSTEMS FUNCTIONED AS DESIGNED. THE CONTROLLER REACTED SWIFTLY AND APPROPRIATELY TO THE INCIDENT. ENTERPRISE EVACUATED 3 MEMBERS OF THE GENERAL PUBLIC; HOWEVER, THE NUMBER EVACUATED BY THE LOCAL FIRE DEPARTMENT ARE STILL (AS OF JUNE 16TH, 2020) NOT AVAILABLE. THERE WERE NO FIRES OR INJURIES. METALLURGICAL ANALYSIS FOUND THAT THE PRIMARY CAUSE OF THE FAILURE WAS A BRITTLE FRACTURE INITIATING IN THE CONTACT MARKS AT THE EDGE OF THE HEAT AFFECTED ZONE (HAZ). BASED ON THE FINDINGS, ENTERPRISE PLANS TO CONDUCT A HYDROTEST IN THE AFFECTED SEGMENT TO DETECT AND REMOVE SIMILAR LOCATIONS. TRRC INCIDENT NUMBER 2180.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20200048 | 33735 | 2020-05-06 17:17 | SUPPLEMENTAL FINAL | 31994 | PANTHER OPERATING COMPANY, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2020-01-06 13:45 | 2020 | CENTRAL | YES | 28.6981 | -89.9964 | 1268088 | 2020-01-06 18:37 | 1268214 | NATURAL GAS |  | 132.409 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REPAIR TEAM REQUESTED LINE STAY ACTIVE TO ASSIST WITH LOCATING THE LEAK |  |  |  | YES | OPERATOR | 2020-01-06 19:44 | NO | [5 empty] | OPERATIONAL CONTROL | INVESTIGATION OF LEAK SOURCE |  | OPERATIONAL CONTROL | INVESTIGATION OF LEAK SOURCE |  | 0 | 2020-01-06 13:45 | 2020-01-07 08:00 | OFFSHORE | [6 empty] | VENICE GATHERING SYSTEM | PSN - 11375 | [20 empty] | 164 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | GRAND ISLE | 82 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 | NO | 0.517 | 65000 | X-65 | OTHER | RESEARCHING ORIGINAL PIPELINE CONSTRUCTION DOCUMENTS | UNKNOWN | EPOXY |  | UNKNOWN | [26 empty] | 1997 | 1997 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 352 | 617.795918367346938775510204081632653061 | 265000 | 275731.080728032655 | 3000 | 3121.483932770181 | 0 | 0 |  | 2.657 | 268352 | 123424.4361026528924664723032069970845481 | 279470.3605791701829387755102040816326531 | 0 | 0 | 0 | 0 | NO |  |  |  | 670 | 15489 | 1480 | 192.619(A)(2) |  | 1997-02-20 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED |  | 277262 | YES | [7 empty] | NO | [6 empty] | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | HELICOPTER CONTRACTED BY ANOTHER OPERATOR SAW AND REPORTED THE LEAK |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS OPERATING AND NO INDICATION OF A LEAK WAS SEEN DURING EXPLORATORY CORRESPONDENCE WITH FIELD PERSONNEL AND THE CONTROL ROOM | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | YES | YES | 1997 | NO | NO | [8 empty] | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KEVIN STANLEY | SR. MANAGER EHS | kstanley@3cmidstream.com | 346-241-3585 |  |  |  |  | KEVIN STANLEY | SR. MANAGER EHS | 356-241-3585 | kstanley@3cmidstream.com | ON JANUARY 6TH AN AIR PATROL WITNESSED BUBBLING IN OCS WATERS IN GRAND ISLE BLOCK 82. INITIALLY REPORTED BY ARENA AND THEN PANTHER OPERATING COMPANY (POC) VERIFIED WITH ARENA THAT THE LEAK WAS ON PSN-11375. POC CONTRACTED WITH ARENA AND MOBILIZED A REPAIR CREW TO THE SITE. THE AREA OF THE LEAK ON THE PIPE WAS UNCOVERED AND VERIFIED LEAK FROM A PINHOLE. A CLAMP WAS INSTALLED, THE PIPELINE WAS PLACED BACK INTO SERVICE AND VISUALLY VERIFIED THAT THE LEAK WAS REPAIRED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200049 | 33739 | 2020-05-12 12:39 | ORIGINAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-04-18 20:45 | 2020 | CENTRAL | YES | 30.0892 | -92.0291 | 1275703 | 2020-04-20 10:55 | 1275714 | NATURAL GAS |  | 4100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY ENGINE #5 SHUT DOWN |  |  |  | YES | OPERATOR | 2020-04-18 21:42 | NO | [11 empty] | 0 | 2020-05-18 20:45 | 2020-04-18 21:08 | ONSHORE | LA | 70592 | YOUNGSVILLE | LAFAYETTE | MILEPOST | 40.1899 | YOUNGSVILLE COMPRESSOR STATION | EUNICE-THIBODEAUX SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1956 | 1956 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATED PREMATURELY | CLASS 1 LOCATION | NO |  | 101 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 6683 | 11729.3469387755102040816326530612244898 | 215 | 223.706348515196305 | 189 | 196.653487764521403 | 0 | 0 |  | 1.63 | 7087 | 7881.612841038431928711370262390670553936 | 12149.7067750552279120816326530612244898 | 0 | 0 | 0 | 0 | NO |  |  |  | 998 | 400000 | 1050 | 192.619(A)(1) |  | 1956-12-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | ELECTRICAL STORMS IN AREA - SEE PART H NARRATIVE | [161 empty] | SHANNON M MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.688.6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.688.6497 | tina.baker@bwpipelines.com | TEXAS GAS' GAS CONTROL RECEIVED A CALL ABOUT NOISE AT ITS YOUNGSVILLE COMPRESSOR STATION ON 4/18/20 AT 20:45. GAS CONTROL DISPATCHED OPERATIONS PERSONNEL WHO ARRIVED AT THE SITE AT 21:08. UPON ARRIVAL, THEY FOUND THAT ENGINE #5 HAD SHUT DOWN DUE TO FIN FAN FAILURE WHICH CLOSED THE UNIT VALVES; THUS, RELIEF VALVE VENTED AND PRESSURE WENT TO 0 PSIG. ALTHOUGH NO EVIDENCE OF DAMAGE WAS FOUND, THE HIGH SIDE PILOT WAS REPLACED TO ENSURE ITS INTEGRITY. EVERYTHING OPERATED AS IT SHOULD. NEAR THE TIME THIS INCIDENT OCCURRED, ELECTRICAL STORMS WERE IN THE AREA. WHILE IT IS UNCLEAR WHETHER TEXAS GAS EXPERIENCED A LIGHTNING STRIKE, THE LIGHTNING STORM CAUSED THE COOLING FANS TO SHUT DOWN ON THIS ENGINE AND ANOTHER. AT THIS TIME PRESSURE DROP WAS SEEN ON THE ENGINE DISCHARGE TRANSMITTER WHICH CONTINUED UNTIL UNIT #5 HIGH TURBO OIL TEMPERATURE SHUT THE UNIT DOWN AT 21:08 INDICATING FAILURE ON HIGH SIDE PILOT FOR RELIEF. UNIT VALVES THEN CLOSED AND THE RELIEF VALVE VENTED TO 0 PSIG. PRESSURE INDICATION WAS NEVER OVER THE SET POINT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200050 | 33764 | 2020-05-13 08:26 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-04-25 11:20 | 2020 | CENTRAL | YES | 31.1153 | -93.9621 | 1276064 | 2020-04-25 11:50 | 1276147 | NATURAL GAS |  | 330 | 680 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-26 14:00 | 2020-04-26 18:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-04-26 14:00 | VALVE CLOSURE |  | 2020-04-26 14:00 | 0 | 2020-04-25 10:18 | 2020-04-25 10:45 | ONSHORE | TX | 75931 | Not Within a Municipality | JASPER | SURVEY STATION NO. | 4607+70 | BEAUMONT LINE | TPL 64 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 14 |  | 0.312 | 24000 | API 5LX | LAP WELDED |  | UNKNOWN | ASPHALT |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1924 | 1924 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 172 |  | NO | NO | [5 empty] | 0 | 0 | 1108 | 1152.868065836453516 | 538 | 944.244897959183673469387755102040816327 | 60000 | 62429.67865540362 | 200 | 208.0989288513454 | 0 | 0 |  | 1.63 | 61846 | 28761.5524061554668122332361516034985423 | 64734.8905480506025894693877551020408163 | 0 | 0 | 0 | 0 | NO |  |  |  | 150 | 471 | 292 | 192.619(C) |  | 2018-04-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 65627 | NO | YES |  | YES |  |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | LEAK WAS IN AN ACETYLENE WELD THAT CRACKED | [12 empty] | YES | [8 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON M MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-688-6357 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-688-6497 | tina.baker@bwpipelines.com | ON 4/25/2020, A LANDOWNER DISCOVERED A POTENTIAL LEAK NEAR GULF SOUTH'S PIPELINE AND CALLED GAS CONTROL AT APPROXIMATELY 10:18 A.M. GAS CONTROL DISPATCHED OPERATIONS PERSONNEL WHO VERIFIED THE LEAK AT 10:45 A.M. ATTEMPTS TO SEAL OFF THE LEAK BY INSTALLING A LEAK CLAMP ON 4/25/2020 WERE UNSUCCESSFUL AND A CONSTRUCTION CREW WAS SCHEDULED TO MOBILIZE THE NEXT DAY. AT THAT POINT, THE LINE SECTION WAS BLOWN DOWN AND A TYPE B WELDOVER PRESSURE CONTAINING SLEEVE WAS INSTALLED. 5/18/2020 UPDATED REPORT AS INSTRUCTED BY PHMSA: UPDATED QUESTION B4 TO INDICATE THAT THE LEAK LOCATION IS NOT WITHIN A MUNICIPALITY. UPDATED QUESTION C6 TO INDICATE "LEAK" AS THE TYPE OF RELEASE WITH "CRACK" AS THE TYPE OF LEAK. ADDITIONALLY, PHMSA ASKED WHAT PART SCADA PLAYED IN IDENTIFYING THIS LEAK SINCE THE THE INITIAL INDICATION WAS NOTIFICATION FROM THE PUBLIC. THE GAS CONTROLLER ON DUTY NOTICED, AFTER TRENDING, THAT THERE WAS A SLIGHT PRESSURE DROP.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200051 | 33756 | 2020-05-14 20:40 | ORIGINAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-14 09:20 | 2020 | CENTRAL | YES | 39.472 | -90.9141 | 1275372 | 2020-04-14 09:38 | 1275497 | NATURAL GAS |  | 3800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ROUTINE TEST WAS BEING CONDUCTED ON ESD SYSTEM. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-04-14 09:00 | 2020-04-14 08:00 | ONSHORE | IL | 62366 | PLEASANT HILL | PIKE | NOT APPLICABLE |  | PLEASANT HILL COMPRESSOR STATION | 300 DISCHARGE RELIEF | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | AIR LEAK ON ESD TUBING PREVENTED ESD SIGNAL PRESSURE FROM REACHING THE TRIP POINT OF THE VALVE. THE VALVE DIDN'T CLOSE TO ISOLATE THE GAS FLOW TO THE RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 179 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 8664 | 15206.2040816326530612244897959183673469 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.28 | 8664 | 9977.492711370262390670553935860058309038 | 15206.2040816326530612244897959183673469 | 0 | 0 | 0 | 0 | NO |  |  |  | 500 | 350 | 900 | 192.619(A)(2) |  | 1954-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS PERSONNEL WERE CONDUCTING AN ESD TEST AND HAD NOTIFIED THE CONTROL ROOM PRIOR TO TESTING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | AN AIR LEAK ON THE ESD SIGNAL TUBING PREVENTED THE PRESSURE FROM BUILDING UP HIGH ENOUGH TO TRIP THE 300 SUCTION SIDE GATE VALVE. | [15 empty] | YES | O-RING AND POPPETS PREMATURELY REACHED END OF LIFE. | [161 empty] | KATHIE HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | DANNY NICHOLS | SENIOR DIRECTOR REGULATORY COMPLIANCE | 713-989-7232 | danny.nichols@energytransfer.com | WHILE CONDUCTING AN ESD TEST THE STATION VENTED 3.8 MMSCF OF NATURAL GAS. DURING A NORMAL ESD, IT TAKES SOME TIME TO BLOWDOWN THE YARD PIPING AFTER ACTIVATION OF THE SYSTEM. WHEN THE BLOWDOWN VALVE CONTINUED TO BLOW, OPERATIONS PERSONNEL BEGAN TO INVESTIGATE AND FOUND THE 300 SUCTION SIDE GATE VALVE TO STILL BE OPEN. THE ISOLATION VALVE UNDER THE BLOWDOWN VALVE WAS CLOSED. OPERATIONS PERSONNEL ISOLATED THE SUCTION SIDE GATE VALVE, THEN TESTED THE VALVE AND IT OPERATED AS DESIGNED. OPERATIONS PERSONNEL TESTED THE ESD SYSTEM AND FOUND THERE WAS AN AIR LEAK ON THE ESD TUBING. THE AIR LEAK WAS REPAIRED AND THE SYSTEM WAS TESTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200052 | 37245 | 2020-05-15 12:12 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-04-16 13:00 | 2020 | CENTRAL | YES | 35.2145 | -92.4078 | 1275515 | 2020-04-16 13:18 | 1275610 | NATURAL GAS |  | 200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A 20% REDUCTION WAS IMPLEMENTED |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | 20% OPERATING PRESSURE REDUCTION IMPLEMENTED AT SOURCE FOR PIPELINE. |  | OPERATIONAL CONTROL | PIPELINE IS STILL IN SERVICE AT A 20% REDUCTION. |  | 0 | 2020-04-15 12:30 | 2020-04-15 12:30 | ONSHORE | AR | 72508 | GREENBRIAR | FAULKNER | NOT APPLICABLE |  | LINE BM-21 | LINE BM-21 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 4 |  | 0.188 | 30000 | UNKNOWN | FURNACE BUTT WELDED |  | UNKNOWN | COAL TAR |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1957 | 1957 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 55 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 348 | 610.775510204081632653061224489795918367 | 122800 | 127772.7423147260756 | 1000 | 1040.494644256727 | 0 | 0 |  | 1.74 | 124148 | 57228.2247073820855702623906705539358601 | 129424.0124691868842326530612244897959184 | 0 | 0 | 0 | 0 | NO |  |  |  | 295 | 1000 | 310 | 192.619(A)(2) |  | 2018-12-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 61776 | NO |  | YES |  |  |  | YES | LACK OF LAUNCHER/RECEIVER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DISCOVERED DURING PATROL. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | CORROSION | [19 empty] | YES | ORIGINAL WELD WITH CORROSION WITH CLAMP CORROSION. | UNKNOWN | [54 empty] | NO | [63 empty] | YES | 2018 | 388 | Yes, but the point of the Accident was not identified as a dig site |  | 2013 |  |  |  |  | CLOSE INTERVAL SURVEY | 2013 |  |  |  |  | YES | NO | [14 empty] | YES | [48 empty] | JIMMY CROSS | SR. MANAGER REGULATORY COMPLIANCE | jimmy.cross@energytransfer.com | 14055768230 |  | JIMMY CROSS | jimmy.cross@energytransfer.com | 14055768230 | JIMMY CROSS | SR. MANAGER REGULATORY COMPLIANCE | 14055768230 | jimmy.cross@energytransfer.com | DURING A ROUTINE PATROL, A SMALL LEAK WAS DISCOVERED ON EGT LINE BM-21. ENABLE OPERATIONS REMOVED DIRT FROM THE AFFECTED AREA AND FOUND THE MINOR LEAK TO BE COMING FROM A LEGACY GIRTH WELD THAT HAD A CLAMP INSTALLED OVER IT. THE WELD WAS COMPLETED IN 1957 AND IT CANNOT BE DETERMINED WHEN THE CLAMP WAS INSTALLED. THE LINE WAS LOWERED 20% AFTER DISCOVERY AND REMEDIATION IS PLANNED TO BEGIN IN LATE JUNE. CURRENTLY, THE LINE IS OPERATING AT REDUCED PRESSURE AND SNIFFED PERIODICALLY. AT THE LOWERED OPERATING PRESSURE THE LEAK CANNOT BE DETECTED USING LEAK DETECTION EQUIPMENT. STOPPLES WILL BE INSTALLED ALLOWING CUSTOMERS TO MAINTAIN SERVICE. REPAIR IS EXPECTED TO EXCEED $50,000. WHEN THE REPAIR IS COMPLETE A SUPPLEMENTAL REPORT WILL BE COMPLETED. THE LINE WAS REPAIRED ON JULY 15TH AND THE LINE WAS RETURNED TO NORMAL OPERATING PRESSURE ON JULY 16TH. THE LEAK WAS DUE TO CORROSION IN THE LEGACY WELD AND CLAMP. THE NRC (#1275515) WAS NOTIFIED ON 4/16/2020 AND A 48 HOUR FOLLOW UP (#1275610) WAS PROVIDED ON 4/18/20. SUPPLEMENTAL 07/27/2020 PART A.5 32.214456 TO 35.214456 PART D.7.C ADDED $1,000 PART H. NARRATIVE SUPPLEMENTAL 10/02/2020 PART H NARRATIVE BT-21 CHANGED TO BM-21 SUPPLEMENTAL 10/20/2022 PART B CLEBURNE COUNTY CHANGED TO FAULKNER COUNTY PART H NARRATIVE BT-21 CHANGED TO BM-21
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200053 | 34294 | 2020-05-15 15:18 | SUPPLEMENTAL FINAL | 12874 | DOMINION ENERGY QUESTAR PIPELINE, LLC | 333 SOUTH STATE STREET P.O. BOX 45922 | SALT LAKE CITY | UT | 84145-0360 | 2020-04-20 14:30 | 2020 | MOUNTAIN | YES | 41.5157 | -109.4587 | 1275729 | 2020-04-20 15:30 |  | NATURAL GAS |  | 98 | 4404 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-04-15 17:21 | 2020-05-13 13:47 |  | YES | OPERATOR | 2020-04-15 16:18 | YES | 2020-04-15 16:04 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 98 | NO | VALVE CLOSURE |  | 2020-04-15 16:36 | VALVE CLOSURE |  | 2020-04-15 16:34 | 0 | 2020-04-15 16:04 | 2020-04-15 16:29 | ONSHORE | WY | 82935 | GREEN RIVER | SWEETWATER | SURVEY STATION NO. | 6132+20 | MAIN LINE 1 | CROSSOVER 19 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2014 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | APPROXIMATELY 0.1" X 0.1" HOLE | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 370 |  | NO | NO | [5 empty] | 0 | 0 | 5967 | 6208.631542279890009 | 133 | 233.428571428571428571428571428571428571 | 110000 | 114454.41086823997 | 2000 | 2080.989288513454 | 0 | 0 |  | 1.355 | 118100 | 54303.1290408003050519795918367346938776 | 122977.4602704618854375714285714285714286 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 45000 | 849 | 192.619(A)(4) |  | 2014-05-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | REMOTELY CONTROLLED | 49464 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONCERNS WITH CONTROLLER ACTIONS OR CONTROL ROOM ISSUES | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | [103 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [261 empty] | CALEB BENTLEY | ENGINEER II | caleb.a.bentley@dominionenergy.com | 8012099761 |  |  |  |  | LORI CREER | VP WESTERN PIPELINE OPERATIONS | 8013245349 | lori.creer@dominionenergy.com | DOMINION ENERGY AND LOCAL EMERGENCY RESPONDERS WERE ALERTED TO AND MITIGATED A FIRE AT A COMPANY FACILITY ON 4/15/2020. THE FIRE WAS CAUSED BY AN ELECTRICAL ARC WHICH DAMAGED ACTUATOR POWER GAS TUBING AND IGNITED THE LEAK IT CAUSED. THIS INCIDENT OCCURRED AT A FACILITY LOCATED NEAR GREEN RIVER, WY ON ML001. INITIAL DAMAGE ESTIMATES WERE BELOW THE $50,000 INCIDENT REPORTING THRESHOLD; HOWEVER, SUBSEQUENT ANALYSIS THAT LED TO A DECISION TO REPLACE ADDITIONAL PIPING OUT OF AN ABUNDANCE OF CAUTION, INCREASED THE ESTIMATED REPLACEMENT COSTS ABOVE THE $50,000 THRESHOLD. THIS REPORTING CRITERIA WAS MET ON 4/20/2020 AT 14:30 AND A NRC REPORT WAS SUBSEQUENTLY MADE. ADDITIONAL TESTING DETERMINED THAT THE REPLACED EQUIPMENT WAS NOT ADVERSELY AFFECTED BY THE FIRE. NOTES ON SPECIFIC QUESTIONS: D2) THE PIR OF THE FAILED TUBING WOULD NOT CREATE AN HCA IN THE AREA; HOWEVER, THE FACILITY IS LOCATED WITHIN AN HCA ON ML001 D3) REPORTED PIR IS FOR ML001 DUE TO ML001 BEING USED IN QUESTION D2 E1A) REPORTED FLOW RATE IS FOR ML001 E2A) MAOP DETERMINATION METHOD REPORTED IN QUESTION E2A IS FOR THE TUBING THAT LEAKED. THE MAXIMUM SAFE OPERATING PRESSURE FOR THE TUBING IS DETERMINED PER 192.619(A)(4) TO BE THE MAIN LINE MAOP. MAIN LINE PIPING MAOP ON THIS SECTION OF ML001 WAS DETERMINED BY 192.619(A)(1). E6) LENGTH BETWEEN VALVES DOES NOT INCLUDE THE BLOCK VALVES LOCATED AT THE FACILITY INVOLVED IN THE INCIDENT
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200054 | 34815 | 2020-05-20 16:20 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-04-20 10:05 | 2020 | EASTERN | YES | 42.6684 | -83.3322 | 1276020 | 2020-04-24 15:59 | 1276117 | NATURAL GAS |  | 1008 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | LEAK WAS INVESTIGATED AND CLASSIFIED |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | LOWER PRESSURE AT THE ORION CITY GATE FROM 259 PSIG TO 207 PSIG |  | VALVE CLOSURE |  | 2020-04-21 18:25 | 0 | 2020-04-20 10:28 | 2020-04-20 10:28 | ONSHORE | MI | 48328 | WATERFORD | OAKLAND | NOT APPLICABLE |  | LINE 1014 | VALVE HA-15 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1968 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 182 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 2953 | 5182.816326530612244897959183673469387755 | 1005527 | 1046245.458155533930129 | 140 | 145.66925019594178 | 0 | 0 |  | 2.93 | 1008620 | 465028.3744980852971799679300291545189504 | 1051573.94373226048415389795918367346939 | 0 | 0 | 0 | 0 | NO |  |  |  | 259 | 8136 | 275 | 192.619(C) |  | 1969-10-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  | MANUAL | 25940 | NO | YES |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [12 empty] | YES | [167 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON APRIL 20, 2020 AT APPROXIMATELY 10:05 HOURS, CONSUMERS ENERGY WAS NOTIFIED BY THEIR CONTRACTOR PERFORMING LEAK SURVEY OF A POTENTIAL LEAK ON LINE 1014. LINE 1014 IS A 16" HIGH PRESSURE CW STEEL PIPELINE INSTALLED IN 1968 AND LOCATE IN WATERFORD, MICHIGAN (OAKLAND COUNTY). A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 10:28 HOURS. THE GSW CONFIRMED THE PRESENCE OF A LEAK AND REQUESTED A GAS DISTRIBUTION CREW BE DISPATCHED TO THE LOCATION. AN INVESTIGATION DETERMINED THE LEAK SOURCE AS A 16" VALVE (VALVE HA-15). THE VALVE WAS INJECTED WITH GREASED IN AN ATTEMPTED TO SEAL THE LEAK ON APRIL 20, 2020 AND APRIL 21, 2020. THE AREA WAS ALSO AERATED TO ELIMINATE ANY RESIDUAL GAS TRAPPED IN THE SOIL. THE SITE WAS MONITOR OVERNIGHT. ON APRIL 21, 2020 AT APPROXIMATELY 18:25 HOURS THE PIPELINE PRESSURE WAS LOWERED FROM 259 PSIG TO 207 PSIG IN PREPARATION FOR THE SITE TO BE EXCAVATED AND THE VALVE FACILITY ASSESSED TO CONFIRM THE GAS RELEASE WAS SECURE. THE CREW CONTINUED THEIR INVESTIGATION AND AS A SAFETY PRECAUTION, PERSONNEL REMAINED ON SITE. ON APRIL 22, 2020 THE LOCATION WAS EXCAVATED AND THE SOURCE OF THE LEAK WAS DETERMINED TO BE AT THE FLANGE. THE LEAK WAS CLASSIFIED AND PLANS TO RETURN TO THE SITE THE FOLLOWING DAY TO TIGHTEN AND/OR REPLACE THE BOLTS. ON APRIL 23, 2020 IT WAS DETERMINE THE ATTEMPT TO TIGHTEN BOLTS TO RESOLVE THE LEAK WAS UNSUCCESSFUL AND VALVE REPLACEMENT WOULD BE REQUIRED. THE LEAK WAS EVALUATED AND RECLASSIFIED PENDING ENGINEERING REVIEW AND REPLACEMENT PLAN DEVELOPMENT. THE SITE EXCAVATION REMAINS OPEN AND HAS BEEN SECURED TO PREVENT POTENTIAL HAZARDS TO THE PUBLIC. A VALVE REPLACEMENT PLAN IS BEING DEVELOPED. IN AUGUST 2020 (AUGUST 15 - SEPTEMBER 2) THE EXISTING 16" S-HP-20%SMYS (HA-15) VALVE WAS REMOVED AND REPLACED WITH AN 8" S-HP (HA-69) VALVE. FOLLOWING VALVE REPLACEMENT, NORMAL OPERATION WAS RESUMED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200055 | 33815 | 2020-05-28 10:17 | SUPPLEMENTAL FINAL | 12498 | MIDWESTERN GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2020-05-07 18:06 | 2020 | CENTRAL | YES | 41.0655 | -88.0882 | 1276856 | 2020-05-07 20:52 | 1276923 | NATURAL GAS |  | 7032 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-07 19:03 | 2020-05-07 21:45 |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-07 18:06 | 2020-05-07 19:00 | ONSHORE | IL | 60941 | Not Within a Municipality | KANKAKEE | MILEPOST | M.P. 323 | MIDWESTERN GAS TRANSMISSION HERSCHER COMPRESSOR | 2100-2121 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | TRIPPED CIRCUT BREAKER | OTHER | [8 empty] | VALVE POSITION FAILURE | CLASS 1 LOCATION | NO |  | 760 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 13565 | 23807.9591836734693877551020408163265306 | 0 | 0 | 250 | 260.12366106418175 | 0 | 0 |  | 1.929 | 13815 | 15736.2580544341247718658892128279883382 | 24068.0828447376511377551020408163265306 | 0 | 0 | 0 | 0 | NO |  |  |  | 817 | 584904 | 936 | 192.619(C) |  | 1970-08-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS HAD TAKEN PLACE AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  | YES | [27 empty] | YES | [166 empty] | NEAL JONES | REQULATORY COMPLIANCE MANAGER | neal.jones@oneok.com | 580-395-6304 | 580-395-2933 | DENIS JUDY | denis.judy@oneok.com | 815-467-5645 | JOHNNIE JARRED | DIRECTOR OF PIPELINE OPERATIONS | 918-588-7827 | johnnie.jarred@oneok.com | AT APPROXIMATELY 18:06 ON MAY 7, 2020 MIDWESTERN GAS TRANSMISSION GAS CONTROLLERS RECEIVED AN ALARM FOR "UNIT CONTROL PANEL TO SYSTEM CONTROL PANEL COMMUNICATION FAILURE K100" AT THE HERSCHER COMPRESSOR STATION. FIELD OPERATIONS PERSONNEL WERE DISPATCHED TO THE LOCATION. UPON ARRIVAL AT THE STATION, OPERATIONS EMPLOYEE IDENTIFIED NATURAL GAS VENTING FROM THE UNIT BLOW DOWN VALVE AS THE UNIT SUCTION AND DISCHARGE VALVES HAD NOT CLOSED. EMPLOYEE ACTIVATED THE STATION EMERGENCY SHUTDOWN WHICH CLOSED THE SUCTION AND DISCHARGE VALVE, STOPPING THE RELEASE. MIDWESTERN GAS TRANSMISSION'S INVESTIGATION FOUND A TRIPPED CIRCUIT BREAKER IN THE STATION CONTROL LOGIC SYSTEM WHICH ALLOWED THE UNIT TO SHUTDOWN WITHOUT CLOSURE OF THE UNIT SUCTION AND DISCHARGE VALVE. 5/28/20 CHANGED REPORT TO FINAL - NEAL JONES
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200056 | 36099 | 2020-05-29 14:33 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-05-03 12:28 | 2020 | EASTERN | YES | 39.4627 | -82.3118 | 1276580 | 2020-05-03 15:04 | 1276670 | NATURAL GAS |  | 79.83 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-03 13:17 | 2021-12-03 17:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-03 12:53 | 2020-05-03 12:53 | ONSHORE | OH | 43138 | Not Within a Municipality | HOCKING | SURVEY STATION NO. | 3+25 | LAURAL RUN E-2 | LINE E-336 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.154 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1956 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 98 |  | NO | NO | [5 empty] | 10000 | 10404.94644256727 | 0 | 0 | 127 | 222.897959183673469387755102040816326531 | 200000 | 208098.9288513454 | 0 | 0 | 5000 | 5202.473221283635 | BOTTLE GAS EXPENSES | 1.59 | 215127 | 98836.9268133473038046647230320699708455 | 223929.2464743799784693877551020408163265 | 0 | 1 | 7 | 0 | NO |  |  |  | 204 | 0.5 | 225 | 192.619(A)(3) |  | 1950-07-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | SMALL TRUCK | ROADWAY | 23 | YES |  | YES | [236 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON MAY 3, 2020, AT 12:28 EASTERN DAYLIGHT TIME (EDT), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) OPERATIONS PERSONNEL RECEIVED A CALL FROM COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY, REGARDING A GAS LEAK AT LAUREL RUN MEASURING AND REGULATING STATION (M&R) 701767 ON LINE E-336. COLUMBIA OPERATIONS PERSONNEL WAS DISPATCHED AND ARRIVED ON SITE AT 12:53 EDT WHERE HE CONFIRMED THAT THE UNINTENDED NATURAL GAS RELEASE WAS DUE TO A VEHICLE ACCIDENT. THE M&R BUILDING WAS DAMAGED DUE TO SIDE IMPACT BY A TRAVELING VEHICLE ALONG LAUREL RUN ROAD THAT LOST CONTROL. AS A RESULT, TO THIS VEHICLE ACCIDENT, AN UNINTENTIONAL NATURAL GAS RELEASE INTO ATMOSPHERE FROM COLUMBIA FACILITY (LAUREL RUN M&R 701767) WAS NOTED. AT 13:17 EDT, THE UNINTENDED RELEASE OF NATURAL GAS WAS ISOLATED, AND THE FACILITY WAS REMOVED FROM SERVICE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1276580 AND THE NRC 48-HOUR REPORT NO.1276670 HAVE BEEN CALLED-IN ON MAY 3RD AND MAY 5TH RESPECTIVELY. ENGINEERING ASSESSMENT AND EVALUATION TO THE LAUREL RUN M&R 701767 FACILITY AND ITS OPERATIONAL REQUIREMENTS WAS COMPLETED, WHERE IT WAS DECIDED TO ABANDON THIS PIPELINE, HENCE DISCONTINUING NATURAL GAS FLOW INTO THIS FACILITY. THIS PROJECT WAS COMPLETED ON DECEMBER 3, 2021.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200057 | 37366 | 2020-06-02 10:02 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-05-04 16:36 | 2020 | EASTERN | YES | 38.3024 | -83.6017 | 1276640 | 2020-05-04 17:40 | 1276770 | NATURAL GAS |  | 51684 | 96400 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-04 17:23 | 2020-11-01 20:45 |  | YES | OPERATOR | 2020-05-04 16:45 | YES | 2020-05-04 16:36 | ALLOWED TO BURN OUT |  | 51684 | YES | VALVE CLOSURE |  | 2020-05-04 17:23 | VALVE CLOSURE |  | 2020-05-04 17:05 | 2 | 2020-05-04 16:36 | 2020-05-04 17:01 | ONSHORE | KY | 41049 | HILLSBORO | FLEMING | MILEPOST | 509.898 | LINE 10 | OWSV-WHEE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.375 | 52000 | API-5LX | DSAW |  | NATIONAL TUBE WORKS | COAL TAR |  | UNKNOWN | [26 empty] | 1952 | 1951 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 30 | 94 |  | CLASS 1 LOCATION | NO |  | 633 |  | NO | NO | [5 empty] | 1000000 | 1040494.644256727 | 191836 | 199604.330575633480772 | 102851 | 180514 | 10000000 | 10404946.44256727 | 2700000 | 2809335.5394931629 | 2000000 | 2080989.288513454 | ENVIRONMENTAL MITIGATION - INVESTIGATIVE COSTS - MISC | 1.99 | 15994687 | 7413215.63064654229229542857142857142857 | 16715884.245406247380772 | 0 | 0 | 0 | 0 | YES |  |  | YES | 674 | 0 | 936 | 192.619(A)(1) |  | 2014-10-07 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 77669 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 5 | 0 | YES | 1 | 0 | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | MICHAEL MCGRATH |  | michael.mcgrath@enbridge.com | 6128056542 |  |  |  |  | NATHAN ATANU |  | 17136275008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 4:36 PM EDT ON MAY 4, 2020, TETLP'S 30-INCH DIAMETER LINE 10 TRANSPORTING NATURAL GAS FROM WHEELERSBURG COMPRESSOR STATION TO OWINGSVILLE COMPRESSOR STATION IN KENTUCKY FAILED AT M.P. 509.898. THE FAILURE RESULTED IN AN EXPLOSION AND FIRE. TETLP RECEIVED A CALL ATTENDANT ALARM AT 4:39 PM EDT FROM THE OWINGSVILLE COMPRESSOR STATION. DURING THE ENSUING MINUTES, TETLP BEGAN RECEIVING REPORTS FROM THE PUBLIC OF A FIRE NORTH OF THE OWINGSVILLE COMPRESSOR STATION. TETLP PERSONNEL WERE IMMEDIATELY DISPATCHED TO CLOSE MAINLINE BLOCK VALVE, MLV 10-367 AT MP 517 AND MLV 10-351 AT THE OWINGSVILLE COMPRESSOR STATION, THUS ISOLATING THE FAILED SEGMENT AT 5:23 EDT. TETLP INITIATED THE NOTIFICATION TO THE NRC AT 5:23 PM EDT AFTER RECEIVING CONFIRMED DISCOVERY OF THE PIPELINE FAILURE AND GATHERING THE INITIAL INFORMATION TO MAKE THE NRC NOTIFICATION WITH THE CALL TERMINATING AT 5:40 PM EDT. NOTE THAT THE NRC RECORDS THE TIME THE CALL WAS TERMINATED ON THE NRC REPORT AND NOT THE TIME OF THE CALL WAS INITIATED. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION BY THE NTSB. THE INCIDENT CAUSE IS BEING REPORTED AS OTHER INCIDENT CAUSE UNTIL THE NTSB RELEASES INFORMATION ABOUT THE INCIDENT CAUSE. THE APPARENT CAUSE WILL BE UPDATED WHEN IT BECOMES AVAILABLE FROM THE NTSB. PART J WILL BE SUPPLEMENTED AS WELL ALONG WITH CAUSE. NOTE THAT E.1.A ESTIMATED GAS FLOW IN PIPE SEGMENT AT THE POINT AND TIME OF THE INCIDENT (MSCF/D): IS WAS APPROXIMATELY 1,433,000 DTH/D RATE THROUGH THE OWINGSVILLE COMPRESSOR STATION WHICH INCLUDES BOTH LINES 10 AND 25. LINE 15, WHICH SHARES THE RIGHT OF WAY WITH LINES 10 AND 25 WAS ISOLATED AT THE TIME OF THE INCIDENT. 11/15/2022 UPDATED PART C6 DATE PIPE MANUFACTURED UPDATED PART D7 ESTIMATED PROPERTY DAMAGE UPDATED PART E11 CONTROL ROOM INVESTIGATION UPDATED PART G APPARENT CAUSE TO NATURAL FORCE LANDSLIDE UPDATED PART H TO INCLUDE NTSB PROBABLE CAUSE "THE NATIONAL TRANSPORTATION SAFETY BOARD DETERMINES THAT THE PROBABLE CAUSE OF THE PIPELINE RUPTURE WAS ENBRIDGE INC.'S ANALYSIS OF AN ACTIVE LANDSLIDE THAT DID NOT FULLY ADDRESS UNCERTAINTIES ASSOCIATED WITH PIPELINE DEFECTS, LANDSLIDE MOVEMENT, AND CORRESPONDING PIPELINE RESPONSE." THE PIPELINE FAILURE INITIATED AT A CIRCUMFERENTIAL WELD JOINT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200058 | 33840 | 2020-06-02 15:49 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-05-05 18:30 | 2020 | CENTRAL | YES | 34.4342 | -92.9037 | 1276720 | 2020-05-05 22:04 | 1276794 | NATURAL GAS |  | 4862 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE RELIEF VALVE WAS ISOLATED AND REPAIRED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-05 18:30 | 2020-05-05 19:20 | ONSHORE | AR | 72104 | MAGNET COVE CITY | HOT SPRING | NOT APPLICABLE |  | BM-28 | LAKE CATHERINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | NIPPLE FAILURE | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 219 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 8460 | 14848.1632653061224489795918367346938776 | 500 | 520.2473221283635 | 500 | 520.2473221283635 | 0 | 0 |  | 1.74 | 9460 | 10201.5919845003474839650145772594752187 | 15888.6579095628494489795918367346938776 | 0 | 0 | 0 | 0 | NO |  |  |  | 130 | 2000 | 175 | 192.619(A)(1) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MECHANICAL FAILURE OF RELIEF VALVE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [165 empty] | YES | [11 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MAY 5TH, 2020 AT 18:30 ENABLE GAS TRANSMISSION SYSTEM CONTROL RECEIVED AN ALARM THAT A RELIEF WAS VENTING AT THE LAKE CATHERINE POWER PLANT. AT 18:35 AN ENABLE O&M TECH WAS DISPATCHED TO THE SCENE. THE O&M TECH REPORTED THAT THE RELIEF VALVE BELONGED TO ENABLE (BM-28) AND CONFIRMED IT WAS VENTING WHEN HE ARRIVED. THE RELIEF WAS ISOLATED AT 19:20 CEASING THE GAS RELEASE. A 3/4' BROKEN NIPPLE ON A GAS SENSING LINE IS THE CAUSE FOR THE MALFUNCTION. IT WAS DETERMINED BY FIELD ENGINEERS THE NIPPLE MOST LIKELY FAILED DUE TO A MIXTURE OF VIBRATION AND THE LENGTH OF THE NIPPLE. THE NIPPLE WAS REPLACED, AND FIELD ENGINEERING IS ACQUIRING A SPECIAL TEST VALVE FOR REPLACEMENT TO ELIMINATE THE POSSIBILITY OF THIS INCIDENT HAPPENING AGAIN. THE GAS RELEASE WAS CONFIRMED TO BE OVER 3,000 MCF ON MAY 5TH AT 21:24 PROMPTING THE NRC TO BE NOTIFIED (MAY 5TH AT 22:04 CST # 1276720). A FINAL GAS LOSS TOTAL (4,862 MCF) WAS DETERMINED ON MAY 6TH AND PROVIDED TO THE NRC DURING THE 48 HOUR FOLLOW UP (MAY 7TH AT 8:12 CST #1276794).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200059 | 34006 | 2020-06-09 14:11 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-05-11 11:30 | 2020 | EASTERN | YES | 37.9172 | -83.9856 | 1277114 | 2020-05-12 15:50 | 1277250 | NATURAL GAS |  | 2342 | 0 | 0.27 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | NORMAL ESD BLOWDOWN. |  |  |  | YES | OPERATOR | 2020-05-11 18:00 | NO | [11 empty] | 0 | 2020-05-11 11:30 | 2020-05-11 11:30 | ONSHORE | KY | 40312 | CLAY CITY | POWELL | SURVEY STATION NO. | 106 | CLAY CITY COMPRESSOR STATION | STATION 106 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2017 | 2017 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | WIRING | OTHER | [8 empty] | RELEASE THROUGH DESIGNED ESD BLOWDOWN PIPING | CLASS 1 LOCATION | NO |  | 820 |  | NO | NO | [5 empty] | 100000 | 104049.4644256727 | 0 | 0 | 4192 | 7357.387755102040816326530612244897959184 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.79 | 104192 | 50730.1605491601128279883381924198250729 | 111406.8521807747408163265306122448979592 | 0 | 0 | 10 | 0 | NO |  |  |  | 737 | 562080 | 748 | 192.619(C) |  | 1968-07-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSED BY A LOOSE WIRE; NO CONTROLLER INVOLVEMENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [13 empty] | YES | [10 empty] | YES | LOOSE WIRE | [161 empty] | KENNETH C. PETERS | SR. ENGINEER | ken_peters@kindermorgan.com | 2053257554 | 2053253729 | DEAN HUNTLEY | dean_huntley@kindermorgan.com | 9312153680 | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON MAY 11, 2020, A LOOSE WIRE ON THE PLC TERMINAL CAUSED A LOSS OF POWER TO THE SAFETY PLC, INITIATING AN ESD AT TENNESSEE GAS PIPELINE'S STATION 106 IN CLAY CITY, KY. THE VOLUME OF GAS VENTED TO ATMOSPHERE WAS BELOW THE PHMSA REPORTABLE THRESHOLD OF 3,000 MCF. HOWEVER, TGP PERSONNEL DISCOVERED LATER THAT DAY THAT A MIST OF COMPRESSOR LUBRICATING OIL AND PIPELINE DISTILLATE WAS RELEASED WITH THE NATURAL GAS. WIND CAUSED THE MIST TO TRAVEL TO SURROUNDING PROPERTIES RESULTING IN A VERY LIGHT COATING ON RESIDENCES. THE NEXT DAY, MAY 12, 2020, IT WAS DETERMINED THAT THE COST OF CLEAN-UP WOULD EXCEED THE PHMSA REPORTABLE AMOUNT OF $50,000 AND THE OCCURRENCE WAS REPORTED TO THE NRC AS A PIPELINE INCIDENT. CLEAN-UP WAS COMPLETED LATER THAT SAME WEEK. A 48-HOUR UPDATE WAS PROVIDED TO THE NRC ON MAY 14, 2020, REPORT #1277250. THIS OCCURRENCE WAS ONLY REPORTABLE AS A PHMSA INCIDENT BECAUSE OF THE COST OF CLEAN-UP OF SURROUNDING PROPERTIES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200060 | 33900 | 2020-06-13 00:37 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-05-14 16:20 | 2020 | PACIFIC | YES | 35.6444 | -119.2766 | 1277298 | 2020-05-14 19:57 | 1277427 | NATURAL GAS |  | 8230 | 1690 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-15 09:00 | 2020-05-16 04:04 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-15 09:00 | VALVE CLOSURE |  | 2020-05-15 09:00 | 0 | 2020-05-14 16:20 | 2020-05-14 17:45 | ONSHORE | CA | 93280 | WASCO | KERN | MILEPOST | 14.73 | LINE 7000 | MILE POST 14.73 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 4 | NO | YES | [6 empty] | YES | UNCASED | POSO CREEK | UNKNOWN | SHORELINE/BANK/MARSH CROSSING | NO | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 46000 | API 5L | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1964 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 3 | 0.4 | [7 empty] | CLASS 1 LOCATION | NO |  | 296 |  | NO | NO | [5 empty] | 0 | 0 | 3938 | 4097.467909082990926 | 19176 | 33655.8367346938775510204081632653061224 | 600000 | 624296.7865540362 | 1000000 | 1040494.644256727 | 0 | 0 |  | 2.33 | 1623114 | 758333.0135317282552723206997084548104956 | 1702544.73545454006847702040816326530612 | 0 | 0 | 2 | 33 | NO |  |  |  | 610 | 44000 | 718 | 192.619(A)(2) |  | 2018-05-21 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 37700 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD-PARTY EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO | [5 empty] | YES | 24 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@socalgas.com | 909-919-0463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-919-0463 | amatin@socalgas.com | ON MAY 14, 2020, SOUTH VALLEY FARMS DAMAGED A 16-INCH STEEL TRANSMISSION LINE WHILE OPERATING A FRONT-END LOADER OVER THE PIPELINE. SOCALGAS CREWS RESPONDED, CONTROLLED THE GAS BY OPERATING MAIN LINE VALVES, AND BLEW DOWN THE LINE TO ASSESS DAMAGES. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. THE 16-INCH MAIN WAS REPAIRED BY WELDING TWO WEDDING BANDS. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS NO VALID USA TICKET FOR THE CONTRACTOR AND NO STANDBY WAS PRESENT DURING THE EXCAVATION ACTIVITY NEAR THE TRANSMISSION LINE. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE. FOR ANY FURTHER QUESTIONS, CONTACT ALI MATIN AT (909) 919-0463.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200061 | 34978 | 2020-06-17 19:31 | SUPPLEMENTAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-05-19 19:25 | 2020 | CENTRAL | YES | 29.5218 | -89.7206 | 1277681 | 2020-05-19 23:28 | 1277804 | NATURAL GAS |  | 448 | 1261 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-19 22:30 |  | YES | YES | OPERATOR | 2020-05-19 23:21 | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-19 22:30 | VALVE CLOSURE |  | 2020-05-19 22:30 | 0 | 2020-05-19 22:42 | 2020-05-20 12:34 | ONSHORE | LA | 70082 | PORT SULPHUR | PLAQUEMINES | MILEPOST | 527-1 + 0.675 | TGP 500 SYSTEM | 500-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | INVESTIGATION STILL ONGOING |  | NO | YES | [6 empty] | YES | UNCASED | MISSISSIPPI RIVER | 98 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.656 | 52000 | API-5LX | DSAW |  | NATIONAL TUBE | OTHER | SOMASTIC | NO | [26 empty] | 1959 | 1959 | CARBON STEEL |  | LEAK |  |  | OTHER | INVESTIGATION STILL ONGOING | [5 empty] | CLASS 1 LOCATION | NO |  | 695 |  | NO | NO | [5 empty] | 0 | 0 | 2333 | 2427.474005050944091 | 829 | 1454.979591836734693877551020408163265306 | 423000 | 440129.234520595521 | 0 | 0 | 0 | 0 | COST TO INSTALL LEAK CLAMP. PERMANENT REPAIR PROJECT STILL ONGOING | 1.85 | 426162 | 196193.7494910081622865043731778425655977 | 444011.6881174831997848775510204081632653 | 0 | 0 | 0 | 0 | NO |  |  |  | 814 | 7000 | 1000 | 192.619(A)(2) |  | 1959-11-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | REMOTELY CONTROLLED | 5064 | YES | [7 empty] | YES |  |  |  |  | YES | IDENTIFIED EXPOSURE MAY LIMIT ILI RUN | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION THAT ANY ACTIONS ON THE PART OF THE CONTROLLER CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | JORGE LOPEZ | MANAGER ENGINEERING - CODES AND COMPLIANCE | jorge_lopez@kindermorgan.com | 701-609-6218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING - CODES AND COMPLIANCE | 281-384-5609 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 7:55 PM ON 5/19/2020, KINDER MORGAN RECEIVED AN EMAIL FROM PHMSA. IT STATED THAT A PRIVATE CITIZEN REPORTED TO THE NRC, THAT THERE WERE BUBBLES IN THE RIVER NEAR THE TENNESSEE GAS PIPELINE COMPANY (TGP) - 500 SYSTEM LINES, LOCATED IN PLAQUEMINES PARISH, LOUISIANA, ON THE EASTERN SIDE OF THE MISSISSIPPI RIVER. TGP OPERATIONS PERSONNEL STARTED THE GAS LEAK INVESTIGATION. AT 10:30 PM, TGP CONFIRMED THE GAS LEAK ON LINE 500-1 AND STARTED THE EMERGENCY RESPONSE LINE (ERL) PROTOCOL. THE LINE WAS ISOLATED AND BLOWN DOWN. TGP CONSULTED WITH A DIVE COMPANY TO SURVEY LINE 500-1. HOWEVER, THE CURRENT RIVER CONDITIONS PREVENTS THE DIVER FROM SAFELY REACHING AND ASSESSING THE LEAK. GIVEN THESE CONDITIONS ON 5/27/2020, TGP HIRED T BAKER SMITH (TBS) TO PERFORM A SONAR SURVEY TO MAP THE LEAK LOCATION. ON 6/15/2020, TGP RECEIVED THE FINAL REPORT FROM TBS. THE INITIAL ASSESSMENT SHOWED UNSUPPORTED PIPE EXPOSURE. THIS EXPOSURE COULD LIMIT THE RUNNING OF A ILI ASSESSMENT IN ITS CURRENT STATE AS NOTED IN SECTION E8. TGP IS ASSESSING THE DATA IN ORDER TO ESTABLISH A PATH FORWARD. THE LINE WILL REMAIN BLOWN DOWN AND ISOLATED UNTIL PERMANENT REPAIRS CAN BE MADE. LEAK CLAMP HAS BEEN INSTALLED TO PREVENT WATER FROM ENTERING THE PIPELINE. THE LEAK CLAMP WILL REMAIN IN PLACE UNTIL PERMANENT REPAIR PROCESS IS COMPLETED. TGP CONTINUES ITS INVESTIGATION AND WILL PROVIDE SUPPLEMENTAL REPORTS AS UPDATES ARE OBTAINED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200062 | 33921 | 2020-06-18 09:57 | ORIGINAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-05-22 00:43 | 2020 | EASTERN | YES | 38.7076 | -82.8533 | 1277824 | 2020-05-22 02:54 | 1277962 | NATURAL GAS |  | 2920 | 49 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-22 03:06 | 2020-05-24 12:04 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-22 03:06 | VALVE CLOSURE |  | 2020-05-22 03:06 | 11 | 2020-05-22 00:43 | 2020-05-22 01:54 | ONSHORE | OH | 45694 | WHEELERSBURG | SCIOTO | SURVEY STATION NO. | 00+00 | LINE R-688 | R688-001 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 | NO | 0.154 | 35000 | TYPE B | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1986 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | DUE TO A CAR ACCIDENT 2-INCH PIPE WAS BROKEN | CLASS 3 LOCATION | NO |  | 86 |  | NO | NO | [5 empty] | 19000 | 19769.398240877813 | 78 | 81.158582252024706 | 4643 | 8148.938775510204081632653061224489795918 | 500000 | 520247.3221283635 | 0 | 0 | 64000 | 66591.657232430528 | DOWNSTREAM CUSTOMERS GAS RELIGHT | 1.59 | 587721 | 272995.0826253740767276559766763848396501 | 614838.4749594340697876326530612244897959 | 0 | 0 | 200 | 13 | NO |  |  |  | 130 | 361 | 225 | 192.619(A)(2) |  | 1986-05-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 18400 | NO | [5 empty] | YES | THIS A 2-INCH SHORT STUB LATERAL LINE. | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | COLUMBIA GAS OF OHIO (COH), THE LOCAL DISTRIBUTION COMPANY |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | PASSENGER CAR | ROADWAY | 25 | YES |  |  | YES | [235 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  | KAMRAN ROSTAMI ASRABADI | kamran_rostami@tcenergy.com | (304)357-2351 | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON MAY 22, 2020, AT 00:19 EASTERN DAYLIGHT TIME (EDT), A COLUMBIA GAS TRANSMISSION, LLC (COMPANY) PIPELINE MECHANIC (TECH) RECEIVED A CALL FROM COMPANY MONITORING CENTER REGARDING A PRESSURE DROP AT DOGWOOD RIDGE MEASURING STATION (MS) 713550 THAT WAS REPORTED BY COLUMBIA GAS OF OHIO, THE LOCAL DISTRIBUTION COMPANY. OPERATIONS PERSONNEL WAS DISPATCHED AND ARRIVED ON SITE AT 01:54 EDT WHERE HE CONFIRMED THAT THERE WAS AN UNINTENDED RELEASE OF NATURAL GAS DUE TO A VEHICLE THAT DAMAGED THE ABOVE GROUND PIPELINE. AT 03:06 EDT, THE UNINTENDED RELEASE OF NATURAL GAS WAS ISOLATED, AND AT 03:20 LINE R-688 WAS BLOWN DOWN AND THE FACILITY WAS ISOLATED AND REMOVED FROM SERVICE. ON MAY 24, 2020 LINE R-688 WAS RETURNED BACK INTO SERVICE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1277824 AND THE NRC 48-HOUR REPORT NO.1277962 HAVE BEEN CALLED-IN ON MAY 22ND AND MAY 23RD RESPECTIVELY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200063 | 33922 | 2020-06-18 11:44 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-05-24 15:00 | 2020 | CENTRAL | YES | 38.4705 | -96.2835 | 1278002 | 2020-05-24 15:25 | 1278122 | NATURAL GAS |  | 12513 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-24 13:25 | 2020-05-24 14:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-24 13:25 | VALVE CLOSURE |  | 2020-05-24 13:56 | 0 | 2020-05-24 13:25 | 2020-05-24 13:45 | ONSHORE | KS | 66835 | Not Within a Municipality | LYON | SURVEY STATION NO. | 100/591 | AMERICUS COMPRESSOR STATION | 181-02-001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1962 | 1961 | CARBON STEEL |  | OTHER | [8 empty] | DURING ESD OF THE AMERICUS COMPRESSOR STATION, THE STATION ISOLATION GATE VALVE #32 FAILED TO CLOSE ALLOWING MAINLINE GAS TO VENT DURING THE STATION BLOW-DOWN | CLASS 1 LOCATION | NO |  | 538 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 20271 | 35577.6734693877551020408163265306122449 | 400 | 416.1978577026908 | 0 | 0 | 0 | 0 |  | 1.62 | 20671 | 23527.7650736835209177842565597667638484 | 35993.8713270904459020408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 833 | 322134 | 900 | 192.619(C) |  | 1970-01-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 1000 | NO | YES |  |  |  |  | YES | COMPRESSOR STATION LINE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AUTOMATIC ESD WAS TRIGGERED AND THE UNINTENTIONAL GAS RELEASE BECAUSE THE ISOLATION VALVE DID NOT CLOSE, THE CONTROLLER WAS NOT AT FAULT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2708524414 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2708524435 | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 5/24/2020 AT 1:25 PM CDT SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) OPERATIONS RECEIVED NOTICE THE AMERICUS COMPRESSOR STATION WENT INTO AN ESD CONDITION DUE TO A FIRE DETECTION EYE INDICATING "LATCHED". RESOURCES ARRIVED ON SITE AT 1:45 PM AND NOTICED GAS WAS STILL BEING VENTED AT THE DISCHARGE STACK. IT WAS DETERMINED THAT THE STATION ISOLATION VALVE #32 LOCATED ON THE STATION DISCHARGE LINE DID NOT CLOSE. IT WAS DETERMINED THAT THE ISOLATION VALVE DID NOT CLOSE DUE TO THE POWER GAS TO THE VALVE BEING SHUT OFF. POWER GAS WAS TURNED ON AND THE ISOLATION VALVE WAS CLOSED AT 1:56 PM STOPPING THE GAS RELEASE. IT WAS DETERMINED THAT ALL EQUIPMENT WAS OPERATIONAL AND UNDAMAGED AND THE STATION WAS RETURNED TO SERVICE AT 2:10 PM ON 5/24/2020. AT 3:00 PM IT WAS DETERMINED THAT THE GAS LOSS EXCEEDED THE REPORTABLE THRESHOLD AND THE NRC WAS NOTIFIED AT 3:25 PM. FURTHER INVESTIGATION DETERMINED THAT THE POWER GAS WAS SHUT OFF DURING MAINTENANCE AND NOT REOPENED. SSCGP CONDUCTED CORRECTIVE ACTION TRAINING TO REMIND ALL PERSONNEL TO KEEP POWER GAS ACTIVE TO ISOLATION VALVES AND REMINDER FOR LOCKOUT/TAGOUT FOR POWER GAS SUPPLY LINES FOR MAINTENANCE TO ENSURE POWER GAS IS RETURNED AFTER MAINTENANCE ACTIVITIES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200064 | 34002 | 2020-06-18 16:57 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-05-17 17:21 | 2020 | CENTRAL | YES | 28.8528 | -92.0271 | 1277657 | 2020-05-19 14:06 | 1277765 | NATURAL GAS |  | 354 | 22692 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-18 07:40 | 2020-05-22 18:12 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-18 07:40 | VALVE CLOSURE |  | 2020-05-18 08:00 | 0 | 2020-05-17 17:21 | 2020-05-19 12:00 | OFFSHORE | [6 empty] | SEA ROBIN PIPELINE | LINE 702 #3334 | [20 empty] | 90 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH MARSH ISLAND | 26 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 26 | NO | 0.5 | 60000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | SAW CRISPIN (S.V.) DUNKERQUE, FRANCE | OTHER | CONCRETE WITH SOMASTIC | NO | [26 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 634 |  | NO | NO | [5 empty] | 0 | 0 | 36307 | 37777.239049028987189 | 566 | 993.387755102040816326530612244897959184 | 252639 | 262869.526430375252553 | 25000 | 26012.366106418175 | 0 | 0 |  | 1.6 | 314512 | 144761.3056207565868277026239067055393586 | 327652.5193409244555583265306122448979592 | 0 | 0 | 0 | 0 | NO |  |  |  | 775 | 11000 | 1250 | 192.619(A)(2) |  | 1970-03-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 122364 | NO |  |  | YES | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL PINHOLE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK. |  |  |  |  | YES | LOW FLOW. |  |  | YES | HISTORICAL DATA. |  |  |  |  | YES | LEAK LOCATED AT THE 6 O'CLOCK POSITION. | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | todd.nardozzi@energytransfer.com | 713-989-7126 | 877-917-0448 |  |  |  | TODD NARDOZZI | SR. MANAGER - DOT COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | SUNDAY, MAY 17, 2020 LATE AFTERNOON OPERATIONS WAS CONTACTED ABOUT BUBBLES IN THE SMI 27 AREA, NEAR TWO OF THE SEA ROBIN WEST PIPELINES. IN TALKING TO THE USCG, BOTH A PRODUCER AND BSEE CALLED IN THE REPORTED BUBBLES BUT WERE UNABLE TO OFFER COORDINATES. SEVERAL ATTEMPTS WERE MADE TO CONTACT THE NRC BUT NO ONE ANSWERED THE HOTLINE. DUE TO THE TIME OF DAY AND WEATHER WE WERE UNABLE TO MAKE A FLIGHT AT THAT TIME. MONDAY, MAY 18, 2020 OUR OVERFLIGHT THIS MORNING CONFIRMS BUBBLES AND A DARK COLORED SHEEN ARE PRESENT. CURRENTS ARE STRONG BUT COORDINATES DO INDICATE IT IS LIKELY TO BE OUR LINE, ALTHOUGH RESPONSIBILITY CANNOT BE CONFIRMED AS OF YET. GIVEN ASSET HISTORY WE ARE GOING TO ISOLATE THE 26" LINE 702 ON BOTH ENDS AND MONITOR PRESSURE. WE WILL ALSO BEGIN SOURCING A DSV TO MAKE AN INVESTIGATION DIVE FOR US AS SOON AS POSSIBLE. THE AFTERNOON OVERFLIGHT HAS SEEN THE SAME AMOUNT OF BUBBLES, BUT NO SHEEN. THE NRC NUMBER WE WERE GIVEN IS1277495; WE HAVE NOT TAKEN RESPONSIBILITY FOR THE LEAK AS WE HAVE YET TO CONFIRM SOURCE. A DSV HAS BEEN IDENTIFIED AND IS EXPECTED TO BE ON LOCATION MID-DAY TOMORROW TO INVESTIGATE. TUESDAY, MAY 19, 2020 THE DSV AND OUR OVERFLIGHT REPORT BUBBLES WITH NO SHEEN PRESENT. THE DSV USED A MESOTECH TO TAKE A SONAR SHOT OF THE LEAK, IT APPEARS TO BE ON THE 26" LINE. WE ARE ALSO IN THE PROCESS OF TAKING THE LINE DOWN TO BOTTOM PRESSURE. GIVEN WE KNOW THE LINE IS OURS WE HAVE UPDATED THE NRC WITH A NEW INCIDENT NUMBER OF 1277657. WEDNESDAY, MAY 20, 2020 OVERFLIGHT AND THE DSV BOTH BUBBLES BUT NO SHEEN AS OF NOW. THE LINE PRESSURE CONTINUES TO DROP AND IS NEAR ENOUGH TO BOTTOM PRESSURE THAT OUR FIRST DIVER IS JETTING THE AREA NOW. ONCE WE ARE AT BOTTOM PRESSURE AND ARE DONE JETTING THE DIVER CAN INSPECT THE LINE THAT WILL TELL US FAILURE METHOD AND REPAIR APPROACH. THE DSV IS STAFFED TO WORK 24 HOURS SO WE WILL CONTINUE TO MAKE PROGRESS OVERNIGHT. USCG HAS BEEN UPDATED EARLIER TODAY. DIVERS ARE REPORTING THE LEAK IS IN THE 6 O'CLOCK POSITION OF THE LINE. PLANS OVERNIGHT ARE TO FINISH REDUCING PRESSURE TO MATCH BOTTOM, COMPLETE THE MASTIC REMOVAL AND UT THE AREA OF THE LEAK TO EVALUATE PIPE FOR A LEAK CLAMP REPAIR. THE NRC WAS UPDATED EARLIER TODAY, WHICH SATISFIES THE PHMSA 48 HOUR UPDATE NRC # 1277765. THURSDAY, MAY 21, 2020 AS OF 3:26PM LEAK CLAMP HAS BEEN INSTALLED CURRENTLY IN THE PROCESS OF BRINGING THE PRESSURE UP TO THE FIRST CHECKPOINT. OVERFLIGHTS INDICATE THERE HAS BEEN NO SHEEN ASSOCIATED WITH THIS EVENT. THE USCG HAS BEEN UPDATED AS TO PROGRESS. 6:12PM ALL PRESSURE CHECKS AND OVERFLIGHTS ARE COMPLETE, WITH NO SIGNS OF ANY LEAKS. THE SEGMENT IS AT LINE PRESSURE AND HAS BEEN RETURNED TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200065 | 34502 | 2020-06-19 09:15 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-05-19 12:46 | 2020 | EASTERN | NO | 44.7702 | -85.0746 | 1277651 | 2020-05-19 14:33 | 1277764 | NATURAL GAS |  | 26.5 | 2156 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-19 13:20 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-05-19 13:50 | NO | [11 empty] | 0 | 2020-05-19 12:46 | 2020-05-19 13:19 | ONSHORE | MI | 49646 | EXCELSIOR TOWNSHIP | KALKASKA | NOT APPLICABLE |  | EXCELSIOR 6 COMPRESSOR STATION | ANR STORAGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE SEAM | 20 |  | 0.375 | 60000 | API-5L PLS2 X60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | SALZGITTER MANNESMANN LINE PIPE | PAINT |  | YES | [26 empty] | 2018 | 2017 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 62.8 | 62.8 |  | CLASS 1 LOCATION | NO |  | 467 |  | NO | NO | [5 empty] | 0 | 0 | 3751 | 3902.895410606982977 | 46 | 80.73469387755102040816326530612244897959 | 400000 | 416197.8577026908 | 0 | 0 | 0 | 0 |  | 1.74 | 403797 | 185385.3364710260360654139941690962099125 | 420181.487807175333997408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 2961 | 0 | 1050 | 192.619(A)(1) |  | 2018-09-22 | NO | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [16 empty] | YES | [176 empty] | ROBERTA PRIMERA | COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 248-561-7803 |  |  |  |  | LEE ROMACK | DIRECTOR PIPELINE REGULATOR COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | A ROOT CAUSE FAILURE ANALYSIS (RCFA) FINAL REPORT, WHICH INCORPORATED THE FINDINGS FROM THE MECHANICAL AND METALLURGICAL TESTING REPORT SUMMARIZED THE EVENT AS, "... A RUPTURE OF FACILITY PIPING ON THE SHELL SIDE OF THE GAS-GAS HEAT EXCHANGER (E-2053) LEADING TO THE EJECTION OF PROCESS PIPING AS WELL AS THE RELEASE OF NATURAL GAS TO THE ENVIRONMENT. CAUSAL FACTORS WERE RECOGNIZED FOR THE EVENT SEQUENCES PERTAINING TO (1) A NATURAL GAS LEAK FROM THE HIGH PRESSURE INJECTION HEADER TO LOWER PRESSURE PROCESS PIPING THROUGH ISOLATION VALVE XV-2070 AND XV-2071 AND (2) INADEQUATE SAFETY SYSTEMS IN THE SHELL SIDE OF THE HEAT EXCHANGER LOOP TO PREVENT RUPTURE OF THE LOWER MAOP PIPING." METALLURGICAL LAB COMPLETED THE FAILURE ANALYSIS OF THE FRACTURED PIPING AND CONCLUDED THAT THE RUPTURE OF THE SHELL SIDE PIPING WAS CAUSED BY DUCTILE OVERLOAD FROM PIPE OVER-PRESSURIZATION. CAUSAL FACTORS WERE IDENTIFIED AS: LEAKING ISOLATION VALVES; INADEQUATE DESIGN-NO OVERPRESSURE PROTECTION OR ALARMS; NO POSITIVE ISOLATION OF SHELL SIDE LOOP. BASED ON THE RCFA, RECOMMENDATIONS AND POTENTIAL IMPROVEMENT OPPORTUNITIES IDENTIFIED, CORRECTIVE ACTIONS HAVE BEEN ASSIGNED TO ADDRESS EACH CONTRIBUTING FACTOR.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200066 | 33954 | 2020-06-26 08:48 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-05-30 21:06 | 2020 | CENTRAL | YES | 35.6919 | -100.2275 | 1278467 | 2020-05-30 23:30 | 1278559 | NATURAL GAS |  | 16100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-05-30 21:06 | 2020-05-30 23:00 | ONSHORE | TX | 79011 | BRISCOE | HEMPHILL | NOT APPLICABLE |  | WOODALL PLANT YARD | AD-23 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1978 | 1978 | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE GAS RELEASE. | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 28175 | 49450 | 500 | 520.2473221283635 | 1000 | 1040.494644256727 | 0 | 0 |  | 1.75 | 29675 | 33134.9681516776349285714285714285714286 | 51010.7419663850905 | 0 | 0 | 0 | 0 | NO |  |  |  | 973 | 2000 | 1000 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | SETPOINT ON PILOT VALVE. | [147 empty] | YES | [13 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 558 4647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 558 4647 | casey.roberts@enablemidstream.com | ON MAY 3OTH , AT 21:06, ENABLE SYSTEM CONTROL RECEIVED A CALL FROM A LANDOWNER NEAR THE WOODALL PLANT THAT A RELIEF VALVE WAS GOING OFF ON LINE AD-23 IN HEMPHILL COUNTY, TEXAS. A O&M TECHNICIAN WAS DISPATCHED TO THE METER LOCATION AND BACKED OFF THE RELIEF VALVE, LOCKED IT OUT, AND RESET IT. APPROXIMATELY 16.1 MMCF OF NATURAL GAS WAS RELEASED. NO INJURIES, NO DAMAGE TO COMPANY PROPERTY. NRC WAS NOTIFIED ON 5/30 (#1278467) AND A 48HR. FOLLOW UP ON 6/1 (#1278559). UPON INVESTIGATION, IT WAS DETERMINED THE SETPOINT HAD LOWERED TO 973 PSIG ON THE PILOT VALVE. THE VALVE WAS INSPECTED AND SET AT 996 PSIG ON MAY 5TH 2020. LINE AD-23 HAS A 1000 PSIG MAOP AND WAS OPERATING AROUND 975 AT THE TIME. ON MAY 31ST, THE PILOT WAS RESET TO THE PROPER SETPOINT (996 PSIG) AND PLACED BACK INTO SERVICE. A SIMILAR INCIDENT OCCURRED IN 2018 WITH THIS RELIEF VALVE AND A LOWER SETPOINT. LINE AD-23 ROUTINELY OPERATES AT THE 975 PSIG RANGE. A STUDY IS CURRENTLY BEING CONDUNCTED TO DETERMINE IF THE 400 SERIES RELIEF SHOULD BE REPLACED WITH A 200 SERIES TO LIMIT THIS OCCURRENCE FROM HAPPENING AGAIN.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200067 | 34153 | 2020-06-28 13:38 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2020-05-27 07:41 | 2020 | EASTERN | NO | 42.5419 | -83.5606 | 1278180 | 2020-05-27 07:41 |  | NATURAL GAS |  | 12000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-05-27 03:24 | 2020-05-27 04:36 | ONSHORE | MI | 48381 | MILFORD | OAKLAND | MILEPOST | 1009 | MILFORD COMPRESSOR STATION | 1009 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2017 | 2017 | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL RELEASE OF GAS THROUGH COMPRESSOR ESD VENT. UPSTREAM PIPELINE VALVE 1009 FAILED OPEN CAUSING RELEASE OF APPROXIMATELY 12 MMCF. | CLASS 3 LOCATION | NO |  | 600 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 19560 | 34329.7959183673469387755102040816326531 | 125 | 130.061830532090875 | 100 | 104.0494644256727 | 0 | 0 |  | 1.63 | 19785 | 22628.6453685242399914723032069970845481 | 34563.9072133251105137755102040816326531 | 0 | 0 | 0 | 0 | NO |  |  |  | 638 | 0 | 1000 | 192.619(A)(1) |  | 2018-10-29 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL RESPONDED TO THE ALARM IDENTIFYING THAT THE VENT VALVE WAS OPEN AND TOOK THE APPROPRIATE ACTIONS AND MADE THE NECESSARY NOTIFICATIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SOLENOID FAILURE CAUSED VENT VALVE TO OPEN AND RELEASED GAS. | [22 empty] | YES | SOLENOID FAILURE CAUSED VENT VALVE TO OPEN AND RELEASED GAS. | [161 empty] | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | DTE GAS (GAS CONTROL) RESPONDED TO A RELEASE OF NATURAL GAS AT THE MILFORD COMPRESSOR STATION ON 5/27/2020 AT APPROXIMATELY 03:24. NATURAL GAS BLEW FOR 1 HOUR AND 12 MINUTES. A TECHNICIAN ARRIVED ON SITE AT APPROXIMATELY 04:26. THE MILFORD TECHNICIAN FOUND VENT VALVE 1009 OPEN AND BLOWING. THE TECH CLOSED THE MANUAL VALVE TO THE BLOWDOWN STACK DOWNSTREAM OF 1009 TO STOP THE RELEASE AND THEN MANUALLY CLOSED VALVE 1009. THIS VALVE SERVES PLANT 1 WHICH WAS NOT OPERATING. AFTER CALCULATING THE AMOUNT OF LOST GAS, IT WAS DETERMINED THAT THIS WAS A REPORTABLE GAS RELATED INCIDENT. UPON FURTHER INVESTIGATION BY MILFORD AND CONTROL MAINTENANCE, IT WAS DETERMINED THE SOLENOID FOR VALVE 1009 WHICH KEEPS THE VALVE CLOSED DURING NORMAL OPERATION SHORTED OUT AND FAILED CAUSING THE VALVE TO OPEN. ADDITIONAL SOLENOIDS WERE REMOVED FROM ALL 6 VENT VALVES AT MILFORD AND RECONNECT THE ESD POWER AND PILOT GAS FOR TRADITIONAL NON- ELECTRONIC OPERATION. THIS WAS COMPLETED ON WEDNESDAY, MAY 27, 2020.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200068 | 34838 | 2020-06-30 18:51 | SUPPLEMENTAL FINAL | 2879 | AMERICAN MIDSTREAM (LOUISIANA INTRASTATE), LLC | BLACK BEAR TRANSMISSION, LLC 1501 MCKINNEY, SUITE 800 | HOUSTON | TX | 77010 | 2020-05-29 15:31 | 2020 | CENTRAL | YES | 29.7698 | -90.0296 | 1278400 | 2020-05-29 17:48 | 1278551 | NATURAL GAS |  | 869 | 214 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-29 17:00 | 2020-06-20 11:15 |  | YES | OPERATOR | 2020-05-29 16:15 | NO | [5 empty] | VALVE CLOSURE |  | 2020-05-29 17:00 | VALVE CLOSURE |  | 2020-05-29 17:00 | 5 | 2020-05-29 16:00 | 2020-05-29 16:30 | ONSHORE | LA | 70037-0000 | BELLE CHASE | PLAQUEMINES |  |  | GLORIA-CHEVRON OAK PT 6-INCH PIPELINE | GLORIA-CHEVRON OAK PT 6-INCH PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 57 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.28 | 42000 | X-42 | SEAMLESS |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 2000 | 2000 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | [8 empty] | CLASS 3 LOCATION | YES | METHOD1 | 157 |  | NO | NO | [5 empty] | 0 | 0 | 636 | 661.754593747278372 | 2581 | 4529.918367346938775510204081632653061224 | 69084 | 71881.532003831728068 | 5633 | 5861.106331098143191 | 12335 | 12834.501436906727545 | PERMITTING, ACCESS FEES, TRAFFIC SOLUTIONS, ENGINEERING SUPPORT, NDE SERVICES | 2.97 | 90269 | 43223.3944383241961214460641399416909621 | 95768.8127329308159515102040816326530612 | 0 | 0 | 3 | 0 | NO |  |  |  | 550 | 550 | 989 | 192.619(A)(2) |  | 2006-10-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | NO | MANUAL | MANUAL | 26400 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY EXCAVATION ACTIVITY. LINE WAS HIT AFTER A ONE CALL WAS NOT CALLED IN FOR WORK BEING COMPLETED ON MAY 29TH 2020. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY |  |  |  |  | YES |  |  |  |  | CONTRACTOR | DIRECTIONAL DRILLING | UNKNOWN/OTHER | NO | [5 empty] | YES | 592 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | TODD RIVERA | SR MANAGER OFFSHORE EHS AND TRAINING | trivera@3cmidstream.com | 346-241-3663 |  |  |  |  | TODD RIVERA | SR MANAGER OFFSHORE EHS AND TRAINING | 3462413663 | trivera@3cmidstream.com | REVISED 2-10-2021 BY AMERICAN MIDSTREAM (LOUISIANA INTRASTATE), LLC. 3CM RECEIVED A CALL AT 1750 HOURS FROM BEVERLY CONSTRUCTION CO., LLC (BEVERLY CONSTRUCTION) STATING THAT THEIR SUBCONTRACTOR, MIXSON BORING, WAS CONDUCTING BORING ACTIVITY AND STRUCK OUR LINE AS THEY WERE RETRIEVING A CASING ACROSS HIGHWAY 23. BEVERLY CONSTRUCTION WAS ORIGINALLY SUPPOSED TO CONDUCT THE DIRECTIONAL DRILLING OPERATIONS ALONG E. OAK GROVE LN. BEVERLY CONSTRUCTION HAD SUBMITTED A ONE CALL TICKET FOR THE DIRECTIONAL DRILLING; HOWEVER, AT A LATER DATE BEVERLY CONSTRUCTION SUBCONTRACTED MIXSON BORING TO COMPLETE THE DIRECTIONAL DRILLING. THE 6-INCH PIPELINE WAS PROPERLY MARKED BY 3CM AFTER THE ONE CALL TICKET WAS RECEIVED FROM BEVERLY CONSTRUCTION, BUT DUE TO THE TIME LAPSE ON BEVERLY GETTING STARTED THEIR ONE CALL TICKET HAD EXPIRED AND A NEW TICKET WAS REQUIRED. TO 3CM'S KNOWLEDGE, MIXSON BORING DID NOT SUBMIT A ONE CALL TICKET PRIOR TO BEGINNING DIRECTIONAL DRILLING OPERATIONS. WITH THAT SAID, THIS INCIDENT WAS PREVENTABLE AND MIXSON BORING & BEVERLY CONSTRUCTION ARE THE LIABLE PARTY AS THEY STRUCK THE 6-INCH NATURAL PIPELINE WHILE CONDUCTING DIRECTIONAL DRILLING OPERATIONS. THE FIRST DROP IN PRESSURE WAS IDENTIFIED AT 1531 AND THE INCIDENT WAS IDENTIFIED AS REPORTABLE AT 1632. THE NOTIFICATION WAS MADE AT 1748 TO THE NATIONAL RESPONDER CENTER.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200069 | 33981 | 2020-06-30 19:34 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-06-04 14:27 | 2020 | EASTERN | YES | 38.2857 | -83.4015 | 1278874 | 2020-06-04 17:21 | 1278946 | NATURAL GAS |  | 11029.8 | 0 | 0.6 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-04 14:45 | 2020-06-05 00:38 |  | NO |  |  | NO | [11 empty] | 0 | 2020-06-04 14:20 | 2020-06-04 14:32 | ONSHORE | KY | 40351 | MOREHEAD | ROWAN | NOT APPLICABLE |  | LINE 100-7 | VALVE 1D7 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2020 | 2016 | CARBON STEEL |  | OTHER | [8 empty] | GAS WAS RELEASED THROUGH THE STATION BLOW DOWN SILENCER. | CLASS 2 LOCATION | NO |  | 458 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 17648 | 30974.0408163265306122448979591836734694 | 450 | 468.22258991552715 | 500 | 520.2473221283635 | 4221 | 4391.927893407644667 | CLEAN-UP OF OIL MIST RESIDUE. | 1.6 | 22819 | 22697.1239885859907171341107871720116618 | 36354.4386217780659292448979591836734694 | 0 | 0 | 0 | 0 | NO |  |  |  | 501 | 171000 | 765 | 192.619(A)(2) |  | 1964-12-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT A CONTRIBUTING FACTOR IN THE EVENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | OTHER MAINTENANCE | NO | [111 empty] | YES | [38 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | AT 2:20 PM TENNESSEE GAS PIPELINE COMPANY, L.L.C. (TGP) CONTROL ROOM RECEIVED AN ALARM OF AN EMERGENCY SHUTDOWN (ESD) AT STATION 110 IN MOREHEAD, KENTUCKY. AT 2:32 PM, AN OPERATOR ARRIVED ON SITE TO BEGIN ASSESSING THE ESD SYSTEM. THE RELEASED WAS STOPPED AT 2:45 PM AND AT 4:30 PM, WHILE ATTEMPTING TO RESET THE ESD SYSTEM, IT WAS DISCOVERED THAT VALVE 1D7, WHICH IS ON A SUCTION LINE COMING OFF OF LINE 100-7, DID NOT CLOSE AS DESIGNED DURING THE ESD. BECAUSE THE VALVE DID NOT CLOSE DURING THE ESD, GAS FROM THE MAINLINE WAS MAKING ITS WAY THROUGH THE SUCTION SIDE OF THE STATION AND OUT OF THE STATION SILENCER, VENTING TO ATMOSPHERE. AN EMERGENCY RESPONSE CALL WAS HELD AT 5:00 PM TO DISCUSS THE EVENT. BECAUSE THE 1D7 VALVE DID NOT CLOSE IT WAS FORECASTED THAT THE GAS LOSS QUANTITY WOULD EXCEED 3,000 MCF. AS A RESULT OF THIS FORECAST THE EVENT WAS REPORTED TO THE NRC. THE INITIAL ASSESSMENT DISCOVERED THAT A LIGHTNING EVENT CAUSED THE STATION TO ESD. AFTER FURTHER INVESTIGATION, IT WAS FOUND THAT THE VALVE OPERATOR ON VALVE 1D7 HAD RECENTLY BEEN REPLACED WITHOUT A MANAGEMENT-OF-CHANGE (MOC). THE VALVE OPERATOR HAD A DEFAULT CONFIGURATION FOR "PRESSURE-UP" ACTIVATION ON AN ESD SYSTEM; HOWEVER, THE ESD SYSTEM AT STATION 110 FUNCTIONS AS A "PRESSURE-DOWN" ESD SYSTEM. INSTALLATION OF THE VALVE OPERATOR WITHOUT AWARENESS OF ITS DEFAULT DESIGN CONFIGURATION, CAUSED VALVE 1D7 NOT TO CLOSE DURING THE ESD AT THE STATION. AS A CORRECTIVE ACTION, TGP REVIEWED ITS MOC PROCEDURE WITH OPERATORS AT STATION 110. OPERATORS WERE RETRAINED TO RECOGNIZE THAT A MOC IS NEEDED FOR MAKING CHANGES TO THE NORMAL DESIGN CONDITIONS OR DESIGN PARAMETERS OF PIPELINE OPERATIONS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200070 | 33989 | 2020-07-02 09:57 | ORIGINAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2020-06-03 16:20 | 2020 | CENTRAL | YES | 33.6526 | -102.5601 | 1278791 | 2020-06-03 16:39 | 1278876, 1278883 | NATURAL GAS |  | 1712 | 13919 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-03 18:01 | 2020-06-04 01:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-06-03 18:00 | VALVE CLOSURE |  | 2020-06-03 18:01 | 0 | 2020-06-03 13:40 | 2020-06-03 15:31 | ONSHORE | TX | 79379 | WHITEFACE | HOCKLEY | MILEPOST | 154+1400 | 1102 - DUMAS TO EUNICE | TAP 27-334 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | 1" THREADED TAP RISER | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | THREADED CONNECTION FAILED | [5 empty] | CLASS 1 LOCATION | NO |  | 19 |  | NO | NO | [5 empty] | 0 | 0 | 20739 | 21578.818427240261253 | 2551 | 4477.26530612244897959183673469387755102 | 2000 | 2080.989288513454 | 3750 | 3901.85491596272625 | 0 | 0 |  | 1.49 | 29040 | 15096.8904855929698088717201166180758017 | 32038.927937838890482591836734693877551 | 0 | 0 | 0 | 0 | NO |  |  |  | 655 | 0 | 780 | 192.619(C) |  | 1948-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91483 | NO | [5 empty] | YES | 1" TAP IS NOT PIGGABLE | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | NO | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | OFF-ROAD | 0 | YES |  |  | YES | [235 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON JUNE 3RD AT 1:40 PM, EL PASO NATURAL GAS COMPANY, L.L.C. (EPNG) GAS CONTROL WAS NOTIFIED BY A FARMER THAT THERE WAS A POTENTIAL NATURAL GAS LEAK IN AN AGRICULTURAL FIELD. AN OPERATOR WAS SENT TO THE SITE AND ARRIVED AT 3:31 PM TO CONFIRM THE LEAK. AN ERL (EMERGENCY RESPONSE LINE) CONFERENCE CALL WAS HELD AT 4:20 PM. AT THAT TIME THE GAS LOSS QUANTITY AND POTENTIAL DAMAGES WERE UNKNOWN, BUT OUT OF AN ABUNDANCE OF CAUTION A NOTIFICATION TO THE NRC WAS MADE. THE NRC WAS CALLED AT 4:25 PM. THE CALLER WAS PUT ON HOLD, AND THE NRC REPORT WAS TAKEN AT 4:39 PM. AS THE INVESTIGATION CONTINUED, EPNG DEEMED THE INCIDENT TO BE SIGNIFICANT PER INTERNAL PROCESSES. IN ORDER TO MINIMIZE CUSTOMER IMPACT, EPNG COMMUNICATED THE SITUATION WITH ITS CUSTOMERS ON THE LINE 1102 VALVE SEGMENT PRIOR TO THE VALVE SEGMENT BEING SHUT-IN AT 6:01 PM. AFTER THE PIPE WAS BLOWN DOWN, IT WAS DISCOVERED THAT THE GUARD RAILS WERE DAMAGED AND THE 1" RISER HAD BEEN BROKEN OFF AT THE THREADED CONNECTION TO THE ELBOW BELOW GRADE BY A FARMER OPERATING A TRACTOR ON THE PROPERTY NOT PERFORMING ANY EXCAVATION ACTIVITIES. TO REPAIR THE TAP EPNG CLOSED THE TAP VALVE, AND PLUGGED AND COATED THE PIPE. ON JUNE 4TH, 2020 AT 1:00 AM THE VALVE SEGMENT ON LINE 1102 WAS BROUGHT BACK INTO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200071 | 34654 | 2020-07-09 09:53 | SUPPLEMENTAL FINAL | 30028 | EGAN HUB STORAGE, LLC (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-06-19 13:53 | 2020 | CENTRAL | NO | 30.2601 | -92.574 | 1279959 | 2020-06-19 13:53 | 1280056 | NATURAL GAS |  | 2 | 59 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | YES |  | 2020-06-19 13:32 | 2020-06-24 08:30 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-06-19 13:17 | NO | [11 empty] | 0 | 2020-06-19 13:17 | 2020-06-19 13:53 | ONSHORE | LA | 70531 | EVANGELINE | ACADIA | MILEPOST | 0.732 | EGAN STORAGE FACILITY | EGAN PR3 SKID | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.218 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | OTHER | FBE | UNKNOWN | [26 empty] | 2008 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 63 |  | NO | NO | [5 empty] | 0 | 0 | 200 | 208.0989288513454 | 7 | 12.28571428571428571428571428571428571429 | 140000 | 145669.25019594178 | 0 | 0 | 0 | 0 |  | 3.39 | 140207 | 64363.5606584355977183673469387755102041 | 145889.6348390788396857142857142857142857 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 0 | 1480 | 192.619(A)(1) |  | 2009-09-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | NO | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES |  |  |  |  | YES | YES |  |  | YES | YES |  |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [19 empty] | YES | [43 empty] | MICHAEL MCGRATH | PIPELINE COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | [5 empty] | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 1:17 PM EDT ON JUNE 19, 2020, TETLP PERSONNEL CONDUCTING A LEAKAGE SURVEY IDENTIFIED A RELEASE OF NATURAL GAS NEAR TETLP'S 24-INCH DIAMETER PIPING BETWEEN THE PR3 SKID AND THE 670 CONTACTOR AT THE EGAN COMPRESSOR STATION IN TEXAS. THE SECTION OF THE PIPE SEGMENT WAS DOWN FOR A PLANNED OUTAGE AND THE RELEASE OF GAS WAS IDENTIFIED WHILE BRINGING THE PIPE SEGMENT BACK TO SERVICE. TETLP SUBSEQUENTLY ISOLATED AND DEPRESSURIZED THIS PIPE SEGMENT. THE LEAK WAS IDENTIFIED ON A 2-INCH LOW POINT DRAIN. THE INVESTIGATION AND METALLURGICAL ANALYSIS DETERMINED THAT THE LEAK WAS THE RESULT OF INTERNAL CORROSION CAUSED BY A BUILD UP A CARBONIC ACID IN THE 2-INCH LOW POINT DRAIN. THE SEGMENT OF PIPE HAS BEEN CUT OUT AND REPLACED AND THE LINE HAS BEEN RESTORED TO IT'S PREVIOUS PRESSURE. UPDATED 12-23-2020 EGAN COMPLETED THE INVESTIGATION AND DETERMINED THE CAUSE OF THE FAILURE WAS INTERNAL CORROSION WITHIN THE LOW POINT DRAIN. UPDATED PART D.3. AND PART G.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20200072 | 34783 | 2020-07-09 12:11 | SUPPLEMENTAL FINAL | 31225 | AK STEEL CORP | 200 PUBLIC SQUARE SUITE 3400 | CLEVELAND | OH | 44114 | 2020-05-15 15:00 | 2020 | EASTERN | YES | 39.4892 | -84.3958 | 1277360 | 2020-05-15 16:53 |  | NATURAL GAS |  | 5153 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-05-15 15:15 | 2020-05-16 18:00 |  | YES | OPERATOR | 2020-05-15 15:00 | YES | 2020-05-15 15:00 | ALLOWED TO BURN OUT |  | 5153 | NO | VALVE CLOSURE |  | 2020-05-15 15:15 | VALVE CLOSURE |  | 2020-05-15 15:22 | 20 | 2020-05-15 15:00 | 2020-05-15 15:10 | ONSHORE | OH | 45043 | MIDDLETOWN | BUTLER | NOT APPLICABLE |  | AK STEEL NATURAL GAS PIPELINE | AIR PRODUCTS INLET PIPING AND METERING | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3.5 | NO | 0.256 | 23242 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 2012 | 2012 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3 | 3 |  | CLASS 3 LOCATION | NO |  | 45 |  | NO | NO | NO |  |  |  |  | 7000 | 7283.462509797089 | 0 | 0 | 46892 | 82300.2448979591836734693877551020408163 | 75000 | 78037.098319254525 | 0 | 0 | 0 | 0 |  | 9.1 | 128892 | 91641.1549739264528688046647230320699708 | 167620.8057270107976734693877551020408163 | 0 | 1 | 0 | 1 | NO |  |  |  | 160 | 12000 | 340 | 192.619(A)(2) |  | 2012-04-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 80 | NO | YES | [6 empty] | YES |  |  |  |  | YES | SMALL DIAMETER PIPE | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | YES | YES | YES |  |  |  | NO | 85 |  | PASSENGER CAR | ROADWAY | 25 | YES |  |  |  | YES | JERSEY BARRIERS | [203 empty] | YES | [29 empty] | JOHN JOHNSON |  | jjohnson@uti-corp.com | 5135948600 |  |  |  |  | JOHN JOHNSON |  | 5135948600 | jjohnson@uti-corp.com | ON 5/15/20 AT APPROXIMATELY 3:00PM, A CAR TRAVELING NORTH ON YANKEE RD IN MIDDLETOWN, OHIO STRUCK AN INLET RISER TO AN AIR PRODUCTS FACILITY. THE VEHICLE WAS TRAVELING AT A HIGH RATE OF SPEED AND CROSSED THE CENTER LINE OF YANKEE RD. THE VEHICLE WENT OFF OF THE ROAD FOR A DISTANCE OF ABOUT 300 FEET BEFORE IT STRUCK AND RUPTURED A 3" NATURAL RISER AND METER SETTING THAT FEEDS THE AIR PRODUCTS FACILITY. THE 3" NATURAL GAS RISER AND METER SETTING IS OPERATED BY AK STEEL CORPORATION (OPID 31225). THE PIPELINE IGNITED WHEN IT WAS RUPTURED BY THE VEHICLE AND CAUGHT THE VEHICLE ON FIRE. ONE OCCUPANT IN THE VEHICLE WAS INJURED AND SUFFERED 2ND AND 3RD DEGREE BURNS. THE OCCUPANT WAS WAS TRANSPORTED TO THE HOSPITAL BUT DID SURVIVE THE ACCIDENT. THE 3" NATURAL GAS PIPELINE WAS SHUT OFF AT THE REGULATOR STATION OUTLET VALVE. REPAIRS WERE MADE TO THE 3" NATURAL GAS PIPELINE AND THE PIPELINE WAS PUT BACK INTO SERVICE THE FOLLOWING DAY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200073 | 34512 | 2020-07-10 14:04 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2020-06-12 15:21 | 2020 | MOUNTAIN | YES | 42.6539 | -113.0082 | 1279463 | 2020-06-12 16:39 | 1279598 | NATURAL GAS |  | 2462 | 5749 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-10 16:05 | 2020-08-12 16:52 |  | YES | OPERATOR | 2020-06-10 18:50 | NO | [5 empty] | VALVE CLOSURE |  | 2020-06-10 16:05 | VALVE CLOSURE |  | 2020-06-10 16:05 | 0 | 2020-06-10 13:29 | 2020-06-10 13:15 | ONSHORE | ID | 83211 | Not Within a Municipality | POWER | MILEPOST | 626.8 | WILLIAMS NORTHWEST PIPELINE | MAINLINE 1400 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | ASPHALT |  | UNKNOWN | [26 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 443 |  | NO | NO | [5 empty] | 0 | 0 | 8853 | 9211.499085604804131 | 0 | 0 | 600000 | 624296.7865540362 | 0 | 0 | 0 | 0 |  | 1.54 | 608853 | 279479.592702255372777 | 633508.285639641004131 | 0 | 0 | 0 | 0 | NO |  |  |  | 383 | 10000 | 850 | 192.619(A)(3) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91783 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | GAS DETECTION IN RESPONSE TO ANOMALIES IDENTIFIED THROUGH IN-LINE INSPECTION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS WERE OF A MINOR NATURE IN TERMS OF GAS LOSS, AND SCADA IS NOT WELL SUITED FOR IDENTIFYING THESE TYPES OF LEAKS. LEAKS WERE DISCOVERED DURING FOLLOW UP ACTIVITIES ASSOCIATED WITH IN-LINE INSPECTION OF THE LINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2020 |  |  |  |  | 2020 | [5 empty] | YES |  | NO | [63 empty] | BRET BURKHART | ENGINEER III - PIPELINE SAFETY | bret.burkhart@williams.com | 801-584-6892 |  | DAVE DICKERSON | david.s.dickerson@williams.com | 208-884-4300 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | IN APRIL OF 2020 WILLIAMS CONTRACTED WITH AN IN-LINE INSPECTION VENDOR TO COMPLETE TOOL RUNS ON THE WILLIAMS NORTHWEST PIPELINE 1400 POCATELLO TO BURLEY SEGMENT. HIGH-RES MFL TOOL RUNS WERE CONDUCTED, AND A PRELIMINARY REPORT WAS PROVIDED TO WILLIAMS WITH CERTAIN HIGH-PRIORITY ANOMALIES ON THE WEEK OF 5/25/2020. A PROJECT WAS INITIATED TO ADDRESS PRELIMINARY HIGH-PRIORITY ANOMALIES. IN PREPARATION TO EXCAVATE, WILLIAMS OPERATIONS CONDUCTED A LEAK SURVEY OF THE EXCAVATION AREA AND IDENTIFIED GAS READINGS AT THREE ANOMALIES WITHIN AN APPROXIMATE 350FT. SPAN ON 6/10/2020 NEAR M.P. 626.8. IN RESPONSE, THE LINE SEGMENT BETWEEN VALVES 9-1 AND 9-2 WAS SHUT-IN AND BLOWN DOWN ON THE SAME DATE. EXCAVATIONS OF THE ANOMALIES CONFIRMED PIN-HOLE LEAKS RESULTING FROM CORROSION. AFTER ASSESSING REPAIR OPTIONS WILLIAMS PROJECT MANAGEMENT DETERMINED THAT REPAIRS WOULD BE BEST ACCOMPLISHED THROUGH PIPE REPLACEMENT OF APPROXIMATELY 400'. THE PRELIMINARY COST OF REPAIRS EXCEEDS $50,000, WITH COST OF CONTRACTOR AND INTERNAL LABOR APPROACHING $600,000. IT WAS DETERMINED THAT THIS QUALIFIED AS A DOT REPORT-ABLE INCIDENT BASED ON COST WHEN WILLIAMS MANAGEMENT SETTLED ON PIPE REPLACEMENT AS THE PREFERRED REPAIR OPTION ON 6/12/2020. THE NRC WAS INITIALLY NOTIFIED OF THE INCIDENT ON 6/12/2020. AT THE TIME OF THIS REPORT THE LINE IS SHUT-IN AND BLOWN-DOWN. THE ANTICIPATED START DATE FOR THE REPLACEMENT PROJECT IS 7/13/2020 WITH ANTICIPATED PROJECT COMPLETION 8/1/2020. ON 8/12/2020 ALL REPAIRS ON THE LINE WERE COMPLETED, AND THE PIPELINE WAS RETURNED TO SERVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200074 | 34055 | 2020-07-13 13:10 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-06-16 18:40 | 2020 | CENTRAL | NO | 28.9033 | -96.7143 | 1279731 | 2020-06-16 19:39 | 1279859 | NATURAL GAS |  | 9 | 2768 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-16 20:59 | 2020-06-17 19:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-06-16 20:47 | VALVE CLOSURE |  | 2020-06-16 20:59 | 0 | 2020-06-16 18:40 | 2020-06-16 18:30 | ONSHORE | TX | 77957 | EDNA | JACKSON | SURVEY STATION NO. | 209+71 | TOM O CONNOR | 3022 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 51 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.312 | 52000 | API5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COAL TAR |  | YES | [26 empty] | 1958 | 1958 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 346 |  | NO | NO | [5 empty] | 0 | 0 | 5038 | 5242.012017765390626 | 16 | 28.08163265306122448979591836734693877551 | 60000 | 62429.67865540362 | 1500 | 1560.7419663850905 | 0 | 0 |  | 1.82 | 66554 | 30561.1233830514678268396501457725947522 | 69260.5142722071623504897959183673469388 | 0 | 0 | 0 | 0 | NO |  |  |  | 665 | 15000 | 880 | 192.619(C) |  | 2014-11-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 40656 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | WATER | NO | [5 empty] | YES | 25 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | TIMOTHY BUNAG | ENGINEER - REGULATORY COMPLIANCE | timothy.bunag.@energytransfer.com | 832-294-5324 |  | TIMOTHY BUNAG | timothy.bunag@energytransfer.com | 832-294-5324 | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | christopher.kresta@energytransfer.com | ON JUNE 16, 2020, AT APPROXIMATELY 6:10 PM, ENERGY TRANSFER GAS CONTROL RECEIVED A CALL FROM A 3RD PARTY CONTRACTOR ABOUT A LINE STRIKE ON THE 3022 TOM O CONNOR 16 IN NATURAL GAS PIPELINE. THIS PIPELINE IS A TRANSMISSION LINE IN A CLASS 1 AREA LOCATED IN JACKSON COUNTY, APPROXIMATELY 4 MILES SOUTH OF EDNA, TX. OPERATIONS PERSONNEL WERE DISPATCHED AND ARRIVED ON LOCATION AT 6:30 PM TO INVESTIGATE. AT 6:40 PM, THE INVESTIGATION CONFIRMED THE 3RD PARTY LINE STRIKE ON THE 16 IN ETC PIPELINE. OPERATIONS PROCEEDED WITH LINE ISOLATION PROCEDURES AND BEGAN PROCESS TO REPAIR. THE UPSTREAM AND DOWNSTREAM VALVES WERE CLOSED TO ISOLATE THE PIPELINE AT 8:47 PM AND 8:59 PM. THE PIPELINE BLOW DOWN WAS COMPLETED AT 11:25 PM. THE REPAIRS WERE MADE AND LINE WAS PUT BACK IN SERVICE AS OF 7:10 PM ON JUNE 17, 2020. THE INVESTIGATION REVEALED THAT THE 3RD PARTY CONTRACTOR WAS TRENCHING ACROSS THE RIGHT-OF-WAY AND HIT THE PIPELINE WITH EXCAVATION EQUIPMENT. THE CONTRACTOR FAILED TO MAKE A ONE CALL NOTIFICATION PRIOR TO EXCAVATING. THIS PIPELINE IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON JUNE 16, 2020, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC#1279731) AT 7:39 PM AND TO THE TXRRC (INCIDENT #2221) AT 8:03 PM. A 48 HOUR NRC UPDATE WAS MADE ON JUNE 18, 2020 AT 9:29 AM (NRC#1279859) **07/16/2020 UPDATED GPS COORDINATES **07/20/2020 UPDATED NARRATIVE DESCRIPTION & INCIDENT TIMES UNDER A4 AND A13
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200075 | 34558 | 2020-07-23 19:50 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-06-24 19:32 | 2020 | CENTRAL | YES | 41.3793 | -91.1951 | 1280350 | 2020-06-25 09:17 | 1280436 | NATURAL GAS |  | 50866 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-06-25 08:07 | 2020-06-25 08:07 | ONSHORE | IA | 52752 | LETTS | MUSCATINE | MILEPOST | 821 | COMPRESSOR STATION 199 | AMARILLO LINE #2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | OTHER | LEAK THROUGH VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 479 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 79860 | 140162.4489795918367346938775510204081633 | 175 | 182.086562744927225 | 150 | 156.07419663850905 | 0 | 0 |  | 1.57 | 80185 | 92116.2389693066362559037900874635568513 | 140500.6097389752730096938775510204081633 | 0 | 0 | 0 | 0 | NO |  |  |  | 550 | 91 | 712 | 192.619(C) |  | 1947-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO INDICATION OF CONTROLLER INVOLVEMENT IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | NORMAL WEAR AND TEAR | [161 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | 713-420-4417 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON THE AFTERNOON OF JUNE 24, 2020, EMPLOYEES AT NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) STATION 199 WERE PERFORMING OPERATIONAL TESTS ON THE BACKUP COMPRESSOR UNIT. WHEN THE TESTS WERE COMPLETE, THE EMPLOYEES STARTED THE SHUTDOWN PROCESS ON THE UNIT AND CHECKED IN THE STATION PLC THAT ALL UNIT VALVES WERE IN THE PROPER POSITION BEFORE LEAVING THE SITE FOR THE DAY. WHEN EMPLOYEES ARRIVED ON SITE THE NEXT MORNING, JUNE 25, 2020 AT 8:07, THEY DISCOVERED THAT GAS WAS VENTING AND CONFIRMED DISCOVERY OF AN INCIDENT. THEY DETERMINED THAT THE 36 INCH DISCHARGE MANIFOLD VALVE ON THE UNIT WAS NOT FULLY CLOSED, DESPITE INDICATING CLOSED ON THE PLC. THIS THEREFORE ALLOWED GAS TO CONTINUE TO VENT. THE EMPLOYEES MANUALLY CLOSED THE VALVE TO STOPPED THE RELEASE AND INITIATED THE ERL PROTOCOL. DURING THE ERL CALL THE INCIDENT WAS DEEMED REPORTABLE AND THE CALL TO THE NRC WAS INITIATED AT 9:01. HOWEVER, DUE TO HOLD TIMES, THE REPORT WAS NOT TAKEN UNTIL 9:17. THE INVESTIGATION IN TO THE RELEASE REVEALED THAT A CRACKED AND PUNCTURED VALVE DIAPHRAGM WAS RESPONSIBLE FOR THE BLOCK VALVE'S FAILURE TO FULLY CLOSE. THE PILOT OPERATOR WAS REPAIRED BY REPLACING THE DAMAGED DIAPHRAGM WITH A NEW DIAPHRAGM. IN ORDER TO PREVENT A REOCCURRENCE, ALL CONTROL DIAPHRAGMS ON SIMILAR PILOT OPERATING VALVES AT THIS STATION WERE INSPECTED AND REPLACED. FINALLY, A PRESSURE MONITORING ALGORITHM WAS ADDED TO THE PLC AND WILL ISSUE A CALL OUT ALARM IF THE COMPRESSOR HAS NOT BLOWN DOWN AFTER A SET TIME
2023-02-28 09:42 | YES | YES | UNGS (Underground Natural Gas Storage) | 20200076 | 34636 | 2020-07-30 11:04 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2020-06-30 16:09 | 2020 | CENTRAL | YES | 36.8513 | -97.4884 | 1280759 | 2020-06-30 16:45 | 1280912 | NATURAL GAS |  | 0 | 14.9 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | ROUTINE SHUTDOWN | [5 empty] | YES | OPERATOR | 2020-06-30 12:23 | NO | [11 empty] | 0 | 2020-06-30 12:10 | 2020-06-30 07:15 | ONSHORE | OK | 74646 | Not Within a Municipality | GRANT | NOT APPLICABLE |  | WEBB STORAGE FIELD | WEBB WELL NUMBER 30 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1965 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | INTENTIONAL GAS RELEASE FOR MAINTENANCE WORK AT STORAGE WELL | CLASS 1 LOCATION | NO |  | 204 |  | NO | NO | NO |  |  |  |  | 0 | 0 | 24 | 24.971871462161448 | 0 | 0 | 0 | 0 | 3000 | 3121.483932770181 | 0 | 0 |  | 1.62 | 3024 | 1388.095793782112016 | 3146.455804232342448 | 0 | 1 | 0 | 0 | NO |  |  |  | 1429 | 941 | 1850 | OTHER | FERC DOCKET IN01-2-000 | 2000-12-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE WELL WAS ISOLATED FOR MAINTENANCE, NO CONTROLLER INVOLVEMENT | [12 empty] | YES | 2 | 0 | YES | 3 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | DURING ROUTINE MAINTENANCE AT THIS WELLHEAD, A THREADED FITTING ON THE CONTRACTOR'S ASSEMBLY ROTATED DURING BLOW DOWN RESULTING IN INJURY. THE EXISTING PROCEDURE DID NOT CALL FOR THESE TYPE FITTINGS TO BE SECURED TO PREVENT ROTATION DURING ROUTINE MAINTENANCE. | YES |  |  |  |  | ROUTINE MAINTENANCE | NO | [150 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 6/30/2020 AT 12:49 PM CDT, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) RECEIVED NOTICE FROM FIELD PERSONNEL THAT THERE HAD BEEN AN ACCIDENT WITH INJURY AT A WELLHEAD LOCATED IN GRANT COUNTY, OKLAHOMA. THE WELL LOCATED IN THE SSCGP WEBB STORAGE FIELD, WELL NUMBER 30 WAS IN THE PROCESS OF BEING ISOLATED AND BLOWN DOWN FOR SCHEDULED MAINTENANCE. DURING THE BLOW DOWN A FITTING ROTATED AT 12:10 PM CDT, CAUSING AN APPARENT INJURY TO THE SSCGP EMPLOYEE. THE EMS WERE CALLED AT 12:23 PM CDT AND ARRIVED ON SITE AT 12:55 PM CDT. THE EMPLOYEE ARRIVED AT THE HOSPITAL AND WAS PLACED UNDER OBSERVATION. AT 4:09 PM CDT, THE EMPLOYEE WAS ADMITTED TO THE HOSPITAL FOR FURTHER TESTING AND OBSERVATION. AT 4:45 PM CDT ON 6/30/2020 THE NRC WAS NOTIFIED OF THE EVENT WITH THE FOLLOW UP CALL AT 12:45 PM CDT ON 7/2/2020. THE EMPLOYEE WAS RELEASED FROM THE HOSPITAL ON 7/5/2020. DURING THE MAINTENANCE ACTIVITY, THE PUMP-IN-SUB AND LUBRICATOR SHOULD HAVE REMAINED STATIONARY BUT THE ASSEMBLY ROTATED, STRIKING THE EMPLOYEE IN THE HEAD. ADDITIONAL INFORMATION IN SUPPLEMENTAL REPORT: ALTHOUGH THIS TYPE OF MAINTENANCE ACTIVITY HAS BEEN PERFORMED NUMEROUS TIMES FOLLOWING THE ESTABLISHED PROCEDURE RESULTING IN NO PREVIOUS ROTATION OR INJURIES, SSCGP HAS UPDATED THE O&M PROCEDURE 85.02.03 PER PHMSA'S RECOMMENDATION TO REQUIRE EQUIPMENT TO BE SECURED TO PREVENT ROTATION SO THE RISK FOR UNINTENDED MOVEMENT IS ELIMINATED TO THE EXTENT POSSIBLE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200077 | 34865 | 2020-07-30 16:21 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-07-02 07:34 | 2020 | CENTRAL | YES | 30.4591 | -93.1457 | 1280884 | 2020-07-02 08:33 | 1281173 | NATURAL GAS |  | 404 | 176 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE STATION WAS CURRENTLY NOT RUNNING. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-07-02 07:34 | 2020-07-02 07:34 | ONSHORE | LA | 70657 | RAGLEY | BEAUREGARD | MILEPOST | 64.4 | GILLIS COMPRESSOR STATION | GILL-OPEL | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 66 | YES | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 10 | NO | 0.5 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 281 |  | NO | NO | [5 empty] | 0 | 0 | 297 | 309.026909344247919 | 683 | 1198.73469387755102040816326530612244898 | 275000 | 286136.027170599925 | 0 | 0 | 0 | 0 |  | 1.69 | 275980 | 127155.132405388662750842565597667638484 | 287643.788773821723939408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 850 | 0 | 1440 | 192.619(A)(1) |  | 1969-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | YES |  | YES | ROOT CAUSE OF THE CORROSION FOUND IN THESE SAMPLES IS ELECTROCHEMICAL CORROSION EXACERBATED BY CHLORIDES, FREE SULFUR AND FREE WATER. A SECONDARY CAUSE OF THE CORROSION IS THE ACCUMULATED WATER WET SOLIDS FOUND AT THE 6:00 POSITION IN THE SAMPLES. POTENTIAL TERTIARY CAUSES OF CORROSION INCLUDE CARBON DIOXIDE AND BIOLOGICAL ACTIVITY. |  | YES |  |  | YES |  | YES |  |  |  | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL MCGRATH | SENIOR ENGINEER | michael.mcgrath@enbridge.com | 16128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 281-686-3829 | nathan.atanu@enbridge.com | ORIGINAL REPORT: AT APPROXIMATELY 7:34 AM CDT ON JULY 2, 2020 AN ENBRIDGE CONTRACTOR DISCOVERED A NATURAL GAS RELEASE BELOW GROUND AT THE GILLIS COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN BEAUREGARD PARISH, LA. THE LEAK WAS LOCATED ON THE 10-INCH EQUALIZER LINE. THE LINE WAS ISOLATED AND BLOWN DOWN ON JULY 2, 2020 AT 8:05 A.M. CDT, AND IT REMAINED ISOLATED UNTIL REPAIR WAS COMPLETE. THE PIPE WAS REPLACED ON JULY 19, 2020. THE APPARENT CAUSE IS INTERNAL CORROSION AND IS UNDER METALLURGICAL INVESTIGATION. 02/16/2021 METALLURGICAL ANALYSIS CONCLUDED THAT THE INTERNAL CORROSION WAS A RESULT OF A COMBINATION OF THE PRESENCE OF SULFUR AND CHLORIDES. THE CORROSION WAS EXACERBATED BY THE PRESENCE OF SOLIDS BUILDUP IN THE STATION PIPING. THIS PIPING AND SIMILAR PIPING IS INCLUDED IN THE ENBRIDGE FACILITY INTEGRALITY PLAN. UNDER THIS PLAN THE NEED FOR DESIGN MODIFICATIONS, PERIODIC ASSESSMENTS AND CLEANING WILL BE CONSIDERED FOR THIS LOCATION AND OTHER SIMILAR LOCATIONS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200078 | 34848 | 2020-08-04 21:27 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-07-05 00:37 | 2020 | EASTERN | YES | 42.8091 | -82.8654 | 1283199 | 2020-07-30 12:45 | 1283435 | NATURAL GAS |  | 1376 | 114 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-05 03:03 |  | YES |  |  |  | YES | 2020-07-05 00:37 | ALLOWED TO BURN OUT |  | 1376 | YES | [6 empty] | 0 | 2020-07-05 01:31 | 2020-07-05 02:12 | ONSHORE | MI | 48062 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION | UNIT 2-6 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE OTHER ENCLOSED SPACE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2013 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | A MECHANICAL SEAL FAILURE OCCURRED IN THE REACTION TURBINE CAUSING OIL TO LEAK INTO THE EXHAUST CHAMBER WHICH RESULTED IN A FIRE. THE PLC SHUT-DOWN AND NO LONGER COMMUNICATE TO THE UNIT. THE ESD SYSTEM DID NOT COMMUNICATE WITH THE PLC TO SHUT DOWN THE UNIT, AND THE PROCESS GAS SUCTION AND DISCHARGE VALVES FAILED TO CLOSE, ALLOWING NATURAL GAS INTO THE ENCLOSURE THROUGH THE SEAL OIL SYSTEM. AN IGNITION OCCURRED WHEN NATURAL GAS CAME INTO CONTACT WITH THE OIL FIRE AT THE TOP OF THE EXHAUST. | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO | [5 empty] | 0 | 0 | 261 | 271.569102151005747 | 3151 | 5530.326530612244897959183673469387755102 | 2000000 | 2080989.288513454 | 980 | 1019.68475137159246 | 0 | 0 |  | 2.29 | 2004392 | 922251.1280353840974083586005830903790087 | 2087810.86889758884310495918367346938776 | 0 | 0 | 0 | 0 | NO |  |  |  | 1133 | 50 | 1800 | 192.619(A)(2) |  | 1969-02-03 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS HAD NO INDICATION OTHER THAN A CHANGE IN RATE THAT ANYTHING WAS OCCURRING UNTIL NOTIFIED BY LOCAL EMERGENCY RESPONDERS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [27 empty] | YES | [166 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JULY 5, 2020 AT APPROXIMATELY 00:13 HOURS CONSUMERS ENERGY'S RAY COMPRESSOR STATION UNIT 2-6 EXPERIENCED AN UNPLANNED SHUTDOWN RESULTING IN A NATURAL GAS FIRE. THE FACILITY IS LOCATED AT 69333 OMO ROAD, ARMADA, MICHIGAN (MACOMB COUNTY). THE FIRE WAS INITIATED IN THE TURBINE EXHAUST CHAMBER DUE TO THE INTERACTION OF OIL AND HIGH TEMPERATURE GAS. THE PRESENCE OF OIL WAS DUE TO A MECHANICAL SEAL FAILURE IN THE TURBINE.THE MECHANICAL SEAL FAILURE RESULTED IN UNSTABLE TURBINE SPEED SENDING MULTIPLE ALARMS TO THE PROGRAMMABLE LOGIC CONTROLLER (PLC). THE PLC FAILED TO CONTINUE OPERATIONS ONCE DATA POINTS REACHED A MAXIMUM OF 959 POINTS. THE PLC REGISTER FAULTED AND COULD NOT OVERWRITE THE DATA WHICH PREVENTED THE EQUIPMENT FROM SHUTTING DOWN PROPERLY. AS A RESULT OF THE PLC FAILURE, THE PROCESS GAS SUCTION, DISCHARGE AND FUEL GAS VALVES FAILED TO CLOSE. A GASKET FAILURE OCCURRED BETWEEN THE TURBINE REACTION CHAMBER AND THE TURBINE RESULTING IN A FIRE IN THE INSULATION PROVIDING A HEAT SOURCE TO IGNITE THE GAS NEAR THE EXHAUST STACK. THE FIRE WAS LIMITED TO THE 2-6 SKID AND EXHAUST STACK. THE LOCAL FIRE DEPARTMENT REPORTED TO THE SITE ENTRANCE BUT WERE NOT UTILIZED TO EXTINGUISH THE FIRE. THE STATION OPERATOR ISOLATED THE FUEL AND PROCESS GAS PIPING SYSTEMS ALLOWING THE FUEL SOURCE TO BURN OFF, EXTINGUISHING THE FIRE. CONSUMERS ENERGY'S RAY COMPRESSOR STATION (PLANT 2) REMAINS OUT OF SERVICE AND REPAIR OPTIONS ARE BEING EVALUATED. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED WHEN A FINAL RESTORATION PLAN A IS DEVELOPED AND NORMAL OPERATIONS RESUMED. FOLLOWING AN EVALUATION OF OPERATIONAL NEEDS, IT WAS DETERMINED THE RAY COMPRESSOR STATION PLANT 2 UNIT 2-6 WOULD BE RETIRED. THE RETIREMENT OF THE UNIT WAS COMPLETED ON DECEMBER 8, 2020.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200079 | 34437 | 2020-08-11 19:08 | SUPPLEMENTAL FINAL | 39193 | ROVER PIPELINE, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-07-12 12:33 | 2020 | EASTERN | YES | 40.4521 | -81.2273 | 1281699 | 2020-07-12 13:33 | 1281846 | NATURAL GAS |  | 3700 | 2800 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-12 01:56 | 2020-07-12 03:10 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-07-12 02:08 | NO | [11 empty] | 0 | 2020-07-12 01:34 | 2020-07-12 01:54 | ONSHORE | OH | 44621 | DENNISON | CARROLL | NOT APPLICABLE |  | ROVER MAINLINE | COMPRESSOR STATION 1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2018 | 2018 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | [5 empty] | 0 | 0 | 4004 | 4166.140555603934908 | 5291 | 9286.244897959183673469387755102040816327 | 100 | 104.0494644256727 | 0 | 0 | 0 | 0 |  | 1.43 | 9395 | 7976.978402348609747661807580174927113703 | 13556.4349179887912814693877551020408163 | 0 | 0 | 0 | 0 | NO |  |  |  | 1262 | 407000 | 1440 | 192.619(A)(1) |  | 2017-10-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE INCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [9 empty] | YES | [172 empty] | KATHRYN HARRYMAN | SR. SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 8326605977 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON 7/12/20 AT 01:34 EST THE HOUSTON CONTROL CENTER RECEIVED A SCADA ALARM FOR SOUND LEVEL AT THE LEESVILLE COMPRESSOR STATION. CONTROL CENTER IMMEDIATELY CONTACTED LOCAL OPERATIONS PERSONNEL TO RESPOND TO THE STATION AND INVESTIGATE. LOCAL OPERATIONS PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 01:54 AND THE STATION WAS SHUTDOWN AT 01:56. AT 02:08 HOUSTON CONTROL CENTER WAS CONTACTED BY LOCAL FIRE DEPT. REGARDING A NOISE COMPLAINT AND EXPLAINED THAT THE SITUATION WAS BEING ADDRESSED. UPON FURTHER INVESTIGATION AFTER THE AREA WAS SAFE OPERATIONS PERSONNEL DISCOVERED FAILED SMALL DIAMETER TUBING ON UNIT 205. THE TUBING WAS REPLACED AND UNIT 205 WAS RETURNED TO SERVICE AT 03:10. AFTER VOLUME RELEASED CALCULATIONS WERE COMPLETED IT WAS DETERMINED THAT THIS EVENT MET REPORTING THRESHOLDS AT WHICH TIME THE NRC WAS NOTIFIED. TO PREVENT RECURRENCE ADDITIONAL SUPPORT WAS PROVIDED FOR THE TUBING. OTHER FACILITIES OF SIMILAR DESIGN WILL BE INSPECTED AND ADDITIONAL SUPPORT WILL BE PROVIDED AS NECESSARY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200080 | 34435 | 2020-08-13 08:39 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2020-07-23 08:30 | 2020 | EASTERN | YES | 29.1788 | -92.2235 | 1282605 | 2020-07-23 08:52 | 1282744 | NATURAL GAS |  | 0.036 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-07-17 13:00 | 2020-07-17 13:00 | OFFSHORE | [6 empty] | 20" FROM VERMILLION 67 TO SHORE | 22-6004 | [20 empty] | 40 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | VERMILLION | 67 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1968 | 1968 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 380 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 66801 | 69506.082730993620327 | 0 | 0 | 0 | 0 |  | 2 | 66801 | 30663.421666811793909 | 69506.082730993620327 | 0 | 0 | 0 | 0 | NO |  |  |  | 760 | 0 | 1168 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A VERY SMALL LEAK NOT CAPTURED BY SCADA | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | VALVE STEM SEAL FAILED DUE TO NORMAL WEAR AND TEAR. | [14 empty] | YES | [163 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST | edgar.x.rodriguez@williams.com | 7132152846 |  | TRAVIS LABOVE | travis.labove@williams.com | 3372633899 | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | WILLIAMS TECH AND APV VALVE SERVICE WERE TROUBLESHOOTING THE WILLIAMS OWNED VERMILLION 67 PLATFORM LC 300 20 INCH PIG LAUNCHER BLOCK VALVE EIM ACTUATOR. WHILE OPERATING THE VALVE BEGAN TO LEAK GAS AND OIL MIX INTERMITTENTLY FROM THE STEM SEAL. TROUBLESHOOTING WAS STOPPED AND NOTIFICATIONS WERE MADE TO THE OPERATIONS SUPERVISOR. THE SUPERVISOR THEN MADE NOTIFICATIONS TO THE SOC, OFFSHORE REGULATORY LEAD, AND THE MANAGEMENT TEAM. THERE IS CURRENTLY NO IMPACT TO WATER, OIL PADS WERE PLACED ON THE ACTUATOR AND A DRIP PAN PLACED UNDER THE VALVE TO PREVENT ANY IMPACT TO THE WATER. ALTHOUGH THE LEAK HAPPENED ON JULY 17TH IT WAS NOT DETERMINED THAT THE COST OF REPAIR THRESHOLD FOR REPORTING WAS GOING TO BE MET UNTIL JULY 23RD HENCE THE CALL TO THE NRC. 8/19/2020 UPDATE. LEAK DETERMINED TO BE DUE TO NORMAL WEAR AND TEAR OF THE VALVE SEAL. ON 8/13/2020 PRESSURE WAS REDUCED AND RECOMPRESSED AND AT THAT TIME THE LEAK STOPPED. THE LEAK TOOK PLACE AFTER THE DEMARCATION POINT AS TO WHAT WILLIAMS CONSIDERS GATHERING AND WHAT IS TRANSMISSION. AS PART OF OUR RESPONSE, WILLIAMS REALIZED THAT THERE IS A MISTAKE WITHIN OUR GIS MAPS AND THIS LINE WAS REPORTED ABANDONED DURING THE 2020 ANNUAL REPORT AND NPMS SUBMITTAL. WILLIAMS IS WORKING ON FIXING THIS ISSUE AND CREATING A SUPPLEMENTAL REPORT OF THE ANNUAL REPORT AND NPMS SUBMITTAL.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200081 | 36511 | 2020-08-13 09:23 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-07-14 10:00 | 2020 | CENTRAL | NO | 28.3858 | -90.1448 | 1281840 | 2020-07-14 10:52 | 1282148 | NATURAL GAS |  | 1488 | 200 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-14 10:00 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-14 10:00 | VALVE CLOSURE |  | 2020-07-14 17:00 | 0 | 2020-07-20 10:00 | 2020-07-14 10:00 | OFFSHORE | [6 empty] | SEA ROBIN PIPELINE | 10941 | [20 empty] | 236 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH TIMBALIER | 229 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 10 | NO | 0.5 | 42000 | API 5L | SEAMLESS |  | US STEEL | EPOXY |  | YES | [26 empty] | 1996 | 1995 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 239 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 344 | 357.930157624314088 | 2559 | 4491.306122448979591836734693877551020408 | 228870 | 238138.00923103710849 | 4000 | 4161.978577026908 | 0 | 0 |  | 1.72 | 235773 | 109998.3331315730760262915451895043731778 | 247149.2240881373101698367346938775510204 | 0 | 0 | 0 | 0 | NO |  |  |  | 939 | 0.5 | 1200 | 192.619(A)(1) |  | 2011-08-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 59664 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | PINHOLE LEAK |  |  |  |  | YES | LOW FLOW | YES | [7 empty] | YES | PINHOLE AT THE 7:00 O'CLOCK POSITION | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TODD NARDOZZI |  | todd.nardozzi@energytransfer.com | [5 empty] | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | TUESDAY, JULY 14, 2020 A LEAK WAS CALLED INTO OUR HOUMA OFFICE BY THE PRODUCER PLATFORM IN ST 229 A SHORT TIME AGO. OVERFLIGHT FOUND A 1 MILE BY 15 MILE SHEEN, RANGING FROM DARK BROWN AT THE SOURCE TO RAINBOW AND SILVER ON OUTER EDGES. WE HAVE CALLED THE NRC WITH CASE NUMBER 1281840 ASSIGNED AND ARE WORKING TO ISOLATE OUR LINE FROM THE REST OF THE SYSTEM, PRODUCTION IS GOING OFFLINE AT ST 229 AS WELL. WEDNESDAY, JULY 15, 2020 OVERFLIGHT THIS MORNING SHOWS THE BUBBLES TO BE REDUCED IN SIZE, WITH A SHEEN APPROXIMATELY 100 FEET BY 15 MILES THAT IS SILVER TO RAINBOW IN COLOR AND DISSIPATING. WE ANTICIPATE A DSV TO BE IN THE FIELD EITHER SATURDAY OR SUNDAY, WATER DEPTH HERE REQUIRES A SAT VESSEL AND THERE IS LIMITED AVAILABILITY. LINE PRESSURE IS DOWN TO 370 PSIG AND FALLING, WE PLAN TO TAKE IT TO BOTTOM PRESSURE AS IS OUR NORMAL. WE HAVE UPDATED THE USCG WITH TODAY'S FINDINGS AND OUR PATH FORWARD. AT THIS TIME WE STILL HAVE NOT CONFIRMED RESPONSIBILITY BUT INDICATIONS ARE THAT IT IS LIKELY OURS. FRIDAY, JULY 17, 2020 WEATHER HAS PREVENTED OVER FLIGHTS THE LAST TWO DAYS BUT THE PRODUCER PLATFORM IS REPORTING NO BUBBLES THIS MORNING WITH A GOLD TO RAINBOW COLORED SHEEN, 150 YDS. BY 2 MILES. WE WILL RESUME OVERFLIGHTS AS SOON AS WEATHER CONDITIONS ALLOW. THE LINE IS CURRENTLY AT APPROXIMATE BOTTOM PRESSURE AND WILL REMAIN SO. THE DIVE VESSEL HAS AN ETA TO THE SITE OF SUNDAY MORNING, THE REPAIR CLAMP WILL BE ONBOARD. WE HAVE BEEN IN DAILY CONTACT WITH THE USCG PROVIDING UPDATES. THE NRC AND USCG WILL BE UPDATED AGAIN TODAY WITH THE INFORMATION AND THAT ALL INDICATIONS ARE THE LEAK IS OUR LINE. MONDAY, JULY 20, 2020 THE LEAK HAS BEEN CONFIRMED AS BEING ON OUR 10 IN. LINE, AT THE 7 O'CLOCK POSITION. THERE HAS BEEN NO SHEEN PRESENT IN THE AREA SINCE THE MORNING OF 7/18. THE PROTECTIVE COATING HAS BEEN REMOVED FROM THE LINE AND THE UT INSPECTION PERFORMED. THE REPAIR CLAMP WAS SUCCESSFULLY INSTALLED ONTO THE LINE AND COVERED, WITH THE LINE REMAINING OUT OF SERVICE. WE ARE RELEASING THE VESSEL PENDING INSTRUCTIONS FOLLOWING FURTHER DISCUSSIONS BETWEEN COMMERCIAL AND THE PRODUCER AT ST 229. BOTH THE NRC AND USCG HAVE BEEN KEPT UPDATED ON OUR STATUS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200082 | 34513 | 2020-08-13 10:17 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2020-07-15 16:00 | 2020 | MOUNTAIN | YES | 42.6492 | -113.0188 | 1282107 | 2020-07-16 15:13 | 1282238 | NATURAL GAS |  | 821 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-06-10 16:05 | 2020-08-12 16:52 |  | YES | OPERATOR | 2020-06-10 18:50 | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-10 16:05 | VALVE CLOSURE |  | 2020-07-10 16:05 | 0 | 2020-07-15 16:00 | 2020-06-10 18:50 | ONSHORE | ID | 83211 | Not Within a Municipality | POWER | MILEPOST | 627.4 | WILLIAMS NORTHWEST PIPELINE | MAINLINE 1400 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | ASPHALT |  | UNKNOWN | [26 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 443 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1264 | 2218.448979591836734693877551020408163265 | 200000 | 208098.9288513454 | 0 | 0 | 0 | 0 |  | 1.54 | 201264 | 93260.9041886992344023323615160349854227 | 210317.3778309372367346938775510204081633 | 0 | 0 | 0 | 0 | NO |  |  |  | 1.5 | 0 | 850 | 192.619(A)(3) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91783 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | CORROSION FEATURE IDENTIFIED THROUGH IN-LINE INSPECTION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS WERE OF A MINOR NATURE IN TERMS OF GAS LOSS, AND SCADA IS NOT WELL SUITED FOR IDENTIFYING THESE TYPES OF LEAKS. LEAKS WERE DISCOVERED DURING FOLLOW UP ACTIVITIES ASSOCIATED WITH IN-LINE INSPECTION OF THE LINE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2020 |  |  |  |  | 2020 | [5 empty] | YES |  | NO | [63 empty] | BRET BURKHART | ENGINEER III - PIPELINE SAFETY | bret.burkhart@williams.com | 801-584-6892 |  | DAVE DICKERSON | david.s.dickerson@williams.com | 208-884-4300 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | THIS INCIDENT IS RELATED TO CORROSION FEATURES ASSOCIATED WITH PRIOR INCIDENT NO. 20200073-34025. IT IS SUBMITTED SEPARATELY DUE TO THE TIME ELAPSED BETWEEN DISCOVERY OF THE INITIAL THROUGH WALL ANOMALIES AND THIS ADDITIONAL THROUGH WALL ANOMALY. AT THE TIME OF DISCOVERY, THE LINE WAS ISOLATED AND BLOWN DOWN DUE TO MAINTENANCE WORK ON THE OTHER FEATURES IDENTIFIED THROUGH IN-LINE INSPECTION. IN APRIL OF 2020 WILLIAMS CONTRACTED WITH AN IN-LINE INSPECTION VENDOR TO COMPLETE TOOL RUNS ON THE WILLIAMS NORTHWEST PIPELINE 1400 POCATELLO TO BURLEY SEGMENT. HIGH-RES MFL TOOL RUNS WERE CONDUCTED, AND A PRELIMINARY REPORT WAS PROVIDED TO WILLIAMS WITH CERTAIN HIGH-PRIORITY ANOMALIES ON THE WEEK OF 5/25/2020. A PROJECT WAS INITIATED TO ADDRESS PRELIMINARY HIGH-PRIORITY ANOMALIES. IN PREPARATION TO EXCAVATE, WILLIAMS OPERATIONS CONDUCTED A LEAK SURVEY OF THE EXCAVATION AREA AND IDENTIFIED GAS READINGS AT THREE ANOMALIES WITHIN AN APPROXIMATE 350FT. SPAN ON 6/10/2020 NEAR M.P. 626.8. IN RESPONSE, THE LINE SEGMENT BETWEEN VALVES 9-1 AND 9-2 WAS SHUT-IN AND BLOWN DOWN ON THE SAME DATE. EXCAVATIONS OF THE ANOMALIES CONFIRMED PIN-HOLE LEAKS RESULTING FROM CORROSION. AFTER ASSESSING REPAIR OPTIONS WILLIAMS PROJECT MANAGEMENT DETERMINED THAT REPAIRS WOULD BE BEST ACCOMPLISHED THROUGH PIPE REPLACEMENT OF THE AFFECTED AREAS. THE PRELIMINARY COST OF REPAIRS EXCEEDS $50,000, WITH COST OF CONTRACTOR AND INTERNAL LABOR APPROACHING $200,000 PER FEATURE. IT WAS DETERMINED THAT THIS QUALIFIED AS A DOT REPORT-ABLE INCIDENT BASED ON COST. THE NRC WAS INITIALLY NOTIFIED OF THE INCIDENT ON 6/16/2020. AT THE TIME OF THIS REPORT THE LINE IS SHUT-IN AND BLOWN-DOWN. AS OF THE DATE OF THIS REPORT, CUT-OUTS/REPLACEMENTS ARE COMPLETE AND THE PIPELINE WAS RETURNED TO SERVICE ON 8/12/2020. A SUPPLEMENTAL REPORT WAS FILED ON 8/19/2020 PER THE REQUEST OF BRIAN PIERZINA (PHMSA) - WHO REQUESTED THAT ITEM A4 BE UPDATED TO THE TIME THAT THE FEATURE WAS FIRST DISCOVERED, RATHER THAN THE TIME WHEN IT WAS DETERMINED THROUGH EVALUATION AND COST ESTIMATES THAT THIS QUALIFIED AS A DOT REPORTABLE INCIDENT. THE THROUGH WALL FEATURE WAS UNCOVERED 7/15/20 AT 16:00 MT. WE DETERMINED THE NEXT DAY THAT REPLACEMENT COSTS WOULD EXCEED $50K AND THAT THIS COULD NOT BE INCLUDED WITH A REVISION OF A FORMER INCIDENT REPORT RELATED TO THE SAME PIGGING PROJECT FOR THE LINE IN QUESTION. THE COST DETERMINATION WAS MADE 7/16/2020 AT 12:48 MT, AND A NOTIFICATION TO THE NRC WAS MADE ON THE SAME DATE AT 15:13 MT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200083 | 34383 | 2020-08-13 10:28 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-07-14 15:35 | 2020 | CENTRAL | NO | 35.7774 | -89.9931 | 1282100 | 2020-07-16 15:31 | 1282893 | NATURAL GAS |  | 3841 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | TWO WAY FED SYSTEM |  |  |  | YES | OPERATOR | 2020-07-14 15:35 | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-14 16:00 | OPERATIONAL CONTROL | INSTALLED SLIT TEE STOOPLE FITTING |  | 0 | 2020-07-14 15:39 | 2020-07-14 15:39 | ONSHORE | AR | 72370 | VICTORIA | MISSISSIPPI | NOT APPLICABLE |  | ARKANSAS LSG | P-600 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.18 |  | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COLD APPLIED TAPE |  | NO | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 10 | 4 | [7 empty] | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 13059 | 22919.8775510204081632653061224489795918 | 3889 | 4046.483671514411303 | 16951 | 17637.424714795779377 | 4688 | 4877.838892275536176 | NON STOCK/OUT OF SERVICE COST/MISC. | 3.4 | 38587 | 26756.8156905289522033119533527696793003 | 49481.6248296061350192653061224489795918 | 0 | 0 | 0 | 0 | NO |  |  |  | 250 | 5000 | 400 | 192.619(A)(4) |  | 1954-01-01 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL |  | 36873 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO | [9 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | PRESTON WALKER | SENIOR COMPLIANCE COORDINATOR | preston.walker@blackhillscorp.com | 4794350170 |  | GARY SWAIN | gary.swain@blackhillscorp.com | 8707639260 | PRESTON WALKER | SENIOR COMPLIANCE COORDINATOR | 4794350170 | preston.walker@blackhillscorp.com | ON JULY 14,2020 @ 15:35 PM BLACK HILLS ENERGY WAS NOTIFIED THAT A 6 INCH TRANSMISSION LINE HAD SUSTAINED SOME DAMAGE IN A FIELD LOCATED ON HIGHWAY 158 NORTH NEAR VICTORIA, AR BY MANN LAND LEVELING COMPANY WHILE IN THE PROCESS OF PUTTING A FIELD TO GRADE FOR VICTORIA PARTNERSHIP. BHEA OPERATIONS TECH WAS DISPATCHED TO THE SCENE ARRIVING ON SITE @ 15:39 PM TO DISCOVER THE SEVERED 6 INCH TRANSMISSION MAIN. BHEA MAINTENANCE CREW WAS DISPATCHED TO THE SITE AND STARTED THE GAS CONTROL PROCESS BY UTILIZING AN ONE EXISTING VALVE TO THE SOUTH AND INSTALLING A SPLIT TEE ON THE NORTHSIDE OF THE DAMAGED SEGMENT TO GAIN CONTROL OF THE ESCAPING GAS. BHEA MAINTENANCE CREW REPLACED THE DAMAGE SEGMENT AND RETURN THE TRANSMISSION LINE BACK TO NORMAL OPERATION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200084 | 34315 | 2020-08-18 15:52 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-07-23 15:50 | 2020 | CENTRAL | YES | 42.4716 | -94.0414 | 1282671 | 2020-07-23 16:40 | 1282806 | NATURAL GAS |  | 4800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-23 19:10 | 2020-07-25 12:00 |  | YES | OPERATOR | 2020-07-23 16:00 | NO | [5 empty] | VALVE CLOSURE |  | 2020-07-23 19:10 | VALVE CLOSURE |  | 2020-07-23 19:10 | 2 | 2020-07-23 15:50 | 2020-07-23 16:18 | ONSHORE | IA | 50532 | Not Within a Municipality | WEBSTER | MILEPOST | 27.37 | OGDEN TO VENTURA | M520A | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | YES | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2.375 | NO | 0.179 | 30000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1931 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 47 |  | NO | NO | [5 empty] | 126 | 131.102325176347602 | 0 | 0 | 14256 | 25020.734693877551020408163265306122449 | 4000 | 4161.978577026908 | 10000 | 10404.94644256727 | 0 | 0 |  | 2.97 | 28382 | 22901.4662156175062261282798833819241983 | 39718.762038648076622408163265306122449 | 1 | 0 | 0 | 0 | NO |  |  |  | 238 | 10 | 380 | 192.619(A)(4) |  | 2017-01-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 46464 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | YES | 2 | 0 | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES |  | NO | YES | YES |  |  |  | 2020 |  |  |  | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [51 empty] | YES | [11 empty] | JOHN A GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | THOMAS CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | NORTHERN IS IN THE PROCESS OF ABANDONING THE M520A MAINLINE BETWEEN OGDEN, IOWA AND VENTURA, IOWA. IN PREPARATION FOR ABANDONMENT, TOWNS SERVED OFF OF THE A-LINE ARE BEING MOVED TO A PARALLEL MAINLINE. ON JULY 23, 2020, MANHATTAN PIPELINE, THE CONTRACTOR WORKING FOR NORTHERN, WAS CAREFULLY EXCAVATING THE TAKE-OFF VALVE ASSEMBLY THAT SERVES THE TOWN OF DUCOMBE, IOWA. UNKNOWN TO THE CONTRACTOR, THERE WAS AN ABANDONED 2-INCH TAKE-OFF VALVE JUST 4 FEET DOWNSTREAM (NORTH) OF THE IN-SERVICE TAKE-OFF VALVE. THE CONTRACTOR DID NOT HIT OR STRIKE THE UNKNOWN, ABANDONED VALVE. ABOUT 3:30 PM, DURING THE EXCAVATION PROCESS, THE COMBINATION OF FORCES FROM THE HAND-DIGGING EFFORTS AND RELEASE OF OVERBURDEN CAUSED THE ABANDONED, 2-INCH-DIAMETER, 1931 VINTAGE, BRANCH CONNECTION AND VALVE ASSEMBLY TO FAIL, RESULTING IN BLOWING GAS. THE FAILURE APPEARS TO BE IN THE THREADED CONNECTION BETWEEN THE NIPPLE WELDED TO THE A-LINE AND THE VALVE. THE ABANDONED VALVE AND NIPPLE WERE SENT TO A LABORATORY FOR FURTHER ANALYSIS. THE M520A LINE WAS OPERATING AT APPROXIMATELY 238 PSIG AT THE TIME OF THE EVENT, AND ULTIMATELY VENTED 4.8 MMSCF OF NATURAL GAS. THE COMPANY HAS INSTITUTED AN EXPANDED PROGRAM OF RECORDS RESEARCH IN AN ATTEMPT TO LOCATE THESE ABANDONED FACILITIES TO PREVENT REOCCURRENCE. ONE CONTRACT EMPLOYEE WAS INJURED WHILE ESCAPING THE EXCAVATION. HE SUSTAINED A BRUISE TO HIS RIGHT WRIST AND ELBOW. HE WAS EXAMINED AND RELEASED FROM THE LOCAL HOSPITAL IN FORT DODGE, IOWA. UPDATE 9/29/20: METALLURGICAL ANALYSIS INDICATED THE ROOT CAUSE WAS THE RESULT OF DEFECTIVE WELDING ,EXTERNAL FORCES BENDING AND FLATTENING THE DAMAGED NIPPLE, AND POSSIBLY DEFECTS IN THE VALVE BODY. PHOTO OBSERVATIONS IN THE REPORT ALSO NOTE SIGNIFICANT CORROSION OF THE THREADED SECTION OF THE VALVE. WHILE IT APPEARS THERE WAS SOME EXTERNAL FORCE TO HAVE CAUSED THE BENDING AND FLATTENING, THE CORROSION OF THE THREADED PIPE NIPPLE IN THE "AS RECEIVED" CONDITION WOULD INDICATE THAT THE EXTERNAL FORCE OCCURRED SOMETIME IN THE PAST AND ONCE THE THREAD WAS DEFORMED AND EXPOSED TO THE ENVIRONMENT, CORROSION INITIATED. WITH THE POOR QUALITY OF THE FORGED VALVE FITTING THE CORROSION OF THE THREADS COULD HAVE BEEN RAPID.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200085 | 34367 | 2020-08-19 16:26 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-07-25 02:27 | 2020 | EASTERN | YES | 37.5555 | -81.4041 | 1282801 | 2020-07-25 14:49 | 1282856 | NATURAL GAS |  | 300 | 50 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-25 15:00 | 2020-09-11 16:00 |  | NO |  |  | YES | 2020-07-25 02:27 | OPERATOR/CONTRACTOR |  | 300 | NO | VALVE CLOSURE |  | 2020-07-25 14:45 | VALVE CLOSURE |  | 2020-07-25 15:00 | 0 | 2020-07-25 02:27 | 2020-07-25 12:47 | ONSHORE | WV | 26267 | Not Within a Municipality | WYOMING COUNTY | MILEPOST | MPID 205117 | LINE KA4 | MPID 205117 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.15 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1933 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 52 |  | NO | NO | [5 empty] | 0 | 0 | 82 | 85.320560829051614 | 489 | 858.244897959183673469387755102040816327 | 300000 | 312148.3932770181 | 0 | 0 | 0 | 0 |  | 1.63 | 300571 | 138308.6903243201541496618075801749271137 | 313091.9587358063352874693877551020408163 | 0 | 0 | 0 | 0 | NO |  |  |  | 70 | 250 | 93 | 192.619(A)(4) |  | 1933-10-08 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 1586 | NO |  | YES | YES | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | INITIAL NOTIFICATION CAME FROM LOCAL PRODUCER INVESTIGATING FIRES IN THE AREA |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER DID NOT INTRODUCE ANY SIGNALS TO OPEN/CLOSE A VALVE, NO OTHER OPERATIONAL INTERACTION WITH GAS CONTROL PERSONNEL EVEN BEFORE THE INCIDENT TOOK PLACE OR SOMETHING SIMILAR. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MARK NEWMAN | COMPLIANCE SPECIALIST | mark_newman@tcenergy.com | 3045490532 | 3047228420 |  |  |  | PAUL SHAFFER | COMPLIANCE MANAGER | 3045504866 | paul-shaffer@tcenergy.com | ON JULY 25, 2020 AT 02:27 EASTERN DAYLIGHT TIME (EDT), COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA), MONITORING CENTER RECEIVED A CALL FROM A LOCAL PRODUCER (DIVERSIFIED) OF A PIPELINE FIRE. AT 04:16 EDT COLUMBIA IDENTIFIED A FIRE WAS ON PIPELINE KA-4 LOCATED IN WYOMING COUNTY, WV NEAR THE UNINCORPORATED COMMUNITY OF TRALEE, WV SOUTH OF ELMORE, WV. . WITH THE ASSISTANCE OF THE LOCAL FIRE DEPARTMENT COLUMBIA WAS ABLE TO ACCESS THE SITE AND USE FIRE EXTINGUISHERS TO EXTINGUISH THE FIRES. THE FIRES WERE SMALL IN SIZE AND REMAINED CONTAINED WITHIN THE PIPELINE RIGHT OF WAY. HOW THE FIRES WERE IGNITED IS UNDER INVESTIGATION. FIRES WERE FUELED BY A (NUISANCE) GAS LEAK ON PIPELINE KA-4. AT APPROXIMATELY 15:00 EDT PIPELINE KA-4 WAS ISOLATED AND SHUTDOWN. INFORMATION ON THE SOURCE OF IGNITION WILL BE PROVIDED WITH A SUPPLEMENT REPORT. THIS SECTION OF PIPELINE KA-4 IS UNCOATED COUPLED PIPELINE WITH NO CATHODIC PROTECTION. THE LEAK ON THE PIPELINE WAS CAUSED BY EXTERNAL CORROSION. PERMANENT REPAIRS WERE MADE TO TWO SECTIONS. SECTION ONE (1) - 40 FEET OF 6 INCH OD IPS, SDR 11, HDPE PIPE WITH COUPLINGS AND 20 FEET OF 6.625 OD, 0.280 WALL, X52 STEEL PIPE WAS COMPLETED ON 09/02/2020. SECTION TWO (2) HAD 5 FEET OF 6 INCH OD IPS, SDR 11, HDPE PIPE WITH COUPLINGS AND 20 FEET OF 6.625 OD, 0.280 WALL, X52 STEEL PIPE WAS COMPLETED ON 9/11/2020. BOTH REPLACEMENT SECTIONS WAS PRESSURE TESTED TO 150 PSIG FOR 1 HOUR. LINE KA-4 WAS RETURNED TO SERVICE ON 9/11/2020.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200087 | 35482 | 2020-08-26 17:37 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-07-29 19:21 | 2020 | EASTERN | YES | 39.443 | -78.9561 | 1283140 | 2020-07-29 19:10 | 1283363 | NATURAL GAS |  | 174 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THIS LINE IS A SINGLE FEED TO THE KEYSER INDUSTRIAL PARK, KEYSER WV |  |  |  | YES | OPERATOR | 2020-07-29 19:10 | NO | [5 empty] | OPERATIONAL CONTROL | LEAK MONITORED. PLANS TO INSTALL PRESSURE REGULATION TO REDUCE PRESSURE. DIVERS TO EVALUATE LEAK. |  | OPERATIONAL CONTROL | INSTALL PRESSURE REGULATION TO LOWER DOWNSTREAM PRESSURE. |  | 0 | 2020-07-28 14:00 | 2020-07-28 14:45 | ONSHORE | MD | 21562 | MCCOOLE | ALLEGANY | SURVEY STATION NO. | 104+53 | LINE 18039 | 2001654 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDER THE NORTH BRANCH POTOMAC RIVER | 12 | NO | YES | [6 empty] | YES | UNCASED | NORTH BRANCH OF THE POTOMAC RIVER | UNKNOWN | BELOW WATER, PIPE ON OR ABOVE BOTTOM | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.219 | 35000 | GRADE B | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 1966 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 140 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 284 | 498.448979591836734693877551020408163265 | 121742 | 126671.898981102458434 | 0 | 0 | 0 | 0 |  | 1.63 | 122026 | 56209.8457793736649089037900874635568513 | 127170.3479606942951686938775510204081633 | 0 | 0 | 0 | 0 | NO |  |  |  | 250 | 8 | 273 | 192.619(A)(2) |  | 1966-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 11786 | NO |  | YES | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | DAMAGE FROM ROCKS AND DEBRIS IN THE RIVER COMING IN CONTACT WITH THE PIPELINE | [251 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 304-357-3596 |  | WILLIAM YOUSE | william_youse@tcenergy.com | 304-357-3596 | PAUL SHAFFER | US REGULATORY COMPLIANCE EAST MANAGER | 304-357-2245 | paul_shaffer@tcenergy.com | PIPELINE 18039 IS A TRANSMISSION PIPELINE THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616). COLUMBIA HAS EXPERIENCED A LEAK ON THIS PIPELINE IN THE NORTH BRANCH OF THE POTOMAC RIVER NEAR THE TOWN OF MCCOOLE, ALLEGANY COUNTY, MD. PIPELINE 18039 IS A 6-INCH CARBON STEEL, 0.219-INCH WALL THICKNESS, ERW, GRADE B PIPE COATED IN THE AREA OF THE REPORTED LEAK. LINE 18039 MAXIMUM ALLOWABLE OPERATING PRESSURE IS 273 PSIG AND ITS OPERATING PRESSURE AT THE TIME OF DISCOVERY WAS APPROXIMATELY 250 PSIG. LOCAL OPERATIONS WERE NOTIFIED OF A LEAK IN THE POTOMAC RIVER, THE LEAK WAS EVALUATED AND DETERMINED NOT TO BE A HAZARD TO LIFE OR PROPERTY. THE PIPELINE IS A SINGLE FEED TO THE KEYSER INDUSTRIAL PARK LOCATED ACROSS THE POTOMAC RIVER IN KEYSER, WEST VIRGINIA, THEREFORE; FROM AN OPERATIONAL-PERSPECTIVE, IT IS NOT FEASIBLE TO DISCONTINUE THE FLOW OR SHUT DOWN THE PIPELINE. IN ORDER TO REDUCE THE GAS LOSS, PRESSURE REGULATING EQUIPMENT WAS INSTALLED TO REDUCE PRESSURE TO APPROXIMATELY 60 PSIG. A QUALIFIED DIVE COMPANY WAS CONTRACTED TO EVALUATE THE PIPELINE CONDITION AND NATURE OF THE LEAK. INTEGRITY ENGINEERS EVALUATED THIS INFORMATION AND DEVELOPED A REPAIR PLAN WHICH WAS PROVIDED TO THE MARYLAND DEPARTMENT OF THE ENVIRONMENT FOR APPROVAL. UPON APPROVAL, OUR CONTRACTOR INSTALLED TWO LEAK CLAMPS, WRAPPED THE PIPELINE WITH AN APPROVED COATING AND INSTALLED A PROTECTIVE OUTER WRAP. THE PIPELINE WAS THEN PRESSURED UP TO THE PRESSURE AT THE TIME OF THE INCIDENT, 285 PSIG, HELD FOR ONE HOUR, INSPECTED FOR LEAKS AND RETURNED TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200088 | 34814 | 2020-08-26 22:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-07-12 00:17 | 2020 | EASTERN | YES | 42.8113 | -82.8666 | 1284994 | 2020-08-19 17:45 | 1285084 | NATURAL GAS |  | 29 | 24 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-07-12 01:19 | 2020-12-09 08:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-07-12 00:17 | 2020-07-12 00:47 | ONSHORE | MI | 48005 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION UNIT 3-1 (THROW 3) | PISTON ROD - CROSS HEAD NUT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2011 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO | [5 empty] | 0 | 0 | 55 | 57.227205434119985 | 66 | 115.836734693877551020408163265306122449 | 136557 | 142086.827135765868939 | 500 | 520.2473221283635 | 0 | 0 |  | 2.29 | 137178 | 63014.0317823101864954635568513119533528 | 142780.1383980222299750204081632653061224 | 0 | 0 | 0 | 0 | NO |  |  |  | 1206.4 | 100 | 1800 | 192.619(A)(2) |  | 2010-02-26 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPROPRIATE ACTIONS/NOTIFICATIONS WERE COMPLETED WHEN SCADA ALARMS WERE RECEIVED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | PISTON ROD - LOSS OF TENSION OF THE CROSS HEAD NUT CAUSING IT TO BACK OUT | [5 empty] | YES | [5 empty] | YES | [171 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JULY 12, 2020 AT APPROXIMATELY 00:17 HOURS CONSUMERS ENERGY GAS CONTROLLED RECEIVED SCADA ALARMS INDICATING MULTIPLE ENGINES WERE OFFLINE AT THE RAY COMPRESSOR STATION PLANT 3. THE FACILITY IS LOCATED AT 69333 OMO ROAD, ARMADA, MICHIGAN (MACOMB COUNTY). STATION PERSONNEL WERE NOTIFIED AND ARRIVE ONSITE AT APPROXIMATELY 00:47 HOURS AND CONFIRMED HIGH GAS LEL IN THE PLANT 3 COMPRESSOR BUILDING. STATION PERSONNEL THEN PROCEEDED TO DEPRESSURIZE UNIT 3-1 BY OPENING VALVES VGV-701 AND VGV-702. THE GAS LEVEL WITHIN THE COMPRESSOR BUILDING GRADUALLY DECREASED TO ZERO. IT WAS THEN CONFIRMED THAT UNIT 3-1 WAS THE CAUSE OF THE GAS LEAK. FOLLOWING THE INCIDENT, THE STATION PERSONNEL HAVE WORKED THROUGH DISCOVERY ON THE UNIT BY DISASSEMBLING THROW #3 ON UNIT 3-1, AS WELL AS INSPECTING THE INTEGRITY OF THE OTHER THROWS. AT THIS TIME THE DAMAGE IS ISOLATED TO THROW #3; HOWEVER, THE ROOT CAUSE HAS NOT BEEN IDENTIFIED. COMPONENTS OF THROW #3 HAVE BEEN SENT TO CONSUMERS ENERGY'S LABORATORY FOR FURTHER ANALYSIS TO ASSIST WITH THE IDENTIFICATION OF THE ROOT CAUSE OF FAILURE. THE INCIDENT INVESTIGATION AND LABORATORY ANALYSIS DETERMINED A SERIES OF FAILURES OCCURRED RESULTING IN THE RELEASE OF GAS WITH PROPERTY DAMAGE IN EXCESS OF $50,000. A MECHANICAL FAILURE ON UNIT 3-1 THROW 3 CAUSED BY LOSS OF TENSION OF THE CROSS HEAD BALANCE NUT WHICH ALLOWED THE PISTON AND ROD ASSEMBLY TO BACK OUT AND MAKE CONTACT WITH THE FIXED VOLUME CLEARANCE POCKET RESULTING IN FAILURE OF THE PISTON ROD. MAINTENANCE RECORDS FOR THE TORQUEING OF THE CROSS-HEAD BALANCE NUT WERE NOT AVAILABLE. THE EXCESSIVE VIBRATION THAT OCCURRED AS A RESULT OF THE MECHANICAL FAILURE CAUSED THE BOLTS ON THE SUCTION VALVE UNLOADER TO LOOSEN AND GAS TO BE RELEASED. THE SAFETY SYSTEM DESIGNED TO ISOLATE AND EVACUATED GAS THROUGH THE VENT VALVE DID NOT TRAVEL AUTOMATICALLY DURING THE EVENT AND INSTEAD REQUIRED MANUAL ACTIVATION. PROBLEM SOLVING WAS COMPLETED FOR THE MECHANICAL AND SAFETY SYSTEM FAILURES AND ACTION ITEMS DEVELOPED TO MINIMIZE FUTURE RE-OCCURRENCE. RESTORATION OF THE EQUIPMENT IS UNDERWAY, A FINAL REPORT WILL BE SUBMITTED WHEN THE NORMAL OPERATIONS IS RESUMED. FOLLOWING THE INCIDENT INVESTIGATION A COMPRESSOR RESTORATION PLAN WAS DEVELOPED FOR THROW #3. THE PLAN INVOLVED REPLACING THE PISTON ROD, PISTON, THE CROSSHEAD, BALANCE NUT, INNER-CYLINDER HEAD AND THE FIXED VOLUME CLEARANCE POCKET. THE SUCTION VALVE UNLOADERS WERE DISASSEMBLED, INSPECTED AND REBUILT. ACTIONS WERE ALSO TAKEN TO CORRECT THE VALVE POSITIONING ALLOWING THE SAFETY MECHANISM TO AUTOMATICALLY TRAVEL WHEN SPECIFIED PERCENTAGE OF GAS IS DETECTED IN THE BUILDING. FOLLOWING REMEDIATION NORMAL OPERATIONS WERE RESUMED ON DECEMBER 9, 2020.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200089 | 34224 | 2020-09-03 10:36 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-08-12 14:38 | 2020 | CENTRAL | YES | 32.989 | -89.5509 | 1284397 | 2020-08-12 15:40 | 1284539 | NATURAL GAS |  | 35.96 | 22375 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-12 14:38 | 2020-08-22 11:58 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-08-12 15:00 | VALVE CLOSURE |  | 2020-08-12 14:45 | 0 | 2020-08-12 14:38 | 2020-08-12 14:38 | ONSHORE | MS | 39090 | KOSCIUSKO | ATTALA | MILEPOST | 376.495 | LINE 31 | CLIN-KOSC | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | WKM |  |  |  | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 759 |  | NO | NO | [5 empty] | 0 | 0 | 48106 | 50054.035356614109062 | 77 | 135.142857142857142857142857142857142857 | 75000 | 78037.098319254525 | 0 | 0 | 0 | 0 |  | 2.15 | 123183 | 56597.5758468152292560408163265306122449 | 128226.2765330114912048571428571428571429 | 0 | 0 | 0 | 0 | NO |  |  |  | 743 | 350000 | 936 | 192.619(A)(1) |  | 2015-05-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 60192 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE | [19 empty] | YES | PRESSURE OF VALVE PIPE NIPPLE AGAINST CONCRETE BLOCK | [161 empty] | MAYRA SALINAS | SENIOR ENGINEER | mayra.salinas@enbridge.com | 832-748-0908 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 281-686-3829 | nathan.atanu@enbridge.com | AT APPROXIMATELY 2:38 PM CDT ON AUGUST 12, 2020 A TEXAS EASTERN TRANSMISSION'S (TETLP) EMPLOYEE WAS PERFORMING A LEAK SURVEY AND DISCOVERED A NATURAL GAS RELEASE FROM TETLP'S LINE 31 AT THE KOSCIUSKO COMPRESSOR STATION IN ATTALA COUNTY, LA. THE LEAK WAS LOCATED ON THE 1/2" THREADED NIPPLE ON MAINLINE VALVE 31-46. THE PIPELINE WAS ISOLATED AND BLOWN DOWN ON AUGUST 12, 2020 AND REMAINED ISOLATED UNTIL THE REPAIR WAS COMPLETED. THE CAUSE OF THE LEAK WAS A NIPPLE OFF THE BODY OF THE VALVE THAT WAS IN CONTACT WITH A CONCRETE SUPPORT WHICH APPLIED PRESSURE TO CAUSE THREADS TO BREAK ON THE NIPPLE. THE PIPELINE WAS RETURNED TO SERVICE ON AUGUST 22, 2020.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200090 | 34245 | 2020-09-03 12:07 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-08-13 10:00 | 2020 | CENTRAL | YES | 32.1176 | -90.3012 | 1285170 | 2020-08-21 11:23 | 1285174 | NATURAL GAS |  | 66 | 48 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-13 07:00 | 2020-08-15 16:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-08-06 16:30 | OPERATIONAL CONTROL | REDUCED PRESSURE CONTROL SET POINT FOR INDEX 302 BY 20% FROM 390 PSIG TO 310 PSIG |  | 0 | 2020-08-06 13:15 | 2020-08-06 13:45 | ONSHORE | MS | 39170 | Not Within a Municipality | HINDS | SURVEY STATION NO. | 744+07 | INDEX 302 | MCCOMB 6-INCH PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.28 | 24000 | API 5L | LAP WELDED |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 104 |  | NO | NO | [5 empty] | 0 | 0 | 89 | 92.604023338848703 | 122 | 214.122448979591836734693877551020408163 | 285000 | 296540.973613167195 | 0 | 0 | 0 | 0 |  | 1.85 | 285211 | 131003.8692225723335354023323615160349854 | 296847.7000854856355397346938775510204082 | 0 | 0 | 0 | 0 | NO |  |  |  | 390 | 6000 | 447 | 192.619(A)(1) |  | 2018-04-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 15048 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM A CENTERPOINT ENERGY EMPLOYEE |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | YES | [6 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  | YES | PHOTOS REVIEWED BY CORROSION DEPARTMENT FOR CONFIRMATION | YES | YES | 1960 | NO | YES |  | YES |  |  |  | 2014 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON AUGUST 6, 2020, A CENTERPOINT ENERGY EMPLOYEE REPORTED A POSSIBLE NATURAL GAS LEAK ON GULF SOUTH PIPELINE'S MCCOMB 6-INCH (INDEX 302) LINE IN TERRY, MS. GULF SOUTH OPERATIONS EMPLOYEES WERE DISPATCHED TO INVESTIGATE AND DETERMINED A MINOR LEAK OF UNKNOWN CAUSE. THE PRESSURE ON THE PIPELINE WAS REDUCED BY 20% UNTIL REPAIRS COULD BE MADE. PREPARATIONS WERE MADE TO INSTALL A WELD OVER BUT, UPON EXCAVATION, IT WAS DETERMINED THAT THIS WOULD NOT BE A FEASIBLE APPROACH. AT THIS POINT, THIS BECAME A REPORTABLE INCIDENT. THE LINE WAS TAKEN OUT OF SERVICE ON AUGUST 13, 2020 AT 07:00 FOR REPAIRS. INITIALLY, THE CAUSE WAS SUSPECTED TO BE A LEAKING DRESSER COUPLING BUT THE CAUSE WAS DETERMINED TO BE EXTERNAL CORROSION. APPROXIMATELY 250 FEET OF PIPE WAS REPLACED AND THE LINE RETURNED TO SERVICE ON AUGUST 15, 2020 AT 16:00. ON PART G, QUESTION 4A OF THIS REPORT, THE RESPONSE TO THE YEAR THAT CATHODIC PROTECTION ON THIS PIPELINE STARTED IS SPECULATION BASED ON EMPLOYEE HISTORICAL KNOWLEDGE; THE EXACT YEAR IS UNKNOWN. 9-8-2020 SUPPLEMENTAL REPORT SUBMITTED TO CORRECT RESPONSES TO QUESTIONS B4 AND C6 AS DIRECTED BY PHMSA AND CORRECT RESPONSE TO QUESTION A20C.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200091 | 34235 | 2020-09-03 18:47 | ORIGINAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-08-10 17:10 | 2020 | CENTRAL | YES | 41.2077 | -93.9893 | 1284223 | 2020-08-10 17:15 | 1284327 | NATURAL GAS |  | 338 | 34306 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-10 17:25 | 2020-08-13 15:58 |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | GAS CONTROL MONITORED PRESSURE AND OPERATIONS REMAINED ON SITE. |  | OPERATIONAL CONTROL | GAS CONTROL MONITORED PRESSURE AND OPERATIONS REMAINED ON SITE. |  | 0 | 2020-08-10 13:08 | 2020-08-10 13:08 | ONSHORE | IA | 50273 | Not Within a Municipality | MADISON | MILEPOST | MP582+0270 | NGPL/X893E2 | AMARILLO LINE NO.2 GRAND RIVER TO CLANTON CREEK | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | PLUG |  | UNKNOWN |  |  |  | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 368 |  | NO | NO | [5 empty] | 0 | 0 | 85765 | 89238.023164678191155 | 845 | 1483.061224489795918367346938775510204082 | 60283 | 62724.138639728273741 | 1000 | 1040.494644256727 | 0 | 0 |  | 2.5 | 147893 | 68472.0170872444146063440233236151603499 | 154485.7176731529878143673469387755102041 | 0 | 0 | 0 | 0 | NO |  |  |  | 665 | 0 | 712 | 192.619(C) |  | 1957-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 60092 | NO | [5 empty] | YES | PIPING THAT CONTAINS THE VALVE IS CONSIDERED X-OVER PIPING AND CANNOT BE DIRECTLY PIGGED. | YES |  |  |  |  | YES | THE X-OVER PIPING CANNOT BE PIGGED. | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS COULD NOT HAVE RESULTED IN THE VALVE PACKING LEAK. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | GAS SEAL PROVIDED BY GREASED VALVE-PACKING MATERIAL NO LONGER EFFECTIVE. | [152 empty] | YES | [8 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-3199 | (719) 329-5673 | MIKE BUCHANAN | mike_bohannan@kindermorgan.com | 319-461-7890 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | (281) 384-5609 | jaime_hernandez@kindermorgan.com | ON AUGUST 10, 2020 AT APPROXIMATELY 12:45 PM LOCAL TIME, NGPL GAS CONTROL CONTACTED LOCAL OPERATIONS OF A REPORT RECEIVED FROM A THIRD PARTY OF GAS VENTING NEAR VALVE V893 IN MADISON COUNTY, IOWA. AT 13:08 PM LOCAL TIME, NGPL OPERATIONS ARRIVED ON LOCATION AND FOUND THAT THE VALVE OPERATOR ON A CROSSOVER, ISOLATION VALVE WAS VENTING FROM A SMALL (1/8' DIAMETER) VENT ON THE VALVE ACTUATOR. AT THAT TIME, THE ESTIMATED QUANTITY GAS RELEASED WAS DETERMINED TO BE 39 MCF FROM THE INITIAL NOTIFICATION RECEIVED FROM THE PUBLIC BY GAS CONTROL AT 12:41 PM LOCAL TIME TO THE TIME OPERATION'S PERSONNEL ARRIVED ON SITE. AT THIS TIME, OPERATIONS BEGAN SERVICING THE VALVE TO STOP THE LEAK FROM THE ACTUATOR VENT. AT 17:00 PM LOCAL TIME, NGPL OPERATIONS REPORTED THAT ATTEMPTS TO STOP THE LEAK WITH APPLICATION OF VALVE GREASE WAS NOT COMPLETELY SUCCESSFUL AS THE LEAKING STOPPED BRIEFLY BUT CONTINUED INTERMITTENTLY. AT 17:10 PM LOCAL TIME, OPERATIONS DECIDES TO REMOVE THE VALVE FROM SERVICE AND ESTIMATES THE COST WOULD BE GREATER THAN $50,000. AT 17:15 PM LOCAL TIME, THE NATIONAL RESPONSE CENTER WAS NOTIFIED (NRC REPORT NO. 1284223). THE 48-HOUR UPDATE COMMUNICATING NO SIGNIFICANT CHANGES WAS COMPLETED AT 16:25 PM LOCAL TIME ON 08/11/2020 (NRC REPORT NO. 1284327). INVESTIGATION: RESULTS OF THE INVESTIGATION SHOWED THAT THE VALVE X893E2, 20' PLUG VALVE INSTALLED IN 1957, PROVIDES CROSSOVER ISOLATION BETWEEN THE #2 AND #3 AMARILLO MAINLINES. APPLICATION OF GREASE DOWN THE CENTER GREASE FITTING FORCES THE STEM PACKING AROUND THE VALVE STEM, SEALING IT, AND PREVENTING GAS FROM TRAVELING UP THE VALVE STEM AND EXITING THE ACTUATOR VENT. AS DISCUSSED ABOVE, OPERATIONS ATTEMPTED TO STOP THE LEAK FROM THE ACTUATOR VENT BY SERVICING THE VALVE WITH GREASE; HOWEVER, THIS ACTION DID NOT COMPLETELY STOP THE LEAK. AT THAT TIME (APPROXIMATELY 17:10 PM LOCAL TIME), NGPL OPERATIONS DECIDED TO REMOVE THE VALVE AND ASSOCIATED CROSSOVER PIPING FROM SERVICE TO AVOID HAVING TO TAKE BOTH THE NGPL AMARILLO MAINLINES NO. 2 AND NO. 3 OUT OF SERVICE, ADVERSELY AFFECTING NATURAL GAS DELIVERIES TO CUSTOMERS DOWNSTREAM FROM THE LOCATION. THE INVESTIGATION DETERMINED THAT ONLY A SMALL AMOUNT OF HARD AND INEFFECTIVE STEM PACKING REMAINED IN THE PLUG ASSEMBLY. THE IMMEDIATE/DIRECT CAUSE OF THE EVENT WAS DETERMINED TO BE THE STEM PACKING IN THE SERVICE LINE WAS DEPLETED AND NO LONGER SERVICEABLE. THE BASIC/ROOT CAUSES INCLUDED THE AGE AND SERVICEABILITY OF THE STEM PACKING. CORRECTIVE ACTIONS: REVIEW VALVE SERVICING AND MAINTENANCE PROCEDURES WITH ALL NGPL OPERATORS INVOLVED IN VALVE SERVICING/MAINTENANCE FOR THESE TYPES OF VALVES TO LIMIT VALVE-PACKING LEAKAGE GOING FORWARD. NGPL REMOVED THE VALVE FROM SERVICE AS DESCRIBED ABOVE.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20200092 | 35343 | 2020-09-04 13:21 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2020-08-06 16:15 | 2020 | EASTERN | YES | 37.9954 | -86.0671 | 1283906 | 2020-08-06 16:15 |  | NATURAL GAS |  | 12324 | 0 | 428 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STORAGE FLD FACILITY WAS NOT SHUT DOWN SEE NARR. SEC. H RE STEPS TAKEN ON WELL. |  |  |  | YES | OPERATOR | 2020-08-06 15:45 | NO | [11 empty] | 0 | 2020-08-06 14:30 | 2020-08-06 15:15 | ONSHORE | IN | 47135 | LACONIA, IN | HARRISON COUNTY, IN | NOT APPLICABLE |  | DOE RUN STORAGE FIELD | A. H. PERKINS 5 GAS STORAGE WELL | NO | PIPELINE RIGHT-OF-WAY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | OTHER | [37 empty] | WELL CASING PIPE AT THREADED COLLAR | 1984 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | WELL CASING PIPE FAILURE AT CASING COLLAR. | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 30136 | 52891.7551020408163265306122448979591837 | 42222 | 43931.764869807527394 | 626641 | 652016.604371679664007 | 0 | 0 |  | 2.4453 | 698999 | 341730.4892081562107124810495626822157434 | 748840.1243435280077275306122448979591837 | 0 | 0 | 0 | 0 | NO |  |  |  | 179 | 264 | 305 | OTHER | WELL CASING THAT FAILED DOES NOT FALL UNDER 192.619 OR 192.620 | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 4 | 0 | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  |  | YES |  |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | RICHARD STOCKE | MANAGER GAS STORAGE INTEGRITY AND COMPLIANCE | richard.stocke@lge-ku.com | 502-333-1770 |  | RICHARD STOCKE | richard.stocke@lge-ku.com | 502-333-1770 | J. GREGORY CORNETT | DIRECTOR LEGAL SERVICES-ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | ON AUGUST 6, 2020 A GAS STORAGE WELL CASING FAILURE OCCURRED AT THE A.H. PERKINS 5 (PERKINS #5) GAS STORAGE WELL IN HARRISON COUNTY NEAR LACONIA, INDIANA, RESULTING IN A UNCONTROLLED NATURAL GAS RELEASE. AT THE TIME OF THE FAILURE, A COMPANY CONTRACTOR CREW WAS INSTALLING AN UNDERGROUND PIPELINE DRIP. THE WELL CASING FAILURE OCCURRED AT THE BOTTOM OF AN ABOVE GROUND CASING COLLAR. THE FAILURE DID NOT CAUSE ANY INJURIES OR SIGNIFICANT THIRD-PARTY PROPERTY DAMAGE. NO IGNITION OF GAS OR LIQUIDS OCCURRED DURING THIS EVENT. LG&E IMPLEMENTED ITS EMERGENCY PROCEDURES AND THE WELL WAS SUCCESSFULLY ISOLATED AND CAPPED ON AUGUST 11, 2020. DNV GL, A GLOBAL QUALITY ASSURANCE AND RISK MANAGEMENT COMPANY, WAS RETAINED TO INVESTIGATE THE WELL CASING FAILURE BY CONDUCTING A METALLURGICAL ANALYSIS AND FINITE ELEMENT ANALYSIS TO DETERMINE THE LIKELY METALLURGICAL CAUSE(S) AND IDENTIFY ANY CONTRIBUTING FACTORS. A CROSS-FUNCTIONAL INTERNAL TEAM WAS FORMED TO PERFORM AN INCIDENT INVESTIGATION. THE TEAM REVIEWED GAS STORAGE WELL DOCUMENTATION, DOCUMENTATION ASSOCIATED WITH PIPELINE DRIP REPLACEMENT, DNVGL METALLURGICAL ANALYSIS REPORT AND THE POST INCIDENT EMERGENCY RESPONSE DOCUMENTATION. THE TEAM ALSO CONDUCTED WITNESS INTERVIEWS AND PERFORMED A ROOT CAUSE ANALYSIS. THE INCIDENT INVESTIGATION TOOK PLACE DURING THE COVID 19 PANDEMIC WHICH LIMITED SOCIAL INTERACTIONS AND REQUIRED STRICT PROTOCOLS FOR ANY IN PERSON MEETINGS, INTERVIEWS, AND COLLABORATIONS. THE INVESTIGATION ULTIMATELY CONCLUDED THE PRIMARY FACTOR CONTRIBUTING TO THE FAILURE OF PERKINS #5 WAS INADEQUATE OPERATIONAL CONTROLS. SPECIFICALLY, CONSTRUCTION ACTIVITIES WERE UNDERTAKEN WHILE FIELD PIPING WAS CONNECTED TO THE GAS STORAGE WELLHEAD RESULTING IN DUCTILE OVERLOAD STRESSES ON WELL CASING FROM EXTERNAL FORCES LIKELY ASSOCIATED WITH THE INSTALLATION OF THE PIPELINE DRIP. THE METALLURGICAL ANALYSIS REPORT BY DNV GL STATED "THE RESULTS OF THE METALLURGICAL ANALYSIS INDICTED THAT THE FAILURE OCCURRED AS A RESULT OF DUCTILE OVERLOAD FROM A SIGNIFICANT EXTERNAL BENDING OR LONGITUDINAL FORCE, LIKELY ASSOCIATED WITH EXCAVATION, AND INSTALLATION OF THE DRIP PIPING". THE INCIDENT INVESTIGATION FOUND THESE PRIMARY FACTORS CONTRIBUTING TO THE INCIDENT INCLUDED: A. CONNECTION OF FIELD PIPELINE TO THE WELLHEAD WHILE UNDER CONSTRUCTION RESULTED IN DUCTILE OVERLOAD AND FAILURE OF THE WELL CASING PIPE. B. PIPELINE DESIGN DRAWINGS WERE NOT ACCOMPANIED BY CONSTRUCTION PROCEDURES THAT PROHIBITED CONNECTION OF FIELD PIPELINE TO THE WELLHEAD WHILE UNDER CONSTRUCTION. C. FIELD PIPELINE DRIP WAS NOT PREFABRICATED IN CONFORMANCE WITH DESIGN DRAWING. D. DESIGN DRAWINGS DID NOT INCLUDE DETAILED NOTES OR REFERENCES. D3 - COMPONENT THAT FAILED IS GAS STORAGE WELL CASING, SO PIR DOESN'T APPLY. USED DEFAULT VALUE OF "1". PIR IS NOT APPLICABLE TO STORAGE WELL. E2 - 3 BECAUSE THE FIELD REQUIRED A NUMERICAL VALUE WE USED THE PIPELINE SYSTEM MAOP. HOWEVER, THE WELL CASING THAT FAILED DOES NOT FALL UNDER 192.619 OR 192.620. E9 - THERE IS NOT A CHOICE FOR RESERVOIR GAS STORAGE WELL. WE CHOSE THE CLOSEST AVAILABLE OPTION. E11 - THE STORAGE FIELD INJECTION RATE AND INJECTION PRESSURE ARE MONITORED BY GAS CONTROL BUT THE INDIVIDUAL WELLS ARE NOT MONITORED. G7.5 - OQ RELATED CONSTRUCTION ACTIVITIES ASSOCIATED WITH THE INSTALLATION OF THE FIELD PIPELINE COMPONENTS RESULTED IN STRESSES IMPOSED ON STORAGE WELL CASING RESULTING IN FAILURE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200093 | 35432 | 2020-09-11 17:11 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-08-12 00:13 | 2020 | CENTRAL | YES | 30.4663 | -92.5226 | 1284343 | 2020-08-12 02:47 | 1284470 | NATURAL GAS |  | 50200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-12 01:36 | 2020-08-12 08:20 |  | YES | OPERATOR | 2020-08-12 02:11 | NO | [11 empty] | 0 | 2020-08-12 00:13 | 2020-08-12 01:25 | ONSHORE | LA | 70535 | EUNICE | ACADIA | NOT APPLICABLE |  | EUNICE COMPRESSOR STATION | ANR 501 MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1973 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VALVE FAILED TO CLOSE COMPLETELY | CLASS 1 LOCATION | NO |  | 731 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 109938 | 192952.4081632653061224489795918367346939 | 55000 | 57227.205434119985 | 0 | 0 | 0 | 0 |  | 2.19 | 164938 | 151851.4366985395197813411078717201166181 | 250179.6135973852911224489795918367346939 | 0 | 0 | 0 | 0 | NO |  |  |  | 643 | 2000 | 903 | 192.619(A)(2) |  | 2015-11-08 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RESPONDED APPROPRIATELY ACCORDING TO PROCEDURES AND DISPATCHED A TECHNICIAN TO THE SITE WHEN THE ALARM WAS DETECTED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [19 empty] | YES | [167 empty] | ROGER R STREET | COMPLIANCE SPECIALIST | roger_street@tcenergy.com | 615-465-5123 |  | ROGER R STREET | roger_street@tcenergy.com | 615-465-5123 | ERIK HUGHES | SENIOR COMPLIANCE MANAGER USGO AND KEYSTONE | 402-492-7447 | erik_hughes@tcenergy.com | ON 12 AUGUST 2020, TC ENERGY/ ANR PIPELINE COMPANY (ANR) REPORTED AN INCIDENT TO THE NATIONAL RESPONSE CENTER (NRC) (NRC REPORT NUMBER 1284343) FOLLOWING THE UNINTENTIONAL RELEASE OF 50.2 MILLION CUBIC FEET OF GAS TO THE ATMOSPHERE FROM THE EUNICE COMPRESSOR STATION LOCATED AT 4202 FOURNERAT ROAD IN EUNICE LOUISIANA (30.46632200, -92.52257600). THE RELEASE WAS CAUSED WHEN THE STATION FIRE DETECTION SYSTEM RECEIVED AN INDICATION OF A FLAME AND INITIATED THE EMERGENCY SHUTDOWN (ESD) SYSTEM. WHEN THE ESD WAS INITIATED, THE GAS CONTROLLER RECEIVED A SCADA ALARM AND DISPATCHED A TECHNICIAN TO THE SITE TO INVESTIGATE. WHEN THE TECHNICIAN ARRIVED AT THE SITE, NATURAL GAS WAS DISCOVERED BEING RELEASED THROUGH THE STATION BLOWDOWN. IMMEDIATE ACTION WAS TAKEN TO STOP THE RELEASE BY CLOSING BLOWDOWN VALVE AND SECURING THE SITE. SINCE THE INCIDENT, EUNICE COMPRESSOR STATION HAS REMAINED STAFFED 24-HOURS A DAY UNTIL REPAIRS CAN BE COMPLETED ON THE ISOLATION VALVE. INVESTIGATION OF THE INCIDENT HAS INDICATED THAT THE ACTIVATION OF THE ESD SYSTEM AND FAILURE OF THE ISOLATION VALVE TO COMPLETELY OPERATE CONTRIBUTED TO THE GAS LOSS. NO EVIDENCE OF FLAME OR FIRE WERE OBSERVED IN THE COMPRESSOR BUILDING FOLLOWING THE INCIDENT THAT WOULD INITIATE THE ESD. ADDITIONALLY, AN AUTOMATIC ISOLATION VALVE FAILED TO COMPLETELY CLOSE RESULTING IN THE CONTINUING RELEASE OF GAS TO THE ATMOSPHERE THROUGH THE STATION'S BLOWDOWN STACK. INVESTIGATION HAS ALSO DETERMINED THAT THREE-WAY PILOT GAS VALVES AND END-OF-TRAVEL STOP VALVES ASSOCIATED WITH AUTOMATIC OPERATION CONTRIBUTED TO THE INCOMPLETE CLOSURE OF THE ISOLATION VALVE DUE TO AN INSUFFICIENT GAS SUPPLY. FIVE VALVES WERE IDENTIFIED DURING THE INVESTIGATION THAT REQUIRED REPAIR AND THE REPLACEMENT OF PILOT VALVES. ON 1 MARCH 2021, REPAIR AND REPLACEMENT WAS COMPLETED ON THREE ESD VALVES IDENTIFIED DURING THE INVESTIGATION. ON APRIL 21, 2021, THE TWO REMAINING VALVES WERE REPAIRED. FOLLOWING THE VALVE REPAIR, A SUCCESSFUL EMERGENCY SHUTDOWN SYSTEM TEST WAS COMPLETED. FOLLOWING THE ESD TEST, THE STATION WAS RETURNED TO UNMANNED OPERATION CAPABILITY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200094 | 34268 | 2020-09-14 09:50 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-08-20 09:25 | 2020 | CENTRAL | YES | 29.9807 | -91.8208 | 1285056 | 2020-08-20 10:13 | 1285144 | NATURAL GAS |  | 142.9 | 102 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK; ARRANGEMENTS TO KEEP CUSTOMERS IN SERVICE DURING REPAIR |  |  |  | YES | OPERATOR | 2020-08-20 09:03 | NO | [5 empty] | OPERATIONAL CONTROL | LOWERED OPERATING PRESSURE BY 20% AT JEANERETTE CHECK STATION. |  | OPERATIONAL CONTROL | LINE IS CUT AND CAPPED ON NORTH END. INSERTED A PLUG IN A STOPPLE FITTING ON AUG.31 |  | 0 | 2020-08-20 09:03 | 2020-08-20 08:40 | ONSHORE | LA | 70560 | Not Within a Municipality | IBERIA | SURVEY STATION NO. | 7170+98 | CALL JUNCTION TO FRANKLIN | INDEX 205 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | DRESSER COUPLING | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING DRESSER COUPLING | [5 empty] | CLASS 2 LOCATION | NO |  | 137 |  | NO | NO | [5 empty] | 0 | 0 | 189 | 196.653487764521403 | 264 | 463.346938775510204081632653061224489796 | 108000 | 112373.421579726516 | 0 | 0 | 0 | 0 |  | 1.85 | 108453 | 49965.6290886591143508542274052478134111 | 113033.4220062665476070816326530612244898 | 0 | 0 | 0 | 0 | NO |  |  |  | 262 | 600 | 480 | 192.619(C) |  | 2018-03-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 21397 | NO | [5 empty] | YES | DRESSER COUPLES | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | EXPANSION & CONTRACTION OF PIPE OVER THE YEARS CAUSING COUPLING TO BECOME LOOSE | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 8/20/2020 AT 07:40, GULF SOUTH GAS CONTROL RECEIVED CALL FROM LANDOWNER REGARDING SUSPECTED SMELL OF GAS. GAS CONTROL CONTACTED LOCAL OPERATIONS PERSONNEL. AT 08:40 OPERATIONS PERSONNEL CONFIRMED GAS SMELL AND PROBABLE LEAK ON AND NEAR GULF SOUTH ASSETS. GULF SOUTH LOWERED THE PRESSURE ON THE PIPELINE BY 20% OF OPERATING PRESSURE (FROM 262 PSIG TO 209 PSIG) PRIOR TO EXCAVATION DUE TO PIPELINE HAVING KNOWN DRESSER COUPLES AS CONNECTORS. AT 08:45, A CONTRACTOR WAS CONTACTED TO EXCAVATE POTENTIAL LEAK SITE. AT 09:03 LA HAZMAT WAS CONTACTED TO REPORT POTENTIAL LEAK. AT 09:30 IT WAS CONFIRMED THAT THE LEAK WAS ON GULF SOUTH'S PIPELINE AND CAUSED BY LEAKING DRESSER COUPLE. LOCAL OPERATIONS PERSONNEL CONTACTED GAS CONTROL AT 09:45 TO INFORM THAT REPAIRS WOULD EXCEED $50,000 DUE TO TYPE OF REPAIR NEEDED. AT 10:13, GAS CONTROL CONTACTED NRC TO REPORT LEAK EXCEEDING $50,000 COST TO REPAIR. ON 8/31/20 THE LEAK WAS STOPPED BY ISOLATING SECTION OF PIPELINE WITH STOPPLE FITTING AND BLOWING DOWN GAS. A TYPE 220 WELD OVER SLEEVE WAS INSTALLED AND THE LINE WAS RETURNED TO SERVICE. TEMPORARY GAS SUPPLY WAS UTILIZED TO PREVENT LOSS OF SERVICE TO CUSTOMERS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200095 | 34870 | 2020-09-16 10:39 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2020-08-18 08:32 | 2020 | CENTRAL | YES | 31.7322 | -101.8011 | 1284828 | 2020-08-18 09:41 | 1285016 | NATURAL GAS |  | 20747 | 107 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-18 09:36 | 2020-08-23 19:05 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-08-18 08:50 | YES | 2020-08-18 08:32 | ALLOWED TO BURN OUT |  | 20747 | YES | VALVE CLOSURE |  | 2020-08-18 08:44 | VALVE CLOSURE |  | 2020-08-18 09:36 | 0 | 2020-08-18 09:36 | 2020-08-18 08:47 | ONSHORE | TX | 79755 | MIDKIFF | MIDLAND | MILEPOST | MP 6-0865 | EPNG L3125 | LAUNCHER TO SPRAYBERRY PLANT | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 57 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.335 | 52000 | API 5L | FLASH WELDED |  | AO SMITH | COAL TAR |  | YES | [26 empty] | 1953 | 1953 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | PIPE WAS RUPTURED LONGITUDINALLY AT THE 12 O'CLOCK POSITION AND 10' OF PIPE WAS EJECTED FROM THE DITCH. |  |  |  | CLASS 1 LOCATION | NO |  | 593 |  | NO | NO | [5 empty] | 591348 | 615294.426891926997996 | 173 | 180.005573456413771 | 33589 | 58952.1224489795918367346938775510204082 | 159136 | 165580.155708438507872 | 2000 | 2080.989288513454 | 59481 | 61889.661935034378687 | INVESTIGATION COSTS - 3RD PARTY METALLURGICAL ANALYSIS, SITE SURVEY, TRAVEL, ETC | 1.619 | 845727 | 411473.9816620790649906880466472303206997 | 903977.3618463493441627346938775510204082 | 0 | 0 | 0 | 0 | NO |  |  |  | 570 | 18800 | 820 | 192.619(A)(1) |  | 1953-07-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | MANUAL | 62832 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON AUGUST 18, 2020 EL PASO NATURAL GAS COMPANY, L.L.C. (EPNG) 30-INCH L3125 EXPERIENCED AN IN-SERVICE FAILURE AT A 3RD PARTY LINE CROSSING WITH A TARGA PIPELINE. AUGUST 18, 2020 - ALL TIMES ARE CDT: 7:37 AM TARGA EDWARDS RECEIPT METER (041787) FLOW WENT TO ZERO ON EPNG'S SCADA AND EMERGENCY 911 CALL RECEIVED BY MIDLAND DISPATCH ["TANK BATTERY FIRE" NOTED AT 07:38] 8:03 AM EPNG GAS CONTROL (GC) RECEIVED A CALL FROM AMERICAN PIPELINE PATROL PILOT STATING THERE WAS A FIRE POSSIBLY OVER TARGA'S OR EPNG'S PIPE. 8:07 AM EPNG GC MADE A PHONE CALL TO EPNG DAMAGE PREVENTION SUPERVISOR TO INFORM OF POSSIBLE FIRE. EPNG DAMAGE PREVENTION INITIATES PROCESS TO DISPATCH SOMEONE TO INVESTIGATE. 8:29 AM MIDLAND FIRE DEPARTMENT BATTALION CHIEF (BAT2) ARRIVED ON-SITE. 8:32 AM EPNG GC OBSERVED THAT PRESSURE AT TARGA OWENS RECEIPT RANCH AND TARGA MIDKIFF RECEIPT METER DROPPED TO AT OR NEAR 0 PSI. ROC ALARMS RECEIVED. 8:36 AM SECONDARY EXPLOSION WITNESSED BY MIDLAND FIRE DEPARTMENT (BAT2) 8:39 AM EPNG GC SET TARGA OWENS RECEIPT RANCH CONTROL VALVE TO ZERO TO ENSURE THAT FLOW WOULD NOT OCCUR. THE METER FLOW WAS ALREADY AT ZERO. 8:44 AM EPNG GC ADJUSTED JAMESON POOL CHECK METER (301166) PRESSURE CONTROL VALVE SETPOINT SET TO ZERO TO ENSURE THAT THE VALVE WAS CLOSED TO ISOLATE L3130 FROM L3125. 8:47 AM EPNG LINE PATROLLER ARRIVED AT MUSTER SITE WITH MIDLAND FIRE DEPARTMENT & TARGA ON SITE AND CONTROLLING THE SITE ACCESS 8:56 AM EPNG GC CONFIRMED TARGA MIDKIFF RECEIPT METER FLOW SHUT OFF 9:00 AM EPNG GC SPOKE TO NAVITAS AND ASKED TO TAKE NAVITAS PHILLIPS SPRAYBERRY RECEIPT METER METER FLOW TO ZERO. 9:36 AM MLV 3 ON L3125 SHUT (LOTO OCCURRED SHORTLY AFTER), ISOLATING THE SEGMENT. BASED ON FIELD OBSERVATION OF FIRE DIMINISHING UPON MLV 3 BEING SHUT, EPNG CONFIRMED DISCOVERY OF THE INCIDENT 9:41 AM EPNG PLACED THE CALL TO THE NRC, MAKING OFFICIAL NOTIFICATION OF THE EVENT. 10:05 AM MLV 0.5 (L3130) SHUT-IN & LOTO BY OPERATIONS. (VALVE IS A SECONDARY VALVE TO THE PRESSURE CONTROL VALVE AT JAMESON POOL CHECK) 10:20 AM MLV 4 (L3125) SHUT-IN & LOTO BY OPERATIONS. AT APPROXIMATELY 11:45 AM - 12:00 PM MIDLAND FIRE DEPARTMENT LEFT THE SITE, HOWEVER EPNG DID NOT GAIN ACCESS TO THE SITE DUE TO 24" TARGA PIPELINE IN THE VICINITY. TARGA WANTED TO BLOW DOWN PIPELINE BEFORE ALLOWING EPNG INTO SITE. AT APPROXIMATELY 4:10 PM TARGA COMPLETED DEPRESSURIZATION OF 24" PIPELINE AND EPNG OPERATIONS WAS ABLE TO ACCESS RUPTURE SITE & OWENS RANCH TAP FOR LOTO. TARGA PERSONNEL, ONCOR PERSONNEL, AND A REPRESENTATIVE OF THE TEXAS RAILROAD COMMISSION PIPELINE SAFETY DEPARTMENT ALSO ENTERED THE SITE. AFTER COMPLETION OF REPAIRS THE PIPE WAS PLACED BACK INTO SERVICE ON AUGUST 23, 2020. AS A PART OF THE EVENT THERE WERE DAMAGES TO A NEARBY ELECTRIC POWER TRANSMISSION FACILITY. THE CAUSE OF THE FIRE WAS A CROSSING TARGA PIPELINE THAT HAD RUPTURED UNDERNEATH THE EPNG 30-INCH L3125 PIPELINE. THE RUPTURE ON THE EPNG 30-INCH L3125 PIPELINE OCCURRED ON THE PIPE BODY WHERE THE PIPE WALL HAD THINNED TO THE LOWEST MEASURED VALUE OF 0.111" FROM AN OTHERWISE NOMINAL WALL THICKNESS OF 0.335". THE LOCALLY THINNED AREA OF THE EPNG PIPE WAS DUE TO HEAT EXPOSURE AND INTERNAL PRESSURE. THERE WAS NO EVIDENCE OF OTHER DAMAGE MECHANISMS OR MATERIAL FAILURES INCLUDING, BUT NOT LIMITED TO, WALL LOSS DUE TO INTERNAL OR EXTERNAL CORROSION, ENVIRONMENTALLY-ASSISTED CRACKING, LONGITUDINAL OR GIRTH WELD ISSUES, DENTS/GOUGES, OR MANUFACTURING DEFECTS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200096 | 34685 | 2020-09-17 10:40 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-08-29 08:45 | 2020 | CENTRAL | YES | 29.8141 | -93.0926 | 1285937 | 2020-08-29 12:46 | 1286038 | NATURAL GAS |  | 7062 | 6000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-29 13:30 | 2020-11-16 10:00 |  | YES | OPERATOR | 2020-08-29 08:30 | NO | [5 empty] | VALVE CLOSURE |  | 2020-08-29 13:24 | OPERATIONAL CONTROL | NO DOWNSTREAM ACTION REQUIRED. THIS IS THE END OF THE PIPELINE. |  | 0 | 2020-08-29 08:45 | 2020-08-29 13:24 | ONSHORE | LA | 70632 | Not Within a Municipality | CAMERON | SURVEY STATION NO. | 89+23 | CREOLE 6" LINE | INDEX 192 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 44 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1960 | 1960 | CARBON STEEL |  | LEAK |  |  | OTHER | BROKEN BODY BLEED SET VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 149 |  | NO | NO | [5 empty] | 0 | 0 | 11100 | 11549.4905512496697 | 13065 | 22930.4081632653061224489795918367346939 | 20000 | 20809.89288513454 | 21500 | 22370.6348515196305 | 0 | 0 |  | 1.85 | 65665 | 39190.4876558553038956268221574344023324 | 77660.4264511691463224489795918367346939 | 0 | 0 | 0 | 0 | NO |  |  |  | 650 | 1 | 965 | 192.619(C) |  | 2018-03-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 34268 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | HURRICANE LAURA | YES | YES | [305 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270.903.5764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270.314.6547 | tina.baker@bwpipelines.com | ON 8/27/2020 AT 19:58, GULF SOUTH RECEIVED REPORT OF A POSSIBLE LEAK DUE TO AIR PATROL OBSERVING BUBBLES IN THE FLOODED STORM SURGE IN CREOLE, LA. GULF SOUTH ACQUIRED A HELICOPTER TO FLY PERSONNEL TO THE SITE AS SOON AS POSSIBLE; ATTEMPTS TO ACCESS THE LOCATION WERE MADE ON 8/28/2020 AT 07:00 AND 13:00 BUT WERE UNSUCCESSFUL DUE TO STORM SURGE FLOODING AND AREA BEING UNDER WATER. ON 8/29/2020, LOCAL OPERATIONS MANAGEMENT NOTIFIED LA HAZMAT AT 08:38. THE LEAK WAS VERIFIED AND WAS LIKELY ON GULF SOUTH'S PIPELINE ALTHOUGH THE SITE STILL COULD NOT BE REACHED. THE 20" MAIN LINE (INDEX 195) WAS SHUT IN AND THE SECTION WAS ISOLATED. THE ONLY CUSTOMER SERVED BY THIS PIPELINE, CENTERPOINT, WAS NOTIFIED. ON 8/31/2020 THE LEAK WAS CHECKED AGAIN AND PERSONNEL WERE ABLE TO ACCESS THE 6" TAP VALVE AND CLOSE IT AT 11:00. BY 9/1/2020 AT 08:30, THE LEAK HAD SUBSIDED. TO DATE, THE AREA REMAINS INACCESSIBLE FOR EVALUATION. ONCE SITE BECOMES ACCESSIBLE FURTHER EVALUATION WILL BE DONE AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED. THE RESPONSE PROVIDED TO PART E, QUESTION 1A SHOULD ACTUALLY BE .133 MCF; HOWEVER, THE PORTAL WILL NOT ALLOW A VALUE LESS THAN 1, THEREFORE, 1 IS THE PROVIDED RESPONSE. 1/5/2021 UPDATE FOR FINAL REPORT INCLUDING CHANGE REQUESTED BY PHMSA, COST, LEAK TYPE. GULF SOUTH WAS ABLE TO ACCESS THE SITE ON 11/12/2020; EXCAVATED VALVE SITE AND DISCOVERED A BROKEN BODY BLEED ON A VALVE. THE VALVE WAS FLANGED ON THE PIPELINE SO GULF SOUTH REMOVED THE VALVE AND BOLTS AND BLIND FLANGED THE TAP FLANGE ON THE PIPELINE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200097 | 34751 | 2020-09-17 13:04 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2020-08-19 12:59 | 2020 | PACIFIC | YES | 39.1783 | -123.21 | 1285001 | 2020-08-19 15:43 | 1285110 | NATURAL GAS |  | 25 | 0.41 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | YES | OPERATOR | 2020-08-19 12:59 | YES | 2020-08-19 12:59 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 25 | NO | VALVE CLOSURE |  | 2020-08-19 17:30 | VALVE CLOSURE |  | 2020-08-19 19:41 | 75 | 2020-09-08 12:59 | 2020-08-19 12:59 | ONSHORE | CA | 95482 | UKIAH | MENDOCINO | MILEPOST | 116.24-.39 | L021E | MP 116.24-.39 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | YES | 0.188 | 42000 | API_5LX-X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | ASPHALT |  | YES | [26 empty] | 1968 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD1 | 147 |  | NO | NO | [5 empty] | 0 | 0 | 1 | 1.040494644256727 | 75 | 131.63265306122448979591836734693877551 | 100000 | 104049.4644256727 | 18000 | 18728.903596621086 | 0 | 0 |  | 3 | 118076 | 54251.9429350371652629358600583090379009 | 122911.0411699992672167959183673469387755 | 0 | 0 | 0 | 2 | NO |  |  |  | 420 | 420 | 610 | 192.619(A)(2) |  | 1968-05-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT, A PINHOLE BLOW THROUGH, OCCURRED DURING A WELDING ON A CLEARANCE, SO OPERATOR EMPLOYEES AND CONTRACTORS WERE ALREADY ON SITE. | [12 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [6 empty] | YES | A QUALIFIED PROCEDURE WAS USED AS WELL AS A QUALIFIED WELDER. PG&E HAD CONTINUAL OBSERVATION OF THE WORK VERIFYING COMPLIANCE TO THE PROCEDURE. THE LEAK LOCATION ON THE PIPE WAS DESTROYED IN THE PROCESS OF RESTORING THE SYSTEM BACK TO SERVICE, SO NO ROOT CAUSE COULD BE CONCLUSIVELY DEVELOPED. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | VINCENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER OF GAS REGULATORY COMPLIANCE | 925-786-0267 | gsr8@pge.com | ON WEDNESDAY, AUGUST 19, 2020 AT 1259 HOURS, PG&E WAS NOTIFIED OF AN UNINTENTIONAL RELEASE OF GAS WITH IGNITION AT 2147 N. STATE ST IN UKIAH, CA. DURING A CLEARANCE ON PLANNED PROJECT R-583 TO RE-ROUTE L-21E, A WELDER WAS WELDING A 2" SAV-A-VALVE ON L-21E MP 115.5 WHEN HE BREACHED THE PIPELINE, CREATING A PIN HOLE LEAK THAT SUBSEQUENTLY IGNITED. ONSITE EMPLOYEES CALLED 911. POLICE PERFORMED STREET CLOSURES AND TRAFFIC CONTROL, AND FIRE DEPARTMENT PERFORMED LOCAL EVACUATIONS (MENDOCINO SHERIFF'S OFFICE ISSUED AN EVACUATION ORDER TO THE GENERAL PUBLIC FROM 3 ZONES SURROUNDING THE INCIDENT. THE NUMBER POPULATED IN A23 IS AN ESTIMATE BASED ON THE NUMBER OF BUILDINGS IN THESE ZONES). THE LINE WAS ISOLATED AT 1730 HOURS AND WAS RETURNED TO SERVICE BY 1941 HOURS. THERE ARE NO REPORTED INJURIES OR FATALITIES. TWO LARGE VOLUME CUSTOMERS WERE IMPACTED FROM 2200 HOURS TO 900 HOURS THE NEXT MORNING. A QUALIFIED PROCEDURE WAS USED AS WELL AS A QUALIFIED WELDER. PG&E HAD CONTINUAL OBSERVATION OF THE WORK VERIFYING COMPLIANCE TO THE PROCEDURE. THE LEAK LOCATION ON THE PIPE WAS DESTROYED IN THE PROCESS OF RESTORING THE SYSTEM BACK TO SERVICE, SO NO ROOT CAUSE COULD BE CONCLUSIVELY DEVELOPED. THIS SAFETY MATTER WAS REPORTED AS A DOT INCIDENT (#1285001) DUE TO THE COMBINATION OF A RELEASE OF GAS RESULTING IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $50K REQUIRING IMMEDIATE MITIGATION TO PROTECT PEOPLE OR PROPERTY. PLEASE NOTE: AN ALCOHOL TEST OF THE CONTRACTOR INVOLVED WAS NOT GIVEN WITHIN 8 HOURS DUE TO EXIGENT CIRCUMSTANCES RELATED TO THE CALIFORNIA WILDFIRES, A DRUG TEST WAS GIVEN AND PASSED. THIS DELAY WAS THE RESULT OF THE UNPRECEDENTED CONFLUENCE OF UNCOMMON OCCURRENCES INCLUDING A CONTRACTOR-INVOLVED DOT-REPORTABLE INCIDENT AND WILDFIRE RELATED TRAFFIC AND PERSONNEL EVACUATION ACTIVITIES. AS SUCH, IT HAS BEEN EVALUATED AS UNLIKELY TO REOCCUR, EVEN WITHOUT THE IMPLEMENTATION OF ANY CORRECTIVE ACTIONS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200098 | 34881 | 2020-09-24 13:51 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2020-08-28 05:00 | 2020 | PACIFIC | YES | 38.5924 | -121.5556 | 1285835 | 2020-08-28 08:00 | 1285915 | NATURAL GAS |  | 531 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-28 11:55 | 2020-08-28 21:34 |  |  |  |  | NO | [11 empty] | 0 | 2020-08-28 05:00 | 2020-08-28 05:25 | ONSHORE | CA | 95605 | WEST SACRAMENTO | YOLO | NOT APPLICABLE |  | WS-004 | WS-004 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1975 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE IMPACT | CLASS 3 LOCATION | YES | METHOD1 | 44 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1593 | 2795.877551020408163265306122448979591837 | 46000 | 47862.753635809442 | 8000 | 8323.957154053816 | 0 | 0 |  | 3 | 55593 | 26621.9292621441285655976676384839650146 | 58982.5883408836661632653061224489795918 | 0 | 0 | 0 | 0 | NO |  |  |  | 45 | 45 | 50 | 192.619(A)(2) |  | 1975-06-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | ROADWAY | 10 | YES |  |  |  | YES | FENCING | [233 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-786-0267 | gsr8@pge.com | ON FRIDAY, AUGUST 28, 2020, AT APPROXIMATELY 05:00 HOURS, PG&E WAS NOTIFIED OF VEHICLE IMPACT TO A REGULATOR STATION, CAUSING A RELEASE OF GAS NEAR 3500 REED AVE, WEST SACRAMENTO. PG&E'S GAS SERVICE REPRESENTATIVE WAS ON SITE APPROXIMATELY AT 05:25 HOURS. PG&E CREWS ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS AT 11:55 HOURS. THE CREW CUT AND CAPPED 8 FEET OF 4" PIPE GOING INTO THE REGULATOR STATION. THE 2" TRANSMISSION WAS TURNED OFF AT VALVE V-1 AND A BLIND FLANGE WAS INSTALLED IN THE STATION. 1 CUSTOMER WAS AFFECTED BUT WAS RETURNED TO SERVICE BY 21:38 HOURS. PG&E IS CURRENTLY ASSESSING A REBUILD AND POSSIBLE RELOCATION OF THIS STATION. THERE WERE NO OF INJURIES AND NO FATALITIES. THERE WAS MEDIA (CHANNEL 31), POLICE, FIRE DEPARTMENT REPORTED. THIS SAFETY MATTER WAS REPORTED AS A DOT INCIDENT (#1285835) DUE TO THE COMBINATION OF A RELEASE OF GAS RESULTING IN ESTIMATED PROPERTY DAMAGE OF AT LEAST $50K REQUIRING IMMEDIATE MITIGATION TO PROTECT PEOPLE OR PROPERTY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200099 | 34917 | 2020-09-30 11:48 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2020-08-31 16:44 | 2020 | MOUNTAIN | YES | 41.6995 | -110.3646 | 1286190 | 2020-09-01 09:06 | 1286364 | NATURAL GAS |  | 150000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-09-01 06:50 | 2020-09-01 06:50 | ONSHORE | WY | 83101 | KEMMERER | LINCOLN | NOT APPLICABLE |  | ROBERSON CREEK COMPRESSOR STATION | RUBY MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2010 | 2010 | CARBON STEEL |  | LEAK |  |  | OTHER | RELEASE THROUGH VENT | [5 empty] | CLASS 1 LOCATION | NO |  | 1100 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 321000 | 563387.7551020408163265306122448979591837 | 100 | 104.0494644256727 | 100 | 104.0494644256727 | 0 | 0 |  | 2.14 | 321200 | 369756.5283094365126454810495626822157434 | 563595.8540308921617265306122448979591837 | 0 | 0 | 0 | 0 | NO |  |  |  | 1250 | 245 | 1440 | 192.619(A)(2) |  | 2011-07-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO INDICATIONS THAT CONTROLLER ACTION CONTRIBUTED TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | PLC MALFUNCTION SIGNALED DISCHARGE VALVE TO OPEN. FURTHER DETAILS PROVIDED IN THE NARRATIVE. | [22 empty] | YES | LISTED SUB CAUSES ARE N/A, SEE NARRATIVE FOR ADDITIONAL SUB CAUSE DISCUSSION | [161 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON AUGUST 31, 2020, THE ROBERSON CREEK COMPRESSOR STATION WAS ON LINE AND ONE OF THE THREE UNITS WAS OPERATING. DURING THE DAY, OPERATIONS WAS WORKING WITH THE ORIGINAL EQUIPMENT MANUFACTURER TO INSPECT UNIT #2 VARIABLE FREQUENCY DRIVE (VFD) FOR THE PRIMARY DRIVER/ELECTRIC MOTOR. DURING THE INSPECTION, ONLY THE POWER TO THE VFD HAD BEEN LOCKED OUT AND NOTHING WAS TOUCHED ON THE GAS PIPING. AT APPROXIMATELY 2:10 PM MT, OPERATIONS STARTED UNIT #2 AT THE ROBERSON CREEK COMPRESSOR STATION TO CHECK THE OPERATION OF THE VFD. AFTER OPERATING THE UNIT FOR APPROXIMATELY 10 MINUTES THE UNIT WAS SHUT DOWN AT APPROXIMATELY 2:20 PM MT BY LOCAL OPERATIONS. EACH TIME A UNIT SHUTS DOWN, A TWO HOUR TIMER STARTS TO BLOWDOWN THE COMPRESSOR CASE. AT APPROXIMATELY 4:00 PM MT, KM PERSONNEL LEFT FOR THE DAY. AT 4:26 PM MT, THE UNIT VENT VALVE OPENED TO VENT THE COMPRESSOR CASE. NORMALLY IN THIS SITUATION, THE UNIT DISCHARGE VALVE WOULD BE IN THE CLOSED POSITION; HOWEVER, THE DISCHARGE VALVE WAS IN THE OPEN POSITION. THIS ALLOWED GAS TO CONTINUE TO VENT FROM THE STATION DISCHARGE. ON SEPTEMBER 1, 2020, AT APPROXIMATELY 6:50 AM MT, STATION PERSONNEL ARRIVED AT THE FACILITY, HEARD THE GAS BLOWING AND CLOSED THE VENT VALVE THAT THEY FOUND IN THE OPEN POSITION. GAS LOSS WAS CALCULATED TO BE APPROXIMATELY 150 MMCF. THE INVESTIGATION REVEALED THAT THE UNIT DISCHARGE VALVE WAS COMMANDED OPEN BY THE UNIT PLC AT 2:25PM. IT COULD NOT BE DETERMINED WHY THE VALVE WAS COMMANDED OPEN OR WHERE THE COMMAND CAME FROM. THE INVESTIGATION TEAM WAS UNABLE TO REPLICATE THE CAUSE OF THE EVENT DURING THEIR INVESTIGATION AND SUSPECTS THAT THE PLC EXPERIENCED A MALFUNCTION THAT CAUSED IT TO SEND THE UNINTENDED SIGNAL TO OPEN. THE INVESTIGATION ALSO REVEALED THAT THERE WAS A FLAW IN THE PLC PROGRAMMING. THERE WAS A LOGIC PATH THAT ALLOWED THE CONFIRMATION OF THE UNIT VALVE CLOSURES TO BE BYPASSED WHEN BLOWING DOWN THE COMPRESSOR UNIT. IN ORDER TO PREVENT A REOCCURRENCE, THE PLC LOGIC WAS MODIFIED TO ENSURE THAT THE UNIT SUCTION AND DISCHARGE VALVES ARE CLOSED BEFORE THE UNIT VENT VALVE IS OPENED. ADDITIONALLY, CIG ASSESSED THE PLC LOGIC OF THE OTHER TWO COMPRESSOR UNITS AND MADE CHANGES AS APPROPRIATE. IN ADDITION, A CALLOUT ALARM WAS ADDED IN THE EVENT THAT UNIT VENT VALVE IS OPEN AT THE SAME TIME AS A UNIT SUCTION OR DISCHARGE VALVE. FINALLY, A VENT STACK FLOW SWITCH WAS INSTALLED TO HELP DETECT ANY FUTURE UNINTENDED RELEASES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200100 | 34625 | 2020-09-30 15:24 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2020-08-29 17:55 | 2020 | CENTRAL | YES | 34.9939 | -95.0541 | 1285969 | 2020-08-29 18:51 | 1286134 | NATURAL GAS |  | 22 | 36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-08-29 17:23 | 2020-09-03 08:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-08-29 17:55 | YES | 2020-08-29 17:31 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 22 | YES | [6 empty] | 0 | 2020-08-29 17:23 | 2020-08-29 17:55 | ONSHORE | OK | 74563 | Not Within a Municipality | LATIMER | NOT APPLICABLE |  | RED OAK COMPRESSOR STATION | R-913 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1992 | 1992 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1.2 | 1.2 |  | CLASS 1 LOCATION | NO |  | 250 |  | NO | NO | [5 empty] | 0 | 0 | 78 | 81.158582252024706 | 48 | 84.24489795918367346938775510204081632653 | 2500000 | 2601236.6106418175 | 1500 | 1560.7419663850905 | 0 | 0 |  | 2.16 | 2501626 | 1148345.58768812454395651895043731778426 | 2602962.75608841379887946938775510204082 | 0 | 0 | 0 | 1 | NO |  |  |  | 680 | 133 | 960 | 192.619(A)(1) |  | 1992-04-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER HANDLED THE ISSUE PROPERLY THROUGH SUDA ACTIONS AND EVERBRIDGE CALL. COMMUNICATIONS WITH THE FIELD, PIPELINE CONTROL MANAGEMENT AND OPERATIONS WERE ALL RECEIVED THROUGH PHONE AND EMAIL. LEADERSHIP REVIEWED THE AOC WITH PIPELINE CONTROL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES |  | YES | [175 empty] | JACK CROW | REGULATORY COMPLIANCE SPECIALIST | jack.crow@oneok.com | 405-323-2492 |  |  |  |  | DAVID MCMULLEN | DIRECTOR OF OPERATIONS | 405-833-4219 | david.mcmullen@oneok.com | AT APPROXIMATELY 17:30 ON 8/29/20 AN EMERGENCY CALL WAS RECEIVED BY ONEOK GAS TRANSPORTATION GAS CONTROL CENTER OF A FIRE AT THE ONEOK RED OAK COMPRESSOR STATION. THE EMERGENCY SHUTDOWN DEVICE AT THE STATION ACTIVATED, ISOLATING THE STATION AND SHUTTING IT DOWN. ONEOK'S INVESTIGATION DETERMINED A 1 1/2 NIPPLE FAILED ALLOWING GAS TO BLOW DIRECTLY INTO THE COMPRESSOR BUILDING WHICH WAS IGNITED AND CAUSED THE FIRE. THE INVESTIGATION ALSO DETERMINED THE 1 1/2 NIPPLE WAS REPLACED WITH A SCHEDULE 80 GRADE NIPPLE AND NOT THE PREFERRED SCHEDULE 160. THE NIPPLE HAD ALSO NOT BEEN PROPERLY SECURED TO THE COMPRESSOR SKID ALLOWING IT TO VIBRATE. ONEOK ALSO REDESIGNED THE PIPING CONFIGURATION OF THE RELIEF LINE TO ELIMINATE STRESS LOADS ON THE RELIEF PIPING. STATION VIBRATION STUDIES WERE CONDUCTED AT THE SITE AFTER THE INSTALLATION AND SECURING OF THE PIPING WITH THE NEW DESIGN. ONEOK CONTACTED THE NRC REGARDING THE ACCIDENT ON 8/29/20 AT 18:50 AND UPDATED THE REPORT ON 8/31/20 AT 16:54.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200101 | 37249 | 2020-09-30 19:58 | SUPPLEMENTAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-09-02 12:06 | 2020 | CENTRAL | YES | 30.4291 | -92.3557 | 1286340 | 2020-09-02 12:59 | 1286500 | NATURAL GAS |  | 5218 | 13 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-02 12:33 |  | YES |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-02 12:33 | OPERATIONAL CONTROL | END OF LINE. UPSTREAM VALVE WAS CLOSED. |  | 0 | 2020-09-02 12:35 | 2020-09-02 12:30 | ONSHORE | LA | 70535 | Not Within a Municipality | ACADIA | SURVEY STATION NO. | 0+4233 | HUNDLEY 4" LINE | HUN 4-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 4 |  | 0.237 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1951 | 1951 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 36 | 6 |  | CLASS 1 LOCATION | NO |  | 143 |  | NO | NO |  |  | NO |  |  | 1800 | 1872.8903596621086 | 34 | 35.376817904728718 | 13462 | 23627.1836734693877551020408163265306122 | 60232 | 62671.073412871180664 | 0 | 0 | 0 | 0 |  | 2.58 | 75528 | 43992.818022535010088460641399416909621 | 88206.5242639074057371020408163265306122 | 0 | 0 | 0 | 0 | NO |  |  |  | 824 | 1 | 1100 | 192.619(C) |  | 2019-08-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 4280 | NO | [5 empty] | YES | NOT EQUIPPED WITH LAUNCHER OR RECEIVER | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING |  |  | YES | [7 empty] | YES |  |  |  | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [13 empty] | YES |  |  |  |  | YES | [12 empty] | YES | [31 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 9-2-2020 AT 12:06 PM, TEXAS GAS'S GAS CONTROL RECEIVED A CALL FROM THE SHERIFF'S DEPARTMENT REPORTING A POTENTIAL PIPELINE LEAK. GAS CONTROL CONTACTED OPERATIONS PERSONNEL AT 12:13 PM. A PIPELINE TECHNICIAN WHO WAS ALREADY IN THE FIELD PERFORMING MAINTENANCE WAS DISPATCHED TO THE SITE AT 12:15 PM. LOCAL OPERATIONS PERSONNEL ARRIVED AT THE HUN 4" TAP VALVE AT APPROXIMATELY 12:30 PM. PERSONNEL SHUT THE TAP VALVE AND OPENED BLOWDOWN VALVE AT 12:33 PM. THE LINE WAS SECURED AND BLOWN DOWN AT 12:33 PM. NO ONE WAS INJURED. SOME GROUND DISTURBANCE OCCURRED. THE PIPELINE BLEW FOR 20 MINUTES AT 824 PSIG. AT THIS TIME THE FAILED PORTION OF PIPELINE IS STILL ATTACHED AND HAS NOT BEEN REMOVED. TEXAS GAS INTENDS TO ABANDON THIS PORTION OF PIPELINE AND REMOVE IT FROM SERVICE. CURRENTLY, THE AREA IS TOO WET TO COMPLETE THIS SCOPE AND, THEREFORE, TEXAS GAS HAS NOT YET HAD THE OPPORTUNITY TO COMPLETELY ASSESS THE CAUSE OF THIS INCIDENT ALTHOUGH IT APPEARS TO BE CORROSION RELATED. EVALUATION IS ONGOING AND A SUPPLEMENTAL/FINAL INCIDENT REPORT WILL BE REQUIRED. THE RESPONSE PROVIDED TO PART E, QUESTION 1A IS 1.0 BUT THE ACTUAL FLOW WAS TOO LOW TO CALCULATE. 3/15/2021 UPDATE REPORT FOLLOWING METALLURGICAL ANALYSIS. THE RUPTURE RESULTED FROM THE INITIATION OF MULTIPLE CRACKS AT THE EXTERNAL SURFACE OF THE PIPE. THE OBSERVED CRACKING WAS CONSISTENT WITH THE OCCURRENCE OF EXTERNAL HIGH PH STRESS CORROSION CRACKING. THE PIPE EXHIBITED MULTIPLE GOUGES AND DENTS IN ITS EXTERNAL SURFACE AND WAS PARTIALLY FLATTENED OVER A LENGTH OF APPROXIMATELY SIX FEET FROM THE GIRTH WELD OF THE ADJACENT JOINT. THE RUPTURE WAS CONTAINED WITHIN THIS FLATTENED LENGTH OF PIPE AND RESIDUAL STRESS IN THE PIPE WALL FROM THIS FLATTENING MAY HAVE CONTRIBUTED TO THE INITIATION AND GROWTH OF STRESS CORROSION CRACKS. THE INTERNAL SURFACE OF THE PIPE EXHIBITED LARGE SHALLOW CORROSION PITS. THE EXTERNAL SURFACE CONDITION SUGGESTS THAT THE OBSERVED GOUGES AND DENTS OCCURRED A SIGNIFICANT PERIOD OF TIME PRIOR TO THE RUPTURE. 10-20-22 UPDATED TO CORRECT LATITUDE AND LONGITUDE PER PHMSA REQUEST. A SUPPLEMENTAL REPORT WILL BE REQUIRED WHEN ABANDONMENT IS COMPLETE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200102 | 34910 | 2020-10-02 10:49 | SUPPLEMENTAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-09-06 18:18 | 2020 | CENTRAL | YES | 29.9301 | -91.0653 | 1286663 | 2020-09-06 19:21 | 1286817 | NATURAL GAS |  | 12000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-06 18:57 | 2020-11-16 12:33 |  | YES | OPERATOR | 2020-09-06 18:33 | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-06 18:57 | VALVE CLOSURE |  | 2020-09-06 18:59 | 0 | 2020-09-06 18:18 | 2020-09-06 18:57 | ONSHORE | LA | 70390 | NAPOLEONVILLE | ASSUMPTION | MILEPOST | MP 1 | LAKE VERRET 12" | 307-0308 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.219 | 42000 | API 5L | OTHER | ERW - DIRECT CURRENT | YOUNGSTOWN STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1964 | 1964 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 182 | 12 |  | CLASS 1 LOCATION | NO |  | 265 |  | NO | NO | [5 empty] | 562000 | 584757.990072280574 | 0 | 0 | 30960 | 54337.9591836734693877551020408163265306 | 118000 | 122778.368022293786 | 0 | 0 | 0 | 0 |  | 2.58 | 710960 | 347791.587361110924664723032069970845481 | 761874.3172782478293877551020408163265306 | 0 | 0 | 0 | 0 | NO |  |  |  | 883 | 0 | 909 | 192.619(A)(2) |  | 1964-03-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 47505 | NO | YES | [6 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS NOT FLOWING AT THE TIME OF THE INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [5 empty] | YES |  |  | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NATHAN L. GRAY JR. | PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985 493 4629 |  | NATHAN L. GRAY JR. | ngray@eprod.com | 985 493 4629 | NHAN TRUONG | COMPLIANCE MANAGER | 713 381 2493 | nvtruong@eprod.com | ON SEPTEMBER 6 AT 18:18, HOUSTON CONTROL CENTER (HCC) RECEIVED A LOW-PRESSURE ALARM AT THE ELM HALL REGULATOR STATION AND A PRESSURE DROP AT THE CHAPARRAL OAKLEY STATION. THE PIPELINE WAS NOT FLOWING AT THE TIME OF THE INCIDENT. HCC CONTACTED THE OPERATIONS SUPERVISOR WHO DISPATCHED TECHNICIANS TO CLOSE THE MANUAL VALVES AT THE ENDS OF THE PIPELINE. AT APPROXIMATELY 18:33, LOCAL EMERGENCY RESPONDERS WERE NOTIFIED OF THE INCIDENT. AT APPROXIMATELY 18:57, TECHNICIANS ARRIVED ONSITE AND FOUND THE PIPELINE HAD RUPTURED IN A SUGAR CANE FIELD. THE PIPELINE WAS ISOLATED AND VENTED TO ATMOSPHERE. ON SEPTEMBER 9, 2020, THE RUPTURED PIPELINE SEGMENT WAS CUT OUT AND REPLACED. METALLURGICAL ANALYSIS INDICATED PIPE WALL THINNING OCCURRED AS A RESULT OF INTERNAL PITTING AND CREVICE CORROSION. THE POTENTIAL MECHANISM FOR THE METAL LOSS COULD BE WATER AND CHLORIDE ACCUMULATION AT THE BOTTOM OF THE PIPE. THE NRC 48 HOUR NOTIFICATION TOOK PLACE ON SEPTEMBER 8, 2020 AT 17:26 CST, #1286817
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200103 | 34518 | 2020-10-08 15:02 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2020-09-12 23:20 | 2020 | CENTRAL | YES | 32.4106 | -91.4874 | 1287197 | 2020-09-13 | 1287311 | NATURAL GAS |  | 5695.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONLY ASSOCIATED PIPING OR EQUIPMENT WERE SHUTDOWN |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-12 22:22 | 2020-09-12 22:45 | ONSHORE | LA | 71232-6405 | Not Within a Municipality | RICHLAND | NOT APPLICABLE |  | DELHI COMPRESSOR STATION | 30 INCH SUCTION HEADER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BLOWDOWN VALVE WAS PARTIALLY OPENED. | CLASS 1 LOCATION | NO |  | 176 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 14011 | 24590.734693877551020408163265306122449 | 0 | 0 | 0 | 0 | 200 | 208.0989288513454 | REPLACEMENT PARTS REPAIR (ARMATURE, SPRING, ORING, AND COIL) | 2.46 | 14211 | 16226.9218954423435492711370262390670554 | 24798.833622728896420408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 938 | 820169 | 1007 | OTHER | ANSI 600 VALVE | 1970-10-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VALVE WAS NOT OPERATED BY CONTROLLERS REMOTELY TO LEAD TO THIS INCIDENT; THE SOLENOID COIL HAD FAILED AS INDICATED BY THE UNUSUALLY HIGH RESISTANCE MEASURE ACROSS IT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | SOLENOID FAILURE | [161 empty] | BENSON HUNLEY | REGULATORY COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304-539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER US REGIONAL COMPLIANCE EAST | 304-550-4866 | paul_shaffer@tcenergy.com | ON SEPTEMBER 12, 2020, AN ALARM WAS ACKNOWLEDGED BY THE US NATURAL GAS CONTROL, EAST TEAM, SUBJECT TO A POSSIBLE ALARM AT DELHI COMPRESSOR STATION (CS) UNIT 811. COLUMBIA GULF TRANSMISSION, LLC (COLUMBIA) OPERATES AND MAINTAINS DELHI CS WHICH IS CLASSIFIED AS A TRANSMISSION CS, IS LOCATED IN RICHLAND PARISH, LOUISIANA AND NEAR THE CITY OF DELHI. AFTER RECEIVING THE NOTIFICATION FROM COLUMBIA MONITORING CENTER, CS PERSONNEL RESPONDED TO THIS POSSIBLE ALARM AT DELHI CS AND ADDRESSED THE UNINTENDED RELEASE OF NATURAL GAS (MATERIAL) THAT WAS VENTING INTO ATMOSPHERE FROM BLOW DOWN DISCHARGE STACK 8SH-1BD. THE CS PERSONNEL INSPECTED AND SECURED THE AREA TO ENSURE THAT IT WAS SAFE TO OPERATE DISCHARGE VALVES BEFORE MANUALLY CLOSING THEM. INVESTIGATION INTO THE INCIDENT IDENTIFIED THE PROBABLE CAUSE THAT LED TO THIS UNINTENDED RELEASE WAS DUE TO THE OPEN COMMAND SOLENOID VALVE COIL (8SH-1BD) FAILING AS DETERMINED BY AN UNUSUALLY HIGH RESISTANCE MEASURED AT THE COIL. THIS SOLENOID VALVE IS A FAIL OPEN SOLENOID THAT REQUIRES VOLTAGE TO THE COIL TO KEEP THE VALVE IN THE CLOSED POSITION. ONCE THE COIL FAILED THE VALVE (8SH-1BD) BEGAN TO OPEN UNTIL THE CLOSED LIMITS WERE BROKEN. ONCE THE LIMITS WERE BROKEN THE CLOSE SOLENOID WHICH IS A FAIL CLOSED SOLENOID ENERGIZED AND ATTEMPTED TO CLOSE THE VALVE UNTIL THE CLOSE LIMIT SWITCHES WERE MADE. THE SOLENOID VALVE WAS REBUILT BY REPLACING ARMATURE, SPRING, ORING, AND COIL. THE LIMIT SWITCH CAMS WERE ADJUSTED AND TIGHTENED TO ENSURE THIS ISSUE DOESN'T RE-OCCUR. ALL ALARMS WERE CLEARED AT THE PLC CONTROL PANEL, REQUIRED FUNCTIONAL TESTS WERE CONDUCTED WITH NO NEW ERRORS GENERATED (TO ENSURE NORMAL OPERATION OF THE UNIT), THEN THE UNIT WAS RETURNED BACK TO SERVICE. ROUTINE SAFETY CHECKS WERE CONDUCTED WHERE THE UNIT WAS MONITORED FOR A WHILE, VERIFIED THAT ALL SYSTEMS ARE RUNNING IN NORMAL MODE WITH NO NEW ERRORS WERE GENERATED THEREAFTER. A CALCULATED VOLUME OF UNINTENDED RELEASED MATERIAL WAS 5,695.60 MCF INTO ATMOSPHERE WHERE THE RELEASED MATERIAL DID NEITHER IGNITE NOR CAUSE ANY DAMAGE TO ANY OF THE CS DEVICES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200104 | 35153 | 2020-10-08 20:00 | SUPPLEMENTAL FINAL | 31485 | ENBRIDGE OFFSHORE (GAS GATHERING) L.L.C. | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-09-11 13:00 | 2020 | CENTRAL | YES | 28.5735 | -91.9594 | 1287127 | 2020-09-11 15:55 | 1287227 | NATURAL GAS |  | 65 | 48181 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | NO | THE PLATFORM WAS SHUT-IN DUE TO HURRICANE LAURA |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-11 13:00 | 2020-09-11 13:00 | OFFSHORE | [6 empty] | ENBRIDGE OFFSHORE GAS GATHERING, L.L.C. | PHMSA OPID #: 31485 | [20 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SM | 76P | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 2 | NO | 0.218 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1997 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 73 |  | NO | NO | [5 empty] | 0 | 0 | 113240 | 117825.61351563176548 | 153 | 268.530612244897959183673469387755102041 | 111000 | 115494.905512496697 | 0 | 0 | 0 | 0 | COST OF $83,000 FOR CONTRACTORS, $28,000 FOR BOAT SERVICE. | 2.3503 | 224393 | 103108.2723186436340900291545189504373178 | 233589.049640373360439183673469387755102 | 0 | 0 | 0 | 0 | NO |  |  |  | 788 | 0 | 1975 | 192.619(A)(2) |  | 1997-02-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. THE LEAK WAS TOO SMALL TO BE IDENTIFIED BY THE CONTROL ROOM PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [14 empty] | YES | [48 empty] | MICHAEL MCGRATH | ENGINEER SPECIALIST OPERATIONAL COMPLIANCE | michael.mcgrath@enbridge.com | 612-805-6542 |  |  |  |  | NATHAN ATANU | MANAGER - OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 1:00 PM. CDT ON SEPTEMBER 11, 2020, ENBRIDGE OFFSHORE GAS GATHERING L.L.C.'S (ENBRIDGE OFFSHORE) DISCOVERED A LEAK ON A 2-INCH DIAMETER BY-PASS LINE ON A PLATFORM (SMI 76) LOCATED ON SM 76P IN THE GULF OF MEXICO. ENBRIDGE OFFSHORE SUBSEQUENTLY DEPRESSURIZED THE LINE AFTER ATTEMPTING TO ISOLATE THE PIPELINE AND STOP THE LEAK. ENBRIDGE OFFSHORE NOTIFIED THE NRC AT 3:55 CDT AFTER MAKING ATTEMPTS TO ISOLATE THE LINE AND STOP THE LEAK. THE PIPELINE REMAINS OUT OF SERVICE AT THIS TIME DUE TO HURRICANE LAURA AND HURRICANE DELTA. THE PRELIMINARY DIRECT CAUSE OF THE LEAK IS ATMOSPHERIC CORROSION. UPDATED 4-8-2021 GARDEN BANKS, SMI-76 EXPERIENCED A PINHOLE LEAK ON A 2-INCH BYPASS LINE LOCATED UPSTREAM OF THE 30-INCH AT A PLATFORM SHUTDOWN VALVE. THE 2-INCH PIPE WAS COVERED WITH A COMPOSITE REINFORCEMENT WRAP. AFTER REMOVING THE COMPOSITE REINFORCEMENT WRAP IT WAS DETERMINED THAT THE LEAK WAS THE RESULT OF AN EXTERNAL CORROSION PIN HOLE BENEATH THE COMPOSITE REINFORCEMENT WRAP. THE LINE HAS BEEN REPLACED AND RECOATED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200105 | 34977 | 2020-10-10 22:12 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-09-10 00:47 | 2020 | EASTERN | YES | 28.8441 | -81.3411 | 1286952 | 2020-09-10 02:24 | 1287145 | NATURAL GAS |  | 22000 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-10 02:08 | 2020-11-24 18:42 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-09-10 02:35 | YES | 2020-09-10 00:53 | OPERATOR/CONTRACTOR |  | 2200 | NO | VALVE CLOSURE |  | 2020-09-10 02:08 | VALVE CLOSURE |  | 2020-09-10 02:09 | 20 | 2020-09-10 00:47 | 2020-09-10 02:29 | ONSHORE | FL | 32771 | SANFORD | SEMINOLE | MILEPOST | 15 | 12" SANFORD LATERAL | FLBOD | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 37 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 12 |  | 0.219 | 42000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET | COLD APPLIED TAPE |  | YES | [26 empty] | 1959 | 1959 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 317 | 24 |  | CLASS 1 LOCATION | NO |  | 235 |  | NO | NO | [5 empty] | 68000 | 70753.635809457436 | 0 | 0 | 48180 | 84560.8163265306122448979591836734693878 | 2054568 | 2137767.000261255078936 | 2000 | 2080.989288513454 | 0 | 0 |  | 2.19 | 2172748 | 1030717.02918016165856039650145772594752 | 2295162.44168575658118089795918367346939 | 0 | 0 | 32 | 93 | NO |  |  |  | 695 | 0 | 713 | 192.619(C) |  | 1989-09-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 38544 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [6 empty] | YES | NEAR NEUTRAL PH STRESS CORROSION CRACKING. | 1062 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2019 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2014 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2014 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KATHRYN HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI | DIRECTOR REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | 09/10/20 AT 00:47 AM EASTERN FGT GAS CONTROL DETECTED A LOW PRESSURE ALARM AT THE DEBARY POWER PLANT. INVESTIGATION BY FIELD OPERATIONS CONFIRMED A FAILURE ON THE 12IN SANFORD LATERAL THAT HAD IGNITED. 09/10/20 AT 02:35 AM EASTERN LOCAL EMERGENCY RESPONDER MADE CONTACT WITH FGT PERSONNEL ON THE SCENE. THE LOCATION OF THE INCIDENT IS IN SEMINOLE COUNTY IN THE NORTHERN PART OF THE ORLANDO METROPOLITAN AREA. THE INCIDENT OCCURRED IN A POWER LINE CORRIDOR AND RESULTED IN DAMAGE TO A DUKE ENERGY 230KV TRANSMISSION LINE. THE PIPELINE WAS ISOLATED AT APPROXIMATELY 2:08 AM. 09/10/20 AT 07:55 AM EASTERN - THREE MARLIN CNG TRUCKS ARRIVED ON SITE AND WAS ABLE TO MOBILIZE ADDITIONAL TANKERS TO THE METER STATIONS TO MEET THE SUPPLY NEEDS FOR FPU CUSTOMERS. 09/10/20 AT 16:00 PM CONSTRUCTION UNDERWAY TO RETURN THE UPSTREAM PORTION OF THE 12IN SANFORD LATERAL TO SERVICE AT A REDUCED PRESSURE (344 PSIG). THIS IS 50% OF THE OPERATING PRESSURE AT THE TIME OF THE FAILURE. UPSTREAM SECTION IS CURRENTLY IN-SERVICE AT 50% MAOP. DOWNSTREAM FAILED SECTION IS STILL OUT OF SERVICE AND ISOLATED. THE ISOLATED SEGMENT IS UNDER A PHMSA CORRECTIVE ACTION ORDER AND THE FAILED PIPE IS UNDERGOING METALLURGICAL ANALYSIS, A SUPPLEMENTAL INCIDENT REPORT WILL BE FILED ONCE THE CAUSE IS DETERMINED. UPDATE: THE PIPELINE HAS SINCE BEEN REPAIRED BY REPLACING THE FAILED SECTION AND WAS RESTARTED ON 11/24/2020 UNDER THE CORRECTIVE ACTION ORDER. THE FAILED SECTION WAS SENT TO A METALLURGICAL LABORATORY FOR ANALYSIS AND VIA THAT ANALYSIS, THE FAILURE WAS IDENTIFIED TO BE NEAR NEUTRAL PH STRESS CORROSION CRACKING.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200106 | 34376 | 2020-10-13 17:34 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2020-09-15 08:55 | 2020 | CENTRAL | YES | 31.9507 | -103.108 | 1287376 | 2020-09-15 10:18 | 1287490, 1287493 | NATURAL GAS |  | 34161.7 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-15 08:30 | 2020-09-18 17:30 |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-15 08:41 | 2020-09-15 08:41 | ONSHORE | TX | 79745 | KERMIT | WINKLER | NOT APPLICABLE |  | KEYSTONE COMPRESSOR STATION | KEYSTONE STATION SUCTION LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1952 | 1952 | CARBON STEEL |  | LEAK |  |  | OTHER | MAOP EXC. LED TO PRV RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 496 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 61491 | 107922.9795918367346938775510204081632653 | 0 | 0 | 100 | 104.0494644256727 | 450 | 468.22258991552715 | RELIEF VALVE TESTING | 1.8 | 62041 | 71065.7152416209637109329446064139941691 | 108495.2516461779345438775510204081632653 | 0 | 0 | 0 | 0 | NO |  |  |  | 620.6 | 0 | 575 | 192.619(A)(3) |  | 1952-06-30 | BI-DIRECTIONAL | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | TWO ACTIVITIES WERE SCHEDULED TO OCCUR ON 9/15/2020 AND A MISUNDERSTANDING OF WHICH ACTIVITIES WERE REQUESTED LED TO THE OVERPRESSURE EVENT AND RELEASE OF NATURAL GAS. | NO |  |  | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | KRISTIN VAN DER LAAN | ENGINEERING MANAGER IC - CODES AND COMPLIANCE | kristin_vanderlaan@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | ENGINEERING DIRECTOR - CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | THE EPNG KEYSTONE CS (A.K.A. KEYSTONE ML OR KML) HAD A SCHEDULED OUTAGE ON 9/15/20 STARTING AT 9:00AM (START OF GAS DAY) TO PERFORM AN ANNUAL ESD TEST. ON 9/14/20, KEYSTONE AREA OPERATIONS WAS TOLD BY EPNG GAS CONTROL THAT THE EPNG WINK CS NEEDED TO BE ONLINE BEFORE THE OUTAGE TO ENSURE THAT THE PRESSURE DID NOT EXCEED MAOP. THE REQUIREMENT OF HAVING THE WINK CS OPERATING WAS NOT INCLUDED IN THE OUTAGE PLAN AND WAS NOT DISCUSSED DURING THE PRE-JOB OR JSA. ON 9/15/20 AT 8:15AM, EPNG OPERATIONS SPECIALIST MADE A CALL TO EPNG GAS CONTROL TO REQUEST PERMISSION TO TAKE KML DOWN EARLIER THAN PLANNED AS OPERATIONS HAD COMPLETED THE PRE-JOB / JSA REVIEWS WITH ALL OF THE KM/EPNG EMPLOYEES AND CONTRACTORS. THE EPNG GAS CONTROLLER STATED HE WOULD CHECK AND CALL THE EPNG OPERATIONS SPECIALIST BACK. AT 8:25AM, THE EPNG GAS CONTROLLER CALLED EPNG OPERATIONS SPECIALIST AND GAVE THE OKAY TO START THE OUTAGE AT 8:33 AM. THE WINK CS WAS NOT ONLINE. BASED ON THE INVESTIGATION INTO THIS EVENT IT WAS LATER DETERMINED THAT THE EPNG GAS CONTROLLER WAS REFERRING TO STARTING THE WINK CS IN PREPARATION FOR THE KEYSTONE ESD SYSTEM TEST. LOCAL OPERATIONS PERSONNEL PUSHED THE ESD BUTTON TO INITIATE THE ESD SYSTEM TEST AT KML. AT 8:41AM, A PRV ON THE 30-INCH PLANT SUCTION LINE, WHICH HAS A MAOP OF 575 PSIG, STARTED TO RELIEVE GAS DUE TO OVER PRESSURE (SET POINT 580 PSI). AT 8:45AM, A SECOND PRV LIFTED ON LINE 3026 (SET POINT 605 PSIG), WHICH HAS A MAOP OF 651 PSIG. AT 8:59AM, THE EPNG OPERATIONS SUPERVISOR FOR KML AND WINK CS CALLED KM KEYSTONE GAS STORAGE (KEYSTOR) TO STOP DELIVERING GAS TO EPNG LINE 3026. AT 9:20AM, THE THIRD PRV LIFTED ON LINE 3026 (SET POINT OF 630 PSIG). THE FOURTH PRV ON LINE 3026 (SET POINT 580 PSIG) DID NOT OPERATE. AT 9:50AM, IN CONFORMANCE WITH O&M PROCEDURE 159 ' EMERGENCY REPORTING AND INVESTIGATION, AN ERL CALL WAS HELD. DURING THE CALL IT WAS DETERMINED THAT THE UNINTENTIONAL GAS RELEASED THROUGH THE RELIEF VALVES WOULD MEET AND EXCEED THE 3,000 MCF REPORTABILITY THRESHOLD. THE ACTUAL GAS LOSS WAS UNKNOWN AT THE TIME. AT 9:55AM THE MAOP EXCEEDED 110% (632.5PSIG) WITH A PRESSURE OF 633 PSIG FOR APPROXIMATELY 1 MINUTE. IN ORDER TO REDUCE THE PRESSURES TO NORMAL AND STOP THE RELEASE OF GAS THROUGH THE RELIEF VALVES: - AT 9:05AM, KEYSTOR STOPPED WITHDRAWAL INTO THE EPNG SYSTEM - AT 9:20AM, THE GC LEADS WORKED WITH KEYSTONE CS SUPERVISION TO ISOLATE SUPPLY INTO KEYSTONE CS. THE L3006, L3028, AND L3082 WERE SHUTOFF AT THE KEYSTONE FIELD VALVE YARD. L1115 WAS OPENED AT GOLDSMITH TO DIVERT THE GAS NORTH TOWARDS PLAINS. ONCE THE WARREN WADDELL INTERCONNECT SHUTDOWN, L3146 VALVE 2 WAS OPENED, AND WINK WAS BROUGHT ONLINE, L1105 VALVE 0 WAS CLOSED. THESE TWO VALVE CLOSURES ISOLATE THE KEYSTONE CS SUCTION PIPING. - AT 10:01AM, KEYSTORE STARTED INJECTION - GAS CONTROL CALLED PERMIAN PRODUCERS ASKING THEM TO SHUT IN EARLY - AT 10:27AM, THE EPNG OPERATIONS SPECIALIST WAS SENT TO LINE 3026 TO CLOSE VALVE 3. - AT 10:14AM, A SECOND EPNG OPERATIONS SPECIALIST OPENED LINE 1115 TO ALLOW GAS TO FLOW NORTH TO PLAINS. BY 11:25AM, ALL OF THE RELIEF VALVES HAD RESEATED AND PRESSURES RETURNED TO BELOW MAOP BY 12:16PM. THE INVESTIGATION DETERMINED THAT THERE WAS A FAILURE OF CLEAR COMMUNICATIONS BETWEEN EPNG OPERATIONS AND THE CONTROL CENTER. NOTES: THE TIME ESTIMATE FOR INCIDENT REPORTING THRESHOLD IS A COMBINATION OF THE RELIEF VALVE ON THE INLET SUCTION PIPING AND ONE OF THE RELIEF VALVES ON LINE 3026 RELIEVING. 1) INLET SUCTION RV, RELEASE TIME: 8:41AM - 9:20AM, TOTAL 5936 MCF 2) RV L3026, RELEASE TIME: 8:45AM - 11:25AM, TOTAL 1586.7 MCF 3) RV L3026, RELEASE TIME: 9:20AM - 11:25AM, TOTAL 12363 MCF FOR PART E1 PRESSURE NOTED IS THE PRESSURE AT 8:55AM CENTRAL TIME WHEN THE GAS LOSS MET THE REPORTING THRESHOLD. A SEPARATE MAOP EXCEEDANCE REPORT (PHMSA REPORT 20-191933) WAS SUBMITTED TO PHMSA ASSOCIATED WITH THIS EVENT AND IN CONFORMANCE WITH 49CFR 191.25(B). L3026 MAOP OF 651PSIG WAS NOT EXCEEDED.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20200107 | 34628 | 2020-10-16 17:16 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2020-09-18 12:00 | 2020 | MOUNTAIN | YES | 45.2519 | -109.1165 | 1287711 | 2020-09-18 12:48 | 1287832 | NATURAL GAS |  | 333186 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-21 17:00 | 2020-12-01 12:04 |  | YES | OPERATOR | 2020-09-18 20:37 | NO | [11 empty] | 0 | 2020-09-16 14:30 | 2020-09-16 07:00 | ONSHORE | MT | 59014 | Not Within a Municipality | CARBON | NOT APPLICABLE |  | DRY CREEK STORAGE | STORAGE WELL BN 8-3 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1983 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 1 LOCATION | NO |  | 266 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 565283 | 992129.3469387755102040816326530612244898 | 650000 | 676321.51876687255 | 150000 | 156074.19663850905 | 0 | 0 |  | 1.6966 | 1365283 | 1018202.98993263950320699708454810495627 | 1824525.06234415711020408163265306122449 | 0 | 0 | 0 | 0 | NO |  |  |  | 1140 | 7872 | 1600 | OTHER | WELL CASING MAOP BELIEVED TO BE EQUAL TO OR EXCEED THE MAOP OF THE FIELD | 1983-08-16 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO ACTIONS THAT THE GAS CONTROLLERS COULD HAVE DONE THAT CAUSED THIS ISSUE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | NWE IS CHANGING TO INTERNAL CORROSION BECAUSE OF DATA THAT WAS GATHERED FROM RUNNING A HIGH RESOLUTION VERTALOG, WHICH CAN DIFFERENTIATE BETWEEN INTERNAL AND EXTERNAL CORROSION. THE INTERNAL CORROSION WAS ALSO VERIFIED WITH A CALIPER LOG THAT WAS RUN DOWN THE CASING WITH THE VERTALOG TOOL. |  |  |  |  | YES | IT IS BELIEVED THAT A WATER INTERFACE OCCURRED AT THIS LOCATION BASED ON NWE CATHODIC NACE SMES. THIS COULD NOT BE VERIFIED. MICROBIOLOGICAL TESTING WAS NOT COMPLETED BECAUSE THE WELL HAD HAD BIOCIDE ADDED AND FOREIGN WATER ADDED TO KILL THE WELL. |  |  | YES | INTERNAL CORROSION WAS SELECTED BECAUSE OF DATA THAT WAS GATHERED FROM RUNNING A HIGH RESOLUTION VERTALOG, WHICH CAN DIFFERENTIATE BETWEEN INTERNAL AND EXTERNAL CORROSION. THE INTERNAL CORROSION WAS ALSO VERIFIED WITH A CALIPER LOG THAT WAS RUN DOWN THE CASING WITH THE VERTALOG TOOL. |  |  |  |  | YES | WELL CASING AT ~1900' BELOW SURFACE. | YES | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | KEITH MEAGOR | MANAGER OF GAS TRANSMISSION COMPLIANCE | keith.meagor@northwestern.com | 406-461-1211 |  |  |  |  | KEITH MEAGOR | MANAGER OF GAS TRANSMISSION COMPLIANCE | 406-497-1211 | keith.meagor@northwestern.com | THIS IS A SUPPLEMENTAL FINAL REPORT FOR INCIDENT REPORT 20200107-34393 SUBMITTED ON 10/16/20. PLEASE REFER TO THAT INCIDENT REPORT FOR THE INITIAL NARRATIVE. THE CAUSE OF THE INCIDENT HAS BEEN CHANGED IN PART G FROM EXTERNAL CORROSION TO INTERNAL CORROSION. THIS CHANGE HAS OCCURRED BECAUSE OF DATA THAT WAS GATHERED FROM RUNNING A HIGH RESOLUTION VERTALOG, WHICH CAN DIFFERENTIATE BETWEEN INTERNAL AND EXTERNAL CORROSION. THE INTERNAL CORROSION WAS ALSO VERIFIED WITH A CALIPER LOG THAT WAS RUN DOWN THE CASING WITH THE VERTALOG TOOL. AS NOTED IN THE INITIAL REPORT, THE WELL WAS KILLED AND THEN A COMPOSITE PLUG WAS PLACED AT 4479' JUST ABOVE THE PERFORATIONS. A PRODUCTION CASING WAS INSTALLED FROM SURFACE TO 4431'. THE PRODUCTION CASING WAS CEMENTED IN PLACE. CEMENT WAS RUN DOWN THE INSIDE OF THE INNER CASING AND THERE WERE RETURNS TO SURFACE THROUGH THE ANNULAR SPACE BETWEEN THE NEW PRODUCTION CASING AND THE OUTER CASING. THIS SEALED THE LEAK IN THE OUTER CASING AND PROVIDES A MITIGATION AGAINST ADDITIONAL LEAKS. A CEMENT BOND LOG WAS RUN FOR THE CEMENTING WORK OF THE INNER CASING AND NO DEFICIENCIES WERE NOTED IN THE LOG. A PRESSURE TEST WAS COMPLETED ON THE NEW INSTALLATION AND NO ISSUES WERE NOTED DURING THE TEST. FOLLOWING THE INTEGRITY TESTING, THE COMPOSITE PLUG WAS DRILLED OUT. THE WELL WAS THEN RE-COMMISSIONED ON 12/01/20. THE WELL HAS BEEN OPERATING FOR TWO WEEKS WITH NO IDENTIFIED ISSUES. AS AN ADDITIONAL MITIGATION, LEAK SURVEYS HAVE BEEN COMPLETED AROUND THE WELL AND ALONG THE PREVIOUS INCIDENT PLUME BOUNDARY. THE PLUME FROM THE INCIDENT HAS DISSIPATED SIGNIFICANTLY. READINGS WITHIN THE PLUME AREA ARE UNDER A PERCENT GAS IN BAR HOLES. NWE IS CONTINUING TO MONITOR THE PLUME AND WILL DO SO UNTIL IT HAS DISSIPATED. THERE ARE NO SAFETY OR PUBLIC SAFETY CONCERNS. THIS WILL BE THE FINAL REPORT FOR THIS INCIDENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200108 | 34833 | 2020-10-17 12:13 | SUPPLEMENTAL FINAL | 31356 | VECTOR PIPELINE, L.P. | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-09-16 12:44 | 2020 | EASTERN | NO | 42.1429 | -85.2644 | 1287496 | 2020-09-16 13:31 | 1287691 | NATURAL GAS |  | 292 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | YES | OPERATOR | 2020-09-16 12:46 | YES | 2020-09-16 12:44 | ALLOWED TO BURN OUT |  | 292 | NO | [6 empty] | 0 | 2020-09-16 12:44 | 2020-09-16 12:44 | ONSHORE | MI | 49011 | Not Within a Municipality | CALHOUN | MILEPOST | MP 168 | VECTOR ATHENS COMPRESSOR STATION | ATHENS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2009 | 2009 | CARBON STEEL |  | OTHER | [8 empty] | OPEN BODY BLEED VALVES ON SUCTION AND DISCHARGE VALVES. | CLASS 1 LOCATION | NO |  | 655 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 599 | 1051.306122448979591836734693877551020408 | 70000 | 72834.62509797089 | 2000 | 2080.989288513454 | 0 | 0 |  | 2.05 | 72599 | 33739.710347581870157434402332361516035 | 75966.9205089333235918367346938775510204 | 0 | 0 | 0 | 0 | NO |  |  |  | 748 | 0 | 1000 | 192.619(A)(2) |  | 2000-12-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE STATION WAS BEING MONITORED REMOTELY (SCADA), BUT WAS UNDER LOCAL CONTROL AT TIME OF THE EVENT. | [12 empty] | YES | 2 | 0 | YES | 2 | 0 | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | ROUTINE MAINTENANCE | NO | [143 empty] | YES | [6 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 16128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 12:44 PM EDT ON SEPTEMBER 16, 2020, VECTOR PIPELINE, L.P.'S (VECTOR) ATHEN'S COMPRESSOR STATION HAD A FIRE DURING THE STARTING SEQUENCE OF THE TURBINE UNIT. DURING THE ENSUING MINUTES, VECTOR EVACUATED THE FACILITY AND SUBSEQUENTLY NOTIFIED THE FIRST RESPONDERS. THE ESD WAS ACTIVATED BY A FLAME DETECTOR IN THE FACILITY, THUS ISOLATING THE COMPRESSOR STATION. THE CAUSE OF THE INCIDENT WAS INCORRECT OPERATION OF THE VALVES. THE BODY BLEEDS ON THE UNIT SUCTION AND DISCHARGE VALVES WERE INADVERTENTLY LEFT OPEN FOLLOWING ROUTINE (SEMI ANNUAL) MAINTENANCE AND AS A RESULT VENTED GAS DURING THE UNIT STARTING SEQUENCE. USING THE BODY BLEEDS AS AND ADDITIONAL SAFETY MEASURE IS A COMMON PRACTICE AND THE LOCK OUT TAG OUT (LOTO) ISOLATION PLAN HAS BEEN UPDATED TO INCLUDE THESE VALVES. VECTOR IS REVIEWING PROCEDURES AND TRAINING TO PREVENT RECURRENCE. 01/04/2021 UPDATED PART G7 (3) AND PART H.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200109 | 34514 | 2020-10-22 00:38 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2020-09-24 15:57 | 2020 | MOUNTAIN | YES | 42.6531 | -113.0101 | 1288206 | 2020-09-24 17:18 | 1288427 | NATURAL GAS |  | 123.2 | 10555 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-24 18:43 | 2020-10-21 11:15 |  | YES | OPERATOR | 2020-09-24 18:05 | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-24 18:43 | VALVE CLOSURE |  | 2020-09-24 18:25 | 0 | 2020-09-24 15:57 | 2020-09-24 15:57 | ONSHORE | ID | 83211 | Not Within a Municipality | POWER | MILEPOST | 626.9 | WILLIAMS NORTHWEST PIPELINE | MAINLINE 1400 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED WESTERN | ASPHALT |  | UNKNOWN | [26 empty] | 1955 | 1955 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 443 |  | NO | NO | [5 empty] | 0 | 0 | 12772 | 13289.197596446917244 | 149 | 261.510204081632653061224489795918367347 | 200000 | 208098.9288513454 | 0 | 0 | 0 | 0 |  | 1.21 | 212921 | 97839.5513004519581818192419825072886297 | 221649.6366518739498970612244897959183673 | 0 | 0 | 0 | 0 | NO |  |  |  | 591 | 178500 | 850 | 192.619(A)(3) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 91783 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS WERE OF A MINOR NATURE IN TERMS OF GAS LOSS, AND SCADA IS NOT WELL SUITED FOR IDENTIFYING THESE TYPES OF LEAKS. LEAKS WERE DISCOVERED DURING FOLLOW UP ACTIVITIES ASSOCIATED WITH IN-LINE INSPECTION OF THE LINE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1975 | YES | YES | YES |  |  |  | 2019 |  |  |  | NO | [190 empty] | YES | YES | [6 empty] | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [45 empty] | NO |  |  | Yes, and an investigative dig was cunducted at the point of the Accident | 2020 |  |  |  |  | 2020 | [5 empty] | YES |  | NO | [63 empty] | BRET BURKHART | ENGINEER III - PIPELINE SAFETY | bret.burkhart@williams.com | 801-584-6892 |  | DAVE DICKERSON | david.s.dickerson@williams.com | 208-884-4300 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | IN APRIL OF 2020 WILLIAMS CONTRACTED WITH AN IN-LINE INSPECTION VENDOR TO COMPLETE TOOL RUNS ON THE WILLIAMS NORTHWEST PIPELINE 1400 POCATELLO TO BURLEY SEGMENT. HIGH-RES MFL TOOL RUNS WERE CONDUCTED, AND A PRELIMINARY REPORT WAS PROVIDED TO WILLIAMS WITH ANOMALIES ON THE WEEK OF 5/25/2020. WILLIAMS INITIATED PROJECTS TO ADDRESS ANOMALIES IN ORDER OF PRIORITY. THIS PARTICULAR DIG DID NOT MEET THE SAME CRITERIA AS OTHER'S IN THE AREA - UNDER CALLED BY THE TOOL. AS A RESULT THIS PIN HOLE WAS NOT DISCOVERED UNTIL REMEDIATION OF OTHER LEAKS IN THE SAME GENERAL AREA HAD BEEN COMPLETED. SIMILAR TO OTHER ANOMALIES IN THE AREA EXCAVATION UNCOVERED A PIN-HOLE LEAK RESULTING FROM CORROSION. LEAK SURVEYS PRIOR TO FEATURE ASSESSMENT DID NOT SHOW ANY SIGNS OF LEAKING. ASSESSMENTS INCLUDED AERIAL LEAK SURVEY 9/22/2020, AND GROUND SURVEY 9/23/2020. THERE WAS NO INDICATION OF FOUL ODORS OR DISCOLORED VEGETATION PRIOR TO DIGGING. THE FIRST INDICATION OF GAS OCCURRED AFTER THE FEATURE WAS UNCOVERED. IT IS ESTIMATED THAT THE FEATURE LEAKED FROM THE FIRST INDICATION OF GAS FOR APPROXIMATELY 3 HOURS BEFORE THE LINE WAS SHUT IN AND BLOWN DOWN FROM AN OPERATING PRESSURE OF ABOUT 600PSIG TO 14PSIG. AFTER ASSESSING REPAIR OPTIONS WILLIAMS PROJECT MANAGEMENT DETERMINED THAT REPAIRS WOULD BE BEST ACCOMPLISHED THROUGH PIPE REPLACEMENT. THE PRELIMINARY COST OF REPAIRS EXCEEDS $50,000, WITH COST OF CONTRACTOR AND INTERNAL LABOR APPROACHING $200,000. IT WAS DETERMINED THAT THIS QUALIFIED AS A DOT REPORT-ABLE INCIDENT BASED ON COST WHEN WILLIAMS MANAGEMENT SETTLED ON PIPE REPLACEMENT AS THE PREFERRED REPAIR OPTION ON 9/24/2020. THE NRC WAS INITIALLY NOTIFIED OF THE INCIDENT ON 9/24/2020. THE LINE WAS RETURNED TO SERVICE ON 10/21/2020
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200110 | 36132 | 2020-10-22 17:53 | SUPPLEMENTAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-09-24 00:44 | 2020 | MOUNTAIN | YES | 32.8153 | -104.1645 | 1288123 | 2020-09-24 05:53 | 1288243 | NATURAL GAS |  | 31757 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-24 04:40 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-24 03:19 | VALVE CLOSURE |  | 2020-09-24 04:40 | 0 | 2020-09-24 04:40 | 2020-09-24 06:00 | ONSHORE | NM | 88255 | LOCO HILLS | EDDY |  |  | INDIAN BASIN PIPELINE | INDIAN BASIN PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 20 |  | 0.235 | 60000 | API 5L GRADE X60 | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET AND TUBE | ASPHALT |  | YES | [26 empty] | 1965 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 810 | 29 |  | CLASS 1 LOCATION | NO |  | 436 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 44460 | 78031.8367346938775510204081632653061224 | 114590 | 119230.28128537834693 | 1794 | 1866.647391796568238 | 78392 | 81566.456152573342984 | INVESTIGATION COST.- 3RD PARTY METALLURGICAL ANALYSIS, SITE SURVEY, TRAVEL, RCFA | 1.4 | 239236 | 140607.6150669172325571778425655976676385 | 280695.2215644421357030204081632653061224 | 0 | 0 | 0 | 0 | NO |  |  |  | 964 | 1500 | 1000 | 192.619(A)(1) |  | 1965-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | AUTOMATIC | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [5 empty] | YES | [5 empty] | YES |  |  | YES | YES | 1965 | YES | YES | YES | YES |  |  | 2020 | 2017 |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2002 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | IMU | 2017 | FREE SWIMMING |  |  |  | YES | 2020 | 1268 | NO | [13 empty] | NO | [63 empty] | JORGE LOPEZ | MANAGER ENGINEERING CODES AND COMPLIANCE | jorge_lopez@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND COMPLIANCE | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON SEPTEMBER 24, 2020 THE NATURAL GAS PIPELINE COMPANY OF AMERICA, LLC (NGPL) 20-INCH INDIAN BASIN PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE WITH NO FIRE. 00:44 - MEASUREMENT TECH 1 WAS CALLED OUT ON LOW-PRESSURE ALARM AT PIN 1753 OXY INDIAN BASIN. 01:20- MEASUREMENT TECH 1 ARRIVED ON SITE PIN 1753 AND STARTED INVESTIGATING. MEASUREMENT TECH 1 PUT HIS PRECISION GAUGE ON MAINLINE AND SAW LINE PRESSURE DROPPING DRASTICALLY. CONSEQUENTLY, CALLED LEAD TECH AND BOTH LOGGED ON CONCENTRATOR (SCADA) TO LOOK OVER MAINLINE PRESSURES USING METER STATION DATA. 01:54 - MEASUREMENT SUPERVISOR RECEIVED CALL FROM LEAD TECH REGARDING A POTENTIAL LINE LEAK AT INDIAN HILL STATION. AFTER CONFIRMING OTHER STATION PRESSURES ALONG THE LINE VIA SCADA, MEASUREMENT SUPERVISOR ADVISED TECHS TO START SHUTTING IN STATIONS. 01:55 - OXY INDIAN BASIN PIN 1753 SHUT -IN IB-4 MAINLINE VALVE ALSO SHUT. 02:20 - FASKEN NORTH INDIAN HILLS PIN 37613 SHUT-IN. 03:12 - EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATIONS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE POTENTIAL INCIDENT. 03:19A- IB-3 SHUT IN. 04:00 - DCP FUEL PIN 1791 SHUT IN. 04:22 - OPERATIONS FOUND IB-1 OPEN AND HOLDING PRESSURE. 04:40- IB-2 FOUND CLOSED. 04:50 - HOLLY PIN 44836 MANUAL ISOLATION VALVE WAS SHUT IN; MEASUREMENT TECH 1 OPENED IT UP TO MONITOR LINE PRESSURE BETWEEN THAT SEGMENT- VALVES DOWN STREAM OF METER WERE LOCKED GOING TO CUSTOMER. 05:20- DCP BIG EDDY PIN 25776 - SHUT IN. 05:53- CALL TO NRC INITIATED (#1288123). 06:00- NGPL PERSONAL ON SITE CONFIRMED THE RUPTURED ON THE INDIAN BASIN PIPELINE. 06:18-ERL+ CALL NOTIFICATION INITIATED PER COMPANY PROCEDURES TO DISCUSS THE RUPTURE INCIDENT. ON SEPTEMBER 28, PIPE WAS REPLACED AND COVERED. THE METALLURGICAL REPORT CONCLUDED THAT THE INDIAN BASIN INCIDENT ORIGINATED IN THE FUSION AREA OF THE DC-ERW LONG SEAM FROM CORROSION ON THE EXTERNAL SURFACE OF THE PIPE IN AN AREA OF COATING DISBONDMENT. METALLURGICAL FAILURE ANALYSIS REPORT WAS COMPLETED AND PROVIDED TO PHMSA ON 11/12/2020. CURRENTLY NGPL IS WAITING APPROVAL FROM PHMSA FOR THE REMEDIAL WORK PLAN (RWP) THAT WAS SENT ON 5/28/2021 IN ACCORDANCE WITH CPF NO. 2-2020-001-CAO, ITEM #13. NOTE: ON OCTOBER 1, 2020, NGPL RECEIVED CORRECTIVE ACTION ORDER (CAO) CPF NO. 2-2020-001-CAO FROM PHMSA. NGPL IS COMPLYING WITH THE REQUIRED CORRECTIVE ACTIONS IN THE CAO.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20200111 | 34416 | 2020-10-23 07:46 | ORIGINAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-09-24 11:00 | 2020 | CENTRAL | NO | 35.1441 | -96.1576 | 1288296 | 2020-09-25 18:34 | 1288409 | NATURAL GAS |  | 1000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE STORAGE FIELD WAS INJECTING AND THE WELL WAS ISOLATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-24 11:00 | 2020-09-24 12:00 | ONSHORE | OK | 74883 | WETUMKA | HUGHES | NOT APPLICABLE |  | WETUMKA STORAGE FACILITY | IW-40 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 4 | NO | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1997 | 1997 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 309 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 2800 | 4914.285714285714285714285714285714285714 | 120000 | 124859.35731080724 | 5000 | 5202.473221283635 | 0 | 0 |  | 2.8 | 127800 | 60602.7881500069923469387755102040816327 | 134976.1162463765892857142857142857142857 | 0 | 0 | 0 | 0 | NO |  |  |  | 715 | 20000 | 827 | 192.619(A)(4) |  | 2018-09-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS MINOR AND IT COULD NOT HAVE BEEN DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [17 empty] | YES | P-SEAL ID PREP FAILED RESULING IN THE DSA RING GASKETS TO FAIL. | [150 empty] | YES | [10 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 626 3981 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 405 626 3981 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 626 3981 | casey.roberts@enablemidstream.com | ON 9/24/20 A THIRD-PARTY WEED CONTROL CONTRACTOR DISCOVERED AND REPORTED A LEAK AT THE IW-40 WELL IN THE WETUMKA STORAGE FACILITY. THE CONTRACTOR REPORTED THE LEAK TO AN ENABLE O&M TECHNICIAN. THE O&M TECHNICIAN ARRIVED AND OBSERVED WATER AROUND THE WELLHEAD AND BUBBLES. THE LEAK WAS MINOR AND WHEN THE WELL WAS ISOLATED (THE STORAGE FIELD WAS INJECTING AT THE TIME) THE LEAK CONTINUED BUT WAS REDUCED. IT WAS DETERMINED THE COST FOR REPAIR WOULD EXCEED $50,000 SO A CALL WAS PLACED TO THE NRC ON 9/25/2020 AT 18:34 CST (NRC#1288296) AND A 48-HR. FOLLOW UP (NRC#1288409) WAS PROVIDED 9/27/20 AT 15:31 CST. A CONTRACTOR WAS HIRED AND UPON INVESTIGATION, IT WAS DETERMINED THE LEAK STARTED IN THE INTERNAL P-SEAL INSIDE THE 11' 3K X 7-1/16' 3K 7-5/8' P-SEAL ID PREP THAT ULTIMATELY MADE ITS WAY ACROSS THE RING GASKET BETWEEN THE P-SEAL ID PREP AND THE DOUBLE-STUDDED ADAPTER (DSA), AND SEPARATELY ACROSS THE RING GASKET BETWEEN THE DSA AND THE CASING HEAD LOCATED BELOW THE DSA. THE WELL WAS FIXED AND WAS PLACED BACK INTO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200112 | 35005 | 2020-10-23 22:42 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-09-24 09:48 | 2020 | EASTERN | YES | 26.6186 | -80.1734 | 1288141 | 2020-09-24 10:53 | 1288281 | NATURAL GAS |  | 12000 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-24 10:13 | 2020-12-11 06:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-09-24 10:45 | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-24 10:06 | VALVE CLOSURE |  | 2020-09-24 10:13 | 0 | 2020-09-24 09:49 | 2020-09-24 09:52 | ONSHORE | FL | 33467 | LAKE WORTH | PALM BEACH | MILEPOST | 844.25 | 18IN MAINLINE | FLMEA21 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 | NO | 0.25 | 52000 | API 5L | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE | COLD APPLIED TAPE |  | YES | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 264 | 18 |  | CLASS 3 LOCATION | YES | METHOD2 | 365 |  | NO | YES | [5 empty] | 190000 | 197693.98240877813 | 0 | 0 | 22920 | 40226.9387755102040816326530612244897959 | 1360000 | 1415072.71618914872 | 2000 | 2080.989288513454 | 0 | 0 |  | 1.91 | 1574920 | 738803.7045509532892827988338192419825073 | 1655074.6266619505080816326530612244898 | 0 | 0 | 0 | 0 | NO |  |  |  | 846 | 4.8 | 866 | 192.619(A)(1) |  | 2004-01-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | HIGH-PH STRESS CORROSION CRACKING. | 1088 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2007 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2007 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [14 empty] | YES | 2018 | 1447 | NO | [13 empty] | NO | [63 empty] | KATHRYN HARRYMAN | SENIOR SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI | DIRECTOR REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | AT ~9:48 EDT ON 9/24/2020, LOCAL OPERATIONS PERSONNEL RECEIVED A CALL FROM LAKE WORTH DRAINAGE DISTRICT ABOUT A GAS LINE RUPTURE JUST NORTH OF THE INTERSECTION OF LAKE WORTH ROAD AND THE FLORIDA TURNPIKE. AT THE SAME TIME THE CONTROL CENTER SAW THE PRESSURE DROP ON THE DISCHARGE SIDE OF COMPRESSOR STATION 21 AND TOOK ACTION TO SHUT DOWN THE PIPELINE. LOCAL OPERATIONS CONFIRMED THE INCIDENT AT ~9:52 AND THE SEGMENT WAS ISOLATED BY CLOSING THE UPSTREAM AND DOWNSTREAM MLV'S. AT ~10:53 EDT ON 9/24/20, INITIAL NOTIFICATION WAS MADE TO THE NRC (REPORT# 1288141) AND AGAIN ON 09/25/20 AT ~4:47 EDT WITH THE 48 HOUR UPDATE NOTIFICATION; NRC # 128828. UPDATE: THE PIPELINE HAS SINCE BEEN REPAIRED AND WAS RESTARTED ON 12/11/2020 UNDER A PHMSA CORRECTIVE ACTION ORDER. THE FAILED SECTION WAS SENT TO THE LABORATORY FOR ANALYSIS AND THROUGH METALLURGICAL ANALYSIS, THE FAILURE WAS IDENTIFIED TO BE HIGH PH - STRESS CORROSION CRACKING.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200113 | 34425 | 2020-10-26 08:25 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-09-29 14:50 | 2020 | EASTERN | NO | 40.4173 | -75.6214 | 1288593 | 2020-09-29 15:02 | 1288776 | NATURAL GAS |  | 226.8 | 16384.89 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-09-30 15:00 | 2020-10-06 12:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-09-30 15:00 | VALVE CLOSURE |  | 2020-09-30 15:00 | 0 | 2020-09-28 08:30 | 2020-09-28 08:30 | ONSHORE | PA | 19504 | Not Within a Municipality | BERKS | MILEPOST | 223.54 | BECHTELSVILLE COMPRESSOR STATION | BECHTELSVILLE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | CHECK |  | WHEATLEY |  |  |  | 1988 | 1987 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 671 |  | NO | NO | [5 empty] | 0 | 0 | 44895 | 46713.007053905758665 | 621 | 1089.918367346938775510204081632653061224 | 70000 | 72834.62509797089 | 0 | 0 | 0 | 0 |  | 2.74 | 115516 | 53454.9824877388527415889212827988338192 | 120637.5505192235874405102040816326530612 | 0 | 0 | 0 | 0 | NO |  |  |  | 957 | 27738 | 1050 | 192.619(A)(2) |  | 1987-06-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 63360 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF THE LEAK WAS TOO MINIMAL TO BE DETERMINED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | O-RING FAILURE | [161 empty] | MICHAEL MCGRATH | PIPELINE PERFORMACE AND COMPLIANCE | michael.mcgrath@enbridge.com | (612)805-6542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan atanu | AT APPROXIMATELY 8:30 AM EDT ON SEPTEMBER 28, 2020 AN ENBRIDGE CONTRACTOR DISCOVERED A NATURAL GAS LEAK BELOW GROUND AT THE BECHTELSVILLE COMPRESSOR STATION ON THE TEXAS EASTERN TRANSMISSION (TETLP) SYSTEM IN BERKS COUNTY, PA. TETLP SUBSEQUENTLY PERFORMED ADDITIONAL INVESTIGATIONS BY PROBING HOLES AROUND THE SUSPECTED LEAK AREA. TETLP DETERMINED THAT THE SOURCE OF THE LEAK WAS FROM A CHECK VALVE ON 09/29/2020 AND DETERMINED COST OF REPAIR WILL EXCEED THE DOT INCIDENT REPORTING THRESHOLD ON 09/29/2020 AT APPROXIMATELY 2:50 PM EDT . TETLP IMMEDIATELY NOTIFIED THE NRC WITHIN ONE HOUR OF CONFIRMED DISCOVERY AT APPROXIMATELY 3:02 PM EDT. THE LINE WAS DEPRESSURIZED AND THE VALVE WAS EXCAVATED FOR INSPECTION. TETLP DETERMINED THAT THE VALVE SEALS WERE LEAKING AND REPLACED THE SEALS. THE LINE WAS RETURNED BACK TO SERVICE ON OCTOBER 6, 2020. THE APPARENT CAUSE OF THE LEAK WAS EQUIPMENT FAILURE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200115 | 35339 | 2020-10-29 12:57 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-09-30 04:28 | 2020 | EASTERN | NO | 44.7786 | -85.1223 | 1288774 | 2020-10-01 12:11 | 1288939 | NATURAL GAS |  | 7970 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | SHUT DOWN FACILITY WAS NOT REQUIRED AS TECHNICIAN WAS ABLE TO ISOLATE RELEASE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-09-30 06:05 | 2020-09-30 06:05 | ONSHORE | MI | 49646 | KALKASKA | KALKASKA | NOT APPLICABLE |  | ANR PIPELINE CO. RAPID RIVER 35 | BLUE LAKE AREA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | PRESSURE SAFETY VALVE (PSV) #9402 PREMATURELY ACTIVATED AUTOMATICALLY RELEASING GAS FROM PIPING. | CLASS 1 LOCATION | NO |  | 406 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 12752 | 22381.0612244897959183673469387755102041 | 1000 | 1040.494644256727 | 0 | 0 | 0 | 0 |  | 1.6 | 13752 | 15144.2742002437877172011661807580174927 | 23421.5558687465229183673469387755102041 | 0 | 0 | 0 | 0 | NO |  |  |  | 723 | 0 | 1050 | 192.619(A)(1) |  | 1979-10-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL CENTER DID NOT RECEIVE ANY ALARMS OR OTHER INDICATIONS THAT THERE WAS A RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | O-RING | [161 empty] | ROBERTA PRIMERA | US REGULATORY COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 248-561-7803 |  |  |  |  | LEE ROMACK | DIRECTOR PIPELINE REGULATOR COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | ON OCTOBER 1, 2020 AT 12:11 ( ALL TIMES ARE EASTERN STANDARD TIME) TC ENERGY/ANR PIPELINE COMPANY (ANR) REPORTED AN INCIDENT TO THE NATIONAL RESPONSE CENTER FOLLOWING THE UNINTENTIONAL RELEASE OF 7. 97 MILLION CUBIC FEET OF GAS TO THE ATMOSPHERE FROM THE RAPID RIVER 35 STORAGE FACILITY NEAR KALKASKA MICHIGAN. TECHNICIAN WAS CONTACTED BY GAS CONTROL BASED ON A NOISE COMPLAINT. TECHNICIAN CONFIRMED THERE WAS NOT AN OVER PRESSURE EVENT AND PROCEEDED TO ISOLATE PSV #9402. PSV #9402 IS A PILOT OPERATED VALVE ON A 4 INCH BRANCH CONNECTION THAT IS CONNECTED TO A 20 INCH PIPE. AFTER ISOLATING PSV #9402 THE TECHNICIAN REMOVED AND INSPECTED THE VALVE. AN O-RING WAS REPLACED AND THE PSV WAS PLACED INTO SERVICE ON THE SAME DAY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200116 | 35247 | 2020-11-02 17:58 | SUPPLEMENTAL FINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-10-04 07:41 | 2020 | CENTRAL | YES | 30.5665 | -94.9448 | 1288965 | 2020-10-04 08:27 | 1288967, 1289056 | NATURAL GAS |  | 118724 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-04 08:43 | 2021-04-14 13:08 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-10-04 08:05 | NO | [5 empty] | VALVE CLOSURE |  | 2020-10-04 08:24 | VALVE CLOSURE |  | 2020-10-04 08:43 | 0 | 2020-10-04 07:41 | 2020-10-04 08:05 | ONSHORE | TX | 77335 | GOODRICH | POLK | MILEPOST | 47.6 | GOODRICH INDEX 85 | CROSBY LAUNCHER TO GOODRICH RECEIVER | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 1 | NO | YES | [6 empty] | YES | UNCASED | TRINITY RIVER | UNKNOWN | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.485 | 60000 | API 5L | DSAW |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1982 | 1982 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | THE PIPE SEGMENT WITH THE RUPTURE ORIGIN WAS NOT ABLE TO BE RECOVERED SO ORIENTATION AND DIMENSION INFORMATION COULD NOT BE DETERMINED. APPROXIMATE SIZE INFORMATION BELOW WAS REQUIRED FOR SUBMITTAL OF REPORT. THE NUMBERS BELOW ARE NOT ACTUAL DIMENSIONS BUT PLACEHOLDERS. IN ADDITION, THE EXACT DEPTH-OF-COVER INFORMATION COULD NOT BE DETERMINED. DEPTH-OF-COVER INFORMATION WAS ALSO REQUIRED IN SECTION B10A. FOR SUBMITTAL OF THE REPORT. THE NUMBER INDICATED IN THIS FIELD IS ALSO A PLACEHOLDER. | 1 | 1 |  | CLASS 1 LOCATION | NO |  | 532 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 219639 | 385488.8571428571428571428571428571428571 | 3500000 | 3641731.2548985445 | 9267 | 9642.263868327089109 | 20000 | 20809.89288513454 | METALLURGICAL EVALUATION | 1.85 | 3748906 | 1872963.71999424092491524489795918367347 | 4057672.26879486327196614285714285714286 | 0 | 0 | 0 | 0 | NO |  |  |  | 926 | 165 | 1032 | 192.619(A)(2) |  | 1982-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 42346 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [306 empty] | SHELLEY DIETZ | PIPELINE ENGINEER | shelley_dietz@kindermorgan.com | [5 empty] | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON OCTOBER 4, 2020 THE KINDER MORGAN TEXAS PIPELINE (KMTP) 24-INCH INDEX 85 PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE WITH NO FIRE. THE SEQUENCE OF EVENTS IS BELOW. 7:41AM LANDOWNER 1 CALLED OPERATOR 1 SPEAKING ABOUT NOISE 7:44AM OPERATOR 1 BEGAN DISPATCH PROCESS 7:44AM LOW ALARM RECEIVED AT PIN 42680 4367 REGULATOR 7:47AM OPERATIONS SUPERVISOR CALLED OPERATOR 1 7:50AM LOW LOW PRESSURE ALARM RECEIVED AT NELSON CS, GAS CONTROL NOTIFIED OPERATOR 1 7:51AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 2 TO MLV 4364 7:52AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 3 TO THE PLANT 7:53AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 4 TO THE PLANT 7:54AM OPERATIONS SUPERVISOR DISPATCHED OPERATOR 5 TO MLV 4367 7:55AM OPERATIONS SUPERVISOR NOTIFIED OPERATIONS MANAGER 7:55AM GAS CONTROL RECEIVED NOTIFICATION FROM LANDOWNER 2 OF A RUPTURE NEAR NELSON CS/GOODRICH AREA 8:00AM OPERATIONS SUPERVISOR INITIATED ERL (EMERGENCY RESPONSE LINE) PROCESS. GAS CONTROL SENT ERL CALL @8:10 POSSIBLE LEAK AND NOTIFIED GAS CONTROL MANAGER ON CALL 8:01AM OPERATIONS SUPERVISOR DIRECTED OPERATOR 6 TO SHUT IN ALL VALVES TIED TO INDEX 85 AT THE PLANT 8:05AM OPERATOR 1 ARRIVED AT TRINITY RIVER BRIDGE. GAS WAS BLOWING FROM THE NORTH RIVER BANK. DPS TROOPER AND GOODRICH FIRE CHIEF WERE ON SITE. DPS HAD STOPPED ALL TRAFFIC ON US 59. 8:10AM OPERATOR 1 NOTIFIED OPERATIONS SUPERVISOR THAT DPS HAD SHUT DOWN BOTH SIDES OF HWY 59 AND RESIDENTS WERE BEING EVACUATED. (KMTP HAS NOT BEEN ABLE TO CONFIRM THAT EVACUATIONS WERE IN FACT ORDERED, SEE ANSWER TO A23.) 8:13AM GAS CONTROL SHUT IN DAYTON STORAGE 200 MMBTU INJECTION. 8:17AM OPERATIONS SUPERVISOR DISPATCHED PERSONNEL TO GOODRICH PLANT (OPERATOR 6), GOODRICH STATION (OPERATOR 1), HWY 223 MLBV (OPERATOR 5), AND PELICAN RD. MLBV (OPERATOR 2). 8:22AM GAS CONTROL NOTIFIED NGPL, MIDCOASTAL, AND TEJAS THAT THEY WERE GOING TO HAVE TO SHUT IN 8:24AM MLV 4367 AND REGULATOR 10IN BYPASSES CLOSED 8:27AM INITIAL REPORT MADE TO NRC (#1288965) 8:31AM GAS CONTROL SENT ERL+ CALL @ 8:40AM KMTP LINE RUPTURE 8:41AM PIN 41835 WELL CONNECT SUPPLYING GAS TO INDEX 85 SHUT IN BY OPERATOR 6 8:43AM OPERATOR 6 REPORTED INDEX 85 SHUT IN AT PLANT 8:51AM INDEX 85 BLOWN DOWN PER ONSITE FIELD PERSONNEL (OPERATOR 1) 9:40AM OPERATIONS CONFIRMED KMTP INDEX 85 24IN LINE RUPTURE LOCATED ON THE NORTH BANK OF THE TRINITY RIVER AND SOUTH OR SUCTION SIDE OF NELSON CS. OPERATIONS SHUT IN MLBV HWY 223 AND NELSON CS SHUT IN. 9:47AM GAS CONTROL SENT ERL + UPDATE INFO ONLY, LINE ISOLATED, INVESTIGATION UNDERWAY. REPORTABLE TO NRC AND TRRC GAS VOLUME LOSS. ALL THE PIECES OF PIPE SURROUNDING THE ORIGIN PIPE WERE FOUND, ANALYZED, AND WERE WITHIN APPLICABLE SPECIFICATIONS. IN ADDITION THERE WERE NO OPERATING OR MAINTENANCE DEFICIENCIES IDENTIFIED. A DEFINITIVE METALLURGICAL ROOT CAUSE OF THE FAILURE COULD NOT BE DETERMINED BECAUSE THE PIECE OF PIPE CONTAINING THE ORIGIN OF THE RUPTURE WAS NOT FOUND DESPITE AN EXTENSIVE SEARCH. WHILE NO DEFINITIVE ROOT CAUSE WAS DETERMINED, USING THE GEOLOGICAL, METEOROLOGICAL, SITE-GATHERED DATA AND HISTORICAL DATA, KINDER MORGAN TEXAS PIPELINE (KMTP) CONDUCTED EXTENSIVE COMPUTER MODELING AND IDENTIFIED EARTH MOVEMENT OF THE SOIL SURROUNDING THE PIPE AS THE MOST PLAUSIBLE CAUSE OF THE RUPTURE. ALTHOUGH EVIDENCE OF CIRCUMFERENTIAL SCC WAS NOT OBSERVED IN THE ILI DATA REVIEW OR METALLURGICAL ANALYSIS PERFORMED ON THE AVAILABLE PIPE, IT CANNOT BE DEFINITIVELY RULED OUT AS A PLAUSIBLE CONTRIBUTING FACTOR OR CAUSE OF THE FAILURE. THE REPAIR AND REPLACEMENT TEAM HAS DETERMINED THAT THE REPAIR OF THE KMTP INDEX 85 PIPE BY THE HORIZONTAL DIRECTIONAL DRILLING METHOD (HDD) SHOULD PREVENT A REOCCURRENCE OF THE FAILURE DUE TO POTENTIAL EARTH MOVEMENT. THE HDD WAS COMPLETED ON APRIL 12, 2021 AND THE PIPELINE WAS RETURNED TO SERVICE ON APRIL 14, 2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200117 | 34472 | 2020-11-04 10:36 | ORIGINAL FINAL | 38932 | BLUESTONE PIPELINE COMPANY OF PA, LLC | 500 WOODWARD AVE. SUITE 2900 | DETROIT | MI | 48226 | 2020-10-05 11:30 | 2020 | EASTERN | YES | 41.983 | -75.547 | 1289015 | 2020-10-05 12:13 | 1289039 | NATURAL GAS |  | 14600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-10-05 08:20 | 2020-10-05 08:50 | ONSHORE | PA | 18847 | Not Within a Municipality | SUSQUEHANNA | NOT APPLICABLE |  | BLUESTONE OF PA | HARMONY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | 2015 | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF THE REGULATOR RESULTED IN THE OPERATION OF AN OVER PRESSURE PROTECTION DEVICE TO OPERATE AND VENTED GAS TO ATMOSPHERE | CLASS 1 LOCATION | NO |  | 712 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 40004 | 70211.1020408163265306122448979591836735 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.74 | 40004 | 46068.7463556851311953352769679300291545 | 70211.1020408163265306122448979591836735 | 0 | 0 | 0 | 0 | NO |  |  |  | 170 | 0 | 220 | 192.619(A)(2) |  | 2015-03-09 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA SENSING ON THAT LEG OF THE FUEL SKID | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [24 empty] | YES | [163 empty] | PATRICK J RAICHEL | SUPERVISOR - CODES AND COMPLIANCE | patrick.raichel@dteenergy.com | 716-327-6630 |  | MICHAEL GRAVES | michael.graves@dteenergy.com | 212-303-0722 | PHILIP COLEMAN | DIRECTOR - CODES AND REGULATORY | 7347304870 | philip.coleman@dteenergy.com | AT APPROXIMATELY 0435 HOURS ON SATURDAY OCT. 3, 2020, A FAILURE OF THE WORKING MONITOR REGULATOR SET UP ON THE FUEL GAS SKID AT HARMONY STATION RESULTED IN THE OPERATION OF THE OVER PRESSURE PROTECTION DEVICE IMMEDIATELY DOWNSTREAM. THIS RESULTED IN THE RELEASE OF 14.6 MMCF OF NATURAL GAS OVER THE NEXT TWO DAYS. THE RELEASE OF GAS WAS SECURED UPON ITS DISCOVERY ON THE MORNING OF MONDAY, OCTOBER 5TH. INTERNAL INVESTIGATION OF THE EVENT DETERMINED THE LIKELY CAUSE OF THE REGULATOR FAILURE WAS EXCESSIVE CYCLING (CHATTERING) OF THE REGULATOR LEADING TO A PREMATURE FAILURE OF THE INTERNAL SOFT COMPONENTS. ENGINEERING IS EVALUATING A CHANGE OF DESIGN AND/OR COMPONENTS TO PREVENT REOCCURRENCE.
2023-02-28 09:42 | NO | NO | UNGS (Underground Natural Gas Storage) | 20200118 | 34517 | 2020-11-05 14:58 | SUPPLEMENTAL FINAL | 32396 | BOBCAT GAS STORAGE (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2020-10-09 20:30 | 2020 | CENTRAL | YES | 30.542 | -91.9156 | 1289408 | 2020-10-09 22:00 | 1289485 | NATURAL GAS |  | 2718 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-09 20:30 | 2020-10-11 21:30 |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-09 20:30 | 2020-10-09 20:30 | ONSHORE | LA | 70577 | Not Within a Municipality | ST. LANDRY | NOT APPLICABLE |  | BOBCAT GAS STORAGE | BOBCAT GAS STORAGE | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 2008 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUTDOWN SYSTEM (ESD) | CLASS 1 LOCATION | NO |  | 804 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 7475 | 13119.3877551020408163265306122448979592 | 0 | 0 | 5000 | 5202.473221283635 | 0 | 0 |  | 2.75 | 12475 | 10903.3680857670435422740524781341107872 | 18321.8609763856758163265306122448979592 | 0 | 0 | 0 | 0 | NO |  |  |  | 920 | 0 | 3395 | 192.619(A)(2) |  | 2014-02-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE ESD WAS THE RESULT OF COMMERCIAL POWER LOSS AS RESULT OF HURRICANE DELTA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | BACKUP GENERATOR FAILED TO START WITH LOSS OF COMMERCIAL POWER. |  |  |  |  | YES | [173 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 612-805-6542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 8:30 PM CDT ON OCTOBER 9, 2020, BOBCAT STORAGE LLC'S (BOBCAT STORAGE) FACILITY LOST COMMERCIAL DUE TO HURRICANE DELTA. FOLLOWING THE LOSS OF COMMERCIAL POWER, THE BACKUP GENERATOR FAILED TO START. AS A RESULT, THE STATION SHUT IN AND CAVERN 5 TOP SIDE VENTED (188 MSCF). AT APPROXIMATELY 12:17 AM CDT ON OCTOBER 10, 2020, THE ESD BATTERIES HAD DRAINED AND THE REMAINING TOPSIDE CAVERN'S VENTED (2530 MSCF). THE TOTAL GAS VENTED FROM THE STATION WAS 2718 MMCF. AN ADDITIONAL GENERATOR WAS BROUGHT TO SITE AND THE STATION WAS RETURNED TO NORMAL OPERATION ON OCTOBER 11, 2020. THERE WERE NO DELIVERIES OR RECEIPTS FLOWING TO ANY CUSTOMERS AT THE TIME OF THE COMMERCIAL POWER OUTAGE. A NEW BACKUP GENERATOR(S) WILL BE PURCHASED AND INSTALLED TO MITIGATE A SIMILAR EVENT. PART D.3. IS THE LARGEST PIR ASSOCIATED WITH THE PIPING AT THE STATION. PART E.2.A-C IS THE MAOP OF THE PIPE ASSOCIATED WITH THE LARGEST PIR.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20200119 | 34904 | 2020-11-06 13:11 | SUPPLEMENTAL FINAL | 39352 | GENESIS OFFSHORE HOLDINGS, LLC | 811 LOUISIANA ST. SUITE 1200 | HOUSTON | TX | 77002 | 2020-10-11 13:00 | 2020 | CENTRAL | YES | 28.0974 | -93.5021 | 1289495 | 2020-10-11 14:34 | 1289544 | NATURAL GAS |  | 25846 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-10-12 18:00 | NO | [11 empty] | 0 | 2020-10-11 12:00 | 2020-10-12 12:30 | OFFSHORE | [6 empty] | HI 330 | PLATFORM | [20 empty] | 255 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HIGH ISLAND | 330 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 | NO | 0.5 | 60000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | STELCO | ASPHALT |  | UNKNOWN | [26 empty] | 1977 | 1976 | CARBON STEEL |  | OTHER | [8 empty] | PIPE WAS SEVERED. | CLASS 1 LOCATION | NO |  | 1138 |  | NO | YES | [5 empty] | 0 | 0 | 0 | 0 | 54277 | 95261.6734693877551020408163265306122449 | 100000000 | 104049464.4256727 | 0 | 0 | 0 | 0 |  | 2.1 | 100054277 | 45965144.26636127900874635568513119533528 | 104144726.099142087755102040816326530612 | 0 | 0 | 0 | 0 | NO |  |  |  | 705 | 0 | 1440 | 192.619(A)(1) |  | 1977-08-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | OFFSHORE GATHERING | YES | YES | NO | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A NATURAL DISASTER. CONTROLLER ACTION HAD NO CAUSE IN THE EVENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS |  |  |  |  | ,,, | YES | YES | [305 empty] | JORGE MORICE | PIPELINE COMPLIANCE SPECIALILST | jorge.morice@genlp.com | 7137251663 |  | NORMAN GIBSON | norman.gibson@genlp.com | 9857463981 | JOHN JEWETT | SR. MANAGER DOT COMPLIANCE | 7138602605 | john.jewett@genlp.com | HURRICANE DELTA PASSED THROUGH THE HIGH ISLAND AREA OF THE GOM BETWEEN 10/8 AND 10/10. GENESIS OFFSHORE FACILITIES WERE EVACUATED ON 10/6, PRIOR TO THE PASSING OF THE HURRICANE. SCADA ALSO SHOWS THAT COMMUNICATIONS WERE LOST TO HI 330 ON 10/6. ON 10/11 A PATROL HELICOPTER WAS SENT TO PATROL THE AREA FOR STATUS IDENTIFICATION. AT 1:00PM THE OFFSHORE PIPELINE MANAGER FOR HIOS RECEIVED A PHONE CALL FROM HI 264 THAT THE PLATFORM ON HI 330A WAS NOT VISIBLE ABOVE THE WATER SURFACE. WHAT REMAINS OF THE STRUCTURE IS THE FOUR LEGS AT VARYING HEIGHTS ABOVE THE WATER SURFACE. NRC CALL WAS MADE AND THE COMPANY HAS WORKED WITH SEVERAL AGENCIES INCLUDING BSEE, PHMSA, AND USCG IN THE DISSEMINATION OF INVESTIGATION DATA. THE DOT ASSETS THAT WERE AFFECTED BY THIS INCIDENT IS A 24" NATURAL GAS PIPELINE FROM HI 370 TO HI 330 AND A 30" HI 330 TO HI 343. THIS REPORT INCLUDES THE PIPE INFORMATION FOR THE 30" HI 330 TO HI 343. BOTH PIPELINES WERE SEVERED ABOVE THE WATER SURFACE. PART A, QUESTION 7: FOR CLARIFICATION THE HIOS 30" HAS A NATURAL GAS VOLUME LOST OF 19,054 MCF AND THE HIOS 24" HAS A NATURAL GAS VOLUME LOST OF 6,792 MCF. THE VOLUME ENTERED IN THIS QUESTION IS THE SUM OF THE VOLUME LOST IN BOTH PIPELINES. PART D, QUESTION 7: DUE TO THE MAGNITUDE OF THE ASSETS LOST, GENESIS IS STILL CALCULATING THE COST OF DAMAGE. SUPPLEMENTAL (2/24/2021): DUE TO THE AFFECTS OF THE HIOS ASSETS (HIA330M PLATFORM/24" PIPELINE/30" PIPELINE) CAUSED BY HURRICANE DELTA, ALL OF THE AFOREMENTIONED ASSETS WILL NOT BE RE-BUILT NOR RETURNED TO SERVICE. ORIGINAL CONSTRUCTION COSTS WERE INCURRED ALMOST 50 YEARS AGO AND THOSE ASSOCIATED COSTS ARE NO LONGER AVAILABLE. A VERY HIGH LEVEL ESTIMATE IN TODAY'S NUMBERS COULD BE AS MUCH AS 100 MILLION PLUS DOLLARS.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20200120 | 36519 | 2020-11-11 16:28 | SUPPLEMENTAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-11 14:55 | 2020 | CENTRAL | YES | 28.0973 | -93.5027 | 1289546 | 2020-10-12 11:51 | 1289549 | NATURAL GAS |  | 63214 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | PIPELINE WAS ALREADY IN IDLE STATUS AND THERE WAS NO FLOW FROM THE PLATFORM. |  | VALVE CLOSURE |  | 2020-10-12 10:00 | 0 | 2020-10-11 14:55 | 2020-10-12 10:00 | OFFSHORE | [6 empty] | 24" 100 LINE | 4813 | [20 empty] | 255 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | HIGH ISLAND | 330 | PLATFORM | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 | NO | 0.5 | 60000 | X60 | SINGLE SAW |  | UNKNOWN | OTHER | CONCRETE | UNKNOWN | [26 empty] | 1977 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 75.4 | 24 |  | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 141599 | 248520.6938775510204081632653061224489796 | 0 | 0 | 0 | 0 | 100000 | 104049.4644256727 | ESTIMATED COSTS UNKNOWN UNTIL RECOVERY PLAN IS FULLY DEVELOPED AND IMPLEMENTED. | 2.24 | 241599 | 208968.5424733583635568513119533527696793 | 352570.1583032237204081632653061224489796 | 0 | 0 | 0 | 0 | NO |  |  |  | 720 | 0 | 1250 | 192.619(A)(1) |  | 1983-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  | MANUAL | 211147 | NO | YES | YES | YES |  |  |  |  | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | GENESIS OPERATOR OF PLATFORM HI 330 |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURAL ENVIRONMENTAL FACTORS. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ,,,,,,CATEGORY 3 HURRICANE DELTA | YES | YES | [268 empty] | YES | [36 empty] | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | todd.nardozzi@energytransfer.com | 7139897126 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 7139897126 | todd.nardozzi@energytransfer.com | THE HI 330 PLATFORM WAS COMPLETELY DESTROYED BY HURRICANE DELTA ON OCTOBER 11TH, 2020. THE CATEGORY 3 STORM IMPACTED THE AREA WITH 125MPH + WINDS AND 10-25 FT WAVES. THE 24" PIPELINE HAD BEEN SHUTDOWN PRIOR TO THE STORM DUE TO PRODUCERS NOT HAVING COME BACK ONLINE YET FROM PRIOR STORMS IN THE GULF. UPON INSPECTION OF THE HI-330 PLATFORM ON OCTOBER 12TH, 2020 AND NOTING THE 24" FAILURE, THE DOWNSTREAM VALVE WAS CLOSED AND THE LINE ISOLATED. A RECOVERY PLAN IS STILL BEING DEVELOPED AND EVALUATED. SUPPLEMENTAL REPORT 11/12/2020 - CLARIFICATION ON A22: NO ACTIONS TAKEN UPSTREAM OF FAILURE. ET OWNERSHIP BEGINS AT HI 330 AND ALL UPSTREAM LINES WERE SEVERED DUE TO HURRICANE DAMAGE. ONLY THE DOWNSTREAM VALVE WAS SHUT IN. - UPDATED RESPONSES TO E6, AND E7. SUPPLEMENTAL/FINAL REPORT 05/03/2021 STINGRAY PIPELINE COMPANY 24" PIPELINE REMAINS ISOLATED AT THIS TIME AND WILL BE ABANDONED IN PLACE. STINGRAY PIPELINE DOES NOT HAVE A FIRM TIMELINE ON REMOVAL OF HI-A330 AS THAT PLATFORM BELONGS TO GENESIS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200121 | 34543 | 2020-11-17 12:03 | ORIGINAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-19 06:02 | 2020 | MOUNTAIN | YES | 32.5324 | -103.8093 | 1290106 | 2020-10-19 07:44 | 1290280 | NATURAL GAS |  | 7894 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-18 08:22 | 2020-10-18 08:35 |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-18 08:11 | 2020-10-18 08:15 | ONSHORE | NM | 88220 | CARLSBAD | LEA | MILEPOST | 79.4 | WT-1 CARLSBAD COMPRESSOR STATION | NMBW119 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1960 | 1959 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPERATION - MALFUNCTION OF RELIEF VALVE DUE TO CONTROL PILOT. | CLASS 1 LOCATION | NO |  | 526 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 4736 | 8312.163265306122448979591836734693877551 | 0 | 0 | 500 | 520.2473221283635 | 0 | 0 |  | 0.6 | 5236 | 5683.50736251256441253644314868804664723 | 8832.410587434485948979591836734693877551 | 0 | 0 | 0 | 0 | NO |  |  |  | 988 | 423 | 1008 | 192.619(C) |  | 1960-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A RELIEF VALVE FAILURE WAS THE CAUSE OF THE GAS RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | SHORTER THAN NORMAL LIFE OF THE PARTS IN THE PILOT THAT CONTROLS THE RELIEF VALVE. | [22 empty] | YES | RELIEF VALVE PILOT FAILURE. | [161 empty] | KATHRYN HARRYMAN |  | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI |  | 713-989-7126 | todd.nardozzi@energytransfer.com | 08:11 MTN, OCTOBER 18TH TECHNICIAN CONTACTED GAS CONTROL TO NOTIFY THEM OF GAS BLOWING. AT 08:22 MTN ISOLATED RELIEF VALVE THEN TESTED AND FOUND THAT THE RELIEF CONTROL PILOT WOULD NOT HOLD A SET POINT. REPLACED WITH SPARE RELIEF CONTROL PILOT, RETESTED AND SET PRESSURE. 08:35 MTN, RESTARTED UNITS AND FOUND THAT EVERYTHING WAS BACK TO NORMAL. 06:46 MTN, OCTOBER 19TH ROUGH CALCULATION OF GAS VOLUME LOSS WAS COMPLETED, NOTIFIED REGULATORY. 07:44 MTN, OCTOBER 19TH NRC NOTIFICATION WAS MADE NRC #1290106. 06:08 MTN, OCTOBER 21ST 48 HOUR NRC NOTIFICATION WAS MADE NRC #1290280, UPDATED GAS VOLUME.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200122 | 34935 | 2020-11-19 16:59 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-11-07 11:30 | 2020 | EASTERN | YES | 46.4958 | -88.7313 | 1291637 | 2020-11-07 11:41 | 1291732 | NATURAL GAS |  | 1958 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE INCIDENT WAS A SMALL LEAK THAT DID NOT REQUIRE TO BE SHUT DOWN. |  |  |  | YES | OPERATOR | 2020-11-07 13:00 | NO | [5 empty] | OPERATIONAL CONTROL | WAKEFIELD COMPRESSOR STATION LOWERED PRESSURE |  | OPERATIONAL CONTROL | MONITORED PRESSURE AT BLOCK VALVE 5 |  | 0 | 2020-11-03 15:05 | 2020-11-04 20:00 | ONSHORE | MI | 49961 | Not Within a Municipality | HOUGHTON | MILEPOST | 63.5 | WAKEFIELD TO MARQUETTE | M433B | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 16 |  | 0.203 | 60000 | API-5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | YOUNGSTOWN | COLD APPLIED TAPE |  | UNKNOWN | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 339 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 4229 | 7422.326530612244897959183673469387755102 | 206646 | 215014.056257075607642 | 688146 | 716012.227466689658142 | 0 | 0 |  | 2.16 | 899021 | 415603.2699221486284959300291545189504373 | 938448.6102543775106819591836734693877551 | 0 | 0 | 0 | 0 | NO |  |  |  | 782 | 60000 | 945 | 192.619(A)(2) |  | 1965-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 107557 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | A CRACK IN THE GIRTH WELD APPROXIMATELY 80% OF THE WALL THICKNESS | [12 empty] | YES | [8 empty] | 1202 | [54 empty] | YES |  |  |  |  | YES | [44 empty] | 2018 | FREE SWIMMING | 2014 | FREE SWIMMING | [10 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | J. DAVID CULLISON | SR. PIPELINE SAFETY ENGINEER | j.cullison@nngco.com | 402-398-7439 |  |  |  |  | TOM CORRELL | VICE PRESIDENT OF PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | ON 11/4/20, A CONTRACTOR WAS EVALUATING THE RIGHT-OF-WAY AND DISCOVERED BUBBLES. LEAK DETECTION FOUND VERY LIMITED AMOUNT OF GAS DETECTED. OPERATIONS CONFIRMED THIS LOCATION HAD A LEAK IN 2017 THAT WAS REMEDIATED WITH A PIPE REPLACEMENT AND ANTICIPATED THE EXISTING STOPPLE MAY BE LEAKING. A STOPPLE TECHNICIAN REPLACED THE BLEED VALVE ON THE STOPPLE AND THE LEAK WAS NO LONGER DETECTED. IT WAS CONFIRMED 11/5/20 AT 0800 HOURS THE LEAK HAD BEEN REMEDIATED. ON 11/6/20, A CONTRACTOR HEARD BUBBLES NEAR THE EDGE OF THE EXCAVATION THAT APPEARED TO BE MIGRATING FROM A SEPARATE LOCATION. HAND EXCAVATION FOUND A GIRTH WELD WAS THE SOURCE OF THE LEAK NOW DETECTED. A TECHNICIAN ARRIVED ON 11/7/20 TO INSTALL A CLAMP TO REMEDIATE THE LEAK. IT WAS DETERMINED THAT CLEARING OFF THE COATING AND PREPARING THE PIPE FOR A CLAMP THAT IT WOULD BE SAFER TO PERFORM A STOPPLE BYPASS. ONCE THIS WAS DETERMINED, THE NRC WAS NOTIFIED AS THE REPAIR WOULD EXCEED THE REPORTING THRESHOLD. A STOPPLE CREW ARRIVED ON SITE 11/9/20. THE PIPE WAS ON BYPASS AT 1103 ON 11/10/20. THE REPAIRS WHERE MADE AND THE PIPE WAS RETURNED TO SERVICE AT 1213 ON 11/11/20. METALLURGICAL EVALUATION DETERMINED THAT THE AMOUNT OF CORROSION PRESENT ON THE SURFACE AS WELL AS THE 80% OF THE WALL THICKNESS, TRANS GRANULAR BRITTLE FRACTURING THE CRACK, POSSIBLY OCCURRED DURING OR SHORTLY AFTER WELDING THE TWO JOINTS OF PIPE, WHICH PRESENTED THE LOCATION OF THE FAILURE POINT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200123 | 34792 | 2020-11-20 12:58 | SUPPLEMENTAL FINAL | 19580 | TRANSCOLORADO GAS TRANSMISSION COMPANY LLC | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2020-10-27 12:45 | 2020 | MOUNTAIN | YES | 37.3484 | -108.2041 | 1290817 | 2020-10-27 13:43 | 1290916 | NATURAL GAS |  | 3820 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-26 18:25 | 2020-10-29 10:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-26 18:25 | 2020-10-26 19:12 | ONSHORE | CO | 81328 | Not Within a Municipality | MONTEZUMA | MILEPOST | MP 242 | TRANSCOLORADO MAINLINE/MANCOS COMPRESSOR STATION | DOLORES TO RED MESA | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BLOWDOWN FROM THE VENT VALVE. | CLASS 1 LOCATION | NO |  | 545 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 6876 | 12068.0816326530612244897959183673469388 | 0 | 0 | 500 | 520.2473221283635 | 0 | 0 |  | 1.8 | 7376 | 8147.938849393030884839650145772594752187 | 12588.3289547814247244897959183673469388 | 0 | 0 | 0 | 0 | NO |  |  |  | 960 | 63218 | 1287 | 192.619(A)(2) |  | 2004-06-22 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTOLLER ACTIONS WERE NOT DETERMINED TO CAUSE THE ESD OR GAS RELEASE FROM VENT PIPING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | BUILDUP OF WATER-ICE IN ESD VENT VALVE SUPPLY PIPING REDUCING PRESSURE REQUIRED TO KEEP THE ESD VENT VALVE SHUT. | [13 empty] | YES | [8 empty] | YES | WATER VAPOR IN DRIED AIR SYSTEM ENDPOINT DEVICES. PERIOD PURGING REQUIRED. | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | 719 351-4199 |  | MIKE JOHNSON | mike_johnson2@kindermorgan.com | 505 632-6042 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON 10/26/2020 AT 18:25 LOCAL TIME, THE TRANS COLORADO GAS TRANSMISSION COMPANY LLC (TCP)- MANCOS COMPRESSOR STATION EXPERIENCED AN UNPLANNED ESD EVENT. UNIT 380 WAS ONLINE AT THE TIME OF THE ESD AND SHUT DOWN. WHEN THE LOCAL OPERATION'S TECHNICIAN ARRIVED ON SITE AT 19:12 LOCAL TIME THAT DAY, THE STATION COMPRESSOR UNIT NOS. 380 AND 381 WERE BOTH OBSERVED TO BE OFF-LINE AND BLOWN-DOWN AS DESIGNED BY THE STATION AUTOMATION SYSTEM. THE ON-SITE GENERATOR UNIT 382 WITH FUEL SYSTEM WAS ALSO COMPLETELY BLOWN-DOWN. THE OPERATION'S TECHNICIAN ALSO CONFIRMED THE STATION YARD PIPING WAS FULLY BLOWN DOWN WITH THE SUCTION SIDE ESD VENT VALVE STUCK IN TRANSITION BETWEEN THE CLOSED AND OPEN POSITIONS. SIDE GATE VALVES WITH THE MAINLINE PIPE WERE IN THE CLOSED POSITION. THE TOTAL ESTIMATED GAS LOSS WAS 184 MSCF AND CALCULATED USING STATION PIPE VOLUME AND PRESSURE AND DETERMINED NOT TO BE A REPORTABLE EVENT SINCE A REPORTABLE QUANTITY HAD NOT BEEN EXCEEDED. WHILE INVESTIGATING THE IMMEDIATE CAUSE, THE OPERATION'S TECHNICIAN OBSERVED THE DISCHARGE SIDE ESD VENT VALVE IN THE CLOSED POSITION. THE EXPECTED POSITION OF THE ESD VENT VALVES AFTER A STATION ESD IS FULL OPEN. PER KINDER MORGAN PROCEDURES, A STATION ESD THAT RESULTS IN A RELEASE OF NATURAL GAS UNDER THE PHMSA REPORTING THRESHOLD FOR NATURAL GAS MUST BE INVESTIGATED AS AN ABNORMAL OPERATION. THE INITIAL INVESTIGATION FOUND ICE PRESENT IN THE PNEUMATIC SYSTEM THAT CONTROLS THE STATIONS TWO MAIN ESD VENT VALVES. OPERATIONS DECIDED TO LEAVE THE STATION DOWN AND RESUME THE INVESTIGATION THE FOLLOWING DAY SINCE THE AMBIENT TEMPERATURES WERE BELOW FREEZING AND IT WAS BECOMING TOO DARK TO WORK SAFELY. ADDITIONAL INVESTIGATION ON 10/27/2020 REVEALED THAT THE SUCTION SIDE ESD VENT VALVE OPENED PRIOR TO THE ESD AT 16:59:08 ON 10/26/2020, ABOUT 86 MINUTES PRIOR TO THE ESD EVENT. BASED ON THIS INFORMATION, AT 12:45 LOCAL TIME, IT WAS DETERMINED THAT GAS LOSS VOLUMES EXCEEDED THE REPORTABLE THRESHOLD OF 3,000 MSCF. AT 13:05 LOCAL TIME ON 10/27/2020, CONFIRMATION OF DISCOVERY THAT A REPORTABLE INCIDENT WAS IMMEDIATELY REPORTED TO THE NRC AT 13:43 LOCAL TIME. THE INVESTIGATION TEAM CONCLUDED THAT THE BUILDUP OF WATER OVER TIME FROZE AND BLOCKED THE SUPPLY OF AIR TO THE SUCTION-ESD BLOWDOWN VENT VALVE OPERATOR, THEREBY REDUCING THE PRESSURE REQUIRED TO KEEP THE SUCTION-ESD VENT VALVE SHUT AND ALLOWING IT TO OPEN SLOWLY AND RELEASE GAS. ONCE THE SUCTION-ESD VALVE OPENED FAR ENOUGH, IT ACTIVATED THE "OPEN" LIMIT SWITCH ON THE SUCTION-ESD BLOWDOWN VALVE AND ALONG WITH SENSING FLOW WITHIN THE ESD VENT PIPING RESULTING IN A FULL STATION ESD. THE ROOT CAUSE OF THE EVENT WAS DETERMINED TO BE FAILURE TO REALIZE THAT END-POINT DEVICES ON A DRIED AIR SYSTEM STILL REQUIRE PERIODIC PURGING/DRAINING TO PREVENT ACCUMULATION OF WATER OVER EXTENDED PERIODS OF TIME. TCP IS WORKING TO IMPLEMENT ADDITIONAL MAINTENANCE PROCEDURES FOR REGULAR PURGING AND DRAINING OF ESD PIPING/ENDPOINT DEVICES ON INSTRUMENT AIR SYSTEMS AND ENTER THEM INTO OUR OPERATION\MAINTENANCE WORK-TRACKING SYSTEM. TCP PLANS TO EVALUATE OTHER STATIONS ON THE TCP SYSTEM TO DETERMINE IF PURGING AND DRAINING MAINTENANCE OF ESD PIPING/ENDPOINT DEVICES IS REQUIRED TO MINIMIZE THE POTENTIAL FOR A REOCCURRENCE OF THIS TYPE OF EVENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200124 | 36399 | 2020-11-23 16:36 | SUPPLEMENTAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-28 00:05 | 2020 | CENTRAL | YES | 31.1169 | -88.0122 | 1290975 | 2020-10-29 13:00 | 1291048 | NATURAL GAS |  | 84000 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | LOST POWER DUE TO HURRICANE ZETA |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-28 22:00 | 2020-10-28 23:59 | ONSHORE | AL | 36560 | MOUNT VERNON | MOBILE | MILEPOST | 190.8 | COMPRESSOR STATION 11 MOUNT VERNON | MSMEA -24 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | FILTER/STRAINER/SEPARATOR | [38 empty] | 2019 | 2019 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | OTHER | ACTUATOR FILTER CLOGGED | [5 empty] | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO |  |  | YES |  | YES | 0 | 0 | 0 | 0 | 261240 | 458502.8571428571428571428571428571428571 | 100 | 104.0494644256727 | 2000 | 2080.989288513454 | 0 | 0 |  | 3.11 | 263340 | 301808.8533715323623693877551020408163265 | 460687.8958957962695571428571428571428571 | 0 | 0 | 0 | 0 | NO |  |  |  | 784 | 250 | 973 | 192.619(C) |  | 1958-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOSS OF POWER DUE TO HURRICANE ZETA ESD'D THE COMPRESSOR STATION, CONTROLLERS HAD NO PART IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | POWER GAS FILTER CLOGGED PREVENTING PROPER OPERATION OF SIDE VALVE. |  |  |  |  | YES | [173 empty] | KATHIE HARRYMAN |  | kathie.harryman@sbcglobal.net | 7139897085 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 7139897126 | todd.nardozzi@energytransfer.com | 10/28/20, 22:00 CST - COMPRESSOR STATION 11 LOST POWER DUE TO HURRICANE ZETA CAUSING THE STATION TO ESD WHEN A SIDE VALVE DID NOT SHUT. 10/28/20, 23:59 CST - THE PIPELINE TECHNICIAN MANUALLY OPERATED THE VALVE WITH HAND PUMP CLOSING THE VALVE. UPON INVESTIGATION THE PIPELINE TECHNICIAN CHECKED THE POWER GAS FILTER AND FOUND IT TO BE CLOGGED WITH GREASE NOT ALLOWING GAS TO OPERATE THE VALVE. ONCE THE GREASE WAS DISCOVERED IN THE FILTER THE TECHNICIAN CHANGED THE FILTER, TOOK ALL TUBING OFF CLEANING IT OUT. ALSO CLEANED ALL THE GREASE OUT OF THE POWER GAS LINE BACK TO THE 2" PLUG VALVE THEN RESTARTED UNITS AND FOUND THAT EVERYTHING WAS BACK TO NORMAL. 2/26/22 UPDATE - UPDATED SUB CAUSE TO "OTHER EQUIPMENT FAILURE".
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20200125 | 34563 | 2020-11-24 08:44 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2020-10-28 13:35 | 2020 | CENTRAL | NO | 30.6737 | -89.9991 | 1290892 | 2020-10-28 14:47 | 1290953 | NATURAL GAS |  | 598 | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS NEVER SHUT DOWN. ONLY TAP VALVE TO CUSTOMER'S METER |  |  |  | YES | OPERATOR | 2020-10-28 13:41 | YES | 2020-10-28 13:15 | ALLOWED TO BURN OUT |  | 598 | NO | VALVE CLOSURE |  | 2020-10-28 14:33 | OPERATIONAL CONTROL | DOWNSTREAM VALVE WAS BROKEN OFF. |  | 0 | 2020-10-28 13:15 | 2020-10-28 13:41 | ONSHORE | LA | 70427 | Not Within a Municipality | WASHINGTON | MILEPOST | 1.969 | INDEX 301-4-2-14 | FRANKLINTON 4" LINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | METER | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VEHICLE ACCIDENT CAUSED TRUCK TO LEAVE ROAD AND STRIKE 1" RISER BREAKING RISER BELOW GROUND. | CLASS 2 LOCATION | NO |  | 90 |  | NO | NO | NO | VEHICLE ACCIDENT THAT RESULTED IN A DEATH DUE TO ACCIDENT IMPACT AND NOT FROM FIRE FROM PIPELINE THAT WAS ALSO IMPACTED. |  |  |  | 0 | 0 | 0 | 0 | 1256 | 2204.408163265306122448979591836734693878 | 5200 | 5410.5721501349804 | 500 | 520.2473221283635 | 0 | 0 |  | 2.1 | 6956 | 4062.864399115537509912536443148688046647 | 8135.227635528650022448979591836734693878 | 0 | 0 | 1 | 0 | NO |  |  |  | 374 | 1000 | 715 | 192.619(A)(2) |  | 2019-05-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 55 | NO | [5 empty] | YES | NO PIG TRAPS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | ROADWAY | 22 | YES |  |  | YES | [235 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON OCTOBER 28, 2020 AT APPROXIMATELY 13:15, GULF SOUTH'S GAS CONTROL RECEIVED A CALL REPORTING A WRECK ON HIGHWAY 16 IN ISABEL, LOUISIANA THAT INVOLVED A PIPELINE AND FIRE. GAS CONTROL DISPATCHED LOCAL OPERATIONS PERSONNEL AND, AFTER NOTICING A SLIGHT PRESSURE DROP FOLLOWED BY AN INCREASED FLOW AT MANDEVILLE JUNCTION, LOWERED THE PRESSURE ON THE NEAREST REGULATOR. AT APPROXIMATELY 13:41 GULF SOUTH PERSONNEL WERE ONSITE. IT WAS NOT IMMEDIATELY CLEAR WHETHER GULF SOUTH ASSETS WERE IMPACTED BECAUSE BOTH GULF SOUTH AND CENTERPOINT HAVE FACILITIES IN THE IMMEDIATE AREA; THE AREA MANAGER COORDINATED WITH CENTERPOINT PERSONNEL TO IDENTIFY WHICH ASSETS WERE INVOLVED. IN THIS AREA, GULF SOUTH'S INDEX 301-4-2-14 RUNS PARALLEL TO HIGHWAY 16. A 1-INCH LINE FROM INDEX 301-4-2-14 CROSSES HIGHWAY 16 AND FEEDS A CENTERPOINT METER. AT 14:00, THE AREA MANAGER REPORTED THAT THE ACCIDENT INVOLVED A FATALITY AND THAT THEY WERE DIGGING DOWN TO THE VALVE TO SHUT OFF GAS FLOW. AT 14:33 GULF SOUTH TAP WAS SHUT OFF AND IT WAS CONFIRMED THAT THE LEAK WAS ON A GULF SOUTH 1" RISER. HIGHWAY 16 WAS BLOCKED OFF, AND AT APPROXIMATELY 14:35 THE FIRE WAS OUT. AT 14:47 NRC NOTIFICATION WAS MADE. OPERATIONS PERSONNEL REPORTED THAT AN 18-WHEELER LOG TRUCK WAS SITTING ON TOP OF THE RISER AND HAD BEEN BURNED. THE DRIVER OF THE 18-WHEELER LOG TRUCK DID NOT HAVE SIGNIFICANT INJURIES. THE FATALITY WAS THE DRIVER OF THE SECOND VEHICLE WHICH WAS CAUSED BY VEHICULAR IMPACT AND NOT THE RESULT OF THE GAS RELEASE OR FIRE. GULF SOUTH COMPLETED REPAIRS TO ITS FACILITIES ON OCTOBER 29, 2020. THE RESPONSES PROVIDED FOR QUESTIONS D3, E1, E1A, E2, E2A, E2B, AND E2C PERTAIN TO THE 4-INCH PARENT PIPE (INDEX 301-2-4-14) BECAUSE THE INCIDENT OCCURRED ON A FARM TAP. THE RESPONSE TO QUESTION D7A IS ZERO BUT THE ACTUAL NUMBER IS UNKNOWN. THIS INCIDENT INCLUDED VEHICLE DAMAGE AND A DEATH BUT THOSE WERE NOT GULF SOUTH'S RESPONSIBILITY AND GULF SOUTH HAS NO KNOWLEDGE OF THE COST ASSOCIATED WITH THESE DAMAGES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200126 | 35819 | 2020-11-24 10:57 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-29 14:10 | 2020 | CENTRAL | YES | 28.9883 | -92.2975 | 1290991 | 2020-10-29 15:10 | 1291102 | OTHER GAS | CONDENSTATE | 0 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | SYSTEM WAS ALREADY SHUTDOWN DUE TO HURRICANE ZETA |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2020-10-29 14:10 | 2020-10-29 14:10 | OFFSHORE | [6 empty] | SEA ROBIN PIPELINE | V-149A | [20 empty] | 80 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | VERMILION | 149 | PLATFORM | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON |  |  |  | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 860 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 585000 | 608689.366890185295 | 2000 | 2080.989288513454 | 0 | 0 |  | 2.95 | 587000 | 269448.489070800183 | 610770.356178698749 | 0 | 0 | 0 | 0 | NO |  |  |  | 710 | 0 | 1200 | 192.619(A)(1) |  | 2012-07-18 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT REQUIRED, POWER OUTAGE DUE TO HURRICANE ZETA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [6 empty] | YES | [162 empty] | YES | [10 empty] | NICKLAS PAVLOVSKY | SPECIALIST - DOT COMPLIANCE | nicklas.pavlovsky@energytransfer.com | 7139894527 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | 10/29/20, VERMILLION 149 LOST POWER DUE TO HURRICANE ZETA. UPON INVESTIGATION TECHNICIAN DISCOVERED VALVE SEAL FAILED ALLOWING CONDENSATE TO FILL PLATFORM PIPING. 10/29/20, 15:10 CST INITIAL NOTIFICATION MADE TO THE NRC # 1290991. 10/31/20, 10:25 CST 48 HOUR NOTIFICATION MADE TO THE NRC # 1291102. 11/17/20 - CURRENTLY PUMPING LIQUID OFF THE PLATFORM, BLOWING DOWN PIPELINE, AND INCREASING SIZE OF GENERATOR TO TRANSITION TO A 24HR OPERATION. 11/24/20 - STILL PUMPING LIQUIDS OFF THE PLATFORM, NO SHEEN PRESENT. PIPELINE REPAIRS ARE STILL NEEDED AND WILL BE PERFORMED WEATHER PERMITTING. 12/15/2020 - LIQUIDS ARE OFF THE PLATFORM AT THIS TIME, OPERATIONS IS STILL BLOWING DOWN THE PIPELINE AND ALMOST DOWN TO 0 PSIG. PLATFORM VALVE IS ISOLATED AND LIQUIDS HAVE BEEN REMOVED, HOWEVER A LIFT BOAT IS NEEDED TO MAKE NECESSARY REPAIRS. EXPECT TO BE COMPLETED AFTER THE FIRST OF THE YEAR, PERMITTING PROPER EQUIPMENT AVAILABILITY. REPAIRS COMPLETED BY REPLACING THE SEAL AND ADDING ANOTHER VALVE DOWNSTREAM OF THE VALVE THAT LEAKED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200127 | 36510 | 2020-11-24 11:38 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-10-26 15:42 | 2020 | CENTRAL | YES | 28.1219 | -92.9758 | 1290995 | 2020-10-29 15:42 | 1291104 | NATURAL GAS |  | 3563 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS PREVIOUSLY SHUTDOWN DUE TO HURRICANE ZETA. |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-10-26 12:00 | VALVE CLOSURE |  | 2020-10-29 15:00 | 0 | 2020-10-29 15:42 | 2020-10-29 14:42 | OFFSHORE | [6 empty] | SEA ROBIN EC 335 | 4093 | [20 empty] | 240 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | EAST CAMERON | 335 | PORTION OF RISER OUTSIDE OF SPLASH ZONE, INCLUDING RISER BEND | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 | NO | 0.5 | 60000 | API5L | OTHER | UNKNOWN | UNKNOWN | PAINT |  | YES | [26 empty] | 1977 | 1977 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 488 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 10511 | 18447.8775510204081632653061224489795918 | 100000 | 104049.4644256727 | 2000 | 2080.989288513454 | 0 | 0 |  | 2.95 | 112511 | 58925.1958301141605655976676384839650146 | 124578.3312652065621632653061224489795918 | 0 | 0 | 0 | 0 | NO |  |  |  | 704 | 0 | 984 | 192.619(A)(1) |  | 2012-07-18 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 237600 | NO | YES |  | YES |  |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT REQUIRED, POWER OUTAGE DUE TO HURRICANE ZETA. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [14 empty] | YES | [48 empty] | NICKLAS PAVLOVSKY | SPECIALIST - DOT COMPLIANCE | nicklas.pavlovsky@energytransfer.com | 17139894527 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 7139897126 | todd.nardozzi@energytransfer.com | 10/29/20, 14:42 CST PRODUCER NOTIFIED OPERATIONS PERSONNEL OF PINHOLE LEAK ON THE RISER CLAMP AREA OF THE PIPELINE DUE TO CORROSION. 10/29/20, 15:42 CST INITIAL NOTIFICATION MADE TO THE NRC # 1290995. ON 10/31/20, PIPELINE WAS ISOLATED AND PRODUCER IS MAKING ARRANGEMENTS TO BLOWDOWN THEIR LATERAL TO BLEED THE PRESSURE OFF THE LEAK SITE. CURRENTLY WAITING ON PRODUCER TO BLOWDOWN THEIR EQUIPMENT ON PLATFORM IN ORDER TO MAKE NECESSARY REPAIRS. 10/31/20, 10:40 CST 48 HOUR NOTIFICATION MADE TO THE NRC # 1291104. 11/24/20 - ONCE PRODUCER BLOWS DOWN THEIR LINE, WE WILL BE WORKING TO INSTALL JUMPER LINE TO BLEED OFF OUR PRESSURE TO THE PRODUCER AND MAKE NECESSARY REPAIRS. 12/15/20 - STILL BLOWING 2" PIPELINE AROUND THE CHECK VALVE BACK DOWN TO THE PRODUCER. OPERATIONS IS CURRENTLY UNABLE TO BLOW INTO THE 30" LINE DUE TO V-149 INCIDENT HAVING THE LINE SHUT IN. NO SHEEN PRESENT AT THIS TIME. WE ARE CURRENTLY WORKING WITH LIMITED WORK HOURS AS THIS PLATFORM IS NOT MANNED 24/7. STARTED AT 570PSI AND CURRENTLY 416PSI, WILL NEED TO BLOWDOWN TO 0 PSIG BEFORE ABLE TO MAKE REPAIRS. 9/3/21 - REPAIRS WERE COMPLETED BY A WELDED FULL ENCIRCLEMENT SLEEVE AROUND THE LEAK SITE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200128 | 35171 | 2020-11-24 12:22 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2020-10-24 12:29 | 2020 | CENTRAL | YES | 38.3622 | -98.678 | 1290636 | 2020-10-25 10:50 | 1290767 | NATURAL GAS |  | 617.4 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-10-24 14:25 | 2020-10-24 22:40 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-10-24 14:25 | VALVE CLOSURE |  | 2020-10-24 14:35 | 0 | 2020-10-24 12:29 | 2020-10-24 13:11 | ONSHORE | KS | 67530 | Not Within a Municipality | BARTON | MILEPOST | 3.7 | P0445 | MP 3.7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 35 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4.5 | NO | 0.237 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 6 | 3 | [7 empty] | CLASS 1 LOCATION | NO |  | 69 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1828 | 3208.326530612244897959183673469387755102 | 0 | 0 | 0 | 0 | 173457 | 180481.079508839095239 | TOTAL EQUIPMENT/LABOR/MISC COSTS OF REPAIR, RESPONSE & RESTORATION | 2.96 | 175285 | 81726.4711761764819809300291545189504373 | 183689.4060394513401369591836734693877551 | 0 | 0 | 901 | 125 | NO |  |  |  | 350 | 184.56 | 459 | 192.619(A)(3) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 39564 | NO | [5 empty] | YES | NO LAUNCHERS OR RECEIVERS | YES |  |  |  |  | YES | NO LAUNCHERS OR RECEIVERS | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE BY THIRD PARTY EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | DRAINAGE | YES | 20525737 |  | CONTRACT LOCATOR | NO | YES | YES | 9 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN THE MARKS | [263 empty] | JUSTIN W CLEMENTS | REGULATORY COMPLIANCE SPECIALIST | justin.clements@onegas.com | 913-599-8980 |  | SCOTT BORNHOLDT | scott.bornholdt@onegas.com | 620-672-1622 | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 913-599-8931 | randalrandy.spector@onegas.com | A 3RD PARTY CONTRACTOR MOVING DIRT WITH A SCRAPER OVER THE COMPANY'S 4" TRANSMISSION LINE CAUSED DAMAGE. EVIDENCE SHOWS THAT THE CONTRACTOR MOVED APPROXIMATELY 36" OF DIRT BEFORE MAKING CONTACT WITH THE TRANSMISSION LINE THAT HAD BEEN PROPERLY LOCATED AND MARKED PRIOR TO THE DAY OF DAMAGE. THE DAMAGE CAUSED THE DOWNSTREAM PRESSURE TO DROP TO 0 PSI. THE COMPANY CLOSED THE UPSTREAM AND DOWNSTREAM VALVES TO ISOLATE THE LINE AND TO ALLOW FOR THE SAFE REPAIR OF THE LINE BY REPLACING APPROXIMATELY 18' OF 4" PIPE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200129 | 34594 | 2020-12-04 16:36 | ORIGINAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2020-11-06 17:30 | 2020 | CENTRAL | NO | 32.4672 | -91.5978 | 1291840 | 2020-11-10 13:50 | 1291982 | NATURAL GAS |  | 5000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-11-06 17:44 | 2020-11-06 23:00 |  | YES | OPERATOR | 2020-11-06 17:30 | NO | [11 empty] | 0 | 2020-11-06 17:30 | 2020-11-06 17:40 | ONSHORE | LA | 71232 | DELHI | RICHLAND | MILEPOST | MP 151.3 | DELHI COMPRESSOR STATION | ANR 501 MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1956 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VALVE FAILURE | CLASS 1 LOCATION | NO |  | 787 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 13350 | 23430.6122448979591836734693877551020408 | 1000 | 1040.494644256727 | 0 | 0 | 0 | 0 | NONE | 2.67 | 14350 | 15832.9330923720676005830903790087463557 | 24471.1068891546861836734693877551020408 | 0 | 0 | 0 | 0 | NO |  |  |  | 786 | 2000 | 858 | 192.619(A)(3) |  | 1967-07-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER IDENTIFIED THE ISSUE VIA SCADA ALARMS AND INITIATED A CALL-OUT OF FIELD OPERATIONAL PERSONNEL, WHO IDENTIFIED THE INCIDENT AND TOOK CORRECTIVE ACTIONS. GAS CONTROL DOES NOT HAVE THE CAPABILITY TO REMOTELY CLOSE VALVES AND THEREFORE COULD PREVENT THE INCIDENT THROUGH THEIR ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [23 empty] | YES | [163 empty] | ROGER R STREET | COMPLIANCE SPECIALIST | roger_street@tcenergy.com | 6154655123 |  |  |  |  | ERIK HUGHES | SENIOR COMPLIANCE MANAGER USGO AND KEYSTONE | 4024927447 | erik_hughes@tcenergy.com | ON NOVEMBER 6 AT 17:30 CT, ANR PIPELINE'S GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN (ESD) ALARM AT DELHI COMPRESSOR STATION LOCATED AT 1984 HWY 80 W, DELHI, LA 71232 (32.46707, -91.59751). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 17:40 CT, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED THROUGH THE STATION'S BLOWDOWN STACKS. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO EMERGENCY EXISTED AND CLOSING THE VALVES, WHICH ENDED THE RELEASE AT 17:44 CT. UNINTENTIONAL GAS LOSS WAS CALCULATED TO 5.0 MILLION CUBIC FEET (MMCF). NO PROPERTY DAMAGE OR INJURIES WERE DOCUMENTED, AND NO EVACUATIONS WERE REQUIRED. FOLLOWING THE RELEASE, INITIAL SITE INSPECTIONS WERE COMPLETED TO LOOK FOR EVIDENCE OF FIRE OR OTHER DAMAGE. NO DAMAGE WAS OBSERVED, AND THE STATION WAS PLACED BACK INTO PARTIAL SERVICE AT 23:00 CT ON NOVEMBER 6. WHEN THE SYSTEM ACTIVATED, STATION ISOLATION VALVE 501-13-25 FAILED TO FULLY CLOSE RESULTING IN THE UNINTENTIONAL RELEASE OF GAS. FOLLOWING THE INCIDENT, VALVE 501-13-25 WAS REMOVED FROM SERVICE FOR INSPECTION. A POPPET BLOCK VALVE, ATTACHED TO THE VALVE OPERATOR WAS REMOVED, DISASSEMBLED, AND INSPECTED FOR POTENTIAL DAMAGE. DAMAGED AND WORN SEALS ON THE POPPET VALVE WERE IDENTIFIED WHICH PREVENTED THE VALVE FROM FULLY CLOSING WHEN ACTUATED. THE POPPET BLOCK VALVES ASSOCIATED WITH VALVE 501-13-25 WERE CLEANED AND THE SEALS WERE REPLACED. AFTER REPAIRING THE VALVES, AN ESD SYSTEM INSPECTION WAS COMPLETED ACCORDING TO PROCEDURES ON NOVEMBER 17, 2020. THE TEST WAS INITIATED BY TRIGGERING THE FLAME DETECTORS AND THEN MONITORING ALL EMERGENCY SYSTEM VALVES FOR OPERATIONS AND TIMING. DURING THE TEST, ALL SYSTEM VALVES PROPERLY OPERATED AND FULLY CLOSED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200130 | 36535 | 2020-12-10 14:34 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-11-11 21:49 | 2020 | EASTERN | YES | 40.1409 | -80.4463 | 1291972 | 2020-11-11 22:50 | 1292099 | NATURAL GAS |  | 7687.2 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-11-11 21:49 | 2020-12-29 13:41 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-11-11 21:45 | NO | [5 empty] | VALVE CLOSURE |  | 2020-11-11 21:45 | VALVE CLOSURE |  | 2020-11-11 21:45 | 0 | 2020-11-11 21:00 | 2020-11-11 21:49 | ONSHORE | PA | 15323 | CLAYSVILLE | WASHINGTON | NOT APPLICABLE |  | 9190 / DONEGAL STORAGE FIELD WELL 3951 | 9190 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 | NO | 0.237 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | NONE |  | NO | [26 empty] | 1948 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4.5 | 4.5 |  | CLASS 1 LOCATION | NO |  | 99 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 17296 | 30356.2448979591836734693877551020408163 | 472395 | 491524.467473656551165 | 0 | 0 | 84880 | 88317.18540451098776 | INVESTIGATION COSTS | 2.25 | 574571 | 275722.0638329850799866618075801749271137 | 610197.8977761267225984693877551020408163 | 0 | 0 | 0 | 0 | NO |  |  |  | 1117 | 574350 | 1280 | 192.619(A)(2) |  | 1969-12-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 472 | NO |  | YES | [5 empty] | YES |  |  |  |  | YES | VALVE TYPE IS PLUG | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | EXTERNAL CORROSION ALONG THE 6:00 ORIENTATION OF THE PIPE | YES | YES | [7 empty] | YES | YES |  |  | YES | YES | 1948 | NO | YES | YES | YES |  |  | 2021 | 2006 |  |  | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | YES | 1970 | 1786 | NO | [13 empty] | NO | [63 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304-539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER USRC EAST | 304-550-4866 | paul_shaffer@tcenergy.com | ON THE EVENING OF NOVEMBER 11TH, 2020, STORAGE FIELD (SF) PERSONNEL FROM COLUMBIA GAS TRANSMISSION, LLC (COMPANY), A TC ENERGY ENTITY, RESPONDED TO AN EVENT AT DONEGAL STORAGE FIELD WHICH IS OPERATED AND MAINTAINED BY THE COMPANY. AT 9:33 PM, COMPANY MONITORING CENTER PERSONNEL RECEIVED A CALL FROM GAS CONTROL REGARDING A PRESSURE DROP. THE PRESSURE HAD DROPPED FROM 1,190 TO 1,156 PSIG, FOLLOWED BY A SUBSEQUENT DROP TO 1,035 PSIG AFTER SHUTTING-IN PRESSURE REGULATION. AT 9:35 PM, FIELD PERSONNEL WERE CONTACTED BY A NEAR-BY PROPERTY OWNER REPORTING THE SOUND OF A GAS LINE LEAK; SUBSEQUENTLY, COMPANY OPERATIONS PERSONNEL WERE NOTIFIED TO RESPOND TO THE EVENT LOCATION. FIRST RESPONDER ARRIVED ON SCENE AT 9:45 PM AND OBSERVED GAS BLOWING; THE LOCAL FIRE DEPARTMENT CLOSED CUNNINGHAM ROAD AT THIS TIME. AT 9:54 PM A COMPANY SF TECHNICIAN CONFIRMED THAT THE REPORTED LEAK HAD BEEN ISOLATED BY OPERATING THE CRITICAL VALVE. THE NATIONAL RESPONSE CENTER (NRC) AND PHMSA ACCIDENT INCIDENT DIVISION WERE CONTACTED WITHIN 1 HOUR OF CONFIRMED DISCOVERY AT 10:50 PM. NRC ONE-HOUR (1291972) AND 48-HR (1292099) REPORTS WERE COMPLETED ON NOVEMBER 11TH AND NOVEMBER 13TH RESPECTIVELY. THE FAILED STORAGE LINE (9190) WAS SECURED AND SENT TO A METALLURGICAL FAILURE ANALYSIS LABORATORY TO EVALUATE AND DETERMINE THE PROBABLE CAUSE BEHIND THIS PIPELINE FAILURE. THE REPAIR OF THE LINE CONSISTED OF PIPE REPLACEMENT. THE METALLURGICAL ROOT CAUSE OF THE FAILURE WAS DUE TO EXTERNAL CORROSION IDENTIFIED ALONG THE 6:00 O'CLOCK ORIENTATION OF THE PIPE. THE ABSENCE OF AN EXTERNAL COATING AND EXPOSURE TO ATMOSPHERE (I.E. DE-COUPLED FROM THE SOIL ELECTROLYTE) WERE CONTRIBUTING FACTORS TO THE CORROSION OF THE PIPE. IN AN EFFORT TO PREVENT FUTURE OCCURRENCE, THE COMPANY HAS LOOKED BEYOND THIS LOCATION TO OTHER SEGMENTS WITH SIMILAR ENVIRONMENTAL CONDITIONS AND PIPE CHARACTERISTICS WHERE CORROSION MAY ADVERSELY IMPACT LINE INTEGRITY; TO THAT END, TWO OPPORTUNITIES FOR MITIGATIVE MEASURES HAVE BEEN SCHEDULED FOR COMPLETION BEFORE DECEMBER 31, 2022. THE PROJECTS WILL INVOLVE REPLACING LINE SEGMENTS AND ASSESSMENT OF THE REMOVED SEGMENTS FOR EXTERNAL CORROSION. NOTE: ALL TIMES WERE RECORDED IN EASTERN STANDARD TIME
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200131 | 34793 | 2020-12-18 10:25 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-12-09 10:53 | 2020 | MOUNTAIN | YES | 39.4805 | -107.2045 | 1293896 | 2020-12-09 10:53 | 1294036 | NATURAL GAS |  | 37162 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2020-11-23 00:36 | 2020-11-23 11:35 | ONSHORE | CO | 81601 | Not Within a Municipality | GARFIELD | SURVEY STATION NO. | SPRING VALLEY | SPRING VALLEY COMPRESSOR STATION | SPRING VALLEY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 | 2014 | CARBON STEEL |  | OTHER | [8 empty] | PURGING VALVE LEFT OUT OF POSITION | CLASS 1 LOCATION | NO |  | 300 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 80567 | 141403.3061224489795918367346938775510204 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.168 | 80567 | 92781.2390670553935860058309037900874636 | 141403.3061224489795918367346938775510204 | 0 | 0 | 0 | 0 | NO |  |  |  | 833 | 0 | 1200 | 192.619(A)(3) |  | 2014-08-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES |  | YES | [6 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | STONEY DAVIDSON | COMPLIANCE COORDINATOR | stoney.davidson@blackhillsenergy.com | 719 359-0586 |  | THOMAS WARNES | thomas.warnes@blackhillsenergy.com | 970 406-1467 | STONEY DAVIDSON | COMPLIANCE COORDINATOR | 719 359-0586 | stoney.davidson@blackhillsenergy.com | ON NOVEMBER 22 THE SPRING VALLEY COMPRESSOR STATION WAS PURGED, PACKED AND MADE READY TO BE PUT ONLINE. THE STATION WAS ON STANDBY WITH NO COMPRESSION RUNNING. ON NOVEMBER 23, 2020 0036 ' THREE HIGH PRIORITY ALARMS WERE RECEIVED BY CONTROLLER 0059 ' CONTROLLER ACKNOWLEDGED ALL THREE ALARMS DID NOT NOTIFY FIELD OPERATIONS. 11:35AM- FIELD OPERATIONS PERSONNEL VISITED THE SITE TO CLEAN UP FROM WEEKEND WORK AND DISCOVERED BLOWING GAS OUT OF THE BLOW-DOWN SILENCER. SECURED THE SITE AND EVALUATED THE SITUATION ON STATION HMI. 11:39AM- RESET ESD SYSTEM SHUTTING IN THE VENTING GAS. IT WAS FOUND THAT A MALFUNCTION OF A FIRE EYE DETECTION DEVICE CAUSED AN EMERGENCY SHUTDOWN (ESD). THERE WERE STATION PURGE LINES LEFT IN THE OPEN POSITION AFTER CHARGING THE STATION WHICH CAUSED A BYPASS OF ESD BLOCK VALVES RESULTING IN THE BLOWING GAS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200132 | 34695 | 2020-12-22 15:40 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2020-12-10 10:10 | 2020 | CENTRAL | YES | 28.5798 | -91.8712 | 1293926 | 2020-12-10 17:58 | 1284035 | NATURAL GAS |  | 636 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-11 06:00 |  | YES | YES | OPERATOR | 2020-12-10 17:58 | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-10 12:30 | VALVE CLOSURE |  | 2020-12-11 06:00 | 0 | 2020-12-10 10:10 | 2020-12-10 12:07 | OFFSHORE | [28 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH MARSH | 78 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 16 | NO | 0.375 | 33000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | CONCRETE | NO | [26 empty] | 1991 | 1989 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1272 | 2232.489795918367346938775510204081632653 | 250000 | 260123.66106418175 | 40000 | 41619.78577026908 | 0 | 0 |  | 2 | 291272 | 134582.4918316313825947521865889212827988 | 303975.9366303691973469387755102040816327 | 0 | 0 | 0 | 0 | NO |  |  |  | 760 | 0 | 1250 | 192.619(A)(1) |  | 1991-05-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 8610 | NO | [5 empty] | YES | PIG LAUNCHER AND SUBSEA NO RECEIVER | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | OTHER OPERATOR NOTIFICATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE MAOP WAS NOT EXCEEDED AND GAS CONTROL WAS NOT THE CAUSE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | HISTORY OF SIMILAR PIPES |  |  |  |  | YES | 6 O'CLOCK POSITION | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SENIOR VICE PRESIDENT | kurt.cheramie@kineticallc.com | 9852092283 |  |  |  |  | KURT CHERAMIE | SENIOR VICE PRESIDENT | 9852092283 | kurt.cheramie@kineticallc.com | KINETICA WAS NOTIFIED OF POTENTIAL LEAK IN SM ISLAND AREA. KINETICA PERFORMED FLY OVER AND PLOTTED COORDINATES. KINETICA WENT TO UPSTREAM VALVE AT PRODUCER PLATFORM AND CLOSED AND LOCKED THE VALVE TO ISOLATE. OBTAINED A DSV AND HEADED TO LOCATION. DOVE ON LEAK TO CONFIRM OWNERSHIP. ONCE OWNERSHIP WAS CONFIRMED TO BE KINETICA'S 16" PIPELINE, DSV RELOCATED TO SUBSEA TIE IN WITH KINETICA'S MAINLINE. DSV THEN CLOSED DOWNSTREAM 16" VALVE TO TOTALLY ISOLATED 16" LINE. PRESSURE WAS BLED DOWN TO BOTTOM PRESSURE. LINE HAS BEEN TOTALLY ISOLATED, BLED DOWN, AND WILL BE ABANDONED IN 2021. THE LEAK WAS FROM UNDER CONCRETE COATING. THE LEAK WAS IN THE 6 O'CLOCK POSITION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20200133 | 34676 | 2020-12-28 19:08 | SUPPLEMENTAL FINAL | 31565 | GULFSTREAM MANAGEMENT & OPERATING SERVICES,LLC | 1905 INTERMODAL CIRCLE, SUITE 310 | PALMETTO | FL | 34221 | 2020-11-29 02:15 | 2020 | EASTERN | NO | 27.7483 | -81.85 | 1293196 | 2020-11-29 16:15 | 1293256 | NATURAL GAS |  | 4200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-11-29 12:00 | 2020-12-10 16:15 |  | NO |  |  | NO | [11 empty] | 0 | 2020-11-29 01:00 | 2020-11-29 02:15 | ONSHORE | FL | 33841 | FORT MEADE | POLK | SURVEY STATION NO. | 6+65 | STATION 415 | TIGER BAY M&R | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2020 | 2020 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTUATION | CLASS 1 LOCATION | NO |  | 338 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 10416 | 18281.1428571428571428571428571428571429 | 600 | 624.2967865540362 | 0 | 0 | 0 | 0 |  | 2.48 | 11016 | 12270.5178729159519306122448979591836735 | 18905.4396436968933428571428571428571429 | 0 | 0 | 0 | 0 | NO |  |  |  | 465 | 30 | 1480 | 192.619(A)(2) |  | 2002-03-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION BY CUSTOMER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DUE TO VALVE NOT RESETTING (EQUIPMENT FAILURE). | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [24 empty] | YES | YES | METAL PIN WAS FOUND WEDGED IN THE RELIEF | [161 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 713-215-4163 |  |  |  |  | TYSON GREEN | PIPELINE SAFETY MANAGER | 713-215-2535 | tyson.green@williams.com | ON 11/29/2020 AT THE GULFSTREAM TIGER BAY M&R STATION, THERE WAS A COMBINED RELEASE OF 4.2 MMCF OF GAS (2.1 MMCF FROM WILLIAMS AND 2.1 MMCF FROM THE CUSTOMER). WILLIAMS DETERMINED THE RELEASE WAS DUE TO THE FAILURE OF A MOONEY FLEXIBLE ELEMENT REGULATOR COUPLED WITH A RELIEF VALVE THAT FAILED TO RESET ONCE THE PRESSURE DROPPED BELOW THE SET POINT. THE CUSTOMER CAME OFFLINE, AT WHICH TIME, THE MOONEY REGULATOR FAILED TO LOCKUP DUE TO INTERNAL DAMAGE TO THE FLEXIBLE ELEMENT (WEAR AND TEAR: SEEING FLEXIBLE ELEMENT LIFE HAS SHORTENED FROM 6 MONTHS TO 2 MONTHS). THE RELIEF VALVE BEGAN TO VENT BUT DID NOT RESET ONCE THE PRESSURE DECREASED BELOW THE SET POINT. THE RELIEF VALVE CONTINUED TO VENT UNTIL THE RESPONDING TECHNICIAN ARRIVED AND SECURED THE FACILITY. WHEN THE RELIEF WAS TORE DOWN TO BE REBUILT AND PUT BACK IN SERVICE, A METAL PIN WAS FOUND TO BE WEDGED IN THE RELIEF AND WAS NOT ALLOWING IT TO RESET. THE VALVE MANUFACTURER WAS CONTACTED TO ASK IF IT WAS AN ALIGNMENT PIN LEFT IN THERE BY MISTAKE BUT THEY HAVE INDICATED THEY DO NOT USE ANYTHING LIKE THAT DURING MANUFACTURING. IT IS UNKNOWN AS TO WHERE THE PIN MAY HAVE COME FROM.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200134 | 35049 | 2020-12-28 21:31 | SUPPLEMENTAL FINAL | 4900 | KINDER MORGAN TEJAS PIPELINE | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2020-12-04 17:02 | 2020 | CENTRAL | NO | 27.8171 | -97.4528 | 1293563 | 2020-12-04 17:02 | 1293611 | NATURAL GAS |  | 104 | 642 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-04 18:52 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-04 18:52 | VALVE CLOSURE |  | 2020-12-04 18:52 | 0 | 2020-12-04 16:40 | 2020-12-04 18:00 | ONSHORE | TX | 78407 | CORPUS CHRISTI | NUECES | SURVEY STATION NO. | 21853.85 | TRANSCO TO AVERY | GOLDSTON TO AVERY 12 INCH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | UNDERGROUND PIPELINE CASING. | 46 | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 | NO | 0.25 | 52000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | FBE | UNKNOWN | [26 empty] | 1988 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 252 |  | NO | NO | [5 empty] | 0 | 0 | 1733 | 1803.177218496907891 | 281 | 493.183673469387755102040816326530612245 | 110536 | 115012.115997561575672 | 500 | 520.2473221283635 | 0 | 0 | NA | 2.7 | 113050 | 52087.5471998281402297463556851311953353 | 117828.7242116562348181020408163265306122 | 0 | 0 | 0 | 0 | NO |  |  |  | 669 | 40000 | 819 | 192.619(A)(2) |  | 1988-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 16913 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  | YES |  |  |  |  | DIRECT CURRENT | DC CURRENT FROM NARROW RAILROAD TRACK LOCATED DIRECTLY ABOVE THE PIPELINE. |  | YES |  |  | YES | YES | 1989 | NO | YES | YES | YES |  |  | 2019 | 2020 |  |  | YES | [190 empty] | YES | YES |  |  | YES |  |  | YES | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [27 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [13 empty] | IMU | 2017 | FREE SWIMMING |  |  |  | NO |  |  | NO | [13 empty] | NO | [63 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-3199 |  | TONY PALACIOS | tony_palacios@kindermorgan.com | (361) 438-3411 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON DECEMBER 4, 2020 AT APPROXIMATELY 15:00 HRS. LOCAL TIME, TEJAS PIPELINE RECEIVED A CALL FROM A LOCAL GAS OPERATING COMPANY OF NATURAL GAS VAPORS OBSERVED FROM A PIPELINE CASING VENT LOCATED NEAR AVERY POINT IN NUECES COUNTY, TEXAS. AT 15:20 HRS. LOCAL TIME, A TEJAS FIELD TECHNICIAN INSPECTED THE LOCATION BUT COULD NOT LOCATE THE LEAK. THE LOCAL GAS OPERATING COMPANY, ORIGINALLY REPORTING THE LEAK, REVISED THE LOCATION DESCRIPTION TO NAVIGATION BLVD IN NUECES COUNTY, TEXAS. UPON ARRIVAL AT NAVIGATION BLVD., THE TEJAS FIELD TECHNICIAN CONFIRMED THE LEAK BELONGED TO TEJAS AT 16:20 HRS. LOCAL TIME BY OBSERVING A LOW-LEVEL EMISSION OF VAPORS FROM THE PIPELINE CASING VENT. THE TEJAS FIELD TECHNICIAN AND MANAGEMENT COMPLETED A ERL TELEPHONE CALL AND DECIDED TO REPORT THE EVENT AS AN INCIDENT SINCE IT WAS DETERMINED THAT THE COST OF REPAIRS WOULD EXCEED $50,000. AS SUCH, TEJAS COMPLETED THE REPORT TO THE NRC AT 17:02 HRS. THE SAME DAY. TEJAS COMPLETED A 48-HOUR NRC UPDATE THE FOLLOWING DAY CITING NO SIGNIFICANT CHANGES. THE PIPE SECTION CONTAINING THE PINHOLE LEAK WAS SHIPPED TO BRYAN LABORATORIES IN HOUSTON, TX FOR METALLURGICAL EVALUATION. BASED ON METALLURGICAL REPORT, THE APPARENT CAUSE OF THE PINHOLE LEAK APPEARED TO BE STRAY CURRENT INDUCED ON THE PIPELINE FROM CLOSE PROXIMITY EXISTING METAL, NARROW-GAUGE RAILROAD LINE THAT CROSSES THE TEJAS PIPELINE. THE ROOT CAUSE OF THE PINHOLE LEAK WAS DETERMINED TO BE DC STRAY CURRENT FROM THE RAILROAD LINES CAUSING EXTERNAL CORROSION OF THE PIPELINE DIRECTLY BELOW THE TRACKS. THE RAILROAD TRACKS HAVE BEEN REMOVED AND THE PIPELINE REPAIRED AND PLACED BACK INTO SERVICE. THE AFFECTED PIPE SEGMENT DID NOT CONTAIN AN INJURIOUS MICROSTRUCTURE OR PROPERTIES THAT COULD HAVE CONTRIBUTE TO THE FAILURE. IN ADDITION, NO INTERNAL CORROSION REPORTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20200135 | 35347 | 2020-12-30 20:34 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-12-03 13:20 | 2020 | EASTERN | YES | 39.6315 | -82.5549 | 1293457 | 2020-12-03 14:54 | 1293539 | NATURAL GAS |  | 200 | 78 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-03 15:00 | 2020-12-24 17:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-12-03 08:30 | 2020-12-03 08:30 | ONSHORE | OH | 43155 | SUGAR GROVE | FAIRFIELD | NOT APPLICABLE |  | SR-696 | SR-696 CRAWFORD COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 | NO | 0.328 | 65000 | X65 | DSAW |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | NO |  | 698 |  | NO | NO | [5 empty] | 0 | 0 | 160 | 166.47914308107632 | 410 | 719.591836734693877551020408163265306122 | 150000 | 156074.19663850905 | 0 | 0 | 30000 | 31214.83932770181 | OTHER COSTS INCLUDE METALLURGICAL ANALYSIS | 2.05 | 180570 | 83170.3512861831858015160349854227405248 | 188175.1069460266301975510204081632653061 | 0 | 0 | 0 | 0 | NO |  |  |  | 460 | 155000 | 850 | 192.619(A)(1) |  | 1977-09-15 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE UNINTENDED RELEASE OF GAS WAS DUE TO A NUISANCE LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES | YES | [6 empty] | YES | BOTTOM OF THE PIPE | YES | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAMRAN ROSTAMI ASRABADI | COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  | KAMRAN ROSTAMI ASRABADI | kamran_rostami@tcenergy.com | (304)357-2351 | PAUL SHAFFER | US REGULATORY COMPLIANCE MANAGER EAST | (304)550-4866 | paul_shaffer@tcenergy.com | ON DECEMBER 3, 2020, AT APPROXIMATELY 08:30 THE PRESENCE OF NATURAL GAS WAS IDENTIFIED BY A COMPANY PERSONNEL PASSING BY ONE OF THE COMPRESSOR BUILDINGS IN CRAWFORD COMPRESSOR STATION (CS). CRAWFORD CS IS A TRANSMISSION FACILITY LOCATED IN FAIRFIELD COUNTY, STATE OF OHIO THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COMPANY). COMPANY PERSONNEL CONDUCTED LEAKAGE SURVEY AT THE DEPICTED LEAK LOCATION AND ITS SURROUNDING TO INVESTIGATE THE SOURCE OF THE POTENTIAL NATURAL GAS LEAK. FURTHERMORE, THROUGHOUT A THOROUGH INVESTIGATION, IT WAS IDENTIFIED THAT THE POTENTIAL RELEASE WAS ALONG LINE SR-696. AT APPROX. 14:25 LINE SR-696 HAD BEEN ISOLATED ON BOTH ENDS OF THE AFFECTED SECTION AND BLOWDOWN COMMENCED FROM 460 PSIG LINE OPERATING PRESSURE. AT APPROX. 15:00 THE LINE AFFECTED SEGMENT OF LINE SR-696 WAS FULLY BLOWN DOWN TO ATMOSPHERIC PRESSURE. THE INITIAL NATIONAL RESPONSE CENTER (NRC) REPORT NO.1293457 AND THE NRC 48-HOUR REPORT NO.1293539 HAVE BEEN CALLED-IN ON DECEMBER 3RD AND DECEMBER 5TH RESPECTIVELY. THE FAILED SECTION OF THE PIPELINE WAS SENT TO A METALLURGICAL LABORATORY TO DETERMINE THE PROBABLE CAUSE BEHIND THE FAILURE OF THE PIPELINE. THE METALLURGICAL FAILURE ANALYSIS REPORT OF LINE SR-696 IDENTIFIED THAT THE CAUSE OF THE LEAK WAS INTERNAL CORROSION. NOTE: ALL TIMES WERE RECORDED IN EASTERN STANDARD TIME
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20210001 | 34672 | 2021-01-04 11:30 | ORIGINAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2020-12-09 14:08 | 2020 | CENTRAL | NO | 29.1617 | -91.1041 | 1293924 | 2020-12-09 14:30 | 1294002 | NATURAL GAS |  | 0.1 | 20 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-09 14:10 |  | YES | YES | OPERATOR | 2020-12-09 14:15 | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-09 14:10 | VALVE CLOSURE |  | 2020-12-09 14:10 | 0 | 2020-12-09 14:08 | 2020-12-09 14:08 | ONSHORE | LA | 70726 | Not Within a Municipality | TERREBONE | MILEPOST | 131 | MOSQUITO BAY | 20" CROSSOVER PIPE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | OTHER | UNDERWATER | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.5 | 52000 | API 5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR |  | YES | [26 empty] | 1962 | 1962 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 373 |  | NO | NO | [5 empty] | 0 | 0 | 50 | 52.02473221283635 | 0 | 0 | 50001 | 52025.772707480606727 | 0 | 0 | 10000 | 10404.94644256727 | DIVING TEAM | 2.48 | 60051 | 27564.993555691008159 | 62482.743882260713077 | 0 | 0 | 0 | 0 | NO |  |  |  | 730 | 20 | 1168 | 192.619(A)(2) |  | 1962-09-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 185 | NO | [5 empty] | YES | CROSSOVER PIPE BETWEEN ONSHORE PLATFORMS. | YES |  |  |  |  | YES | NO PIG TRAPS | TYPE B GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PINHOLE LEAK FOUND BY AERIAL PATROL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | PAST EXPERIENCE OF SIMILAR LEAKS OF AN AGING SYSTEM. | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-215-2846 |  | ERNEST DAIGLE | ernest.daiglejr@williams.com | (985) 446-7142 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | APPROXIMATELY 2:08PM ON APPROACH TO MOSQUITO BAY, TECHNICIANS NOTICED BUBBLES BETWEEN A AND B PLATFORMS. AT THAT TIME THEY REALIZED THE LEAK WAS CLOSE TO THE PROXIMITY OF OUR 20" CROSSOVER PIPE. TECHNICIANS CLOSED AND ISOLATED THE LINE AND BUBBLES STOPPED. LINE STOPPED LEAKING AT 2:40PM AFTER CLOSING AND ISOLATING THE LINE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210002 | 35515 | 2021-01-04 18:14 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-12-05 07:20 | 2020 | EASTERN | YES | 42.7187 | -82.7159 | 1293954 | 2020-12-10 08:40 | 1294029 | NATURAL GAS |  | 15.5 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-05 07:24 | 2021-01-15 15:00 |  | NO |  |  | NO | [11 empty] | 0 | 2020-12-05 07:23 | 2020-12-05 07:23 | ONSHORE | MI | 48023 | IRA | ST. CLAIR | NOT APPLICABLE |  | ST. CLAIR COMPRESSOR STATION PLANT 4 (DEHYDRATION) | DEHYDRATION SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | 2018 | 2018 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | THE PLANT SAFETY SYSTEM IDENTIFIED A HIGH HEAT SIGNATURE ON THE THERMAL OXIDIZER WHICH INITIATED THE FIREGATE ACTIVATION. | CLASS 3 LOCATION | YES | METHOD1 | 680 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 51 | 89.51020408163265306122448979591836734694 | 208000 | 216422.886005399216 | 125 | 130.061830532090875 | 0 | 0 |  | 3.3 | 208176 | 95593.5985379832166016763848396501457726 | 216642.4580400129395280612244897959183673 | 0 | 0 | 0 | 0 | NO |  |  |  | 1060 | 1060 | 1440 | 192.619(A)(2) |  | 1969-10-27 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATOR RESPONDED AS REQUIRED WHEN ALARM WAS GENERATED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [33 empty] | YES | [164 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 5, 2020 AT APPROXIMATELY 07:20 HOURS CONSUMERS ENERGY GAS CONTROL RECEIVED AN ALARM NOTIFICATION WHICH INDICATED A POSSIBLE FIRE AT THE ST. CLAIR COMPRESSOR STATION (PLANT 4 - DEHYDRATION SYSTEM BUILDING). THE CONSUMERS ENERGY ST. CLAIR COMPRESSOR STATION IS LOCATED IN IRA, MICHIGAN (ST. CLAIR COUNTY). A STATION MECHANIC AT THE SITE WAS NOTIFIED AND CONFIRMED ACTIVATION OF THE PLANT FIREGATE SYSTEM OCCURRED DUE TO THE FIRE DETECTION ALARM. FOLLOWING THE EVENT, THE PLANT WAS REMOVED FROM SERVICE AND THE SCENE WAS MADE SAFE. ADDITIONAL PERSONNEL WERE DISPATCHED TO THE STATION TO DETERMINE THE POTENTIAL CAUSE OF THE ACTIVATION. DURING THE INCIDENT INVESTIGATION, SCORCH MARKS WERE DISCOVERED ON INSULATION ON THE REBOILER VENT STACK. THE PLANT SAFETY SYSTEM IDENTIFIED A HIGH HEAT SIGNATURE ON THE THERMAL OXIDIZER WHICH INITIATED THE FIREGATE ACTIVATION. THE EQUIPMENT WAS TAKEN OFF-LINE AND PHYSICALLY INSPECTED. SEVERAL CRACKED WELDS WERE IDENTIFIED ON THE EXHAUST LINE OF THE THERMAL OXIDIZER. THE INCIDENT WAS REPORTED TO MICHIGAN PUBLIC SERVICE COMMISSION ON DECEMBER 5, 2020 BECAUSE THE EMERGENCY SHUT-DOWN SYSTEM WAS ACTIVATED, AND GAS RELEASED. HOWEVER, A MORE IN-DEPTH VISUAL INSPECTION CONFIRMED ADDITIONAL EQUIPMENT DAMAGE ANTICIPATED TO EXCEED PHMSA REPORTING CRITERIA OF $50,000. ONCE THIS WAS DISCOVERED, ON DECEMBER 10, 2020 A NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER. ADDITIONAL INVESTIGATION SUBSEQUENT TO THE EVENT HAS IDENTIFIED A CONCERN RELATIVE TO DESIGN/ACTUAL UNIT OPERATING TEMPERATURE, MATERIAL TEMPERATURE LIMITS OF THE EXHAUST SYSTEM COMPONENTS, AND EXCESSIVE THERMAL CYCLING CAUSED BY SYSTEM PROGRAMMING. FURTHER PROBLEM SOLVING IS REQUIRED TO DETERMINE THE ROOT CAUSE OF THE FAILURE. HOWEVER WITH THE CONCERNS DEFINED, CONSUMERS ENERGY HAS TAKEN ACTION TO REMEDIATE EACH CONCERN THROUGH A DECREASE IN THE OPERATING TEMPERATURE OF THE SYSTEM AND A REDUCTION IN THERMAL CYCLING OF THE EQUIPMENT. ALL DAMAGED MATERIALS HAVE BEEN REPLACED AND WELDS HAVE BEEN IMPROVED IN THE RESTORATION PROCESS. FURTHER ANALYSIS CONFIRMED THE SYSTEM DESIGN AND MATERIAL SUPPLY OF THE THERMAL OXIDIZER SUPERHEATER TO THE EXHAUST STACK INADEQUATELY ACCOUNTED FOR THE STRESS LEVELS PRESENT ON THE SYSTEM DUE TO THE OPERATING TEMPERATURE RANGE OF THE SYSTEM. IN ADDITION TO THE INITIAL REMEDIAL ACTIONS TAKEN, THE EQUIPMENT WAS ANALYZED TO DETERMINE FATIGUE AND STRESS. THE EVALUATION RESULTED IN EQUIPMENT DESIGN MODIFICATIONS TO (1) REDUCE THE STRESS PRESENT IN THE SYSTEM AND (2) PROVIDE ACCESS FOR INSPECTIONS AND REPAIRS. ADDITIONALLY, THERMAL CYCLES WILL BE MONITORED AND INSPECTED AT A PREDETERMINED CYCLE COUNT TO CONFIRM SYSTEM INTEGRITY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210003 | 35195 | 2021-01-08 16:31 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2020-12-08 08:46 | 2020 | EASTERN | YES | 36.1731 | -76.4724 | 1293797 | 2020-12-08 12:38 | 1293931 | NATURAL GAS |  | 4000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS PLACED ON A BYPASS TO MAINTAIN SERVICE. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE REDUCTION AND MAINLINE VALVE MONITORING UNTIL BYPASS COMPLETED. |  | OPERATIONAL CONTROL | PRESSURE REDUCTION AND MAINLINE VALVE MONITORING UNTIL BYPASS COMPLETED. |  | 25 | 2020-12-08 09:28 | 2020-12-08 09:28 | ONSHORE | NC | 27944 | HERTFORD | PERQUIMANS | SURVEY STATION NO. | 2641+00 | TRANSMISSION LINE 208 | LINE 208 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | BELOWGROUND UNDERWATER | 360 | NO | YES | [6 empty] | YES | UNCASED | RACOON CREEK | 11 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | YES | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.256 | 42000 | 10 INCH 256 API5L GRADE X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | FBE WITH POWERCRETE | UNKNOWN | [26 empty] | 2002 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 195 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 10000 | 17551.0204081632653061224489795918367347 | 5600000 | 5826770.0078376712 | 1500000 | 1560741.9663850905 | 0 | 0 |  | 2.5 | 7110000 | 3270603.38149765664052478134110787172012 | 7405062.99463092496530612244897959183673 | 0 | 0 | 7 | 0 | NO |  |  |  | 400 | 2520 | 800 | 192.619(A)(1) |  | 2002-06-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 38500 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY LINE DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO | YES | OTHER | [9 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A THIRD-PARTY CONTRACTOR WAS REPLACING A BRIDGE USING A PILE DRIVER WHEN A 10" STEEL TRANSMISSION LINE WAS STRUCK APPROXIMATELY 30 FEET DEEP BELOW WATER SURFACE. 25 RESIDENTS WERE INITIALLY EVACUATED AND RELOCATED AT THE TIME OF INCIDENT. ON THE FIRST DAY 18 RESIDENTS WERE ALLOWED BACK INTO THE HOMES AND 7 REMAINED RELOCATED FOR THE DURATION OF THE LEAK. AS LOCATION OF PIPELINE AND DAMAGE IS IN DRILLED SECTION BELOW WATER, PIPE WAS NOT EXPOSED; THEREFORE, ACTUAL SIZE OF MECHANICAL PUNCTURE IS UNKNOWN.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210004 | 35581 | 2021-01-11 13:53 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2020-12-13 09:39 | 2020 | EASTERN | NO | 39.3815 | -79.1523 | 1294187 | 2020-12-13 12:56 | 1294323 | NATURAL GAS |  | 98.43 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE 8025 IS THE SINGLE FEED TO THE TOWN OF KITZMILLER, MD. |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-13 11:54 | NO | [11 empty] | 0 | 2020-12-13 10:50 | 2020-12-13 10:50 | ONSHORE | WV | 26717 | ELK GARDEN | MINERAL | NOT APPLICABLE |  | LINE 8025 | V-182 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1974 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | NO |  | 74 |  | NO | NO |  |  | NO |  |  | 40000 | 41619.78577026908 | 0 | 0 | 202 | 354.530612244897959183673469387755102041 | 50000 | 52024.73221283635 | 5000 | 5202.473221283635 | 0 | 0 |  | 2.05 | 95202 | 43840.1306558128943586005830903790087464 | 99201.521816633962959183673469387755102 | 0 | 0 | 0 | 1 | NO |  |  |  | 25 | 105 | 30 | 192.619(A)(1) |  | 1974-07-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | REPORTED BY LOCAL DISTRIBUTION COMPANY PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO VEHICULAR STRIKE AND REPORTED ON COST OF REPAIR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | YES |  | YES | SMALL TRUCK | ROADWAY | 18 | NO | [238 empty] | WILLIAM YOUSE | COMPLIANCE SPECIALIST | william_youse@tcenergy.com | 13043573596 |  | WILLIAM YOUSE | william_youse@tcenergy.com | 13043573596 | PAUL SHAFFER |  | 13043572245 | paul_shaffer@tcenergy.com | PIPELINE 8025 IS A TRANSMISSION PIPELINE OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (OPID 2616), A TC ENERGY ENTITY. THIS IS A 3.5 INCH CARBON STEEL PIPELINE WITH A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 30 PSIG. ON DECEMBER 13, 2020 AN ABOVE GROUND SECTION CONNECTED TO 8025 WAS STRUCK BY A PICKUP TRUCK DAMAGING A PIPE NIPPLE BELOW GROUND AND CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS. THE VEHICLE WAS BEING OPERATED ON THE NEAR BY STATE ROUTE 42, AKA COTTAGE STREET IN ELK GARDEN, MINERAL COUNTY WEST VIRGINIA, WHEN IT LEFT THE ROADWAY AND STRUCK THE ABOVE GROUND PIPELINE APPURTENANCE. THE DRIVER WAS EXAMINED BY EMS AT THE SCENE AND RELEASED. PIPELINE 8025 IS A SINGLE FEED FOR THE NEARBY TOWN OF KITZMILLER, MARYLAND THAT REQUIRED THE PIPELINE TO STAY IN SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210005 | 34761 | 2021-01-13 08:15 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-12-14 02:05 | 2020 | CENTRAL | NO | 35.6205 | -100.9744 | 1294211 | 2020-12-14 03:02 | 1294327 | NATURAL GAS |  | 36994 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-14 02:45 | 2020-12-14 06:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-14 02:15 | NO | [11 empty] | 0 | 2020-12-14 02:05 | 2020-12-14 02:30 | ONSHORE | TX | 79065 | PAMPA | GRAY | SURVEY STATION NO. | 4509+30.9 | P-3 PAMPA COMPRESSOR STATION | TXBP132 24IN LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 1 | NO | 0.179 | 35000 | API 5L | SEAMLESS |  | US STEEL | PAINT |  | YES | [26 empty] | 1983 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | FIRE DETECTOR FAULT ON UNIT 304 TURBINE CAUSED THE STATION TO ESD. SUCTION VALVE DIDN'T CLOSE DUE TO THE POWER GAS SUPPLY LINE BEING FROZEN CAUSING GAS TO RELEASE UNTIL TECHNICIAN ARRIVED ONSITE AND ISOLATED THE STATION. | CLASS 1 LOCATION | NO |  | 526 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 79406 | 139365.6326530612244897959183673469387755 | 500 | 520.2473221283635 | 0 | 0 | 0 | 0 |  | 2.33 | 79906 | 91673.740598664167911078717201166180758 | 139885.8799751895879897959183673469387755 | 0 | 0 | 0 | 0 | NO |  |  |  | 710 | 25 | 1008 | 192.619(A)(1) |  | 1994-12-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER RECEIVED AN ALARM FROM SCADA AND CALLED TECHNICIAN IMMEDIATELY REQUESTING THEM TO GO TO THE SITE FOR FURTHER INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | POWER GAS LINE FROZE PREVENTING CLOSURE OF THE STATION SUCTION VALVE. | [161 empty] | KATHRYN HARRYMAN |  | kathryn.harryman@energytransfer.com | 7139897085 |  |  |  |  | TODD NARDOZZI |  | 7139897126 | todd.nardozzi@energytransfer.com | 02:05 CST SCADA INDICATED A DROP IN PRESSURE AT P-3 PAMPA COMPRESSOR STATION, CONTROLLER CONTACTED TECHNICIAN. 02:30 CST TECHNICIAN ARRIVED ON SITE AND MANUALLY SHUT SUCTION VALVE. THE TECHNICIAN WAS ABLE TO DETERMINE A FIRE DETECTOR FAULT ON UNIT 304 TURBINE CAUSED THE STATION TO ESD. SUCTION VALVE DIDN'T CLOSE DUE TO THE POWER GAS SUPPLY LINE BEING FROZEN CAUSING GAS TO RELEASE UNTIL TECHNICIAN ARRIVED ONSITE AND ISOLATED THE STATION. THE POWER GAS LINE WAS STEAM CLEANED TO DEFROST THEN RE-PRESSURED THE POWER GAS LINE AND PUT THE STATION BACK INTO SERVICE. CURRENTLY THE POWER GAS LINE COMES OFF THE SIDE OF THE 24" DISCHARGE LINE, THEN DIVES BELOW GROUND. TO PREVENT THIS FROM HAPPENING AGAIN, OPERATIONS PLANS TO RELOCATE THE POWER GAS LINE CLOSER TO THE SUCTION VALVE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210006 | 34995 | 2021-01-14 08:00 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2020-12-18 15:22 | 2020 | CENTRAL | NO | 33.0026 | -93.9451 | 1294597 | 2020-12-18 16:18 | 1294630 | NATURAL GAS |  | 22575 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-18 16:49 | 2020-12-19 05:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-18 16:02 | NO | [5 empty] | VALVE CLOSURE |  | 2020-12-18 16:30 | VALVE CLOSURE |  | 2020-12-18 16:49 | 0 | 2020-12-18 15:22 | 2020-12-18 16:40 | ONSHORE | LA | 71044 | IDA | CADDO | NOT APPLICABLE |  | LINE A-SOUTH | LINE A-SOUTH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.312 | 46000 | API 5LX | SEAMLESS |  | UNKNOWN | OTHER | WAX | YES | [26 empty] | 1947 | 1947 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 16 | 0.2 |  | CLASS 1 LOCATION | NO |  | 192 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 58469 | 102619.0612244897959183673469387755102041 | 101550 | 105662.23112427062685 | 5000 | 5202.473221283635 | 27000 | 28093.355394931629 | LAB ANALYSIS | 2.59 | 192019 | 128636.0789177765085243440233236151603499 | 241577.1209649756867683673469387755102041 | 0 | 0 | 0 | 0 | NO |  |  |  | 276 | 11 | 300 | 192.619(A)(1) |  | 2012-10-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 22964 | NO |  | YES |  |  |  | YES | DRESSER COUPLERS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE RUPTURE | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | YES | HOT CRACKING IN THE WELD | [19 empty] | YES | ACETYLENE GIRTH WELD | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [10 empty] | YES | [10 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 405 626 3981 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 405 626 3981 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 405 626 3981 | casey.roberts@enablemidstream.com | ON DECEMBER 18TH, 2020 AT 15:22 ENABLE GAS TRANSMISSION LINE A-SOUTH EXPERIENCED A FAILURE IN CADDO PARISH LOUISIANA. THE FAILURE WAS AT AN ORIGINAL ACETYLENE GIRTH WELD COMPLETED IN 1947. THE FAILED SECTION WAS REMOVED AND SENT TO A LAB FOR METALLURGICAL ANALYSIS. THE NRC WAS NOTIFIED ON 12/18/2020 (NRC # 1294597). A 48 HR FOLLOW UP CALL WAS PROVIDED TO THE NRC ON 12/20/2020 (NRC # 1294630). AT TIME OF REPORT SUBMISSION, ENABLE MIDSTREAM PARTNERS HAS NOT YET RECEIVED THE RESULTS OF THE LAB ANALYSIS. A SUPPLEMENTAL REPORT WILL BE FILED WHEN THE REPORT IS COMPLETED. 03.15.2021 UPDATE ON DECEMBER 18TH, 2020 AT 15:22 ENABLE GAS TRANSMISSION SYSTEM CONTROL DETECTED LOSS OF PRESSURE VIA SCADA FOR LINE A-SOUTH IN CADDO PARISH LOUISIANA. LOCAL OPERATIONS WAS IMMEDIATELY DISPATCHED TO LOCATE THE FAILURE. ENABLE RECEIVED A CALL FROM THE LOCAL EMERGENCY RESPONDER AT 16:02 NOTIFYING THEM OF THE EXACT FAILURE LOCATION. THE FAILURE WAS FOUND BY LOCAL PUBLIC WHO NOTIFIED THE LOCAL EMERGENCY RESPONDER. ENABLE OPERATIONS WERE ONSITE AT 16:40. THE FAILED SECTION WAS REMOVED AND SENT TO A LAB FOR METALLURGICAL ANALYSIS. THE LAB RESULTS PERFORMED ON THE SUBMITTED FRACTURED GIRTH WELD INDICATE THAT THE CAUSE OF FAILURE IS RELATED TO A TENSILE LOAD ACTING ON THE GIRTH WELD THAT HAD HOT CRACKING PRESENT IN THE ROOT AND CAP WELD METAL. THE INITIATION OF THE FRACTURE IS THOUGHT TO HAVE OCCURRED IN THE GIRTH WELD DUE TO THE REDUCED EFFECTIVE WALL THICKNESS IN THE GIRTH WELD METAL CAUSED BY THE PRESENCE OF HOT CRACKING AND STRESS RISERS CAUSED BY THE PRESENCE OF HOT CRACKING. THE TENSILE LOAD IS PRESUMED TO BE ASSOCIATED WITH CONSTRUCTION THAT OCCURRED ON A-SOUTH IN CLOSE PROXIMITY TO THE FAILED GIRTH WELD IN JUNE OF 2020. THE JUNE 2020 JOB CONSISTED OF INSTALLING 88 FEET OF PIPE TO REMEDIATE DRESSER COUPLES (DC) ON THE LINE. TO HELP STABILIZE THE LEGACY PIPE, 3 SLEEVES WERE INSTALLED UPSTREAM AND 3 SLEEVES WERE INSTALLED DOWNSTREAM ON ACETYLENE GIRTH WELDS (AGW) AND DC PRIOR TO THE NEW CONSTRUCTION. THE FAILURE LOCATION WAS A MISSED GIRTH WELD (FIRST ACETYLENE WELD DOWNSTREAM OF REPLACEMENT) WHICH WAS NOT IDENTIFIED PRIOR TO AND DURING CONSTRUCTION. TO INCREASE PIPE STABILITY THE STANDARD PRACTICE HAS BEEN TO INSTALL SLEEVES WHEN AGW ARE EXPOSED AND PRIOR TO CONSTRUCTION. THE 88-FOOT REPLACEMENT WAS PERFORMED IN JUNE 2020. THE SLEEVES WERE INSTALLED IN FEBRUARY OF 2020 IN ADVANCE OF THE PIPE REPLACEMENT PROJECT. THE PROCESS TO EXPOSE A GIRTH WELD IS TO REMOVE AS LITTLE DIRT AS POSSIBLE (TO LIMIT STRESS ON PIPE WHILE PRESSURIZED) UNTIL A AGW IS DISCOVERED AND A SLEEVE CAN BE INSTALLED. GOING FORWARD, ENABLE WILL UPDATE THEIR DC AND AGW PROCEDURES TO INCLUDE THE PRACTICE OF REMOVING ALL DIRT (WHILE THE PIPELINE SEGMENT IS FULLY EVACUATED) FROM THE LEGACY PIPE CUTOUT TO THE FIRST GIRTH WELD UPSTREAM AND DOWNSTREAM. THIS WILL ENSURE THE FIRST JOINT HAS NOT BEEN MISSED AND HAS THE REQUIRED INSTALLED SLEEVE PRIOR TO THE PIPE BEING RE-PRESSURIZED. 03.15.2021 SUPPLEMENTAL REPORT C.3E CHANGED TO SEAMLESS D.7D ADDED $27,000 G.2 ADDED HOT CRACKING H. UPDATED
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210007 | 34878 | 2021-01-20 13:48 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 2800 POST OAK BLVD | HOUSTON | TX | 77056 | 2020-12-20 23:28 | 2020 | PACIFIC | NO | 45.7243 | -121.49 | 1294705 | 2020-12-21 01:24 | 1294836 | NATURAL GAS |  | 1068 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-21 02:20 | 2020-12-23 14:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-12-21 00:08 | NO | [11 empty] | 1 | 2020-12-20 23:28 | 2020-12-21 01:05 | ONSHORE | WA | 98672 | WHITE SALMON | KLICKITAT | MILEPOST | 4.6 | HOOD RIVER METER STATION | HOOD RIVER LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1972 | 1972 | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 116 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 2670 | 4686.122448979591836734693877551020408163 | 1200000 | 1248593.5731080724 | 100000 | 104049.4644256727 | 0 | 0 | ECONOMIC IMPACT TO COMMUNITIES OF WHITE SALMON AND HOOD RIVER NOT CALCULATED | 2.5 | 1302670 | 599809.0842236295717201166180758017492711 | 1357329.15998272469183673469387755102041 | 1 | 0 | 0 | 1 | NO |  |  |  | 372 | 5150 | 946 | 192.619(A)(2) |  | 1972-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS THE RESULT OF A MOTOR VEHICLE INCIDENT INVOLVING AN IMPAIRED DRIVER COLLIDING WITH OUR FACILITY. FOR FURTHER INFORMATION REFERENCE FULL NARRATIVE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | YES | YES | YES | YES |  |  | UNKNOWN | 50 |  | PASSENGER CAR | ROADWAY | 70 | NO | [238 empty] | BRET BURKHART | ENGINEER SR. | bret.burkhart@williams.com | 8015846892 |  | LARRY WEST | larry.west@williams.com | 3606662141 | TYSON GREEN | MANAGER PIPELINE SAFETY | 7132152535 | tyson.green@williams.com | DETAILS FROM WILLIAMS OPERATOR LOG (12/20/2020 TO 12/21/2020): THE HOOD RIVER METER STATION ALARMED FOR "LOW LOW" AT 280 PSIG FROM 372PSIG. FLOW WENT FROM A RANGE OF 1800-8500MCFD JUMPING TO 10500MCFD BETWEEN SCANS. LOCAL OPERATIONS PERSONNEL WERE INITIALLY CONTACTED AT 11:35PM (LOCAL TIME). WILLIAMS CONTACTED NORTHWEST NATURAL AT 11:45PM LOCAL TIME, AND THEY REPORTED SEEING ABNORMAL FLUCTUATIONS AS WELL. SOON AFTERWARDS A NORTHWEST NATURAL REPRESENTATIVE CALLED BACK TO REPORT THAT A CAR HAD CRASHED INTO THE METER STATION AND THAT THE KLIKITAT FIRE DEPARTMENT WAS CLOSING THE HOOD RIVER BRIDGE AT HWY 14. AT 12:08PM KLICKITAT EMERGENCY DISPATCH CALLED TO LET US KNOW ABOUT THE INCIDENT AND ALSO REPORTED A STRONG ODOR OF GAS AND LOUD NOISE. AT 12:17PM THE LOCAL DISTRICT MANAGER WAS INFORMED OF THE SITUATION, AND ADDITIONAL LOCAL PERSONNEL WERE DISPATCHED. AT 12:36PM THE INCIDENT WAS REPORTED TO WILLIAMS SAFETY OPERATIONS CENTER. AT ABOUT 1:00AM TECHNICIANS FROM NORTHWEST NATURAL AND WILLIAMS ARRIVED ON SITE. AT 1:35AM IT WAS DETERMINED THAT THE LATERAL FEEDING THE STATION WOULD NEED TO BE COMPLETELY SHUT-IN TO ISOLATE THE INCIDENT. AT 2:20AM VALVES 75-0 AND 75-0X WERE CLOSED TO ISOLATE THE LATERAL, AND BY 3:15AM THE FLOW AND PRESSURE REACHED 0. BY 2PM THAT DAY THE STATION WAS ISOLATED AT ITS TAP VALVE, AND THE LATERAL WAS RE-PACKED IN ANTICIPATION OF A MOBILE METER STATION, AND REPAIRS/RETURN TO SERVICE OF THE PERMANENT FACILITY. CASE SUMMARY FROM DEPUTY REPORT FOR INCIDENT 20-B1728: "ON 12/20/2020, AT ABOUT 2330 HOURS, I WAS DISPATCHED TO AN MVC INVOLVING UNKNOWN INJURIES NEAR BRIDGEMART ON HWY 14. ON ARRIVAL AT THE COLLISION SCENE, I OBSERVED A VEHICLE THAT APPEARED TO HAVE COLLIDED WITH A GAS PLANT LOCATED ON THE NORTH SIDE AT THE INTERSECTION OF HWY 14 AND THE HOOD RIVER BRIDGE. I ATTEMPTED TO MAKE CONTACT WITH THE VEHICLE, BUT WAS UNABLE TO DUE TO MULTIPLE POTENTIAL HAZARDS. LOCAL FIRE DEPARTMENTS, EMS, AND LAW ENFORCEMENT AGENCIES ARRIVED TO ASSIST WITH VARIOUS TASKS. NW NATURAL, OWNER OF THE GAS PLANT, SENT CREWS TO SHUT OFF LINES THAT WERE DAMAGED AND RELEASING GAS INTO THE SURROUNDING ATMOSPHERE. THIS CREATED A HAZARDOUS RISK FOR ANYONE WITHIN .5 MILES OF THE COLLISION SCENE. THE DRIVER OF THE VEHICLE, BENJAMIN SOLORIO, WAS ABLE TO SELF EXTRICATE AND MAKE CONTACT WITH A WASHINGTON STATE PATROL TROOPER. SOLORIO WAS EVALUATED BY EMS AND TAKEN TO SKYLINE HOSPITAL ER, WHERE HE WAS TREATED FOR MINOR INJURIES. IT WAS DETERMINED BY THE WSP TROOPER THAT SOLORIO WAS DRIVING UNDER THE INFLUENCE OF ALCOHOL DURING THE TIME OF THE COLLISION AND AT AN EXCESS SPEED OF AT LEAST TWICE THAT OF THE POSTED SPEED LIMIT, 25 MPH OR MORE, ON THE HOOD RIVER BRIDGE AND THROUGH THE INTERSECTION AT HWY 14. ALL AGENCIES INVOLVED TOOK APPROPRIATE PRECAUTIONS, AND THE COLLISION SCENE WAS HANDLED PER STANDARD PROTOCOLS. THE COMMUNITY, INCLUDING THE SURROUNDING COMMUNITY OF HOOD RIVER, OR. WAS GREATLY AFFECTED BY THIS INCIDENT. MANY WERE... LEFT WITHOUT NATURAL GAS FOR HEATING, COOKING, ETC. SOLORIO WAS PROCESSED FOR DUI THE NIGHT OF THE INCIDENT AND CITED FOR RECKLESS DRIVING ON 12/27/2020" ADDITIONAL DETAIL FROM POLICE REPORT: "BRIDGEMART WAS CLOSED AND THE STORE EMPLOYEE WAS ADVISED TO EVACUATE. THE RESIDENTS STAYING AT THE RV PARK WERE ALSO ADVISED TO STAY CLEAR OF THE INCIDENT AS FAR AWAY AS POSSIBLE. RESIDENCES NORTH OF THE COLLISION, INCLUDING SE OAK ST FROM SE 1ST TO SE 7TH ST, WERE ADVISED TO SHELTER IN PLACE BY CLOSING ALL DOORS AND WINDOWS. DISPATCH ASSISTED BY USING A REVERSE 911 SYSTEM TO ADVISE AND FIRE UNITS ALSO WENT DOOR-TO-DOOR TO RESIDENCES." A TEMPORARY SKID, PROVIDING PRESSURE REGULATION AND METERING, WAS PUT INTO SERVICE ON 12/23/2020 TO RETURN SERVICE TO THE CUSTOMER. THIS WILL REMAIN IN SERVICE UNTIL A FULL METER STATION REBUILD (PLANNED FOR SUMMER 2021) CAN BE COMPLETED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210008 | 34864 | 2021-01-21 09:37 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2020-12-24 15:19 | 2020 | CENTRAL | NO | 41.9007 | -96.5246 | 1294941 | 2020-12-24 16:11 | 1295014 | NATURAL GAS |  | 8180 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-24 16:41 | 2020-12-26 22:29 |  |  |  |  | YES | 2020-12-24 15:19 | ALLOWED TO BURN OUT |  | 8180 | YES | VALVE CLOSURE |  | 2020-12-24 16:37 | VALVE CLOSURE |  | 2020-12-24 16:41 | 0 | 2020-12-24 15:20 | 2020-12-24 16:00 | ONSHORE | NE | 68038 | Not Within a Municipality | BURT | MILEPOST | 21.32 | HOOPER TO SOUTH SIOUX CITY C-LINE | NEM50103-M570C | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.312 | 52000 | 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | AO SMITH | COAL TAR |  | YES | [26 empty] | 1961 | 1961 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 102 | 72 |  | CLASS 1 LOCATION | NO |  | 468 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 21922 | 38475.3469387755102040816326530612244898 | 100000 | 104049.4644256727 | 50000 | 52024.73221283635 | 0 | 0 |  | 2.68 | 171922 | 94099.4099199500817784256559766763848397 | 194549.5435772845602040816326530612244898 | 0 | 0 | 0 | 0 | NO |  |  |  | 745 | 225 | 800 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 70072 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 203021735 |  | UTILITY OWNER | NO | NO | YES | 36 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [119 empty] | YES | YES |  |  | YES |  |  |  | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [27 empty] | 2020 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [18 empty] | YES | NO |  |  | NO | [13 empty] | YES |  |  |  | 2020 | [6 empty] | YES | [51 empty] | YES | JOHN GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  | JOHN GORMLEY | john.gormley@nngco.com | 402-398-7494 | TOM CORRELL | VP PIPELINE SAFETY AND RISK | 402-398-7715 | thomas.correll@nngco.com | AT 15:19 ON DECEMBER 24, 2020, NORTHERN NATURAL GAS RECEIVED NOTIFICATION FROM THE LYONS NE VOLUNTEER FIRE DEPARTMENT OF A PIPELINE RUPTURE SOUTH OF COUNTY ROAD P IN BURT COUNTY, NEBRASKA. THE RUPTURED LINE WAS IDENTIFIED AS THE 179NEM50103-M570C HOOPER TO SOUTH SIOUX CITY C-MAINLINE AT MILEPOST 21.32. THIS LOCATION IS 3.8 MILES SOUTH OF THE NEB56001 LYONS, NEBRASKA BRANCH LINE TAKE-OFF. OPERATIONS STAFF ISOLATED THE RUPTURED SEGMENT AT 16:46 HOURS AFTER 8.18 MILLION CUBIC FEET OF GAS LOSS. INITIAL OBSERVATIONS BY THE FIELD INVESTIGATION TEAM INDICATED THE FAILURE MAY HAVE BEEN CAUSED BY PREVIOUS THIRD PARTY DAMAGE. THE FIELD INVESTIGATION TEAM IDENTIFIED A SERIES OF GOUGES AND SCORES ACROSS A SEGMENT OF PIPE WHICH WAS FOUND ABOUT 100 YARDS SOUTH OF THE FAILURE SITE. THE ROOT CAUSES OF THIS EVENT ARE A THIRD PARTY CONTRACTOR COMMENCING EXCAVATION PRIOR TO THE CLEARING OF A ONE CALL TICKET. THERE WERE TWO ONE CALL TICKETS REGARDING THIS PROPERTY. ONE FOR OCT 30 TO CLEAR TREES AND REMOVE TERRACES AND ONE FROM DEC 4 TO BURY LEFT OVER DEBRIS FROM A BURN PILE. THE DAMAGE TO THE PIPELINE PROBABLY OCCURRED AT THE OCT 30 WORK. A CONTRIBUTING FACTOR WAS A FIELD OPERATIONS FAILURE TO FOLLOW NORTHERN PROCEDURE BY GIVING VERBAL APPROVAL FOR EXCAVATION ACTIVITIES IN PROXIMITY TO A PIPELINE BEGIN BEFORE THE EMPLOYEE ARRIVED ON SITE. BOTH TIMES THE ONE CALL TICKETS WERE COMPLETED BY THE SAME EMPLOYEE AND THE PIPELINES MARKED IN ACCORDANCE WITH COMPANY PROCEDURES. THE EMPLOYEE REMAINED ON SITE UNTIL ALL WORK WAS COMPLETED. NORTHERN NATURAL GAS MOBILIZED THE EMERGENCY RESPONSE TEAM AND CONSTRUCTION RESOURCES TO THE INCIDENT SITE AND COMPLETED REPAIRS AT 22:29 HOURS DECEMBER 25, 2020.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210009 | 35255 | 2021-01-23 10:01 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2020-12-26 05:21 | 2020 | EASTERN | NO | 32.6133 | -84.8203 | 1295001 | 2020-12-26 06:43 | 1295064 | NATURAL GAS |  | 85900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2020-12-26 06:30 | 2020-12-26 22:15 |  | NO |  |  | NO | [11 empty] | 0 | 2020-12-26 05:19 | 2020-12-26 06:04 | ONSHORE | GA | 31807 | Not Within a Municipality | HARRIS | MILEPOST | MP 311 - 30+4 | ELLERSLIE COMPRESSOR STATION | SOUTH MAIN LINE SYSTEM, | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1958 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 860 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 226862 | 398165.9591836734693877551020408163265306 | 12518 | 13024.911956805708586 | 3604 | 3749.942697901244108 | 2505 | 2606.439083863101135 | METALLURGICAL LAB COSTS | 2.641 | 245489 | 269805.3573938302466362944606413994169096 | 417547.2529222435232167551020408163265306 | 0 | 0 | 0 | 0 | NO |  |  |  | 856 | 1743 | 1200 | 192.619(C) |  | 1953-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [12 empty] | YES | [174 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 |  | CAROL PARRAMORE | carol_parramore@kindermorgan.com | 2292264744 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON DECEMBER 26, 2020, SOUTHERN NATURAL GAS COMPANY (SNG) COMPRESSOR STATION KNOWN AS ELLERSLIE COMPRESSOR STATION ON THE SOUTH MAIN SYSTEM NEAR MILEPOST 311 EXPERIENCED AN EMERGENCY SHUT DOWN (ESD) EVENT. AT 05:19-HOURS, GAS CONTROL RECEIVED A SCADA ALARM. THE CONTROLLER ON DUTY, USING THE CALL-OUT SYSTEM, NOTIFIED THE PROPER OPERATIONS PERSONNEL AT THAT TIME. AT 06:04-HOURS, OPERATIONS PERSONNEL ARRIVED AT ELLERSLIE COMPRESSOR STATION AND CONFIRMED NATURAL GAS WAS VENTING. UPON SAFELY ENTERING THE COMPRESSOR STATION PROPERTY, THE OPERATIONS PERSONNEL BEGAN INSPECTING THE COMPRESSOR STATION TO DETERMINE WHY NATURAL GAS WAS STILL VENTING FOLLOWING THE ESD FUNCTION. OPERATIONS PERSONNEL FOUND VALVE #19 WHICH IS PART OF THE ESD SYSTEM LOCATED IN THE SUCTION SIDE OF THE STATION PIPING, HAD NOT FULLY CLOSED. OPERATIONS PERSONNEL MANUALLY CLOSED VALVE #19 AND THE STATION WAS SHUT DOWN AT 6:30-HOURS. FIELD OPERATIONS INITIATED THE EMERGENCY RESPONSE LINE (ERL) PROCESS FOLLOWING INTERNAL PROCEDURES AND THE INCIDENT WAS DEEMED REPORTABLE DURING THE ERL CALL. AS PART OF SNG'S POST INCIDENT INVESTIGATION PROCESS THE OPERATIONS PERSONNEL ON SITE DISCOVERED AN EXIT POINT IN THE COMPRESSOR STATION YARD WITH SOME ICE FORMED NEAR AN UNDERGROUND ESD FACILITY PIPE. SNG STARTED THE EXCAVATION PROCESS TO IDENTIFY THE SOURCE OF THE UNDERGROUND LEAK. AFTER EXPOSING THE UNDERGROUND ESD PIPE, SNG DISCOVERED THAT THE 1/2-INCH ESD PIPE HAD A CRACK IN A THREADED CONNECTION. DURING THE ROOT-CAUSE ANALYSIS IT WAS DETERMINED THAT THE CRACKED UNDERGROUND ESD PIPE WAS THE CAUSE OF THE ESD EVENT. FURTHERMORE, THE ANALYSIS ALSO REVEALED THAT VALVE #19 DID NOT FULLY CLOSE AS DESIGNED ALLOWING THE VOLUME OF GAS RELEASED TO BE ABOVE THE PHMSA REPORTABLE THRESHOLD. OPERATIONS MANAGEMENT EXPEDITED A CONTRACTOR TO COME ON SITE AND REPAIR THE BURIED 1/2-INCH ESD LINE. THE CRACKED PIPE WAS SENT TO A LAB FOR FURTHER ASSESSMENT AND THE LINE REPAIR WAS COMPLETED ON DECEMBER 26, 2020. OPERATIONS PERSONNEL CHECKED AND CYCLED VALVE #19 WITH NO ISSUE. VALVE #19 IS CLOSED AND LOCKED OUT OF SERVICE. SNG OPERATIONS HAS ORDERED A NEW SHAFER OPERATOR FOR 2021 INSTALLATION. WITH GENERAL SAFETY INSPECTION OF THE COMPRESSOR STATION AND COORDINATION WITH GAS CONTROL, THE COMPRESSOR STATION RETURNED TO SERVICE AT 22:15-HOURS, DECEMBER 26, 2020. THE LABORATORY ANALYSIS OF THE 1/2-INCH ESD LINE PIPE SPECIMEN DETERMINED THE CRACK OCCURRED BECAUSE OF HIGH CYCLE, LOW NOMINAL STRESS BENDING FATIGUE INITIATING IN THE ROOT OF THE THREADS. THE ANALYSIS ALSO NOTED THE STEEL PIPE CHEMISTRY DID NOT MEET ASTM A53 GRADE B STANDARDS DUE TO HIGHER PHOSPHORUS CONTENT. HOWEVER, TESTING FOUND THE TENSILE STRENGTH OF THE STEEL MEETS THE MINIMUM REQUIREMENTS OF ASTM A53 GRADE B. THE 1/2-INCH ESD LINE WAS PROMPTLY REPAIRED TO RETURN THE STATION TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210010 | 37243 | 2021-01-27 10:10 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2021-01-02 09:30 | 2021 | CENTRAL | YES | 35.7281 | -98.8014 | 1295377 | 2021-01-02 11:05 | 1295443 | NATURAL GAS |  | 127718.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-02 09:34 | 2021-01-04 12:00 |  | NO |  |  | NO | [11 empty] | 0 | 2021-01-02 09:30 | 2021-01-02 09:30 | ONSHORE | OK | 73669 | Not Within a Municipality | CUSTER | NOT APPLICABLE |  | THOMAS COMPRESSOR STATION | M-2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2015 | 2015 | CARBON STEEL |  | OTHER | [8 empty] | THE RELEASE OCCURRED THROUGH THE RELIEF VALVE. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 291837 | 291837 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2.285 | 291837 | 191487.7325581395348837209302325581395349 | 291837 | 0 | 0 | 0 | 0 | NO |  |  |  | 868 | 15 | 985 | 192.619(A)(1) |  | 2015-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE WAS DUE TO FIELD RELATED ISSUES. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | ROOT VALVE ON TRANSMITTER WAS CLOSED |  | YES |  | YES | ROOT VALVE FOR TRANSMITTER WAS CLOSED. | ROUTINE MAINTENANCE | NO | [150 empty] | PAULA GATES RIPPE | COMPLIANCE SPECIALIST | paula.gatesrippe@oneok.com | 5807471324 |  | PAULA GATES RIPPE | paula.gatesrippe@oneok.com | 5807471324 | RANDY MASHBURN | OPERATIONS MANAGER | 918-497-8407 | randy.mashburn@oneok.com | 10/20/22 UPDATE: ADDED COUNTY 5/21/21 UPDATE: JAN. 2ND, 2021 ONEOK EMPLOYEE IDENTIFIED THE OGT THOMAS COMPRESSOR WAS VENTING GAS TO ATMOSPHERE AT APPROXIMATELY 9:20AM. EMPLOYEE INITIATED ESD OF THE STATION AT 9:34AM. THE STATION LOGS IDENTIFIED VENTING BEGAN APPROXIMATELY AT 12:39AM. IT WAS DETERMINED THAT LOSS OF INSTRUMENT AIR ALLOWED THE STATION ESD SUCTION & DISCHARGE VENT VALVES TO OPEN RELEASING GAS. THE ONEOK INVESTIGATION DISCOVERED THE LOSS OF INSTRUMENT AIR WAS NOT IDENTIFIED BECAUSE THE INSTRUMENT AIR PRESSURE TRANSMITTER MANIFOLD VALVE WAS FOUND IN CLOSED POSITION. AN ONEOK EMPLOYEE HAD INSPECTED THE VALVE IN APRIL AND THE VALVE WAS IN THE CORRECT POSITION. SINCE APRIL THERE WAS NUMEROUS MAINTENANCE AND CONSTRUCTION ACTIVITIES AT THOMAS COMPRESSOR FACILITY. KNOWING THE VALVE WAS IN THE PROPER POSITION IN APRIL, THEN CLOSED AT THE TIME OF THE RELEASE, WITH THE OTHER ACTIVITIES THAT TOOK PLACE AT THE FACILITY, ONEOK IS UNABLE TO DETERMINE WHO CLOSED THE VALVE OR WHEN THE VALVE WAS CLOSED. AFTER COMPLETION OF THE INVESTIGATION, THE THOMAS COMPRESSOR WAS RETURNED TO SERVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210011 | 35143 | 2021-02-11 09:17 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-01-27 10:30 | 2021 | CENTRAL | NO | 32.0841 | -95.1518 | 1296806 | 2021-01-27 12:08 | 1296886 | NATURAL GAS |  | 487 | 395 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK ONLY |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | MINOR LEAK ONLY. NO ACTION TAKEN |  | OPERATIONAL CONTROL | MINOR LEAK ONLY. NO ACTION TAKEN |  | 0 | 2021-01-27 10:30 | 2021-01-27 12:08 | ONSHORE | TX | 75789 | Not Within a Municipality | CHEROKEE | SURVEY STATION NO. | 1898+44 | LONGVIEW CS TO BOGGY CREEK TO HUNTSVILLE ML | INDEX 11 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | EXISTING SPLIT SLEEVE/CLAMP | [5 empty] | CLASS 1 LOCATION | NO |  | 121 |  | NO | NO | [5 empty] | 0 | 0 | 976 | 995.666666666666944 | 1203 | 1203 | 82500 | 84162.39754098363 | 0 | 0 | 0 | 0 |  | 2.47 | 84679 | 38357.8202882468507786445182724252491694 | 86361.064207650296944 | 0 | 0 | 0 | 0 | NO |  |  |  | 345 | 8000 | 430 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 33992 | NO |  | YES | YES |  |  | YES | NO PIG TRAPS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | SPLIT SLEEVE/CLAMP |  |  |  | YES | [174 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | GULF SOUTH'S GAS CONTROL RECEIVED A CALL ON 1/27/21 AT 10:30 AM REPORTING A POTENTIAL LEAK. OPERATIONS PERSONNEL RESPONDED AT 12:08 PM AND CONFIRMED THE LEAK. UPON EXCAVATION, A LEAKING CLAMP AND SPLIT SLEEVE WERE FOUND. AFTER INSPECTING THE LEAK AND PIPELINE, THE LEAK WAS CONSIDERED GRADE 3 (MINOR LEAK) AND GULF SOUTH WILL CONTINUE TO MONITOR UNTIL REPAIRED. GULF SOUTH IS IN THE PROCESS OF SCHEDULING A SHUTDOWN TO REPLACE PIPE AND MUST COORDINATE WITH CENTERPOINT BECAUSE THEY HAVE TO PROVIDE CNG TRUCKS AT CITY GATES TO PREVENT ANY CUSTOMER LOSS. GULF SOUTH DETERMINED THAT THE REPAIR WOULD BE PIPE REPLACEMENT WHICH WOULD EXCEED $50,000 AND MADE THE REQUIRED NRC NOTIFICATION. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED ONCE REPAIRS ARE COMPLETED. UPDATE 3/29/2021: PIPE WAS REPLACED ON 3/10/2021. REPORT UPDATED TO ADJUST COST AND INCLUDE BLOWDOWN GAS LOSS DURING REPAIR. REPORT IS ALSO REVISED TO UPDATE ANSWERS TO QUESTIONS A4, A13, AND E2B AS REQUESTED BY PHMSA.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210012 | 36008 | 2021-02-11 13:59 | SUPPLEMENTAL FINAL | 32655 | EAST CHEYENNE GAS STORAGE, LLC | 34511 COUNTY ROAD 39 | PEETZ | CO | 80747 | 2021-01-18 14:53 | 2021 | MOUNTAIN | NO | 40.9416 | -103.2205 | 1296264 | 2021-01-18 16:10 | 1296366 | NATURAL GAS |  | 384 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-18 14:53 | 2021-01-20 20:59 |  | YES | OPERATOR | 2021-01-18 17:39 | NO | [11 empty] | 0 | 2021-01-18 14:53 | 2021-01-18 14:53 | ONSHORE | CO | 80747 | Not Within a Municipality | LOGAN | NOT APPLICABLE |  | EAST CHEYENNE GAS STORAGE | UNGS FACILITY - COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 20 | NO | 0.594 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | SALZGITTER MANNESMANN | PAINT |  | NO | [26 empty] | 2012 | 2012 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 1018 | 1018 | 15000 | 15302.25409836066 | 0 | 0 | 0 | 0 |  | 2.65 | 16018 | 7418.72525325418423588039867109634551495 | 16320.25409836066 | 0 | 0 | 0 | 0 | NO |  |  |  | 1000 | 0 | 1440 | 192.619(A)(1) |  | 2012-08-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | YES | OTHER | LOUD NOISE FROM THE FACILITY HEADER BLOWDOWN |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | HYDRATE FORMATION INSIDE FACILITY PIPING | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | OTHER | HYDRATE FORMATION IN FACILITY PIPING | NO | [295 empty] | YES | [10 empty] | JOE CARDOSO | PHMSA COMPLIANCE SPECIALIST | joe.cardoso@enstorinc.com | 832-933-8383 |  | CHASE BENNETT | chase.bennett@enstorinc.com | 970-580-1726 | TODD CASH | VICE PRESIDENT COMPLIANCE | 281-374-3085 | todd.cash@enstorinc.com | ON THE AFTERNOON OF MONDAY, JANUARY 18 AT APPROXIMATELY 14:53 MOUNTAIN TIME ENSTOR PERSONNEL RESPONDED TO AN INCIDENT (LOUD AUDIBLE NOISE) AT THE EAST CHEYENNE GAS STORAGE FACILITY, LOCATED IN A REMOTE AREA MORE THAN 20 MILES NORTH OF STERLING, COLORADO. NO INJURIES OR FATALITIES OCCURRED. THE FACILITY SUSTAINED MINOR PIPING DAMAGE WHEN SOME ICE THAT HAD COLLECTED IN A SECTION OF PIPE GAVE WAY WHILE THE LINE WAS BEING PRESSURED UP FOR USE AND DAMAGED A BLOWDOWN VALVE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210013 | 35123 | 2021-02-15 10:41 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-01-23 09:34 | 2021 | CENTRAL | NO | 29.9617 | -91.7881 | 1296876 | 2021-01-28 09:55 | 1296952 | NATURAL GAS |  | 2 | 99 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REDUCED PRESSURE BY 20% |  |  |  | YES | OPERATOR | 2021-01-28 08:55 | NO | [5 empty] | OPERATIONAL CONTROL | REDUCED PRESSURE BY 20% |  | OPERATIONAL CONTROL | REDUCED PRESSURE BY 20% |  | 0 | 2021-01-28 08:30 | 2021-01-28 08:30 | ONSHORE | LA | 70560 | Not Within a Municipality | IBERIA | MILEPOST | 138.15 | IOWA TO FRANKLIN | INDEX 205 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 45 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | MECHANICAL COUPLING | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 128 |  | NO | NO | [5 empty] | 0 | 0 | 245 | 249.93681693989078 | 5 | 5 | 134950 | 137669.2793715847378 | 0 | 0 | 0 | 0 |  | 2.47 | 135200 | 60847.9567042577033817774086378737541528 | 137924.21618852462858 | 0 | 0 | 0 | 0 | NO |  |  |  | 254 | 1800 | 480 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 21397 | NO |  | YES | YES | YES |  | YES | NO PIG TRAPS, PIPE CONNECTED WITH COUPLINGS AND ACETYLENE WELDS | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | MINOR PIPELINE MOVEMENT DUE TO TEMPERATURE CHANGES CAUSED MINOR SEEPAGE OF GAS | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 1/23/21, A GULF SOUTH TECHNICIAN, WHO WAS PERFORMING ROUTINE INSPECTIONS USING A LASER LEAK DETECTION DEVICE, FOUND A GAS LEAK INDICATION. FIELD OPERATIONS PERSONNEL MONITORED THE SITE UNTIL THE POTENTIAL LEAK COULD BE VERIFIED. ON 1/25/21 THE PRESSURE WAS LOWERED FROM 254 PSIG TO 200 PSIG IN PREPARATION FOR EXCAVATION DUE TO THE LINE BEING CONSTRUCTED WITH MECHANICAL COUPLINGS. ON 1/28/21, THE LINE WAS EXPOSED AND A MINOR LEAK THROUGH A DRESSER COUPLE WAS CONFIRMED. THE PIPELINE BELL HOLE WAS BACKFILLED AND PROPER NOTIFICATIONS WERE MADE INCLUDING AN NRC NOTIFICATION DUE TO THE ANTICIPATED REPAIR COST EXCEEDING $50,000. THE LEAK REPAIR WILL REQUIRE THE PIPELINE TO BE SHUT DOWN. ON 1/28/21, GULF SOUTH CONTACTED CENTERPOINT ENERGY TO COORDINATE ALTERNATIVE GAS SUPPLY FOR THEIR CUSTOMERS DURING THE OUTAGE. THE REPAIR IS CURRENTLY SCHEDULED FOR 2/24/21 BUT THAT IS CONTINGENT ON WEATHER/TEMPERATURES. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED ONCE REPAIRS ARE COMPLETE. 4/2/21 UPDATE A4 TO BE WHEN LEAK WAS DISCOVERED RATHER THAN WHEN IT MET REPORTING CRITERIA AS REQUESTED BY PHMSA; UPDATE GAS LOSS TO INCLUDE INTENTIONAL GAS LOSS; AND UPDATE COST.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210014 | 34873 | 2021-02-18 09:14 | ORIGINAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2021-01-19 15:20 | 2021 | CENTRAL | NO | 32.6814 | -99.8031 | 1296316 | 2021-01-19 16:17 | 1296448 | NATURAL GAS |  | 1667.5 | 0.89 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | INSTALLED TWO 12 INCH STOPPLE FITTINGS AND BUILT A BY-PASS BETWEEN THEM |  |  |  | YES | OPERATOR | 2021-01-19 11:00 | NO | [5 empty] | OPERATIONAL CONTROL | NO ACTION REQUIRED. UPSTREAM PIPELINE PRESSURE AND FLOW WERE ADEQUATE |  | OPERATIONAL CONTROL | USED STEEL SQUEEZERS ON 1 INCH TAP TO SQUEEZE OFF LEAK |  | 0 | 2021-01-19 10:03 | 2021-01-19 10:17 | ONSHORE | TX | 79525 | HAWLEY | JONES | SURVEY STATION NO. | 936+67 | KC 17 1" FARM TAP | N/A | NO | PIPELINE RIGHT-OF-WAY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 1.25 | NO | 0.126 | 24000 | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1953 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | VALVE KNOCKED OFF OF 1.25" RISER | CLASS 1 LOCATION | NO |  | 24 |  | NO | NO | [5 empty] | 0 | 0 | 5 | 5.10075136612022 | 9785 | 9785 | 161563 | 164818.538592896220772 | 0 | 0 | 0 | 0 |  | 5.868 | 171353 | 79134.2674146288778793887043189368770764 | 174608.639344262340992 | 0 | 0 | 0 | 0 | NO |  |  |  | 650 | 0 | 800 | 192.619(A)(1) |  | 1953-12-14 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 37561 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL TO BE PICKED UP BY CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | YES | ACTIVITY IS EXEMPT AND DID NOT EXCEED THE LIMITS OF THE EXEMPTION |  | RAILROAD COMMISSION OF TEXAS | FARMER WAS TILLING AT A DEPTH OF LESS THAN 16 INCHES | NO |  |  |  |  | YES | [6 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | NO |  | ABANDONED FACILITY | [266 empty] | ROBERT O'DELL | OPERATIONS SUPERVISOR | robert.odell@atmosenergy.com | 325-280-1778 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON JANUARY 19, 2021, A FARMER STRUCK A FARM TAP OFF OF LINE KC 17 WITH A PLOW NEAR HAWLEY, TEXAS. ATMOS ENERGY WAS NOTIFIED OF THE INCIDENT AT 10:03 AM, AT WHICH POINT WORK BEGAN TO DETERMINE HOW TO MAKE REPAIRS. THE DECISION WAS MADE TO SQUEEZE OFF THE 1.25" STEEL RISER AND AFTER THE SQUEEZE OFF OCCURRED AT APPROXIMATELY 1 PM, IT WAS DISCOVERED THAT A THREADED CONNECTION WAS LEAKING UNDER THE SQUEEZED OFF SECTION OF THE RISER. WORK THEN BEGAN ON A BYPASS ON KC17 TO ENSURE CONTINUED SERVICE ON THE LINE. AT THE POINT IT WAS DETERMINED A BYPASS WOULD BE NEEDED TO MAKE THE NECESSARY REPAIRS, IT WAS ANTICIPATED THAT THE COST ASSOCIATED WITH REPAIRING THE DAMAGE WOULD EXCEED $50,000. A CALL WAS MADE TO THE NATIONAL RESPONSE CENTER AT 16:17 CT ON 1/19/2021. STOPPLES WERE WELDED ON FOR THE BYPASS, WHICH WAS COMPLETED ON JANUARY 20, 2021. ON JANUARY 21, 2021, 5 FEET OF 12" PIPE WAS REPLACED AND LINE KC17 WAS THEN RETURNED TO NORMAL OPERATION.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20210015 | 35131 | 2021-02-26 09:57 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2021-02-22 09:29 | 2021 | MOUNTAIN | NO | 36.9872 | -107.8759 | 1298777 | 2021-02-23 10:25 | 1298593 | NATURAL GAS |  | 587 | 172 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-16 12:00 | 2021-01-31 17:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-01-16 12:05 | VALVE CLOSURE |  | 2021-01-16 12:10 | 0 | 2021-01-16 12:00 | 2021-01-16 12:00 | ONSHORE | NM | 87410 | Not Within a Municipality | SAN JUAN | SURVEY STATION NO. | 223+41 | MD-7 LOOP | MD-7 LOOP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 16 |  | 0.188 | 52000 | API-5L-X-52-52000 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [7 empty] | PIPE GIRTH WELD |  | YES | 0.375 | 52000 | API-5L-X-52-52000 | SEAMLESS |  | US STEEL | EPOXY OTHER THAN FBE |  | YES | [7 empty] | 1997 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 175 |  | NO | NO | [5 empty] | 0 | 0 | 258 | 263.198770491803352 | 881 | 881 | 85000 | 86712.77322404374 | 0 | 0 | 0 | 0 |  | 1.5 | 86139 | 38948.5325094630159721794019933554817276 | 87856.971994535543352 | 0 | 0 | 0 | 0 | NO |  |  |  | 85 | 3000 | 250 | 192.619(A)(1) |  | 1997-01-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 23543 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK DID NOT GENERATE ANY ALARMS AND PIPELINE CONTROL CANNOT ACTUATE EQUIPMENT ON THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [12 empty] | YES |  | YES | [8 empty] | 1054 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | YES | 2018 | [6 empty] | YES | [33 empty] | YES | YES | [20 empty] | GORDON WILLIAMS | ENGINEER - PIPELINE COMPLIANCE | gswilliams@eprod.com | 713-381-6211 |  | GORDON WILLIAMS | gswilliams@eprod.com | 713-381-6211 | GORDON WILLIAMS | ENGINEER - PIPELINE COMPLIANCE | 713-381-6211 | gswilliams@eprod.com | ON JANUARY 16, AN ENTERPRISE TECHNICIAN PATROLLING LINE MD-7 LOOP DETECTED A GAS LEAK IN A CLASS 2 LOCATION. THE LINE MD-7 LOOP WAS ISOLATED AND DE-PRESSURED. ON THE SAME DAY, THE NMPRC WAS NOTIFIED BECAUSE ENTERPRISE BELIEVED THE COST TO REPAIR THE LINE MAY EXCEED THE $5,000 BUT LESS THAN $50,000 AT THE TIME. THE FAILED WELD WAS EXAMINED AND IT WAS DETERMINED THE WELD FAILED DUE TO CRACKING ALONG THE TOE OF THE WELD. ON FEBRUARY 22, 2021, ENTERPRISE RECEIVED AN UPDATED INVOICE WHICH EXCEEDED THE ORIGINAL ESTIMATE AND, CONSEQUENTLY, RESULTED IN THE RELEASE MEETING THE DEFINITION OF AN INCIDENT PER §191.3 DUE TO THE COST EXCEEDING $50,000. MITIGATIVE MEASURES TAKEN TO PREVENT THE RECURRENCE WERE TO EXPANDED THE EXCAVATION TO RELIEVE BENDING STRESS AND THE PIPELINE WAS CUT-OUT AND REPLACED. LINE MD-7 LOOP WAS PLACED BACK INTO SERVICE ON 1/31/2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210016 | 34958 | 2021-03-02 12:48 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2021-02-15 00:26 | 2021 | EASTERN | NO | 41.5127 | -77.984 | 1298052 | 2021-02-15 15:26 | 1298166 | NATURAL GAS |  | 5100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-15 00:40 | 2021-02-15 02:00 |  | NO |  |  | NO | [11 empty] | 0 | 2021-02-15 00:26 | 2021-02-15 00:27 | ONSHORE | PA | 16720 | Not Within a Municipality | POTTER | MILEPOST | 9.4763 | STATION 535 | LLWSA-T-T-T | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2019 | 2018 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STEEL TUBING/PILOT LINES, O-RINGS | OTHER | [8 empty] | FROZEN PILOT/SENSING LINES ON A PRESSURE SAFETY VALVE (PSV) CAUSED IT TO MALFUNCTION AND ACTIVATE AT A PRESSURE LOWER THAN IT'S SET POINT PRESSURE. | CLASS 1 LOCATION | NO |  | 234 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 9824 | 9824 | 100 | 102.0150273224044 | 0 | 0 | 650 | 663.0976775956286 | LABOR FOR TWO OPERATIONS TECHNICIANS FOR 10 HOURS TO REPAIR PSV. | 2.456 | 10574 | 6783.518488576330474252491694352159468439 | 10589.112704918033 | 0 | 0 | 0 | 0 | NO |  |  |  | 1038 | 0 | 1200 | 192.619(A)(3) |  | 2002-09-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ROOT CAUSE OF THE INCIDENT WAS CLEARLY DUE TO FROZEN PHYSICAL PILOT LINES WHICH HAVE NO IMPACT ON CONTROL ROOM PROCEDURES. ALL CONTROL ROOM PROCEDURES WERE FOLLOWED AND SERVED THEIR PURPOSE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | FROZEN SENSING/PILOT TUBING | [161 empty] | THOMAS DARK | PIPELINE SAFETY ENGINEER | thomas.dark@williams.com | (385)261-0465 | (918)573-6723 | WENDY WAGSTER | wendy.wagster@williams.com | (570) 550-8009 | TYSON GREEN | PIPELINE SAFETY MANAGER | (713) 215-2535 | tyson.green@williams.com | ON MONDAY (2/15/2021) THE 535 CONTROLLER RECEIVED AN ALARM INDICATING A POSSIBLE RELIEF VALVE ACTUATION. THE CONTROLLER CALLED THE ON-CALL PERSON FOR SUPPORT AT WHO WAS ALREADY AT STATION 535. THIS PARTICULAR COMPRESSOR FACILITY IS A CONSTANTLY MANNED FACILITY. THE CONTROLLER DISCOVERED PSV 15030 FROZEN OPEN THEY PROCEEDED TO SHUT IN WITHDRAW FROM THE CPR IN ORDER TO STOP THE GAS FLOW THROUGH THE PSV. THE CONTROLLER THEN CLOSED SDV50114 TO ISOLATE THE SECTION OF PIPE CONNECTED TO PSV 15030. AT THAT TIME, PSV 15030 FULLY RESEATED AND STOPPED VENTING. THE STATION WAS RETURNED THE STATION TO SERVICE AFTER PROPER ISOLATION OF PSV 15030 WAS CONFIRMED. NRC NOTIFICATION WAS MADE UPON DETERMINATION THAT THE EVENT QUALIFIED AS A DOT INCIDENT. THE PSV WAS RETURNED TO SERVICE ON 2/15/2021. UPSTREAM OF THE PSV IS THE OPP DEVICE THAT PROTECTS THE MAOP FOR THIS SYSTEM. PSV 15030 IS NOT THE PRIMARY OVER PRESSURE PROTECTION DEVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210017 | 34942 | 2021-03-02 15:26 | ORIGINAL FINAL | 31202 | ENABLE MIDSTREAM PARTNERS, LP | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-02-01 16:15 | 2021 | CENTRAL | NO | 35.1671 | -94.079 | 1297164 | 2021-02-01 16:46 | 1297256 | NATURAL GAS |  | 2 | 28 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-30 14:00 | 2021-02-04 15:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-01-30 14:00 | VALVE CLOSURE |  | 2021-01-30 14:00 | 0 | 2021-01-30 14:00 | 2021-01-30 14:00 | ONSHORE | AR | 72936 | GREENWOOD | SEBASTION | NOT APPLICABLE |  | LINE O-1650 | LINE O-1650 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.188 | 42000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY |  | YES | [26 empty] | 2004 | 2004 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 131 |  | NO | NO | [5 empty] | 0 | 0 | 76 | 77.531420765027344 | 5 | 5 | 60000 | 61209.01639344264 | 500 | 510.075136612022 | 0 | 0 |  | 2.71 | 60581 | 27265.5840095855514387774086378737541528 | 61801.622950819689344 | 0 | 0 | 0 | 0 | NO |  |  |  | 675 | 1.5 | 1000 | 192.619(A)(2) |  | 2004-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 300 | NO | [5 empty] | YES | LACK OF PIG TRAPS | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PINHOLE LEAK WAS DISCOVERED BY PUBLIC WHO CONTACTED ENABLE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [19 empty] | YES | [43 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MGR. | casey.roberts@enablemidstream.com | 4056263981 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4056263981 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MGR. | 4056263981 | casey.roberts@enablemidstream.com | ON JANUARY 30TH, ENABLE MIDSTREAM RECEIVED A PHONE CALL FROM A LANDOWNER IN SEBASTIAN COUNTY, ARKANSAS DESCRIBING A POSSIBLE LEAK ON LINE O-1650. LINE O-1650 IS AN INTRASTATE PIPELINE CONSISTING OF 2,649 FT OF 6", X42, .188 WT ERW PIPE INSTALLED IN 2004. AN O&M TECH WAS DISPATCHED TO INVESTIGATE AND DISCOVERED A MINOR LEAK SOUTH OF OLD ARKANSAS HIGHWAY 10. THE LEAKING AREA OF PIPELINE WAS IMMEDIATELY ISOLATED, AND A REPAIR PLAN WAS INITIATED. A REPAIR CONTRACTOR WAS DETERMINED AND A QUOTE WAS OBTAINED ON FEBRUARY 1ST FOR MORE THAN $50,000 TO REPAIR THE PIPE. A CALL WAS IMMEDIATELY PLACED TO THE NRC TO NOTIFY OF AN INCIDENT (NRC #1297164, 1297256). THE LINE WAS REPAIRED AND PLACED BACK INTO SERVICE ON FEBRUARY 4TH. IT WAS DETERMINED THE LEAK WAS DUE TO WATER IN THE LOW POINT OF THE PIPE. THIS PIPELINE IS NON-PIGGABLE. FOLLOWING THE LEAK, THE LINE WAS TREATED WITH INHIBITOR AND BACTERIA RESULTS WERE NEGATIVE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210018 | 34961 | 2021-03-08 14:34 | ORIGINAL FINAL | 14435 | OZARK GAS TRANSMISSION, L.L.C | 1501 MCKINNEY SUITE 800 | HOUSTON | TX | 77010 | 2021-02-12 11:15 | 2021 | CENTRAL | NO | 35.1048 | -95.1211 | 1297858 | 2021-02-12 11:15 | 1297956 | NATURAL GAS |  | 3400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | COMP ENGINE PILOT VALVE FROZE; ENGINE RELIEF BEGAN BLOWING DOWN |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-02-11 23:55 | NO | [11 empty] | 0 | 2021-02-11 23:41 | 2021-02-12 00:30 | ONSHORE | OK | 74943 | LEQUIRE | HASKELL | NOT APPLICABLE |  | LEQUIRE COMPRESSOR STATION | OZARK GAS TRANSMISSION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED AND RELEASED NATURAL GAS. | CLASS 1 LOCATION | NO |  | 108 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 8058 | 8058 | 0 | 0 | 0 | 0 | 500 | 510.075136612022 | EMPLOYEE OVERTIME COST TO RESPOND TO INCIDENT. | 2.37 | 8558 | 5512.25152837536095847176079734219269103 | 8568.075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 757 | 30 | 1200 | 192.619(A)(1) |  | 1998-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE WAS DUE TO A RELIEF VALVE FUNCTIONING AS INTENDED, RATHER THAN A PIPELINE BREAK. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | [52 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | YES |  |  |  | YES | ARCTIC WEATHER SYSTEM | [263 empty] | YES | [37 empty] | RONDA LOUDERMAN | VICE PRESIDENT EHSR | rlouderman@blackbearllc.com | 13619605671 |  |  |  |  | RONDA LOUDERMAN | VICE PRESIDENT EHSR | 13619605671 | rlouderman@blackbearllc.com | AT 11:41PM ON 2-11-21 A FISHER TYPE REGULATOR THAT PROVIDES PILOT GAS TO THE ESD BLOW DOWN VALVE(LQ7A) ON THE COMPRESSOR FROZE AND ALLOWED THE VALVE TO COME FULLY OPEN. AS A RESULT OF THIS, GAS WAS ALLOWED TO BLOW TO ATMOSPHERE FOR A TIME OF 68 MINUTES. NOTIFICATION TO BBT TECHNICIAN WAS BY A NEARBY HOMEOWNER, REPORTING EXTREME NOISE AT THE LEQUIRE COMPRESSOR STATION. THERE WERE NO INJURIES, FATALITIES OR FIRES RELATED TO THE EVENT. THE LOCAL HASKELL COUNTY FIRE DEPARTMENT DID RESPOND DUE TO THE HOMEOWNER ALSO MAKING NOTIFICATION TO 911. INITIAL INDICATION WAS THAT THE AMOUNT OF GAS LOSS WAS BETWEEN 1-2 MMCF, BUT AFTER FURTHER CALCULATIONS, IT WAS DETERMINED TO BE A REPORTABLE AMOUNT AT 3.4 MMCF TOTAL BLOWN DOWN TO ATMOSPHERE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210019 | 36732 | 2021-03-11 18:10 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2021-02-09 21:10 | 2021 | MOUNTAIN | NO | 38.9617 | -106.1964 | 1297689 | 2021-02-09 21:31 | 1297827 | NATURAL GAS |  | 275 | 338 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-09 22:00 | 2021-02-10 17:18 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-03-09 22:00 | VALVE CLOSURE |  | 2021-03-09 22:10 | 0 | 2021-02-09 17:15 | 2021-02-09 17:50 | ONSHORE | CO | 81211 | Not Within a Municipality | CHAFFEE | NOT APPLICABLE |  | 6'(8') UPPER ARKANSAS VALLEY | LINE LOOP # 720090 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.188 | 42000 | API 5L X42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1962 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.3 | 0.2 | [7 empty] | CLASS 1 LOCATION | NO |  | 128 |  | NO | NO |  |  | NO |  |  | 3000 | 3060.450819672132 | 761 | 776.334357923497484 | 619 | 619 | 45000 | 45906.76229508198 | 40000 | 40806.01092896176 | 17270 | 17617.99521857923988 | 200 HOUSE SERVICE OUTAGE RESTORATION AND RE-LIGHTS. | 2.25 | 106650 | 48125.5364010334699940431893687707641196 | 108786.553620218609364 | 0 | 0 | 200 | 1 | NO |  |  |  | 690 | 1080 | 790 | 192.619(A)(2) |  | 1962-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | REMOTELY CONTROLLED | MANUAL | 45900 | YES | [7 empty] | YES |  |  |  |  | YES | SHORT RADIUS FITTINGS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SIZE OF PUNCTURE DID NOT RESULT IN UNUSUAL FLOWS OR PRESSURES MONITORED BY CONTROLLERS OR SCADA ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [9 empty] | CONTRACTOR | AUGER | POLE | YES | A036500784 | NOT APPLICABLE - SINGLE ONE-CALL CENTER | FACILITY OWNER | NO | YES | YES | 12 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | MARK NOLAN | PRINCIPAL ENGINEER | mark.nolan@xcelenergy.com | 13035713931 |  | MARK NOLAN | mark.nolan@xcelenergy.com | 13035713931 | CHRIS AKINS | MANAGER PIPELINE COMPLIANCE AND STANDARDS | 13035713298 | christopher.a.akins@xcelenergy.com | ON 12/30/2020 A CONTRACTOR FOR AN ELECTRIC UTILITY REQUESTED LOCATES TO INSTALL UTILITY POLES. ON 12/31/2020 COMPANY PROVIDED LOCATES. ON 02/09/2021 CONTRACTOR RETURNED TO SITE TO INSTALL POLE GUY WIRE ANCHORS BY AUGERING AND DAMAGED 6" TRANSMISSION LINE. THE AUGERING OCCURRED MORE THAN 30 DAYS FROM TIME OF LOCATES, AND MARKS WERE NO LONGER VISIBLE IN DIG AREA.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210020 | 36438 | 2021-03-15 12:37 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2021-02-18 17:21 | 2021 | CENTRAL | NO | 41.6066 | -106.2068 | 1298376 | 2021-02-18 18:04 | 1298444 | NATURAL GAS |  | 18255 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-18 18:35 | 2021-02-22 14:00 |  | NO |  |  | NO | [11 empty] | 0 | 2021-02-18 17:21 | 2021-02-18 18:35 | ONSHORE | WY | 82083 | Not Within a Municipality | CARBON | NOT APPLICABLE |  | ARLINGTON COMPRESSOR STATION | ARLINGTON STATION DISCHARGE LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1998 | 1997 | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL OPERATION OF THE STATION BLOW DOWN VALVE | CLASS 1 LOCATION | NO |  | 171 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 46003 | 46003 | 0 | 0 | 500 | 510.075136612022 | 3500 | 3570.525956284154 | PARTS AN LABOR TO REMOVE, INSPECT, CLEAN AND REINSTALL BLOW DOWN VALVE. | 2.52 | 50003 | 31984.8976090626883322259136212624584718 | 50083.601092896176 | 0 | 0 | 0 | 0 | NO |  |  |  | 685 | 119000 | 960 | 192.619(A)(2) |  | 1998-01-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS RELEASE WAS NOT CAUSED BY OPERATOR'S ACTIONS. OPERATOR ON DUTY GAVE PROMPT NOTICE TO FIELD PERSONNEL AND MANAGEMENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | POLAR VORTEX. APPROXIMATELY ZERO DEGREES F WITH 30 TO 50 MPH WINDS | [301 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 2/18/2021 AT 5:21 PM CST, SOUTHERN STAR CENTER GAS PIPELINE (SSCGP) GAS CONTROL OPERATOR RECEIVED A SCADA ALARM THAT THE STATION BLOW DOWN VALVE AT THE ARLINGTON COMPRESSOR STATION IN CARBON COUNTY, WYOMING WAS OPEN. THE GAS CONTROL OPERATOR ON DUTY IMMEDIATELY NOTIFIED FIELD OPERATIONS TO DISPATCH PERSONNEL TO THE SITE. THE NRC WAS NOTIFIED AT 6:04 PM CST (NRC#1298376). SSCGP PERSONNEL ARRIVED ON SITE AT 6:35 PM CST AND IMMEDIATELY ACTIVATED THE STATION ESD SYSTEM STOPPING GAS FLOW INSTANTLY. DUE TO THE EXTREME COLD AND WINDY CONDITIONS THE STATION REMAINED ON ESD UNTIL 2/22/2021 SO THE BLOW OFF VALVE COULD BE REMOVED, INSPECTED AND REINSTALLED. UPON INSPECTION, CONDENSATION WAS FOUND IN THE VALVE ACTUATOR. NO OTHER OBVIOUS MECHANICAL OR OPERATIONAL CAUSES WERE DISCOVERED. THE STATION WAS PLACED BACK IN SERVICE ON 2/22/2021 AT 2:00 PM CST. BECAUSE CONDENSATION IN THE ACTUATOR, A DESICCANT FILTER WILL BE INSTALLED ON THE POWER GAS LINE. REASON FOR SUPPLEMENTAL REPORT: UPDATE TO PART H-NARRATIVE: DESICCANT FILTER HAS BEEN INSTALLED ON THE POWER GAS LINE. THE PLC WAS NOT REPROGRAMMED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210021 | 35379 | 2021-03-15 14:52 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-02-19 22:40 | 2021 | CENTRAL | NO | 32.8412 | -91.9509 | 1298469 | 2021-02-19 23:45 | 1298607 | NATURAL GAS |  | 209 | 17614 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-19 23:40 | 2021-03-05 17:45 |  | YES | OPERATOR | 2021-02-19 23:49 | NO | [5 empty] | VALVE CLOSURE |  | 2021-02-19 23:40 | VALVE CLOSURE |  | 2021-02-19 23:40 | 0 | 2021-02-19 22:40 | 2021-02-19 22:40 | ONSHORE | LA | 71220 | Not Within a Municipality | MOREHOUSE | MILEPOST | 10+1474 | BASTROP-EUNICE 26" LINE | BAE 26-1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | WKM, INC. |  |  |  | 1951 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 551 |  | NO | NO | [5 empty] | 0 | 0 | 48615 | 49594.60553278689906 | 577 | 577 | 400000 | 408060.1092896176 | 1000 | 1020.150273224044 | 0 | 0 |  | 2.76 | 450192 | 202728.3799008429443211129568106312292359 | 459251.86509562854306 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 450000 | 810 | OTHER | 192.611(A)(1)(I) | 2021-01-28 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 116160 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [35 empty] | YES | FATIGUE | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 2/19/2021, TEXAS GAS' GAS CONTROL RECEIVED NOTIFICATION FROM A MEMBER OF THE GENERAL PUBLIC REPORTING A LOUD NOISE AT TEXAS GAS' BLOCK VALVE YARD. FIELD OPERATIONS PERSONNEL WERE DISPATCHED AND CONFIRMED A LEAK ON TEXAS GAS' ASSET. APPROPRIATE NOTIFICATIONS WERE MADE TO AUTHORITIES AND CUSTOMERS. THE SYSTEM WAS ISOLATED AND PRESSURE RELIEVED WHILE CUSTOMER IMPACT WAS EVALUATED. ON 2/20/2021, THE SITE WAS EXCAVATED AND THE CAUSE, A CRACKED BLOCK VALVE (IDENTIFIED AS BLOCK VALVE 2), WAS IDENTIFIED. PLANS WERE MADE TO ADDRESS THE INCIDENT AND CUSTOMERS WERE UPDATED. PRESSURE WAS MAINTAINED AT APPROXIMATELY 145 PSI FROM BLOCK VALVE 2 TO BASTROP TO SUPPLY THE CUSTOMER UNTIL OUTAGE OCCURRED. ON 3/3/2021, THE BLOCK VALVE WAS REPLACED AND THE SEGMENT WAS RESTORED TO SERVICE. 6/7/2021 FINAL REPORT SUBMITTED FOR THE FOLLOWING: UPDATED TO CORRECT LAT/LONG AND 48-HOUR FOLLOW-UP NRC CALL NUMBER PER PHMSA REQUEST. UPDATED PROPERTY DAMAGE COSTS. UPDATED TO INCLUDE RESULTS OF ROOT CAUSE ANALYSIS. AFTER PERFORMING THE ANALYSIS, THE METALLURGICAL LAB CONCLUDED THAT THE FAILURE WAS LIKELY DUE TO FATIGUE THAT CONCENTRATED AT THE TOE OF A MACHINED CHAMFER. THIS CHAMFER, MEASURED AT APPROXIMATELY 60°, RESULTED IN A HIGH STRESS CONCENTRATOR, CONTRIBUTING TO THE FRACTURE. 6/8/2021 SUPPLEMENTAL/FINAL REPORT SUBMITTED TO REVISE LONGITUDE AS REQUESTED BY PHMSA.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210022 | 35613 | 2021-03-15 17:09 | SUPPLEMENTAL FINAL | 15485 | PHILLIPS 66 COMPANY - SWEENY REFINERY | 2331 CITYWEST BLVD. S820-06 | HOUSTON | TX | 77042 | 2021-02-15 09:00 | 2021 | CENTRAL | YES | 29.0747 | -95.7307 | 1298027 | 2021-02-15 11:02 | 1298334 | HYDROGEN GAS |  | 6837 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-15 09:57 | 2021-02-22 14:30 |  | YES | OPERATOR | 2021-02-15 09:08 | YES | 2021-02-15 09:04 | ALLOWED TO BURN OUT |  | 6837 | YES | [6 empty] | 0 | 2021-02-15 09:04 | 2021-02-15 09:07 | ONSHORE | TX | 77463 | Not Within a Municipality | BRAZORIA | NOT APPLICABLE |  | FM 524 STATION | SR-28 PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 2017 | 2017 | CARBON STEEL |  | LEAK |  |  | OTHER | EROSION | [5 empty] | CLASS 1 LOCATION | NO |  | 226 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 13674 | 13674 | 4000000 | 4080601.092896176 | 50000 | 51007.5136612022 | 452553 | 461672.066598360784332 | COST OF RESPONSE, TEMPORARY AND ESTIMATED COSTS OF PERMANENT REPAIRS. | 2 | 4516227 | 2035351.65643296378408385714285714285714 | 4606954.673155738984332 | 0 | 0 | 0 | 0 | NO |  |  |  | 1796 | 77240 | 2445 | 192.619(A)(2) |  | 2017-09-08 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | METER TUBE FAILURE | [14 empty] | YES | [125 empty] | YES | [37 empty] | JEFF SHOUSE | DOT COORDINATOR | jeff.d.shouse@p66.com | 832-765-1858 |  | JEFF SHOUSE | jeff.d.shouse@p66.com | 832-765-1858 | TODD FUKSA | DIRECTOR DOT OPERATIONS COMPLIANCE | 832-765-1632 | todd.t.fuksa@p66.com | ON 2/15/2021, A HYDROGEN RELEASE AND SUBSEQUENT FIRE OCCURRED AT THE SR-28 FM524 PIPELINE METER STATION. LOCAL REFINERY EMERGENCY RESPONSE TEAM RESPONDED AND SECURED THE AREA. THE PIPELINE WAS ISOLATED, AND THE FIRE EXTINGUISHED ITSELF. DURING WINTER STORM URI, THE SWEENY AREA WAS EXPERIENCING ABNORMAL FREEZING CONDITIONS THROUGHOUT THE AREA AND WIDESPREAD POWER OUTAGES WERE OCCURRING. AS A RESULT, THIRD PARTY HYDROGEN SUPPLY TO THE SWEENY REFINERY WAS REDUCED. THESE UPSETS RESULTED IN THE NEED TO EXPORT LARGER THAN NORMAL FLOW RATES ON THE SR-28 HYDROGEN PIPELINE. THE INCIDENT INVESTIGATION IDENTIFIED THAT THERE WAS EROSION OF THE FLOW TUBES IN THE 3-INCH CORIOLIS METER. THE INITIAL EVENT LED TO SUBSEQUENT FAILURES ON THE SKID INCLUDING THE CORIOLIS METER HOUSING, METER FLANGE, AN 8-INCH MANUFACTURED ELBOW, AND AN 8-INCH BYPASS LINE. THE METER STATION WILL BE REDESIGNED AND RECONSTRUCTED TO MINIMIZE THE RISK OF EROSION. PERMANENT REPAIRS SCHEDULED TO BE COMPLETED IN 2022. SUPPLEMENTAL FINAL UPDATE AS PER PHMSA AID WITH ESTIMATED COSTS OF FINAL REPAIR IN 2022.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210023 | 35424 | 2021-03-15 19:21 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-02-16 23:55 | 2021 | PACIFIC | NO | 35.4488 | -119.0477 | 1298195 | 2021-02-17 03:46 | 1298822 | NATURAL GAS |  | 531 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | N/A | [6 empty] | NO | [11 empty] | 0 | 2021-02-16 23:55 | 2021-02-17 00:24 | ONSHORE | CA | 93308 | BAKERSFIELD | KERN | MILEPOST | MP 6.6 | L-375 | 105-106 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1989 | 1988 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD1 | 44 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1593 | 1593 | 46000 | 46926.912568306024 | 8000 | 8161.202185792352 | 0 | 0 |  | 3 | 55593 | 25348.0072572300134152823920265780730897 | 56681.114754098376 | 0 | 0 | 0 | 0 | NO |  |  |  | 445 | 531 | 465 | 192.619(A)(2) |  | 1975-06-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | PASSENGER CAR | ROADWAY | 10 | NO | [208 empty] | YES | [29 empty] | SAJJAD AZHAR |  | s1at@pge.com | [5 empty] | SUSIE RICHMOND |  | 9257860267 | gsr8@pge.com | ON TUESDAY, FEBRUARY 16, 2021 AT 2355 HOURS, PG&E WAS NOTIFIED OF A VEHICLE IMPACT TO PETROL RD REG STATION AT 1601 PETROL RD, BAKERSFIELD (L-375 MP 6.6). GSR ARRIVED AT 0024 AND REQUESTED GAS CREW FOR REPAIRS. THE REPAIRS HAVE BEEN COMPLETED AND ALL SERVICE RESTORED. THERE ARE NO REPORTS OF INJURIES. FIRE DEPT AND CHP REPORTED ON SITE. THIS INCIDENT WAS REPORTED TO THE DOT (1298195) AND CPUC (210217-13784) DUE TO THE UNINTENTIONAL RELEASE OF GAS AND EXPECTED REPAIR COSTS BEING ESTIMATED AT OVER $50K
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210024 | 35593 | 2021-03-16 16:43 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-02-20 16:18 | 2021 | CENTRAL | NO | 34.6453 | -89.519 | 1298537 | 2021-02-20 18:14 | 1298546, 1298696, | NATURAL GAS |  | 56902 | 8033 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-20 19:29 | 2021-03-01 16:28 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-02-20 19:29 | VALVE CLOSURE |  | 2021-02-20 19:29 | 23 | 2021-02-20 19:29 | 2021-02-20 18:25 | ONSHORE | MS | 38685 | Not Within a Municipality | MARSHALL | SURVEY STATION NO. | 187+56 | TGP LINE 100-1 | VALVE SECTION 67-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 66 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.281 | 45000 | API-5L | SEAMLESS |  | NATIONAL TUBE | COAL TAR |  | YES | [26 empty] | 1944 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 454 |  | NO | NO |  |  | NO |  |  | 3500 | 3570.525956284154 | 26107 | 26633.063183060116708 | 184932 | 184932 | 95340 | 97261.12704918035496 | 20895 | 21316.03995901639938 | 121375 | 123820.7394125683405 | INVESTIGATION, PIPE SPECIMEN SHIPMENT, METALLURGICAL LABORATORY COSTS; | 3.25 | 452149 | 241603.7646446613129649468438538205980066 | 457533.495560109365548 | 0 | 0 | 9 | 0 | NO |  |  |  | 720 | 117000 | 750 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 58080 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | RE-HEATING FOR WRINKLE BEND, POLAR VORTEX SEVERE WEATHER | [16 empty] | YES |  |  |  |  | 1988 | [54 empty] | YES | YES | YES |  | YES | YES |  | YES | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2011 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2018 | FREE SWIMMING | HIGH RESOLUTION | [17 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2011 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2018 | FREE SWIMMING | [6 empty] | TDW MULTI DATA SET TOOL | 2016 | FREE SWIMMING |  |  |  | YES | 1988 | 997 | NO | [13 empty] | NO | [25 empty] | YES | [15 empty] | YES | [21 empty] | WILLIAM MARTIN MULLER | SPECIALIST-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2054104383 | 2053253509 | WILLIAM COX | william_cox@kindermorgan.com | 6627122022 | JAIME HERNANDEZ | DIRECTOR ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON FEBRUARY 20, 2021, AT 16:30-HOURS, AN EMPLOYEE OF HOLLY SPRINGS GAS DEPARTMENT CALLED AN EMPLOYEE OF TENNESSEE GAS PIPELINE (TGP). THE CALLER INFORMED THE TGP EMPLOYEE OF A POTENTIAL INCIDENT WITH ONE OF THE TGP PIPELINES LOCATED IN MARSHALL COUNTY, MISSISSIPPI. THE EMPLOYEE IMMEDIATELY CALLED THE RESPONSIBLE OPERATIONS SUPERVISOR WHO IN TURN CALLED THE AREA MANAGER. THE AREA MANAGER DIRECTED THE OPERATIONS SUPERVISOR TO BEGIN CALLING AND MOBILIZING PERSONNEL TOWARDS THE HOLLY SPRINGS AREA. THE AREA MANAGER THEN CONTACTED TGP'S GAS CONTROL STAFF TO ASCERTAIN IF THEY HAD SEEN ANY PRESSURE CHANGES AND THEY HAD NOT. THE AREA MANAGER THEN CALLED THE HOLLY SPRINGS GAS DEPARTMENT WHO DIRECTED HIM TO THE MARSHALL COUNTY EMERGENCY MANAGEMENT AGENCY (EMA) STAFF. AT 16:56-HOUR, THE AREA MANAGER CONTACTED THE EMA FOR ANY INFORMATION AVAILABLE AND WAS MADE AWARE THAT THE EMA PERSONNEL HAD BLOCKED JACK THOMPSON ROAD AFTER EVACUATING SOME RESIDENCES IN THE AREA. TGP DIVISION STAFF AND THE LOCAL AREA MANGER INITIATED AN EMERGENCY RESPONSE LINE CONFERENCE CALL TO DISCUSS THE PENDING SITUATION AND ACTIONS CURRENTLY TAKEN. OUT OF ABUNDANCE OF CAUTION, TGP DECIDED TO CALL THE NRC AND REPORT THE POTENTIAL INCIDENT SITUATION. AT 18:25, A TGP FIELD EMPLOYEE ARRIVED AT MLV #68 TO INSTALL A MANUAL PRESSURE GAUGE IN ORDER TO IDENTIFY ANY PRESSURE ISSUES ON THE TGP LINE 100-1. SUBSEQUENTLY, AT 18:37, ANOTHER TGP FIELD EMPLOYEE ARRIVED AT MLV #67 TO INSTALL A MANUAL PRESSURE GAUGE TO IDENTIFY ANY PRESSURE ISSUES ON THE PIPELINE AS WELL. THESE RESPONSE TIMES WERE MUCH LONGER THAN NORMAL DUE TO INCLEMENT WEATHER AND VERY ICY ROAD CONDITIONS. AT 19:20-HOUR, FIELD PERSONAL CONFIRMED LINE 100-1 WAS LOSING PRESSURE AND PROCEEDED TO CLOSE BOTH MLV'S. AT 21:40 TGP REPORTED TO THE EMA THAT THE PRESSURE BETWEEN MLV #68 AND #67 WAS ZERO (0) PSIG. CONSEQUENTLY, THE EMA OPENED JACK THOMPSON ROAD, AND THE EVACUATED RESIDENTS RETURNED HOME. TGP STARTED THE REMEDIATION PROCESS FOR LINE 100-1 BY REPLACING THE SEGMENT CONTAINING THE LEAK. ON MARCH 1, 2021, THE REMOVED PIPE SPECIMEN CONTAINING THE LEAK BEGAN TRANSPORTATION BY TRUCK FROM THE HOLLY SPRINGS AREA TO BLADE ENERGY PARTNERS IN HOUSTON TX FOR LABORATORY ANALYSIS. IN ADDITION, THE VALVE SECTION OF LINE 100-1 RETURNED TO SERVICE AT 16:28-HOUR ON THE SAME DAY. THE INVESTIGATION WAS COMPLETED AND THE LABORATORY REPORT WAS LAST ISSUED ON JUNE 30, 2021. THE ANALYSIS RESULTED IN FINDING A LARGE THROUGH-WALL CRACK WITH A MAXIMUM CRACK OPENING OF 0.27 INCH AS FOUND ALONG THE CREST OF THE SECOND WRINKLE FROM THE UPSTREAM. THE LENGTH OF THE CRACK IS 4.1 FEET. THE FRACTURE SURFACE APPEARS TO BE CRYSTALLINE TYPE AND SHINY, WITH NUMEROUS FRESH RUST SPOTS. CHEVRON MARKS ARE OBSERVED WITH THEIR APEXES TOWARDS THE 1.5-FOOT LONG ORIGIN OF THE CRACKING. THE FAILURE APPEARS TO BE BRITTLE, LITTLE PLASTIC DEFORMATION WAS OBSERVED NEAR THE FRACTURE SURFACE. CHEMICAL ANALYSIS OF THE SAMPLE INDICATES THE MATERIAL COMPLIES WITH API REQUIREMENTS OF THE 1940'S. TENSILE TESTS SHOWS THE SAMPLE CONFORMS TO SMYS FOR X45 STEEL. ADDITIONAL ANALYSIS AND HARDNESS MEASUREMENTS FOUND DIFFERENCES, WHICH MAY BE CONTRIBUTED TO RE-HEATING THE PIPE BODY IN THE FIELD FOR THE BENDING DURING INSTALLATION. IT IS NOTED THE TEMPERATURE DROP DURING THE POLAR VORTEX IN THE WEEK OF FEBRUARY 14, 2021, COULD HAVE CONTRIBUTED TO THE FAILURE IN THE WRINKLE BEND AS WELL AS HARD SPOTS FROM RE-HEATING OF THE STEEL, WHICH INCREASED BRITTLENESS. CLEAVAGE CRACKING OCCURRED WHEN THE TEMPERATURE OF THE PIPE DROPPED NEAR OR BELOW FREEZING TEMPERATURE AND PROPAGATED RAPIDLY THROUGH THE WALL IN BRITTLE MANNER.
2023-02-28 09:42 | NO | NO | UNGS (Underground Natural Gas Storage) | 20210025 | 35020 | 2021-03-18 13:10 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-02-21 13:23 | 2021 | EASTERN | NO | 41.8702 | -77.9942 | 1298603 | 2021-02-21 17:34 | 1298717 | NATURAL GAS |  | 28216 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-21 13:35 | 2021-02-21 14:33 |  | NO |  |  | NO | [11 empty] | 0 | 2021-02-21 13:51 | 2021-02-21 13:51 | ONSHORE | PA | 16915 | Not Within a Municipality | POTTER | NOT APPLICABLE |  | HEBRON STORAGE FIELD | 313C-100 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELEASE FROM VALVE DUE TO LOSS OF POWER GAS DESIGNED TO KEEP THE VALVE CLOSED DURING NORMAL OPERATION. | CLASS 1 LOCATION | NO |  | 382 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 66308 | 66308 | 2500 | 2550.37568306011 | 200 | 204.0300546448088 | 0 | 0 |  | 2.35 | 69008 | 44722.8791834595073152823920265780730897 | 69062.4057377049188 | 0 | 0 | 0 | 0 | NO |  |  |  | 1161 | 282527 | 1250 | OTHER | ANSI 600 RATED VALVE | 2005-08-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | WATER ACCUMULATION AND FREEZING. | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-4199 |  | JAKE TAYLOR | jake_taylor@kindermorgan.com | 814 274-3122 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON SUNDAY FEBRUARY 21ST, AT 13:20 EST THE HEBRON WITHDRAWAL RELIEF VALVE (313C-103) AT TENNESSEE GAS PIPELINE'S (TGP) LITTLE ACRE STORAGE FACILITY ACTUATED. AT THE TIME OF EVENT, THE TGP OPERATOR, WORKING FROM COMPRESSOR STATION 313, RECOGNIZED A FLOW CHANGE AND INITIATED INVESTIGATION. SIMULTANEOUSLY, A NATIONAL FUEL GAS (NFG) OPERATOR, WORKING IN THE AREA OF THE LITTLE ACRE FACILITY, HEARD THE RELEASE AND CONTACTED THE ON-DUTY TGP OPERATOR AT 13:21 EST. THE TGP OPERATOR NOTIFIED OPERATIONS SUPERVISOR AND ON-CALL OPERATIONS SPECIALIST AT 13:25 EST. AFTER CONFIRMING ASSET OWNERSHIP, PERFORMING SAFE APPROACH PROTOCOLS, AND CONFIRMING PRESSURE WAS BELOW ESTABLISHED MAOP, THE TGP OPERATIONS SPECIALIST ISOLATED RELIEF VALVE AT APPROXIMATELY 13:51 EST. LINE PRESSURE AT THE TIME OF EVENT WAS 1161 PSIG AND SET PRESSURE OF RELIEF VALVE WAS 1250 PSIG. AT 17:20 EST, AN INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL COMMENCED AND DURING THAT CALL, TGP PERSONNEL ANNOUNCED THAT IT HAD DETERMINED THE RELEASE VOLUME EXCEEDED 3,000 MSCF. AT 17:34 EST, TGP NOTIFIED THE NRC (REPORT NO. 1298603) OF THE EVENT AND ESTIMATED THE TOTAL GAS LOSS AT GREATER THAN 3,000 MSCF. THE TOTAL UN-INTENTIONAL GAS LOSS WAS LATER DETERMINED TO BE 28,216 MSCF AND REPORTED TO THE NRC (REPORT NO. 1298717) AS A 48-HR UPDATE. IMMEDIATE CAUSE OF THE RELIEF VALVE MALFUNCTION INCLUDED ICE BUILD-UP WITHIN THE POWER GAS TUBING LINE RUNNING FROM THE BODY OF THE RELIEF VALVE TO PILOT CONTROL. THE POWER GAS TUBING LINE BROKE OFF WHERE THE TUBING THREADS INTO THE VALVE BODY DUE TO THE BUILD-UP OF ICE INSIDE THE TUBING AND RELIEF VALVE BODY. FAILURE OF THE RELIEF VALVE PILOT CONTROL LINE, WHICH SUPPLIES PRESSURE TO THE TOP OF THE VALVE, KEEPING IT IN THE CLOSED POSITION, ULTIMATELY REMOVED PRESSURE FROM THE TOP OF THE RELIEF VALVE AND ALLOWED THE RELIEF VALVE SEAT TO LIFT, INITIATING THE RELEASE. THE ICE FORMATION WITHIN THE POWER GAS TUBING AND RELIEF DEVICE RESULTED FROM EXCESS HYDRATE FORMATION DUE TO EXTREMELY COLD AMBIENT TEMPERATURES LEADING UP TO THE EVENT. THE ROOT CAUSE OF THE ICE FORMATION WAS INSUFFICIENT METHANOL DRIPS TO BREAK THE FORMATION OF HYDRATES IN THE SYSTEM. FOLLOWING THE EVENT, THE FREQUENCY OF METHANOL DRIP INSPECTIONS CHANGED FROM WEEKLY TO EVERY OTHER DAY FOR THOSE LOCATIONS WITH A HISTORY OF HYDRATE PRODUCTION DURING COLD AMBIENT TEMPERATURES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210026 | 35354 | 2021-03-18 14:53 | SUPPLEMENTAL FINAL | 1007 | TALLGRASS INTERSTATE GAS TRANSMISSION, LLC | 370 VAN GORDON ST | LAKEWOOD | CO | 80228 | 2021-02-16 15:09 | 2021 | CENTRAL | NO | 40.8152 | -99.1605 | 1298164 | 2021-02-16 15:46 | 1298352 | NATURAL GAS |  | 4179.44 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE WAS ISOLATED; COMPLETE SHUTDOWN UNNECESSARY |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-02-16 06:45 | 2021-02-16 08:05 | ONSHORE | NE | 68870 | Not Within a Municipality | BUFFALO | NOT APPLICABLE |  | RIVERDALE MAINLINE BORDER STATION | RIVERDALE MAINLINE BORDER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | 2007 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | RUBBER SLEEVE | OTHER | [8 empty] | SLEEVE FAILED DUE TO FREEZING TEMPERATURES. | CLASS 1 LOCATION | NO |  | 149 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 8493 | 8493 | 470 | 479.47062841530068 | 200 | 204.0300546448088 | 0 | 0 |  | 2.0321 | 9163 | 5874.183825431621558106312292358803986711 | 9176.50068306010948 | 0 | 0 | 0 | 0 | NO |  |  |  | 512 | 4936 | 535 | 192.619(A)(1) |  | 2020-05-21 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS THE RESULT OF A COMPONENT FAILURE DUE TO FREEZING TEMPERATURES, NOT RELATED TO THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | EXTREME LOW TEMPERATURES | [301 empty] | BRADLEY ARMSBURY | COMPLIANCE ENGINEER | brad.armsbury@tallgrassenergylp.com | 3037633112 |  |  |  |  | BRADLEY ARMSBURY | COMPLIANCE ENGINEER | 3037633112 | brad.armsbury@tallgrassenergylp.com | OPERATIONS PERSONNEL WERE NOTIFIED OF THE VENTING OF GAS THROUGH A RELIEF VALVE AT THE RIVERDALE MAINLINE BORDER STATION ON 2/16/21. THE RELIEF VALVE WAS ISOLATED, AND UPON INSPECTION IT WAS DETERMINED THAT THE RUBBER AXIAL RELIEF VALVE SLEEVE FAILED TO MAINTAIN ITS SETPOINT DUE TO EXTREME COLD AMBIENT TEMPERATURES, WHICH REACHED -26 DEGREES F, FALLING BELOW THE MANUFACTURER'S OPERATING MINIMUM RANGE. THE RELIEF VALVE SLEEVE WAS REPLACED "IN-KIND" AND THE LINE WAS RETURNED TO SERVICE ON 2/16/21
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210027 | 35146 | 2021-03-19 13:56 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-02-19 07:45 | 2021 | CENTRAL | NO | 32.727 | -97.2154 | 1298390 | 2021-02-19 07:56 | 1298491 | NATURAL GAS |  | 93696 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | WOULD HAVE REDUCED ELECTRIC GENERATION FOR THE AREA AT A CRITICAL TIME |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-02-19 07:03 | 2021-02-19 09:00 | ONSHORE | TX | 76112 | FT WORTH | TARRANT | NOT APPLICABLE |  | HANDLEY 12IN LATERAL 2100 YARD | 9046 HANDLEY 12IN LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 1960 | 1960 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | NATURAL GAS WAS RELEASED AT THE RELIEF VALVE | CLASS 2 LOCATION | YES | METHOD2 | 499 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 281088 | 281088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 281088 | 184434.817275747508305647840531561461794 | 281088 | 0 | 0 | 0 | 0 | NO |  |  |  | 380 | 50 | 811 | 192.619(A)(2) |  | 1960-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. INCIDENT CAUSED BY WEATHER CONDITIONS (EXTREME WINTER WEATHER). | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | WINTER STORM, EXTREME WINTER TEMPERATURES | [301 empty] | ANGELA MORGAN | LEAD SPECIALIST - REGULATORY COMPLIANCE | angela.morgan@energytransfer.com | 903-243-6541 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 9795319036 | chris.kresta@energytransfer.com | ON FRIDAY 02/19/21, AT 06:45, A RELIEF VALVE OPENED ON THE 2ND CUT REGULATOR AT THE HANDLEY 2100 YARD AT THE TEXGEN HANDLEY POWER PLANT DUE TO A FREEZE IN THE GAS SUPPLY LINE TO THE INSTRUMENTATION. THE TEXGEN HANDLEY POWER PLANT IS SUPPLIED NATURAL GAS VIA PIPELINE FROM THE 9046 HANDLEY 12IN LATERAL AT THE HANDLEY 2100 YARD. GAS CONTROL NOTIFIED OPERATIONS PERSONNEL THAT THE RELIEF VALVE ACTUATED AT APPROXIMATELY 06:45. OPERATIONS PERSONNEL WERE DISPATCHED TO THE LOCATION AT 06:58, AND OPERATIONS MANAGER WAS NOTIFIED AT 07:03. DUE TO HAZARDOUS ROAD CONDITIONS RESPONSE TIME WAS GREATER THAN NORMAL. GAS CONTROL DID NOT CLOSE THE CONTROL VALVE AT THE SUPPLY POINT BECAUSE THE TEXGEN HANDLEY POWER PLANT COULD NOT BE OFFLINE DURING THE EXTREME WINTER WEATHER CONDITIONS, AS IT WAS CRITICAL TO THE ELECTRIC GRID. OPERATIONS PERSONNEL ARRIVED ON LOCATION AT 09:00 AND THE MAINLINE BLOCK VALVE WAS CLOSED AT 09:16. ONCE THE PRESSURE WAS RELIEVED ENOUGH FOR THE RELIEF VALVE TO RE-SEAT, THEN THE MAINLINE BLOCK VALVE WAS RE-OPENED IN ORDER TO MAINTAIN THE GAS SUPPLY TO THE POWER PLANT. OPERATIONS BEGAN ASSESSMENT OF THE SITUATION AND DETERMINED THAT THE GAS SUPPLY LINE TUBING EXPERIENCED A FREEZE, THE FREEZE WAS IDENTIFIED, AND THE SUPPLY LINE WAS CLEARED. OPERATIONS REINSULATED THE GAS SUPPLY LINES. THE FLOW TO THE TEXGEN HANDLEY POWER PLANT AT THE HANDLEY 2100 YARD WAS NEVER FULLY INTERRUPTED. DUE TO THE CRITICAL NATURE OF THE SUPPLY POINT TO THE TEXGEN HANDLEY POWER PLANT DURING THE EXTREMELY COLD WEATHER CONDITIONS, OPERATIONS PERSONNEL REMAINED ON SITE AT THE LOCATION TO MINIMIZE ANY DOWN TIME TO THE TEXGEN HANDLEY POWER PLANT. ENERGY TRANSFER'S PLAN TO PREVENT A RECURRENCE INCLUDES OVERHAULING THE REGULATOR AT THE HANDLEY 2100 YARD. DUE TO THE AGE OF THE REGULATOR THE LEAD TIME FOR REPLACEMENT PARTS IS CURRENTLY 12 WEEKS. REPLACEMENT OF THE PILOT AND HEATER FOR THE GAS SUPPLY LINE WAS COMPLETED MARCH 3, 2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210028 | 35147 | 2021-03-19 14:03 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-02-20 08:35 | 2021 | CENTRAL | NO | 32.7295 | -97.2207 | 1298490 | 2021-02-20 09:26 | 1298629 | NATURAL GAS |  | 8760 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | WOULD HAVE REDUCED ELECTRIC GENERATION FOR THE AREA AT A CRITICAL TIME |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-02-20 01:22 | 2021-02-20 01:30 | ONSHORE | TX | 76112 | FT WORTH | TARRANT | NOT APPLICABLE |  | HANDLEY 12IN LATERAL 2000 YARD | 9046 HANDLEY 12IN LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 1960 | 1960 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | OTHER | [8 empty] | NATURAL GAS WAS RELEASED AT THE RELIEF VALVE | CLASS 3 LOCATION | YES | METHOD2 | 401 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 26280 | 26280 | 0 | 0 | 0 | 0 | 0 | 0 |  | 3 | 26280 | 17243.5215946843853820598006644518272425 | 26280 | 0 | 0 | 0 | 0 | NO |  |  |  | 400 | 45 | 753 | 192.619(A)(2) |  | 1960-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. INCIDENT CAUSED BY WEATHER CONDITIONS (EXTREME WINTER WEATHER). | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | WINTER STORM, EXTREME WINTER TEMPERATURES | [301 empty] | ANGELA MORGAN | LEAD SPECIALIST - REGULATORY COMPLIANCE | angela.morgan@energytransfer.com | 9032436541 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 9795319036 | chris.kresta@energytransfer.com | ON SATURDAY, 02/20/21, AT 01:22, A RELIEF VALVE OPENED ON THE 2ND CUT REGULATOR AT THE HANDLEY 2000 YARD AT THE TEXGEN HANDLEY POWER PLANT DUE TO A FREEZE IN THE GAS SUPPLY LINE TO THE INSTRUMENTATION. THE TEXGEN HANDLEY POWER PLANT IS SUPPLIED NATURAL GAS VIA PIPELINE FROM THE 9046 HANDLEY 12IN LATERAL AT THE HANDLEY 2000 YARD. AT APPROXIMATELY 01:23, GAS CONTROL NOTIFIED OPERATIONS PERSONNEL THAT THE RELIEF VALVE ACTUATED AT APPROXIMATELY 01:22. OPERATIONS PERSONNEL WERE ON LOCATION AT THE HANDLEY 2100 YARD DUE TO THE EXTREME WEATHER CONDITIONS WHEN THE RELIEF VALVE AT HANDLEY 2000 YARD ACTUATED. OPERATIONS PERSONNEL ARRIVED ON LOCATION AT THE HANDLEY 2000 YARD AT 01:30 AND THE MAINLINE BLOCK VALVE WAS CLOSED AT 01:38. ONCE THE PRESSURE WAS RELIEVED ENOUGH FOR THE RELIEF VALVE TO RE-SEAT, THEN THE MAINLINE BLOCK VALVE WAS RE-OPENED IN ORDER TO MAINTAIN THE GAS SUPPLY TO THE POWER PLANT. OPERATIONS BEGAN ASSESSMENT OF THE SITUATION AND DETERMINED THAT THE GAS SUPPLY LINE TUBING EXPERIENCED A FREEZE, THE FREEZE WAS IDENTIFIED AND THE SUPPLY LINE WAS CLEARED. OPERATIONS REINSULATED THE GAS SUPPLY LINES. THE FLOW TO THE TEXGEN HANDLEY POWER PLANT AT THE HANDLEY 2000 YARD WAS NOT FULLY INTERRUPTED TO THE TEXGEN HANDLEY POWER PLANT. DUE TO THE CRITICAL NATURE OF THE SUPPLY POINT TO THE TEXGEN HANDLEY POWER PLANT DURING THE EXTREMELY COLD WEATHER CONDITIONS, OPERATIONS PERSONNEL REMAINED ON SITE AT THE LOCATION TO MINIMIZE ANY DOWN TIME TO THE TEXGEN HANDLEY POWER PLANT. ENERGY TRANSFER'S PLAN TO PREVENT A RECURRENCE INCLUDES OVERHAULING THE REGULATOR AT THE HANDLEY 2000 YARD. DUE TO THE AGE OF THE REGULATOR THE LEAD TIME FOR REPLACEMENT PARTS IS CURRENTLY 12 WEEKS. REPLACEMENT OF THE PILOT AND HEATER FOR THE GAS SUPPLY LINE WAS COMPLETED MARCH 3, 2021.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210029 | 35165 | 2021-03-19 15:02 | SUPPLEMENTAL | 40139 | VENICE GATHERING SYSTEM, L.L.C. | 2103 RESEARCH FOREST DR. 300 | THE WOODLANDS | TX | 77380 | 2021-01-21 18:43 | 2021 | CENTRAL | NO | 29.2186 | -89.4058 | 1296228 | 2021-01-21 18:43 | 1296326 | NATURAL GAS |  | 50 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-01-17 12:01 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-01-17 | OPERATIONAL CONTROL | PRODUCTION SHUT DOWN AND ESD VALVES SHUT |  | 0 | 2021-01-17 12:00 | 2021-01-17 12:00 | OFFSHORE | [6 empty] | 22" PIPELINE | 10793 | [20 empty] | 1 | IN STATE WATERS | LA | GULF OF MEXICO |  | PLAQUEMINES |  |  |  | SHORELINE/BANK/MARSH CROSSING | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 22 | NO | 0.5 | 52000 | X52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 576 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 167 | 167 | 1025000 | 1045654.0300546451 | 0 | 0 | 0 | 0 | ESTIMATED COST OF REPAIR. | 3.34 | 1025167 | 461412.0866578620578903654485049833887043 | 1045821.0300546451 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 1 | 1440 | 192.619(A)(2) |  | 1969-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 100320 | NO | [5 empty] | YES | BEND RADIUS | YES |  | YES | YES |  |  |  | TYPE A GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | KRISTYN CHRISTIE | AGENT | kristyn@thecompgroup.com | 9364476100 | 9365886106 | AIMEE DEADY | aimee@arenaoffshore.com | 2812103180 | AIMEE DEADY |  | 2812103180 | aimee@arenaoffshore.com | TARGA CALLED VENICE GAS GATHERING AT NOON ON 1/15/2021 TO SAY A TUG BOAT SAW BUBBLES IN THE MARSH AROUND THE VGS PIPELINE. A VGS OPERATOR EMPLOYEE DISPATCHED AN AIRBOAT AT 8AM ON 1/16 TO INVESTIGATE THE SOURCE. AN INTERNAL REPORT WAS SENT OUT ON 1/17/2021 ONCE OPERATOR EMPLOYEE WAS DONE WITH SITE VISIT AND A DECISION WAS MADE TO SHUT IN VGS. THE LEAK INVESTIGATION IS PENDING. *THE 30 DAY FOLLOW UP REPORT WAS DUE TO BE SUBMITTED THE WEEK OF A FREEZE DISASTER WHICH DELAYED THE SUBMISSION ALONG WITH PORTAL ACCESS ISSUES. A FOLLOW UP REPORT WILL BE COMPLETED. VGS IS ACTIVELY WORKING TO MAINTAIN COMPLIANCE WITHIN REPORTING GUIDELINES. UPDATE TO INCLUDE QUESTIONS AND ANSWERS PROVIDED TO OTHER PARTIES: COULD YOU DESCRIBE WHAT THE REMEDIATION THAT WAS CONDUCTED AFTER THE RELEASE SINCE IT WAS IDENTIFIED, I.E. WAS THE LEAKING SECTION CUT OUT OR A CLAMP (TYPE OF CLAMP) INSTALLED? TWO LEAKS WERE IDENTIFIED ON THE UNDER SIDE OF PIPE, AND TWO PLIDCO MECHANICAL SPLIT SLEEVE REPAIR CLAMPS WERE INSTALLED OVER THE LEAKS. CLAMP INSTALLATION WAS COMPLETED 3/20. IS THIS SYSTEM UNDER A SCADA SYSTEM AND WAS IT IDENTIFIED ON THE LEAK DETECTION SYSTEM (LDS). VGS GATHERING SYSTEM DOES NOT USE SCADA. IF THERE ARE PHOTOGRAPHS OF THE INCIDENT AND/OR EXPOSED PIPE REPORTS (CFR PART 192.459), PLEASE PROVIDE. PHOTOS OF LEAK SITE UPON INITIAL INVESTIGATION JAN. 16, 2021 ARE AVAILABLE.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20210030 | 36184 | 2021-03-24 14:11 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2021-02-26 10:04 | 2021 | CENTRAL | NO | 37.1423 | -94.5291 | 1299051 | 2021-02-26 10:32 | 1299193 | NATURAL GAS |  | 76 | 0 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-26 10:04 | 2021-03-01 07:30 |  | YES | OPERATOR | 2021-02-26 10:05 | NO | [5 empty] | VALVE CLOSURE |  | 2021-02-26 10:04 | VALVE CLOSURE |  | 2021-02-26 10:04 | 0 | 2021-02-26 10:04 | 2021-02-26 10:04 | ONSHORE | MO | 64834 | CARL JUNCTION | JASPER | SURVEY STATION NO. | 110/484 | JOPLIN-LONE ELM 10" | LINE FM | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.365 | 42000 | API 5L | SEAMLESS |  | UNKNOWN | COLD APPLIED TAPE |  | YES | [26 empty] | 1991 | 1990 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | OUTSIDE RADIUS OF THE ELBOWS DUE TO ILI TOOL IMPACT. | 10 | 10 |  | CLASS 3 LOCATION | NO |  | 138 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 192 | 192 | 500000 | 510075.136612022 | 3000 | 3060.450819672132 | 288619 | 294434.751707650355236 | ROOT CAUSE FAILURE ANALYSIS, SHIPPING OF PIPE SAMPLES, GROUND PENETRATING RADAR | 2.52 | 791811 | 356395.0843184945836672524916943521594684 | 807762.339139344487236 | 1 | 0 | 1145 | 0 | NO |  |  |  | 350 | 0 | 400 | 192.619(A)(2) |  | 1991-02-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 11000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 11 | 0 | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PLEASE REFERENCE THE CONTRIBUTING FACTORS, CAUSAL FACTORS AND ROOT CAUSES CONTAINED IN THE KIEFNER REPORT DATED SEPTEMBER 17,2021. | YES |  |  |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 12702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 12708524670 | shawn.patterson@southernstar.com | ON 2/26/2021 SOUTHERN STAR CENTER GAS PIPELINE (SSCGP) AND A CONTRACTOR WERE PERFORMING AN INLINE INSPECTION ON LINE FM IN JASPER COUNTY, MISSOURI. AFTER THE INLINE INSPECTION TOOL (PIG) WAS LAUNCHED, IT BECAME LODGED IN THE LINE. AT 10:04 AM, THE PIG DISLODGED AND A PIPELINE RUPTURE OCCURRED. THE MAINLINE VALVES ON LINE FM WERE ALREADY CLOSED DUE TO THE INLINE INSPECTION. THE KICKER VALVE AT THE PIG LAUNCHER WAS BEING MANNED AT THE TIME AND WAS IMMEDIATELY CLOSED TO STOP GAS FLOW. LINE FM WAS COMPLETELY BLOWN DOWN BY 10:07 AM. TWO SSCGP EMPLOYEES WERE PRESENT AT THE RUPTURE LOCATION WHEN THE RUPTURE OCCURRED AND ONE EMPLOYEE WAS INJURED. OTHER SSCGP AND CONTRACTOR EMPLOYEES ASSISTED AND LOCAL EMERGENCY RESPONDERS WERE NOTIFIED AT 10:05 AM AND WERE ON SITE WITHIN 10 MINUTES. ONE SSCGP EMPLOYEE WAS TRANSPORTED TO THE LOCAL HOSPITAL BY AMBULANCE AND WAS ADMITTED TO THE HOSPITAL FOR HIS INJURIES. ANOTHER SCCGP EMPLOYEE WAS TAKEN TO THE HOSPITAL BY CAR AS A PRECAUTION AND WAS EXAMINED AND RELEASED WITH NO OBSERVED INJURIES. THE EMPLOYEE THAT WAS ADMITTED WAS RELEASED FROM THE HOSPITAL ON 2/28/2021. REPAIRS ON LINE FM WERE COMPLETED AND THE LINE WAS RETURNED TO SERVICE ON 3/1/2021 AT 7:30 AM. NOTE: EDITS CONTAINED IN THE FINAL SUPPLEMENT INCIDENT REPORT ARE IN: PART C, 3B, 3E, 3G, 3H, C6 PART D, 7D, 7E, 13A PART G7- INCORRECT OPERATION PLEASE REFER TO THE CONTRIBUTING FACTORS, CAUSAL FACTORS, AND ROOT CAUSES CONTAINED IN THE KIEFNER REPORT DATED SEPTEMBER 17, 2021.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210031 | 35078 | 2021-03-25 09:32 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-03-02 12:46 | 2021 | CENTRAL | NO | 29.6755 | -91.2202 | 1299523 | 2021-03-03 14:20 | 1299506 | NATURAL GAS |  | 875 | 746 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-03-05 10:35 | 2021-03-11 15:30 |  | YES | OPERATOR | 2021-03-03 14:13 | NO | [5 empty] | VALVE CLOSURE |  | 2021-03-05 09:15 | VALVE CLOSURE |  | 2021-03-05 10:00 | 0 | 2021-02-26 12:25 | 2021-03-01 09:00 | ONSHORE | LA | 70342 | Not Within a Municipality | ST. MARY | MILEPOST | 99+2341 | EUNICE-THIBODAUX 26" LINE | EUT 26-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 54 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | MAINLINE | GATE |  | WKM, INC. |  |  |  | 1967 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 597 |  | NO | NO | [5 empty] | 0 | 0 | 2059 | 2100.489412568306596 | 2415 | 2415 | 173000 | 176485.997267759612 | 0 | 0 | 0 | 0 |  | 2.76 | 177474 | 80370.111209731272576488372093023255814 | 181001.486680327918596 | 0 | 0 | 0 | 0 | NO |  |  |  | 940 | 320 | 1080 | 192.619(A)(1) |  | 2011-02-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 48773 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [35 empty] | YES | O-RING FAILURE BETWEEN BODY AND BONNET | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 2/26/2021, TEXAS GAS OPERATIONS PERSONNEL RECEIVED NOTIFICATION FROM THE CONTRACT CREW WHO WAS PERFORMING RIGHT-OF-WAY MAINTENANCE THAT THEY OBSERVED BUBBLES IN THE BATEMAN ISLAND AREA INDICATING A POTENTIAL LEAK. OPERATIONS PERSONNEL MADE APPROPRIATE INTERNAL AND EXTERNAL NOTIFICATIONS. THE LEAK WAS INVESTIGATED ON 3/3/2021. INVESTIGATION REVEALED THAT VALVE EUT 10-1 HAD A SLIGHT LEAK COMING FROM BETWEEN THE VALVE BODY AND THE VALVE BONNET. GAS IN THE EUNICE-THIBODAUX 26-INCH LINE (EUT 26) WAS EVACUATED FROM THE EUT 26 TO THE EUNICE-THIBODAUX 20-INCH LINE (EUT 20); THE REMAINDER OF THE PRESSURE IN THE LINE WAS BLOWN TO ATMOSPHERE. THE VALVE BONNET WAS REMOVED, REPAIRED AND REINSTALLED ON 3/11/2021. THE VALVE COMPANY WHO PERFORMED THE REPAIR REPORTED THAT THE O-RING BETWEEN THE VALVE BODY AND VALVE BONNET WAS DAMAGED. THIS EVENT IS A REPORTABLE INCIDENT BECAUSE THE COST TO ACCESS THE LOCATION, WHICH IS IN A WET AREA, CAUSED THE REPAIR COST TO EXCEED $50,000. 3/25/21 UPDATE COST FROM $165,000 TO $173,000 FOR MORE ACCURATE REPORTING.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210032 | 35080 | 2021-03-25 14:18 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-02-25 09:30 | 2021 | CENTRAL | NO | 31.4037 | -89.3454 | 1298958 | 2021-02-25 09:30 | 1299047 | NATURAL GAS |  | 1 | 22 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-27 10:05 | 2021-03-15 16:00 |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | USED EXISTING STOPPLE |  | OPERATIONAL CONTROL | USED EXISTING STOPPLE |  | 0 | 2021-02-24 08:30 | 2021-02-25 09:30 | ONSHORE | MS | 39402 | Not Within a Municipality | FORREST | SURVEY STATION NO. | 4048+64 | HATTIESBURG 8" LINE | INDEX 387 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.188 | 24000 | API 5L | LAP WELDED |  | UNKNOWN | OTHER | ENAMEL | UNKNOWN | [26 empty] | 1931 | 1931 | CARBON STEEL |  | OTHER | [8 empty] | ONLY VAPORS WERE DETECTED WITH AN INSTRUMENT. DUE TO LOCATION BETWEEN LAKES, GULF SOUTH DECIDED TO REPLACE THE PIPE. | CLASS 2 LOCATION | NO |  | 78 |  | NO | NO | [5 empty] | 0 | 0 | 61 | 62.229166666666684 | 3 | 3 | 575000 | 586586.4071038253 | 0 | 0 | 0 | 0 |  | 2.76 | 575064 | 258808.8785307514809970664451827242524917 | 586651.636270491966684 | 0 | 0 | 0 | 0 | NO |  |  |  | 148 | 3000 | 165 | 192.619(A)(4) |  | 2021-02-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 29316 | NO | YES | YES | YES | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) | [5 empty] | YES | YES | [6 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | LEAKING CLAMP | [5 empty] | YES | [122 empty] | YES | [49 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 1/25/2021 DURING ANNUAL LINE PATROL ON INDEX 387 NEAR STATION # 4048+04, BUBBLES WERE NOTICED IN A WET AREA BETWEEN TWO LAKES. TECHNICIAN ATTEMPTED TO VERIFY IF BUBBLES WERE COMING FROM POTENTIAL LEAK ON PIPE BUT WAS UNABLE TO CONFIRM. AFTER FURTHER INVESTIGATION AND VERIFICATION OF NO HAZARDS TO PEOPLE, PROPERTY OR ENVIRONMENT, GULF SOUTH DECIDED TO EXCAVATE PIPE ON 3/5/2021 TO DETERMINE IF A LEAK WAS PRESENT. APPROXIMATELY 10 FEET OF PIPE WERE EXPOSED, SOME PITTING WAS FOUND, BUT NO VISIBLE LEAK ON EXPOSED PIPE WAS DETECTED; HOWEVER, SINCE GAS FUMES WERE DETECTED, FURTHER EXCAVATION WOULD BE REQUIRED. DUE TO PIPE DEPTH AND SOIL CONDITIONS BETWEEN TWO LAKES, GULF SOUTH DECIDED TO REPLACE PIPE IN AREA BETWEEN LAKES. ON 3/6/2021 A SECTION OF PIPE WAS BLOWN DOWN, EXCAVATED, REPLACED AND LINE WAS RETURNED TO SERVICE ON 3/15/2021. THE CAUSE IS IDENTIFIED IN PART G OF THIS REPORT AS A LEAKING CLAMP BUT IT IS UNCLEAR WHETHER THIS OR EXTERNAL CORROSION WAS THE ACTUAL CAUSE. EXTERNAL CORROSION IS IDENTIFIED AS A CONTRIBUTING FACTOR IN PART K.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210033 | 35346 | 2021-03-26 12:32 | SUPPLEMENTAL FINAL | 39010 | BLUE RACER MIDSTREAM, LLC | 5949 SHERRY LANE SUITE 1700 | DALLAS | TX | 75225 | 2021-02-19 08:13 | 2021 | EASTERN | YES | 40.0038 | -80.8921 | 1298392 | 2021-02-19 09:08 | 1298705 | NATURAL GAS |  | 21759 | 559.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-02-19 03:16 | 2021-02-22 14:15 |  | YES | OPERATOR | 2021-02-19 08:30 | NO | [5 empty] | VALVE CLOSURE |  | 2021-02-19 03:16 | VALVE CLOSURE |  | 2021-02-19 04:15 | 0 | 2021-02-19 01:40 | 2021-02-19 03:16 | ONSHORE | OH | 43928 | Not Within a Municipality | BELMONT | NOT APPLICABLE |  | TPL7 | TPL7 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 | NO | 0.375 | 42000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 0.7 |  | CLASS 2 LOCATION | NO |  | 309 |  | NO | NO | [5 empty] | 0 | 0 | 1863 | 1900.539959016393972 | 72457 | 72457 | 220804 | 225253.260928961811376 | 0 | 0 | 0 | 0 |  | 3.33 | 295124 | 147753.9408418319339571395348837209302326 | 299610.800887978205348 | 0 | 0 | 0 | 0 | NO |  |  |  | 620 | 150000 | 720 | 192.619(A)(2) |  | 2012-02-29 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 28267 | YES | [7 empty] | NO | [6 empty] | TYPE A GATHERING | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THAT THE CONTROLLER ACTIONS WERE NOT A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [306 empty] | DANIEL A. GARCIA | REGULATORY COMPLIANCE MANAGER | dgarcia@blueracermidstream.com | 412-980-2282 |  | DANIEL A. GARCIA | dgarcia@blueracermidstream.com | 412-980-2282 | DANIEL A. GARCIA | REGULATORY COMPLIANCE MANAGER | 412-980-2282 | dgarcia@blueracermidstream.com | A THIRD PARTY SUBJECT MATTER EXPERT DETERMINED THE PROXIMATE CAUSE OF THIS INCIDENT WAS LAND MOVEMENT, OR SLIP, EXERTED FORCE ON THE PIPE CAUSING A CIRCUMFERENTIAL CRACK IN AN AREA WHERE EVIDENCE OF SCC AND GENERAL CORROSION WERE FOUND AND IS STILL PENDING FURTHER INVESTIGATION TO DETERMINE IF THERE WERE ANY OTHER CONTRIBUTING FACTORS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210034 | 35101 | 2021-03-30 08:15 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-03-09 10:00 | 2021 | CENTRAL | NO | 36.0576 | -98.5086 | 1299908 | 2021-03-09 12:54 | 1300071 | NATURAL GAS |  | 6736 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-03-09 17:00 | 2021-03-11 17:11 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-03-09 10:06 | NO | [5 empty] | VALVE CLOSURE |  | 2021-03-09 17:00 | VALVE CLOSURE |  | 2021-03-09 17:00 | 0 | 2021-03-09 10:05 | 2021-03-09 10:15 | ONSHORE | OK | 73724 | CANTON | BLAINE | NOT APPLICABLE |  | LINE 2-H | LINE 2-H | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | YES | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 3 | NO | 0.216 | 24000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1928 | 1928 | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 2 LOCATION | NO |  | 23 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 16840 | 16840 | 62300 | 63555.3620218579412 | 5000 | 5100.75136612022 | 0 | 0 |  | 2.5 | 84140 | 41337.949407031226206312292358803986711 | 85496.1133879781612 | 0 | 0 | 0 | 0 | NO |  |  |  | 100 | 2.6 | 120 | 192.619(A)(4) |  | 2012-11-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 32540 | NO | YES | YES | [5 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY LINE STRIKE. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY |  |  | YES | [6 empty] | UTILITY | UNKNOWN/OTHER | TELECOMMUNICATIONS | YES | 21030308530816V |  | UTILITY OWNER | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY WAS NOT LOCATED OR MARKED | [231 empty] | YES | [32 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 4056263981 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4056263981 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 4056263981 | casey.roberts@enablemidstream.com | ON MARCH 9TH, 2021, A THIRD-PARTY CONTRACTOR (HMI UTILITIES) INSTALLING POLY CONDUIT FOR FIBER OPTIC SERVICE WITH A VIBRATORY PLOW TRENCHER STRUCK A 3" SEGMENT OF ENABLE GAS TRANSMISSION (EGT) LINE 2-H. THE LINE STRIKE TOOK PLACE EAST OF CANTON, OKLAHOMA ALONG THE SOUTH SIDE OF STATE HIGHWAY 51 BETWEEN COUNTY ROADS N2520 AND N2530 IN BLAINE COUNTY. ON THE MORNING OF MARCH 8TH, 2021, AN OKIE ONE CALL TICKET (# 21030308530816V) WAS CLEARED IN KORWEB AT 6:57AM. THE TICKET WAS DUE THAT MORNING AT 7:00AM. THERE ARE NO COMMENTS ON THE COMPLETED TICKET IN KORWEB. ON THE MORNING OF MARCH 9TH, 2021, ENABLE RECEIVED A SCADA LOW-PRESSURE NOTIFICATION FROM THE ENABLE CANTON TOWN BORDER DELIVERY AT 10:05AM. ENABLE OPS PERSONNEL ARRIVED AT THE LINE STRIKE SITE SOMETIME AROUND 10:15AM. AFTER SEEING GAS VENTING FROM THE AREA AROUND THE VIBRATORY PLOW OPERATED BY HMI UTILITIES, IT WAS ASSUMED THE VENTING GAS WAS EGT LINE 2-H. THE LOCAL FIRE DEPARTMENTS AND COUNTY SHERIFFS OFFICES WERE ASKED TO BLOCK OFF STATE HIGHWAY 51 TO PREVENT TRAFFIC FROM PASSING INTO THE VENTING GAS PLUME. THE HIGHWAY REMAINED BLOCKED OFF UNTIL A COMPRESSED NATURAL GAS TRANSPORT TRUCK COULD BE DELIVERED TO THE CANTON TOWN BORDER WHICH WOULD ENSURE SUPPLY TO THE CITY OF CANTON. THE TRANSPORT TRUCK ARRIVED AROUND 4:00PM AND CONNECTED TO THE PIPELINE. THE DAMAGED PIPELINE WAS ISOLATED AND VENTED FLAT AT 5:00PM. THE AREA AROUND THE VIBRATORY PLOW WAS VERIFIED TO BE CLEAR OF ALL VENTING GAS WHEN THE ENABLE CONTRACTOR BEGAN EXCAVATING THE PIPELINE TO CONFIRM DAMAGE. IT WAS FOUND THAT 255 FEET OF LINE WOULD NEED TO BE REPLACED DUE TO DAMAGE FROM THE HMI PLOW. THE LINE STRIKE IS DUE TO THE ENABLE EMPLOYEE INCORRECTLY CLEARING THE OKIE ONE CALL TICKET 21030308530816V IN KORWEB. THE ENABLE EMPLOYEE DID NOT COMMUNICATE WITH HMI UTILITIES TO DETERMINE A SCOPE OF WORK. A CALL WAS PLACED TO THE NRC ON 3/9/2021 (#1299908) AND A 48-HOUR FOLLOW UP WAS PLACED ON 3/11/2021 (#1300071).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210035 | 35108 | 2021-03-31 08:31 | ORIGINAL FINAL | 21252 | VIKING GAS TRANSMISSION CO | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2021-03-08 14:00 | 2021 | CENTRAL | NO | 44.743 | -90.7192 | 1299916 | 2021-03-08 14:36 | 1300096 | NATURAL GAS |  | 570 | 8291 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE REDUCED TO 80% OF MAINLINE PRESSURE AND STOPPLE UTILIZED FOR REPAIRS |  |  |  | YES | OPERATOR | 2021-03-08 14:36 | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE REDUCTION TO 80% OF MAINLINE PRESSURE |  | OPERATIONAL CONTROL | PRESSURE REDUCTION TO 80% OF MAINLINE PRESSURE |  | 0 | 2021-03-08 09:30 | 2021-03-08 09:30 | ONSHORE | WI | 54493 | Not Within a Municipality | CLARK | SURVEY STATION NO. | 1044+96 | ONEOK VIKING PIPELINE - ONEOK INDEX NUMBER 2227 | VIKING 24" PIPELINE CHIPPEWA FALLS TO MARSHFIELD | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TUBING | [35 empty] | CARBON STEEL | RIGID |  | 1960 | 1960 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 490 |  | NO | NO | [5 empty] | 3000 | 3060.450819672132 | 29931 | 30534.117827868860964 | 2058 | 2058 | 292000 | 297883.879781420848 | 5000 | 5100.75136612022 | 130 | 132.61953551912572 | ENVIRONMENTAL PCB WIPE TEST FOR REMOVED PIPE. | 3.61 | 332119 | 149894.7076999143123425813953488372093023 | 338769.819330601186684 | 0 | 0 | 0 | 0 | NO |  |  |  | 753 | 11748 | 877 | OTHER | 192.611(A)(3)(III) | 1970-11-11 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 68640 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROLLER ACTIONS WERE PERFORMED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [19 empty] | YES | SOIL MOVEMENT BELIEVED TO STRESS 1/2" LINE CAUSING CRACK. | [161 empty] | BRENT THEEDE | REGULATORY COMPLIANCE SPECIALIST | brent.theede@oneok.com | 620-820-3047 |  | GREG LINDBLOM | gregory.lindblom@oneok.com | 1-651-994-0332 | ROGER THORPE | VP NATURAL GAS OPERATIONS | 1-918-588-7405 | roger.thorpe@oneok.com | ON MARCH 8 WHILE COMPLETING A SECURITY PATROL, LEAKING GAS WAS IDENTIFIED FROM UNDERGROUND, NEAR MAINLINE VALVE 2229. THE PIPELINE PRESSURE WAS REDUCED TO 80% OF THE OPERATING PRESSURE OF WHEN THE LEAK WAS DISCOVERED. ON MARCH 9, THE OPERATIONS TEAM DECIDED A STOPPLE WOULD NEED TO BE INSTALLED ON THE MAINLINE TO ISOLATE THE VALVE AND DETERMINE THE CAUSE OF THE RELEASE. SINCE THE EXPENSE OF THE WORK RELATED TO RELEASE COULD POSSIBLY EXCEED $50,000.00 AN NRC REPORT WAS SUBMITTED (NRC #1299916 & 1300096). UPON EXCAVATION, A CRACK IN THE TREADED AREA OF A 1/2" PIPE NIPPLE WAS DISCOVERED TO BE THE CAUSE OF THE LEAK. THIS 1/2" LINE WAS TO PROVIDE A PATH FOR BODY BLEED GAS TO GET FROM THE VALVE BODY BLEED PORT (LOCATED AT THE BOTTOM OF THE GATE VALVE) TO ABOVE GRADE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210036 | 35111 | 2021-03-31 12:36 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-03-03 08:15 | 2021 | CENTRAL | NO | 32.727 | -97.2154 | 1299475 | 2021-03-03 09:17 | 1299643 | NATURAL GAS |  | 11500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE POWER PLANT WAS NOT ONLINE AT THE TIME OF THE RELEASE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-03-03 06:54 | 2021-03-03 07:10 | ONSHORE | TX | 76112 | FT. WORTH | TARRANT | NOT APPLICABLE |  | HANDLEY 12IN LATERAL 2100 YARD | 9046 HANDLEY 12IN LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | PILOT WAS PREVIOUSLY DAMAGED | 1960 | 1960 | CARBON STEEL |  | OTHER | [8 empty] | NATURAL GAS WAS RELEASED AT THE RELIEF VALVE | CLASS 2 LOCATION | YES | METHOD2 | 499 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 34500 | 34500 | 2500 | 2550.37568306011 | 0 | 0 | 0 | 0 |  | 3 | 37000 | 23762.171263139263264119601328903654485 | 37050.37568306011 | 0 | 0 | 0 | 0 | NO |  |  |  | 380 | 0 | 811 | 192.619(A)(2) |  | 1960-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | EXCELON EMPLOYEES NOTIFIED GAS CONTROL OF RELIEF VALVE OPENED. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES |  | YES | PILOT DIAPHRAGM WAS DAMAGED PREVIOUSLY DUE TO EXTREME WINTER WEATHER IN FEBRUARY | [22 empty] | YES | EXTREME WINTER WEATHER | [123 empty] | YES | [37 empty] | ANGELA MORGAN | LEAD SPECIALIST - REGULATORY COMPLIANCE | angela.morgan@energytransfer.com | 19032436541 |  | ANGELA MORGAN | angela.morgan@energytransfer.com | 19032436541 | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 9795319036 | chris.kresta@energytransfer.com | ON WEDNESDAY 3/3/21, AT APPROXIMATELY 06:54, A RELIEF VALVE OPENED CAUSING A RELEASE OF NATURAL GAS AT THE HANDLEY 2100 YARD WHICH SUPPLIES THE EXCELON (TEXGEN) HANDLEY POWER PLANT. EXCELON NOTIFIED GAS CONTROL OF THE RELEASE AT 06:55 AND GAS CONTROL IMMEDIATELY NOTIFIED OPERATIONS. ADDITIONAL OPERATIONS PERSONNEL WERE NOTIFIED TO DETERMINE WHO HAD THE SHORTEST RESPONSE TIME. OPERATIONS PERSONNEL ARRIVED ON SCENE AT 07:10 AND BECAUSE THE HANDLEY POWER PLANT WAS NOT ONLINE AT THE TIME OF THE RELEASE, THE VALVE WAS CLOSED AT 07:15. OPERATIONS PERSONNEL ASSESSED THE SITUATION AND DETERMINED THE PILOT FOR THE 2ND CUT REGULATOR WAS DAMAGED DURING THE EXTREME COLD WEATHER THAT OCCURRED FEBRUARY 14 - 21, 2021. THIS MALFUNCTION OCCURRED WHILE BRINGING THE STATION ON LINE FOR THE FIRST TIME SINCE THE COLD WEATHER EVENT. OPERATIONS PERSONNEL REPLACED THE PILOTS AT EACH CUT AND AT 09:15 RESTORED NORMAL OPERATIONS TO THE HANDLEY POWER PLANT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210037 | 36405 | 2021-04-05 18:23 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-03-07 11:27 | 2021 | EASTERN | NO | 41.8571 | -78.0014 | 1299771 | 2021-03-07 12:51 | 1299835 | NATURAL GAS |  | 10651 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STATION POSESS RELIEF VALVE REDUNDANCY. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-03-07 11:24 | 2021-03-07 11:24 | ONSHORE | PA | 16915 | Not Within a Municipality | POTTER | NOT APPLICABLE |  | COMPRESSOR STATION 313 | COMPRESSOR STATION 313 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELEASE FROM VALVE DUE TO LOSS OF POWER GAS DESIGNED TO KEEP THE VALVE CLOSED DURING NORMAL OPERATION. | CLASS 1 LOCATION | NO |  | 574 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 26521 | 26521 | 2500 | 2550.37568306011 | 100 | 102.0150273224044 | 0 | 0 |  | 2.49 | 29121 | 18571.7860206415779807308970099667774086 | 29173.3907103825144 | 0 | 0 | 0 | 0 | NO |  |  |  | 1049 | 140712 | 1250 | OTHER | ANSI 600 RATED VALVE | 2005-08-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | WATER ACCUMULATION AND FREEZING. | [161 empty] | JORGE LOPEZ | MANAGER ENGINEERING | jorge_lopez@kindermorgan.com | 713-420-4675 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON SUNDAY MARCH 7TH, AT 11:24 EST THE HEBRON WITHDRAWAL RELIEF VALVE (313C-101) AT TENNESSEE GAS PIPELINE'S (TGP) COMPRESSOR STATION 313, ACTUATED PREMATURELY. AT THE TIME OF EVENT, THE TGP OPERATOR, WORKING FROM COMPRESSOR STATION 313, WAS PERFORMING HIS HOURLY CHECKS HEARD THE RELEASE OF GAS, INITIATED THE INVESTIGATION AND CONTACTED THE OPERATIONS SUPERVISOR AT 11:25 AM. AFTER CONSIDERING SAFE APPROACH PROTOCOLS, AND CONFIRMING PRESSURE WAS BELOW ESTABLISHED MAOP, THE TGP OPERATOR ISOLATED RELIEF VALVE AT APPROXIMATELY 11:35 EST. LINE PRESSURE AT THE TIME OF EVENT WAS 1049 PSIG AND SET PRESSURE OF RELIEF VALVE WAS 1250 PSIG. DUE TO REDUNDANT OVER PRESSURE PROTECTION, NO FACILITIES WERE TAKEN OUT OF SERVICE DUE TO THIS INCIDENT. AT 12:30 EST, AN INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL COMMENCED AND DURING THAT CALL, TGP PERSONNEL ANNOUNCED THAT IT HAD DETERMINED THE RELEASE VOLUME EXCEEDED 3,000 MSCF. AT 12:51 EST, TGP NOTIFIED THE NRC OF THE EVENT AND ESTIMATED THE TOTAL GAS LOSS AT GREATER THAN 3,000 MSCF. THE TOTAL UN-INTENTIONAL GAS LOSS WAS LATER DETERMINED TO BE 10,651MSCF AND REPORTED TO THE NRC AS A 48-HR UPDATE. AFTER ISOLATION, TGP OPERATOR PERFORMED A VISUAL INVESTIGATION FOR THE IMMEDIATE CAUSE OF MALFUNCTION AND FOUND NO EXTERNAL ISSUES WITH RELIEF VALVE. TGP OPERATOR THEN REMOVED THE RELIEF VALVE FROM SERVICE AND CONDUCTED ROOT CAUSE ANALYSIS. WATER WAS DISCOVERED INSIDE THE VALVE HOUSING WHICH ALLOWED THE FORMATION OF HYDRATES INSIDE THE RELIEF VALVE'S PILOT CONTROL DEVICE, WHICH SUPPLIES PRESSURE TO THE TOP OF THE VALVE TO KEEP IT IN THE CLOSED POSITION. WITHOUT THE PRESSURE FROM THE TOP OF THE RELIEF THE VALVE THE VALVE SIT LIFTED ALLOWING THE GAS RELEASE. EXCESSIVE WATER, COUPLED WITH AN UNPRECEDENTED AMOUNT OF FREEZE AND THAW CYCLES IN THE PAST MONTH, ALLOWED FOR THE RELIEF VALVE TO ACTIVATE. THE VALVE WAS SERVICED BY AN OEM APPROVED VENDOR FOR COMPLETE REBUILD AND INSPECTION TO ENSURE THERE WAS NO MECHANICAL DAMAGE TO THE VALVE'S INTEGRAL PARTS. RELIEF VALVE WAS REINSTALLED AND BACK IN-SERVICE ON 3/22/2021. FOLLOWING THE EVENT, THE FREQUENCY OF METHANOL DRIP INSPECTIONS CHANGED FROM WEEKLY TO EVERY OTHER DAY FOR THOSE LOCATIONS WITH A HISTORY OF HYDRATE PRODUCTION DURING COLD AMBIENT TEMPERATURES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210038 | 35167 | 2021-04-13 14:29 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-03-14 01:00 | 2021 | CENTRAL | NO | 35.3914 | -98.4758 | 1300269 | 2021-03-14 03:58 | 1300352 | NATURAL GAS |  | 23573 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-03-13 11:47 | 2021-03-14 01:03 | ONSHORE | OK | 73053 | LOOKEBA | CADDO | NOT APPLICABLE |  | HINTON COMPRESSOR STATION | AD-WEST | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | ESD | [5 empty] | CLASS 1 LOCATION | NO |  | 523 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 60818 | 60818 | 500 | 510.075136612022 | 500 | 510.075136612022 | 0 | 0 |  | 2.58 | 61818 | 40355.549568378628893687707641196013289 | 61838.150273224044 | 0 | 0 | 0 | 0 | NO |  |  |  | 760 | 320 | 1000 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION ESD | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [142 empty] | YES | [5 empty] | YES | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@enablemidstream.com | 4055584647 |  | CASEY ROBERTS | casey.roberts@enablemidstream.com | 4055584647 | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | 4055584647 | casey.roberts@enablemidstream.com | AN ESD WAS ACTIVATED AT THE ENABLE GAS TRANSMISSION (EGT) HINTON TURBINE COMPRESSOR STATION. THE STATION ESD ACTIVATED OPENING THE 6" AND 2" STATION VENT VALVES. THE STATION MAIN LINE SUCTION BLOCK VALVE TIED TO EGT LINE AD-WEST DID NOT CLOSE. ENABLE GAS CONTROL RECEIVED ALARMS AND IMMEDIATELY NOTIFIED OPERATIONS TO INVESTIGATE THE INCIDENT. THE OPERATIONS TEAM VERIFIED THE STATION ESD VENTS WERE IN THE OPEN POSITION AND CLOSED THE MAIN LINE SUCTION BLOCK VALVE SECURING THE STATION. AS A RESULT, ROUGHLY 23,000 MCF OF NATURAL GAS VENTED TO THE ATMOSPHERE UNINTENTIONALLY. ENABLE CONTACTED THE NRC TO PROVIDE NOTICE OF INCIDENT ON MARCH 14TH (#1300269) AND A 48 HR. FOLLOW UP (#1300352) ON MARCH 15TH. IT WAS LATER DETERMINED THAT A POWER GAS SUPPLY VALVE, WHICH IS ALSO THE SUPPLY GAS FOR THE STATION ESD SYSTEM, WAS IN THE CLOSED POSITION. THE CLOSED POWER GAS SUPPLY VALVE ISOLATED NOT ONLY THE ACTUATOR SUPPLY GAS TO THE STATION MAIN LINE SUCTION VALVE, BUT ALSO ISOLATED THE ESD PILOT SUPPLY GAS. IT IS ASSUMED THAT THERE WAS A SMALL LEAK ON THE POWER SUPPLY/ESD SUPPLY GAS PIPING THAT CAUSED THE ESD PILOT PRESSURE TO FALL BELOW THE ESD PRESSURE SWITCH SETPOINT. WHEN THE PRESSURE SETPOINT OPENS THE ELECTRIC SIDE OF THE ESD SYSTEM WILL TRIGGER AN ESD AND VENT THE REMAINING ESD PILOT PRESSURE CAUSING THE STATION ESD VALVES TO ACTUATE. PRIOR TO THE ESD (3/10/2021), ANNUAL VALVE MAINTENANCE OCCURRED AT THE INACTIVE HINTON TURBINE COMPRESSOR STATION. ALL STATION VALVES WERE OPERATED AND LUBRICATED DURING MAINTENANCE THIS DAY, INCLUDING THE POWER GAS SUPPLY VALVE. ON THIS DAY, THE TECHNICIAN STATED HE FOUND THE POWER GAS SUPPLY VALVE IN THE CLOSED POSITION. ALTHOUGH IT WAS CLOSED, THE TECHNICIAN PERFORMED THE REQUIRED MAINTENANCE AND LEFT THE VALVE IN A CLOSED POSITION. IT CANNOT BE DETERMINED WHEN THE VALVE WAS INADVERTENTLY CLOSED. BASED ON THE FINDINGS, OQ DISQUALIFICATIONS WERE RECOMMENDED ON OQ TASK 007 OPERATE VALVES FOR 2 ENABLE OPERATIONS EMPLOYEES AS NEITHER ONE RECOGNIZED THE SUPPLY GAS VALVE BEING IN THE WRONG POSITION, OR THAT THE POWER SUPPLY GAS LINE WAS LEAKING PRIOR TO THE MAINTENANCE AND VALVE OPERATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210039 | 35209 | 2021-04-23 15:53 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-03-29 00:41 | 2021 | CENTRAL | YES | 32.6401 | -88.6606 | 1301466 | 2021-03-29 10:12 | 1301608 | NATURAL GAS |  | 42561 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-03-29 01:05 | 2021-03-29 08:30 |  | NO |  |  | NO | [11 empty] | 0 | 2021-03-29 00:35 | 2021-03-29 00:55 | ONSHORE | MS | 39326 | Not Within a Municipality | KEMPER | NOT APPLICABLE |  | STATION 542 | VALVE 542AS-2R | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2014 | 2014 | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE OUT OF COMPRESSOR STATION VENT STACK | CLASS 1 LOCATION | NO |  | 760 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 106828 | 106828 | 0 | 0 | 500 | 510.075136612022 | 0 | 0 |  | 2.51 | 107328 | 70319.8096679102446794019933554817275748 | 107338.075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 915 | 132200 | 936 | 192.619(C) |  | 1963-11-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR OF COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON MARCH 29TH, 2021, AT 12:35AM, TENNESSEE GAS PIPELINE COMPANY, LLC (TGP) RECEIVED AN ESD ALARM AT ITS COMPRESSOR STATION 542 IN KEMPER COUNTY, MISSISSIPPI. UPON RECEIPT OF THE ALARM, GAS CONTROL DISPATCHED A TECHNICIAN TO THE SITE TO INVESTIGATE. AFTER ARRIVING ON SITE AT APPROXIMATELY 12:55AM THE TECHNICIAN FOUND VALVE 542AS-2R, AN EMERGENCY VALVE WHICH IS USED TO ISOLATE THE STATION IN THE EVENT OF THE ESD, OPEN AND THE VALVE SELECTOR IN THE MANUAL POSITION. AFTER CHANGING THE VALVE SELECTOR TO THE AUTOMATIC POSITION THE VALVE CLOSED AT 1:05AM, ENDING THE GAS RELEASE. INITIAL GAS RELEASE ESTIMATES PUT THE RELEASE BELOW THE 3,000 MCF THRESHOLD FOR REPORTING. LATER THAT MORNING AT 9:40AM TGP HAD CONFIRMED DISCOVERY OF THE INCIDENT WHEN IT WAS DISCOVERED THAT THE INITIAL GAS RELEASE CALCULATIONS WERE INCORRECT AND THE GAS LOSS WOULD EXCEED THE REPORTABLE THRESHOLD. TGP BEGAN TESTING THE ESD SYSTEM AT STATION 542 ON OCTOBER 26, 2020. DURING THIS TEST, TGP SWITCHED THE VALVE 542AS-2R SELECTOR INTO THE MANUAL POSITION AND INSTALLED PLUGS WITHOUT WEEP HOLES INTO THE ESD SYSTEM. TGP STATION 542 HAS A PRESSURE TO ACTIVATE ESD SYSTEM. THE PLUGS WITH WEEP HOLES DO NOT ALLOW A SMALL VALVE LEAK ON THE ESD SYSTEM TO PRESSURIZE THE ESD SYSTEM AND TRIGGER AN ESD. AFTER COMPLETION OF THE ESD TEST, TGP DID NOT REINSTALL THE PLUGS WITH WEEP HOLES INTO THE SYSTEM. THE ESD SYSTEM WAS ACTIVATED AS A RESULT OF THE SYSTEM SLOWLY BECOMING PRESSURIZED DUE TO NOT REINSTALLING THE PLUGS WITH WEEP HOLES INTO THE ESD SYSTEM AFTER COMPLETION OF THE ESD TEST. BECAUSE THE VALVE 542AS-2R SELECTOR WAS IN THE MANUAL POSITION, THE VALVE DID NOT CLOSE WHEN THE ESD SYSTEM WAS ACTIVATED. RESULTANTLY, AFTER THE ESD, GAS CONTINUED TO VENT UNTIL THE VALVE 542AS-2R SELECTOR WAS PLACED INTO THE AUTOMATIC POSITION. TGP HAS REVOKED THE OPERATOR QUALIFICATION ASSOCIATED WITH ESD TESTING FOR THE INDIVIDUALS INVOLVED IN THE OCTOBER 2020 ESD TEST. TGP WILL INSTALL SIGNAGE TO REMIND EMPLOYEES TO LEAVE THE ESD REMOTE VALVE SELECTORS IN THE AUTOMATIC POSITION. TGP WILL REVISE ITS STATION 542 ESD TESTING PROCEDURES TO PROVIDE INSTRUCTIONS FOR LEAVING THE WEEP-HOLE PLUGS IN THE ESD SYSTEM DURING THE TEST AND LEAVING ESD VALVE SELECTORS IN THE CORRECT POSITION UPON COMPLETION OF THE TEST. IN PART E 1.A, THE ESTIMATED GAS FLOW IN PIPE SEGMENT AT THE POINT AND TIME OF THE INCIDENT (MSCF/D) IS 1,322,000 MSCF/D.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210040 | 35578 | 2021-04-27 12:14 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-03-31 01:50 | 2021 | CENTRAL | YES | 30.9828 | -94.1408 | 1301650 | 2021-03-31 09:17 | 1301783 | NATURAL GAS |  | 3770 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ISOLATION WAS ONLY NECESSARY FOR THE FAILED RELIEF VALVE. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-03-31 02:11 | 2021-03-31 02:26 | ONSHORE | TX | 75951 | JASPER | JASPER | SURVEY STATION NO. | 32 | STATION 32 | JASPER COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATION RELEASED GAS THROUGH VENT SYSTEM | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 9029 | 9029 | 5986 | 6106.619535519127384 | 106 | 108.135928961748664 | 0 | 0 | VALVE MANUFACTURER JUST REBUILT RELIEF VALVE SO COSTS ARE CAPTURED IN 7B | 2.395 | 15121 | 8666.055943984534130644518272425249169435 | 15243.755464480876048 | 0 | 0 | 0 | 0 | NO |  |  |  | 740 | 60000 | 1440 | 192.619(A)(1) |  | 2007-10-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE MECHANICAL MALFUNCTION IN THE FIELD | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | MECHANICAL FAILURE BUT OEM DECIDED TO JUST REBUILD THE RELIEF VALVE | [161 empty] | KENNETH PETERS | SENIOR PIPELINE ENGINEER | ken_peters@kindermorgan.com | 12058076163 | 12053253729 | JOE SYDES | joe_sydes@kindermorgan.com | 14096580848 | JAIME HERNANDEZ | DIRECTOR COMPLIANCE CODES STANDARDS | 17133699443 | jaime_hernandez@kindermorgan.com | KINDER MORGAN TENNESSEE GAS PIPELINE (TGP) GAS CONTROL IN HOUSTON, TX NOTICED A PRESSURE DROP VIA SCADA ON MARCH 31, 2021 AT 2:11 AM CDT AT THE TGP JASPER COMPRESSOR STATION 32. LOCAL PERSONNEL WERE CALLED TO THE SITE AND GAS CONTROL ADVISED THAT LOGS SHOWED PRESSURE DROP BEGAN AT 1:50 AM CDT ON 3/31/21. LOCAL PERSONNEL FOUND THAT A GARRETT ANSI 600 3" X 4" RELIEF VALVE HAD FAILED, PREMATURELY RELEASING GAS BELOW ITS SETPOINT OF 800 PSIG. THE RELIEF VALVE WAS ISOLATED AND THE GAS RELEASE CEASED AFTER 36 MINUTES, RELEASING A TOTAL OF 3,770 MCF OF NATURAL GAS. THE RELIEF VALVE WAS SHIPPED TO THE ORIGINAL EQUIPMENT MANUFACTURER (OEM) WHO DECIDED TO REBUILD THE RELIEF VALVE AND SHIP IT BACK TO TGP. RELIEF VALVE WAS REINSTALLED AND PLACE BACK INTO SERVICE APRIL 9, 2021. A 48-HOUR UPDATE WAS MADE TO THE NRC ON APRIL 1, 2021, ASSIGNED NRC REPORT #1301783.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210041 | 35241 | 2021-04-28 09:32 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-03-31 15:00 | 2021 | CENTRAL | YES | 40.2205 | -96.074 | 1301696 | 2021-03-31 15:45 | 1301837 | NATURAL GAS |  | 10 | 40 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR GRADE 3 LEAK DISCOVERED AND CONTROLLED UNTIL REPAIRS COULD BE MADE |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE IN THE PIPELINE WAS LOWERED TO LESSEN GRADE 3 LEAK AND CONTINUE SERVICE TO 3 TOWNS |  | OPERATIONAL CONTROL | PRESSURE IN THE PIPELINE WAS LOWERED TO LESSEN GRADE 3 LEAK AND CONTINUE SERVICE TO 3 TOWNS |  | 0 | 2021-03-17 16:00 | 2021-03-31 08:00 | ONSHORE | NE | 68447 | Not Within a Municipality | PAWNEE | MILEPOST | 3.95 | PAWNEE CITY BRANCH LINE | NEB46401 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4.5 | NO | 0.188 | 24000 | UNKNOWN | SEAMLESS |  | US STEEL | NONE |  | NO | [26 empty] | 1932 | 1932 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 62 |  | NO | NO | [5 empty] | 100 | 102.0150273224044 | 144 | 146.901639344262336 | 36 | 36 | 122000 | 124458.333333333368 | 100 | 102.0150273224044 | 0 | 0 |  | 3.6 | 122380 | 55084.6888854093255287973421926910299003 | 124845.265027322439136 | 0 | 0 | 0 | 0 | NO |  |  |  | 293 | 2 | 400 | 192.619(C) |  | 1932-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 25449 | NO |  |  |  | YES |  |  |  | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1960 | NO | YES | YES |  |  |  | 2020 |  |  |  | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JOHN A GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 4023987494 |  | JOHN GORMLEY | john.gormley@nngco.com | 4023987494 | TOM CORRELL | VP PIPELINE SAFETY AND RISK | 4023987715 | thomas.correll@nngco.com | ON MARCH 17, 2021 ENERGY ECONOMICS REPORTED A GAS LEAK ON THE PAWNEE CITY (NEB46401) 4-INCH BRANCH LINE AT MP 3.95 WHILE CONDUCTING A GAS LEAK DETECTION SURVEY. ON MARCH 31, 2021, THE LEAK WAS INVESTIGATED BY OPERATIONS PERSONNEL, REPORTED TO PIPELINE SAFETY, AND CLASSIFIED AS GRADE 3. THE LEAK IS AT THE EDGE OF A MARSH AND HAS THREE FEET OF COVER IN THE VICINITY OF THE LEAK. THE LEAK IS VERY MINOR AND IS ONLY DETECTABLE WITH GAS LEAK DETECTION EQUIPMENT. THIS INCIDENT REPORT IS BEING SUBMITTED BECAUSE THE REPAIRS WILL EXCEED THE INCIDENT REPORTING LIMIT. AT THIS TIME (04/28/21 08:27 CDT). UPDATE 05/03/21 09:44 CDT - THE PIPE HAS BEEN REPLACED AND THE PIPELINE PLACED BACK IN SERVICE. THE ROOT CAUSE WAS GENERAL EXTERNAL CORROSION. THE CORROSION RESULTED IN A PIN-HOLE LEAK. THE REMOVED PIPE WILL NOT BE SUBMITTED FOR METALLURGICAL ANALYSIS. THE NEW PIPE IS COATED WITH FUSION BONDED EPOXY AND CATHODICALLY PROTECTED. APPROXIMATELY 700 FEET OF 4-INCH PIPE WAS INSTALLED. THE REPAIR WAS COMPLETED ON MAY 2, 2021 AND THE PIPELINE PLACED BACK IN SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210042 | 36143 | 2021-04-29 19:53 | SUPPLEMENTAL FINAL | 32645 | HILCORP ALASKA, LLC | 3800 CENTERPOINT DR. SUITE 1400 | ANCHORAGE | AK | 99503 | 2021-04-01 16:50 | 2021 | ALASKA | YES | 60.7836 | -151.4559 | 1301801 | 2021-04-01 17:19 | 1301803, 1301896 | NATURAL GAS |  | 2619 | 34 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-04-03 13:30 |  | YES | YES | OPERATOR | 2021-04-01 17:19 | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE AND FLOW RATE REDUCED |  | OPERATIONAL CONTROL | PRESSURE AND FLOW RATE REDUCED |  | 0 | 2021-04-01 16:50 | 2021-04-01 17:19 | OFFSHORE | [6 empty] | MIDDLE GROUND SHOAL GAS PIPELINE | MGS A PIPELINE | [20 empty] | 80 | IN STATE WATERS | AK | ALASKA | SEC 18 OF TOWNSHIP 8N RANGE 12W SEWARD MERIDIAN AK | KENAI PENINSULA BOROUGH |  |  |  | BELOW WATER, PIPE ON OR ABOVE SEABED | INTRASTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 8 | NO | 0.594 | 35000 | API 5L GR B | SEAMLESS |  | UNKNOWN | OTHER | X-TRU COAT W/ CONCRETE WEIGHT COAT | NO | [26 empty] | 1965 | 1965 | CARBON STEEL |  | LEAK |  |  | OTHER | MULTIPLE CAUSE FAILURE | [5 empty] | CLASS 1 LOCATION | NO |  | 133 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 238 | 242.795765027322472 | 18333 | 18333 | 750000 | 765112.704918033 | 200000 | 204030.0546448088 | 1103000 | 1125225.751366120532 | DIVERS, LABOR, ENGR, LAB, MTRLS, STABILIZATION, FREEZE PROTECTION & LOGISTICS | 7 | 2071571 | 936091.4142799281360720465116279069767442 | 2112944.306693989654472 | 0 | 0 | 0 | 0 | NO |  |  |  | 200 | 2000 | 499 | 192.619(A)(2) |  | 2017-09-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 37193 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED | YES | YES | YES | FRACTOGRAPHIC, SEM, MECHANICAL, ETC. | [13 empty] | OTHER | TIME-DEPENDENT CRACKING MECHANISM, EXACERBATED BY ADDITIONAL FACTORS INCLUDING PIPELINE BENDING STRESS, METAL LOSS, INCREASED STRESS CONCENTRATION FACTORS FROM ADJACENT CLAMP, POTENTIAL HISTORIC MECHANICAL DAMAGE, ETC. THE OBSERVED FAILURE MECHANISM WAS NOT CONSISTENT WITH TRADITIONAL ONSHORE PIPELINE STRESS CORROSION CRACKING. |  |  | YES |  | YES | [6 empty] | YES | METAL LOSS DUE TO EXTERNAL CORROSION AND EXTERNAL ABRASIVE DAMAGE DUE TO PIPE MOVEMENT CAUSED BY HIGH CURRENT VELOCITIES. | 754 | [54 empty] | YES |  |  | YES | YES | [23 empty] | 2017 | FREE SWIMMING | WALL MEASUREMENT |  | STANDARD RESOLUTION | [7 empty] | 2017 | FREE SWIMMING | STANDARD RESOLUTION |  | INSIDE ILI CUPS | [19 empty] | YES | 2017 | 754 | NO | [13 empty] | NO | [13 empty] | YES | [23 empty] | YES |  |  |  |  | YES | [20 empty] | CHRIS HEIMLICH | COMPLIANCE ENGINEER | cheimlich@hilcorp.com | 907-777-8536 |  |  |  |  | BEN WASSON | RISK COMPLIANCE MANAGER | 907-777-8447 | bwasson@hilcorp.com | AT APPROXIMATELY 16:30 HOURS ON APRIL 1, 2021 DURING NORMAL HELICOPTER OPERATIONS BUBBLES WERE OBSERVED AT THE SURFACE OF THE WATER. NRC WAS NOTIFIED LESS THAN ONE HOUR LATER. THE LOCATION OF THE BUBBLES WAS MAPPED AND CONFIRMED TO BE WITHIN CLOSE PROXIMITY TO MGS A PIPELINE. PRODUCTION ON THE PLATFORM WAS SHUT-IN AND PIPELINE PRESSURE WAS REDUCED TO LIMIT THE LEAK TO THE FULLEST EXTENT POSSIBLE WHILE MAINTAINING POSITIVE PRESSURE INSIDE THE PIPELINE. LOCAL DIVE RESOURCES WERE CONTACTED AND CONTRACTED TO BEGIN GATHERING AND PLANNING FOR PIPELINE REPAIRS. ON APRIL 2, 2021 THE PIPELINE PRESSURE WAS LOWERED TO 64 PSIG. ARRANGEMENTS WERE MADE TO MAINTAIN ELECTRICAL GENERATION AND HEAT UTILIZING DIESEL GENERATORS. SUBSEA SONAR RESOURCES WERE ENGAGED AND BEGAN PREPARING FOR A MULTI-BEAM SONAR SURVEY OF THE AREA TO VERIFY THE LEAK AND DETERMINE THE LEAK LOCATION. MONITORING OF ICE FLOWS AND WEATHER CONDITIONS BEGAN FOR THE AREA, SO THE SUBSEA RESOURCES COULD BE SAFELY MOBILIZED. ON APRIL 3, 2021 OPERATIONS SHUT IN MGS A GAS PIPELINE. HILCORP POSITIVELY IDENTIFIED THE LEAK LOCATION ON APRIL 6, 2021. DIVERS HAVE BEEN MOBILIZED TO THE SITE AND HILCORP IS CURRENTLY WORKING TO DETERMINE THE CAUSE OF THE GAS LEAK IN ACCORDANCE WITH THE AMENDED CORRECTIVE ACTION ORDER ISSUED BY PHMSA ON APRIL 6, 2021. THE DAMAGED PIPELINE SEGMENT WAS REMOVED FOR FURTHER INVESTIGATION AND PIPELINE ENDS STABILIZED. ON AUGUST 27, 2021 ADV INTEGRITY ISSUED A ROOT CAUSE FAILURE ANALYSIS TO HILCORP AS FOLLOWS: 1. THE SUBJECT FAILURE OCCURRED DUE TO A TIME-DEPENDENT CRACKING MECHANISM, LIKELY FATIGUE, WHICH WAS LIKELY EXACERBATED BY OTHER ENVIRONMENTAL FACTORS. THE FEATURES IDENTIFIED WERE NOT CONSISTENT WITH TYPICAL PIPELINE STRESS CORROSION CRACKING. 2. THE LOCAL STRESS STATE CONTRIBUTED TO THE OBSERVED THROUGH-WALL CRACK. THIS LOCAL STRESS STATE INCLUDED: (1) THE HIGH TENSILE LOAD RESULTING FROM THE PIPE'S CONTOUR ACROSS THE ROCKY OUTCROPPING, (2) THE PRESENCE OF THE PLIDCO CLAMP IMMEDIATELY ADJACENT TO THE FAILURE WHICH CONTRIBUTED TO THE RIGIDITY OF THE PIPELINE, AND (3) THE REDUCED WALL THICKNESS AS A RESULT OF EXTERNAL CORROSION AND ABRASION. 3. MECHANICAL PROPERTIES OF THE PIPE AND GIRTH WELD WERE CONSISTENT WITH API 5L, GRADE B MATERIAL. SUBPART K SELECTION DESCRIPTIONS: - PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION: THE PREVIOUS OWNER INSTALLED A PLIDCO PIPE CLAMP IN 2014 JUST UPSTREAM OF THE FAILURE LOCATION. IMPROPER SUPPORT OF THE PIPELINE DURING AND AFTER LIFTING COULD ALSO IMPART RESULTING STRESS AT AND NEARBY THE PLIDCO. - EXTERNAL CORROSION, GALVANIC: REDUCED WALL THICKNESS DUE TO EXTERNAL CORROSION AND ABRASION WHERE FOUND AT THE SITE OF THE LEAK. - INSTALLATION RELATED: INCREASED TENSILE LOAD RESULTING FROM THE PIPE'S CONTOUR ACROSS THE ROCKY OUTCROPPING, AND THE INCREASED RIGIDITY FROM THE NEAR BY PLIDCO CLAMP INCREASING THE STRESS CONCENTRATION FACTOR IN THAT LOCATION. THIS PIPELINE WILL NOT BE BROUGHT BACK INTO SERVICE AS HILCORP HAS DECIDED TO PURSUE THE ABANDONMENT OF THIS LINE. NOTE: THE ORIGINAL REPORT SUBMITTED ON 4/29/21 ERRONEOUSLY REPORTED 1,052 MCF UNINTENTIONAL AND 1,567 MCF INTENTIONAL RELEASE VOLUMES DUE TO CONFUSION OVER THE DEFINITION OF THESE TWO METRICS. 2,619 MCF OF GAS WAS UNINTENTIONALLY RELEASED FROM THE TIME THE LEAK BEGAN UNTIL THE SHUT-IN PIPELINE PRESSURE EQUALIZED WITH THE ATMOSPHERIC PRESSURE AT THE BOTTOM OF THE INLET. CONTROLLED AND INTENTIONAL DISPLACEMENT OF GAS USING NITROGEN WAS USED TO DETERMINE THE EXACT LOCATION OF THE LEAK. MULTI-BEAM SONAR FIRST CONFIRMED THE LOCATION. THEN DIVERS WERE MOBILIZED TO INSPECT THE LOCATION. THE PIPELINE WAS AT 35 PSIG (STATIC HEAD PRESSURE) WHEN LEAK LOCATION OPERATIONS WERE ENACTED. AT 35 PSIG THE TOTAL PIPELINE VOLUME IS ESTIMATED AT 34 MCF OF NATURAL GAS. THEREFORE HILCORP IS ASSUMING A MAXIMUM INTENTIONAL GAS RELEASE OF 34 MCF.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210043 | 35854 | 2021-04-30 10:36 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2021-04-13 09:00 | 2021 | EASTERN | NO | 36.1063 | -79.7491 | 1302684 | 2021-04-14 17:01 | 1303027 | NATURAL GAS |  | 0.1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ISOLATED SECTION FOR REPAIR. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-04-13 09:00 | 2021-04-13 09:00 | ONSHORE | NC | 37081 | GREENSBORO | GUILFORD | SURVEY STATION NO. | 3081 | LINE 200 | 200-MLV-6 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | FLANGE ASSEMBLY | [38 empty] | 1974 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 162 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 275000 | 280541.3251366121 | 0 | 0 | 0 | 0 |  | 2.5 | 275000 | 123764.088114754175 | 280541.3251366121 | 0 | 0 | 0 | 0 | NO |  |  |  | 405 | 3100 | 550 | 192.619(A)(2) |  | 1974-07-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK SURVEYOR DISCOVERED THE LEAK. ALSO THE LEAK WAS TOO INSIGNIFICANT TO PERFORM AN INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [16 empty] | YES | [163 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | LEAK SURVEYOR DETECTED GAS ON LINE 200 NEAR THE VICINITY OF THE WHITE STREET REGULATOR STATION (3081) ON 04/12/2021. FURTHER INVESTIGATION FOUND THE SOURCE OF THE LEAK TO BE A CRACKED INSULATOR AT A FLANGE ON A UNDERGROUND VALVE. EXISTING COMPONENT WAS REPLACED ON 04/26/2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210044 | 37080 | 2021-05-03 15:14 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2021-04-03 11:13 | 2021 | EASTERN | YES | 43.4385 | -85.5138 | 1301882 | 2021-04-03 11:13 | 1301977 | NATURAL GAS |  | 7104 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-04-03 05:13 | 2021-04-03 06:20 | ONSHORE | MI | 49329 | HOWARD CITY | MONTCALM | NOT APPLICABLE |  | WINFIELD COMPRESSOR STATION | ANR LATERAL 249 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUT DOWN (ESD) | CLASS 1 LOCATION | NO |  | 155 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 12361 | 12361 | 1000 | 1020.150273224044 | 0 | 0 | 0 | 0 |  | 1.74 | 13361 | 8560.674153096236867109634551495016611296 | 13381.150273224044 | 0 | 0 | 0 | 0 | NO |  |  |  | 650 | 0 | 850 | 192.619(A)(1) |  | 1967-09-08 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR IDENTIFIED THE ALARM AND FOLLOWED THE PROCEDURES TO INITIATE AN INVESTIGATION. FIELD PERSONNEL WAS DISPATCHED TO THE SITE AND RESPONDED TO THE LOCATION OF THE ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | FIRE EYE | [18 empty] | YES | [159 empty] | YES | [6 empty] | ROBERTA PRIMERA | COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 2485617803 |  | ROBERTA PRIMERA | roberta_primera@tcenergy.com | 2485617803 | ROGER STREET | COMPLIANCE MANAGER WEST | 16154655123 | roger_street@tcenergy.com | A SUSPECTED FALSE TRIGGER OF THE WINFIELD ESD SYSTEM FROM A NEW FIRE EYE(S) ACTIVATED THE STATION'S ESD SYSTEM. THIS FALSE TRIGGER ASSUMPTION IS BECAUSE THERE WAS NOT FIRE FOUND ONSITE AFTER A THOROUGH INSPECTION OF THE AREAS THAT THE FIRE EYES COVER. SUPPORTING THE IDEA OF THE FALSE FIRE EYE OUTPUT IS THE FIRE EYES ARE NEW AND ARE NOW GETTING REPLACED BECAUSE THE MANUFACTURE STATED THEY ARE TO SENSITIVE FOR OUR APPLICATION. THE ESD SYSTEM'S ACTIVATION, RESULTED IN A RELEASE OF THE COMPRESSOR STATIONS YARD PIPING GAS TO ATMOSPHERE. DURING THE ESD AN EXTENDED RELEASE OCCURRED WHEN THE LINE BLOCK VALVE (249-1-16) FAILED TO SHUT. THE VALVE WAS CLOSED BY THE ON-CALL TECHNICIAN. TC ENERGY HAS REPLACED ALL FIRE EYES AT THE WINFIELD STATION WITH NEW DETECTORS, WHICH WERE CALIBRATED AND TESTED. AFTER REPLACING DETECTORS, AN ESD SYSTEM INSPECTION WAS COMPLETED ACCORDING TO PROCEDURES ON APRIL 14, 2021. THE TEST WAS INITIATED BY TRIGGERING THE FLAME DETECTORS AND THEN MONITORING ALL EMERGENCY SYSTEMS VALVES FOR OPERATIONS AND TIMING. DURING THE TEST, ALL SYSTEMS VALVE PROPERLY OPERATED AND FULLY CLOSED. AN INVESTIGATION IS ONGOING AS TO WHY VALVE 249-1-16 FAILED TO SHUT. 20210526 UPDATE: DURING THE RELEASE EVENT VALVE 249-1-16 DID NOT CLOSE WHICH PROLONGED THE RELEASE OF GAS. THE ACTUATOR FOR THE VALVE HAS TWO STATES (MANUAL AND AUTOMATIC) AND THE VALVE WAS IN MANUAL. THIS MEANT THAT THE STATION CONTROL LOGIC WAS NOT ABLE TO CYCLE THE VALVE DURING THE FALSE TRIP OF THE FIRE EYE. PRIOR TO THE EVENT THE STATION VALVE CONFIGURATION WAS CHANGED FROM INJECTION MODE TO WITHDRAWAL MODE. THIS PROCESS FOR CHANGING MODES OF OPERATION REQUIRES LOCAL PERSONNEL TO MANUALLY CONFIGURE SEVERAL YARD VALVES AND IS NOT PART OF THE STATION CONTROL LOGIC. STATION PERSONNEL UTILIZED A MODE DIAGRAM TO VERIFY ALL VALVES ARE SET IN THE PROPER POSITION. VALVE 249-1-16 WAS LEFT IN THE MANUAL STATE AFTER THE YARD VALVES WERE RE-POSITIONED FOR WITHDRAWAL MODE. SUBSEQUENTLY A PROCEDURAL CHECKLIST HAS BEEN CREATED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210045 | 35598 | 2021-05-07 16:14 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-04-17 22:56 | 2021 | CENTRAL | YES | 30.9828 | -94.1408 | 1302959 | 2021-04-18 02:04 | 1303037 | NATURAL GAS |  | 15480 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | SINGLE ENGINE UNIT SHUTDOWN RESULTED FROM A FAILED RELIEF VALVE. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-04-17 22:41 | 2021-04-18 01:20 | ONSHORE | TX | 75951 | Not Within a Municipality | JASPER | SURVEY STATION NO. | 32 | STATION NO. 32 | JASPER COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE ACTIVATION RELEASED GAS THROUGH VENT SYSTEM. | CLASS 1 LOCATION | NO |  | 236 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 37152 | 37152 | 0 | 0 | 150 | 153.0225409836066 | 0 | 0 |  | 2.4 | 37302 | 24444.6505415690866928571428571428571429 | 37305.0225409836066 | 0 | 0 | 0 | 0 | NO |  |  |  | 740 | 60000 | 1440 | 192.619(A)(1) |  | 2007-10-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE MECHANICAL MALFUNCTION IN THE FIELD. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | DEFECTIVE EQUIPMENT OR MATERIALS. | [161 empty] | STEPHEN R. DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-4199 |  | JOE SYDES | joe_sydes@kindermorgan.com | (409) 658-0848 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713 369-9443 | jaime_hernandez@kindermorgan.com | ON APRIL 18, 2021 AT APPROXIMATELY 1:10 AM LOCAL TIME, TGP GAS CONTROL NOTICED A PRESSURE DROP AT CS32 JASPER ON THE DISCHARGE PIPING AND NOTIFIED LOCAL OPERATIONS OF THE PRESSURE DROP. OPERATIONS PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE LOCATION. AT 1:20 AM LOCAL TIME ON APRIL 18, 2021, OPERATIONS PERSONNEL ARRIVED AT THE SITE AND CONFIRMED THAT THE RELIEF VALVE ON UNIT NO. 6-B COMPRESSOR WAS VENTING, AND THE UNIT WAS SHUT DOWN AND THE RELIEF VALVE ISOLATED. AN INTERNAL ERL CALL WAS COMPLETED WITH MANAGEMENT AT 1:50 AM LOCAL TIME TO CONFIRM REPORTABILITY AND THE NRC WAS NOTIFIED AT 2:04 AM LOCAL TIME OF THE EVENT (NRC REPORT NO. 1302959). A 48-HR. UPDATE WAS ALSO PROVIDED NOTING NO SIGNIFICANT CHANGES (NRC REPORT NO. 1303037). THE RESULTS OF TGP'S INVESTIGATION IDENTIFIED THE IMMEDIATE CAUSE OF THE EVENT TO BE DEFECTIVE EQUIPMENT OR MATERIALS. AFTER TESTING OF THE VALVE, TGP COULD NOT IDENTIFY WHY THE PILOT VALVE WOULD NOT RESET AND THE CAVITY ON TOP OF THE VALVE COULD NOT REACH A HIGH ENOUGH PRESSURE TO RE-SEAT THE MAIN VALVE PLUNGER. THEREFORE, THE VALVE WAS REPLACED WITH A NEW ANDERSON GREENWOOD PILOT RELIEF VALVE.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210046 | 36520 | 2021-05-11 16:33 | SUPPLEMENTAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-04-11 14:28 | 2021 | CENTRAL | YES | 28.3092 | -93.2653 | 1302453 | 2021-04-11 14:37 | 1302658 | NATURAL GAS |  | 10652 | 0 | 0.5 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-04-11 14:28 | 2021-05-29 14:15 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-04-11 16:42 | NO | [5 empty] | VALVE CLOSURE |  | 2021-04-11 14:28 | VALVE CLOSURE |  | 2021-04-11 16:37 | 0 | 2021-04-11 14:28 | 2021-04-11 14:40 | OFFSHORE | [6 empty] | STINGRAY PIPELINE | STINGRAY 30" LINE 3394 | [20 empty] | 185 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 551 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 0.568 | 60000 | X60 | DSAW |  | U.S. STEEL | OTHER | CONCRETE | NO | [26 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 25352 | 25352 | 494337 | 504298.025614754238828 | 0 | 0 | 0 | 0 |  | 2.38 | 519689 | 239111.5925815929159371727574750830564784 | 529650.025614754238828 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 1000 | 1200 | 192.619(A)(1) |  | 1975-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 132000 | YES | [7 empty] | YES |  |  |  |  | YES | LAUNCHER IS SUBSEA | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | ARENA OPERATOR OF PLATFORM WC 544 |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK AND TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES | [7 empty] | YES | BOTTOM OF PIPE | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GARRETT RAY | MANAGER - INTERSTATE PIPELINES | garrett.ray@energytransfer.com | 713-989-7225 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 2812295579 | todd.nardozzi@energytransfer.com | ON APRIL 11, 2021 AT 14:28, STINGRAY OPERATION MANAGER WAS NOTIFIED BY ARENA OF SUSPECTED BUBBLES LOCATED IN THE VICINITY OF THE 30INCH STINGRAY LINE 3394 IN GOM BLOCK WC-551. ARENA PLATFORM (WC-544) SHUT IN AND MONITORING PRESSURE ON APRIL 11, 2021 AT 1637. CURRENTLY COORDINATING WITH THE DIVE COMPANY ON THE DATE TO FIND AND CLAMP THE LEAK. THE PIPELINE IS STILL SHUTDOWN WITH BOTTOM PRESSURE. REPAIR WAS MADE ON 5/29/21 WITH 30INCH CLAMP.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210047 | 35298 | 2021-05-12 18:02 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-04-16 10:40 | 2021 | PACIFIC | YES | 38.1765 | -121.5681 | 1302885 | 2021-04-16 18:00 |  | NATURAL GAS |  | 500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | N/A |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | CUT AND CAP |  | OPERATIONAL CONTROL | CUT AND CAP |  | 0 | 2021-04-16 10:40 | 2021-04-16 12:15 | ONSHORE | CA | 95641 | ISLETON | SACRAMENTO | NOT APPLICABLE |  | L168 |  | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 | NO | 0.156 | 42000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | NONE |  | UNKNOWN | [26 empty] | 1979 | 1979 | CARBON STEEL |  | OTHER | [8 empty] | DIG-IN | CLASS 1 LOCATION | NO |  | 78 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 1500 | 1500 | 122000 | 124458.333333333368 | 0 | 0 | 0 | 0 |  | 3 | 123500 | 55890.4692691030240332225913621262458472 | 125958.333333333368 | 0 | 0 | 0 | 0 | NO |  |  |  | 603 | 600 | 795 | 192.619(A)(1) |  | 1989-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | NO |  |  | 100 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | UNKNOWN |  |  |  |  | NO | YES | COUNTY ROAD | [9 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | NO | [268 empty] | SAJJAD AZHAR |  | s1at@pge.com | [5 empty] | SUSIE RICHMOND |  | 9257860267 | gsr8@pge.com | ON APRIL 16, 2021 AT APPROXIMATE 10:40 HOUR PG&E WAS NOTIFIED OF A POTENTIAL DIG-IN IN ISLETON, CA INVOLVING A PIECE OF FARM EQUIPMENT CONTACTING A 4 INCH TRANSMISSION LINE RESULTING IN A RELEASE OF GAS. NO FATALITIES, INJURIES, OR IGNITION WAS REPORTED. PG&E PERSONNEL RESPONDED AND STOPPED GAS FLOW AROUND 12:15 HOURS. 1 CUSTOMER WAS IMPACTED; CNG SUPPORT WAS ARRANGED. FIRE DEPARTMENT PRESENCE WAS REPORTED ON SITE. THIS EVENT WAS DETERMINED TO BE A DOT REPORTABLE INCIDENT ~17:55 HOURS ONCE ESTIMATED PROPERTY DAMAGE WAS CONFIRMED TO BE AT LEAST $122,000.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210048 | 35721 | 2021-05-17 12:06 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-04-23 09:15 | 2021 | CENTRAL | YES | 30.657 | -93.4231 | 1303674 | 2021-04-28 09:48 | 1303808 | NATURAL GAS |  | 2 | 856 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-05-02 07:00 | 2021-05-02 18:00 |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | REDUCED PRESSURE BY 20% |  | OPERATIONAL CONTROL | REDUCED PRESSURE BY 20% |  | 0 | 2021-04-28 09:15 | 2021-04-28 07:00 | ONSHORE | LA | 70660 | Not Within a Municipality | BEAUREGARD | SURVEY STATION NO. | 763+93 | INDEX 201-6 | SINGER SCHOOL TAP SITE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1941 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 155 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 2217 | 2261.673155737705548 | 5 | 5 | 121706 | 124158.409153005499064 | 4500 | 4590.676229508198 | 0 | 0 |  | 2.59 | 128428 | 57800.2097780281932977774086378737541528 | 131015.758538251402612 | 0 | 0 | 0 | 0 | NO |  |  |  | 370 | 4600 | 505 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 54384 | NO |  | YES |  |  |  | YES | NO LAUNCHERS OR RECEIVERS | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [52 empty] | HIGH WINDS | [5 empty] | YES | YES | [305 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 4/23/2021, GULF SOUTH RESPONDED TO AN EMERGENCY ONE-CALL TICKET FROM ITS CUSTOMER, CENTERPOINT. CENTERPOINT THOUGHT THERE WAS A LEAK ON THEIR FACILITY AND IT WAS IN CLOSE PROXIMITY TO GULF SOUTH FACILITIES. WHEN GULF SOUTH PERSONNEL ARRIVED AT APPROXIMATELY 9:15 AM, IT WAS UNCLEAR WHETHER THE LEAK WAS ON CENTERPOINT'S OR GULF SOUTH'S FACILITY. THE INDICATION LED BOTH OPERATOR PERSONNEL TO BELIEVE IT WAS A PACKING LEAK. GULF SOUTH PLACED A ONE-CALL REQUEST AND IT WAS AGREED THAT THE SITE WOULD BE EXCAVATED ON 4/28/2021 WHEN THE ONE-CALL TICKET WAS CLEAR. ON 4/28/2021 AT APPROXIMATELY 7:00 AM, THE SITE WAS EXCAVATED AND IT WAS DISCOVERED THAT GULF SOUTH'S 2" TAP PIPE BETWEEN THE VALVE AND 10-INCH PIPELINE HAD SUSTAINED A CRACK IN THE THREADS. IT IS BELIEVED THAT THIS RESULTED FROM A TREE HAVING FALLEN ON CENTERPOINT'S ABOVE GROUND PIPING WHICH IS CONNECTED TO GULF SOUTH'S PIPELINE TAP VALVE WHICH IS UNDERGROUND. GULF SOUTH LOWERED THE PRESSURE ON ITS PIPELINE BY 20% AND MADE ARRANGEMENTS TO REPAIR. ON 5/1/2021 AT APPROXIMATELY 7:00 AM, THE VALVE WAS REMOVED FROM SERVICE AND A NEW VALVE AND PIPE WERE REPLACED. THE PIPELINE WAS RETURNED TO SERVICE ON 5/1/2021 AT APPROXIMATELY 6:00 PM. A SUPPLEMENTAL/FINAL REPORT WILL BE SUBMITTED ONCE ACTUAL COSTS CAN BE FINALIZED. 9/8/2021: UPDATE COST OF REPAIRS; CORRECTED DATE PIPELINE WAS TAKEN OUT OF SERVICE; AND ADDED DATE AND TIME PIPELINE WAS RETURNED TO SERVICE. THE DATE AND TIME PIPELINE WAS REMOVED FROM SERVICE WAS 5/2/2021 AT APPROXIMATELY 7:00 AM AND NOT 5/1/2021 AS PREVIOUSLY REPORTED. THE PIPELINE WAS RETURNED TO SERVICE THE SAME DAY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210049 | 35426 | 2021-05-20 07:52 | SUPPLEMENTAL FINAL | 32614 | WILLIAMS OLEFINS FEEDSTOCK PIPELINES, LLC | ONE WILLIAMS CENTER P.O. BOX 645 | TULSA | OK | 74172 | 2021-04-30 16:30 | 2021 | CENTRAL | YES | 29.724 | -95.0732 | 1303925 | 2021-04-30 17:00 | 1304022 | OTHER GAS | ANHYDROUS HYDROGEN CHLORIDE GAS | 0.021 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-04-29 08:04 | 2021-04-29 08:04 | ONSHORE | TX | 77523 | LAPORTE | HARRIS | MILEPOST | 14.5 | DPKC - OXY VINYL METER STATION | 1893 HCL PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | GROVE |  |  |  | 2021 | 2021 | CARBON STEEL |  | OTHER | [8 empty] | FUGITIVE EMISSION DUE TO A POSSIBLE FAULTY O'RING | CLASS 1 LOCATION | YES | METHOD1 |  | NOT FLAMMABLE | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 204030.0546448088 | 1 | 1.020150273224044 | 0 | 0 |  | 1 | 200001 | 90010.695952868908197 | 204031.074795082024044 | 0 | 0 | 0 | 0 | NO |  |  |  | 108 | 0 | 673 | 192.619(A)(1) |  | 2011-08-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS NOT FLOWING AT THE TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | O-RING | [17 empty] | YES | APPARENT FAULTY O'RING | [161 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-215-2846 |  | JOHN DIXON | john.dixon@williams.com | 281-457-4056 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | 4/29/21 THE PAINTING CREW, HIRED BY WILLIAMS TO COAT NEW VALVES THAT WERE INSTALLED AT THE OXY METER STATION, NOTICED SOME CONDENSATION AROUND THE TOP WORKS OF THE NEW VALVE THEY WERE PAINTING. WILLIAMS OPS TECHS WERE ON SITE AND CHECKED THE AREA WITH A PH STIP - READINGS WERE INDICATIVE TO THE PRESENCE OF HCL. MANAGEMENT AND ENGINEERING WERE NOTIFIED, AND A FIRST REPAIR ATTEMPT WAS MADE (INJECTING PACKING INTO THE VALVE). AFTER THE PACKING WAS INJECTED INTO THE VALVE, THE TEAM BEGAN TO SEE SMALL/INTERMITTENT "PUFFS" OF HCL. 4/30/21 WILLIAMS'S CUSTOMER PULLED THE LINE PACK OF HCL DOWN TO ABOUT 3 PSI. AFTER THE LINE WENT FROM ~100 PSI TO ~3 PSI, THE "PUFFS OF HCL" WERE NO LONGER VISIBLE. 5/1/21 N2 LINE PURGING BEGAN 5/7/21 VALVE WAS REPLACED WITH A PRE-FABRICATED SPOOL PIECE
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210050 | 35445 | 2021-05-25 18:16 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2021-04-22 13:12 | 2021 | EASTERN | YES | 42.6078 | -83.5692 | 1303280 | 2021-04-22 17:16 | 1303442 | NATURAL GAS |  | 16073 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE HORSE POWER WAS REDUCE BUT THE PIPELINE WAS STILL FLOWING |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-04-22 13:30 | NO | [5 empty] | OPERATIONAL CONTROL | HORSEPOWER WAS SHUT DOWN |  | OPERATIONAL CONTROL | GAS CONSUMPTION ON THE SYSTEM LOWERED THE PRESSURE |  | 0 | 2021-04-22 13:12 | 2021-04-22 13:30 | ONSHORE | MI | 48381 | MILFORD TOWNSHIP | OAKLAND | MILEPOST | 117.4 MP | C-LINE | 8000 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | OPP FOR A SEGMENT OF THE C LINE, PROTECTING AT A LOWER PRESSURE | CLASS 2 LOCATION | NO |  | 601 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 36164 | 36164 | 0 | 0 | 300 | 306.0450819672132 | 0 | 0 |  | 2.25 | 36464 | 23863.8858007461468076411960132890365449 | 36470.0450819672132 | 0 | 0 | 0 | 0 | NO |  |  |  | 808 | 676 | 811 | 192.619(A)(1) |  | 1980-05-01 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | NO |  |  |  | 11000 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | MILFORD COMPRESSOR STATION K-LINE DISCHARGE PRESSURE CREPT UPWARD DUE TO WARMER WEATHER AND REDUCED DOWNSTREAM USAGE CAUSING THE C LINE RELIEF VALVE TO TRIP AT THE LOWER SET POINT DETERMINED IN E4 ABOVE. |  |  |  | YES | MILFORD COMPRESSOR STATION K-LINE DISCHARGE PRESSURE CREPT UPWARD DUE TO WARMER WEATHER AND REDUCED DOWNSTREAM USAGE CAUSING THE C LINE RELIEF VALVE TO TRIP AT THE LOWER SET POINT DETERMINED IN E4 ABOVE. | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | NO | [150 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  | FRENAE F SMITH | frenae.smith@dteenergy.com | 13134601681 | FRENAE F SMITH | MANGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | MILFORD COMPRESSOR STATION WAS DISCHARGING INTO THE K-LINE WHICH FEEDS THE C LINE AT MILFORD JUNCTION APPROXIMATELY 5 MILES AWAY. AS THE WEATHER WARMED UP, THERE WERE ONLY TWO OF THE THREE PIPELINES AVAILABLE (B & C LINES, A-LINE WAS OUT OF SERVICE), SYSTEM PRESSURES STARTED TO BACK UP DUE TO LOWER DEMAND AND EXCESS GAS. ONCE THE DISCHARGE PRESSURE STARTED TO RISE THE UNITS SWITCHED FROM DISCHARGE PRESSURE CONTROL TO SUCTION PRESSURE CONTROL AND THIS WAS ANOTHER FACTOR THAT LED TO THE HIGHER DISCHARGE OF 827 PSIG. HOWEVER, THIS WAS WELL BELOW THE MAOP OF THE K-LINE (858 PSIG) BUT PUSHED CLOSE TO THE NEW 811 PSIG ON THE C-LINE TRIPPING THE RELIEF VALVE WHICH WAS SET AT 808 PSIG.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210051 | 35617 | 2021-06-01 15:20 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2021-04-30 19:00 | 2021 | CENTRAL | YES | 32.3219 | -98.3264 | 1304200 | 2021-05-04 10:24 | 1304392 | NATURAL GAS |  | 2425 | 44 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | LEAK WAS MONITORED AND A STOPPLE & BYPASS WAS UTILIZED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-04-30 19:30 | 2021-04-30 19:30 | ONSHORE | TX | 76401 | Not Within a Municipality | ERATH | NOT APPLICABLE |  | NORTH TEXAS GAS SYSTEM | 225 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 45 | NO | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 36 | NO | 0.438 | 65000 | API-5L-X-65 | DSAW |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 805 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 112 | 114.256830601092928 | 6184 | 6184 | 1300000 | 1326195.3551912572 | 10000 | 10201.50273224044 | 0 | 0 |  | 2.55 | 1316296 | 593675.1243668649149742990033222591362126 | 1342695.114754098732928 | 0 | 0 | 0 | 0 | NO |  |  |  | 750 | 800000 | 1051 | 192.619(A)(1) |  | 1970-09-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [6 empty] | YES | [14 empty] | YES | [8 empty] | 1402 | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GORDON WILLIAMS | ENGINEER - PIPELINE COMPLIANCE | gswilliams@eprod.com | 713-381-6211 |  | GORDON WILLIAMS | gswilliams@eprod.com | 713-381-6211 | GORDON WILLIAMS | ENGINEER - PIPELINE COMPLIANCE | 713-381-6211 | gswilliams@eprod.com | ON APRIL 30, 2021, AT APPROXIMATELY 7:00 PM, A THIRD PARTY REPORTED TO ENTERPRISE THERE WAS BUBBLING AT A METER SITE. AT 7:30 PM, AN ENTERPRISE TECHNICIAN ARRIVED ON SITE AND CONFIRMED IT WAS NATURAL GAS BUBBLING FROM THE GROUND NEAR SEVERAL PIPELINES, INCLUDING ENTERPRISE LINE 225. ON MAY 1, ENTERPRISE EXPOSED THE LEAK AREA AND IDENTIFIED A MINOR LEAK FROM A TEE ON LINE 225. THE LEAK SITE WAS MONITORED WHILE ENTERPRISE DEVELOPED A PLAN TO REPAIR THE LEAK. ON MAY 4, AT 9:55 AM, ENTERPRISE DETERMINED THAT THE CHOSEN REPAIR METHOD WOULD EXCEED THE $122,000 REPORTING THRESHOLD AND NOTIFIED THE NRC AND TEXAS RRC. THE RRC WAS NOTIFIED AT 10:30 AM AND ASSIGNED INCIDENT #2422. A STOPPLE AND BYPASS WAS INSTALLED AND THE TEE WAS REMOVED AND REPLACED. LAB ANALYSIS DETERMINED THE LEAK WAS THE RESULT OF A CRACK THAT INITIATED AT THE OD TOE OF THE FILLET WELD OF THE 10-INCH TAP TO THE 36-INCH PIPE. THE CRACK APPEARED TO BE STRESS INITIATED, LIKELY THE RESULT OF A LOADING EVENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210052 | 35360 | 2021-06-03 17:13 | ORIGINAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2021-05-05 22:08 | 2021 | CENTRAL | YES | 29.8968 | -92.065 | 1304384 | 2021-05-06 02:31 | 1304523, 1304524 | NATURAL GAS |  | 2650 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-05-05 22:25 | 2021-05-15 17:15 |  | YES | OPERATOR | 2021-05-06 00:58 | NO | [5 empty] | VALVE CLOSURE |  | 2021-05-05 22:25 | VALVE CLOSURE |  | 2021-05-05 22:25 | 0 | 2021-05-05 22:08 | 2021-05-05 22:25 | ONSHORE | LA | 70533 | ERATH | VERMILION | SURVEY STATION NO. | 5+79 | SEA ROBIN 30" INLET | 307-0716 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | PRESSURE SAFETY VALVE RELIEVED | [5 empty] | CLASS 1 LOCATION | YES | METHOD2 | 671 |  | NO | NO | [5 empty] | 246000 | 250956.967213114824 | 0 | 0 | 7765 | 7765 | 1000 | 1020.150273224044 | 0 | 0 | 0 | 0 |  | 2.93 | 254765 | 116257.6287715811374053156146179401993355 | 259742.117486338868 | 0 | 0 | 0 | 0 | NO |  |  |  | 693 | 84000 | 1050 | 192.619(A)(1) |  | 1972-08-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | REMOTELY CONTROLLED | 579 | NO | YES |  |  |  |  | YES | THIS IS STATION PIPING | YES |  |  |  |  | YES | THIS IS STATION PIPING | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [22 empty] | YES | [168 empty] | NATHAN L. GRAY JR. | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985-493-4629 |  | NATHAN L. GRAY JR. | ngray@eprod.com | 985-493-4629 | NHAN TRUONG | COMPLIANCE MANAGER | 713-381-2493 | nvtruong@eprod.com | ON MAY 5, 2021 AT 22:08, ENTERPRISE OPERATIONS SUPERVISOR RECEIVED A PHONE CALL REPORTING A RELIEF VALVE DISCHARGE ON THE 30 INCH INLET PIPELINE TO THE SEA ROBIN GAS PLANT. THE SEA ROBIN OPERATIONS PERSONNEL VERIFIED THE PIPELINE PRESSURE WAS BELOW MAXIMUM ALLOWABLE OPERATING PRESSURE (MAOP) AND ISOLATED THE RELIEF VALVE TO STOP THE DISCHARGE. ON MAY 6, 2021 AT 01:38, ENTERPRISE DETERMINED THE INCIDENT TO EXCEED ESTIMATED REPORTABLE VOLUME REQUIREMENTS AND REPORTED TO THE NRC AT 02:31. THE VOLUME ESTIMATES WERE REDUCED BASED ON ADDITIONAL INFORMATION AFTER THE 48-HOUR NOTIFICATION. AFTER FURTHER INVESTIGATION OF THE PILOT VALVE, IT WAS DETERMINED THAT FLUID CONTAMINATED THE PILOT VALVE AND ALLOWED THE RELIEF VALVE TO ACTIVATE BEFORE THE MAOP SETTING. A NEW RELIEF VALVE AND ANDERSON GREENWOOD PILOT WAS INSTALLED TESTED AND PLACED INTO SERVICE. THE LA DNR WAS NOTIFIED ON 5/6/2021 AT 00:58. THE 48-HOUR UPDATE TO THE NRC TOOK PLACE ON 5/7/2021 AT 13:30 #1304523. THE NRC INCORRECTLY ENTERED RELEASED MATERIAL ON REPORT #1304523 AND ISSUED A CORRECTED REPORT #1304524.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210053 | 35420 | 2021-06-18 15:09 | SUPPLEMENTAL FINAL | 32467 | ETC TIGER PIPELINE, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-05-20 19:00 | 2021 | CENTRAL | YES | 32.3242 | -92.4605 | 1305609 | 2021-05-20 19:32 | 1305672 | NATURAL GAS |  | 22773 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | YES | OPERATOR | 2021-05-20 15:30 | NO | [11 empty] | 0 | 2021-05-20 14:20 | 2021-05-20 14:20 | ONSHORE | LA | 71226 | CHATHAM | JACKSON | NOT APPLICABLE |  | CHATHAM COMPRESSOR STATION | LAMT134 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2010 | 2010 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | ESD | OTHER | [8 empty] | LOSS OF POWER TO THE PLC AND BROKEN DRIVE PIN ON FUEL GAS ACTUATOR CAUSED VALVES TO TRAVEL TO THEIR FAIL SAFE POSITIONS. THE TWO 42" ESD (HEADER) VALVES REMAINED PARTIALLY OPEN ALLOWING LINE PRESSURE TO VENT THROUGH TWO 8IN VALVES FOR APPROXIMATELY 10 MINUTES UNTIL EMPLOYEES COULD MANUALLY CLOSE VALVES. | CLASS 1 LOCATION | NO |  | 1100 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 61487 | 61487 | 435 | 443.76536885245914 | 100 | 102.0150273224044 | 0 | 0 |  | 2.7 | 62022 | 40585.2375406772508435049833887043189369 | 62032.78039617486354 | 0 | 0 | 0 | 0 | NO |  |  |  | 1150 | 50.26 | 1440 | 192.619(A)(2) |  | 2010-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATIONS NOTIFIED GAS CONTROL OF EMPLOYEES WORKING ON SITE PERFORMING CHECKS ON PLC. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | BROKEN FUEL GAS ACTUATOR DRIVE PIN CAUSED THE ESD HEADER TO HANG OPEN | [161 empty] | KATHRYN HARRYMAN |  | kathryn.harryman@energytransfer.com | 7139897085 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | 14:20 CST, MAY 20TH WHILE WORKING TO UPGRADE COMMUNICATIONS (SWITCHES) FOR BOTH SCADA AND LOCAL COMMUNICATIONS, THE ESD WAS ACTIVATED. DURING THE ESD TWO 42IN ESD (HEADER) VALVES REMAINED OPEN FOR 10 MINUTES ALLOWING LINE PRESSURE TO VENT THROUGH TWO 8IN VALVES. 14:30 CST, MAY 20TH ESD BLOW-OFF VALVES WERE MANUALLY CLOSED AND STATION WAS BY-PASSED. 15:30 CST, MAY 20TH LOCAL LAW ENFORCEMENT WAS NOTIFIED REPORT # 21-02113. 19:32 CST, MAY 20TH NRC NOTIFICATION WAS MADE NRC #1305609 ROUGH CALCULATION OF GAS VOLUME LOSS WAS COMPLETED BY REGULATORY. THIS NOTIFICATION WAS MADE ONCE THE GAS VOLUME WAS CALCULATED. MAY 21ST, DURING THE INVESTIGATION, IT WAS DISCOVERED THAT THE ACTUATOR ON THE FUEL GAS VALVE HAD MALFUNCTIONED INTERNALLY LEAVING THE VALVE IN THE CLOSED POSITION CAUSING THE PLC TO LOSE POWER THERE BY FORCING VALVES TO RETURN TO THEIR FAIL SAFE POSITION. SINCE THE VALVE CLOSED THERE WAS A REDUCTION IN POWER GAS TO ASSIST IN CLOSING THE ESD VALVES ON THE SUCTION AND DISCHARGE HEADERS. TO PREVENT THIS ISSUE FROM HAPPENING AGAIN, PERSONNEL HAVE SINCE TESTED AND ARE REPLACING ALL SOFT PARTS ON ALL OTHER ACTUATORS ON THE FUEL GAS VALVE ON FUEL SKIDS AT ALL COMPRESSOR STATIONS ON TIGER PIPELINE. 14:57 CST, MAY 21ST PHMSA 48 HOUR NRC NOTIFICATION WAS MADE NRC # 1305672, UPDATED THE GAS VOLUME, PHYSICAL ADDRESS, AND COORDINATES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210054 | 36054 | 2021-06-24 17:17 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-05-25 14:00 | 2021 | EASTERN | NO | 39.0097 | -76.9761 | 1305962 | 2021-05-25 14:35 | 1306192 | NATURAL GAS |  | 9184 | 5880 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-05-25 16:07 | 2021-05-28 00:15 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-05-25 16:07 | NO | [5 empty] | VALVE CLOSURE |  | 2021-05-25 14:13 | VALVE CLOSURE |  | 2021-05-25 14:02 | 20 | 2021-05-25 12:06 | 2021-05-25 12:26 | ONSHORE | MD | 20783 | ADELPHI | PRINCE GEORGES | NOT APPLICABLE |  | STRIP 12 | 22716938 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 62 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.312 | 42000 | API 5LX-42 | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN SHEET & TUBE CO. | COAL TAR |  | NO | [26 empty] | 1950 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 3 LOCATION | YES | METHOD2 | 278 |  | NO | NO | [5 empty] | 0 | 0 | 15433 | 15743.979166666671052 | 24105 | 24105 | 75290 | 76807.11407103827276 | 10112 | 10315.759562841532928 | 0 | 0 |  | 2.6247 | 124940 | 61197.3193819440943288870431893687707641 | 126971.85280054647674 | 0 | 0 | 1 | 0 | NO |  |  |  | 176 | 30.72 | 300 | 192.619(C) |  | 1965-08-12 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 4990 | YES | [7 empty] | YES |  |  |  |  | YES | SEE PART H. | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 2" X 3" HOLE IN THE 22" WRAPPED STEEL PIPELINE WAS SMALL ENOUGH THAT IT DID NOT HAVE A SIGNIFICANT IMPACT ON PRESSURE OR FLOW OF THE PIPELINE, AND DID NOT CAUSE ANY ALARMS IN GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | AUGER | ELECTRIC | YES | 21361671 |  | CONTRACT LOCATOR | YES | NO | YES | 60 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7036397825 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | (703)639-7825 | SHANNON B. MALONEY | MANAGER PIPELINE SAFETY COMPLIANCE QUALITY | (703)750-5558 | smaloney@washgas.com | WASHINGTON GAS WAS NOTIFIED BY ULCS (UTILITY LINES CONSTRUCTION SERVICES) ON 5/25/21 1206 HRS OF A DAMAGED FACILITY NEAR 9412 ADELPHI RD. ADELPHI, MD. WASHINGTON GAS ARRIVED AT 1226 HRS AND IDENTIFIED THE DAMAGED FACILITIES TO BE 22" WRAPPED TRANSMISSION. ULCS WAS EXCAVATING WITH AN AUGER AND DAMAGED WG FACILITIES. WASHINGTON GAS IDENTIFIED AND OPERATED 2 CRITICAL VALVES TO DISCONTINUE THE FLOW OF GAS. DUE TO THE LOCATION OF THE EXISTING POWER POLE, THE LOCATION OF THE NEWLY INSTALLED POWER POLE, BOTH HAVING TO BE RELOCATED, WHICH TOOK ADDITIONAL TIME. WASHINGTON GAS WAS DELAYED IN MAKING IMMEDIATE REPAIRS. MINIMUM IMPACT TO TRAFFIC, IT WAS ISOLATED TO ONE LANE OF THE FOUR LANE ROAD WHILE REPAIRS WERE MADE. NO CUSTOMERS WERE AFFECTED AND REPAIRS ARE COMPLETE. PART D QUESTION 7 WILL BE SUBMITTED IN A SUPPLEMENTAL, ONCE DATA IS RECEIVED. PART E QUESTION 8 THIS PIPE LINE WAS RECENTLY CONFIGURED TO ACCOMMODATE AN INTERNAL INSPECTION TOOL. A PRELIMINARY EXPLORATORY RUN IS SCHEDULED FOR MID JULY 2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210055 | 35817 | 2021-07-01 11:07 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2021-06-24 16:15 | 2021 | CENTRAL | YES | 28.5747 | -91.3272 | 1308929 | 2021-06-26 20:11 | 1309167 | NATURAL GAS |  | 25 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | TUBING LEAK ISOLATED BY 1/2" VALVE CLOSURE | [6 empty] | NO | [11 empty] | 0 | 2021-06-26 18:15 | 2021-06-25 08:00 | OFFSHORE | [28 empty] | 100 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SHIP SHOAL | 199 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PLATFORM, INCLUDING PLATFORM-MOUNTED EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 100 | 100 | 5000 | 5100.75136612022 | 75000 | 76511.2704918033 | 0 | 0 | NONE | 4 | 80100 | 36069.7129785959593355481727574750830565 | 81712.02185792352 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 80 | 1250 | 192.619(A)(1) |  | 1972-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SUBSEA VALVE OPERATOR TUBING CRACK, ASSUMED TO BE A RESULT OF OUTSIDE FORCES | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KURT CHERAMIE | SENIOR VICE PRESIDENT | kurt.cheramie@kineticallc.com | 9852236165 |  | KURT CHERAMIE | kurt.cheramie@kineticallc.com | 9852236165 | KURT CHERAMIE | SENIOR VICE PRESIDENT | 9852236165 | kurt.cheramie@kineticallc.com | NOTIFIED BY USCG ON 6/25/2021. LEAK CONFIRMED BY HELICOPTER OVERFLIGHT ON 6/26/2021. DIVE VESSEL DISPATCHED ON 6/26/2021. DIVERS FOUND A CRACKED 1/2" TUBING ON A 12" SUBSEA VALVE OPERATOR. CLOSED ISOLATION VALVE TO STOP LEAK. ASSUMED TO BE CAUSED BY OUTSIDE FORCES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210056 | 35610 | 2021-07-13 15:38 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2021-06-21 14:00 | 2021 | CENTRAL | YES | 39.5377 | -95.1233 | 1308375 | 2021-06-21 15:13 | 1308602 | NATURAL GAS |  | 13500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-06-21 17:52 | 2021-06-21 20:02 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-06-21 17:52 | VALVE CLOSURE |  | 2021-06-21 17:52 | 0 | 2021-06-21 14:00 | 2021-06-21 14:00 | ONSHORE | KS | 66002 | NOT WITHIN A MUNICIPALITY | ATCHISON | SURVEY STATION NO. | 120/78210 | ATCHISON 10" LINE | LINE EG | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 175 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 38205 | 38205 | 5550 | 5661.8340163934442 | 0 | 0 | 0 | 0 |  | 2.83 | 43755 | 27565.8491078236494961794019933554817276 | 43866.8340163934442 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 7259 | 395 | 192.619(C) |  | 1969-08-27 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 20592 | NO | YES | [6 empty] | YES |  | YES |  |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ACTION OF THE OPERATOR CONTRIBUTED TO THE CAUSE OF THE INCIDENT. THE LEAK WAS SLOW ENOUGH THAT THERE WAS NO PRESSURE LOSS TO TRIGGER ALARMS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [6 empty] | YES | [175 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 6/21/2021 SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) CONDUCTED A LEAK PATROL ON LINE EG AND DISCOVERED A LEAK ON AN ONE INCH RISER GOING TO A DOMESTIC SERVICE AT 2:00 PM LOCAL TIME. THE LEAK WAS MONITORED AND OPERATIONS WAS NOTIFIED IMMEDIATELY. THE LEAK WAS NOT SEVERE ENOUGH TO TRIGGER ANY PRESSURE LOSS ALARMS. RECORDS WERE REVIEWED AND IT WAS DETERMINED AT 2:20 PM THAT 13,500 MCF OF GAS LOSS COULD BE ATTRIBUTED TO THIS RISER LEAK OVER THE COURSE OF 28 DAYS. THE NRC WAS NOTIFIED ON 6/21/2021 AT 3:13 PM LOCAL TIME. THE LEAK ON THE RISER WAS ISOLATED ON 6/21/2021 BY CLOSING THE ISOLATION VALVE TO THAT SERVICE AT 5:52 PM. IT WAS DISCOVERED THAT A THREADED FITTING FAILED ON THE DOWNSTREAM SIDE OF THE ISOLATION VALVE. REPAIRS WERE MADE AND COMPLETE ON 6/21/2021 AT 8:02 PM.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210057 | 36521 | 2021-07-14 10:25 | SUPPLEMENTAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-06-01 11:44 | 2021 | CENTRAL | YES | 28.3059 | -93.2693 | 1306564 | 2021-06-01 13:05 | 1307097 | NATURAL GAS |  | 703.5 | 0 | 87 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-06-01 11:55 | 2021-06-06 10:30 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-06-01 12:10 | VALVE CLOSURE |  | 2021-04-11 16:37 | 0 | 2021-06-01 11:44 | 2021-06-04 06:15 | OFFSHORE | [6 empty] | STINGRAY PIPELINE | STINGRAY 30" LINE 3394 | [20 empty] | 185 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 551 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 0.568 | 60000 | X60 | DSAW |  | U.S. STEEL | OTHER | CONCRETE | NO | [26 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 2005 | 2005 | 494337 | 504298.025614754238828 | 0 | 0 | 0 | 0 |  | 2.85 | 496342 | 223792.5477310945770667408637873754152824 | 506303.025614754238828 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 1000 | 1200 | 192.619(A)(1) |  | 1975-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 132000 | YES | [7 empty] | YES |  |  |  |  | YES | LAUNCHER IS SUBSEA | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK AND TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES | [7 empty] | YES | TOP OF PIPE | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [18 empty] | YES | [44 empty] | GARRETT RAY | MANAGER - INTERSTATE PIPELINES | garrett.ray@energytransfer.com | 7139897225 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 2812295579 | todd.nardozzi@energytransfer.com | ON JUNE 1, 2021 AT 11:44, STINGRAY OPERATION MANAGER WAS NOTIFIED BY COMPANY AIR PATROL OF A SHEEN IN THE VICINITY OF THE 30INCH STINGRAY LINE 3394 IN THE GOM WC-551 BLOCK. ARENA PLATFORM (WC-544) WAS NOTIFIED TO SHUT IN ON JUNE 1, 2021 @ 11:55. ON JUNE 1, 2021 AT 13:05 A CALL WAS PLACED TO THE NRC (NRC# 1306564). CREWS ARRIVED ON SITE ON 6/4 TO REPAIR THE LINE VIA A 30 INCH CLAMP. THE LINE WAS RESTARTED ON 6/6/21. A PREVIOUS LEAK ON THIS LINE APPROXIMATELY 200 FT. AWAY WAS REPAIRED ON 5/29/21 VIA 30INCH CLAMP.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210058 | 36522 | 2021-07-14 11:00 | SUPPLEMENTAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-06-14 08:24 | 2021 | CENTRAL | NO | 28.3061 | -93.2692 | 1307727 | 2021-06-14 09:26 | 1308003 | NATURAL GAS |  | 20000 | 0 | 11 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | YES |  | 2021-06-14 08:24 | 2021-08-16 16:42 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-06-14 08:24 | VALVE CLOSURE |  | 2021-04-11 16:37 | 0 | 2021-06-14 08:24 | 2021-07-08 02:30 | OFFSHORE | [6 empty] | STINGRAY PIPELINE | STINGRAY 30IN LINE 3394 | [20 empty] | 185 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 551 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 0.568 | 60000 | API 5L X-60 | DSAW |  | US STEEL | OTHER | CONCRETE | NO | [26 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 57000 | 57000 | 828304 | 844994.551912568541376 | 0 | 0 | 0 | 0 |  | 2.85 | 885304 | 410179.5658324712291504584717607973421927 | 901994.551912568541376 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 1000 | 1200 | 192.619(A)(1) |  | 1975-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 132000 | YES | [7 empty] | YES |  |  |  |  | YES | LAUNCHER IS SUBSEA | OFFSHORE GATHERING | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK AND TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES | [7 empty] | YES | BOTTOM OF PIPE | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | YES | 1975 |  | NO | [13 empty] | NO | [63 empty] | NICKLAS PAVLOVSKY | DOT COMPLIANCE SPECIALIST | nicklas.pavlovsky@energytransfer.com | 713-989-4527 |  |  |  |  | TODD NARDOZZI | DIRECTOR REGULATORY COMPLIANCE | 7139897126 | todd.nardozzi@energytransfer.com | ON JUNE 14, 2021 AT 8:24AM, STINGRAY OPERATION MANAGER WAS NOTIFIED BY COMPANY AIR PATROL OF A SHEEN IN THE VICINITY OF THE 30INCH STINGRAY LINE 3394 IN THE GOM WC-551 BLOCK. THIS PART OF THE LINE WAS REPAIRED ON 5/29 AND AGAIN ON 6/4. ARENA PLATFORM (WC-544) WAS NOTIFIED TO SHUT IN ON JUNE 14, 2021 @ 08:24. ON JUNE 14, 2021 A CALL WAS PLACED TO THE NRC (NRC# 1307727.) DUE TO SEA CONDITIONS AND WEATHER, CREWS ARRIVED ON SITE ON 7/8 TO DEPRESSURIZE AND REPAIR THE LINE VIA A 30-INCH CLAMP. THE CLAMP WAS INSTALLED ON JULY 12, 2021. THE LINE WAS RESTARTED TO FULL PRESSURE ON 8/16/21 AT 16:42..
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210059 | 35635 | 2021-07-15 18:07 | SUPPLEMENTAL FINAL | 31335 | MARITIMES & NORTHEAST PIPELINE, L.L.C. (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2021-06-15 11:51 | 2021 | EASTERN | YES | 43.1413 | -70.7904 | 1308024 | 2021-06-16 19:21 | 1308099, 1308117 | NATURAL GAS |  | 19498.91 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STATION WAS PRESSURIZED, UNITS WERE NOT RUNNING. |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-06-15 12:04 | NO | [11 empty] | 300 | 2021-06-15 11:51 | 2021-06-15 11:51 | ONSHORE | ME | 03903 | Not Within a Municipality | YORK COUNTY | MILEPOST | 51.445 | ELIOT COMPRESSOR STATION | ELIO | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2008 | 2008 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 786 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 63371 | 63371 | 200 | 204.0300546448088 | 1400 | 1428.2103825136616 | 0 | 0 |  | 3.25 | 64971 | 42300.7215020968361302325581395348837209 | 65003.2404371584704 | 0 | 0 | 0 | 2 | NO |  |  |  | 1114 | 200000 | 1440 | 192.619(A)(2) |  | 2008-03-31 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS DETERMINED THAT THE ACTIONS OF THE CONTROLLER COULD NOT HAVE CONTRIBUTED TO THE INCIDENT. THE INCIDENT WAS TRIGGERED BY A TUBING RELEASED FROM ITS TERMINATION POINT WHICH RESULTED IN THE LOSS OF POWER GAS AND SUBSEQUENTLY CAUSED THE ESD OF THE STATION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 16128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 17136275008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 11:51 AM ET ON JUNE 15, 2021 MNE'S ELIOT COMPRESSOR STATION ESD SYSTEM WAS INADVERTENTLY ACTIVATED. THE APPARENT CAUSE OF THE ESD WAS IMPROPER INSTALLATION OF TUBING WHICH DISENGAGED FROM ITS TERMINATION POINT. THE TUBING WAS UNDER PIPELINE PRESSURE AT THE TIME AND RESULTED IN A DROP IN SUPPLY POWER GAS PRESSURE WHICH TRIGGERED THE ESD. THE RELEASE WAS DUE TO A SINGLE STATION ESD VALVE MOVING OUT OF SEQUENCE WITH THE OTHER FOUR (4) ESD SYSTEM VALVES. THE OUT OF SEQUENCE ESD VALVE WAS INADVERTENTLY LEFT CONNECTED TO THE PREVIOUS POWER GAS SYSTEM, WHICH ALLOWED IT TO MOVE WHILE THE OTHER ESD VALVES DID NOT. THE REMAINING FOUR (4) ESD VALVES THAT DID NOT MOVE WERE CORRECTLY CONNECTED TO THE NEW POWER GAS SYSTEM INSTALLED IN 2020. THE NEW ESD SYSTEM HAS BEEN TESTED TWICE SINCE INSTALLATION, AND THE ISSUE WAS NOT MADE EVIDENT IN THE TESTS. CORRECTIVE ACTION HAS BEEN TAKEN, AND THE SYSTEM WILL BE RETESTED BEFORE BEING PUT BACK INTO SERVICE. VERIFICATION OF TUBING CONNECTIONS AND POWER GAS SYSTEM WILL BE CONDUCTED BEFORE RETURNING TO SERVICE AS WELL. DUE TO THE INCORRECT POWER GAS SUPPLY, THE ESD BLOW OFF VALVE FAILED TO THE OPEN POSITION WHILE THE MAINLINE TAP VALVES REMAINED IN THE OPEN POSITION. AS A RESULT, THE STATION WAS NOT ISOLATED FROM THE MAINLINE WHICH RESULTED IN THE STATION BLOWDOWN VENTING GAS FOR APPROXIMATELY 8 MINUTES. MNE'S FIELD PERSONNEL SUBSEQUENTLY CLOSED THE MAINLINE TAP VALVES AFTER RECOGNIZING THAT THE MAINLINE TAP VALVES REMAINED IN THE OPEN POSITION. A NEARBY SCHOOL NOTIFIED FIRST RESPONDERS AND WAS SUBSEQUENTLY EVACUATED AS A PRECAUTION. AN ADDITIONAL NEARBY SCHOOL RELEASED THEIR FACULTY. AT THE TIME OF THE ESD, THE PRELIMINARY GAS LOSS WAS INITIALLY ESTIMATED TO BE LESS THAN THE DOT REPORTING THRESHOLD, SINCE A NORMAL ESD AT THIS LOCATION IS LESS THAN THE REPORTING THRESHOLD. SHORTLY BEFORE 6 PM EST ON JUNE 16, 2021 MNE CONFIRMED THAT THE GAS LOSS WOULD EXCEED THE DOT REPORTING THRESHOLD AND SUBSEQUENTLY NOTIFIED THE NRC AT APPROXIMATELY 7:21 PM EST ON JUNE 16, 2021. THE DELAY WAS DUE TO RECONFIRMATION THAT THE INCIDENT MET THE DOT REPORTING THRESHOLD. 08/12/2021 SUPPLEMENTAL REPORT CHANGES - UPDATED PART A4 TO MATCH PART A13 - ADDED ESTIMATED COST FOR PART D7C - REVISED PART G7 TO REFLECT INCORRECT OPERATION - UPDATED PART H TO INDICATE GAS LOSS WAS UNDERESTIMATED
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210060 | 35639 | 2021-07-19 13:58 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2021-06-22 10:27 | 2021 | CENTRAL | YES | 28.4312 | -91.0844 | 1308449 | 2021-06-23 11:30 | 1308680 | NATURAL GAS |  | 2630 | 11880 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-06-22 13:10 | 2021-06-28 06:50 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-06-22 13:10 | VALVE CLOSURE |  | 2021-06-23 06:30 | 0 | 2021-06-23 16:30 | 2021-06-23 09:00 | OFFSHORE | [6 empty] | SS02241 | SEGMENT 1636 | [20 empty] | 140 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SHIP SHOAL | 242 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 | NO | 0.5 | 52000 | API 5L | SEAMLESS |  | UNITED STATESSTEEL CORPORATION | OTHER | CONCRETE | NO | [26 empty] | 1972 | 1972 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 39917 | 40721.338456284164348 | 8837 | 8837 | 253000 | 258098.019125683132 | 0 | 0 | 0 | 0 |  | 3.36 | 301754 | 137626.019781227955931392026578073089701 | 307656.357581967296348 | 0 | 0 | 0 | 0 | NO |  |  |  | 709 | 0 | 1440 | 192.619(A)(1) |  | 1972-08-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 197322 | NO | [5 empty] | YES | PIPELINE TIES INTO AN UNDERWATER PLATFORM. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM THIRD PARTY OPERATOR - KINETICA |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAK ON PIPELINE | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 7133039956 |  | TRACI BRENTANO | traci.brentano@williams.com | 2815200007 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | PIPE CONTROL RECEIVED A CALL ON JUNE 22 2021 STATING THAT A 3RD PARTY NOTICED BUBBLES IN THE SS-242 BLOCK APPROXIMATELY 2 MILES SOUTH OF SS-229. WE HAVE NOTIFIED THE SOC, WITT O'BRIEN'S, PHMSA, USCG, AND MANY OTHERS. WE ARE CURRENTLY SHOWING 709 PSIG ON THAT SECTION OF THE LINE LOOKING AT SCADA. WE CURRENTLY HAVE THE DSV LADY MONROE WITH C-DIVE DEPARTING THE DOCK AT 11:45 PM ON 6/22/2021, ETA ABOUT NOON 6/23/2021 BUT THEY WILL UPDATE ONCE IN ROUTE. THEY WILL HAVE A 20" REPAIR CLAMP ON BOARD IF IT IS OURS TO REPAIR AT THAT TIME. WE ALSO HAVE THE ANDI NICOLE IN ROUTE TO SS-214C WITH 2 TECHS, TO START BLOWING DOWN OUR 20" PIPELINE THAT IS REFERRED TO AS THE SS-269 LINE. THEIR ETA IS 6 AM 6/23/21. RESOLUTION NARRATIVE: 6-23-21 9 AM -WILLIAMS EMPLOYEES STARTED BLOWING DOWN 20" PIPELINE WITH 709PSIG 10:15 AM -DIVERS ARE ON LOCATION AND SETTING ANCHORS 1:15 AM -DIVERS BELIEVED TO HAVE FOUND THE SOURCE OF THE BUBBLES BUT RAN OUT OF BOTTOM TIME TO CONFIRM LINE SIZE. THEY WILL BE JUMPING ANOTHER DIVER TO VERIFY LINE SIZE 4:30 PM -DIVER IDENTIFIED IT IS WILLIAMS 20" PIPELINE 6-24-21 4 AM- COMPLETED BLOWDOWN TO TARGET PRESSURE OF 250 PSI TO INSTALL PLIDCO CLAMP 8 AM -CONTINUING TO PREP PIPE FOR CLAMP INSTALLATION 9 AM -FINISHED PREP ON THE PIPE AND PULLING UT READINGS AND AVERAGE OF .490 12:34 PM -CLAMP GOING DOWN ON PIPELINE TO BE INSTALLED 4:40 PM- REPAIR CLAMP WAS PUT INTO POSITION AND WILL TORQUE IN STEPS UNTIL 100% 6-25-21 4:34 AM -CLAMP INSTALLATION COMPLETE BUT THE NEW CLAMP IS LEAKING FROM THE 12OCLOCK POSITION 7 AM- CLAMP IS BEING REMOVED AND NEW SEALS BEING TRANSPORTED FROM BELLE CHASE TO DIVE VESSEL 7 PM -NEW SEALS ARRIVE AND ARE BEING INSTALLED ON THE CLAMP 8:40 PM- CLAMP BEING INSTALLED AND WILL BE TORQUED TO 100% 6-26-21 6 AM- THE SAME ISSUE WITH THE CLAMP SO PETROQUIP WAS CONTACTED AGAIN AND A NEW CLAMP IN ROUTE TO THE DOCK TO BE PUT ON THE M/V 1 PM -CLAMP WAS RECOVERED AND PICTURES SENT TO PETROQUIP FOR INSPECTION OF SEALS. 6-27-21 DOWN ON WEATHER MOST OF THE MORNING 4 PM- CLAMP GOING INTO THE WATER FOR INSTALLATION 10 PM- CLAMP WAS INSTALLED AND TORQUED TO 100% 6-28-21 1:28 AM- STARTED PRESSURING UP THE SYSTEM WHILE CHECKING FOR LEAKS 6:45 AM- REACHED PIPELINE PRESSURE 600PSI AND NO LEAKS REPORTED 6:50 AM -PRODUCERS WERE NOTIFIED TO RESUME FLOW 8 AM- PLACING SANDBAGS AND 3N1 OVER THE CLAMPED AREA. JOB COMPLETE
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210061 | 35820 | 2021-07-19 16:33 | SUPPLEMENTAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-06-19 23:50 | 2021 | MOUNTAIN | YES | 35.0156 | -107.404 | 1308279 | 2021-06-20 05:44 | 1308368 | NATURAL GAS |  | 37886 | 0 | 0.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-06-20 03:50 | 2021-06-22 13:45 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-06-20 03:20 | NO | [11 empty] | 0 | 2021-06-20 03:40 | 2021-06-20 03:40 | ONSHORE | NM | 87026 | LAGUNA | CIBOLA | NOT APPLICABLE |  | COMPRESSOR STATION 6 (LAGUNA) | NMMM165 | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2002 | 2001 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS | OTHER | [8 empty] | SENSING LINE BROKE CAUSING THE RELIEF VALVE ON UNIT 601 TO GO FULLY OPEN. | CLASS 1 LOCATION | NO |  | 657 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 111764 | 111764 | 50 | 51.0075136612022 | 100 | 102.0150273224044 | 0 | 0 |  | 2.95 | 111914 | 73401.0292791106149320598006644518272425 | 111917.0225409836066 | 0 | 0 | 0 | 0 | NO |  |  |  | 988 | 1920 | 1008 | 192.619(A)(2) |  | 1992-01-06 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | KATHRYN HARRYMAN | SR. SPECIALIST - DOT COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON JUNE 19TH 2021 AT 23:23HRS MST, THE RELIEF VALVE AT THE LAGUNA 6 COMPRESSOR STATION ALONG THE TRANSWESTERN PIPELINE LIFTED AND BEGAN RELEASING NATURAL GAS. AT 03:20 MST ON THE MORNING OF JUNE 20TH, THE LOCAL POLICE CALLED THE CONTROL CENTER AND REPORTED THE COMPRESSOR STATION RELIEF WAS GOING OFF. AT 03:40 MST, THE LOCAL TECHNICIAN ARRIVED ON SCENE AND CONFIRMED THE RELIEF VALVE WAS OPEN. AT 03:50 MST THE PIPELINE WAS SHUTDOWN AND THE TECHNICIAN WAS ABLE TO GET THE RELIEF VALVE CLOSED. THE CAUSE OF THE RELEASE WAS A BROKEN SENSING TUBE ON THE RELIEF VALVE. THE SENSING TUBE HOLDS PRESSURE ON THE VALVE AND KEEPS THE RELIEF VALVE CLOSED. ONCE THE TUBE WAS BROKEN, THE RELIEF WAS ALLOWED TO ENGAGE. IT IS BELIEVED THE TUBE BROKE DUE TO EXCESSIVE VIBRATION. AT 05:30 MST OPERATIONS COMPLETED THEIR VOLUME RELEASED CALCULATIONS AND CONFIRMED THE 3MMCF LIMIT HAD BEEN MET. REGULATORY COMPLIANCE WAS NOTIFIED AND A NRC NOTIFICATION (1308279) WAS MADE AT 05:44 MST ON JUNE 20TH. THE 48HOUR NRC NOTIFICATION (1308368) WAS MADE ON JUNE 21ST AT 13:13 MST. ON JUNE 22ND AT APPROXIMATELY 13:45 MST, THE PIPELINE WAS RESTARTED AFTER REPLACING THE BROKEN TUBING ON THE RELIEF VALVE WITH TUBING THAT IS MORE FLEXIBLE TO ALLEVIATE VIBRATION INDUCED ISSUES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210062 | 36882 | 2021-07-23 19:35 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-06-26 19:25 | 2021 | EASTERN | YES | 42.8772 | -77.5513 | 1308933 | 2021-06-26 22:23 | 1309098 | NATURAL GAS |  | 9162 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-06-26 19:30 | 2021-09-22 19:07 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-06-26 19:30 | VALVE CLOSURE |  | 2021-06-26 19:30 | 0 | 2021-06-26 19:25 | 2021-06-26 21:48 | ONSHORE | NY | 14585 | Not Within a Municipality | ONTARIO | MILEPOST | 234-1 MP 9.63 | 200-1 | VS 234-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 51 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.281 | 52000 | API-5L | FLASH WELDED |  | A O SMITH | COAL TAR |  | UNKNOWN | [26 empty] | 1951 | 1951 | CARBON STEEL |  | OTHER | [8 empty] | THE PRELIMINARY ASSESSMENT INDICATED A PIPELINE BUCKLE AT THE LOCATION OF THE RUPTURE ASSOCIATED WITH GAS RELEASE. | CLASS 1 LOCATION | NO |  | 457 |  | NO | NO |  |  | NO |  |  | 1500 | 1530.225409836066 | 0 | 0 | 31151 | 31151 | 465635 | 475017.67247267772794 | 3000 | 3060.450819672132 | 156080 | 159225.05464480878752 | INVESTIGATION COST, SPECIMEN SHIPMENT AND SPECIMEN LABORATORY COST; | 3.4 | 657366 | 302268.4403210270793716112956810631229236 | 669984.40334699471346 | 0 | 0 | 0 | 0 | NO |  |  |  | 659 | 125000 | 760 | 192.619(C) |  | 1971-01-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 61459 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | CONTROLLER ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT AND CONTROLLER RESPONSE WAS TIMELY AND APPROPRIATE. | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | YES | [7 empty] | YES | OVERSTRESS RESULTING IN BUCKLE CONDITION | [10 empty] | YES |  |  |  |  | YES | [5 empty] | 1128 | [54 empty] | YES | YES | YES |  | YES |  |  | YES | 2020 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2013 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2020 | FREE SWIMMING | HIGH RESOLUTION | [17 empty] | 2020 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2013 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [8 empty] | RESIDUAL | 2020 | FREE SWIMMING |  |  |  | YES | 1986 | 1128 | NO | [13 empty] | NO | [63 empty] | WM. MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253787 | THOMAS SUTTON | tom_sutton@kindermorgna.com | 7166462022 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND COMPLIANCE | 7133699443 | jaime_hernandez@kindermorgan.com | ON JUNE 26, 2021, TENNESSEE GAS PIPELINE, (TGP) 24-INCH LINE 200-1 PIPELINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE WITH NO FIRE. THE EVENT OCCURRED IN VALVE SECTION 234-1 BETWEEN UPSTREAM CS 233 AND DOWNSTREAM CS 237. 19:25-HOURS, GAS CONTROL BEGAN TO NOTICE SLIGHT DROP IN PRESSURE HOWEVER THE PRESSURE BEGAN RETURNING TO NORMAL. 19:25-HOURS, (APPROXIMATE TIME) THE LINE BREAK DETECTION DEVICES BEGAN TO CLOSE UPSTREAM VALVE 234-1 AND DOWNSTREAM VALVE 235-1. 19:30-HOURS, (POST EVENT ESTIMATED TIME) BOTH UPSTREAM AND DOWNSTREAM MAIN LINE VALVES ARE CLOSED 20:00-HOURS, ONTARIO COUNTY SHERRIFF DEPARTMENT PERSONNEL CALLED TGP GAS CONTROL LOCATED IN HOUSTON, TEXAS; GAS CONTROL STAFF IMMEDIATELY BEGAN DISPATCHING OPERATIONS STAFF TO ONTARIO AND LIVINGSTON COUNTIES. 21:48-HOURS, OPERATIONS STAFF WAS ON SITE AND CONFIRMED THE PIPELINE BUCKLE; THERE WAS NO ACTIVE RELEASE OF GAS, NO EVIDENCE OF FIRE AND NO EMERGENCY RESPONDERS WERE ON SITE. THERE WAS NO PUBLIC EVACUATION. OTHER OPERATIONS STAFF PROMPTLY CONFIRMED THE UPSTREAM AND DOWNSTREAM MAIN LINE VALVES WERE CLOSED AND ALSO CLOSED THE TAP VALVE TO THE METER STATION CONNECTED TO LINE 200-1 IN VALVE SECTION 234-1. THERE WAS NO CUSTOMER IMPACT AS SAID METER STATION IS ALSO CONNECTED TO LINE 200-2. 22:05-HOURS, OPERATIONS STAFF CONDUCTED AN EMERGENCY RESPONSE LINE CALL AS REQUIRED BY PROCEDURE OM-159. 22:23-HOURS, TGP PROVIDED TELEPHONIC NOTIFICATION TO THE NRC OF THE EVENT WITH AN ESTIMATE OF 11,000 MCF OF GAS UNINTENTIONALLY RELEASED TO ATMOSPHERE. THE NRC REPORT NUMBER IS 1308933. 22:32-HOURS, TGP IMMEDIATELY CALLED THE PHMSA ACCIDENT INVESTIGATION DIVISION (AID) FOLLOWING THE TELEPHONIC NOTICE TO THE NRC. ON JUNE 28, 2021, TELEPHONIC NOTIFICATION WAS PROVIDED TO THE NRC FOR THE REQUIRED 48-HOUR UPDATE. THE NRC REPORT NUMBER IS 1309098. ON JUNE 28, 2021, THE FAILURE BASED ON FIELD VISUAL OBSERVATION WAS PRELIMINARILY CLASSIFIED AS A BUCKLE OR WRINKLE. SUBSEQUENT TO THE INITIAL FIELD OBSERVATIONS, A THIRD PARTY ILI VENDOR REVIEWED AND REANALYZED PRIOR IN-LINE INSPECTION (ILI) DATA FOR THE APPLICABLE SEGMENT OF PIPELINE AND IDENTIFIED THIS AS A LOCALIZED EVENT AND CLASSIFIED THE FEATURE AS A BUCKLE. THIS INFORMATION WAS SHARED WITH PHMSA SOUTHERN REGION DURING A MEETING HELD ON 7/14/2021 JULY 14, 2021. AFTER THE JUNE 28, 2021 48 HOUR NRC UPDATE REPORT 1309098, IT WAS DETERMINED THE CORRECT UNINTENTIONAL GAS RELEASE VOLUME WAS 9,162 MCF. ON JULY 9, 2021, TGP RECEIVED CORRECTIVE ACTION ORDER (CAO) CPF NO. 2-2021-010-CAO FROM PHMSA. TGP INITIATED ACTIONS TO ADDRESS THE CAO. HOWEVER, IN PARALLEL WAS MEETING WITH PHMSA TO AMEND THE CAO WHICH WAS RECEIVED ON JULY 23, 2021. ON JULY 16, 2021, THE TGP PIPELINE REPAIR WAS COMPLETED BY PIPE REPLACEMENT AND COVERED. PER THE CAO, AN INDEPENDENT THIRD PARTY METALLURGICAL FIRM WILL ANALYZE THE SPECIMEN. THE INVESTIGATION INTO THE CAUSE IS ONGOING AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED WHEN ADDITIONAL INFORMATION IS OBTAINED. UPDATED JULY 20, 2022: ON MAY 24, 2022, THE DIRECTOR APPROVED THE REMOVAL OF THE PRESSURE RESTRICTIONS, AS ALLOWED BY ITEM NO. 5.A ON THE AMENDED CAO (ACAO) CPF NO. 2-2021-010-CAO. ON JUNE 29, 2022, THE DIRECTOR APPROVED THE REMEDIAL WORK PLAN (RWP), AS ALLOWED BY ITEM NO. 11.B. AND ITEM NO. 11.G. ON THE AMENDED CAO (ACAO) CPF NO. 2-2021-010-CAO. ON JULY 18, 2022, VIA EMAIL, TGP SUBMITTED CORRECTIVE ACTION ITEM NO 12. CAO DOCUMENTATION REPORT (CDR) AS REQUIRED BY AMENDED CAO (ACAO) CPF NO. 2-2021-010-CAO AND REQUESTED PROPER CLOSURE OF THE ACAO.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210063 | 35543 | 2021-07-28 16:53 | ORIGINAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2021-07-01 16:45 | 2021 | CENTRAL | YES | 28.5778 | -91.5942 | 1309463 | 2021-07-01 18:09 | 1310176 | NATURAL GAS |  | 300 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REPAIRS MADE WITHOUT NEEDING TO SHUT-IN PIPELINE |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-07-01 17:30 | NO | [5 empty] | OPERATIONAL CONTROL | NONE LOCATION WAS ALREADY ISOLATED |  | OPERATIONAL CONTROL | NONE LOCATION WAS ALREADY ISOLATED |  | 0 | 2021-07-01 18:09 | 2021-07-02 20:00 | OFFSHORE | [28 empty] | 110 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | EUGENE ISLAND | 228 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | OTHER | LEAKING BODY BLEED ON VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 1200 | 1200 | 48000 | 48967.213114754112 | 47000 | 47947.062841530068 | 0 | 0 |  | 4 | 96200 | 43542.2422185611070265780730897009966777 | 98114.27595628418 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 50000 | 1200 | 192.619(A)(2) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 195457 | NO | [5 empty] | YES | INSUFFICIENT LAUNCHER/RECEIVER LENGTH | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE MAOP WAS NEVER EXCEEDED | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [103 empty] | ROUTINE OR NORMAL FISHING OR OTHER MARITIME ACTIVITY NOT ENGAGED IN EXCAVATION | [261 empty] | KURT CHERAMIE | SENIOR VICE PRESIDENT | kurt.cheramie@kineticallc.com | 985-223-6165 |  | KURT CHERAMIE | kurt.cheramie@kineticallc.com | 985-223-6165 | KURT CHERAMIE | SENIOR VICE PRESIDENT | 985-223-6165 | kurt.cheramie@kineticallc.com | GAS BUBBLES REPORTED BY PRODUCER HELICOPTER AT 4:45 PM ON 7/1/2021. COORDINATES PLOTTED 650' FROM SUBSEA TIE-IN ON KINETICA 30" PIPE IN EUGENE ISLAND BLOCK 228. DIVER VESSEL MOBILIZED ON 7/2/2021 AND ARRIVED ON SITE AT 8:00 PM. DIVERS INVESTIGATED AND FOUND DAMAGE TO 1/2" STAINLESS STEEL VALVE ON BLIND FLANGE. DRIVERS REPLACED VALVE AND STOPPED LEAK. SECOND LEAK WAS LEAKING FROM BODY BLEED ON THE 12" GOOSENECK VALVE. DIVERS CYCLED THE VALVE AND LEAK STOPPED. DIVERS THEN REMOVED BODY BLEED PLUG AND REPLACED WITH 1/2" STAINLESS STEEL VALVE.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20210064 | 37444 | 2021-07-28 17:30 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2021-06-28 15:35 | 2021 | CENTRAL | YES | 33.2124 | -96.3918 | 1309092 | 2021-06-28 16:40 | 1309333 | NATURAL GAS |  | 1 | 0 | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | YES | 0 | 2 | 0 | 0 | 0 | 2 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE PIPELINE CONTINUED TO OPERATE AND DID NOT REQUIRE A SHUTDOWN. |  |  |  | YES | OPERATOR | 2021-06-28 15:35 | YES | 2021-06-28 15:35 | OTHER | SINGLE FLASH | 1 | NO | OPERATIONAL CONTROL | THIS EVENT OCCURRED ON A PIG LAUNCHER AND THE UPSTREAM VALVE DURING THE EVENT WAS CLOSED. |  | OPERATIONAL CONTROL | CLOSURE DOOR WAS IMMEDIATELY SHUT FOLLOWING INCIDENT TO SECURE THE RELEASE. |  | 0 | 2021-06-28 15:35 | 2021-06-28 14:29 | ONSHORE | TX | 75442 | FARMERSVILLE | COLLIN | NOT APPLICABLE |  | D17 / D17-9 JUNCTION LOT | SEE ABOVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | SUBJECT TO THE INVESTIGATION | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SUBJECT TO THE INVESTIGATION | OTHER | [8 empty] | THE RESPONSE TO C6 IS SUBJECT TO THE INVESTIGATION AND CANNOT BE ANSWERED AT THIS TIME. | CLASS 1 LOCATION | NO |  | 468 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 578204 | 589854.968579235136976 | 0 | 0 | 0 | 0 | THE RESPONSE TO 7A-D IS SUBJECT TO THE INVESTIGATION. | 0 | 578204 | 260221.421106557538188 | 589854.968579235136976 | 1 | 0 | 0 | 0 | NO |  |  |  | 0 | 0 | 800 | 192.619(A)(2) |  | 2008-09-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 32 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT UNRELATED TO SCADA. | [12 empty] | YES | 2 | 0 | YES | 5 | 0 | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | MAINLINE VALVE | [22 empty] | YES | DAMAGE ALONG SEALING SURFACES | [161 empty] | BILL BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  |  |  |  | JEFF KNIGHTS | SR. V.P. TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON JUNE 28, 2021, ABOUT 3:35 P.M. LOCAL TIME, A NATURAL GAS IGNITION OCCURRED DURING ROUTINE MAINTENANCE ACTIVITIES AT AN ATMOS ENERGY CORPORATION (ATMOS) FACILITY NEAR FARMERSVILLE, TEXAS. THE NATURAL GAS IGNITED AFTER WORKERS INSERTED AN IN-LINE TOOL (OR PIG) INTO A LAUNCHER. TWO WORKERS FROM ATMOS AND FIVE EMPLOYEES FROM TWO OF ITS CONTRACTORS WERE ON-SITE AT THE TIME OF THE ACCIDENT AND PERFORMING WORK FOR ATMOS. THE IGNITION OCCURRED WHILE THE WORKERS WERE REMOVING THE PIG INSERTION TOOL DURING THE SIXTH OF A SERIES OF IN-LINE INSPECTIONS. A PIG EJECTED FROM THE LAUNCHER. AN ATMOS WORKER CALLED 9-1-1 AT 3:35 P.M. THE COLLIN COUNTY ASSISTANT FIRE MARSHAL WAS THE FIRST EMERGENCY RESPONDER ON THE SCENE, WITH OTHER AGENCIES, INCLUDING THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) ARRIVING THEREAFTER FOR ADDITIONAL SUPPORT IN EMERGENCY RESPONSE. THE NTSB LEAD AN INVESTIGATION INTO THE MATTER. THE NTSB'S PIPELINE INVESTIGATION REPORT DETERMINED THAT THE PROBABLE CAUSE OF THE EVENT WAS A LEAKING MAINLINE VALVE THAT ALLOWED NATURAL GAS TO ENTER THE LAUNCHER WHERE IT MIXED WITH AIR, CREATING A FLAMMABLE GAS-AIR MIXTURE THAT WAS IGNITED BY AN UNDETERMINED SOURCE. DUE TO THE CIRCUMSTANCES OF THIS EVENT, THE ESTIMATED VOLUME OF COMMODITY RELEASED IS UNMEASURABLE. THEREFORE, ATMOS ENERGY HAS RESPONDED TO QUESTIONS A7 AND A21C WITH 1.00, WHICH IS THE MINIMUM VALUE ALLOWED. NOTE THAT THE DISTANCE REFLECTED IN RESPONSE TO QUESTION E6, IS ACTUALLY BETWEEN THE VALVE AND THE LAUNCHER DOOR, WHICH IS WHERE THE INCIDENT OCCURRED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210065 | 35749 | 2021-07-29 14:03 | SUPPLEMENTAL FINAL | 6690 | GREAT PLAINS NATURAL GAS CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2021-06-30 02:06 | 2021 | CENTRAL | YES | 46.6221 | -95.8051 | 1309316 | 2021-06-30 14:16 | 1309456 | NATURAL GAS |  | 8082 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE SHUT-IN SECTION WAS BY-PASSED. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | MONITORED NON HAZARDOUS LEAK FOR MIGRATION. REDUCED OPERATING PRESSURE TO 475 PSIG. |  | OPERATIONAL CONTROL | MONITORED NON HAZARDOUS LEAK FOR MIGRATION. REDUCED OPERATING PRESSURE TO 475 PSIG. |  | 0 | 2021-06-21 11:45 | 2021-06-21 11:45 | ONSHORE | MN | 56587 | VERGAS | OTTER TAIL | NOT APPLICABLE |  | GPNG TRANSMISSION LINE | NA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 78 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.188 | 42000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1966 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 150 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 31069 | 31069 | 0 | 0 | 163290 | 166580.33811475414476 | 0 | 0 |  | 3.8442 | 194359 | 93874.6709142340196914617940199335548173 | 197649.33811475414476 | 0 | 0 | 0 | 0 | NO |  |  |  | 638 | 10802 | 730 | 192.619(A)(3) |  | 1990-12-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 89241 | NO | YES | [6 empty] | YES |  |  |  |  | YES | NO PIG LAUNCHER/RECEIVER | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE NON-HAZARDOUS LEAK DID NOT CHANGE THE PRESSURE IN THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [64 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [10 empty] | NO | YES | OTHER | [9 empty] | UTILITY | UNKNOWN/OTHER | TELECOMMUNICATIONS | NO | [5 empty] | YES | 24 | OTHER |  |  |  | THE DAMAGE OCCURRED DURING A COMMUNICATION LINE INSTALLATION. THE DATE OF INSTALLATION OF THE COMMUNICATION LINE CROSSING THE PIPELINE AT THE POINT OF DAMAGE IS UNKNOWN. | [117 empty] | NO | [62 empty] | NO | NO |  |  | NO | [13 empty] | NO | [63 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  | GREG WATKINS | greg.watkins@mdu.com | 208-377-6032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | AT 11:45 A.M. CST ON 6/21/2021 A GREAT PLAINS NATURAL GAS (GPNG) SERVICEPERSON NOTICED DEAD VEGETATION OVER AN 8" TRANSMISSION LINE ON PRIEBS PARK DRIVE IN VERGAS, MN. AN ONSITE LEAK INVESTIGATION IDENTIFIED A NON-HAZARDOUS GRADE 2 LEAK. AFTER DETERMINING THE SEGMENT OF PIPELINE WOULD BE REPLACED, ESTIMATED COSTS OF $315,500 WERE CALCULATED AT 2:06 P.M. CST ON 6/30/2021. THE LEAK WAS ISOLATED WITH LINE STOPPER FITTINGS AT 10:30 A.M. CST ON 7/28/2021. THE SHUT-IN SECTION OF PIPELINE WAS BYPASSED DURING THE SHUT-IN. THE NEW SEGMENT OF PIPELINE WAS PLACED IN SERVICE AT 6:07 P.M. CST ON 7/28/2021. DURING THE BYPASS, THREE INDUSTRIAL CUSTOMERS WERE CURTAILED FOR APPROXIMATELY 24 HOURS. THE PIPELINE HAD AN EXCAVATION DAMAGE (DENT AND GOUGES) AT A COMMUNICATION LINE CROSSING. THE DAMAGED SECTION HAD A 3/4" LONG CRACK LOCATED IN THE DENTED AREA. ESTIMATED VOLUME OF GAS RELEASED UNINTENTIONALLY (PART A QUESTION 7) WAS CALCULATED FROM THE DATE OF DISCOVERY (PART A QUESTION 13) TO WHEN THE LEAK WAS ISOLATED (7/28/2021). ACTUAL COSTS WILL BE UPDATED ON THE FINAL REPORT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210066 | 37528 | 2021-08-05 16:11 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-07-15 15:54 | 2021 | CENTRAL | YES | 38.3335 | -98.1729 | 1310849 | 2021-07-15 15:38 |  | NATURAL GAS |  | 61000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-07-15 15:08 | NO | [11 empty] | 7 | 2021-07-15 14:47 | 2021-07-15 15:45 | ONSHORE | KS | 67554 | Not Within a Municipality | RICE | SURVEY STATION NO. | WELL 02-05 | LYONS WELL 02-05 | LYONS WELL 02-05 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2021 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | A SEPARATION OF COMPONENTS INSTALLED TO PERFORM IN-LINE INSPECTION. | CLASS 1 LOCATION | NO |  | 116 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 215330 | 215330 | 311494 | 317770.689207650361736 | 32710 | 33369.11543715847924 | 0 | 0 |  | 3.53 | 559534 | 296197.390212270669423880398671096345515 | 566469.804644808840976 | 3 | 0 | 7 | 0 | NO |  |  |  | 1140 | 0 | 1440 | 192.619(A)(3) |  | 1976-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS NOT RELATED TO CONTROLLERS OR THE CONTROL ROOM. | [12 empty] | NO |  |  | YES | 8 | 0 | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | [204 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED | [6 empty] | YES | INFERIOR EQUIPMENT WAS SUPPLIED BY A SUB-CONTRACTOR. | ROUTINE MAINTENANCE | NO | [146 empty] | YES |  |  |  | JEFFREY CULLISON |  | j.cullison@nngco.com | 402-398-7439 |  |  |  |  | TOM CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | A CONTRACTOR AND SUBCONTRACTOR WERE PREPARING TO INSPECT A CASING ON WELL 02-05 ON JULY 15, 2021. AFTER INSTALLING A REDUCING ASSEMBLY THAT ALLOWS A TOOL TO BE LOWERED IN THE CASING PROVIDED BY THE CONTRACTOR, BOTH PARTIES PROCEEDED TO TEST THE COMPLETED ASSEMBLY. THE WELLHEAD MASTER VALVE WAS PARTIALLY OPENED TO EQUALIZE PRESSURE. THE CONTRACTOR NOTED THAT THE MASTER VALVE WAS DIFFICULT TO OPERATE AS EXPECTED DUE TO RELATIVELY HIGH-PRESSURE DIFFERENTIAL ACROSS THE VALVE. THEY REPORTED THE PRESSURE WAS 1,140 PSIG AT 0900 HOURS. NO GAS COULD BE HEARD FLOWING THROUGH THE VALVE, BUT THE SUBCONTRACTOR INDICATED THERE WAS A SLIGHT LEAK BUBBLING BETWEEN THE COMPANION FLANGE AND THE REDUCING FITTING, THEREFORE, BOTH THE CONTRACTOR AND SUBCONTRACTOR CLOSED THE MASTER VALVE AND THEN OPERATED A BLEED-OFF VALVE, RELEASING THE PRESSURE BUILDUP. THE LEAK WAS REMEDIATED BY TIGHTENING THE REDUCING FITTING WITH A PIPE WRENCH BY APPROXIMATELY A HALF-TURN ON THE FITTING. WITH THE LEAK REMEDIATED, THE MASTER VALVE WAS SLOWLY OPENED AGAIN WITH DIFFICULTY. IT TYPICALLY TAKES 2-4 TURNS OF THE VALVE TO ACHIEVE FULL-OPEN STATUS, AFTER APPROXIMATELY 1 1/2 TO 2 TURNS OF THE MASTER VALVE, THE ASSEMBLY FAILED. THE SIX PERSONNEL ON-SITE VACATED THE WORK AREA, THREE OF WHICH RECEIVED MEDICAL ATTENTION DUE TO FACIAL ABRASIONS AND POTENTIAL HEARING LOSS. ONCE THE AREA WAS SECURED AND NORTHERN NATURAL GAS EVALUATED THE SCENARIO, A WELL CONTROL CONTRACTOR WAS TO MOBILIZE TO REMEDIATE THE VENTING GAS. THE WELL CONTROL CONTRACTOR ARRIVED ON-SITE AT AND CONFERRED WITH EMERGENCY RESPONDERS AT 2345 HOURS, AND DUE TO LACK OF DAYLIGHT AND PRESENCE OF NEARBY EQUIPMENT AND VEHICLES, IT WAS DECIDED TO RE-EVALUATE THE NEXT MORNING. AROUND 0700 ON JULY 16, 2021, THE WELL CONTROL CONTRACTOR DELAYED THE RESPONSE EFFORT DUE TO POOR LIGHTING AND LIMITED VISIBILITY CAUSED BY EARLY MORNING FOG. ONCE THE FOG LIFTED, THE WELL CONTROL CONTRACTOR ASSESSED THE SITE AND CLOSED THE MASTER VALVE AT 1001 HOURS ON JULY 16, 2021. IT WAS NOTED BY THE WELL CONTROL CONTRACTOR THAT THE MASTER VALVE HAD A SLIGHT LEAK AND WAS REMEDIATED BY INSTALLING A SECOND MASTER VALVE ABOVE THE ORIGINAL CONTAINING THE LEAK FULLY AT 1125 HOURS. THE PRELIMINARY EVALUATION DETERMINED THE THREADED CONNECTION BETWEEN THE COMPANION FLANGE AND REDUCING FITTING DID NOT HAVE SUFFICIENT THREAD ENGAGEMENT. THE INADEQUATE CONNECTION COULD NOT PROVIDE SUFFICIENT HYDRAULIC STRENGTH TO WITHSTAND THE PRESSURE NOR THE MECHANICAL STRENGTH TO RESIST THE BENDING MOMENT IMPARTED BY THE SUSPENDED WIRELINE ASSEMBLY. PRELIMINARY LAB ANALYSIS CONDUCTED BETWEEN AUGUST 30, 2021 ' SEPTEMBER 1, 2021 FOUND THE COMPANION FLANGE, SWAGE PIN, WAS UNDERSIZE BY 0.0325 INCHES AND THE REDUCING FITTING WAS OVER SIZED BY 0.0305 INCHES. THE THREADS ON THE COMPANION FLANGE WERE ALSO SHORT LENGTH 2-INCHES INSTEAD OF THE FULL LENGTH OF 4-INCHES, WHICH LIMITED THE NUMBER OF THREADS AVAILABLE FOR FULL ENGAGEMENT ACROSS 4-INCHES. THIS LACK OF AVAILABLE ENGAGEMENT AND COMPONENTS OUTSIDE ACCEPTABLE TOLERANCE, PREVENTED THE ASSEMBLY FROM PROPERLY HOLDING TOGETHER UNDER THE DESIGNED PRESSURE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210067 | 36327 | 2021-08-10 08:01 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-07-13 11:52 | 2021 | CENTRAL | YES | 32.1643 | -90.2895 | 1310580 | 2021-07-13 15:50 | 1310758 | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | LEAK WAS MINOR ALLOWING REPAIR CLAMP TO BE INSTALLED SAFELY |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-07-13 21:55 | OPERATIONAL CONTROL | NO ACTION TAKEN TO CONTROL FLOW DOWNSTREAM BECAUSE UPSTREAM VALVE CLOSURE LOWERED PRESSURE. |  | 0 | 2021-07-13 11:52 | 2021-07-13 12:30 | ONSHORE | MS | 39272 | Not Within a Municipality | HINDS | SURVEY STATION NO. | 565+21 | INDEX 302 | MCCOMB 6" PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 26 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | FILLET WELD | [18 empty] | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 95 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 4 | 4 | 307929 | 314133.853483606644876 | 1500 | 1530.225409836066 | 0 | 0 |  | 3.62 | 309433 | 139261.5264802094974864219269102990033223 | 315668.078893442710876 | 0 | 0 | 0 | 0 | NO |  |  |  | 393 | 4000 | 447 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 16632 | NO |  | YES | YES |  |  |  |  | YES |  |  |  |  | YES | HIGH VOLUME FLOWS ON SMALL DIAMETER PIPE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM A CENTERPOINT ENERGY EMPLOYEE |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | UNKNOWN | [13 empty] | YES | [7 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | A CENTERPOINT ENERGY TECHNICIAN REPORTED A MINOR LEAK ON GULF SOUTH PIPELINE'S INDEX 302 (MCCOMB 6") AT APPROXIMATELY 11:52 AM ON 07/13/21 TO A GULF SOUTH TECHNICIAN IN THE FLOWOOD, MS AREA. GULF SOUTH DISPATCHED TECHNICIANS TO INVESTIGATE LEAK CALL. GULF SOUTH MADE AN EMERGENCY 811 LOCATE CALL AND STARTED EXCAVATION ABOUT 3:00 PM TO DETERMINE IF THE LEAK WAS ON A GULF SOUTH PIPELINE. GULF SOUTH CLOSED MAIN LINE BLOCK VALVE #120085 AT WYNNDALE RD. AND REDUCED GAS SUPPLY PRESSURE BY 20% ON INDEX 302. ONCE THE AREA OF CONCERN WAS EXCAVATED, GULF SOUTH DISCOVERED A LEAK ON A WELD JOINT ON THE SOUTHSIDE OF AN EXISTING WELD OVER THAT WAS PREVIOUSLY INSTALLED ON GSPL INDEX 302 PIPELINE. THE LEAK WAS A PINHOLE LEAK PRODUCING CONTINUOUS BUBBLES ONLY. THE COMBUSTIBLE GAS INDICATOR (CGI) INDICATED 14% GAS ON 100% SCALE. GULF SOUTH INSTALLED A SKINNER BRAND BAND CLAMP ON THE LEAK AT THE WELD JOINT TO STOP THE LEAK THEN TESTED THE SURROUNDING AREA WITH CGI TO ENSURE THERE WAS NO MIGRATION OR OTHER GAS LEAKS IN THE AREA. PERMANENT REPAIR WILL BE MADE BY PIPE REPLACEMENT. ESTIMATE FOR THE PIPE REPLACEMENT EXCEEDS $122,000; A SUPPLEMENTAL INCIDENT REPORT WILL BE REQUIRED. 2/10/22 UPDATE A7 PER PHMSA INSTRUCTION. THE LEAK WAS VERY MINOR AND THE ORIGINAL RESPONSE WAS .001 BUT IT RENDERED AS "0" ON THE PDF SO IT HAS BEEN CHANGED TO "1" ALTHOUGH IT WAS ACTUALLY LESS THAN 1 MCF. UPDATED B4, TO INDICATE LEAK DID NOT OCCUR WITHIN A MUNICIPALITY. UPDATED REPAIR COST. PIPE REPLACEMENT WAS COMPLETED ON 10/12/21 AND LINE WAS RETURNED TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210068 | 35691 | 2021-08-10 09:59 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2021-07-10 15:50 | 2021 | CENTRAL | YES | 29.6168 | -88.6336 | 1310329 | 2021-07-10 17:26 | 1310448 | NATURAL GAS |  | 12460 | 20700 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-07-16 20:00 | 2021-08-12 14:45 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-07-30 05:30 | VALVE CLOSURE |  | 2021-07-19 01:30 | 0 | 2021-07-16 16:30 | 2021-07-16 16:00 | OFFSHORE | [28 empty] | 60 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | MP | 96 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 24 | NO | 0.5 | 52000 | API 5L | DSAW |  | UNKNOWN | OTHER | 2" CONCRETE COAT OVER 5/8" SOMASTIC | NO | [26 empty] | 1988 | 1988 | CARBON STEEL |  | LEAK |  |  | OTHER | SUSPECT INTERNAL CORROSION | [5 empty] | CLASS 1 LOCATION | NO |  | 629 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 82800 | 84468.4426229508432 | 49840 | 49840 | 100000 | 102015.0273224044 | 370000 | 377455.60109289628 | 0 | 0 | VESSELS, DIVERS AND CONSUMABLES =$300,000 BLOWDOWN EQUIPMENT=$70000 | 4 | 602640 | 281490.6452535266504372093023255813953488 | 613779.0710382515232 | 0 | 0 | 0 | 0 | NO |  |  |  | 944 | 3000 | 1440 | 192.619(A)(1) |  | 1988-10-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 127000 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | AIR PATROL |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE PRESSURE WAS BEING MONITORED BY GAS CONTROL AT THE ONLY INPUT INTO THE SYSTEM, PRESSURE CHANGE CAUSED BY THE LEAK WOULD NOT HAVE CAUSED AN ALARM | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [5 empty] | YES |  |  |  | YES | [5 empty] | NO | YES | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | LISA WU | ENGINEER SPECIALIST OPERATIONAL COMPLIANCE | lisa.wu@enbridge.com | 713-627-4889 | 7133864466 | LISA WU | lisa.wu@enbridge.com | 713-627-4889 | NATHAN ATANU | MANAGER - OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | ON JULY 10, 2021 AT 3:50 P.M. CST, A HELICOPTER PILOT DISCOVERED BUBBLES IN THE GULF OF MEXICO. AT THAT TIME TETLP COULD NOT CONFIRM THAT IT WAS A TETLP ACTIVE LINE IN THE VICINITY. AFTER PRELIMINARY INVESTIGATION AND DISCUSSION WITH FIELD OPERATIONS, TETLP MADE THE NOTIFICATION TO THE NRC AT 5:26 P.M. CST BASED REPAIR COSTS THAT WOULD EXCEED THE DOLLAR THRESHOLD FOR REPORTING ASSUMING THE LEAK WAS ON TETLP'S SYSTEM. DUE TO LIMITED CONTRACTOR AVAILABILITY IN THE GULF COAST REGION, A DIVING VESSEL CONTRACTOR COULD NOT START MOBILIZING TO THE BUBBLE SITE UNTIL JULY 14, 2021. AT APPROXIMATELY 4:30 PM CST ON JULY 16, 2021 IT WAS CONFIRMED THAT THE LEAK WAS ON TETLP'S LINE 40-B-4. THE LINE 40-B-4 WAS TAKEN OUT OF SERVICE ON JULY 16, 2021; REPAIR WAS COMPLETED ON AUGUST 12, 2021 BY INSTALLING A MECHANICAL COUPLING AND THE LINE WAS RESTARTED AUGUST 12 AT 2:45 P.M. CST. THE LEAK WAS A PIN HOLE IN THE PIPE WALL CAUSED BY INTERNAL CORROSION AT THE 6 O'CLOCK POSITION. THE ROOT CAUSE IS BELIEVED TO BE DUE TO A MIX OF GAS, WATER AND CONDENSATE TRANSPORTED ON THIS PIPELINE SYSTEM.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210069 | 35697 | 2021-08-10 17:07 | SUPPLEMENTAL FINAL | 22655 | WBI ENERGY TRANSMISSION, INC. | 1250 WEST CENTURY AVENUE | BISMARCK | ND | 58503 | 2021-07-12 16:14 | 2021 | MOUNTAIN | YES | 44.8715 | -108.4195 | 1310473 | 2021-07-12 16:39 | 1310675 | NATURAL GAS |  | 4757 | 3162 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-07-12 16:01 | 2021-08-26 13:00 |  | YES | OPERATOR | 2021-07-12 15:19 | NO | [5 empty] | VALVE CLOSURE |  | 2021-07-12 16:01 | VALVE CLOSURE |  | 2021-07-12 16:07 | 0 | 2021-07-12 15:03 | 2021-07-12 15:45 | ONSHORE | WY | 82420 | Not Within a Municipality | BIG HORN COUNTY | SURVEY STATION NO. | 3100+16 | WORLAND_CABIN CREEK LINE | LOVELL COMPRESSOR STATION TO COWLEY VALVE NO. 59.6 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.25 | 42000 | API 5L | OTHER | UNKNOWN SEAM TYPE. | YOUNGSTOWN STEEL | COAL TAR |  | YES | [26 empty] | 1950 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 12 | 18 | [7 empty] | CLASS 1 LOCATION | NO |  | 260 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 9486 | 9677.145491803281384 | 14271 | 14271 | 17637 | 17992.390368852464028 | 2171 | 2214.746243169399524 | 0 | 0 |  | 3 | 43565 | 22547.66284345897009407973421926910299 | 44155.282103825144936 | 0 | 0 | 0 | 0 | NO |  |  |  | 482 | 0 | 800 | 192.619(A)(2) |  | 1960-05-01 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | YES | MANUAL | MANUAL | 18120 | NO | [5 empty] | YES | PIPELINE WAS CONSTRUCTED PRIOR TO REQUIREMENTS TO BE ABLE TO PASS INSPECTIONS TOOLS, THEREFORE THERE ARE NO LAUNCHERS OR RECEIVERS INSTALLED ON THE LINE TO ACCOMMODATE THEM. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A THIRD PARTY DIGGING WITHOUT A ONE CALL NOTIFICATION AND HIT OUR PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | FARMER | UNKNOWN/OTHER | LANDSCAPING | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | KENT KAHL | COMPLIANCE AND PIPELINE INTEGRITY SUPERVISOR | kent.kahl@wbienergy.com | 406-359-7222 | 406-359-7244 |  |  |  | KENT KAHL | COMPLIANCE AND PIPELINE INTEGRITY MANAGER | 406-359-7222 | kent.kahl@wbienergy.com | THE LANDOWNER WAS USING A JD 850 BULLDOZER WITH RIPPERS TO BREAKUP SOIL TO LEVEL A SECTION OF GROUND. THE DOZER STRUCK AND PUNCTURED WBI ENERGY'S STEEL HIGH PRESSURE PIPELINE ON JULY 12, 2021. THE LANDOWNER DIDN'T CONTACT 811 TO HAVE LOCATES DONE. PRIOR TO THE FARMER LEVELING ANY OF THE LAND, THE PIPELINE HAD APPROXIMATELY 36" OF COVER, WHEN IT WAS HIT THERE WAS ONLY ABOUT 12" OF COVER REMAINING. THE DAMAGE TO THE LINE OCCURRED IN AN AREA WHERE THE PIPELINE IS LOOPED, SO THERE WAS NO INTERRUPTION OF SERVICE. REPAIRS WERE MADE ON 8/26/2021. AFTER THE REPAIR WAS COMPLETE, OUR CREW DUG AN ADDITIONAL 70 FEET TO THE NORTH AND 30 FEET TO THE SOUTH LOOKING FOR ADDITIONAL DAMAGE, NOW WAS FOUND. THE LINE WAS THEN REBURIED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210070 | 36400 | 2021-08-20 08:04 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2021-05-05 11:45 | 2021 | EASTERN | YES | 39.1445 | -77.0923 | 1311366 | 2021-07-21 12:41 | 1311569 | NATURAL GAS |  | 105 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | AREA WHERE LEAK OCCURING WAS ABLE TO BE ISOLATED AND BYPASSED |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-06-02 12:00 | VALVE CLOSURE |  | 2021-06-02 12:00 | 0 | 2021-05-06 12:00 | 2021-08-06 12:00 | ONSHORE | MD | 20853 | OLNEY | MONTGOMERY | MILEPOST | MP 1616 | 185-20 VALVE STATION | 185-20 VALVE STATION CROSSOVER C08 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1970 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 656 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 8000 | 8161.202185792352 | 242000 | 246876.366120218648 | 0 | 0 |  | 0 | 250000 | 112512.80737704925 | 255037.568306011 | 0 | 0 | 0 | 0 | NO |  |  |  | 613 | 40000 | 650 | 192.619(A)(2) |  | 1970-10-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1 | NO | [5 empty] | YES | LEAK ON PIPING/COMPONENT IN VALVE STATION. NOT LOCATED ON THE MAINLINE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK IS SMALLER THAN ABLE TO BE CAPTURED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | VALVE THREADS | [19 empty] | YES | THREADED CONNECTIONS | [161 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 918-264-0522 |  |  |  |  | TYSON GREEN | MANAGER OF PIPELINE SAFETY | 346-439-8090 | tyson.green@williams.com | PIPELINE OPERATIONS RECEIVED AN AERIAL PATROL REPORT INDICATING A POTENTIAL LEAK ON MAY 5, 2021. THE LEAK WAS VERIFIED ON THE GROUND AT VALVE STATION 185-20 ON MAY 6, 2021 BY HAND DIGGING AND PROBING THE AREA BY WILLIAMS' PERSONNEL. INITIALLY IT WAS NOT SUSPECTED TO MEET THE REPORTING THRESHOLD AS THE LEAK WAS VERY SMALL. OPERATIONS BEGAN TO INVESTIGATE BY HYDROVACING AND PROBING AROUND THE SITE TO LOCATE THE LEAK. COST TO LOCATE THE LEAK BEGAN TO REACH $120K AND WAS REPORTED TO THE NRC ON JULY 21, 2021 (NRC #1311366). THE SUSPECTED AREA OF THE VALVE SITE CONTAINING THE LEAK HAS BEEN ISOLATED AND PURGED OF GAS. MOST RECENT DETAILS AS OF 8/19: -CURRENTLY: 0 PSI -EXCAVATING POSSIBLE SOURCES UNDERGROUND (FLANGES, VALVE THREADED FITTINGS) AND PROBING WITH GAS DETECTOR. -OPERATIONS STARTED INVESTIGATING MLA VALVE 185-A-20. IT WAS DISCARDED IT AS LEAK SOURCE AND WE ARE EXCAVATING FLANGES AND CROSSOVER VALVES IN CROSSOVER HEADER. NO CUSTOMERS AFFECTED. -CO7 VALVE EXCAVATED, VALVE THREADED GREASE FITTING FOUND LOOSE (POSSIBLE LEAK SOURCE) -185A20, CO1, CO2, A-LINE INSULATING FLANGES EXCAVATED AND RE-COATED. -POWER GAS LINE HEADER EXCAVATED, SECTIONS FOUND DAMAGED BY PRIOR EXCAVATION. NEXT STEPS: -REPLACE DAMAGED SECTIONS OF POWER GAS HEADER -REPAIR LOOSE GREASE FITTINGS ON CO7 ULTIMATELY, A FLIR CAMERA WILL BE USED IF WE ARE UNABLE TO FIND THE LEAK SOURCE. UPDATE: LEAK WAS FIXED AND SEGMENT WAS PUT INTO SERVICE ON AUGUST 31, 2021. GAS WAS FOUND TO BE COMING FROM UNDERGROUND THREADED CONNECTIONS ON THE CO8 (30" CROSSOVER) VALVE. THE GREASE FITTING AND BODY BLOWDOWN CONNECTION POINTS WERE DISCOVERED TO BE HAND TIGHT. OPERATIONS APPLIED BELZONA 1111 WITH REINFORCING CLOTH TO ALL UNDERGROUND THREADED CONNECTIONS. GAS WAS REINTRODUCED TO THIS SEGMENT AND NO FURTHER GAS LEAKS WERE DETECTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210071 | 36559 | 2021-08-20 11:36 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-07-22 13:19 | 2021 | CENTRAL | YES | 38.8426 | -98.074 | 1311499 | 2021-07-22 14:23 | 1311723 | NATURAL GAS |  | 197700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-07-22 13:44 | 2021-08-06 12:00 |  | NO |  |  | YES | 2021-07-22 13:19 | ALLOWED TO BURN OUT |  | 197700 | NO | VALVE CLOSURE |  | 2021-07-22 14:15 | VALVE CLOSURE |  | 2021-07-22 14:48 | 0 | 2021-07-22 13:19 | 2021-07-22 14:15 | ONSHORE | KS | 67439 | Not Within a Municipality | ELLSWORTH | MILEPOST | 27.35 | KSM20605-M640E | BUSHTON TO TESCOTT E-LINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.344 | 60000 | 5LX | DSAW |  | REPUBLIC | COAL TAR |  | YES | [26 empty] | 1966 | 1965 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 720 | 30 |  | CLASS 1 LOCATION | NO |  | 670 |  | NO | NO |  |  | NO |  |  | 100 | 102.0150273224044 | 0 | 0 | 490296 | 490296 | 100000 | 102015.0273224044 | 60000 | 61209.01639344264 | 210000 | 214231.55737704924 | METALLURGICAL LAB AS OF 12/1/21 AND RISING! | 2.48 | 860396 | 488269.8072170634439192691029900332225914 | 867853.6161202186844 | 0 | 0 | 0 | 0 | NO |  |  |  | 958 | 240 | 991 | 192.619(A)(2) |  | 1988-06-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 100547 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 1966 | NO | YES | YES | YES |  |  | 2021 | 2021 |  |  | NO | [190 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [27 empty] | 2017 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | [19 empty] | YES | 1988 | 1280 | NO | [13 empty] | NO | [63 empty] | JOHN GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  |  |  |  | TOM CORRELL | VP PIPELINE SAFETY AND RIST | 402-398-7715 | thomas.correll@nngco.com | ON JULY 22, 2021, AT 1:23 PM CDT THE ELLSWORTH COUNTY SHERIFFS OFFICE CONTACTED NORTHERN'S OPERATIONS COMMUNICATION CENTER TO REPORT A GAS LINE EXPLOSION NEAR 23RD ROAD AND AVENUE C OUTSIDE OF ELLSWORTH, KANSAS. THERE WAS FIRE BLOWING APPROXIMATELY 100 FEET IN THE AIR FROM THE M640E LINE AT MILEPOST 27.32. NO INJURIES WERE REPORTED AT THE SCENE. FIRE PERSONNEL WERE DISPATCHED TO THE SITE AT 23RD ROAD AND AVENUE C. THE SHERIFF CLOSED LOCAL ROADS SURROUNDING THE SITE. FIELD OPERATIONS PERSONNEL SHUT IN THE PIPELINE AT ISOLATION VALVES 640EBE01, LOCATED AT THE BUSHTON (KS) COMPRESSOR STATION AT MILEPOST 0, AND 640EBE0A, LOCATED AT THE TESCOTT (KS) COMPRESSOR STATION AT MILEPOST 46, AT 1:44 PM CDT. A MEMBER FROM THE FIELD TEAM ARRIVED AT 2:15 PM CDT TO CLOSE BLOCK VALVE 3 (640EBE03) AT MILEPOST 16.3. GRASS FIRES WERE BURNING IN THE AREA SURROUNDING THE INCIDENT SITE. ANOTHER TEAM MEMBER CLOSED BLOCK VALVE 5 (640EBE05) AT MILEPOST 34.8 AT 2:48 PM CDT, AND THE LINE FIRE WAS EXTINGUISHED. EMERGENCY SERVICES PUT OUT THE SURROUNDING GRASS FIRES. APPROXIMATELY 60 FEET OF PIPING WAS EJECTED FROM THE RUPTURE SITE IN FOUR SECTIONS. 11/30/21 UPDATE - CORRECTIONS PROVIDED BY PHMSAS ACCIDENT INVESTIGATION DIVISION: VOLUME OF GAS LOST CORRECTED TO 197,700; TIME VALVE 5 WAS ACTUALLY CLOSED CORRECTED TO 14:48; 'NOT WITHIN A MUNICIPALITY WAS CHECKED; PIR WAS CORRECTED AND NORTHERN IS USING 0.71 FOR HIGH BTU GAS; METALLURGICAL LAB COSTS WERE ENTERED AND THERE IS MORE COSTS TO COME; TOTAL COSTS UPDATED AUTOMATICALLY WHEN THE CORRECT NUMBERS WERE ENTERED; CAUSE IN PART G CHANGED TO METALLURGICAL ANALYSIS; AND TIME CHANGED TO 2:45 IN THE NARRATIVE FOR VALVE 5. THE METALLURGICAL ANALYSIS WAS WITNESSED BY PHMSA PERSONNEL AT STRESS ENGINEERING AND BRYAN LABS. 04/04/22 UPDATE: NO NEW INFORMATION. ACCIDENT INVESTIGATION DIVISION HAS METALLURGICAL REPORT. MARKED FINAL. 04/07/22 UPDATE: FOUND ERROR. AN EXTRA DECIMAL WAS INCLUDED IN 21C. ALL THE GAS WAS CONSUMED BY FIRE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210072 | 35656 | 2021-08-20 14:43 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-07-23 23:09 | 2021 | EASTERN | YES | 38.2703 | -82.5766 | 1311641 | 2021-07-24 01:45 | 1311750 | NATURAL GAS |  | 92804 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | TWO UNITS WERE RUNNING NORMALLY; |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-07-24 01:30 | 2021-07-24 00:10 | ONSHORE | KY | 41129 | Not Within a Municipality | BOYD | NOT APPLICABLE |  | CS-114 CATLETTSBURG COMPRESSOR STATION | CS-114 CATLETTSBURG COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2015 | 2015 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | PILOT O-RING | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 541 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 364720 | 364720 | 950 | 969.1427595628418 | 635 | 647.79542349726794 | 650 | 663.0976775956286 | INTERNAL LABOR COST TO CONDUCT INVESTIGATION; | 3.93 | 366955 | 240315.499049445836906295681063122923588 | 367000.03586065573834 | 0 | 0 | 0 | 0 | NO |  |  |  | 758 | 950000 | 765 | 192.619(A)(1) |  | 1959-11-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PROCESS AND ACTIONS OF THE CONTROLLERS DID NOT CONTRIBUTE TO THE CAUSE OF THE INCIDENT; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | O-RING WITHIN VALVE OPERATOR PILOT FAILED | [161 empty] | WM MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253509 | TIM HAMMOND | tim_hammond@kindermorgan.com | 6067392102 | JAIME HERNANDEZ | DIRECTOR ENGR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 23, 2021, AT 23:06, TENNESSEE GAS PIPELINE COMPANY (TGP) GAS CONTROL BEGAN TO OBSERVE INDICATIONS OF DECREASING DISCHARGE PRESSURE READINGS FROM 758 PSIG TO 666 PSIG AT COMPRESSOR STATION 114. TGP GAS CONTROLLER CALLED THE FIELD OPERATOR TO GO OUT AND ASSESS THE PRESSURE CHANGES. FIELD OPERATOR ARRIVED AT 00:10, SAFELY ENTERED THE STATION, AND BEGAN THE INVESTIGATION. FIELD OPERATOR FOUND ESD VALVE BDS-2 IN THE OPEN POSITION RELEASING NATURAL GAS TO ATMOSPHERE. IMMEDIATELY THE FIELD OPERATOR ATTEMPTED TO CLOSE VALVE BDS-2 WITHOUT SUCCESS AND SUBSEQUENTLY BEGAN CLOSING AN ADJACENT MANUAL ISOLATION VALVE TO SUCCESSFULLY STOP THE RELEASE OF GAS. FIELD OPERATOR ISOLATED VALVE BDS-2 WITHOUT AFFECTING NORMAL OPERATIONS. ROOT CAUSE INVESTIGATION FOUND A FAILED O-RING IN THE PILOT CHAMBER SERVING THE BIFFI VALVE OPERATOR ON VALVE BDS-2. THE FAILED O-RING ALLOWED REVERSING GAS TO ENTER THE POWER SIDE OF THE CONTROLLER THEREBY UNINTENTIONALLY OPENING VALVE BDS-2, RELEASING GAS TO ATMOSPHERE. IN ORDER TO PREVENT RECURRENCE TGP STAFF DISCUSSED THE O-RING FAILURE INVESTIGATION WITH THE PILOT VENDOR. THE VENDOR SUGGESTED INSTALLING A CHECK VALVE AT THE VALVE PILOT TO PREVENT UNINTENTIONAL REVERSING GAS PRESSURE IN THE EVENT OF AN O-RING FAILURE. ALSO KNOWING THAT COMPRESSOR STATION 114 HAD SIMILAR STATION PILOT VALVES INSTALLED AT THE STATION, TGP STAFF WILL BE ASSESSING THE OTHER PILOT VALVES AND WILL INSTALL CHECK VALVES AS APPLICABLE. TGP STAFF WILL MODIFY THE STATION'S ESD SYSTEM TESTING PROCEDURE TO INCLUDE REVERSING GAS SUPPLY VALVES AND FUNCTIONALITY AND WILL REVIEW STATION CONTROLS AND ALARMS WITH CONSIDERATION OF APPROPRIATE CALL-OUT STATUS FOR OPEN VENT AND BLOWDOWN VALVES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210073 | 35778 | 2021-08-25 13:50 | SUPPLEMENTAL FINAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2021-07-27 21:47 | 2021 | CENTRAL | NO | 31.9492 | -103.1086 | 1311976 | 2021-07-27 22:52 | 1312067 | NATURAL GAS |  | 6560 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PLANT WAS PREVIOUSLY DOWN DUE TO LOSS OF COMMERCIAL POWER |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-07-27 21:20 | 2021-07-27 21:20 | ONSHORE | TX | 79745 | KERMIT | WINKLER | NOT APPLICABLE |  | EPNG KEYSTONE COMPRESSOR STATION | EPNG KEYSTONE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1992 | 1991 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE | CLASS 1 LOCATION | NO |  | 462 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 28208 | 28208 | 3912 | 3990.827868852460128 | 0 | 0 | 0 | 0 |  | 4.3 | 32120 | 20269.1718384074952354285714285714285714 | 32198.827868852460128 | 0 | 0 | 0 | 0 | NO |  |  |  | 668 | 465000 | 580 | 192.619(A)(1) |  | 2005-11-04 | NO | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [22 empty] | YES | [173 empty] | BALARK CHETHAN | PIPELINE ENGINEER | balark_chethan@kindermorgan.com | 832-920-2845 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING COMPLIANCE CODES STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON JULY 27, 2021 AT 20:30 (CST), THE EL PASO NATURAL GAS (EPNG), KEYSTONE COMPRESSOR (KC) STATION LOST COMMERCIAL POWER. AT THE SAME TIME, THE KC STATION EXPERIENCED HIGH INLET PRESSURE FROM LINES 3026 AND 1105. SINCE THIS IS A MANNED STATION, OPERATORS BEGAN CLOSING BLOCK VALVES ON THE 3026 LINE AND 1105 LINE IN ORDER TO ISOLATE THE COMPRESSOR STATION. THE 3026 LINE BLOCK VALVE (MLV 2) WAS THE FIRST VALVE CLOSED AT 21:20 PM, WHICH RESULTED IN THE ACTIVATION OF MULTIPLE RELIEF VALVES PV 13, PV 14 AND PV 15. ONCE THE PRESSURE RELIEF VALVES VENTED, THE NEXT STEP THAT WAS TAKEN WAS TO CLOSE THE 1105 LINE BLOCK VALVE (MLV 0). HOWEVER, ONE OF THE THREE PRVS CONTINUED TO VENT AND IT WAS DISCOVERED THAT THE VALVE SPRING WAS BROKEN AND FAILED TO RESET. THIS RESULTED IN THE 3026 AND 1105 LINE BEING VENTED FLAT AND A GAS LOSS OF 164 MCF. AT 21:24, THE 2-STAGE VALVE THAT KEEPS THE PLANT A DISCHARGE GAS CONTAINED OPENED DUE TO UTILITY AIR BLEEDING. THIS RESULTED IN THE PLANT A DISCHARGE FEEDING BOTH THE PLANT A AND PLANT B SUCTION LINES, WHICH RESULTED IN ACTIVATION OF PSV 45. AT 21:30 THE EMERGENCY RESPONSE LINE (ERL) WAS ACTIVATED AND THE INCIDENT WAS DEEMED REPORTABLE. THE 2-STAGE VALVE WAS CLOSED AT 21:53 AND COMMERCIAL POWER WAS RESTORED TO THE STATION AT 22:45. THE KC STATION RETURNED TO NORMAL OPERATIONS AT 00:00 AM. THE FIRST RELEASE POST-ACCIDENT INVESTIGATION REVEALED THAT THE ROOT CAUSE OF THE ACTIVATION OF PV 13, PV 14 AND PV 15 WAS CLOSING THE 3026 LINE BLOCK VALVE BEFORE CLOSING THE 1105 LINE BLOCK VALVE. IT WAS LATER DETERMINED THE 1105 LINE WAS HOLDING A HIGHER PRESSURE. THIS COUPLED WITH THE MALFUNCTIONING OF THE PRESSURE RELIEF VALVES RESULTED IN THE LOSS OF 164 MCF. SUBSEQUENTLY, THE RELIEF VALVES HAS SINCE BEEN REPLACED AND REPAIRED. CHANGES TO THE LOCAL STATION PROTOCOL REGARDING THE ISOLATION OF THE STATION WERE INCORPORATED IN ORDER TO IDENTIFY THE LINE WITH THE HIGHEST PRESSURE BEFORE STARTING THE ISOLATION PROCESS. THE SECOND RELEASE POST-INCIDENT INVESTIGATION REVEALED THE ROOT CAUSE OF THE PV 45 ACTIVATING WAS THE LACK OF UTILITY AIR TO THE 2-STAGE VALVE DUE TO LOSS OF COMMERCIAL POWER. THE 2 STAGE VALVE OPENING WAS THE CAUSE OF THE MAOP EXCEEDANCE RESULTING IN PV 45 ACTIVATION. PV 45 PROTECTS THE SUCTION LINE INTO BOTH PLANT A AND PLANT B. THE SUCTION LINE EXPERIENCED A PRESSURE OF 668 AND HAS AN MAOP OF 580. THE GAS LOSS DUE TO THIS INCIDENT WAS 6,396 MCF. THE 2-STAGE VALVE OPERATION HAS SINCE BEEN MODIFIED FROM AUTOMATIC TO MANUAL AND IS CURRENTLY TAGGED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210074 | 35678 | 2021-08-27 10:42 | ORIGINAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-08-02 13:34 | 2021 | CENTRAL | YES | 32.5978 | -94.6652 | 1312544 | 2021-08-02 14:23 | 1312643, 1312656 | NATURAL GAS |  | 3409 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-02 13:34 | 2021-08-02 18:55 |  | NO |  |  | NO | [11 empty] | 0 | 2021-08-02 13:34 | 2021-08-02 13:34 | ONSHORE | TX | 75605 | Not Within a Municipality | HARRISON | NOT APPLICABLE |  | STATION 388, UNIT NO. 1. | STATION 388 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1974 | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL, COPPER, EPOXY | OTHER | [8 empty] | EMERGENCY BLOWDOWN OF NATURAL GAS FROM COMPRESSOR STATION. | CLASS 1 LOCATION | NO |  | 756 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 10769 | 10769 | 500 | 510.075136612022 | 0 | 0 | 0 | 0 | NONE APPLICABLE. | 3.159 | 11269 | 7291.063820734164945182724252491694352159 | 11279.075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 2337 | 150000 | 3000 | 192.619(A)(2) |  | 1974-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [9 empty] | YES | MATERIAL FAILURE OF FENWAL TEMPERATURE SENSOR. | [13 empty] | YES | [171 empty] | STEPHEN DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-4199 |  | MARK GRANT | mark_grant@kindermorgan.com | 903-736-1076 | JAIME HERNADEZ | DIRECTOR OF ENGINEERING - CODES AND STANDARDS | 281-384-5609 | jaime_hernandez@kindermorgan.com | ON AUGUST 2, 2021 AT APPROXIMATELY 13:34 HOURS LOCAL TIME, NGPL COMPRESSOR STATION 388 EXPERIENCED AN UNPLANNED EMERGENCY SHUTDOWN (ESD) AND RELEASED AN ESTIMATED TOTAL OF 3,409 MCF OF NATURAL GAS TO THE ATMOSPHERE VIA THE ESD VENT STACK. DURING THE EVENT OPERATIONS, PERSONNEL WERE ON SITE WORKING AND CONFIRMED THE RELEASE. OUT OF AN ABUNDANCE OF CAUTION, NGPL NOTIFIED THE NRC OF THE EVENT AT APPROXIMATELY 14:23 HOURS LOCAL TIME (NRC REPORT NO. 1312544) BEFORE CONFIRMATION OF THE RELEASE VOLUME. UPON COMPLETION OF THE INVESTIGATION INTO THE EVENT, NGPL DETERMINED THAT THE ESD OCCURRED WHEN A FENWAL HEAT SENSOR FAILED AND THE ESD SYSTEM FUNCTIONED AS DESIGNED DUE TO THE DEVICE FAILURE. NGPL TESTED THE FENWAL DETECT-A-FIRE (D-A-F) SENSOR AND DISCOVERED AN ELECTRICAL SHORT DEFECT IN THE DEVICE. THE ELECTRICAL SHORT RESULTS IN A "CLOSED" SIGNAL, AND WHEN INTERPRETED BY THE ESD SYSTEM CONTROL LOGIC, WOULD COMMAND A STATION ESD SINCE THE STATION CONTROL LOGIC INTERPRETS A CLOSED SIGNAL AS A RAPID TEMPERATURE INCREASE, I.E., A FIRE BY THE ESD LOGIC. THEREFORE, THE STATION ESD SYSTEM TRIPPED AND VENTED THE STATION. NGPL REPLACED THE DEFECTIVE HEAT SENSOR. TO AVOID A REOCCURRENCE OF THIS TYPE OF EVENT, NGPL PLANS TO REPLACE THE STATION HEAT SENSORS AT A MINIMUM OF EVERY 10-YEARS AT THIS STATION OR REPLACE WITH SOME OTHER TYPE OF HEAT-SENSING DEVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210075 | 35679 | 2021-08-27 11:20 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-08-02 15:56 | 2021 | CENTRAL | NO | 33.45 | -88.3609 | 1312563 | 2021-08-02 16:40 | 1312639 | NATURAL GAS |  | 11236 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-08-02 15:55 | 2021-08-02 07:00 | ONSHORE | MS | 39702 | Not Within a Municipality | LOWNDES | NOT APPLICABLE |  | STATION 546 | STATION 546 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1959 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | MECHANICAL MALFUNCTION OF STATION SIDE-GATE VALVE. | CLASS 3 LOCATION | NO |  | 760 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 35495 | 35495 | 1000 | 1020.150273224044 | 500 | 510.075136612022 | 0 | 0 |  | 3.159 | 36995 | 23964.985482136049652823920265780730897 | 37025.225409836066 | 0 | 0 | 0 | 0 | NO |  |  |  | 875 | 0 | 936 | 192.619(A)(1) |  | 1964-12-28 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | YES | PIPELINE DEBRIS CLOGGING INLET FILTER TO SIDE-GATE ACTUATOR PREVENTING CLOSURE. | [22 empty] | YES | ELECTRICAL SHORT IN ESD SOLENOID CAUSED BY AN ELECTRICAL STORM. | [161 empty] | STEPHEN DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-4199 |  | JAY STREET | jay_street@kindermorgan.com | 662-574-6922 | JAIME HERNANDEZ | DIRECTOR OF ENGINEERING - CODES AND STANDARDS | 281-384-5609 | jaime_hernandez@kindermorgan.com | ON AUGUST 2, 2021 AT 15:55 LOCAL TIME, TGP STATION 546 UNDERWENT AN EMERGENCY SHUTDOWN (ESD) THAT OCCURRED WHILE THE STATION WAS OFFLINE RESULTING IN THE RELEASE OF NATURAL GAS EXCEEDING THE PHMSA REPORTING THRESHOLD DUE TO NEARBY PIPELINE MAINTENANCE. TGP STATION PERSONNEL ON SITE DURING THE EVENT CONFIRMED THE GAS RELEASE AT 15:55 LOCAL TIME AND AT 16:30, TGP CONFIRMED THE RELEASE EXCEEDED THREE (3) MMSCF AFTER THE STATION ESD SIDE GATE FAILED TO CLOSE DURING THE EVENT. ALL NATURAL GAS SAFELY DISCHARGED TO THE ATMOSPHERE THROUGH THE STATION VENT STACK AT THE STATION. TGP NOTIFIED THE NRC OF THE RELEASE AT 16:40 LOCAL TIME. THE INVESTIGATION REVEALED THAT THE ESD SOLENOID CONTAINED AN INTERNAL SHORT THAT CAUSED THE STATION TO ESD. TGP IDENTIFIED THE ROOT CAUSE OF THE SHORT TO BE AN ELECTRICAL SURGE SUSPECTED TO HAVE ORIGINATED DUE TO A RECENT ELECTRICAL STORM THAT CAUSED THE ESD. TGP ALSO IDENTIFIED THAT THE STATION SIDE-GATE VALVE REMAINED SLIGHTLY OPEN AFTER THE ESD RESULTING IN EXCEEDING THE PHMSA REPORTING THRESHOLD FOR AN UNINTENDED GAS RELEASE. TGP'S INVESTIGATION FOUND THAT PIPELINE DEBRIS WAS PRESENT IN THE SIDE-GATE VALVE ACTUATOR. TGP REPLACED THE DAMAGED SOLENOID AND CLEANED ALL DEBRIS FROM THE SIDE-GATE VALVE INLET FILTERS. THE STATION BECAME AVAILABLE FOR SERVICE ON AUGUST 6, 2021.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210077 | 36422 | 2021-09-07 11:08 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2021-08-09 15:18 | 2021 | CENTRAL | NO | 32.5258 | -86.9301 | 1313231 | 2021-08-09 16:34 | 1313359 | NATURAL GAS |  | 5722.17 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-09 16:15 |  | YES | NO |  |  | YES | 2021-08-09 15:18 | ALLOWED TO BURN OUT |  | 5722.17 | NO | [6 empty] | 0 | 2021-08-09 15:18 | 2021-08-09 16:00 | ONSHORE | AL | 36703 | Not Within a Municipality | DALLAS | NOT APPLICABLE |  | SNG SELMA METER STATION 2 | SNG SELMA METER STATION 2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1965 | 1965 | CARBON STEEL |  | OTHER | [8 empty] | RELEASE OF FUEL DUE TO HIGH ENERGY EXTERNAL EVENT, SUCH AS LIGHTNING STRIKE | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 25178 | 25178 | 956600 | 975875.7513661204904 | 5000 | 5100.75136612022 | 0 | 0 |  | 4.4 | 986778 | 449289.7108000656239043189368770764119601 | 1006154.5027322407104 | 0 | 0 | 0 | 0 | NO |  |  |  | 927 | 4797 | 1200 | 192.619(A)(1) |  | 1966-11-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | CUSTOMER CALLED GAS CONTROL AT 15:18 |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DEEMED INDEPENDENT FROM THE CONTROLLER'S ACTIONS | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | YES |  |  |  | YES | LIGHTNING STORM IN THE AREA | [301 empty] | BALARK CHETHAN | PIPELINE ENGINEER | balark_chethan@kindermorgan.com | 713-420-5629 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 15:18 CST ON 8/9/2021, SOUTHERN NATURAL GAS (SNG) GAS CONTROL WAS NOTIFIED OF A FIRE BY A CUSTOMER AT THE SELMA #2 METER STATION IN SELMA, AL. THE CUSTOMER NOTIFIED EMERGENCY RESPONDERS ABOUT THE INCIDENT AT THE SITE. AT 15:19 SNG GAS CONTROL DISPATCHED EMPLOYEES TO THE SITE OF THE FIRE. TWO SNG OPERATIONS EMPLOYEES RESPONDING TO THE INCIDENT ARRIVED AT THE STATION AT 16:00 AND IMMEDIATELY BEGAN ISOLATING THE FACILITY. AT 16:02, VALVE 49 AND VALVE 50, WHICH ARE THE INLET BLOCK VALVES TO THE METER STATION, WERE CLOSED, RESULTING IN THE SNG SELMA #2 METER STATION BEING ISOLATED. ONCE THE SNG SELMA #2 METER STATION WAS ISOLATED, THE PRIMARY FIRE SUBSIDED IMMEDIATELY AND WAS ALLOWED TO COMPLETELY BURN OUT. AT 16:10 AN EMERGENCY RESPONSE LINE (ERL) CALL WAS INITIATED TO SUPPORT THE EMERGENCY RESPONSE. SMALL RESIDUAL FIRES CONTINUED AND BURNED OUT AT 18:00. THE INCIDENT WAS DEEMED SIGNIFICANT PER 49 CFR PART 191.3, THEREFORE REPORTABLE TO PHMSA. THE FIRE BURNED DOWN THE SNG METER STATION, AND FOLLOWING INTERNAL AND THIRD PARTY INVESTIGATIONS OF THE INCIDENT, THE CAUSE OF THE FIRE WAS DETERMINED TO BE A SECONDARY LIGHTNING STRIKE IN THE AREA. DURING THE INVESTIGATION, SNG WAS PROVIDED WITH A PHOTOGRAPH FROM THE CUSTOMER WITH A TIME STAMP OF 15:13 SHOWING SMALL FLAMES IN THE VICINITY OF THE METER STATION. THE THIRD PARTY INVESTIGATION CONCLUDED THAT THE FIRE ORIGINATED OUTSIDE OF THE SNG REGULATOR BUILDING. SNG HAS COMPLETED THEIR REBUILD OF THE METER STATION. IN ORDER TO PREVENT REOCCURRENCE, SNG HAS INSTALLED LIGHTNING ARRESTORS AT THE METER STATION AND RELOCATED THE STATION FURTHER FROM THE CUSTOMER'S FACILITY. THE METER STATION IS CURRENTLY OFFLINE AS SNG IS WAITING FOR THE CUSTOMER TO COMPLETE THEIR PROJECT REBUILDING THE DOWNSTREAM CONNECTION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210078 | 37110 | 2021-09-08 23:35 | SUPPLEMENTAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2021-08-09 15:15 | 2021 | CENTRAL | NO | 32.5258 | -86.9301 | 1313235 | 2021-08-09 16:30 | 1313381 | NATURAL GAS |  | 40 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-09 17:00 |  | YES | YES | OPERATOR | 2021-08-09 15:15 | YES | 2021-08-09 15:15 | ALLOWED TO BURN OUT |  | 40 | NO | [6 empty] | 0 | 2021-08-09 15:15 | 2021-08-09 15:15 | ONSHORE | AL | 36701 | SELMA | DALLAS | NOT APPLICABLE |  | SELMA #2 STATION | SELMA #2 FEEDER - SE-A1 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | ODORIZATION SYSTEM | [38 empty] | 1966 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 84 | 36 |  | CLASS 1 LOCATION | NO |  | 170 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 473 | 473 | 491000 | 500893.784153005604 | 2000 | 2040.300546448088 | 0 | 0 |  | 11.82 | 493473 | 222185.6132903982638571428571428571428571 | 503407.084699453692 | 0 | 0 | 0 | 0 | NO |  |  |  | 502.8 | 0 | 600 | 192.619(A)(1) |  | 1966-08-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR WAS ALREADY ONSITE WHEN THE FIRE FROM KINDER MORGAN'S BORDER STATION SPREAD TO SPIRE'S STATION/EQUIPMENT. THE CONTROLLERS WERE ALREADY INFORMED OF THE CONDITION. THE RESULTING FIRE EVENTUALLY DAMAGED THE CONTROL TELEMETRY. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [306 empty] | JARED JACKSON | COMPLIANCE ENGINEER | jared.jackson@spireenergy.com | 205-842-3692 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD-PARTY INVESTIGATION OF THIS EVENT DETERMINED THAT A LIGHTNING STRIKE CAUSED A FIRE AT THE NEIGHBORING KINDER MORGAN BORDER STATION FACILITY. THE FIRE SPREAD TO CAUSE SECONDARY DAMAGE TO THE SPIRE BORDER STATION FACILITIES AND A RELEASE OF GAS FROM CONNECTED SENSING PIPELINES. THE ENTIRE BORDER STATION IS BEING REPLACED DUE TO THIS EVENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210079 | 35790 | 2021-09-11 17:24 | SUPPLEMENTAL FINAL | 18508 | SOUTHERN INDIANA GAS & ELECTRIC CO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2021-09-09 16:10 | 2021 | CENTRAL | YES | 38.0239 | -87.8165 | 1316330 | 2021-09-10 07:42 |  | NATURAL GAS |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-09 16:10 |  | YES | YES | OPERATOR | 2021-09-09 16:00 | NO | [11 empty] | 0 | 2021-09-09 16:00 | 2021-09-09 16:00 | ONSHORE | IN | 47620 | Not Within a Municipality | POSEY | NOT APPLICABLE |  | OLIVER NATURAL GAS STORAGE FIELD | N/A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | COMPRESSOR BUILDING | 1954 | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | SEE PART H - NARRATIVE | OTHER | [8 empty] | NO RELEASE OF NATURAL GAS. | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | YES | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 23000000 | 23463456.284153012 | 100000 | 102015.0273224044 | 0 | 0 |  | 0 | 23100000 | 10396183.4016393507 | 23565471.3114754164 | 0 | 0 | 0 | 0 | NO |  |  |  | 500 | 0 | 0 | 192.619(A)(1) |  | 1954-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE COMPRESSOR BUILDING CAUGHT FIRE - NOT THE COMPRESSOR OR PIPING MONITORED BY THE CONTROLLERS. | [12 empty] | YES | 3 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | UPDATED: COMPRESSOR BUILDING CAUGHT FIRE. PER THIRD PARTY FIRE INVESTIGATOR, "FIRE ORIGIN WAS IN THE NORTHEAST UPPER SECTION OF THE BUILDING, AND INVOLVES THE COOLING OIL COMING IN CONTACT WITH A HOT SURFACE; EITHER THE LIGHT FIXTURE OR THE EXHAUST SYSTEM IN THE NORTHEAST UPPER SECTION OF THE STRUCTURE. THE ELECTRICAL SYSTEM AND NATURAL GAS ARE ELIMINATED AS BEING INVOLVED WITH IGNITION OR CAUSE." | [145 empty] | SCOTT CHANDLER | OPERATIONS SPECIALIST | scott.chandler@centerpointenergy.com | 812-491-4117 |  | SCOTT CHANDLER | scott.chandler@centerpointenergy.com | 812-491-4117 | SHANE ALEXANDER | MANAGER PIPELINE SAFETY AND COMPLIANCE | 3177183603 | shane.alexander@centerpointenergy.com | TWO STORAGE FIELD TECHS HAD COMPLETED THEIR END OF DAY CHECKS AND WERE IN THE OFFICE DOCUMENTING THE RESULTS (ALL WERE NORMAL) OF THE CHECKS WHEN THE THREE ON-SITE TECHS HEARD A NOISE SIMILAR TO AN EMPTY DUMPSTER BEING SET DOWN. THEY WENT TO INVESTIGATE THE NOISE AND SAW THE COMPRESSOR BUILDING ENGULFED IN FIRE. THEY REACTED AND FOLLOWED THEIR EMERGENCY SHUT DOWN PROCEDURE. THE PROCEDURE INCLUDED HITTING THE EMERGENCY STOP BUTTON FOR THE COMPRESSOR, CLOSING VALVES, AND MAKING NOTIFICATIONS. AT NO TIME DID THE TECHS DETECT THE PRESENCE OF NATURAL GAS EITHER VISUALLY NOR DID THEY SMELL ODORANT INDICATING THE PRESENCE OF NATURAL GAS. MEMBERS OF THE RESPONDING FIRE DEPARTMENTS DID NOT DETECT THE PRESENCE OF NATURAL GAS EITHER VISUALLY WHILE FIGHTING THE FIRE NOR DID ANYONE SMELL ODORANT INDICATING THE PRESENCE OF NATURAL GAS. THE FIRE DEPARTMENTS REMAINED ON SITE UNTIL ABOUT 2100HRS. TWO FIRE CHIEFS AND A DISTRICT FIRE CHIEF STATED THEY WERE NOT ABLE TO DETERMINE THE EXACT POINT OF ORIGINATION OF THE FIRE, INITIAL FUEL SOURCE OF THE FIRE, OR THE POINT OF IGNITION. THEY RELEASED THE SCENE BACK TO ON SITE COMPANY PERSONNEL BEFORE DEPARTING. THE STORAGE FIELD TECHS CONDUCTED CHECKS OF JOINTS IN AND AROUND THE COMPRESSOR BUILDING THAT MAY HAVE BEEN IMPACTED BY THE HEAT OF THE FIRE WITH COMBUSTIBLE GAS INDICATOR INSTRUMENTS. GAS WAS NOT DETECTED. CONTACT WAS MADE WITH A THIRD-PARTY FIRE INVESTIGATOR. THE INVESTIGATOR REVIEWED THE COMPRESSOR BUILDING IN PERSON THE MORNING AFTER THE FIRE. THE FIRE INVESTIGATOR WAS NOT ABLE TO DETERMINE THE EXACT POINT OF ORIGINATION OF THE FIRE, INITIAL FUEL SOURCE OF THE FIRE, OR THE POINT OF IGNITION. THE LOSS IS ESTIMATED TO BE A TOTAL LOSS OF THE BUILDING AND POSSIBLY THE TWO COMPRESSORS IN THE BUILDING. NOTE: THE BUILDING IS INTACT. IT IS A STEEL FRAMED BUILDING WITH A SHEET METAL SKIN. THERE IS NO DEBRIS FIELD. WHILE DOORS (THE MAJORITY OF WHICH WERE OPEN) AND WINDOWS WERE DAMAGED, THEY WERE DAMAGED BY THE FIRE ' AS AN EXAMPLE, METAL DOORS SHOWED SIGNS OF WARPING FROM BEING SUPERHEATED AS OPPOSED TO BULGING FROM AN OVERPRESSURE EVENT. GLASS FROM LIGHTS IN DOORS AND WINDOWS WERE ON THE GROUND IN THE IMMEDIATE VICINITY OF THE WINDOW NOT MORE THAN TWO FEET FROM THE BASE OF THE WALL, AGAIN CHARACTERISTIC OF FIRE DAMAGE, NOT OVER PRESSURIZATION. THE COMPRESSORS ARE SKID MOUNTED AND DON'T APPEAR TO HAVE MOVED OR SHIFTED POSITION. THERE DID NOT APPEAR TO BE A SHEEN OF OIL ANYWHERE IN THE BUILDING THAT ANYONE NOTED. THE PAINT ON THE COMPRESSOR THAT WAS RUNNING AT THE TIME OF THE FIRE SHOWS SIGNS OF HEAT DAMAGE BUT OTHERWISE NO SCORCHING INDICATING IT WAS A POTENTIAL SOURCE OF FUEL OR IGNITION. WHAT APPEARS TO BE THE HOTTEST SPOT OF THE FIRE IS IN THE NORTHEAST CORNER OF THE BUILDING ON THE DISCHARGE SIDE OF THE RUNNING COMPRESSOR. IT IS CLOSER TO THE RADIATOR THAN THE COMPRESSOR. ALL WIRING TO THE VARIOUS SENSORS ON THE COMPRESSORS APPEARS TO BE DAMAGED/MELTED AS THE RESULT OF THE FIRE. AT THIS POINT, IT IS TOO EARLY TO DETERMINE IF THE COMPRESSORS AND BUILDING ARE A TOTAL LOSS. THEY WILL HAVE TO BE ASSESSED BY ENGINEERS TO DETERMINE WHAT EXACTLY CAN BE SALVAGED. AT THE TIME THE STORAGE FIELD AND COMPRESSORS WERE PLACED INTO SERVICE (1954), AN ESD WAS NOT REQUIRED BY CODE. PLANS TO INSTALL AN ESD SYSTEM HAD BEEN DISCUSSED WITH THE STATE REGULATORY AGENCY EARLIER IN 2021 AND HAD ADVANCED TO THE COMPLETED ENGINEERING PHASE AND WERE WAITING FOR APPROVAL AND AUTHORIZATION. GAS CONTROL AND THE STORAGE FIELD TECHS CAN OPERATE VALVES TO BYPASS THE COMPRESSOR BUILDING TO FEED EITHER THE STORAGE FIELD OR THE DISTRIBUTION SYSTEMS. THESE COMPRESSOR/STORAGE FIELD FACILITIES ARE NOT THE SOLE SOURCE OF GAS TO THE DISTRIBUTION SYSTEMS IT AUGMENTED.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20210080 | 37345 | 2021-09-14 15:54 | SUPPLEMENTAL | 4280 | EL PASO NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002-5089 | 2021-08-15 05:29 | 2021 | MOUNTAIN | NO | 32.9222 | -111.4977 | 1313733 | 2021-08-15 06:24 | 1313743, 1313836, 1313903, 1313932 | NATURAL GAS |  | 202996 | 0 | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-15 05:52 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-08-15 06:02 | YES | 2021-08-15 05:29 | ALLOWED TO BURN OUT |  | 202996 | YES | VALVE CLOSURE |  | 2021-08-15 08:15 | VALVE CLOSURE |  | 2021-08-15 06:29 | 0 | 2021-08-15 05:36 | 2021-08-15 06:29 | ONSHORE | AZ | 85128 | COOLIDGE | PINAL | MILEPOST | 497 | L2000 | MCCAMEY TO EHRENBERG | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 30 |  | 0.281 | 70000 | API 5L | DSAW |  | UNKNOWN | OTHER | UNDER INVESTIGATION | YES | [26 empty] | 1986 | 1985 | CARBON STEEL |  | OTHER | [8 empty] | UNDER NTSB INVESTIGATION | CLASS 1 LOCATION | NO |  | 636 |  | NO | NO | NO |  | NO |  |  | 3000000 | 3060450.819672132 | 0 | 0 | 832284 | 832284 | 1690106 | 1724162.097677596108664 | 19350 | 19739.9077868852514 | 0 | 0 |  | 4.1 | 5541740 | 2665596.42989216404870575415282392026578 | 5636636.825136613360064 | 0 | 0 | 1 | 0 | NO |  |  |  | 863 | 550000 | 944 | OTHER | PIPE SEGMENT UNDER NTSB INVESTIGATION | 2002-11-08 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 100742 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | OTHER | NTSB IS INVESTIGATING THE INCIDENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER'S ACTIONS, NTSB IS INVESTIGATING THE INCIDENT | [12 empty] | YES | 2 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | NONE | 1273 | [54 empty] | YES | YES | YES |  | YES |  |  | YES | 2016 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2009 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2021 | FREE SWIMMING | HIGH RESOLUTION | [17 empty] | 2016 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2009 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [8 empty] | IMU | 2016 | FREE SWIMMING |  |  |  | YES | 2002 | 1212 | NO | [13 empty] | NO | [63 empty] | BALARK CHETHAN | PIPELINE ENGINEER | balark_chethan@kindermorgan.com | 8329202845 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | PER THE NTSB PRELIMINARY REPORT POSTED 9/21/21: "ON AUGUST 15, 2021, ABOUT 5:29 A.M. LOCAL TIME, PIPELINE (LINE) 2000, A 30-INCH DIAMETER NATURAL GAS TRANSMISSION PIPELINE OWNED AND OPERATED BY KINDER MORGAN, INC. (KINDER MORGAN) RUPTURED IN A RURAL AREA IN COOLIDGE, ARIZONA. THE FAILURE RESULTED IN AN EXPLOSION, FIRE, AND EJECTION OF A 46-FOOT SECTION OF THE PIPELINE. A HOME NEAR THE INTERSECTION OF E RANDOLPH ROAD AND N VAIL ROAD WAS DESTROYED BY THE EXPLOSION AND SUBSEQUENT FIRE, RESULTING IN TWO FATALITIES AND ONE INJURY. SHORTLY AFTER THE RUPTURE, THE KINDER MORGAN'S COLORADO SPRINGS CONTROL CENTER OBSERVED A PRESSURE DECREASE THROUGH ITS SUPERVISORY CONTROL AND DATA ACQUISITION SYSTEM AND CONTACTED FIELD PERSONNEL TO ISOLATE THE AFFECTED PIPELINE SEGMENT. ABOUT THE SAME TIME, THE CONTROL CENTER RECEIVED A REPORT OF THE FIRE FROM A NEARBY POWER PLANT. ISOLATION OF THE AFFECTED SEGMENT REQUIRED CLOSING TWO MANUALLY OPERATED VALVES, ONE UPSTREAM AND ONE DOWNSTREAM OF THE RUPTURE. KINDER MORGAN FIELD PERSONNEL MANUALLY ISOLATED THE NEAREST DOWNSTREAM VALVE ABOUT 1 HOUR AFTER THE RUPTURE BUT HAD DIFFICULTY ACCESSING THE NEAREST UPSTREAM VALVE. THE NEAREST UPSTREAM WAS ISOLATED ABOUT 2 1/2 HOURS AFTER THE RUPTURE, AND THE FIRE WAS EXTINGUISHED AT 8:08 A.M." THE NTSB IS CONTINUING TO INVESTIGATE THE INCIDENT. THE RECORDED PRESSURE NEAREST THE INCIDENT SITE WAS 830 PSIG. EPNG CALCULATED THE PRESSURE AT THE TIME AND PLACE OF THE INCIDENT TO BE 863 PSIG. THE PIPE INVOLVED WAS 30" OD, 0.281 WALL THICKNESS, AND SMYS OF 70,000. PER THE NTSB PIPELINE OPERATIONS AND INTEGRITY MANAGEMENT FACTUAL REPORT POSTED ON 9/15/2022: THE NTSB "EXAMINATION FOUND EVIDENCE OF MULTIPLE COLONIES OF LONGITUDINAL CRACKS CONSISTENT WITH STRESS CORROSION CRACKING (SCC) NEAR THE LONGITUDINAL SEAM"; ADDITIONALLY, "THE NTSB MATERIALS LABORATORY OBSERVED INDICATORS OF HIGH PH SCC AT THE RUPTURE ORIGIN".
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210081 | 35866 | 2021-09-16 08:52 | SUPPLEMENTAL FINAL | 2714 | EASTERN GAS TRANSMISSION AND STORAGE, INC. | 925 WHITE OAKS BOULEVARD | BRIDGEPORT | WV | 26330 | 2021-08-18 23:22 | 2021 | EASTERN | NO | 42.0735 | -77.3918 | 1314115 | 2021-08-19 00:34 | 1314191 | NATURAL GAS |  | 8100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-19 | 2021-09-15 11:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-08-18 23:00 | VALVE CLOSURE |  | 2021-08-19 | 0 | 2021-08-18 21:37 | 2021-08-18 22:15 | ONSHORE | NY | 14898 | WOODHULL | STEUBEN COUNTY | SURVEY STATION NO. | 60+95 | WP00695D1 DRIP BLOWDOWN | LN-695 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 2015 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | 1 INCH NIPPLE WAS DETACHED | [5 empty] | CLASS 1 LOCATION | NO |  | 425 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 23571 | 23571 | 5000 | 5100.75136612022 | 1000 | 1020.150273224044 | 0 | 0 |  | 2.91 | 29571 | 18166.3289717335673820598006644518272425 | 29691.901639344264 | 0 | 0 | 0 | 0 | NO |  |  |  | 1734 | 0 | 2160 | 192.619(A)(2) |  | 2015-05-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 10451 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [52 empty] | HEAVY RAINS/FLOODS |  | FLOTATION |  |  |  | YES |  |  |  | YES | SEVERE FLASH FLOODING | [289 empty] | YES | [11 empty] | DANIEL STAHL | PIPELINE INTEGRITY ENGINEER | daniel.stahl@bhegts.com | 681-842-3365 |  | TERRY MASCHO | terry.mascho@bhegts.com | 814-367-7612 | MICHAEL FERGUSON | MANAGER - PIPELINE INTEGRITY | 803-888-3477 | michael.ferguson@bhegts.com | GAS CONTROL RECEIVED INITIAL NOTIFICATION OF THIS INCIDENT ON 8/18/21 AT 21:37 FROM A HOMEOWNER WHO REPORTED THAT A RELEASE OF GAS WAS AUDIBLE IN THE AREA NEAR A DRIP (WD00695D1) INSTALLED ON LN-695 BETWEEN COUNTY ROAD 129 AND TUSCARORA CREEK IN WOODHULL, NEW YORK. LN-695 IS A TRANSMISSION PIPELINE IN A STORAGE FUNCTION AND HAS A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 2160 PSIG. AT THE TIME OF THE INCIDENT, THE OPERATING PRESSURE ON LN-695 WAS 1734 PSIG AND LN-695 WAS NOT FLOWING GAS. PROTECTION FOR THE ABOVEGROUND PORTIONS OF WD00695D1 FROM OUTSIDE FORCES WAS PROVIDED BY THREE CONCRETE JERSEY BARRIERS THAT WERE INSTALLED WHEN WD00695D1 WAS INSTALLED IN 2015. THE RESPONSE TO THIS INCIDENT WAS COMPLICATED BY THE PREVAILING WEATHER CONDITIONS. AT THE TIME OF THE INCIDENT, STEUBEN COUNTY WHICH CONTAINS WOODHULL, WAS EXPERIENCING SEVERE FLASH FLOODING SPECIFICALLY IN AREAS NEAR TUSCARORA CREEK AND A STATE OF EMERGENCY WAS DECLARED FOR STEUBEN COUNTY BY THE STATE OF NEW YORK ON 8/18/21. GAS CONTROL CONTACTED OPERATIONS MANAGEMENT ON 8/18/21 AT 21:40 AND COMMUNICATED THE INFORMATION THAT WAS RECEIVED FROM THE HOMEOWNER. OPERATIONS MANAGEMENT DISPATCHED OPERATIONS PERSONNEL TO THE SITE TO INVESTIGATE ON 8/18/21 AT 21:45. OPERATIONS PERSONNEL ARRIVED AT THE SITE ON 8/18/21 AT APPROXIMATELY 22:15 AND OBSERVED THAT THE RELEASE OF GAS WAS COMING FROM WD00695D1. AT THIS TIME, IT WAS BELIEVED THAT THE RELEASE OF GAS WAS COMING FROM THE DRIP STINGER ON WD00695D1. IT WAS LATER CONFIRMED THAT THE RELEASE OF GAS WAS COMING FROM A 1 INCH NIPPLE THAT HAD BEEN DETACHED FROM THE DRIP BLOWOFF ON WD00695D1 BY FLOATING DEBRIS THAT WAS ADRIFT AS A RESULT OF THE FLOODING OF TUSCARORA CREEK. OPERATIONS PERSONNEL CONTACTED OPERATIONS MANAGEMENT AND COMMUNICATED THE SITUATION. OPERATIONS PERSONNEL BEGAN ISOLATING THE SECTION OF LN-695 CONTAINING WD00695D1 BY CLOSING MANUAL VALVES ON LN-695 UPSTREAM AND DOWNSTREAM OF WD00695D1 AND CLOSING MANUAL VALVES AT THE CONNECTIONS BETWEEN LN-695 AND OTHER TRANSMISSION PIPELINES IN STORAGE FUNCTIONS. OPERATIONS PERSONNEL COMPLETED ISOLATING THE SECTION OF LN-695 CONTAINING WD00695D1 ON 8/19/21 AT APPROXIMATELY 00:00. OPERATIONS PERSONNEL CONTACTED OPERATIONS MANAGEMENT AND COMMUNICATED THE SITUATION. IT WAS DETERMINED ON 8/19/21 AT 00:32 THAT THE INCIDENT LIKELY INVOLVED AN UNINTENTIONAL ESTIMATED GAS LOSS OF THREE MILLION CUBIC FEET OR MORE WHICH WOULD CLASSIFY IT AS REPORTABLE INCIDENT. INITIAL TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER ON 8/19/21 AT 00:34. THE NATIONAL RESPONSE CENTER ASSIGNED INCIDENT REPORT 1314115 TO THE INITIAL NOTIFICATION OF THE INCIDENT. A FOLLOW UP TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER ON 8/19/21 AT 17:13 TO CONFIRM THE INITIAL TELEPHONIC NOTIFICATION, UPDATE THE CAUSE OF THE INCIDENT, AND UPDATE THE VOLUME OF UNINTENTIONAL ESTIMATED GAS LOSS. THE NATIONAL RESPONSE CENTER ASSIGNED INCIDENT REPORT #131491 TO THE FOLLOW UP TELEPHONIC NOTIFICATION. THE FOLLOWING REMEDIAL ACTIONS WERE COMPLETED: THE UNDERGROUND PORTION OF WD00695D1 WAS EXCAVATED, INSPECTED FOR ADDITIONAL DAMAGE, AND A SHORT SECTION OF PIPE THAT HAD BEEN BENT BY THE FLOATING DEBRIS WAS CUT OUT AND REPLACED; A REPLACEMENT 1 INCH NIPPLE WAS INSTALLED ON THE DRIP BLOWOFF ON WD00695D1; UPGRADED BARRIERS WERE INSTALLED TO PROVIDE ENHANCED PROTECTION FOR THE ABOVEGROUND PORTIONS OF WD00695D1 FROM OUTSIDE FORCES. FOLLOWING COMPLETION OF THE REMEDIAL ACTIONS, THE SECTION OF LN-695 CONTAINING WD00695D1 WAS RETURNED TO SERVICE ON 9/15/21 AT 11:00 BY OPENING THE MANUAL VALVES ON LN-695 UPSTREAM AND DOWNSTREAM OF WD00695D1 AND OPENING THE MANUAL VALVES AT THE CONNECTIONS BETWEEN LN-695 AND OTHER TRANSMISSION PIPELINES IN STORAGE FUNCTIONS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210082 | 36063 | 2021-09-21 17:19 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-08-31 20:05 | 2021 | CENTRAL | YES | 36.6168 | -100.4296 | 1315304 | 2021-08-31 22:00 | 1315591 | NATURAL GAS |  | 32000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-31 20:00 | 2021-08-31 20:45 |  | NO |  |  | NO | [11 empty] | 0 | 2021-08-31 20:00 | 2021-08-31 20:40 | ONSHORE | OK | 73844 | Not Within a Municipality | BEAVER | NOT APPLICABLE |  | BEAVER COMPRESSOR STATION | BEAVER COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | ESD OF THE STATION. | CLASS 1 LOCATION | NO |  | 693 |  | NO | NO |  |  | YES |  | YES | 0 | 0 | 0 | 0 | 132800 | 132800 | 2500 | 2550.37568306011 | 2480 | 2529.97267759562912 | 0 | 0 |  | 4.15 | 137780 | 89377.4677475355386679734219269102990033 | 137880.34836065573912 | 0 | 0 | 0 | 0 | NO |  |  |  | 610 | 0 | 1000 | 192.619(C) |  | 1967-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS NOT CAUSED BY THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | FIRE DETECTION ALARM | [16 empty] | YES | [153 empty] | YES | [12 empty] | JEFFREY CULLISON |  | j.cullison@nngco.com | 4023987439 |  |  |  |  | TOM CORRELL |  | 4023987715 | thomas.correll@nngco.com | ON AUGUST 31, 2021, AT 2000 HOURS THE BEAVER COMPRESSOR STATION EXPERIENCED AN UNPLANNED EMERGENCY SHUTDOWN (ESD). THE ESD WAS INITIATED BY FIRE DETECTION HEAD 14B WHICH IS ABOVE DCP UNIT 14. THE AMOUNT OF GAS THAT VENTED CAUSED THE EVENT TO REACH THE REPORTING THRESHOLD AT 2005 HOURS. THE DETECTION HEAD WAS REPLACED AND TESTED BEFORE THE DCP UNIT 14 WAS RETURNED TO SERVICE. DET-TRONICS REVIEWED THE FIRE DETECTOR HEAD AND DETERMINED THAT THE HEATING ELEMENT MALFUNCTIONED AND REMAINED ON CONTINUOUSLY, CAUSING THE DEVICE TO OVERHEAT AND ULTIMATELY FAIL.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20210083 | 35935 | 2021-09-21 17:25 | SUPPLEMENTAL FINAL | 32296 | TARGA RESOURCES OPERATING LLC | 811 LOUISIANA ST SUITE 2100 | HOUSTON | TX | 77002 | 2021-08-20 08:26 | 2021 | CENTRAL | YES | 29.578 | -93.1509 | 1314223 | 2021-08-20 10:13 |  | NATURAL GAS |  | 17 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | VALVES HAD BEEN PREVIOUSLY CLOSED IN PREPARATION FOR PIPELINE DECOMMISSION. |  | OPERATIONAL CONTROL | VALVES HAD BEEN PREVIOUSLY CLOSED IN PREPARATION FOR PIPELINE DECOMMISSION. |  | 0 | 2021-08-20 08:26 | 2021-08-20 08:26 | OFFSHORE | [6 empty] | SEAHAWK | WC72 TO 71 | [20 empty] | 45 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 71 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 | NO | 0.375 | 42000 | API-5X | SEAMLESS |  | UNKNOWN | OTHER | CONCRETE. | UNKNOWN | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 310 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 68 | 68 | 219810 | 224239.23155737711164 | 0 | 0 | 0 | 0 |  | 4 | 219878 | 98970.3786983961181181727574750830564784 | 224307.23155737711164 | 0 | 0 | 0 | 0 | NO |  |  |  | 15 | 0 | 1235 | OTHER | 192.11 | 1997-04-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 10044 | NO | [5 empty] | YES | SUBSEA TIE-INS. | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | NO |  |  |  |  | OTHER | REPORT FROM FIELDWOOD ENERGY |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  |  | YES | [5 empty] | YES |  |  |  | YES | YES | 1997 | NO | YES | YES |  |  |  | 2020 |  |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIM HUFFER | MANAGER OPERATIONAL DISCIPLINE | thuffer@targaresources.com | 3375835257 | 3375834630 | TIM HUFFER | thuffer@targaresources.com | 3375835257 | TIM HUFFER | MANAGER OPERATIONAL DISCIPLINE | 3375835257 | thuffer@targaresources.com | FIELDWOOD ENERGY IDENTIFIED A LIQUID HYDROCARBON LEAK PRODUCING A SMALL SHEEN IN THE VICINITY OF ITS PIPELINE. FIELDWOOD'S PIPELINE IS IN CLOSE PROXIMITY TO TARGA'S PIPELINE. FIELDWOOD WAS UNDER THE ASSUMPTION THAT THE LEAK WAS ORIGINATING FROM THEIR LINE AND BEGAN THE PROCESS OF RESPONDING AN REPAIRING THE LEAK. A DIVE BOAT WAS DISPATCHED AND UPON INVESTIGATION DETERMINED THE LEAK ORIGINATED FROM TARGA'S. FIELDWOOD NOTIFIED TARGA THAT THE LEAK WAS FROM TARGA'S PIPELINE. TARGA USED THE DIVE BOAT DISPATCHED ON LOCATION BY FIELDWOOD TO COMPLETE THE REPAIR TO TARGA'S PIPELINE. TARGA'S PIPELINE INVOLVED IN THIS INCIDENT WAS PREVIOUSLY BLOCKED IN AND BLED DOWN AND NOT IN SERVICE AT THE TIME OF THE INCIDENT. PREPARATION WAS UNDERWAY TO DE-COMMISSION AN UPSTREAM PIPELINE CONNECTED TO THIS PIPELINE SEGMENT. THE PIPELINE HAD NOT BEEN PIGGED. CONDENSATE REMAINED IN THE LINE. REPAIR WAS COMPLETED TO THE PIPELINE BY THE INSTALLATION OF A BOLTED-ON CLAMP. THE INCIDENT WAS ATTRIBUTED TO A PIN-HOLE LEAK SO SMALL THAT DAMAGE TO THE CONCRETE COATING WAS UNDISCERNIBLE. ONCE THE CONCRETE COATING WAS REMOVED, THE EXACT LOCATION OF THE PINHOLE LEAK WAS NOT ABLE TO BE IDENTIFIED. PAST PIN-HOLE LEAKS IN THIS GATHERING SYSTEM HAVE BEEN ATTRIBUTED TO MICROBIOLOGICAL CORROSION. WITHOUT REMOVAL OF THE SECTION OF PIPE, DETERMINATION OF THE ROOT CASE CANNOT BE ASCERTAINED WITH CERTAINTY. BUT SINCE THE CONCRETE COATING WAS INTACT WITH NO VISIBLE SIGN OF LOSS OF COATING, THE FAILURE IS ATTRIBUTED TO MICROBIOLOGICAL CORROSION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210084 | 36004 | 2021-09-29 15:58 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-08-19 01:00 | 2021 | EASTERN | YES | 41.8535 | -78.001 | 1315256 | 2021-08-31 13:27 | 1315344 | NATURAL GAS |  | 72768 | 9 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | VALVE WAS CLOSED TO TERMINATE UNINTENTIONAL RELEASE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-08-30 20:30 | 2021-08-30 19:00 | ONSHORE | PA | 16915 | Not Within a Municipality | POTTER | MILEPOST | MP 0 | COMPRESSOR STATION 313 | 313-1S | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2006 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | VALVE OPERATOR FAILED TO CLOSE | [5 empty] | CLASS 2 LOCATION | NO |  | 566 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 35 | 35.70525956284154 | 285978 | 285978 | 12000 | 12241.803278688528 | 50 | 51.0075136612022 | 5000 | 5100.75136612022 | COMPANY LABOR FOR THE INCIDENT INVESTIGATION; | 3.93 | 303063 | 195332.4973491708015589534883720930232558 | 303407.26741803279174 | 0 | 0 | 0 | 0 | NO |  |  |  | 1100 | 450000 | 1170 | 192.619(A)(1) |  | 1990-07-21 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | VALVE OPERATOR FAILED TO FULLY CLOSE VALVE | [160 empty] | YES | WM. MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253509 | JAKE TAYLOR | jake_taylor@kindermorgna.com | 8142743122 | JAIME HERNANDEZ | DIRECTOR ENGR COMPLIANCE CODES AND STANDARDS | 17133699443 | jaime_hernandez@kindermorgan.com | ON AUGUST 30, TENNESSEE GAS PIPELINE (TGP), AN ON-DUTY STATION TECHNICIAN WAS PERFORMING HIS INSPECTION ROUNDS AT COMPRESSOR STATION 313 AND DISCOVERED AN AUTOMATED EMERGENCY SHUT DOWN (ESD) FUEL GAS BLOCK VALVE PARTIALLY OPEN ALLOWING NATURAL GAS TO VENT TO ATMOSPHERE. UPON DISCOVERY OF THE UNDESIRABLE SITUATION, THE ON-DUTY STATION TECHNICIAN MANUALLY CLOSED THE AUTOMATED ESD FUEL GAS BLOCK VALVE THEREBY IMMEDIATELY TERMINATING THE NATURAL GAS RELEASE. OPERATIONS INITIATED THE EMERGENCY RESPONSE LINE (ERL) PER O&M PROCEDURES AND THE INCIDENT WAS REPORTED. THE TGP INVESTIGATION CONCLUDED THE GAS RELEASE BEGAN AFTER AN ESD EVENT DEMONSTRATION REQUESTED BY PHMSA ON AUGUST 18, 2021. AFTER THE ESD DEMONSTRATION EVENT, THE AUTOMATED VALVE OPERATOR FAILED TO FULLY CLOSE THE AUTOMATED ESD FUEL BLOCK VALVE. THE ESD SYSTEM VENT VALVE WAS IN THE CORRECT OPEN POSITION THUS ALLOWING THE NATURAL GAS TO RELEASE TO ATMOSPHERE. THE INVESTIGATION FURTHER CONCLUDED THE STATION TECHNICIAN PERFORMING THE DEMONSTRATION FAILED FOLLOW THE SITE-SPECIFIC PROCEDURE AND DID NOT VISUALLY CHECK THE FINAL POSITIONS OF THE AUTOMATED ESD FUEL BLOCK VALVE AND THE ESD VENT VALVE. TGP REVOKED THE ASSOCIATED ESD TESTING OPERATOR QUALIFICATION (OQ) FOR THE STATION TECHNICIAN INVOLVED WITH THE ESD TEST DEMONSTRATION. ADDITIONALLY, SUBSEQUENT INVESTIGATION TESTING FOUND THE AUTOMATED VALVE OPERATOR APPLICABLE TO THE ESD FUEL BLOCK VALVE TO BE UNRELIABLE. A REPLACEMENT VALVE OPERATOR HAS BEEN ORDERED FOR THE AUTOMATED ESD FUEL BLOCK VALVE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210085 | 36330 | 2021-10-05 16:29 | SUPPLEMENTAL FINAL | 39701 | BOARDWALK TEXAS INTRASTATE, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-09-14 18:10 | 2021 | CENTRAL | YES | 28.3088 | -97.299 | 1316767 | 2021-09-14 18:10 | 1317005 | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINOR LEAK; SECURING TEMPORARY GAS TO KEEP 2 CITY GATES IN SERVICE |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | NO ACTION WAS TAKEN. THIS IS MINOR LEAK ONLY REPORTABLE BECAUSE THE REPAIR COST WILL MEET THRESHOLD. |  | OPERATIONAL CONTROL | NO ACTION WAS TAKEN. THIS IS MINOR LEAK ONLY REPORTABLE BECAUSE THE REPAIR COST WILL MEET THRESHOLD. |  | 0 | 2021-08-09 13:30 | 2021-08-09 13:30 | ONSHORE | TX | 78377 | Not Within a Municipality | REFUGIO | SURVEY STATION NO. | 1592+13 | WHITE POINT FIELD TO REFUGIO | INDEX 46 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | DRESSER COUPLING | 1927 | 1927 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 201 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 4 | 4 | 463318 | 472653.984289617617992 | 0 | 0 | 0 | 0 |  | 3.68 | 463322 | 208519.4601379964256194219269102990033223 | 472657.984289617617992 | 0 | 0 | 0 | 0 | NO |  |  |  | 250 | 100 | 310 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 26400 | NO | [5 empty] | YES | DRESSER COUPLING | YES |  |  |  |  | YES | COULD ONLY DISPLACE GAS TO ATMOSPHERE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [19 empty] | YES | DRESSER SEALS LEAKING | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 270-903-5764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 270-314-6547 | tina.baker@bwpipelines.com | ON 8/9/2021, A GULF SOUTH TECHNICIAN WHO WAS TAKING ROUTINE RECTIFIER READINGS IN AN AREA THAT HAD RECENTLY RECEIVED RAIN, NOTICED MINOR BUBBLING ON THE PIPELINE RIGHT-OF-WAY. THE TECHNICIAN CHECKED FOR AND IDENTIFIED TWO MINOR LEAKS APPROXIMATELY 30 FEET APART. ON 9/14/2021, THE SITE WAS EXCAVATED AND THE LEAKS WERE IDENTIFIED AS GRADE 2 LEAKS. GULF SOUTH ANTICIPATED INSTALLING WELD OVER SLEEVES BUT, AFTER EXCAVATING, DETERMINED TO REPLACE APPROXIMATELY 40 FEET OF PIPE INSTEAD. ARRANGEMENTS ARE CURRENTLY BEING MADE TO PERFORM THE PIPE REPLACEMENT; THE LEAKS ARE BEING MONITORED. THE LINE IS NOT ISOLATED BECAUSE THESE ARE MINOR LEAKS AND THE LINE SERVES TWO CITY GATES. ARRANGEMENTS ARE BEING MADE TO SUPPLY TEMPORARY GAS DURING THE PIPE REPLACEMENT. PART A, QUESTION 10 SHOWS 1 MCF OF GAS LOSS BUT IT WAS ACTUALLY SO MINIMAL IT COULD NOT BE MEASURED. 2/10/2022 UPDATE REPAIR COST AND SUBMIT FINAL REPORT. DURING THE REPAIR TIMEFRAME, A THIRD PINHOLE LEAK WAS DISCOVERED AND WAS REPAIRED AS PART OF THE PIPE REPLACEMENT THAT WAS ALREADY BEING DONE. REPAIRS WERE COMPLETED BY PIPE REPLACEMENT ON 11/4/2021.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210086 | 37682 | 2021-10-11 11:03 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-09-14 14:09 | 2021 | CENTRAL | YES | 33.3521 | -92.7408 | 1316739 | 2021-09-14 14:46 | 1316931 | NATURAL GAS |  | 100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STOPPLES WERE INSTALLED AND THE PIPE WAS REPAIRED. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | A 20% REDUCTION IN PRESSURE WAS IMPLEMENTED. |  | OPERATIONAL CONTROL | A 20% REDUCTION IN PRESSURE WAS IMPLEMENTED. |  | 0 | 2021-09-13 12:00 | 2021-09-13 12:30 | ONSHORE | AR | 71762 | SMACKOVER | UNION | NOT APPLICABLE |  | K-NORTH | K-NORTH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | YES | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | NO |  | 143 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 407 | 407 | 145000 | 147921.78961748638 | 2500 | 2550.37568306011 | 0 | 0 |  | 4.07 | 147907 | 66649.6078474756687956810631229235880399 | 150879.16530054649 | 0 | 0 | 0 | 0 | NO |  |  |  | 265 | 17.5 | 300 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 126 | NO |  | YES | [5 empty] | YES |  |  |  |  | YES | LACK OF PIG TRAPS | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THE LOCAL DISTRIBUTION COMPANY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DUE TO FAILURE OF CLAMP STYLE TAP THREADS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | OLD STYLE CLAMP LEAKING AT TAP VALVE.THE LEAK WAS IN A THREADED CONNECTION FOR 2" TAP BELOW GROUND WITH NO CORROSION FOUND. | [18 empty] | YES | BREAKDOWN OF THREADS. | [149 empty] | YES | [11 empty] | JIMMY CROSS |  | jimmy.cross@energytransfer.com | 14055768230 |  | JIMMY CROSS | jimmy.cross@energytransfer.com | 14055768230 | JIMMY CROSS |  | 14055768230 | jimmy.cross@energytransfer.com | ON SEPTEMBER 13TH ENABLE MIDSTREAM PARTNERS RECEIVED NOTIFICATION FROM THE LOCAL DISTRIBUTION COMPANY (LDC) OF A POSSIBLE MINOR LEAK ON ENABLE GAS TRANSMISSION LINE K-NORTH. THE POSSIBLE LEAK WAS IN SMACKOVER, ARKANSAS. ON 9/13/21 ENABLE EXCAVATED AND DID CONFIRM A MINOR LEAK WAS ORIGINATING FROM AN OLD-STYLE CLAMP LEAKING AT THE TAP VALVE THREADS ON LINE K-NORTH. THIS TAP ON LINE K-NORTH FEEDS 5 DOMESTIC CUSTOMERS IN THE AREA. A 20% REDUCTION IN PRESSURE WAS IMMEDIATELY IMPLEMENTED ON 9/13. A REPAIR PLAN WAS DETERMINED ON 9/14 THAT WOULD REPLACE THIS SECTION OF 12" PIPELINE REMOVING THE BOLT ON CLAMP. TO KEEP THE DOMESTIC CUSTOMERS SUPPLIED WITH GAS DURING REPAIR, STOPPLES WOULD NEED TO BE INSTALLED PRIOR TO PIPE REPLACEMENT. PRIOR TO STOPPLE REPLACEMENT, REINFORCING SLEEVES WOULD NEED TO BE INSTALLED ON THE FIRST 3 DRESSER COUPLERS JOINTS UPSTREAM AND DOWNSTREAM OF THE LEAK TO STABILIZE THE LINE FOR STOPPLE INSTALLATION. IT WAS DETERMINED AT THIS TIME THAT THE REPAIR WOULD EXCEED THE $122,000 THRESHOLD FOR AN INCIDENT. A CALL WAS PLACED TO THE NRC ON 9/14/2021 (#1316739) AND THE 48 HR. FOLLOW UP WAS PLACED ON 9/16/2021 (#1316931). THE LINE WAS REPAIRED ON 9/16. SUPPLEMENTAL 10/20/22: PART B CHANGED CALHOUN COUNTY TO UNION COUNTY
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210087 | 37134 | 2021-10-11 11:36 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2021-09-14 10:46 | 2021 | CENTRAL | YES | 29.7425 | -92.3531 | 1316694 | 2021-09-14 10:46 | 1316959 | NATURAL GAS |  | 1509 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE IS BLOCKED AND IN IDLE STATUS. NOT FLOWING |  |  |  | YES | OPERATOR | 2021-04-28 09:00 | NO | [5 empty] | OPERATIONAL CONTROL | OPERATIONS MONITORED THE LEAK RATE DURING THIS TIME |  | OPERATIONAL CONTROL | OPERATIONS MONITORED THE LEAK RATE DURING THIS TIME |  | 0 | 2021-04-28 08:00 | 2021-04-28 08:00 | ONSHORE | LA | 70548 | KAPLAN | VERMILLION | MILEPOST | 10.78 | CENTRAL LOUISIANA LATERAL | MAIN LINE C | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | OTHER | VALVE SETTING OVER BAYOU CANAL. |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | STEM - CORROSION | [5 empty] | CLASS 1 LOCATION | NO |  | 188 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 8134 | 8134 | 254536 | 259664.969945355263584 | 0 | 0 | 0 | 0 |  | 5.39 | 262670 | 119891.332777354245545488372093023255814 | 267798.969945355263584 | 0 | 0 | 0 | 0 | NO |  |  |  | 619 | 0 | 1547 | 192.619(A)(2) |  | 1969-08-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 42270 | NO |  |  |  | YES |  | YES | NO FLOW IN THE PIPELINE | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER DID NOT SEE ANY ALARMS FOR THE SMALL LEAK. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | NO | [335 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 7133039956 |  | JOHN BELL | john.bell@williams.com | 3373179145 | TYSON GREEN | MANAGER PIPELINE SAFETY | 713-215-2535 | tyson.green@williams.com | APRIL 28TH A LEAK WAS DISCOVERED BY A TECHNICIAN WHILE PERFORMING OTHER MAINTENANCE ON SITE. END OF APRIL/EARLY MAY WILLIAMS BEGAN ASSESSING POTENTIAL OPTIONS TO STOP THE LEAK. AFTER IT WAS DETERMINED THAT A BLOWDOWN WAS TOO RISKY DUE TO LIQUIDS KNOWN TO BE IN THE PIPELINE, ALTERNATIVE METHODS WERE REVIEWED AND A CLAMP WAS SELECTED AS THE BEST OPTION. MID-LATE MAY MULTIPLE VENDORS WERE CONTACTED ABOUT THE CLAMP, AND SITE VISITS WERE CONDUCTED TO TAKE MEASUREMENTS BECAUSE OF THE FACT THAT IT WOULD HAVE TO BE A CUSTOM MADE/ENGINEERED CLAMP TO STOP THE LEAK. EARLY JUNE VENDOR SUPPLIED US WITH A QUOTE FOR THE CLAMP, BUT REQUESTED A SECOND SITE VISIT DUE TO CONCERNS OVER THE INITIAL MEASUREMENTS. ADDITIONAL MEASUREMENTS WERE TAKEN AND AN UPDATED DESIGN WAS SUBMITTED ON JUNE 11TH. PO ISSUED TO VENDOR TO BEGIN MANUFACTURING. EXPEDITED OPTION WAS SELECTED AND THE LEAD TIME WAS 8 WEEKS, WHICH LEADS TO AN EARLY AUGUST DELIVERY JULY 28TH VENDOR UPDATES WILLIAMS AND INFORMS THEM THAT THE CLAMP DELIVERY IS ON TRACK AUGUST 2ND VENDOR INFORMS WILLIAMS THAT THE HEAT TREATMENT FACILITY WAS EXPERIENCING DELAYS THAT WERE BEING WORSENED BY COVID IMPACTS, AND THAT THERE WAS NOW A 2-3 WEEK DELAY IN THE DELIVERY DATE. AUGUST 18TH THE CLAMP SHIPS FROM THE MANUFACTURER TO WILLIAMS CONTRACTOR WHO WILL BE INSTALLING IT IN THE FIELD AUGUST 23RD CLAMP ARRIVES AT CHET MORRISONS FACILITY IN HOUMA, LA END OF AUGUST CLAMP WAS TO BE INSTALLED BY THE END OF AUGUST, BUT HAD TO BE DELAYED DUE TO HURRICANE IDA EARLY SEPTEMBER CONTRACTORS SHOP WAS DIRECTLY IMPACTED BY HURRICANE IDA AND IT TOOK A FEW DAYS BEFORE WE COULD GET A HOLD OF THE CONTRACTOR AND DETERMINE IF THE CLAMP WAS STILL SECURED. MID-SEPTEMBER DUE TO HURRICANE IDA MANY BOATS IN THE SOUTH LOUISIANA AREA ARE HARD TO SECURE BECAUSE OF HIGH DEMAND. OUR CONTRACTOR IS FINALLY ABLE TO SECURE A BOAT AND A NEW MOBILIZATION DATE OF 9/12 IS COORDINATED. BOAT ARRIVED ON SITE AT THE SHORE SCRUBBERS ON 9/14, BUT IS ON STANDBY UNTIL WEATHER PASSES AND ALLOWS FOR INSTALLATION. 9/19 CLAMP INSTALLED, LEAK STOPPED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210088 | 35851 | 2021-10-11 15:04 | ORIGINAL FINAL | 32512 | GOLDEN TRIANGLE STORAGE, INC. | 919 MILAM STREET SUITE 2425 | HOUSTON | TX | 77002 | 2021-09-15 14:30 | 2021 | CENTRAL | YES | 30.0241 | -94.0766 | 1316874 | 2021-09-15 16:05 | 1317050 | NATURAL GAS |  | 5000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | BLOWDOWN VALVE WAS FOUND PARTIALLY OPEN AND WAS CLOSED BY OPERATOR. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-09-14 10:00 | 2021-09-13 20:30 | ONSHORE | TX | 77705-6522 | BEAUMONT | JEFFERSON | NOT APPLICABLE |  | GOLDEN TRIANGLE STORAGE | COMPRESSOR C MANIFOLD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2010 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | INCOMPLETE CLOSURE OF AUTOMATED VALVE | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 25000 | 25000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 25000 | 16403.6544850498338870431893687707641196 | 25000 | 0 | 0 | 0 | 0 | NO |  |  |  | 2362 | 90235 | 2600 | 192.619(A)(2) |  | 2010-07-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | INCOMPLETE CLOSURE AUTOMATED VALVE | [22 empty] | YES | BLOCKED VENT ON VALVE ACTUATOR DIDN'T ALLOW THE CYLINDER TO FULLY DEPRESSURIZE | [161 empty] | ROBERT CORNELL | DIRECTOR WEST REGION | rcornell@southernco.com | 409-242-4890 |  |  |  |  | JAMES HOTINGER | DIRECTOR COMPLIANCE AND QA | 804-514-7954 | jhoting@southernco.com | ON 9-13-2021 THE EVENT STARTED WHEN PREPARING FOR TROPICAL STORM NICHOLAS. AS PART OF THE PREPAREDNESS OPERATIONS, THE FACILITY WAS SWITCHED TO GENERATOR POWER TO ENSURE THE SAFETY OF OPERATIONS SHOULD THERE BE A LOSS OF COMMERCIAL POWER. DURING THE POWER TRANSFER, THE AUTO TRANSFER SWITCH DID NOT CHANGE OVER QUICKLY ENOUGH TO PREVENT THE ESD SYSTEM FROM SENSING A POWER LOSS. AS A RESULT, THE ESD SYSTEM ACTUATED AND BLEW DOWN THE COMPRESSOR BUILDING PIPING. WITH GENERATOR POWER ONLINE, THE OPERATOR RESET THE ESD AND STARTED COMPRESSOR C. HOWEVER, AN AUTOMATED BLOWDOWN VALVE REQUIRED FOR THE ESD ON COMPRESSOR C FAILED TO CLOSE TO 100% DESPITE THE VALVE CLOSE LIMIT INDICATOR SHOWED CLOSED. THE ESD ACTIVATED DETECTION SYSTEM AT THE BLOWDOWN SILENCER DID NOT ACTIVATE DUE TO THE LOW FLOW RATE OF GAS AT THE BLOWDOWN SILENCER. THE OPERATOR ON SHIFT NOTICED GAS VAPORS COMING OUT OF THE BLOWDOWN SILENCER AT 8:30 PM. THE OPERATOR CALLED THE I&E TECH. AT 8:30 PM 9/13/21 TO NOTIFY HIM OF THE VAPORS COMING OUT OF THE BLOWDOWN SILENCER. THE I&E TECH WAS ALREADY ON HIS WAY TO WORK TO STAY THE NIGHT FOR THE STORM. WHEN THE I&E TECH ARRIVED, THE LEAK APPEARED TO BE SMALL, AND WAS TOO DANGEROUS WITH WINDS, RAIN, AND LIGHTING TO INVESTIGATE THE LEAK. ONCE THE STORM PASSED AT 8:30 AM THE I&E TECH DISCOVERED THE PARTIALLY OPEN BLOWDOWN VALVE AND COMPLETELY CLOSED IT. THIS FAILURE TO HAVE 100% CLOSURE RESULTED IN NATURAL GAS ESCAPING THROUGH THE VENT OUT OF THE BLOWDOWN SILENCER. DURING A REVIEW OF THE SYSTEM BALANCE ANALYSIS EQUATIONS FOUND THAT ENOUGH GAS MAY HAD BEEN RELEASED TO THE ATMOSPHERE TO TRIGGER REPORTING. FURTHER INVESTIGATION INDICATED THAT A REPORT OF THE RELEASE REQUIRED. THE REPORT WAS MADE AT 2:15 CST. TO THE NRC.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210089 | 35853 | 2021-10-12 10:19 | ORIGINAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-09-13 09:49 | 2021 | CENTRAL | YES | 35.5459 | -100.6642 | 1316587 | 2021-09-13 11:40 | 1316761 | NATURAL GAS |  | 6460 | 313 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-13 09:52 | 2021-09-17 16:00 |  | NO |  |  | NO | [11 empty] | 0 | 2021-09-13 09:48 | 2021-09-13 07:00 | ONSHORE | TX | 79065 | Not Within a Municipality | GRAY | MILEPOST | 54 | COMPRESSOR STATION 154 PAMPA | OKLAHOMA EXTENSION #1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1969 | 1969 | CARBON STEEL |  | LEAK |  |  | OTHER | VALVE DID NOT CLOSE | [5 empty] | CLASS 1 LOCATION | NO |  | 481 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 1497 | 1527.164959016393868 | 30898 | 30898 | 2250 | 2295.338114754099 | 25 | 25.5037568306011 | 100 | 102.0150273224044 | NGPL INVESTIGATION LABOR COST; | 4.783 | 34770 | 22016.2030118185294816744186046511627907 | 34848.021857923498368 | 0 | 0 | 0 | 0 | NO |  |  |  | 611 | 77857 | 720 | 192.619(A)(2) |  | 1969-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | LIMIT SWITCH SENT ERRANT VALVE POSITION SIGNAL | [161 empty] | WM. MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253509 | ROBERT DOLLOFF | robert_dolloff@kindermorgan.com | 8067318904 | JAIME HERNANDEZ | DIRECTOR ENGR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON SEPTEMBER 13, 2021, NATURAL GAS PIPELINE (NGPL) OPERATIONS STAFF ARRIVED AT COMPRESSOR STATION 154 AT 07:00-HOURS TO COMMENCE STATION FILTER REPLACEMENT. IN ORDER TO COMPLETE THE TASK, THE STATION WOULD UNDERGO AN INTENTIONAL ESD. DURING THE ESD, THE STAFF REALIZED THE DISCHARGE SIDE GATE VALVE 154-3 DID NOT PROPERLY CLOSE. THEREFORE, UNINTENTIONAL NATURAL GAS RELEASE CONTINUED THROUGH THE BLOWDOWN SYSTEM. CONSEQUENTLY, OPERATIONS STAFF MANUALLY CLOSED VALVE 154-3 THEREBY SECURING THE NATURAL GAS RELEASE. THE EMERGENCY RESPONSE LINE (ERL) WAS EXECUTED AND THE INCIDENT WAS REPORTED ACCORDINGLY. POST EVENT INVESTIGATION FOUND THE ACTUATOR LIMIT SWITCH ON VALVE 154-3 HAD FAILED, BY SENDING ERRANT VALVE POSITION DURING THE ESD, THEREBY ALLOWING UNINTENTIONAL NATURAL GAS TO RELEASE THROUGH THE BLOWDOWN SYSTEM. IN ORDER TO PREVENT REOCCURRENCE, OPERATIONS STAFF REBUILT SIMILAR LIMIT SWITCHES ON THE SUCTION AND DISCHARGE STATION VALVE ACTUATORS. ALL RECOMMENDED ACTIONS PER THE INCIDENT WERE ADDRESSED ON SEPTEMBER 17, 2021. HOWEVER, THE COMPRESSOR STATION CONTINUES TO BE OFF-LINE FOR ADDITIONAL UNRELATED MAINTENANCE TASKS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210090 | 36321 | 2021-10-12 13:55 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-09-13 17:40 | 2021 | CENTRAL | YES | 35.9218 | -99.0521 | 1316652 | 2021-09-13 19:55 | 1316842 | NATURAL GAS |  | 18741 | 12937 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-13 18:58 | 2021-09-20 12:30 |  |  | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-09-13 18:00 | NO | [5 empty] | VALVE CLOSURE |  | 2021-09-13 18:00 | VALVE CLOSURE |  | 2021-09-13 18:58 | 0 | 2021-09-13 18:00 | 2021-09-13 20:05 | ONSHORE | OK | 73667 | Not Within a Municipality | DEWEY | MILEPOST | 125 | 24-INCH MOUNTAIN VIEW MINEOLA LINE | CS 156 TO CS 158 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.25 | 52000 | API-5L | OTHER | ELECTRIC FUSION WELD | A O SMITH | ASPHALT |  | NO | [26 empty] | 1960 | 1960 | CARBON STEEL |  | MECHANICAL PUNCTURE | 91 | 74 | [7 empty] | CLASS 1 LOCATION | NO |  | 444 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 61878 | 63124.858606557394632 | 89638 | 89638 | 108238 | 110419.025273224074472 | 1850 | 1887.2780054644814 | 5445 | 5554.71823770491958 | SPECIMEN TRANSPORTATION, HANDLING, METALLURGICAL REPORT, OPERATOR INVESTIGATION, | 4.783 | 267049 | 138659.6699075146183656710963455149501661 | 270623.880122950870084 | 1 | 0 | 0 | 0 | NO |  |  |  | 655 | 58124 | 720 | 192.619(A)(1) |  | 1960-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 81312 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | WATERWAY IMPROVEMENTS | NO | [5 empty] | YES | 163 | OTHER |  |  |  | THIRD PARTY CLEARING LAND FOR PRIVATE LAND OWNER ENTERED INTO PIPELINE EASEMENT; NO ONE CALL TICKET FOR THIS LOCATION; | [262 empty] | WM. MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253509 | PAUL O'BRIANT | paul_obriant@kindermorgan.com | 5809282447 | JAIME HERNANDEZ | DIRECTOR ENGR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | AT APPROXIMATELY 17:29 HOURS IN DEWEY COUNTY OKLAHOMA, THE NGPL 24-INCH MOUNTAIN VIEW TO MINEOLA LINE WAS STRUCK BY A THIRD PARTY CONTRACTOR, EMPLOYED BY A PRIVATE LANDOWNER. AN IN-SERVICE RUPTURE INSTANTANEOUSLY FOLLOWED THE PIPELINE STRIKE EVENT. A RESPONDING FIRE DEPARTMENT CREW ARRIVED ON SITE AND IMMEDIATELY CALLED NGPL GAS CONTROL TO REPORT THE UNDESIRED INCIDENT. WITH THE PIPELINE STRIKE AND SUBSEQUENT RUPTURE, THERE WAS NO FIRE, HOWEVER, THE EQUIPMENT OPERATOR WAS INJURED AND RECEIVED MEDICAL TREATMENT WITHOUT IN-PATIENT HOSPITALIZATION. NGPL CONDUCTED AN EMERGENCY RESPONSE LINE (ERL) IN ACCORDANCE WITH O&M PROCEDURE 159. DURING THE ERL CALL, THE UNDESIRABLE INCIDENT WAS DEEMED REPORTABLE AND A NATIONAL RESPONSE CENTER (NRC) CALL WAS COMPLETED. ADDITIONAL INCIDENT NOTIFICATIONS WERE ALSO MADE TO THE CHEMICAL SAFETY BOARD (CSB), THE OKLAHOMA CORPORATE COMMISSION (OCC), AND THE PHMSA ACCIDENT INVESTIGATION DIVISION (AID). NGPL UPDATED THE CSB REGARDING NO HOSPITALIZATION OF THE EQUIPMENT OPERATOR; THEREFORE, THE CSB REQUIRED NO FURTHER INFORMATION. NGPL INCIDENT INVESTIGATION COMMENCED AS WELL AS THE PIPELINE REPAIR PROCESS. THE SPECIMEN CONTAINING THE RUPTURE WAS SHIPPED TO A THIRD PARTY LABORATORY FOR FURTHER EXAMINATION. THE METALLURGICAL REPORT CONCLUDED THE PIPELINE STRIKE WAS RESPONSIBLE FOR THE PIPELINE RUPTURE. FURTHERMORE, THE OKLAHOMA CORPORATION COMMISSION (OCC) DETERMINED THE THIRD PARTY CONTRACTOR WAS RESPONSIBLE FOR THE EXCAVATION DAMAGE AND FAILED TO CREATE AN OKLAHOMA ONE CALL TICKET. REPAIRS WERE COMPLETED AND THE PIPELINE RETURNED TO SERVICE ON SEPTEMBER 20, 2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210091 | 36019 | 2021-10-12 16:10 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2021-09-15 19:21 | 2021 | CENTRAL | YES | 31.5461 | -102.4934 | 1316964 | 2021-09-16 11:10 | 1317082 | NATURAL GAS |  | 14400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-09-15 19:21 | 2021-09-15 20:30 | ONSHORE | TX | 79731 | Not Within a Municipality | CRANE | NOT APPLICABLE |  | CRANE COMPRESSOR STATION | CRANE COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | ESD VENT VALVE | CLASS 1 LOCATION | NO |  | 537 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 68112 | 68112 | 10000 | 10201.50273224044 | 0 | 0 | 0 | 0 |  | 4.73 | 78112 | 49191.9408665105414285714285714285714286 | 78313.50273224044 | 0 | 0 | 0 | 0 | NO |  |  |  | 915 | 0 | 1050 | 192.619(A)(1) |  | 1970-01-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO THE POWER LOSS TO THE CRANE COMPRESSOR STATION ESD SYSTEM, THE ESD SYSTEM INITIALLY RELEASE GAS AS IT WAS DESIGN TO DO. THE ENTERPRISE PRODUCTS OPERATOR DID NOT CAUSE THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | STATION ISOLATION AND VENT VALVES FAILED TO CLOSE WHEN THE STATION ESD. | [161 empty] | GORDON WILLIAMS | ENGINEER - COMPLIANCE | gswilliams@eprod.com | 832-252-7446 |  | GORDON WILLIAMS | gswilliams@eprod.com | 832-252-7446 | GORDON WILLIAMS | ENGINEER - COMPLIANCE | 832-252-7446 | gswilliams@eprod.com | ON 9-15-2021 AT 19:21, THE CONTROLLER NOTICED PRESSURE DECREASING AT THE IDLED CRANE STATION AND DISPATCHED A TECHNICIAN. UPON ARRIVAL, THE TECHNICIAN FOUND THE THE STATION HAD ESD AND PROCEEDED TO ISOLATE THE STATION TO STOP THE DISCHARGE OF GAS THROUGH THE ESD VENT VALVE. IT WAS DETERMINED THAT THE STATION HAD ESD, AS DESIGNED, DUE TO A LOSS OF POWER; HOWEVER, AN ISOLATION VALVE DID NOT PROPERLY CLOSE, WHICH ALLOWED GAS INTO THE STATION, AND THE ESD VENT VALVE FAILED TO CLOSE, WHICH ALLOWED GAS TO DISCHARGE FROM THE STATION. THE MALFUNCTIONED VALVES WAS REPAIRED AND REPROGRAMMED. TO PREVENT RECURRENCE, THE CRANE ESD SYSTEM WAS TESTED TO ENSURE THAT IT WORKED AS DESIGNED. THE NRC AND THE TXRRC (2491) WERE NOTIFIED ON 9-16-2021 FOLLOWING THE DETERMINATION THAT THE CALCULATED GAS VOLUME DISCHARGED EXCEEDED 3 MMSCF.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210092 | 35869 | 2021-10-13 11:06 | ORIGINAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-09-13 13:40 | 2021 | CENTRAL | YES | 32.1923 | -97.4177 | 1316608 | 2021-09-13 13:50 | 1316851 | NATURAL GAS |  | 6.519 | 44950 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-13 14:30 | 2021-09-15 07:52 |  | YES | OPERATOR | 2021-09-13 11:15 | NO | [5 empty] | VALVE CLOSURE |  | 2021-09-13 14:30 | VALVE CLOSURE |  | 2021-09-13 14:30 | 5 | 2021-09-13 12:10 | 2021-09-13 12:10 | ONSHORE | TX | 76627 | RIO VISTA | HILL | SURVEY STATION NO. | 4314+60 | REED TO CLEBURNE 42INCH | 20051001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 67 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 42 | NO | 0.484 | 70000 | API 5LX | SPIRAL WELDED |  | IPSCO | EPOXY |  | NO | [26 empty] | 2005 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1.5 | 0.1 | [7 empty] | CLASS 1 LOCATION | NO |  | 987 |  | NO | NO |  |  | NO |  |  | 2500 | 2550.37568306011 | 221154 | 225610.313524590226776 | 32 | 32 | 394680 | 402632.90983606568592 | 0 | 0 | 0 | 0 |  | 4.92 | 618366 | 278302.9736244623475853754152823920265781 | 630825.599043716022696 | 0 | 0 | 2 | 0 | NO |  |  |  | 916 | 6000 | 1160 | 192.619(A)(1) |  | 2007-03-18 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 81998 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | UTILITY | AUGER | POLE | YES | 2173949353 | TEXAS 811 | UTILITY OWNER | YES | NO | YES | 42 | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | NICK PAVLOVSKY | SPECIALIST - DOT COMPLIANCE | nicklas.pavlovsky@energytransfer.com | 713-989-4527 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON 9/13/21, AT APPROXIMATELY 10:45AM HILCO ELECTRIC COOPERATIVE WAS INSTALLING POLES AND ANCHORS FOR A NEW ELECTRICAL SERVICE IN HILL COUNTY NEAR CR 1120. WHILE DRILLING TO SET A POLE, THE ET REED TO CLEBURNE 42-INCH PIPELINE WAS STRUCK WITH AN AUGER. THE LINE STRIKE WAS REPORTED TO ET AT 11:09 AND OPERATIONS PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 12:10PM. ET PERSONNEL SECURED THE AREA AND ADDITIONAL PERSONNEL WERE DISPATCHED TO BEGIN ISOLATING THE AFFECTED SEGMENT. TWO HOMES IN THE AREA WERE CONTACTED TO EVACUATE. NEITHER HOME WAS OCCUPIED AT THE TIME AND THE INDIVIDUALS WERE CONTACTED AND REQUESTED NOT TO RETURN TO THE RESIDENCES UNTIL NOTIFIED THAT THE AREA WAS SAFE. THE PIPELINE WAS ISOLATED AT 2:30PM BY CLOSING THE BLOCK VALVES AT THE CLEBURNE COMPRESSOR STATION AND MAINLINE BLOCK VALVE #1 AND THEN THE LINE WAS BLOWN DOWN FOR ASSESSMENT AND REPAIR. UPON BEING EXCAVATED IT WAS DISCOVERED THAT THE LINE STRIKE CAUSED A SERIES OF GOUGES ON THE PIPELINE AT APPROXIMATELY THE 1 TO 3 O'CLOCK POSITIONS. A 13-INCH GOUGE NEAR THE 1 O'CLOCK POSITION ALSO CONTAINED A 1.5-INCH LEAK. REPAIR WAS COMPLETED USING A WELD ON SLEEVE AND PIPELINE WAS PLACED BACK INTO SERVICE AT 7:52AM ON 9/15/21. INVESTIGATION OF THE INCIDENT INDICATED THAT THE PIPELINE WAS NOT LOCATED AND MARKED CORRECTLY IN RESPONSE TO ONE CALL TICKET. INDIVIDUALS INVOLVED IN THE LOCATING AND MARKING OF THE PIPELINE HAD OQ SUSPENDED FOR SPECIFIC COVERED TASKS AND WILL RECEIVE RETRAINING PRIOR TO OQ BEING REINSTATED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210093 | 36123 | 2021-10-14 13:42 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2021-09-14 10:54 | 2021 | EASTERN | YES | 41.2463 | -81.6384 | 1316688 | 2021-09-14 11:09 | 1316946 | NATURAL GAS |  | 0 | 46.6 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-08-30 20:15 | 2021-10-22 14:30 |  | NO |  |  | NO | [11 empty] | 0 | 2021-08-30 17:00 | 2021-08-30 17:30 | ONSHORE | OH | 44286 | BRECKSVILLE | SUMMIT | NOT APPLICABLE |  | BRUSH STATION | STATION PIPE | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 30 | NO | 0.375 | 52000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 560 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 265 | 270.33982240437166 | 0 | 0 | 422323 | 430832.923838797934212 | 0 | 0 | 0 | 0 |  | 5.6947 | 422588 | 190186.248975409953836 | 431103.263661202305872 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 45000 | 630 | 192.619(A)(1) |  | 1988-09-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT SIGNIFICANT ENOUGH TO REGISTER IN SCADA. THE OPERATING PRESSURE WAS WELL BELOW MAOP AND NO MAJOR CHANGES WERE MADE TO THE SUPPLY PRIOR TO THE LEAK BEING DISCOVERED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN | [5 empty] | YES | FLUID COLLECTING IN A LOW SPOT. | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CAROL HAGER | MANAGER COMPLIANCE AND INTEGRITY | carol.m.hager@dominionenergy.com | 13304379557 |  | CAROL HAGER | carol.m.hager@dominionenergy.com | 13304379557 | CAROL HAGER | MANAGER COMPLIANCE AND INTEGRITY | 13304379557 | carol.m.hager@dominionenergy.com | DEO WAS NOTIFIED OF A LEAK INSIDE DEO'S BRUSH STATION BY A DEO CONTRACTOR WORKING NEAR-BY ON AUGUST 30TH. DEO SHUT IN THE SECTION OF LINE AND BEGAN CLEAN UP OF THE FLUID. THE ESTIMATE FOR CLEAN UP AND REPLACEMENT OF THE SECTION REACHED THE $122,000 THRESHOLD ON SEPTEMBER 14TH. A PINHOLE LEAK WAS FOUND AT THE 6:00 POSITION OF THE PIPE SEGMENT. THIS SECTION OF LINE HAS BEEN REPLACED AND THE LINE IS BACK IN SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210094 | 35886 | 2021-10-16 19:57 | ORIGINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2021-09-16 10:30 | 2021 | CENTRAL | YES | 38.4875 | -89.1403 | 1316963 | 2021-09-16 11:15 | 1317172 | NATURAL GAS |  | 6421.78 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-16 15:45 | 2021-09-17 04:00 |  | YES | OPERATOR | 2021-09-16 11:09 | NO | [5 empty] | VALVE CLOSURE |  | 2021-09-16 13:24 | VALVE CLOSURE |  | 2021-09-16 13:24 | 8 | 2021-09-16 08:17 | 2021-09-16 08:30 | ONSHORE | IL | 62801 | CENTRALIA | MARION | NOT APPLICABLE |  | SYSTEM 1894 | 2 IN ST STUB OFF 10 IN ST FACID 6675453 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 96 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 2 | NO | 0.154 | 52000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1971 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  | 2 |  | CLASS 3 LOCATION | NO |  | 41 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 42153 | 42153 | 23785 | 24264.27424863388654 | 31626 | 32263.272540983615544 | 0 | 0 |  | 6.564 | 97564 | 52596.3185786109298806212624584717607973 | 98680.546789617502084 | 0 | 0 | 8 | 0 | NO |  |  |  | 702.67 | 0 | 720 | 192.619(A)(1) |  | 1971-01-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 12600 | NO | [5 empty] | YES | DAMAGE OCCURRED TO A LATERAL 2" STEEL STUB (NOT INSPECTABLE) OFF OF THE 10" STEEL TRANSMISSION MAIN (WHICH IS INTERNALLY INSPECTABLE) | YES |  |  |  |  | YES | DAMAGE OCCURRED TO A LATERAL 2" STUB | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT OCCURRED DURING EXCAVATION ACTIVITIES BY THE OPERATOR AND WAS PROMPTLY REPORTED TO GAS CONTROL. | [12 empty] | YES | 8 | 0 | YES | 8 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | X00242229000X | ILLINOIS JULIE | CONTRACT LOCATOR | YES | YES | YES | 13 | ABANDONED FACILITY | [232 empty] | YES | [33 empty] | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MANAGEMENT | jbozarth@ameren.com | [5 empty] | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MANAGEMENT | 217-625-6854 | jbozarth@ameren.com | A CONTRACTOR FOR AMEREN ILLINOIS WAS EXCAVATING A 10" STEEL GAS TRANSMISSION MAIN TO REMOVE A CASING UNDER OLD HIGHWAY 51 SOUTH OF CENTRALIA, IL. THE LINE HAD BEEN LOCATED AND EXPOSED, HOWEVER AN UNMAPPED 2" STEEL ABANDONED STUB WAS STRUCK BY THE EXCAVATOR RESULTING IN THE DAMAGE AND BLOWING GAS. THE SYSTEM WAS ISOLATED USING A SERIES OF VALVES, REPAIR WAS MADE AND THE LINE WAS SUBSEQUENTLY PLACED BACK INTO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210095 | 35888 | 2021-10-18 15:20 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-09-24 05:38 | 2021 | CENTRAL | YES | 42.0456 | -94.0455 | 1317759 | 2021-09-24 09:05 | 1317837 | NATURAL GAS |  | 17878 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | COMPRESSOR UNIT 18 RELIEF VALVE VENTING |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-09-24 05:38 | 2021-09-24 06:00 | ONSHORE | IA | 50212 | OGDEN | BOONE | NOT APPLICABLE |  | OGDEN COMPRESSOR STATION | IA-062 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 87066 | 87066 | 250 | 255.037568306011 | 250 | 255.037568306011 | 0 | 0 |  | 4.87 | 87566 | 57353.0488705680519883720930232558139535 | 87576.075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 838 | 416 | 1000 | 192.619(A)(2) |  | 1968-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | JOHN GORMLEY |  | john.gormley@nngco.com | 4023987494 |  | JOHN GORMLEY | john.gormley@nngco.com | 4023987494 | TOM CORRELL | VP PIPELINE SAFETY AND RIST | 4023987715 | thomas.correll@nngco.com | PILOT PRESSURE TUBING FROM THE PILOT TO THE RELIEF VALVE PISTON CRACKED, DROPPING RETENTION PRESSURE ON THE PILOT AND RELIEVE VALVE DOME, RESULTING IN THE UNIT 18 LEAD LINE RELIEF VALVE OPENING. A SENIOR PIPELINE TECHNICIAN WITH THE OGDEN, IOWA, TEAM, INVESTIGATED AND DISCOVERED BROKEN TUBING, WHICH CAUSED THE PILOT GAS TO LOSE PRESSURE. THIS ACTIVATED THE UNIT 18 RELIEF VALVE CAUSING IT TO VENT GAS AT THE OGDEN, IOWA, COMPRESSOR STATION. THE TUBING WAS REPLACED AND THE STATION WAS RETURNED TO NORMAL OPERATIONS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210096 | 36546 | 2021-10-18 15:22 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-09-26 13:03 | 2021 | CENTRAL | YES | 41.4224 | -97.287 | 1317917 | 2021-09-26 14:03 | 1318009 | NATURAL GAS |  | 9112 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A RELIEF VALVE WAS VENTING GAS AT A TOWN BORDER STATION. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-09-26 13:03 | 2021-09-26 14:00 | ONSHORE | NE | 68601 | COLUMBUS | PLATTE | NOT APPLICABLE |  | COLUMBUS #4 TOWN BORDER STATION | NER-0063 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | 2010 | 2010 | CARBON STEEL |  | OTHER | [8 empty] | A FAILED OUTPUT GAUGE WAS DISCOVERED ON THE FISHER 4100 CONTROLLER. | CLASS 1 LOCATION | NO |  | 40 |  | NO | NO |  |  | NO |  |  | 250 | 255.037568306011 | 0 | 0 | 44375 | 44375 | 250 | 255.037568306011 | 0 | 0 | 0 | 0 |  | 4.87 | 44875 | 29341.5123257175536495016611295681063123 | 44885.075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 105 | 8000 | 350 | 192.619(A)(2) |  | 2008-05-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [21 empty] | YES | [174 empty] | JOHN GORMLEY |  | john.gormley@nngco.com | 4023987494 |  | JOHN GORMLEY | john.gormley@nngco.com | 4023987494 | TOM CORRELL | VP PIPELINE SAFETY AND RIST | 4023987715 | thomas.correll@nngco.com | ON SEPTEMBER 26, 2021 AT 13:03 NORTHERN'S GAS CONTROL NOTIFIED THE SOUTH SIOUX CITY ON CALL TECHNICIAN THAT THE PRESSURE WAS DROPPING AT THE COLUMBUS #4 TOWN BORDER STATION. AT 13:20 CHAD HOMOLKA FROM ADM CORN PLANT COLUMBUS #4 TOWN BORDER STATION CALLED TO REPORT AT RELIEF VALVE VENTING GAS. THE RELIEF AT THE NER-0063 - COLUMBUS 8-INCH BRANCH LINE TAKE-OFF WAS PULLING DOWN THE LINE PRESSURE. A MEASUREMENT TECHNICIAN WAS DISPATCHED TO THE NER-0063 BRANCH LINE REGULATOR SETTING. THE RELIEF VALVE WAS DISCOVERED TO BE VENTING AND WAS ISOLATED TO STOP THE VENTING GAS. A FAILED OUTPUT GAUGE WAS DISCOVERED ON THE FISHER 4100 CONTROLLER. UPDATES MADE AT THE REQUEST OF PHMSAS ACCIDENT INVESTIGATION DIVISION: GPS LOCATION CORRECTED; NRC INITIAL CALL TIME CORRECTED; INSTALLATION DATE ESTIMATED, AND NARRATIVE UPDATED;
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210097 | 36010 | 2021-10-21 17:05 | SUPPLEMENTAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-09-23 16:25 | 2021 | PACIFIC | YES | 38.2858 | -122.4692 | 1317732 | 2021-09-23 16:25 | 1318001 | NATURAL GAS |  | 500 | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | BURN THROUGH |  |  |  | YES | OPERATOR | 2021-09-23 16:25 | YES | 2021-09-23 15:02 | ALLOWED TO BURN OUT |  | 500 | NO | OPERATIONAL CONTROL | BURN OUT TOOK PLACE AS CNG INJECTION WAS COORDINATED. |  | OPERATIONAL CONTROL | BURN OUT TOOK PLACE AS CNG INJECTION WAS COORDINATED. |  | 0 | 2021-09-23 15:02 | 2021-09-23 15:02 | ONSHORE | CA | 95476 | SONOMA | SONOMA | MILEPOST | 3.67 | R-519 | DFM-1305-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | FILLET WELD | [18 empty] | 1969 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BURN-THROUGH | CLASS 3 LOCATION | NO |  | 84 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 1500 | 1530.225409836066 | 1500 | 1500 | 145362 | 148291.084016393483928 | 150000 | 153022.5409836066 | 0 | 0 | 0 | 3 | 298362 | 134587.3273633653678472225913621262458472 | 304343.850409836149928 | 0 | 0 | 0 | 0 | NO |  |  |  | 200 | 75 | 200 | 192.619(A)(2) |  | 1969-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 3168 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PG&E CONTRACTOR WAS CAUSE OF INCIDENT AND ONSITE. NO CONTROL ROOM ASSISTANCE WAS NECESSARY. | [12 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | [6 empty] | YES | YET TO BE DETERMINED. DETAILS WILL BE PROVIDED ONCE INVESTIGATION REPORT IS COMPLETE. | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | rosa.duenas@pge.com | 510-298-7063 |  |  |  |  | SUSIE RICHMOND | GAS OPERATIONS COMPLIANCE AND RISK MANAGER | 925-786-0267 | gsr8@pge.com | ON THURSDAY, SEPTEMBER 23, 2021 AT 1502 HOURS, PG&E WAS NOTIFIED OF LEAKING GAS WITH IGNITION AT THE INTERSECTION OF 5TH AND MACARTHUR IN SONOMA. DURING A CLEARANCE ON PLANNED PROJECT NORTH OF R-519 ON DFM 1305-1, A WELDER WAS WELDING A SAV-A-VALVE WHEN HE BREACHED THE PIPELINE, CREATING A PIN HOLE LEAK AND IGNITING ESCAPING GAS. ONSITE EMPLOYEES CALLED 911. POLICE ONSITE PERFORMED STREET CLOSURES AND TRAFFIC CONTROL AND FIRE DEPARTMENT PERFORMED LOCAL EVACUATIONS. THERE WERE NO REPORTED INJURIES OR FATALITIES; NO MEDIA REPORTED; NO CUSTOMERS IMPACTED. THIS INCIDENT WAS REPORTED DUE TO THE REPAIR COSTS BEING OVER $122K.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210098 | 35907 | 2021-10-22 10:10 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2021-09-27 12:00 | 2021 | MOUNTAIN | YES | 37.2505 | -102.8814 | 1318005 | 2021-09-27 12:53 | 1318202 | NATURAL GAS |  | 9183 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-25 12:53 | 2021-10-04 08:00 |  | NO |  |  | NO | [11 empty] | 0 | 2021-09-25 12:38 | 2021-09-25 14:48 | ONSHORE | CO | 81064 | Not Within a Municipality | BACA | MILEPOST | 3.6 | PRITCHETT PUMP STATION | FR-1.2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2018 | 2013 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 120 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 50507 | 50507 | 200 | 204.0300546448088 | 100 | 102.0150273224044 | 0 | 0 |  | 5.5 | 50807 | 33274.9904519089375053156146179401993355 | 50813.0450819672132 | 0 | 0 | 0 | 0 | NO |  |  |  | 740 | 0 | 1480 | 192.619(A)(1) |  | 2019-05-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM GAS PROVIDER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [30 empty] | YES | CONTAMINATION OF VALVE STEM PACKING | [161 empty] | HANS DEEB | SR. PIPELINE COMPLIANCE ENGINEER | hdeeb@eprod.com | 713-381-4277 |  |  |  |  | HANS DEEB | SR. PIPELINE COMPLIANCE ENGINEER | 713-381-4277 | hdeeb@eprod.com | ON 9/25/21 ENTERPRISE PIPELINE CONTROL WAS CONTACTED BY AN ENTERPRISE TECHNICIAN REPORTING A POTENTIAL LEAK ON THE NATURAL GAS FUEL PIPELINE FEEDING PRITCHETT STATION. THE PIPELINE WAS REGISTERING FLOW BUT THE STATION WAS NOT RUNNING AT THAT TIME. THE TECHNICIAN TOLD THE GAS SUPPLIER TO CLOSE THEIR SDV AT THE METER SITE, AND HE THEN PROCEEDED TO BLOCK IN THE SYSTEM AT THE STATION. FURTHER INVESTIGATION REVEALED THAT A MALFUNCTIONING 2IN BYPASS VALVE AT THE STATION ALLOWED THE PRODUCT TO LEAK AROUND A BLOCK VALVE TO ATMOSPHERE. THE BYPASS VALVE WAS REPLACED AND SCADA WILL BE MODIFIED TO ALLOW FOR EARLY DETECTION OF FUTURE LEAKS. INITIAL CALL TO NRC WAS MADE ON 09/27/2021 AT 13:53 CDT (NRC#1318005). THE CALL WAS MADE BASED ON ESTIMATED VOLUME OF PRODUCT RELEASE EXCEEDING 3 MMCF. 48HR UPDATE CALL TO NRC WAS MADE ON 09/29/2021 AT 12:19 CDT (NRC#1318202).
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210099 | 36656 | 2021-10-22 17:04 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2021-09-23 12:01 | 2021 | CENTRAL | YES | 30.4663 | -92.5226 | 1317723 | 2021-09-23 16:27 | 1317804 | NATURAL GAS |  | 7860 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-CONSTRUCTION COMMISSIONING | [5 empty] | YES | OPERATOR | 2021-09-23 12:10 | NO | [11 empty] | 0 | 2021-09-23 12:01 | 2021-09-23 12:01 | ONSHORE | LA | 75035 | EUNICE | ACADIA | MILEPOST | MP 0.0 | EUNICE COMPRESSOR STATION | ANR 501 MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1966 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | UNINTENDED OPERATION OF A VALVE | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 38828 | 38828 | 10000 | 10201.50273224044 | 0 | 0 | 0 | 0 |  | 4.94 | 48828 | 29977.3561489025680066445182724252491694 | 49029.50273224044 | 0 | 0 | 0 | 0 | NO |  |  |  | 667 | 0 | 858 | 192.619(A)(1) |  | 1998-02-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AT THE TIME OF THE INCIDENT, THE STATION HAD BEEN PLACED INTO "LOCAL" OPERATIONS FOR THE PURPOSE OF COMMISSIONING FACILITIES. | [12 empty] | YES | 4 | 0 | YES | 5 | 0 | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ROGER R STREET | MANAGER USRC WEST | roger_street@tcenergy.com | 6154655123 |  | ROGER R STREET | roger_street@tcenergy.com | 6154655123 | ROGER R STREET | MANAGER USRC WEST | 6154655123 | roger_street@tcenergy.com | ON SEPTEMBER 23, 2021, AN UNINTENTIONAL RELEASE OF APPROXIMATELY 7.9 MILLION CUBIC FEET NATURAL GAS OCCURRED WHEN VALVE 1-25 OPENED AS PART OF COMMISSIONING ACTIVITIES. VALVE 1-25 WAS UNINTENTIONALLY OPENED ALLOWING GAS TO ENTER PIPING THAT WAS INTENDED TO BE ISOLATED. THE SEGMENT WAS ISOLATED DUE TO CONSTRUCTION AND ABANDONMENT WORK OCCURRING ON THE DOWNSTREAM PIPING WHERE A CAP THAT HAD BEEN TACKED IN PLACE WAS DISLODGED AND PROPELLED THROUGH A COMPRESSOR BUILDING WALL. IMMEDIATE ACTIONS AT THE TIME OF THE INCIDENT INCLUDED CLOSING VALVE 1-25 WITHIN 90 SECONDS, STOPPING THE RELEASE OF GAS AND SECURING THE SITE. THE SITE WAS SECURED SUBSEQUENTLY WITH A NEW ISOLATION PLAN IMPLEMENTED PRIOR TO ANY ADDITIONAL WORK CONTINUING AT THE STATION. FOLLOWING THE EVENT, NINE PERSONNEL ON SITE AT THE TIME WERE SENT FOR DRUG AND ALCOHOL TESTING AND OPERATOR QUALIFICATIONS WERE SUSPENDED. IT WAS DETERMINED THAT DURING THE EVENT, VALVE 1-25 WAS ABLE TO BE OPENED BECAUSE IT WAS NOT DISCONNECTED FROM POWER GAS, LOCKED OUT, OR TAGGED OUT IN ACCORDANCE WITH TC ENERGY'S "LOCKOUT AND TAGOUT PROCEDURE (CAN-US-MEX)". TC ENERGY DETERMINED THAT ITS LOCKOUT AND TAGOUT (LOTO) PROCEDURES AND THE ISOLATION PLAN DEVELOPED FOR THE PROJECT WERE NOT FOLLOWED. TC ENERGY (OWNER OF ANR PIPELINE COMPANY) HAS COMPLETED A REVIEW OF THE EVENT AT EUNICE COMPRESSOR STATION AND IS CURRENTLY UPDATING PROCEDURES AND PROCESSES. TO PREVENT RECURRENCE OF SIMILAR EVENTS IN THE FUTURE, TC ENERGY IS CREATING A NEW LOCKOUT AND TAGOUT PROCEDURE (US) AND UPDATING THE GAS HANDLING PROCEDURE (US). THESE UPDATES ARE TARGETED TO BECOME EFFECTIVE JULY 1, 2022. IN ADDITION, TC ENERGY HAS CREATED NEW POSITIONS WITHIN THE ORGANIZATION CALLED THE ENERGY ISOLATION & GAS HANDLING TECHNICAL (EIGHT) ADVISOR. THESE ADVISORS WILL BE PLACED THROUGHOUT TC ENERGY'S/ANR PIPELINE COMPANY'S US GAS OPERATIONS AND WILL PROVIDE PROACTIVE SUBJECT MATTER EXPERT SUPPORT ON ENERGY ISOLATION AND GAS HANDLING. TC ENERGY INTENDS TO HAVE THE ADVISOR ROLES FILLED BY END OF YEAR 2022.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210100 | 35965 | 2021-10-25 11:43 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-09-26 11:45 | 2021 | CENTRAL | YES | 28.2353 | -91.7053 | 1317910 | 2021-09-26 12:13 | 1318019, 1318243 | NATURAL GAS |  | 300 | 2974.6 | 19 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-09-27 07:25 | 2021-09-30 16:35 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-09-27 07:30 | VALVE CLOSURE |  | 2021-09-27 12:20 | 0 | 2021-09-27 16:30 | 2021-09-27 00:04 | OFFSHORE | [6 empty] | SEA ROBIN EI BLOCK 330 | SEGMENT # 3787 LINE 716-10 | [20 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | EUGENE ISLAND | 330 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 | NO | 0.438 | 52000 | API 5L X-52 | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | YES | [26 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 318 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 16241 | 16568.260587431698604 | 1638 | 1638 | 375000 | 382556.3524590165 | 75000 | 76511.2704918033 | 0 | 0 |  | 5.46 | 467879 | 210907.1027389917425932790697674418604651 | 477273.883538251498604 | 0 | 0 | 0 | 0 | NO |  |  |  | 1080 | 10 | 1306 | 192.619(A)(1) |  | 1977-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 31680 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  | YES | MULTIPLE DIAMETER PIPE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PLATFORM PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  | YES | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NICKLAS PAVLOVSKY | DOT COMPLIANCE SPECIALIST | nicklas.pavlovsky@energytransfer.com | 713-989-4527 |  |  |  |  | GARRETT RAY | MANAGER - REGULATORY COMPLIANCE | 713-989-7225 | garrett.ray@energytransfer.com | AT APPROXIMATELY 1145 HRS. ON THE MORNING OF 9/26/2021, SEA ROBIN GAS CONTROL WAS NOTIFIED BY EI 331 RENAISSANCE PERSONNEL OF BUBBLES AND SHEEN SPOTTED IN THE EI 330 BLOCK AREA. CALL WAS MADE TO RENAISSANCE EI 331 PLATFORM TO GET SPECIFICS AND COORDINATES OF THE LEAK SITE. A CALL WAS MADE TO THE NRC AT 1213 HRS. TO REPORT THE LEAK, AT WHICH TIME THE EMPLOYEE WAS INFORMED BY THE NRC ON DUTY OFFICER THAT QUARTER NORTH ENERGY HAD ALSO REPORTED THE LEAK AND TOOK RESPONSIBILITY. QUARTER NORTH WAS ABLE TO SECURE THE TRITON EXPLORER DIVE VESSEL ON THE EVENING OF 9/26/21, TO HEAD TOWARDS THE LEAK LOCATION TO BEGIN A FORMAL INVESTIGATION. ONCE THE DIVE VESSEL REACHED ITS DESTINATION ON THE MORNING OF 9/27/21, IT BECAME APPARENT THAT THE ACTUAL LEAK SITE WAS ALSO IN THE VICINITY OF SEA ROBIN 12INCH SEGMENT #3787 AND SEA ROBIN 24INCH SEGMENT #15532. CALLS WERE MADE TO ALL PRODUCERS TIED INTO SEGMENT #3787 AND HAD THEM SHUT IN UNTIL FURTHER INVESTIGATION COULD BE COMPLETED. BY 1220 HRS. ON 9/27/21, ALL VALVES UPSTREAM AND DOWNSTREAM OF THE LEAK LOCATION WERE ISOLATED ON SEGMENT #3787. AFTER FURTHER INVESTIGATION BY THE DIVE VESSEL, THE LEAK WAS FOUND EMITTING FROM UNDER SEVERAL LAYERS OF 3/1 CEMENT BAGS AT THE 12INCH X 24INCH CROSSING. AT APPROXIMATELY 1600 HRS. ON 9/27/21, SEA ROBIN TOOK RESPONSIBILITY AWAY FROM QUARTER NORTH AND PICKED UP THE DIVE VESSEL TO EVALUATE THE LEAK WHICH WAS FOUND COMING FROM THE 12INCH SEGMENT #3787 AND MAKE NECESSARY REPAIRS. ARENA EI 338 PLATFORM ASSISTED AND BEGAN BLOWING DOWN SEGMENT #3787. AGAIN, A CALL WAS PLACED TO THE NRC AT 1635 HRS. ON 9/27/21 TO ACCEPT RESPONSIBILITY ON BEHALF OF SEA ROBIN PIPELINE AND PROVIDE UPDATE. WE RECEIVED CONTACT INFORMATION FROM AN OPERATOR WITH QUARTER NORTH ON THE BSEE REPRESENTATIVE HE HAD BEEN DEALING WITH. A CALL WAS PLACED WITH BSEE REPRESENTATIVE TO GIVE AN UPDATE AND ACCEPT RESPONSIBILITY ON BEHALF OF SEA ROBIN PIPELINE. CALLS WERE MADE WITH PHMSA FOR PERIODIC UPDATES. NO SHEENS WERE NOTED ON 9/28/21 AS THE DIVE VESSEL CONTINUED ITS SITE PREPARATION FOR REPAIRS. BY 1015 HRS. ON 9/28/21, THE PIPELINE PRESSURE WAS BLOWN DOWN TO 162 PSI AT THE REQUEST OF THE DIVE SUPERINTENDENT TO SAFELY WORK AROUND THE LEAK SITE. DIVE WORK CONTINUED THROUGHOUT THE DAY OF 9/29/21 WITH NO VISIBLE SHEEN. CALLED NRC AT 1535 HRS. ON 9/29/21 TO MAKE 48 HR. UPDATE. ALSO CALLED BSEE AND PHMSA TO GIVE UPDATES. AT APPROXIMATELY 0600 HRS. ON 9/30/21, THE REPAIR CLAMP WAS INSTALLED AND TORQUED. EI 338 PRODUCER BEGAN PRESSURIZATION OF PIPELINE TO PERFORM LEAK CHECKS AT MULTIPLE STAGES. NO LEAKS WERE OBSERVED BY THE DIVERS OR OVERFLIGHT PERSONNEL THROUGHOUT EACH INCREASE IN PRESSURE POINTS. BY 1635 HRS. ON 9/30/21, ALL VALVES WERE IN THE OPEN POSITION AND PIPELINE WAS RESTORED TO NORMAL OPERATIONS.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20210101 | 36924 | 2021-11-10 19:39 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2021-10-12 17:28 | 2021 | CENTRAL | YES | 36.8552 | -97.4838 | 1319313 | 2021-10-12 17:48 | 1319481 | NATURAL GAS |  | 525000 | 3882 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-10-12 17:28 | 2021-10-28 16:30 |  | NO |  |  | NO | [11 empty] | 9 | 2021-10-12 17:28 | 2021-10-12 14:27 | ONSHORE | OK | 74646 | NOT WITHIN A MUNICIPALITY | GRANT | NOT APPLICABLE |  | WEBB STORAGE FIELD | WELL #9 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | UNKNOWN AT THIS TIME | [5 empty] | CLASS 1 LOCATION | NO |  | 204 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 21662 | 22098.495218579241128 | 2929500 | 2929500 | 0 | 0 | 484000 | 493752.732240437296 | 1855000 | 1892378.75683060162 | WELL LOGGING, CRANE RENTAL, TOOLS, CONSULTANTS, WELL MUD, PLUGGING WELL, LIDAR | 5.58 | 5290162 | 2984599.06811141888129772093023255813953 | 5337729.984289618157128 | 0 | 0 | 9 | 0 | NO |  |  |  | 1584 | 14000 | 1850 | OTHER | FERC DOCKET IN01-2-000 | 2000-12-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROL ROOM ACTION CONTRIBUTED TO THE CAUSE OR DETECTION OF THIS LEAK | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | SUBSURFACE GROUND DISPLACEMENT. PLEASE REFER TO THE CAUSAL FACTORS CONTAINED IN THE KIEFNER REPORT DATED JULY 26, 2022. | NO | [306 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 12702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 12708524670 | shawn.patterson@southernstar.com | ON 10/12/2021 AT 2:27 PM CDT SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) RECEIVED NOTICE FROM FIELD OPERATIONS OF GAS BUBBLING TO THE SURFACE IN THE SSCGP WEBB STORAGE FIELD. INITIAL INDICATIONS WERE A LEAK IN THE LATERAL TO WELL #22. IT WAS DECIDED TO CLOSE ALL OF THE LATERALS IN THE STORAGE FIELD AND THESE WERE CLOSED FOR EVALUATION. FOR SAFETY PURPOSES, ALL LATERALS WERE BLOWN DOWN BY 4:48 PM. GAS CONTINUED TO BUBBLE TO THE SURFACE SO THE WELL HEAD VALVES WERE ALL SHUT IN BY 5:28 PM. CLOSURE OF THE WELL HEAD VALVES INDICATED THAT THIS WOULD BE A REPORTABLE INCIDENT. AT 5:48 PM THE NRC WAS NOTIFIED. GAS CONTINUED TO BUBBLE TO SURFACE, ADDITIONAL SSCGP PERSONNEL AND WELL CONTRACTING COMPANIES WERE MOBILIZED TO BEGIN THE METHODICAL PROCESS OF LOGGING ALL OF THE WELLS IN THE STORAGE FIELD. ON 10/19/2021 A SIGNIFICANT ANOMALY WAS DISCOVERED IN WELL #9 AT 1933 FT. ON 10/19/2021, WELL #9 WAS KILLED WITH 15# MUD AND A CEMENT RETAINER WAS PLACED BELOW THE ANOMALY TO ISOLATE THE STORAGE RESERVOIR. A PLUG AND ABANDONMENT PLAN WAS SUBMITTED TO THE OKLAHOMA CORPORATION COMMISSION FOR REVIEW AND APPROVAL. ON 10/23/2021 THE CEMENT RETAINER WAS DRILLED OUT WITH COILED TUBING AND A BRIDGE PLUG WAS INSTALLED NEAR TOTAL DEPTH IN WELL #9 AND THE CASING WAS PARTIALLY FILLED WITH CEMENT AND ANOTHER BRIDGE PLUG WAS INSTALLED ON TOP OF THE CEMENT. ON 10/28/2021 AT 4:30 PM, WEBB STORAGE FIELD EXCEPT FOR WELL #9 WAS RETURNED TO SERVICE. SINCE PLUGGING WELL #9, GAS BUBBLING AT THE SURFACE HAS DECREASED NOTICEABLY. SMALL GAS BUBBLES ATTRIBUTED TO RESIDUAL GAS FROM WELL #9 CONTINUE TO SURFACE AND ARE BEING MONITORED. CONTAINED IN THIS SUPPLEMENTAL REPORT: PART E1A, CORRECTED THE ESTIMATED GAS FLOW IN PIPE AT TIME OF INCIDENT. PART G2, NATURAL FORCE DAMAGE, EARTH MOVEMENT. PLEASE REFER TO THE EXTERNAL FACTORS, CONTRIBUTING FACTORS, CAUSAL FACTORS, AND ROOT CAUSES CONTAINED IN THE KIEFNER REPORT DATED JULY 26, 2022.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210102 | 37293 | 2021-11-11 17:50 | SUPPLEMENTAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-10-17 20:30 | 2021 | CENTRAL | NO | 30.0097 | -92.7301 | 1319730 | 2021-10-18 08:23 | 1319865 | NATURAL GAS |  | 5257 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-10-18 06:48 | 2021-10-18 06:48 | ONSHORE | LA | 70548 | GUEYDAN | CAMERON PARISH | NOT APPLICABLE |  | GUEYDAN CS 346 | GUEYDAN CS 346 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE FOR THE FUEL GAS SYSTEM | 1990 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | FUEL GAS RELIEF VALVE VENTED. | CLASS 1 LOCATION | NO |  | 687 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 26390 | 26390 | 1254 | 1279.268442622951176 | 500 | 510.075136612022 | 0 | 0 |  | 5.02 | 28144 | 18105.0875309759821891627906976744186047 | 28179.343579234973176 | 0 | 0 | 0 | 0 | NO |  |  |  | 150 | 0 | 150 | OTHER | THE INCIDENT OCCURED AT THE COMPRESSOR STATION FUEL GAS SYSTEM. NOT PIPELINE. | 1990-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT FROM CONTROLLER(S) ACTIONS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE DID NOT RE-SEAT PROPERLY | [147 empty] | YES | [13 empty] | JORGE LOPEZ | MANAGER ENGINEERING CODES AND STANDARDS | jorge_lopez@kindermorgan.com | 701-609-6218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 713-369-5609 | jaime_hernandez@kindermorgan.com | ON 10/17/2021 AT APPROXIMATELY 6:48 AM, AN OPERATOR FROM NATURAL GAS PIPELINE COMPANY OF AMERICA (NGPL) ARRIVED AT STATION 346 AND HEARD GAS VENTING TO ATMOSPHERE. THE OPERATOR IMMEDIATELY STARTED THE INVESTIGATION AND DISCOVERED A FUEL GAS RELIEF VALVE OPEN ALLOWING GAS TO VENT. THE OPERATOR VERIFIED THE FUEL GAS PRESSURES MAKING SURE THEY WERE NORMAL AND THEN CLOSED THE ISOLATION VALVE BELOW THE RELIEF VALVE ENDING THE RELEASE. SUBSEQUENTLY AN EMERGENCY RESPONSE LINE (ERL) WAS INITIATED AND THE INCIDENT WAS DEEMED REPORTABLE. THE INVESTIGATION CONCLUDED THAT A GROVE FLEXFLOW REGULATOR WAS LEAKING INTERNALLY ALLOWING PRESSURE TO BUILD IN THE PIPING DOWNSTREAM. THE STATION HAS AN UPSTREAM PRESSURE MONITOR REGULATOR THAT CLOSES ON INCREASING DOWNSTREAM PRESSURE. HOWEVER, THE MONITOR REGULATOR IS NOT A POSITIVE SEAL VALVE. THUS, ALLOWED GAS TO CONTINUE TO FLOW TO THE GROVE FLEXFLOW REGULATOR. THE PRESSURE CONTINUED TO RISE UNTIL THE RELIEF VALVE ACTUATED AS DESIGNED. UPON ACTUATION, THE FUEL GAS RELIEF VALVE DID NOT RE-SEAT PROPERLY RESULTING IN A SLOW GAS RELEASE FOR APPROXIMATELY 23HRS. BECAUSE THE FUEL GAS RELIEF VALVE FAILED TO RE-SEATING PROPERLY, THIS INCIDENT WAS REPORTABLE DUE TO THE VOLUME RELEASE, WHICH WAS MORE THAN THE 3,000 MCF THRESHOLD. OPERATIONS DISCOVERED THAT THE RELIEF VALVE FAILED TO RE-SEAT DUE TO DEBRIS ACCUMULATION IN THE VALVE SEAT. IN ORDER TO PREVENT REOCCURRENCE OPERATIONS REPAIRED THE FLEXFLOW REGULATOR AND CLEANED THE FUEL GAS VALVE SEAT. IN ADDITION, CALLOUT ALARMS FOR HIGH FUEL GAS PRESSURE AND HMI CONFIGURATIONS HAVE BEEN INSTALLED FOR UNITS 1, 2 AND 3 AT NGPL COMPRESSOR STATION 346.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210103 | 35988 | 2021-11-11 17:54 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-10-16 22:36 | 2021 | EASTERN | NO | 42.1203 | -72.0028 | 1319668 | 2021-10-17 00:21 | 1319725 | NATURAL GAS |  | 4290 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-10-16 21:48 | 2021-10-16 22:45 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-10-16 22:40 | NO | [11 empty] | 0 | 2021-10-16 21:59 | 2021-10-16 22:40 | ONSHORE | MA | 01507 | CHARLTON | WORCESTER | NOT APPLICABLE |  | TGP CS 264 | TGP CS 264 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2007 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASED FROM A 4" BLOW DOWN VALVE | CLASS 2 LOCATION | NO |  | 579 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 21536 | 21536 | 3000 | 3060.450819672132 | 1000 | 1020.150273224044 | 0 | 0 |  | 5.02 | 25536 | 15930.9690376341169036544850498338870432 | 25616.601092896176 | 0 | 0 | 0 | 0 | NO |  |  |  | 557 | 551000 | 783 | 192.619(A)(1) |  | 1986-03-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER(S) ACTIONS WERE DEEMED INDEPENDENT FROM THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [27 empty] | YES | POWER SUPPLY FEEDING THE LOCAL PANEL WAS NOT SUPPLING/OUTPUTTING 24VDC POWER. | [161 empty] | JORGE LOPEZ | MANAGER ENIGNEERING CODES AND STANDARDS | jorge_lopez@kindermorgan.com | 701-609-6218 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENIGNEERING CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorga.com | ON 10/16/2021 AT 21:59 EASTERN, GAS CONTROL RECEIVED A STATION WARNING ASSOCIATED WITH TENNESSEE GAS PIPELINE (TGP) STATION 264 AND IMMEDIATELY COMMUNICATED THE WARNING TO THE OPERATIONS TECHNICIAN ON CALL. AT THE SAME TIME, A NEARBY RESIDENT CALLED THE FIRE DEPARTMENT TO REPORT LOUD NOISE AND GAS SMELL IN THE AREA. AT 22:40, THE OPERATIONS TECHNICIAN AND THE CHARLTON FIRE DEPARTMENT ARRIVED ON SITE. THE OPERATIONS TECHNICIAN STARTED HIS INVESTIGATION AND FOUND GAS VENTING THROUGH A VENT VALVE ON COMPRESSOR UNIT 1C. AT 22:45 THE OPERATION TECHNICIAN MANUALLY CLOSED, THE 4" VENT VALVE, ENDING THE EVENT. THE EVENT WAS DETERMINED TO EXCEED THE REPORTABLE THRESHOLD OF 3,000 MCF AND SUBSEQUENTLY REPORTED TO THE NRC. THE INTERNAL INCIDENT INVESTIGATION CONCLUDED THAT THE STATION WARNING OCCURRED BECAUSE UNIT 1C EXPERIENCED A FAILURE OF THE 120VDC/24VDC POWER SUPPLY THAT POWERS THE SOLAR PANEL, PLC AND ASSOCIATED I/O'S. THE PLC CONTROLS THE POSITIONS (OPEN OR CLOSE) FOR THE COMPRESSOR UNIT MANIFOLD VALVES. BECAUSE THE PLC POWER FAILED, THE MANIFOLD VALVES REMAINED IN THE LAST POSITION AND THE UNIT BLOWDOWN VALVE OPENED. THE UNIT WAS RUNNING AT THE TIME OF THE PLC FAILURE. THEREFORE, THE UNIT SHUT DOWN THE MANIFOLD VALVES AND THE BLOWDOWN VALVE REMAINED OPEN ALLOWING GAS TO VENT. IN ORDER TO PREVENT REOCCURRENCE AT TGP STATION 264, OPERATIONS WILL INSTALL A REDUNDANT POWER SUPPLY FOR UNIT 1C. IN ADDITION, OPERATIONS ISSUED AN INCIDENT FLASH FORM FOR DIVISION 10 TO EVALUATE COMPRESSOR STATIONS TO IDENTIFY UNIT MANIFOLD VALVES THAT DO NOT CLOSE OR UNIT BLOWDOWN VALVES THAT DO NOT OPEN UPON FAILURE OF UNIT PLC. THE REVIEW WILL IDENTIFY UNITS WHERE MODIFICATIONS ARE REQUIRED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210104 | 36040 | 2021-11-15 10:45 | SUPPLEMENTAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-10-22 11:50 | 2021 | CENTRAL | YES | 30.1215 | -92.0439 | 1320158 | 2021-10-22 11:50 | 1320260 | NATURAL GAS |  | 3715 | 239 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-10-22 14:05 | 2021-10-23 01:00 |  | YES | OPERATOR | 2021-10-22 13:53 | NO | [5 empty] | VALVE CLOSURE |  | 2021-10-22 14:00 | VALVE CLOSURE |  | 2021-10-22 14:00 | 0 | 2021-10-22 11:50 | 2021-10-22 12:05 | ONSHORE | LA | 70508 | Not Within a Municipality | LAFAYETTE | MILEPOST | 1.95 | INDEX 205-7 | ACADIA-VERMILION RICE IRRIGATING COMPANY, INC. | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 20 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.188 | 24000 | API 5L | SEAMLESS |  | NATIONAL PIPE | COAL TAR |  | UNKNOWN | [26 empty] | 1931 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 2.5 | 2.5 | [7 empty] | CLASS 1 LOCATION | NO |  | 104 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 1396 | 1424.129781420765424 | 21696 | 21696 | 10000 | 10201.50273224044 | 0 | 0 | 0 | 0 |  | 5.84 | 33092 | 19364.5313197810608525315614617940199336 | 33321.632513661205424 | 0 | 0 | 10 | 1 | NO |  |  |  | 530 | 1000 | 557 | 192.619(A)(1) |  | 1931-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 20592 | NO |  | YES | YES | YES |  | YES | DRESSER COUPLINGS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | YES | 210635669 |  | UTILITY OWNER | YES | YES | YES | 11 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON 10/22/2021 AT APPROXIMATELY 11:50 AM, GULF SOUTH RECEIVED A PHONE CALL THAT A FARMER HAD HIT A GULF SOUTH PIPELINE WITH THE TOOTH OF A TRACTOR IMPLEMENT. GULF SOUTH PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 12:05 PM AND CONFIRMED THE DAMAGE WAS ON GULF SOUTH'S INDEX 205-7 PIPELINE. SITE WAS SECURED BY 2:05 PM. THE PIPELINE PRESSURE DROPPED FROM APPROXIMATELY 530 PSIG TO 85 PSIG WHILE GULF SOUTH WORKED TO SECURE A METHOD TO BACK FEED THE PIPELINE. GULF SOUTH'S CUSTOMER, CENTERPOINT, REPORTED LOST SERVICE TO 10 FARM TAP RESIDENTIAL CUSTOMERS AND ONE FISH PROCESSING PLANT. ONCE BACK FEED WAS SECURED, THE PIPELINE SEGMENT WAS BLOWN DOWN TO 0 PSIG. APPROXIMATELY 2 HOURS AFTER CONFIRMATION, GULF SOUTH'S REPAIR CREW WAS ONSITE AND INSTALLED TWO WELDOVER SLEEVES. IN ADDITION TO THE PUNCTURE ON THE PIPELINE, THERE WAS A DENT CREATED BY A SECOND TOOTH OF THE FARMING IMPLEMENT THAT STRUCK THE PIPELINE. REPAIRS WERE COMPLETED THE SAME DAY. 11/24/21 CORRECT INITIAL NRC REPORT NUMBER PER PHMSA REQUEST.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210105 | 36065 | 2021-11-16 14:45 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-10-22 09:04 | 2021 | CENTRAL | YES | 34.2358 | -88.0759 | 1320145 | 2021-10-22 10:29 | 1320232 | NATURAL GAS |  | 6353 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-10-22 09:06 | 2021-10-22 18:55 |  | NO |  |  | NO | [11 empty] | 0 | 2021-10-22 09:04 | 2021-10-22 09:04 | ONSHORE | AL | 35570 | Not Within a Municipality | MARION | NOT APPLICABLE |  | 500-2 | VALVE 550-AD2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2015 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASE THROUGH COMPRESSOR STATION VENT STACK | CLASS 1 LOCATION | NO |  | 760 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 31892 | 31892 | 300 | 306.0450819672132 | 50 | 51.0075136612022 | 0 | 0 |  | 5.02 | 32242 | 21083.3318838162410430232558139534883721 | 32249.0525956284154 | 0 | 0 | 0 | 0 | NO |  |  |  | 664 | 1426000 | 936 | 192.619(C) |  | 1963-12-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS DEEMED INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | VALVE MAINTENANCE PROCEDURES WERE NOT FOLLOWED. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [135 empty] | YES | [13 empty] | DANIEL GRANT | PIPELINE ENGINEER | daniel_grant@kindermorgan.com | 7134204409 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | 7133699443 | jaime_hernandez@kindermorgan.com | ON 10/22/2021 AT 9:02AM CENTRAL TIME, AN ESD OCCURRED AT TENNESSEE GAS PIPELINE COMPANY, L.L.C. (TGP) COMPRESSOR STATION 550 IN HAMILTON, ALABAMA. AT APPROXIMATELY 9:04AM TGP PERSONNEL AT THE STATION BEGAN TO NOTICE THAT THE STATION WAS NOT ISOLATED. ESD VALVE 550-AD2 WAS FOUND IN THE OPEN POSITION ALLOWING GAS TO PASS THROUGH AND OUT OF THE VENT STACK. AT APPROXIMATELY 9:06AM THE VALVE WAS SHUT, ENDING THE EVENT. AT APPROXIMATELY 9:54AM, THE GAS RELEASE WAS DETERMINED TO EXCEED THE REPORTABLE THRESHOLD OF 3,000 MCF. THE EVENT WAS SUBSEQUENTLY REPORTED TO THE NRC AT 10:29AM. DURING THE INVESTIGATION, IT WAS FOUND THAT THE PILOT ON THE ESD VALVE CONTROLLER FOR VALVE 550-AD2 HAD FAILED DURING THE ESD AND DID NOT ALLOW ENOUGH GAS TO PASS THROUGH AND ACTUATE THE VALVE. THE PILOT WAS REPLACED AND THE STATION WAS RETURNED TO SERVICE AT 6:55PM ON 10/22/2021. THE ESD WAS TRIGGERED BY AN INADVERTENT KEY TURN IN THE CONTROL CABIN OF THE STATION, CAUSED BY CLOTHING ON A CONTRACTOR CATCHING AND TURNING THE KEY ON THE PANEL AS THE INDIVIDUAL WAS PASSING BY. THE INVESTIGATION INTO THE FAILURE OF THE PILOT ON VALVE 550-AD2 REVEALED THAT, PER THE MANUFACTURER, THE LIFE EXPECTANCY OF THE PILOT WAS ONE YEAR. THE PILOT HAD BEEN IN-SERVICE SINCE 2015. AT STATION 550, TGP WILL REVIEW THE LIFE EXPECTANCY OF ALL ESD PILOTS AND REPLACE ANY THAT ARE PAST THE LIFE EXPECTANCY STATED BY THE MANUFACTURER. TGP REVOKED OQ'S PERTAINING TO THE AUTOMATED VALVE MAINTENANCE TASK FOR THE INDIVIDUALS WHO SERVICED ESD VALVE 550-AD2. THOSE INDIVIDUALS WILL BE RETRAINED ON VALVE MAINTENANCE PROCEDURES. THE ANSWER TO QUESTION E1A WAS UPDATED AND THE ANSWERS TO A8 AND D7G WERE CORRECTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210106 | 36007 | 2021-11-16 16:25 | SUPPLEMENTAL FINAL | 19270 | TEXAS GAS TRANSMISSION, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2021-10-15 07:00 | 2021 | CENTRAL | YES | 37.2961 | -87.3139 | 1320057 | 2021-10-21 12:28 | 1320156 | NATURAL GAS |  | 131 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-CONSTRUCTION COMMISSIONING | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-10-15 08:00 | VALVE CLOSURE |  | 2021-10-15 08:00 | 0 | 2021-10-15 07:00 | 2021-10-15 07:00 | ONSHORE | KY | 42325 | Not Within a Municipality | MUHLENBERG | NOT APPLICABLE |  | MIDLAND 3 COMPRESSOR STATION YARD | MIDLAND 3 COMPRESSOR STATION YARD | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.625 | 65000 | API 5L | DSAW |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 2005 | 2005 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 695 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 765 | 765 | 355000 | 362153.34699453562 | 0 | 0 | 0 | 0 |  | 5.84 | 355765 | 160270.1383026524599169435215946843853821 | 362918.34699453562 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 0 | 1000 | 192.619(A)(1) |  | 1973-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 100 | NO | [5 empty] | YES | LEAK WAS IN STATION VALVE YARD | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | STAGNANT FLUIDS (DEAD END DUE TO CLOSED VALVE) | YES | [6 empty] | YES | YES | DEAD-LEG | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | TEXAS GAS'S MIDLAND 3 COMPRESSOR STATION YARD PIPING WAS BEING RE-PRESSURIZED FOLLOWING CONSTRUCTION AND ROUTINE MAINTENANCE ACTIVITIES. THE AFFECTED AREA WAS PRESSURIZED LATE IN THE DAY AND LEFT OVERNIGHT. UPON RETURN ON 10/15/21 AT APPROXIMATELY 7:00 AM, BUBBLING WAS DISCOVERED BY THE AREA MANAGER AS HE PASSED THE AREA. THE SUSPECTED LEAK AREA WAS ISOLATED AND BLOWN DOWN. THE LEAK CAUSE IS SUSPECTED TO BE INTERNAL CORROSION DUE TO SLUDGE. FOR THIS REASON, TEXAS GAS DECIDED TO REPLACE THE PIPE BETWEEN FITTINGS AND INSTALL A LOW-POINT DRAIN. ONCE THIS DECISION WAS MADE, IT WAS DETERMINED THAT THE COST OF REPAIRS WOULD EXCEED THE $122,000 THRESHOLD FOR INCIDENT REPORTING AND NOTIFICATION WAS MADE TO THE NRC. TEXAS GAS ALSO SCANNED THE ENTIRE HEADER AND INSTALLED A SLEEVE ON AN AREA WHERE CORROSION WAS IDENTIFIED. THE REPAIRS WERE COMPLETED ON 11/11/21. IN RESPONSE TO PART G, QUESTION 13, WHILE THIS PARTICULAR LOCATION IS NOT MONITORED WITH CORROSION COUPONS, TEXAS GAS DOES MONITOR FOR CORROSION IN THE STORAGE FIELD.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210107 | 36441 | 2021-11-18 13:45 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2021-10-20 08:25 | 2021 | EASTERN | YES | 37.993 | -86.0841 | 1319916 | 2021-10-20 09:53 | 1320275 | NATURAL GAS |  | 11163 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-10-20 09:06 |  | YES | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-10-20 09:06 | VALVE CLOSURE |  | 2021-10-20 09:06 | 0 | 2021-10-20 08:25 | 2021-10-20 08:45 | ONSHORE | KY | 40108 | BRANDENBURG | MEADE COUNTY | NOT APPLICABLE |  | DOE RUN STORAGE FIELD | DRKY FERRY HILL TRUNK/315884 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8.625 |  | 0.188 | 52000 | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1950 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 84.6 | 14.3 |  | CLASS 1 LOCATION | NO |  | 96 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 48671 | 48671 | 152484 | 155556.594262295125296 | 200 | 204.0300546448088 | 0 | 0 |  | 4.36 | 201355 | 100650.9126239039693526511627906976744186 | 204431.624316939934096 | 0 | 0 | 0 | 0 | NO |  |  |  | 234 | 1704 | 305 | 192.619(C) |  | 1970-07-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 5400 | NO | YES |  | YES | YES |  | YES | LACK OF INLINE INSPECTION TOOL LAUNCHERS AND RECEIVERS. | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INJECTION OPERATIONS WERE UNDERWAY IN STORAGE FIELD WHICH RESULTED IN STORAGE FIELD WELLS BACK-FEEDING GAS TO RUPTURE SITE. A PRESSURE REDUCTION WOULD HAVE NOT BEEN VISIBLE TO CONTROLLERS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | OTHER | SELECTIVE SEAM WELD CORROSION | YES | YES | [5 empty] | YES |  |  | YES | [5 empty] | NO | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | PETER J. CLYDE | MANAGER GAS T AND D INTEGRITY AND COMPLIANCE | peter.clyde@lge-ku.com | (502) 364-8715 |  |  |  |  | J. GREGORY CORNETT | VICE PRESIDENT DEPUTY GENERAL COUNSEL | 502-627-2756 | gcornett@pplweb.com | ON OCTOBER 20, 2021 AT APPROXIMATELY 08:25 A.M. OPERATOR WAS NOTIFIED BY LANDOWNER OF PIPELINE RUPTURE NEAR BRANDENBURG, KENTUCKY, RESULTING IN AN UNCONTROLLED NATURAL GAS RELEASE. OPERATOR ARRIVED ON SITE AT APPROXIMATELY 08:45 A.M. AND THE VALVES WERE ISOLATED BY 09:06 A.M. RUPTURE OCCURRED ON AN 8-INCH CARBON STEEL PIPELINE LOCATED IN THE DOE RUN STORAGE FIELD. THE RUPTURE DID NOT CAUSE ANY INJURIES OR SIGNIFICANT THIRD-PARTY PROPERTY DAMAGE. NO IGNITION OF GAS OCCURRED DURING THIS EVENT. A SECTION OF THE PIPELINE MEASURING 7,677 FEET, INCLUDING THE SEGMENT OF PIPING INVOLVED IN THIS INCIDENT, WAS ABANDONED. THE BULK OF THE ABANDONED PIPE HAD BEEN ISOLATED BY VALVES DURING THE INCIDENT RESPONSE. SELECTIVE SEAM INTERNAL WELD CORROSION WAS IDENTIFIED AS THE CAUSE OF THE INCIDENT. LINE PIPE METALLURGY AND PIPELINE CONSTRUCTION ALSO WERE CONTRIBUTING FACTORS IN THE RUPTURE. EARLY VINTAGE (PRE-1970S) ERW LINE PIPE IS PARTICULARLY SUSCEPTIBLE TO SELECTIVE SEAM WELD CORROSION AS A RESULT OF THE STEEL CHEMISTRY AND THE ABSENCE OF A POST WELD HEAT TREATMENT THAT FULLY NORMALIZED THE SEAM WELD OF THE LINE PIPE. INSTALLING THE SEAM WELD NEAR THE 6:00 ORIENTATION CONTRIBUTED TO THE INCIDENT AS WELL BECAUSE ANY WATER AND/OR DEPOSITS THAT ACCUMULATE IN THE PIPE WILL BE IN CONTACT WITH THE CORROSION-SUSCEPTIBLE MICROSTRUCTURE OF THE SEAM WELD.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210108 | 36336 | 2021-11-19 09:56 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2021-10-29 16:04 | 2021 | EASTERN | YES | 34.739 | -79.2003 | 1320823 | 2021-10-30 12:05 | 1320920 | NATURAL GAS |  | 532.7 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-11-02 01:11 | 2021-11-02 12:32 |  | YES | OPERATOR | 2021-10-29 | NO | [5 empty] | OPERATIONAL CONTROL | A BYPASS WAS INSTALLED WHILE THE DAMAGED SECTION OF PIPE WAS REPLACED. UNABLE TO MAKE DETERMINATION |  | OPERATIONAL CONTROL | A BYPASS WAS INSTALLED WHILE THE DAMAGED SECTION OF PIPE WAS REPLACED. UNABLE TO MAKE DETERMINATION |  | 0 | 2021-10-29 16:04 | 2021-10-29 16:47 | ONSHORE | NC | 28364 | PEMBROKE | ROBESON | NOT APPLICABLE |  | LINE 5 | LINE 5 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.219 | 42000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | 3/8 INCH HOLE DISCOVERED IN EXPOSED PIPE. SEE NARRATIVE. | CLASS 2 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 2397 | 2397 | 120000 | 122418.03278688528 | 120000 | 122418.03278688528 | 0 | 0 |  | 4.5 | 242397 | 109585.0774739938580730897009966777408638 | 247233.06557377056 | 0 | 0 | 0 | 0 | NO |  |  |  | 502 | 24000 | 885 | 192.619(A)(1) |  | 1959-05-05 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 30782 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS OPERATING NORMALLY WHEN THE LEAK WAS DISCOVERED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | UNDETERMINED. SEE NARRATIVE. | [251 empty] | CHRISTOPHER RANSOME | GAS REGULATORY ANALYST | christopher.ransome@duke-energy.com | (704) 731-4680 |  |  |  |  | FARRIS BERRY | MANAGER PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | ON OCTOBER 29, 2021, AT APPROXIMATELY 3:00 PM, A NEARBY RESIDENT REPORTED A GAS LEAK CLOSE TO THE ADDRESS OF 625 WL MOORE WOODS ROAD, PEMBROKE, NC; MORE SPECIFICALLY, ALONG THE RIGHT-OF-WAY FOR TRANSMISSION LINE #5, WHICH IS A NATURAL GAS PIPELINE THAT RUNS FROM PEMBROKE TO GREENVILLE, NC. UPON ARRIVAL, OPERATOR DETERMINED LINE #5 WAS LEAKING AND DAMAGE TO THE PIPELINE IN THE FORM OF A SMALL HOLE WAS IDENTIFIED. THE DAMAGE OCCURRED TO AN EXPOSED SECTION OF TRANSMISSION LINE #5 THAT WAS EXCAVATED EARLIER THAT DAY AS PART OF AN ILI ASSESSMENT ANOMALY DIG. THERE WAS NO LEAK ON THE LINE WHEN IT WAS EXPOSED. THE DAMAGE RESEMBLED A BULLET HOLE. WHILE SHELL CASINGS WERE FOUND APPROXIMATELY 200 YARDS AWAY FROM THE LOCATION OF THE LEAK, NO SHELL CASINGS WERE FOUND IN THE IMMEDIATE VICINITY OF THE DAMAGED PIPELINE. NEARBY RESIDENTS STATED THAT THE DISCHARGE OF FIREARMS FOR HUNTING OR SPORTING IS COMMON IN THE AREA. NO OTHER SECTIONS OF THE PIPELINE WERE FOUND DAMAGED. FEDERAL AND STATE LAW ENFORCEMENT WERE CONTACTED. A BYPASS WAS INSTALLED WHILE THE DAMAGED SECTION OF PIPE WAS REPLACED. INVESTIGATIONS WERE UNABLE TO MAKE A DEFINITIVE DETERMINATION ON THE CAUSE OF THE HOLE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210109 | 36023 | 2021-11-19 12:45 | ORIGINAL FINAL | 39193 | ROVER PIPELINE, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-10-22 19:36 | 2021 | EASTERN | YES | 40.2528 | -81.0258 | 1320188 | 2021-10-22 22:00 | 1320190 | NATURAL GAS |  | 5074 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | TUBING WAS ISOLATED AND REPAIRED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-10-22 19:36 | 2021-10-22 19:36 | ONSHORE | OH | 43907 | CADIZ | HARRISON | MILEPOST | 0 | ROVER PIPELINE | CADIZ STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2017 | 2017 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | YES | METHOD2 | 831 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 25979 | 25979 | 5 | 5.10075136612022 | 0 | 0 | 0 | 0 |  | 5.12 | 25984 | 17048.2718508319263670598006644518272425 | 25984.10075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 1070 | 704.85 | 1440 | 192.619(A)(2) |  | 2017-09-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [20 empty] | YES | [177 empty] | NICKLAS PAVLOVSKY | DOT COMPLIANCE SPECIALIST | nicklas.pavlovsky@energytransfer.com | 713-989-4527 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON OCTOBER 22, 2021, OPERATIONS WERE NOTIFIED OF A GAS RELEASE AT THE CADIZ STATION, ONCE FIELD PERSONNEL ARRIVED ON SITE AT 19:36 THE COMPRESSOR WAS ISOLATED. AT 21:51 IT WAS DETERMINED THAT THE VOLUME WOULD EXCEED 3 MILLION CUBIC FEET; SO, CALL WAS PLACED TO THE NRC AT 22:00. NRC # 1320188. IT WAS DETERMINED THAT THE U-BOLT HOLDING THE PSV TUBING FAILED AND WITH THE VIBRATION OF THE COMPRESSOR, THE TUBING SEPARATED FROM THE PSV RESULTING IN THE RELEASE OF 5 MMCF OF NATURAL GAS. THE TUBING WAS RE-ATTACHED, AND A NEW U-BOLT WAS INSTALLED TO PREVENT THE VIBRATION FROM DISLODGING THE TUBING. THE COMPRESSOR WAS RESTARTED AFTER WORK WAS COMPLETE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210110 | 36591 | 2021-12-01 16:03 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2021-11-12 21:00 | 2021 | CENTRAL | NO | 42.282 | -93.2815 | 1321904 | 2021-11-12 22:05 | 1321930 | NATURAL GAS |  | 8375 | 2975 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-CONSTRUCTION COMMISSIONING | [5 empty] | YES | OPERATOR | 2021-11-12 22:05 | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE WAS REDUCED UPSTREAM TO SAFELY APPROACH THE LOCATION. |  | OPERATIONAL CONTROL | PRESSURE WAS REDUCED UPSTREAM TO SAFELY APPROACH THE LOCATION. |  | 3 | 2021-11-12 10:30 | 2021-11-12 10:30 | ONSHORE | IA | 50122 | Not Within a Municipality | HARDIN | MILEPOST | 21.78 | 30" LOOP LINE FROM OGDEN COMPRESSOR STATION | M521D | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2021 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BODY BLEED PLUG WAS MISSING, CAUSING THE LOCATION OF THE RELEASE. | CLASS 1 LOCATION | NO |  | 692 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 14012 | 14294.345628415304528 | 39446 | 39446 | 1700181 | 1734440.111680328351964 | 840 | 856.92622950819696 | 0 | 0 |  | 4.71 | 1754479 | 797735.0524898226554013322259136212624585 | 1789037.383538251853452 | 0 | 0 | 2 | 0 | NO |  |  |  | 800 | 211 | 1000 | 192.619(A)(2) |  | 1997-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 44246 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM HAD NO IMPACT TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [5 empty] | YES |  |  | CONSTRUCTION | NO | [145 empty] | YES |  |  |  | YES | DAVID CULLISON |  | david.cullison@nngco.com | 402-398-7439 |  |  |  |  | TOM CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | ON NOVEMBER 12, 2021, NEW VALVES WERE BEING MANIPULATED FOR COMMISIONING AND LUBRICATION. AT 10:30, A 30 INCH BYPASS VALVE WAS MANIPULATED WHEN THEN GROUND WAS REPORTED TO RAISE AND SETTLE WITH A MUFFLED SOUND. THE ON-SITE PERSONNEL EVACUATED THE LOCATION TO REPORT THE EVENT. INITIAL REPORTING DID NOT SEE ANY PRESSURE CHANGES ON SCADA, AND DUE TO EXTREMLEY HIGH WINDS, NO VISUAL OR AUDIBLE INDICATIONS COULD BE MADE OF VENTING GAS. A PLAN WAS CREATED TO REDUCE PRESSURE TO 600 POUNDS FOR THE B, C AND D LINES AS THEY WERE ALL IN COMMON AT THE LOCATION. AT 21:00, IT WAS REPORTED THAT AS TECHNICIANS APPROACHED THE VALVE SETTING, THE LEL MONITORING EQUIPMENT DETECTED GAS APPROXIMATELY 100 YARDS UPWIND OF THE VALVE ASSEMBLY. THE PIPELINE WAS ISOLATED AT 1555 ON NOVEMBER 14, 2021. EXCAVATION OF THE VALVE FOUND THAT A 1.5 INCH DIAMETER BODY BLEED PLUG WAS MISSING, CONCLUDING IT WAS NOT INSTALLED OR IMPROPERLY INSTALLED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210111 | 37128 | 2021-12-03 15:52 | SUPPLEMENTAL | 2392 | CITIZENS GAS & COKE UTILITY | 2020 NORTH MERIDAN ST | INDIANAPOLIS | IN | 46202 | 2021-11-05 02:37 | 2021 | EASTERN | YES | 39.7789 | -86.2508 | 1321225 | 2021-11-05 02:37 | 1321259 | NATURAL GAS |  | 559.97 | 76.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-11-05 02:44 | 2021-11-12 16:30 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-11-05 02:44 | VALVE CLOSURE |  | 2021-11-05 02:44 | 0 | 2021-11-05 01:30 | 2021-11-05 01:30 | ONSHORE | IN | 46224 | INDIANAPOLIS | MARION | NOT APPLICABLE |  | WEST LEG | GMN116405 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.312 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1960 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD1 | 267 |  | NO | NO | [5 empty] | 0 | 0 | 413 | 421.322062841530172 | 3013 | 3013 | 0 | 0 | 0 | 0 | 0 | 0 | THERE WAS NO PROPERTY DAMAGE. | 5.38 | 3426 | 2162.839596325091341066445182724252491694 | 3434.322062841530172 | 0 | 0 | 0 | 0 | NO |  |  |  | 320 | 1200 | 375 | 192.619(A)(3) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 41597 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [22 empty] | YES | [8 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | Yes, but the point of the Accident was not identified as a dig site |  | 2021 | 2021 | [5 empty] | YES |  |  |  |  | NO | [63 empty] | BENJAMIN S. WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | bwarren@citizensenergygroup.com | 3179274622 |  |  |  |  | BENJAMIN S. WARREN | DIRECTOR GAS TRANSMISSION AND DISTRIBUTION | 3179274622 | bwarren@citizensenergygorup.com | A CRACK OCCURRED ON A 20" NATURAL GAS TRANSMISSION PIPELINE. THERE WERE NO INJURIES, NO IGNITION AND NO PROPERTY DAMAGE AS A RESULT OF THIS FAILURE. APPROXIMATELY 560 MCF OF NATURAL GAS WAS RELEASED TO ATMOSPHERE, THIS INCLUDES INTENTIONAL AND UNINTENTIONAL. THE APPROXIMATE 10" LINEAR CRACK IS IN THE PROXIMITY OF 3:00 ON THE 20" CEG TRANSMISSION PIPELINE AND WAS WITHIN 1" OF A4" WELDED TIE IN. (NOT SURE ON THE NATURE OF THE CRACK, THE LAB ANALYSIS WILL HELP DETERMINE ROOT CAUSE.) THE SECTION OF PIPE, INCLUDING THE 4" TIE IN, WAS REMOVED AND SENT FOR A LABORATORY ANALYSIS. LAB RESULTS INDICATED THE FOLLOWING: "THE 20' GAS MAIN FAILURE WAS CAUSED BY A SUDDEN OVERLOAD CONDITION. THIS INTRODUCED A THROUGH WALL CRACK IN THE LENGTHWISE DIRECTION AT THE 12 O'CLOCK LOCATION ADJACENT TO THE WELD JOINT BETWEEN THE MAIN LINE AND THE LATERAL LINE. THE CRACK INITIATED ON THE OD SURFACE AND PROPAGATED UNDER A FAST AND SUDDEN OVERLOAD CONDITION, AS INDICATED BY THE BRITTLE CLEAVAGE FRACTURE MORPHOLOGY. THIS IS CONSISTENT WITH THE SCENARIO IF THE 4' LATERAL LINE IS IMPROPERLY SUPPORTED BY THE BACKFILL. THE PIPELINE HAS A SUCCESSFUL SERVICE HISTORY SINCE 1969. THE FAILURE OCCURRED AFTER A LENGTH OF 10' OF THE 4' LATERAL PIPE WAS EXPOSED AND SUBJECTED TO SOIL REMOVAL AND REPLACEMENT. THE CRACK INITIATION POINT WOULD HAVE EXPERIENCED THE HIGHEST BENDING MOMENT TO INITIATE THE CRACK. OVERALL CONDITION OF THE GAS MAIN IS ACCEPTABLE WITHOUT ANY SIGNIFICANT ANOMALIES. CORROSION OR ANY OTHER ANOMALIES WERE NOTED WHICH COULD HAVE CONTRIBUTED TO THIS FAILURE. THE GAS MAIN IS IDENTIFIED TO BE A CARBON STEEL (AISI 1025) WITH A FERRITE/PEARLITE MICROSTRUCTURE; TYPICAL FOR GAS MAINS. THE PIPE ALSO MEETS THE REQUIRED SPECIFICATION ASTM A53 GRADE B. THE HARDNESS OF THE PIPE IS MEASURED AT ~80 ROCKWELL B WHICH IS AGAIN TYPICAL FOR THESE PIPES AND IS IN AGREEMENT WITH THE MICROSTRUCTURE. TENSILE AND CHARPY TESTING IS BEING PERFORMED AND WILL BE SUBMITTED IN THE MATERIAL ANALYSIS REPORT. WE DO NOT EXPECT ANY UNUSUAL TENSILE AND CHARPY TESTING RESULTS AS THE HARDNESS AND MICROSTRUCTURE IS TYPICAL OF THIS ALLOY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210112 | 36300 | 2021-12-06 08:58 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2021-11-05 23:15 | 2021 | EASTERN | NO | 44.6593 | -85.8375 | 1321306 | 2021-11-05 22:01 | 1321391 | NATURAL GAS |  | 5800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-CONSTRUCTION COMMISSIONING | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2021-11-05 01:00 | 2021-11-05 01:20 | ONSHORE | MI | 49643 | INTERLOCHEN | BENZIE | NOT APPLICABLE |  | LEELANAU GATE STATION | FRANKFORT 8-INCH PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2021 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | GAS WAS RELEASED THROUGH THE RELIEF VALVE AS DESIGNED. | CLASS 2 LOCATION | NO |  | 170 |  | NO | NO |  |  | YES |  | YES | 0 | 0 | 0 | 0 | 25695 | 25695 | 0 | 0 | 1390 | 1418.00887978142116 | 0 | 0 |  | 2.91 | 27085 | 17485.2472887506130991029900332225913621 | 27113.00887978142116 | 0 | 0 | 0 | 0 | NO |  |  |  | 507 | 41.46 | 812 | 192.624(C)(1) |  | 2021-08-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THE ROOT CAUSE WAS DETERMINED TO BE INADEQUATE PROCEDURAL ADHERENCE TO THE RETURN TO SERVICE PRESSURE CONTROL PROCEDURE (PCP) FOR THE LEELANAU GATE STATION THAT TOOK PLACE ON SEPTEMBER 20, 2021. THE INTENT OF THE PCP WAS TO RUN THE STATION ON BYPASS BUT OPERATIONS MISINTERPRETED ENGINEERING'S PLANNED FLOW PATH IN THE PCP AND OPENED A LEG OF THE STATION PIPING FOR PURGING WHICH ALLOWED THIS NEW RELIEF VALVE TO BE EXPOSED TO THIS HIGHER PRESSURE ONCE THE SYSTEM WAS REPRESSURIZED. | YES |  |  |  |  | COMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  | FRENAE F SMITH | frenae.smith@dteenergy.com | 13134601681 | FRENAE F SMITH | MANAGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | A RELIEF VALVE WENT OFF AT LEELANAU GATE STATION AT APPROXIMATELY 8:35 PM ON NOVEMBER 4, 2021 (AT THIS TIME DTE GAS WAS NOT AWARE OF THE RELEASE). DTE GAS RECEIVED A CALL OF ODOR IN THE AIR/GAS BLOWING AT 1:00 AM AND DTE DISTRIBUTION ARRIVED AT 1:20 AM. DTE GAS TRANSMISSION OPERATIONS WERE CALLED AT 1:30 AM. THE TRANSMISSION TECH ARRIVED AT 03:30 AM ON NOVEMBER 5 AND BLOCKED IN THE RELIEF, AS THERE IS NO NEED TO PROTECT A LOWER MAOP DOWNSTREAM. ONLY 1 QUALIFIED PERSON WAS AVAILABLE. HE HAD TO GET A CONFIRMATION (FROM THE OTHER TECH) TO SHUT IT IN. THE GAS CONTINUED TO BE RELEASED INTO THE AIR UNTIL APPROXIMATELY 3:30 AM ON NOVEMBER 5, RESULTING IN ODOR IN THE AIR. THIS RELEASED 5.8 MMCF OF GAS INTO THE ATMOSPHERE, MAKING IT REPORTABLE TO BOTH THE STATE OF MICHIGAN, PHMSA, AND EGLE. GAS CONTROL WAS GIVEN THE RELEASE TO BRING THE PETOSKEY/TRAVERSE CITY SYSTEM PRESSURE BACK UP (HAD BEEN ON A PRESSURE REDUCTION TO BELOW 500 PSIG SINCE JUNE, TO NORMAL LINE PRESSURE, GENERALLY JUST ABOVE 500 PSIG ) AND STARTED BRINGING PRESSURE UP TO AROUND 8:00 PM ON NOVEMBER 4, 2021. AS PART OF THE TRAVERSE CITY ALPENA REINFORCEMENT PROGRAM (TCARP), WE WERE INSTALLING A BRAND NEW STATION/TOTALLY REBUILT AN EXISTING STATION; DE-PRESSURIZED TO INSTALL THE NEW FRANKFORT LOOP PIPELINE. THERE ARE NO ALARMS ON THIS RELIEF (NO HIGH-PRESSURE ALARM BELOW RELIEF POINT) WHICH IS NOT UNUSUAL. THE RELIEF WAS PRESET TO PROTECT THE FRANKFORT PL DOWNSTREAM OF LEELANAU GATE IN THE CITY OF INTERLOCHEN. IT APPEARS LIKE IT DID PROTECT THE SYSTEM (THE RELIEF WENT OFF) AT APPROXIMATELY 507-513 PSIG. THERE WAS NO RETURN TO SERVICE PROCEDURE FOR THE PETOSKEY SYSTEM TO STIPULATE THE NEED FOR A RELIEF OR THE NEED TO BLOCK IN THE RELIEF. THE 8" DOWNSTREAM PIPELINE STILL HAD AN 812 PSIG MAOP AND HAD NOT YET BEEN DERATED TO 486 PSIG MAOP. THEREFORE, THE RELIEF VALVE SHOULD NOT HAVE BEEN PUT INTO SERVICE PRIOR TO THE DURATION. THE ROOT CAUSE WAS DETERMINED TO BE INADEQUATE PROCEDURAL ADHERENCE TO THE RETURN TO SERVICE PRESSURE CONTROL PROCEDURE (PCP) FOR THE LEELANAU GATE STATION THAT TOOK PLACE ON SEPTEMBER 20, 2021. THE INTENT OF THE PCP WAS TO RUN THE STATION ON BYPASS BUT OPERATIONS MISINTERPRETED ENGINEERING'S PLANNED FLOW PATH IN THE PCP AND OPENED A LEG OF THE STATION PIPING FOR PURGING WHICH ALLOWED THIS NEW RELIEF VALVE TO BE EXPOSED TO THIS HIGHER PRESSURE ONCE THE SYSTEM WAS REPRESSURIZED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210113 | 36246 | 2021-12-07 11:47 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2021-11-07 13:49 | 2021 | EASTERN | YES | 40.7704 | -73.9642 | 1321382 | 2021-11-07 14:10 |  | NATURAL GAS |  | 850 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-11-07 13:49 | 2021-11-09 11:23 |  |  |  |  | NO | [5 empty] | OPERATIONAL CONTROL | FLOW MONITORED VIA SCADA. UPSTREAM SYSTEM SUPPORTED ADDITIONAL SUPPLY. NO ACTION REQUIRED. |  | VALVE CLOSURE |  | 2021-11-07 13:49 | 0 | 2021-11-07 13:49 | 2021-11-06 07:46 | ONSHORE | NY | 10021 | NEW YORK CITY | NEW YORK | NOT APPLICABLE |  | TRANSCO CENTRAL MANHATTAN | M-3 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 135 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 30 | NO | 0.5 | 35000 | UNKNOWN | OTHER | ELECTRO FUSION WELDED | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | 5/8" HOLE IN MAIN | [5 empty] | CLASS 4 LOCATION | YES | METHOD1 |  | NOT FLAMMABLE | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 4250 | 4250 | 91885 | 93736.50785519128294 | 800 | 816.1202185792352 | 95297 | 97217.260587431721068 | SUPPORT STAFF | 5 | 192232 | 87390.1514878683602147973421926910299003 | 196019.888661202239208 | 0 | 0 | 15 | 0 | NO |  |  |  | 300 | 9000 | 350 | 192.619(A)(2) |  | 1959-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  | MANUAL | 3585 | NO |  | YES | YES | YES |  |  |  | YES |  |  |  |  | YES | PIPE BEND RESTRICTIONS | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | THE SUSPECTED CAUSE WAS A A HIGH-PRESSURE STEAM LEAK BLOWING DIRECTLY ON THE GAS TRANSMISSION MAIN | [227 empty] | YES | [23 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | leono@coned.com | 718-319-2350 |  | OSCAR LEON | leono@coned.com | 718-319-2350 | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 718-319-2350 | leono@coned.com | ON 11/6/21 AT 07:26, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A REPORT FROM ITS CUSTOMER OPS. CALL CENTER OF A GAS ODOR INSIDE AND OUTSIDE OF A RESIDENTIAL BUILDING LOCATED AT 733 PARK AVE. THE GAS ODOR HAD BEEN REPORTED TO THE CALL CENTER BY AN OCCUPANT OF THE SAME BUILDING. THE AREA IS SUPPLIED BY A 6-INCH LOW-PRESSURE CAST IRON GAS MAIN (INSTALLED IN 1897) AND A 30-INCH STEEL GAS TRANSMISSION MAIN (INSTALLED IN 1959), AS WELL AS UNDERGROUND ELECTRIC FACILITIES. CON EDISON GAS DISTRIBUTION SERVICES (GDS) RESPONDED TO THE LOCATION, INVESTIGATED, AND REPORTED A TYPE 1 GAS LEAK, WITH A NATURAL GAS READING OF 0.4% DETECTED IN THE GAS POINT-OF-ENTRY (POE) AT 733 PARK AVENUE. ADDITIONALLY, GDS DETECTED NATURAL GAS READINGS OF 15% IN TWO NEARBY ELECTRIC SUBSURFACE STRUCTURES (SSS'S) MANHOLE #M41786 AND SERVICE BOX #12935; THE COVERS OF THOSE TWO SSS'S WERE REMOVE BY GDS FOR VENTING. THE GERC THEN INITIATED A CODE MURRE, NOTIFIED THE FDNY, AND DISPATCHED ADDITIONAL CON EDISON GDS SUPERVISION TO THE LOCATION. UPON FURTHER INVESTIGATION, GDS DETECTED NATURAL GAS READINGS OF 0.3% IN THE ATMOSPHERE OF TWO BUILDING BASEMENTS AT 106 & 110 E. 71ST STREET. GDS SEALED THE ELECTRIC POE'S TO THOSE BUILDINGS AND VENTED THE READINGS IN THE TWO BASEMENTS TO 0% WITH ASSISTANCE FROM THE FDNY. GDS REPORTED THAT ALL OTHER BUILDINGS AND ADJACENT SSS'S WERE CLEAR OF GAS READINGS, AND THAT ELECTRIC MH #M41786 AND SB #12935 HAD BEEN VENTED TO 0%. CON EDISON EMERGENCY GAS CONSTRUCTION PERSONNEL WERE DISPATCHED TO THE LOCATION TO PINPOINT THE SOURCE OF THE LEAK. ON 11/7/21 AT 00:50, EMERGENCY GAS CONSTRUCTION REPORTED FINDING A POTENTIAL LEAK ON THE 30-INCH TRANSMISSION MAIN AFTER DETECTING NATURAL GAS READINGS OF ~100% IN THE VICINITY OF THE MAIN. ALL ADJACENT SSS'S, BUILDINGS, AND PROTECTION TEST POINTS WERE CHECKED AND FOUND TO BE CLEAR OF GAS READINGS. THE TRANSMISSION MAIN WAS OPERATING AT ~300 PSIG. NO OUTAGES OR NEGATIVE GAS SYSTEM IMPACT WERE REPORTED. GAS TRANSMISSION ENGINEERING AND GAS CONTROL WERE NOTIFIED OF THE POTENTIAL TRANSMISSION MAIN LEAK. CONTINGENCY CASE 6-C WAS ESTABLISHED AND PUT INTO EFFECT, AND GAS OPERATIONS PERSONNEL WERE ASSIGNED TO STAFF MULTIPLE MAIN VALVES AS PART OF THE CONTINGENCY. GAS OPERATIONS CREWS REMAINED ON LOCATION AND MONITORED THE CONDITION THROUGHOUT THE NIGHT. ON 11/7/21 AT 13:49, TWO TRANSMISSION MAIN VALVES WERE CLOSED TO ISOLATE A SEGMENT OF THE 30-INCH TRANSMISSION MAIN DUE TO THE LEAK CONDITION, WHICH APPEARED TO PROGRESSIVELY WORSEN. THE ISOLATION OF THE TRANSMISSION MAIN INTERRUPTED SERVICE TO FIFTEEN (15) GAS SERVICES AND NINE HUNDRED THIRTY-TWO (932) CUSTOMERS. CON EDISON GAS CONTROL ISSUED A LIMIT WORK ORDER AND A CONDITION YELLOW SYSTEM STATUS. CONSTRUCTION ACTIVITIES BEGAN AND THE COATING ON THE TRANSMISSION MAIN WAS SAFELY REMOVED. ONCE FULLY EXPOSED, A LEAK WAS FOUND ON THE TRANSMISSION MAIN AT THE 1 O'CLOCK POSITION. A NITROGEN BARRIER WAS INSTALLED, AND A HIGH HAT (A PERMANENT STEEL CAP) WAS WELDED OVER THE LEAK THAT WAS FOUND ON THE BODY OF THE TRANSMISSION MAIN. A PRESSURE TEST WAS CONDUCTED, AND THE TEST PASSED. TRANSMISSION PRESSURE WAS REINTRODUCED TO THE MAIN UP TO FULL OPERATING PRESSURE (327 PSIG) AT 50 PSIG INCREMENTS WITH LEAK SURVEYS CONDUCTED OVER THE AFFECTED AREA AT EVERY INCREMENTAL PRESSURE INCREASE, WITHOUT ANY FURTHER LEAKS DETECTED. THE REPAIR PROCEDURE WAS SUCCESSFULLY COMPLETED, AND SERVICE WAS SAFELY RESTORED ON 11/9/21 AT 18:09. THE SUSPECTED CAUSE OF THE NATURAL GAS LEAK WAS A HIGH-PRESSURE STEAM LEAK THAT WAS BLOWING DIRECTLY ON THE GAS TRANSMISSION MAIN. THERE WERE NO REPORTED INJURIES OR EVACUATIONS ASSOCIATED WITH THIS INCIDENT. NOTIFICATIONS WERE MADE TO PSC, DEP AND PHMSA.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20210114 | 36119 | 2021-12-13 11:11 | SUPPLEMENTAL FINAL | 38987 | KINETICA ENERGY EXPRESS LLC | 1001 MCKINNEY STREET, SUITE 900 | HOUSTON | TX | 77002 | 2021-10-31 14:05 | 2021 | CENTRAL | NO | 29.6324 | -93.0383 | 1320885 | 2021-10-31 14:05 | 1321021 | NATURAL GAS |  | 260 | 10550 | 0.095 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-11-01 10:58 | 2021-11-10 13:00 |  | YES | OPERATOR | 2021-10-31 14:05 | NO | [5 empty] | VALVE CLOSURE |  | 2021-11-01 10:58 | VALVE CLOSURE |  | 2021-11-01 12:53 | 0 | 2021-10-31 14:05 | 2021-11-01 10:20 | OFFSHORE | [28 empty] | 35 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 68 | SPLASH ZONE OF RISER | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 20 | NO | 0.5 | 42000 | X-42 | DSAW |  | NATIONAL TUBE | COMPOSITE |  | YES | [26 empty] | 1970 | 1962 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 600 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 42200 | 43050.3415300546568 | 1040 | 1040 | 48000 | 48967.213114754112 | 47000 | 47947.062841530068 | 0 | 0 |  | 4 | 138240 | 62429.4207151027014897009966777408637874 | 141004.6174863388368 | 0 | 0 | 0 | 0 | NO |  |  |  | 660 | 18963 | 999 | 192.619(A)(2) |  | 1970-10-08 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 69484 | NO |  |  | YES |  |  |  |  | YES |  |  |  |  | YES | TOOL WILL NOT FIT IN LAUNCHER | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS OPERATING WELL BELOW MAOP/MOP | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KURT CHERAMIE | SENIOR VICE PRESIDENT | kurt.cheramie@kineticallc.com | 9852236165 |  | KURT CHERAMIE | kurt.cheramie@kineticallc.com | 9852236165 | KURT CHERAMIE | SENIOR VICE PRESIDENT | 9852236165 | kurt.cheramie@kineticallc.com | AT 13:25 ON 10/31/2021, KINETICA GAS CONTROL RECEIVED A CALL FROM A 3RD PARTY VESSEL REGARDING A LEAK ON A PIPELINE RISER AT KINETICA'S WC-68CG PLATFORM. OVERFLIGHT ON 11/1/2021 CONFIRMED LEAK WAS ON KINETICA PIPING. PIPELINE WAS COMPLETELY ISOLATED AT 10:58 ON 11/1/2021. BLOWDOWN COMMENCED TO REDUCE PRESSURE ON PIPELINE AT 11:00 ON 11/1/2021 AT KINETICA'S GRAND CHENIER FACILITY. AT 09:37 ON 11/8/2021, LINE WAS COMPLETELY BLOWN DOWN. DIVE VESSEL ON SITE & BEGAN SCAFFOLD INSTALLATION TO INSTALL REPAIR CLAMP. CLAMP INSTALLATION COMPLETE AND LEAK REPAIR COMPLETE AT 13:00 ON 11/10/2021.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20210115 | 36140 | 2021-12-14 15:31 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2021-11-19 01:20 | 2021 | EASTERN | YES | 38.4019 | -81.4173 | 1322483 | 2021-11-19 03:21 | 1322509 | NATURAL GAS |  | 4370 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-11-19 01:38 | 2021-11-19 04:01 |  | NO |  |  | NO | [11 empty] | 0 | 2021-11-19 01:20 | 2021-11-19 01:50 | ONSHORE | WV | 25156 | PINCH | KANAWHA | NOT APPLICABLE |  | COCO COMPRESSOR STATION | N/A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELEASE INVOLVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) BLOW-DOWN VALVE AND BLOW-OFF STACK, DESIGN TO SAFELY EVACUATE GAS FROM THE STATION. | CLASS 2 LOCATION | NO |  | 276 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 24297 | 24297 | 125 | 127.5187841530055 | 350 | 357.0525956284154 | 0 | 0 |  | 5.56 | 24772 | 16156.1580549466261331395348837209302326 | 24781.5713797814209 | 0 | 0 | 0 | 0 | NO |  |  |  | 916 | 0 | 1000 | 192.619(A)(1) |  | 2007-11-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION WAS NOT DEEMED NECESSARY BASED ON HAVING AN OPERATOR/RESPONDER (EMPLOYEE) ON-SITE DURING THE EVENT AND ACTIONS OF THE CONTROL ROOM PLAYED A MINOR ROLE DURING THE RESPONSE EFFORTS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | POSSIBLY MOISTURE IN THE VALVE ACTUATOR SENSING LINE. | [161 empty] | CHRISTOPHER L LEGG | US REGULATORY COMPLIANCE SPECIALIST | chris_legg@tcenergy.com | 304-545-4350 |  | CHRISTOPHER L LEGG | chris_legg@tcenergy.com | 304-545-4350 | LEE ROMACK | DIRECTOR US REGULATORY COMPLIANCE | 832-320-5315 | lee_romack@tcenergy.com | COCO COMPRESSOR STATION'S EMERGENCY SHUTDOWN SYSTEM (ESD) BLOWDOWN VALVE (6"- BDV#:197) UNINTENTIONALLY OPENED AT 1:02AM ON NOVEMBER 19, 2021 AND RELEASED 4370 MCF OF NATURAL GAS THROUGH THE ESD BLOW-DOWN STACK FOR APPROXIMATELY18 MINUTES BEFORE THE VALVE WAS MANUALLY CLOSED. THE OPERATING PRESSURE AT THE TIME OF THE RELEASE WAS 916 PSIG. THE STATION OPERATOR WAS ON-SITE DURING THE EVENT AND WAS ABLE TO ISOLATE THE STATION PIPING AND STOP THE RELEASE. AS PART OF THE PRELIMINARY INVESTIGATION, ICE/MOISTURE WAS FOUND IN THE PILOT CONTROL VALVE OF THE BLOW-DOWN ACTUATOR VALVE, POTENTIALLY CAUSED THE EVENT. THE ISOLATED ESD FACILITIES WERE RETURNED BACK TO SERVICE AT 4:01 AM EST AFTER THE PILOT CONTROL VALVE ASSOCIATED SENSING LINES WERE CLEARED OF MOISTURE/ICE AND INSPECTED.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20210116 | 36180 | 2021-12-28 14:44 | ORIGINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2021-12-01 11:00 | 2021 | CENTRAL | NO | 33.2015 | -96.8133 | 1323344 | 2021-12-01 14:04 | 1323550 | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | INCIDENT INVOLVED GEAR BOX ON VALVE, SO NO SHUT DOWN OF PIPELINE NEEDED |  |  |  | YES | OPERATOR | 2021-12-01 13:50 | NO | [11 empty] | 0 | 2021-12-01 11:00 | 2021-12-01 11:00 | ONSHORE | TX | 75034 | FRISCO | COLLIN | SURVEY STATION NO. | 0+10 | WN2-8 | WN2-8 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | CAMERON VALVE |  |  |  | 2018 | 2017 | CARBON STEEL |  | OTHER | [8 empty] | THE INVESTIGATION OF THIS INCIDENT IS ONGOING. THIS RESPONSE WILL BE UPDATED. | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | THE RESPONSE TO 7A-D IS SUBJECT TO THE INVESTIGATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NO |  |  |  | 340 | 1 | 728 | 192.619(A)(2) |  | 2018-04-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT INVOLVED A VALVE ON THE PIPELINE AND AN INVESTIGATION WAS NOT WARRANTED | [12 empty] | YES | 1 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | CHUCK KENNEDY | COMPLIANCE SUPERVISOR | charles.kennedy@atmosenergy.com | 601-624-6385 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-957-3295 | marlo.sutton@atmosenergy.com | ON DECEMBER 1, 2021, AT APPROXIMATELY 11:00 AM, AN ATMOS ENERGY EMPLOYEE AND A CONTRACTOR EMPLOYEE WERE ONSITE AT A VALVE SITE ON LINE WN2-8, NEAR 7786 COUNTY ROAD 24 IN FRISCO, TX. THE CONTRACTOR WAS PERFORMING MAINTENANCE ON A VALVE WHEN A PART OF THE VALVE STRUCK HIM IN THE FACE, RESULTING IN INJURY. THE ATMOS EMPLOYEE ONSITE CALLED 911, AND THE CONTRACTOR WAS TAKEN TO THE HOSPITAL AND ADMITTED FOR TREATMENT. THIS INCIDENT IS STILL UNDER INVESTIGATION. VOLUME OF GAS RELEASED (PART A 7.), IF ANY, IS STILL UNKNOWN AT THIS TIME, AND THE COST OF REPAIRS (PART D 7.) HAS NOT BEEN FINALIZED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220001 | 36289 | 2022-01-07 16:42 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2022-01-02 17:17 | 2022 | CENTRAL | NO | 40.967 | -95.9302 | 1325770 | 2022-01-02 21:40 | 1325882 | NATURAL GAS |  | 3510 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE RELIEF VALVE WAS ISOLATED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-02 17:20 | 2022-01-02 17:20 | ONSHORE | NE | 68048 | Not Within a Municipality | CASS | MILEPOST | 0 | OMAHA 1ST TAKE-OFF REGULATOR | MYNARD TEST SITE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2021 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE CAUSED BY DEBRIS | CLASS 1 LOCATION | NO |  | 291 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 12622 | 12622 | 300 | 300 | 0 | 0 | 0 | 0 |  | 3.596 | 12922 | 8414.225586622874232890365448504983388704 | 12922 | 0 | 0 | 0 | 0 | NO |  |  |  | 460 | 55000 | 490 | 192.619(A)(2) |  | 2004-08-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS WAS RELEASING AT A PRESSURE BELOW THE ALARMS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | MOISTURE CAUSED THE PILOT IN THE REGULATOR TO STOP ADJUSTING | [161 empty] | DAVID CULLISON |  | david.cullison@nngco.com | 4023987439 |  |  |  |  | TOM CORRELL |  | 4023987715 | thomas.correll@nngco.com | ON JANUARY 2, 2022, AT 1800 HOURS, THE OPERATOR WAS NOTIFIED BY A PASSERBY OF A LOUD NOISE NEAR THE OMAHA 1ST BRANCH LINE REGULATOR. TECHNICIANS ARRIVED ON SITE AND FOUND A RELIEF VALVE VENTING AT APPROXIMATELY 1920 HOURS. PRESSURE WAS VERIFIED TO BE NORMAL (SETPOINT 460 PSIG) DOWNSTREAM OF THE REGULATORS. TECHNICIANS ISOLATED THE RELIEF VALVE AT 1930 HOURS AND RETURNED THE RELIEF VALVE TO SERVICE AT 0030 HOURS JANUARY 3, 2022. INVESTIGATION CONCLUDED THAT MOISTURE BUILDUP IN THE RELIEF VALVE PILOT SENSE LINE STARTED FREEZING DUE TO AMBIENT TEMPERATURES, CAUSING ICE TO FORM IN THE SENSE LINE AND INCREASE PRESSURE TO THE PILOT ASSEMBLY. THIS ICE BUILDUP CAUSED THE RELIEF TO VENT BELOW THE SETPOINT. ADDITIONALLY, A SLIVER OF MATERIAL PREVENTED THE SEAL ON THE RELIEF VALVE TO CLOSE. THE SITE WAS CHECKED REGULARLY FOR REOCCURRENCE WITH NO NEW CONCERNS FOUND. THE INVESTIGATION WAS SHARED WITH OTHER TEAMS TO EVALUATE SIMILAR SCENARIOS.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220002 | 36523 | 2022-01-12 09:17 | SUPPLEMENTAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-12-12 15:12 | 2021 | CENTRAL | NO | 28.2942 | -93.2935 | 1324367 | 2021-12-12 17:50 | 1324511 | NATURAL GAS |  | 119739 | 0 | 4 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-12-12 17:00 | 2022-02-11 15:30 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-12-12 17:00 | VALVE CLOSURE |  | 2021-12-12 17:00 | 0 | 2021-12-13 13:35 | 2021-12-16 19:30 | OFFSHORE | [6 empty] | STINGRAY PIPELINE | STINGRAY 30-INCH LINE 1004C-100 | [20 empty] | 190 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 550 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 0.568 | 60000 | API 5L X-60 | DSAW |  | US STEEL | OTHER | CONCRETE | UNKNOWN | [26 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 484943 | 484943 | 935059 | 953900.694330601358596 | 0 | 0 | 0 | 0 |  | 4.05 | 1420002 | 739017.9492904460424103754152823920265781 | 1438843.694330601358596 | 0 | 0 | 0 | 0 | NO |  |  |  | 930 | 1000 | 1200 | 192.619(A)(1) |  | 1975-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 318991 | YES | [7 empty] | YES |  |  |  |  | YES | LAUNCHER IS SUBSEA | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK AND TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES |  |  |  | YES |  |  |  | YES | DROP OUT. | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PEGGY WEST | SR. REGULATORY ANALYST | peggy.west@energytransfer.com | 409-202-3088 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | AT 4:53 PM ON 12/12/2021, ET OPERATION MANAGER RECEIVED A CALL FROM ARENA OFFSHORE LP PRODUCTION FOREMAN, STATING THAT WHILE THEY WERE FLYING OVER STINGRAY 30-INCH LINE 3394 IN THE WC 550 BLOCK A SHEEN WAS NOTICED. A CALL WAS PLACED TO THE NRC BY THE PRODUCER AT 5:50PM ON 12/12/21 (NRC # 1324367) ET MANAGEMENT NOTIFIED OPERATIONS PERSONAL TO BLOCK IN THE INCOMING 30-INCH VALVE TOPSIDE ON THE WEST CAMERON 509 PLATFORM AND FOR ARENA TO ISOLATE THEIR DEPARTING VALVE TOPSIDE ON THEIR WC 544 PLATFORM AND MONITOR PRESSURE UNTIL AN OBSERVATION FLIGHT CAN BE MADE BY ET OPERATION PERSONAL. ONCE THE AERIAL CONFIRMED THE RELEASE; ENERGY TRANSFER PLACED A CALL TO THE NRC ON 12/13/21 TO TAKE OWNERSHIP OF THE RELEASE AND THE NRC REPORT 1324367. AT 2:11PM ON 12/14/21 A 48HR UPDATE TO THE NRC WAS PLACED (NRC # 1324511). DUE TO SEA CONDITIONS AND MOBILIZING RESOURCES, CREW ARRIVED ONSITE AT 7:30PM ON 12/16/21 TO START DEPRESSURIZING THE LINE. DEPRESSURIZING THE LINE AND REPAIRS ARE CURRENTLY UNDERWAY. THE CLAMP WAS INSTALLED AND LINE WAS RESTARTED ON 2/11/22.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220003 | 37373 | 2022-01-14 13:23 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2021-12-06 16:30 | 2021 | EASTERN | YES | 37.5605 | -81.8847 | 1324944 | 2021-12-20 11:43 | 1325035 | NATURAL GAS |  | 455 | 6857 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2021-12-10 12:00 | 2022-01-07 14:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2021-12-10 11:00 | VALVE CLOSURE |  | 2021-12-10 11:00 | 0 | 2021-12-06 16:30 | 2021-12-06 14:37 | ONSHORE | WV | 25608 | BAISDEN | MINGO | NOT APPLICABLE |  | SM-123 | 11099 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.312 | 65000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | STUPP | EPOXY |  | NO | [26 empty] | 1997 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 629 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 37028 | 37774.124316939901232 | 2457 | 2457 | 122000 | 124458.333333333368 | 500 | 510.075136612022 | 0 | 0 | THERE WAS NO EMERGENCY RESPONSE; THIS WAS A GRADE 2 LEAK. COSTS ARE PRELIMINARY. | 5.4 | 161985 | 73407.9237037743486904186046511627906977 | 165199.532786885291232 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 73000 | 1183 | 192.619(A)(2) |  | 1997-10-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 63712 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS UNRELATED TO CONTROL ROOM ACTIVITY. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | LANDSLIDE |  |  |  |  | NO | [288 empty] | YES | [17 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304.539.9311 |  |  |  |  | PAUL SHAFFER | MANAGER | 304.550.4866 | paul_shaffer@tcenergy.com | ON DECEMBER 06, 2021, A LANDOWNER CONTACTED COLUMBIA GAS (OPID:2616) REGARDING A LEAK ON PIPELINE SM-123 IN MINGO COUNTY, WV NEAR THE TOWN OF BAISDEN, WV. OPERATIONS IMMEDIATELY RESPONDED TO THE LEAK LOCATION AND GRADED THE LEAK AS A GRADE 2, NON-EMERGENCY/SCHEDULE FOR REPAIR. THE PIPELINE PRESSURE WAS LIMITED TO 800 PSIG IMMEDIATELY AFTER THE LEAK WAS DISCOVERED ON DEC 06, 2021 AT APPROX. 4:15 PM EST. THE PIPELINE PRESSURE WAS FURTHER REDUCED TO 695 PSIG (20% REDUCTION OF THE 60 DAY HIGH PRESSURE) ON DECEMBER 08, 2021 AT 2:00 PM EST. ON DECEMBER 10, 2021, THE PIPELINE SEGMENT WAS ISOLATED AT 12:30 PM EST AND PRESSURE REDUCED TO 0 PSIG AND VENTED. OPERATIONS BEGAN EXCAVATION TO DETERMINE THE CAUSE OF THE LEAK AND MAKE THE REPAIRS ON DECEMBER 12, 2021. APPROXIMATELY 20 FEET OF PIPE HAS BEEN EXPOSED REVEALING A BUCKLE IN THE PIPE, WHICH WAS DETERMINED TO NOT BE THE LEAK LOCATION. BASED ON THE MAGNITUDE OF THE PROJECT, OPERATIONS TURNED THE INVESTIGATION AND REPAIR OVER TO THE PROJECTS TEAM ON DECEMBER 15, 2021. A SECOND BUCKLE, WHERE THE LEAK OCCURRED WAS DISCOVERED. THE DAMAGED PIPE WAS REPLACE AND THE PIPELINE WAS PUT BACK INTO SERVICE ON JANUARY 7, 2022 BASED ON THE ESTIMATED COST OF THE REPAIR, THE EVENT EXCEEDED THE PHMSA REPORTABLE VALUE ($122K). AFTER INVESTIGATION IT WAS DETERMINED THAT THE PRIMARY CAUSE OF THE LEAK WAS EARTH MOVEMENT. EARTH MOVEMENT AT THE ACCESS ROAD CROSSING CAUSED SM 123 TO BUCKLE AT TWO LOCATIONS, ONE OF WHICH RESULTED IN A LEAK AT THE PEAK OF THE BUCKLE. SHALLOW, EXTERNAL FATIGUE OR SCC CRACKS AT THE LEAK INITIATION SITE WERE OBSERVED AND DETERMINED TO BE CONTRIBUTING FACTORS TO THE FAILURE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220004 | 36262 | 2022-01-21 09:18 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2021-12-24 14:00 | 2021 | CENTRAL | NO | 34.7094 | -96.2977 | 1325220 | 2021-12-24 14:30 | 1325255 | NATURAL GAS |  | 6500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | BLOWDOWN VALVE WAS CLOSED ELIMINATING RELEASE OF GAS. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2021-12-24 14:00 | 2021-12-24 13:45 | ONSHORE | OK | 74534 | CENTRAHOMA | COAL | NOT APPLICABLE |  | CHILES DOME STORAGE FACILITY | CHILES DOME | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | VALVE DID NOT FULLY CLOSE. | [5 empty] | CLASS 1 LOCATION | NO |  | 285 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 24440 | 24440 | 0 | 0 | 500 | 510.075136612022 | 0 | 0 |  | 3.76 | 24940 | 16261.2382393388161079734219269102990033 | 24950.075136612022 | 0 | 0 | 0 | 0 | NO |  |  |  | 164 | 1 | 1700 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT PROGRAMMING | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PROGRAMMING ISSUE | [147 empty] | YES | [13 empty] | CASEY ROBERTS | LEAD SPECIALIST | casey.roberts@energytransfer.com | 4056263981 |  | SUSIE SJULIN | susie.sjulin@energytransfer.com | 4055575271 | CASEY ROBERTS | LEAD SPECIALIST | 4056263981 | casey.roberts@energytransfer.com | ON 12/24/2021 A UNIT 1 VENT VALVE WAS DISCOVERED OPEN BY AN OPERATIONS EMPLOYEE AT THE CHILES DOME STORAGE FACILITY. THE VALVE WAS IMMEDIATELY CLOSED AND UPON INVESTIGATION IT WAS DETERMINED THAT A REPORTABLE RELEASE OF NATURAL GAS HAD OCCURRED. THE NRC WAS NOTIFIED (NRC# 1325220, 1325255) AND AN INVESTIGATION WAS INITIATED TO DETERMINE CAUSE. THE RELEASE OCCURRED WHILE THE STATION WAS INJECTING INTO THE STORAGE FIELD. AFTER FURTHER INVESTIGATION, THE VENT VALVE DID NOT CLOSE WHEN THE UNIT RESET, DUE TO THE CLOSE COMMAND BEING TURNED OFF IN THE PROGRAMMING. THE LIMIT SWITCH DID NOT CATCH THIS BECAUSE IT WAS OFF SEATED ON THE SUCTION VALVE SHOWING THE VALVE TO BE CLOSED WHEN IT WAS CRACKED OPEN. BOTH ISSUES WERE IMMEDIATELY CORRECTED AND WE HAVE PERFORMED SEVERAL STARTS ON THE UNIT AND EVERYTHING IS WORKING CORRECTLY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220005 | 36273 | 2022-01-25 17:41 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2021-12-28 10:25 | 2021 | EASTERN | NO | 37.4159 | -85.3952 | 1325398 | 2021-12-28 11:15 | 1325538 | NATURAL GAS |  | 10410 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVES WERE CLOSED AND ISOLATED FROM THE SYSTEM |  |  |  | YES | OPERATOR | 2021-12-28 10:31 | NO | [11 empty] | 0 | 2021-12-28 10:23 | 2021-12-28 10:23 | ONSHORE | KY | 42718 | CAMPBELLSVILLE | TAYLOR | NOT APPLICABLE |  | STATION 96 | RELIEF VALVES 96-1A AND 96-2A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 2015 | 2015 | CARBON STEEL |  | LEAK |  |  | OTHER | RELIEF VALVE ACTIVATION | [5 empty] | CLASS 2 LOCATION | NO |  | 567 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 35810 | 35810 | 5500 | 5610.826502732242 | 250 | 255.037568306011 | 150 | 153.0225409836066 | NITROGEN FOR TESTING RELIEF VALVES PRIOR TO RETURNING TO SERVICE | 3.44 | 41710 | 26151.8969384837443598006644518272425249 | 41828.8866120218596 | 0 | 0 | 0 | 0 | NO |  |  |  | 732.9 | 1375 | 750 | 192.619(C) |  | 1957-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY LOCAL OPERATING CONDITIONS AND NOT RELATED TO THE ACTIONS OF THE CONTROLLERS OR CONTROL ROOM ISSUES | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [177 empty] | KRISTIN VAN DER LAAN | MANAGER ENGINEERING - CODES AND STANDARDS | kristin_vanderlaan@kindermorgan.com | 3039147753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING - CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 10:23 AM CST ON 12/28/2021 RELIEF VALVES 96-1A AND 96-2A ACTIVATED IN THE STATION YARD OF STATION 96 IN CAMPBELLSVILLE, KENTUCKY VENTING NATURAL GAS TO THE ATMOSPHERE. THESE VALVES ARE LOCATED 34-FEET APART ON COMMON DISCHARGE PIPING AND ARE 8-INCH MERCER BRAND VALVES. COMPANY PERSONNEL ON SITE VERIFIED THAT STATION DISCHARGE PRESSURE DID NOT EXCEED MAOP AND REDUCED HORSEPOWER IN AN EFFORT TO REDUCE PRESSURE AND ALLOW THE VALVES TO RESET. WHEN THE RELIEF VALVES DID NOT RESET THE MANUAL VALVES, LOCATED BELOW THE RELIEF VALVES, WERE CLOSED AT 10:29 AM CST. THE INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATION WAS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. IT WAS DETERMINED ON THE CALL THAT THE QUANTITY OF GAS RELEASED WOULD MEET THE PHMSA-REPORTABLE THRESHOLD AND THE NRC AND PHMSA ACCIDENT INVESTIGATION DIVISION WERE BOTH NOTIFIED. THE INVESTIGATION INTO THE INCIDENT BEGAN THE SAME DAY AS THE EVENT. STATION PERSONNEL ALONG WITH THE RELIEF VALVE VENDOR, TESTED THE VALVE SETPOINTS. THE NORMAL SET-POINT FOR THESE VALVES IS 772 PSIG AND BOTH VALVES WERE SERVICED ON 9/21/2021 BY OPERATOR QUALIFIED PERSONNEL, WHO LEFT THE VALVES AT 772 PSIG. BENCH TESTING THE VALVES SHOWED THAT VALVE 96-1A RELIEVED AT 743 PSIG AND VALVE 96-2A RELIEVED AT 738 PSIG. THE RELIEF VALVES WERE CALIBRATED TO 772PSIG, PLACED BACK INTO SERVICE, AND THE HORSEPOWER RETURNED TO NORMAL OPERATIONS. THE MERCER VALVE REPRESENTATIVES PROVIDED MERCER VALVE CO., INC. TECHNICAL BULLETIN ETB00013, PUBLISHED ON JULY 31, 2015 AFTER THE INSTALLATION DATE OF VALVES 96-1A AND 96-2A, INDICATING THAT EXCESSIVE VIBRATION ON THE RELIEF VALVES PILOTS CAN LEAD TO A REDUCTION DRIFT OF THE SET-POINT PRESSURE REQUIRED TO ACTIVATE THE RELIEF VALVE. THEY INDICATED THAT THE VALVES ARE ALSO SUSCEPTIBLE TO PULSATION IN THE PILOT SENSING LINES WHEN LOCATED CLOSE TO COMPRESSION. IT IS BELIEVED THAT THE DRIFTING SET POINT AND PILOT SENSING LINE PULSATION LED TO THE ACTIVATION OF THESE VALVES AT A LOWER PRESSURE THAN THE NORMAL SETPOINT. ON JANUARY 12, 2022, BASED ON THE INPUT FROM THE VALVE REPRESENTATIVES, THE PILOTS ON THE RELIEF VALVES WERE REPLACED AND DAMPENERS WERE INSTALLED TO ENSURE PULSATION DOES NOT PLAY A FACTOR IN THE FUTURE. ADDITIONAL REMEDIAL ACTIONS WILL BE EVALUATED TO ADDRESS THE SET-POINT DRIFT. UNTIL ADDITIONAL REMEDIAL ACTIONS ARE ASSESSED, THE TESTING FREQUENCY FOR THESE VALVES WILL BE INCREASED FROM ANNUALLY TO MONTHLY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220006 | 36275 | 2022-01-26 12:27 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-01-01 11:16 | 2022 | EASTERN | NO | 41.244 | -74.6461 | 1325677 | 2022-01-01 12:07 | 1325681, 1325725 | NATURAL GAS |  | 11116 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | JUST THE UNIT SHUTDOWN, THE REST OF THE FACILITY CONTINUED TO RUN |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-01 12:00 | NO | [11 empty] | 0 | 2022-01-01 10:56 | 2022-01-01 12:00 | ONSHORE | NJ | 07461 | LIBERTYVILLE | SUSSEX | MILEPOST | 325-1+0.00 | 300-1 LINE | STATION 325 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2011 | 2011 | CARBON STEEL |  | LEAK |  |  | OTHER | COMPRESSOR UNIT VENTING | [5 empty] | CLASS 3 LOCATION | NO |  | 708 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 43352 | 43352 | 39213 | 39213 | 788 | 788 | 0 | 0 |  | 3.9 | 83353 | 46092.1583592577989938438538205980066445 | 83353 | 0 | 0 | 0 | 0 | NO |  |  |  | 1056 | 1600 | 1170 | 192.619(A)(1) |  | 1986-03-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY LOCAL OPERATING CONDITIONS AND NOT RELATED TO THE ACTIONS OF THE CONTROLLERS OR CONTROL ROOM ISSUES | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [31 empty] | YES | CPU FAILURE | [161 empty] | KRISTIN VAN DER LAAN | MANAGER IC - CODES AND STANDARDS | kristin_vanderlaan@kindermorgan.com | 303-914-7753 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING - CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | AT 10:56 AM ON JANUARY 1, 2022, KM GAS CONTROL RECEIVED A STATION ALARM FROM STATION 325. TGP GAS CONTROL NOTIFIED DISTRICT PERSONNEL IMMEDIATELY AND THEY WERE DISPATCHED TO STATION 325. IMMEDIATELY AFTER RECEIVING THE ALARM, TGP GAS CONTROL RECEIVED CALLS FROM THREE NEIGHBORS LOCATED NEAR STATION 325 REPORTING LOUD SOUNDS COMING FROM THE STATION. UPON ARRIVAL AT STATION 325, DISTRICT PERSONNEL ENCOUNTERED THE LOCAL FIRE COMPANY AT THE MAIN GATE AND THE NJ STATE POLICE AT THE STATION YARD GATE. COMPANY PERSONNEL REQUESTED THAT THE FIRE COMPANY STAND-BY UNTIL GAS VENTING SUBSIDED AT WHICH POINT THE AREA WOULD BE SECURED. PERSONNEL COMPLETED A SITE EVALUATION AND DETERMINED UNIT 4A HAD GONE OFFLINE. WHEN UNIT 4A WENT OFFLINE THE COMPRESSOR CASE VENT OPENED AS DESIGNED BUT THE UNIT SUCTION AND DISCHARGE VALVES WERE UNABLE TO CLOSE DUE TO THE CPU FAILURE WHICH ALLOWED FOR THE UNINTENTIONAL RELEASE OF NATURAL GAS. THE INTERNAL EMERGENCY RESPONSE LINE (ERL) CALL NOTIFICATION WAS INITIATED PER COMPANY PROCEDURES TO DISCUSS THE INCIDENT. IT WAS DETERMINED ON THE CALL THAT THE QUANTITY OF GAS RELEASED WOULD MEET THE PHMSA-REPORTABLE THRESHOLD AND THE NRC WAS NOTIFIED. PERSONNEL MANUALLY CLOSED BOTH SUCTION AND DISCHARGE VALVES AT 12:10 PM AND VENTING CEASED. SOLAR WAS CONTACTED AND A SOLAR FIELD SERVICE REPRESENTATIVE (FSR) ARRIVED ON SITE AT APPROXIMATELY 5 PM TO BEGIN TROUBLESHOOTING UNIT 4A. THE SOLAR FSR WAS ABLE TO DETERMINE UNIT 4A SHUTDOWN WAS A RESULT OF A MAJOR PROCESSOR (CPU) FAILURE CAUSING A UNIT 'FAST STOP'. A NEW PROCESSOR WAS INSTALLED AND UNIT 4A STARTED NORMALLY AFTER GOING THROUGH ITS AUTOMATIC PRESTART CHECKS. UNIT 4A WAS RETURNED TO SERVICE ON SUNDAY EVENING, JANUARY 2, 2022, AFTER ADDITIONAL TESTING ENSURED NO OTHER ABNORMAL ISSUES WERE PRESENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220007 | 36527 | 2022-01-31 16:52 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-01-03 17:30 | 2022 | CENTRAL | NO | 37.7051 | -101.2034 | 1325831 | 2022-01-03 19:49 | 1325936 | NATURAL GAS |  | 22878 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | STATION WAS DOWN AT TIME OF RELEASE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-02 09:13 | 2022-01-02 10:00 | ONSHORE | KS | 67880 | ULYSSES | GRANT | NOT APPLICABLE |  | COLUMBIAN STATION | COLUMBIAN DISCHARGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1974 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE FAILED OPEN DUE TO LIQUIDS IN THE PILOT. | CLASS 1 LOCATION | NO |  | 111 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 52162 | 52162 | 400 | 400 | 235 | 235 | 0 | 0 |  | 2.28 | 52797 | 34506.0346899132122536378737541528239203 | 52797 | 0 | 0 | 0 | 0 | NO |  |  |  | 467 | 0 | 960 | 192.619(A)(1) |  | 1974-12-18 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. THIS COMPRESSOR STATION WAS DOWN AT THE TIME OF THE INCIDENT AND THE LINE WAS OPERATING BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | LIQUIDS IN THE PILOT | [161 empty] | KATHIE HARRYMAN | SR. SPECIALIST REGULATORY COMPLIANCE | kathryn.harryman@energytransfer.com | 713-989-7085 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON 01/02/22 AT 09:13 GAS CONTROL RECEIVED A CALL FROM A LANDOWNER ABOUT A NOISE AT THE COLUMBIAN BOOSTER STATION. THE OPERATOR WAS CALLED OUT AND SHUT THE VALVE UNDER THE RELIEF VALVE. THE STATION WAS DOWN AT THE TIME SO TAKING THIS VALVE OUT OF SERVICE HAD NO NEGATIVE IMPACT ON PRESSURE PROTECTION. THE TEMPERATURES THE MORNING OF 1/2/2022 WERE IN THE SINGLE DIGITS. ON 1/03/22 IT WAS DETERMINED THAT THE THRESHOLD FOR IMMEDIATE NOTIFICATION WAS MET AND A CALL WAS PLACED TO THE NRC AT 7:49PM (NRC # 1325831). A 48HR UPDATE WAS PLACED ON 1/05/22 AT 12:14PM (NRC # 1325936). WHEN THE RELIEF VALVE WAS DISASSEMBLED AND REBUILT, LIQUIDS WERE FOUND IN THE PILOT AND ON TOP OF THE DOME. THIS LED TO THE CONCLUSION THAT WHEN THE LIQUIDS IN THE PILOT FROZE, THE PILOT MALFUNCTIONED CAUSING THE RELIEF VALVE TO FAIL OPEN. SUPPLEMENTAL - A4 DATE CHANGE AS PER PHMSA SW REGION DUE TO 01/03/22 BEING THE EARLIEST DATE AN INCIDENT REPORTING CRITERIA WAS MET.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220008 | 36348 | 2022-02-01 18:14 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2022-01-02 06:10 | 2022 | EASTERN | NO | 43.4441 | -85.1433 | 1325714 | 2022-01-02 06:10 | 1325804 | NATURAL GAS |  | 35011 | 489 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-02 02:45 | 2022-01-02 16:00 |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-02 02:45 | 2022-01-02 02:45 | ONSHORE | MI | 48886 | SIX LAKES | MONTCALM | SURVEY STATION NO. | W.C. TAGGART | W.C. TAGGART COMPRESSOR STATION | W.C. TAGGART COMPRESSOR STATION PLANT 2 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1996 | 1996 | CARBON STEEL |  | OTHER | [8 empty] | THE TYPE OF RELEASED INVOLVED WAS FROM TWO 20" ESD ISOLATION VALVES (P2S1, AND P2D2) NOT FULLY CLOSING DURING THE ESD EVENT. GAS WAS RELEASED DUE TO VALVES NOT FULLY CLOSED THEREFORE ESD CONTINUED TO VENT UNTIL FULLY ISOLATED. | CLASS 2 LOCATION | NO |  | 436 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 1467 | 1467 | 105033 | 105033 | 6000 | 6000 | 3000 | 3000 | 0 | 0 |  | 3 | 115500 | 73534.641182388361055312292358803986711 | 115500 | 0 | 0 | 0 | 0 | NO |  |  |  | 511 | 96000 | 1020 | 192.619(A)(2) |  | 1996-05-26 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR ON-SITE MADE A CONSERVATIVE CALL TO ESD THE PLANT WHEN AN ISSUE WAS FOUND INSIDE PLANT 2. ESD SYSTEM DID NOT OPERATE AS INTENDED, LEADING TO THE GAS VENTED. THE OPERATOR SHOULD BE ABLE TO EXPECT THE SYSTEM TO FUNCTION AS DESIGNED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | HYDRAULIC SYSTEM ON THE ESD ISOLATION VALVES NOT PERFORMING DUE TO COLD | [161 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  | FRENAE F SMITH | frenae.smith@dteenergy.com | 13134601681 | FRENAE F SMITH | MANAGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | AT 2:41 AM 1/02/2022 THE STATION SUPERVISOR RECEIVED A CALL FROM THE OPERATOR ON SHIFT LETTING ME KNOW WHAT HE WAS SMELLING AND IDENTIFIED A GAS LEAK IN THE BUILDING AND WAS GOING TO INITIATE AN ESD. GAS CONTROL WAS CALLED BY THE OPERATOR AND NOTIFIED THE CONTROLLER ON SHIFT OF THE CURRENT STATE OF THE PLANT. AT 2:45 AM THE ESD WAS INITIATED. THEN, AT 2:49 AM THE SUPERVISOR CALLED THE STATION MANAGER TO LET HIM KNOW THE SITUATION OF THE PLANT. AT 3:21 AM THE SUPERVISOR CALLED THE MANAGER OF CODES ABOUT THE UNPLANNED ESD EVENT. CODES & STANDARD MANAGER CONTACTED THE MPSC AT 3:25 AM. AT 4:27 AM THE SUPERVISOR CALLED GAS CONTROL AGAIN TO MAKE SURE THEY ARE AWARE OF THE STATE OF THE PLANT. THE OPERATOR ON SHIFT CALLED THE SUPERVISOR AT 4:30 AM AND NOTIFIED ME THAT GAS WAS STILL VENTING AT PLANT 2 AND HE CALLED IN TECHNICIANS IN TO HELP. AT 5:05 AM THE FIRST TECHNICIAN ARRIVED ONSITE TO HELP WITH THE SITUATION. THE STATION MANAGER AND SUPERVISOR ARRIVED ONSITE AT 5:20 AM. WHILE ONSITE IT WAS IDENTIFIED THAT SUCTION 1 PLANT 2 ESD VALVE AND DISCHARGE 2 PLANT 2 ESD VALVE FAILED TO CLOSE, WHICH RESULTED IN OPERATIONS RECONFIGURING THE PLANT TO ISOLATE THE CONTINUED VENTING ASSOCIATED WITH THE SUCTION 1 ESD ISOLATION VALVE NOT CLOSING. AFTER THE PLANT WAS RECONFIGURED, GAS STOPPED VENTING AT 5:35 AM. THE STATION MANAGEMENT CONTACTED CODES TO LET THEM KNOW THAT WE VENTED APPROXIMATELY 35.5 MMCF OF GAS DUE TO THE UNANTICIPATED VALVE OPERATION. THE CODES & STANDARDS SUPERVISOR CONTACTED THE NRC AT 6:10 AM. AT 7:19 AM A DTE CODES REPRESENTATIVE AND GAS SAFETY ENGINEER FROM THE MPSC ARE EN ROUTE TO THE STATION. THE MPSC REPRESENTATIVE AND CODES REPRESENTATIVE ARRIVED AT 9:06 AM AND COMPLETED A PLANT WALK DOWN OF THE STATION. DURING THE REST OF THE TIME TECHNICIANS AND OPERATIONS STARTED TO TROUBLESHOOT EACH VALVE. AT 4:00 PM, PLANT 2 WAS RETURNED BACK TO NORMAL OPERATIONS. THERE WAS NO IMPACT TO NOMINATIONS TO GAS CONTROL THROUGHOUT THE ENTIRE EVENT AS PLANT 1 WAS ABLE TO MEET THE ORDER FOR THE DAY. DTE GAS WILL INSTITUTE THE FOLLOWING CHANGES TO PREVENT REOCCURRENCE: 1. REPLACE HAND PUMPS AND CHANGE ALL HYDRAULIC FLUID ON 17 ESD VALVES AT TAGGART 2. ADD PREVENTIVE MAINTENANCE WORK ORDERS IN MAXIMO TO TEST FOR MOISTURE, CHECK O-RINGS, CHECK FOR CORROSION, AND CHANGE THE HYDRAULIC FLUID. 3. EXPAND ACROSS FLEET; HYDRAULIC OVER-RIDE SIDE SHOULD HAVE HIGHER RIGOR OF MAINTENANCE. VALVES WITH BOTH HYDRAULIC AND POWER GAS COMPONENTS, NOT ELECTRIC. 4. ADD UPSTREAM FILTRATION ON THE POWER GAS SIDE OF ACTUATORS AND/OR INSTALL/REPLACE CONTROL BLOCKS. 5. STRENGTHEN THE ONBOARDING PROCESS. CONSIDER PFMEA ON THE ESD PROCESS. 6. USE AN ACTUAL CHECKLIST FOR ESD EVENTS; MAKE SURE EXPECTATIONS ARE CLEAR AS TO WHAT CONSTITUTES NORMAL VS. ABNORMAL. 7. MAKE MIMIC BOARD ADJUSTMENTS TO SHOW IF VALVES DID NOT CLOSE, PER THE ESD PROTOCOL.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220009 | 36562 | 2022-02-09 09:21 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-01-11 18:20 | 2022 | CENTRAL | NO | 29.2353 | -90.6694 | 1326361 | 2022-01-11 19:17 | 1326470 | NATURAL GAS |  | 1.37 | 84.8 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-11 22:36 | 2022-01-20 09:45 |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-11 18:20 | 2022-01-11 22:10 | ONSHORE | LA | 70344 | COCODRIE | TERREBONE | NOT APPLICABLE |  | COCODRIE CS | COCODRIE CS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2013 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 518 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 385 | 385 | 6 | 6 | 361800 | 361800 | 900 | 900 | 5000 | 5000 | METALLURGICAL REPORT | 4.54 | 368091 | 162388.9414803574669551328903654485049834 | 368091 | 0 | 0 | 0 | 0 | NO |  |  |  | 864 | 45 | 980 | 192.619(C) |  | 1956-07-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | 3RD PARTY FACILITY OWNER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT OF CONTROLLE(S) ACTIONS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [6 empty] | YES |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [313 empty] | JORGE LOPEZ | MANAGER ENGINEERING CODES AND STANDARDS | jorge_lopez@kindermorgan.com | 7134204675 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | AT 6:20 PM, ON 1/11/2022, TENNESSEE GAS PIPELINE COMPANY (TGP) WAS NOTIFIED BY THE 3RD PARTY FACILITY OWNER OF A POTENTIAL LEAK ON A 24 INCH U BOLT PIPE SUPPORT INSIDE THE COCODRIE COMPRESSOR STATION. TGP FIELD OPERATOR ARRIVED ON SITE AT 10:36 PM AND UPON ARRIVAL, A LEAK WAS CONFIRMED AND ISOLATED. AT 11:13 PM, THE SEGMENT OF PIPE CONTAINING THE LEAK WAS BLOWN DOWN. TGP DEEMED THE INCIDENT REPORTABLE FROM A COST OF REPAIRS STANDPOINT. A NATIONAL RESPONSE CENTER (NRC) CALL WAS COMPETED AND TGP STARTED THE INTERNAL INCIDENT INVESTIGATION. THE PINHOLE LEAK WAS LOCATED AT THE 6 O CLOCK POSITION. THE PIPE IN THE AREA OF THE PINHOLE LEAK WAS ULTRASONICALLY SCANNED IN THE FIELD TO DETERMINE IF THERE WAS INTERNAL PIPE WALL LOSS. THE FIELD RESULTS CONCLUDED INTERNAL WALL LOSS IN THE PIPE CLAMP AREA RANGING FROM 30 - 50%. THE PIPE WAS REPLACED AND THE SPECIMEN CONTAINING THE LEAK WAS SHIPPED TO A METALLURGICAL LABORATORY FOR FURTHER ASSESSMENTS. THE LINE WAS PUT BACK IN SERVICE ON 1/20/2022. ON 3/10/2022, THE METALLURGICAL REPORT WAS COMPLETED CONCLUDING INTERNAL CORROSION WAS THE APPARENT CAUSE FOR THE LEAK EVENT. IN ORDER TO PREVENT REOCCURRENCE, TGP WILL BE REVIEWING THE ENGINEERING DESIGN TO MINIMIZE THE INTERNAL CORROSION IN THE STATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220010 | 36983 | 2022-02-10 08:55 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 220 W MAIN ST, PO BOX 32010 | LOUISVILLE | KY | 40202 | 2022-01-13 03:25 | 2022 | CENTRAL | NO | 37.1677 | -85.7077 | 1326455 | 2022-01-13 06:52 | 1326603 | NATURAL GAS |  | 134.1 | 17.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-13 05:21 | 2022-01-25 09:41 |  | YES | OPERATOR | 2022-01-13 05:15 | YES | 2022-01-13 03:25 | OTHER | OPERATOR CLOSED VALVE AND LOCAL FIRE DEPT APPLIED WATER TO BUILDING WHILE FIRE BURNED OUT. | 18.6 | NO | [6 empty] | 0 | 2022-01-13 04:54 | 2022-01-13 05:19 | ONSHORE | KY | 42746 | Not Within a Municipality | METCALFE | NOT APPLICABLE |  | CENTER COMPRESSOR STATION | CENTER COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL TUBING | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 6 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 76 | 76 | 585 | 585 | 17000000 | 17000000 | 0 | 0 | 78000 | 78000 | OUTSIDE ENGINEERING SUPPORT. | 4.36 | 17078661 | 7534576.89841084026368495681063122923588 | 17078661 | 0 | 0 | 0 | 0 | NO |  |  |  | 166 | 231 | 500 | 192.619(A)(1) |  | 2014-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | NO | OTHER | SENIOR OPERATOR AT MAGNOLIA COMPRESSOR STATION |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [5 empty] | YES | INCORRECT PLC CONFIGURATION. | YES | 2 | 0 | NO |  |  | EQUIPMENT FAILURE | DEFECTIVE OR LOOSE TUBING OR FITTING | MATERIAL/WELD/EQUIP FAILURE | DEFECTIVE OR LOOSE TUBING/FITTING | [166 empty] | DEFECTIVE OR LOOSE TUBING OR FITTING | [22 empty] | YES |  |  | YES | [172 empty] | PETER J. CLYDE | MANAGER GAS T AND D INTEGRITY AND COMPLIANCE | peter.clyde@lge-ku.com | (502) 364-8715 |  |  |  |  | KELSEY COLVIN | SENIOR COUNSEL | (502) 888-4127 | kacolvin@pplweb.com | ON JANUARY 13, 2022 AT 04:54 A.M. CST, A SENIOR OPERATOR AT MAGNOLIA COMPRESSOR STATION (UNMANNED FROM 05:00 P.M. TO 05:00 A.M.) REPORTED FOR THE START OF HIS SHIFT AND NOTICED THE SECURITY VIDEO FEED OF THE UNMANNED CENTER COMPRESSOR STATION FAILED. HE ALSO OBSERVED THERE WAS NO FLOW OF GAS ON THE SCADA SYSTEM. THE OPERATOR WAS ABLE TO REWIND THE VIDEO FEED AND REALIZED A FIRE HAD STARTED AT 03:25 A.M. HE CALLED HIS SUPERVISOR AND AN EMPLOYEE THAT LIVED NEAR THE CENTER COMPRESSOR STATION. THAT EMPLOYEE CALLED 911 AT 05:15 A.M., ARRIVED AT THE STATION AT 05:19 A.M., AND WAS ABLE TO SHUT OFF THE GAS BY 05:21 A.M. THE INCIDENT DID NOT CAUSE ANY INJURIES, THIRD-PARTY PROPERTY DAMAGE, OR LOSS OF GAS SUPPLY. THE CAUSE OF THE FIRE HAS BEEN INVESTIGATED. A RIGID, STAINLESS STEEL TUBING COMPRESSION FITTING USED FOR THE GAS PRESSURE MEASUREMENT HAS BEEN IDENTIFIED AS THE CAUSE OF THE INCIDENT. AS NOTED IN PART A 16(B), THE CENTER STORAGE FIELD AND THE FLOW OF GAS WERE RETURNED TO NORMAL OPERATIONS ON 01/25/2022. THE COMPRESSOR STATION HAS BEEN PHYSICALLY DISCONNECTED FROM THE CENTER STORAGE FIELD. THE COMPANY HAS NOT MADE A DECISION ON WHETHER THE DAMAGED BUILDING AND EQUIPMENT WILL BE REPLACED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220011 | 36780 | 2022-02-10 12:51 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-01-12 08:53 | 2022 | EASTERN | NO | 41.4276 | -77.8533 | 1326392 | 2022-01-12 11:26 | 1326550 | NATURAL GAS |  | 4600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE RESET ITSELF |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-01-12 09:12 | VALVE CLOSURE |  | 2022-01-12 09:12 | 0 | 2022-01-12 08:53 | 2022-01-12 11:45 | ONSHORE | PA | 17764 | Not Within a Municipality | CLINTON | MILEPOST | 80 | TEXAS EASTERN LINE 24 | PERU-LEID | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REGULATOR/CONTROL VALVE | [38 empty] | 1960 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE | CLASS 1 LOCATION | NO |  | 566 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 22356 | 22356 | 0 | 0 | 500 | 500 | 0 | 0 | LABOR FOR INTERNAL RESPONDERS | 4.86 | 22856 | 14889.3848370624869551495016611295681063 | 22856 | 0 | 0 | 0 | 0 | NO |  |  |  | 1147 | 3500 | 1170 | 192.619(A)(2) |  | 1960-12-31 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 59136 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | BHE - LEIDY STORAGE FIELD |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INDICATION OR EVIDENCE OF CONTROL ROOM OR CONTROLLER CONTRIBUTION TO THE INCIDENT; OPERATIONS (I.E., PRESSURES AND FLOWS) IN THE AREA WERE NORMAL AND WITHIN DESIGNED RANGES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | WEAR ON SOFT GOODS AND DEBRIS IN VALVE. | [161 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 16128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 17136275008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 7:53 A.M. CT A 4-INCH RELIEF VALVE ON LINE 24 BEGAN RELIEVING GAS AND AUTOMATICALLY RESET ITSELF AT APPROXIMATELY 8:12 A.M. CT. THE 4-INCH RELIEF VALVE IS ON TEXAS EASTERN LINE 24 WHICH IS A 24-INCH BIDIRECTIONAL LINE THAT HAS A 1170 PSI MAOP. THE LINE IS BIDIRECTIONAL ASSOCIATED WITH THE LEIDY STORAGE FIELD NOT OWNED OR OPERATED BY ENBRIDGE. THE LINE PRESSURE AT THE TIME OF THE RELEASE WAS APPROXIMATELY 1147 PSI SO THE 1170 PSI MAOP WAS NOT EXCEEDED. AT THIS TIME THE EQUIPMENT FAILURE IS STILL UNDER INVESTIGATION. 6/21/2022 THE INVESTIGATION DETERMINED THAT THERE WAS WEAR ON SOFT GOOD AND DEBRIS IN VALVE. THE SOFT GOODS WERE REPLACED, DEBRIS REMOVED, SET PRESSURE ADJUSTED AND VALVE WAS PLACE BACK INTO SERVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220012 | 36873 | 2022-02-14 10:50 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-01-21 08:30 | 2022 | CENTRAL | NO | 36.4293 | -95.7011 | 1327011 | 2022-01-21 09:46 | 1327084 | NATURAL GAS |  | 4172 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | VALVE WAS CLOSED TO RE-SEAT RELIEF VALVE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-21 08:30 | 2022-01-21 08:30 | ONSHORE | OK | 74053 | OOLOGAH | ROGERS | NOT APPLICABLE |  | NORTHEAST POWER STATION | NORTHEAST POWER STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | REGULATOR FAILURE DUE TO ICING | [5 empty] | CLASS 3 LOCATION | YES | METHOD2 | 407 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 16313 | 16313 | 9500 | 9500 | 500 | 500 | 0 | 0 |  | 3.91 | 26313 | 15115.3296316151876079734219269102990033 | 26313 | 0 | 0 | 0 | 0 | NO |  |  |  | 390 | 2.68 | 605 | 192.619(A)(2) |  | 2019-05-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EQUIPMENT FAILURE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | ICING | [123 empty] | YES | [23 empty] | YES | [13 empty] | JIMMY CROSS | SR. MANAGER REGULATORY COMPLIANCE | jimmy.cross@energytransfer | 4055768230 |  | JIMMY CROSS | jimmy.cross@energytransfer.com | 4055768230 | JIMMY CROSS | LEAD SPECIALIST | 4055768230 | jimmy.cross@energytransfer.com | ON 01/21/2022 A RELIEF VALVE WAS DISCOVERED VENTING WHEN A ENERGY TRANSFER EMPLOYEE ARRIVED AT THE NORTHEAST POWER STATION IN OOLOGAH, OKLAHOMA. GAUGES WERE INSTALLED TO VERIFY PRESSURES. THE RELIEF VALVE WAS IMMEDIATELY CLOSED AND UPON INVESTIGATION IT WAS DETERMINED THAT A REPORTABLE RELEASE OF NATURAL GAS HAD OCCURRED. THE NRC WAS NOTIFIED (NRC# 1327084, 1327011) AND AN INVESTIGATION WAS INITIATED TO DETERMINE CAUSE. IT WAS DETERMINED THAT REGULATOR MALFUNCTION HAD OCCURRED DUE TO ICE BUILDUP ON THE REGULATOR. THE REGULATOR WAS DE-ICED AND THE RELIEF VALVE WAS REBUILT BEFORE BEING PLACED BACK INTO SERVICE. EXTREME TEMPERATURES OF 16 DEGREES OCCURED ON THS DAY AND CONTRIBUTED TO ICING OF THE REGULATOR, AND ULTIMATELY CAUSED THE RELEASE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220013 | 36507 | 2022-02-15 08:21 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-01-26 17:30 | 2022 | EASTERN | NO | 35.0988 | -78.9633 | 1327398 | 2022-01-27 06:43 | 1327498 | NATURAL GAS |  | 264 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A BYPASS WAS MADE ON THE PIPE. | [6 empty] | NO | [5 empty] | OPERATIONAL CONTROL | A BYPASS WAS MADE ON THE PIPE. |  | OPERATIONAL CONTROL | A BYPASS WAS MADE ON THE PIPE. |  | 0 | 2022-01-26 18:15 | 2022-01-26 18:15 | ONSHORE | NC | 28303 | FAYETTEVILLE | CUMBERLAND | NOT APPLICABLE |  | LINE 5 | LINE 5 ORIGINAL INSTALL/0 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.219 | UNKNOWN | UNKNOWN | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | NO |  | 200 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 1056 | 1056 | 50000 | 50000 | 253125 | 253125 | 0 | 0 |  | 4 | 304181 | 134420.0308910596268583887043189368770764 | 304181 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 600 | 718 | 192.619(A)(2) |  | 1959-06-22 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 33845 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A 3RD PARTY DAMAGE DUE TO THE CONTRACTOR DRILLING INTO THE TRANSMISSION LINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | A220111538 | N/A | CONTRACT LOCATOR | NO | UNKNOWN/OTHER | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR BORED INTO A 12" TRANSMISSION LINE WHILE INSTALLING TELECOMMUNICATION LINES. THE CONTRACTOR HAD NOTIFIED THE ONE CALL CENTER BUT DID NOT WAIT FOR THE LINE TO BE MARKED. (FROM PART G: EXCAVATION PRACTICE NOT SUFFICIENT-OTHER). THE SMYS (SPECIFIED MINIMUM YIELD STRENGTH) OF PIPE IN PSI FROM PART C 3C IS 42,000. ALSO AFTER SPEAKING WITH ONE OF THE ACCIDENT INVESTIGATORS FROM PHMSA AND RE-ENTERING THE SMYS INFORMATION, I WAS STILL NOT ABLE TO UNSELECT UNKNOWN AND ENTER 42,000 IN THE SMYS OF PIPE SECTION.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220014 | 36702 | 2022-02-16 07:58 | SUPPLEMENTAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2022-01-23 20:04 | 2022 | EASTERN | NO | 40.82 | -82.4218 | 1327142 | 2022-01-23 21:16 | 1327254 | NATURAL GAS |  | 14118.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | IT WAS ON ESD SYSTEM AND VALVE WAS REPAIRED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-23 19:51 | 2022-01-23 20:04 | ONSHORE | OH | 44903 | MANSFIELD | RICHLAND |  |  | PAVONIA COMPRESSOR STATION | C 109-229 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1991 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BLOW OFF VALVE ON ESD SYSTEM OPENED UNINTENTIONALLY. | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 46592 | 46592 | 280 | 280 | 1200 | 1200 | 0 | 0 |  | 3.3 | 48072 | 31224.0821077381839786046511627906976744 | 48072 | 0 | 0 | 0 | 0 | NO |  |  |  | 430 | 338852 | 495 | 192.619(A)(1) |  | 1990-10-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MALFUNCTION OF BLOW OFF VALVE WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [15 empty] | YES | [171 empty] | KAMRAN ROSTAMI ASRABADI | US REGULATORY COMPLIANCE SPECIALIST | kamran_rostami@tcenergy.com | (304)357-2351 |  |  |  |  | CHRISTOPHER LEGG | US REGULATORY COMPLIANCE MANAGER EAST | (304)545-4350 | chris_legg@tcenergy.com | ON JANUARY 23RD, 2022, PAVONIA COMPRESSOR STATION (CS) WAS SUBJECT TO AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) RESULTING IN MATERIAL LOSS EXCEEDING 3,000 MCF. PAVONIA IS A TRANSMISSION CS IS LOCATED IN RICHLAND COUNTY, OHIO THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COMPANY), A TC ENERGY ENTITY. AT 19:51 EST, A COMPANY PERSONNEL RECEIVED A NOTIFICATION FROM THE PUBLIC OF A POTENTIAL RELEASE OF MATERIAL AT PAVONIA CS. COMPANY OPERATIONS PERSONNEL ARRIVED ON-SITE AT 20:04 EST WHERE THE UNINTENDED RELEASE OF MATERIAL WAS IDENTIFIED AND ISOLATED AT 20:51 EST. THE PRELIMINARY MATERIAL LOSS CALCULATIONS WERE DETERMINED TO BE GREATER THAN 3,000 MCF, HENCE, THE EVENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER (NRC). THE PRELIMINARY ASSESSMENT DETERMINED A SMALL CONTROL AIR LEAKAGE ON THE BLOW-OFF VALVE AND FROST IN THE LINE CAUSED THE UNINTENTIONAL OPERATION OF THE BLOW-OFF VALVE. AN INVESTIGATION WAS COMPLETED, AND IT WAS CONFIRMED THAT MOISTURE IN THE TRIGGER AIRLINE FREEZING-OFF IS THE MOST LIKELY CASUAL FACTOR FOR THE UNINTENTIONAL OPENING OF THE BLOW-OFF VALVE. THE TRIGGER AIR SYSTEM FOR BLOW-OFF VALVE IS A STAGNATE SYSTEM UNLESS A LEAK ALLOWS FLOW IN THE TRIGGER AIRLINES. A LEAK IN THE SYSTEM IS THE MOST PROBABLE CAUSE AS THE LEAK WOULD INDUCE FLOW IN THE TRIGGER SYSTEM AND ALLOW PRESSURE TO DISSIPATE ONCE A BLOCKAGE EXIST. VALVE. THE INITIAL NRC REPORT NO.1327142 AND THE NRC 48-HOUR REPORT NO.1327254 HAVE BEEN CALLED-IN ON JANUARY 23RD AND JANUARY 25TH RESPECTIVELY. TWO RECOMMENDATIONS WERE ISSUED IN ORDER TO AVOID FUTURE RE-OCCURRENCE FROM TAKING PLACE AT THIS CS. THEY WERE: I) CHECK ALL ABOVE GRADE ESD TRIGGER AIR PIPING AND CONNECTIONS FOR LEAKS, II) ADD A PROJECT TO INSTALL A MOISTURE ANALYZER ON THE AIR DRYER. THE FINAL REPORT WILL BE SUBMITTED AFTER COMPLETION OF THE PROJECT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220015 | 36454 | 2022-02-18 11:41 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2022-01-20 13:20 | 2022 | CENTRAL | NO | 34.6286 | -97.2165 | 1326974 | 2022-01-20 14:58 | 1327160 | NATURAL GAS |  | 7465.91 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE CONTINUED OPERATION THROUGH BYPASS PIPING AND DID NOT REQUIRE SHUTDOWN. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE REDUCTION BYPASS STOPPLE FITTING |  | OPERATIONAL CONTROL | BYPASS |  | 0 | 2022-01-20 10:38 | 2022-01-20 11:00 | ONSHORE | OK | 73098 | WYNNEWOOD | GARVIN | NOT APPLICABLE |  | LINE L-56 | LINE L-56 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.188 | 42000 | X42 API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 1994 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1.5 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO |  |  | YES |  | YES | 0 | 0 | 0 | 0 | 54725 | 54725 | 10000 | 10000 | 73477 | 73477 | 0 | 0 |  | 7.33 | 138202 | 72734.4549573623407977375415282392026578 | 138202 | 0 | 0 | 0 | 0 | NO |  |  |  | 530 | 18.12 | 680 | 192.619(A)(3) |  | 1993-12-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 14322 | NO | YES | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | [7 empty] | FARMER | GRADER/SCRAPER | UNKNOWN/OTHER | NO | [5 empty] | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@gmail.com | 4052487018 |  | SETH SLIFER | seth.slifer@onegas.com | 4052487018 | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 4052390573 | meghan.booker@onegas.com | LANDOWNER WAS BURYING A HORSE IN A RAVINE WITHOUT A ONE-CALL LOCATE REQUEST. DURING EXCAVATION THE OPERATOR STRUCK AN 8" HIGH PRESSURE PIPELINE THAT IS LAID IN ONG RIGHT OF WAY. BY-PASS FITTINGS WERE UTILIZED TO AVOID SERVICE INTERRUPTION TO DOWNSTREAM CUSTOMERS. BYPASS FITTINGS AND PIPE INSTALLATION COMPLETE ON 1/21/2022.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220016 | 36362 | 2022-02-18 12:27 | ORIGINAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2022-01-27 00:51 | 2022 | CENTRAL | NO | 37.5858 | -100.4511 | 1327393 | 2022-01-27 01:23 | 1327514 | NATURAL GAS |  | 22539 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-27 01:24 | 2022-01-27 11:00 |  | YES | OPERATOR | 2022-01-27 01:10 | NO | [11 empty] | 1 | 2022-01-27 00:51 | 2022-01-27 01:15 | ONSHORE | KS | 67867 | MONTEZUMA | GRAY | NOT APPLICABLE |  | MONTEZUMA COMPRESSOR STATION | MONTEZUME STATION DISCHARGE LINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1955 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | FAILURE OF ISOLATION VALVE TO CLOSE DURING STATION ESD. | CLASS 1 LOCATION | NO |  | 413 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 134107 | 134107 | 2700 | 2700 | 300 | 300 | 0 | 0 |  | 5.95 | 137107 | 89317.2807831722639235880398671096345515 | 137107 | 0 | 0 | 1 | 0 | NO |  |  |  | 850 | 140000 | 899 | 192.619(C) |  | 1967-06-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ICE AND DEBRIS BUILD-UP IN CONTROL CYLINDER FOR VALVE ACTUATOR | [161 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 12702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP CHIEF OPERATIONS OFFICER | 12708524670 | shawn.patterson@southernstar.com | ON 1/27/2022 AS 12:51 AM CST, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) LEADER, FIELD OPERATIONS WAS NOTIFIED BY A SSCGP FIELD EMPLOYEE THAT GAS WAS VENTING AT THE MONTEZUMA COMPRESSOR STATION. THE LEADER CONTACTED GAS CONTROL (GC) AT 12:53 AM AND GC CONFIRMED THE STATION HAD AN ESD IN PROGRESS. LEADER WAS INFORMED LOCAL POLICE WERE ON SITE AND SPOKE WITH THEM AT 1:10 AM. LOCAL POLICE CLOSED ROAD 12 AND REQUESTED THE RESIDENCE AT THE CORNER OF ROAD 12/GERONIMO ROAD TO VOLUNTARILY EVACUATE. SSCGP PERSONNEL ARRIVED ON SITE AT 1:15 AM TO BEGIN INSPECTION. BLOW-OFF VALVE WAS CLOSED AT 1:24 AM TO STOP GAS FROM VENTING. GC NOTIFIED THE NRC AT 1:23 AM (#1327393) BASED ON THE ESTIMATED RATE OF GAS LOSS. AT 2:10 AM, THE LOCAL POLICE WERE NOTIFIED TO GIVE THE ALL CLEAR AND THAT SSCGP PERSONNEL WOULD REMAIN ON SITE TO MONITOR. THE STATION WAS PLACED BACK IN SERVICE ON 1/27/2022 AT 11:00 AM. THE STATION WAS INSPECTED FOR THE CAUSE OF THE ESD AND THE CAUSE OF THE ISOLATION VALVE CLOSURE FAILURE. THE ESD WAS TRIGGERED BY AN OIL LEAK ON ENGINE 3, THIS OIL LINE FITTING WAS REPLACED ON THE MORNING OF 1/28/2022. THE ACTUATOR AND CONTROL CYLINDER WERE INSPECTED, ICE AND DEBRIS REMOVED, O-RINGS AND HYDRAULIC FLUID WERE REPLACED ON 1/28/2022. THE STATION ESD WAS TESTED ON 1/28/2022 AFTER ALL REPAIRS WERE COMPLETED AND ALL VALVES ACTUATED PROPERLY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220017 | 36435 | 2022-02-18 16:01 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-01-21 17:00 | 2022 | CENTRAL | NO | 28.8887 | -90.8233 | 1327078 | 2022-01-22 14:03 |  | NATURAL GAS |  | 57802 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-22 14:30 | 2022-01-30 20:30 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-22 14:00 | NO | [5 empty] | VALVE CLOSURE |  | 2022-01-22 10:00 | VALVE CLOSURE |  | 2022-01-22 14:30 | 0 | 2022-01-29 11:00 | 2022-01-22 08:45 | OFFSHORE | [6 empty] | SEA ROBIN - EAST | 300-2 | [20 empty] | 20 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SHIP SHOAL | 93 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 4.06 | 65000 | API-5LX-6500 | DSAW |  | KAISER | EPOXY |  | NO | [26 empty] | 1981 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | 1INCH X 7/8INCH OVAL HOLE | [5 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 274560 | 274560 | 225382 | 225382 | 5000 | 5000 | 0 | 0 |  | 4.75 | 504942 | 281787.2099479806696350631229235880398671 | 504942 | 0 | 0 | 0 | 0 | NO |  |  |  | 930 | 0 | 1200 | 192.619(A)(2) |  | 2004-12-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 174240 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | STATIC SHUT-IN TEST OR OTHER PRESSURE OR LEAK TEST |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PEGGY WEST | SR. REGULATORY ANALYST | peggy.west@energytransfer.com | 409-202-3088 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713.989.7126 | todd.nardozzi@energytransfer.com | AT APPROXIMATELY 3:14 PM ON 01/21/2022, GAS CONTROL RECEIVED A CALL FROM A 3RD PARTY REPORTING SEEING BUBBLES IN THE AREA NEAR THE SEA ROBIN 300-2 PIPELINE IN SHIP SHOAL 93. THE INITIAL NRC REPORT (1327078) WAS SUBMITTED BY A THIRD PARTY PRODUCER ON 1/22/22 AT 2.03 PM. OFFSHORE WEATHER CONDITIONS CAUSED A DELAY IN DETERMINING THE SOURCE OF THE LEAK AND THE REPAIRS. AN OVERFLIGHT WAS ABLE TO BE ACCOMPLISHED ON 01/22/22 AND BASED ON THE COORDINATES OF THE LEAK AND THE 300-2 LINE WAS ISOLATED AT APPROXIMATELY 2:30 PM ON 1/22/22. DUE TO CONTINUED POOR OFFSHORE WEATHER CONDITIONS THE REPAIR CONTRACTOR WAS NOT ABLE TO DEPLOY UNTIL 1/29/22 TO INSPECT THE PIPE AND AFFECT A REPAIR. THE CAUSE OF THE RELEASE WAS DETERMINED TO BE DUE TO INTERNAL CORROSION. A MECHANICAL CLAMP WAS USED TO REPAIR THE PIPELINE ON 1/30/22 AT APPROXIMATELY 8:30 PM AND IS AVAILABLE FOR SERVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220018 | 37222 | 2022-02-22 17:27 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-01-23 22:41 | 2022 | EASTERN | NO | 42.8119 | -82.8676 | 1327259 | 2022-01-25 09:53 | 1327299 | NATURAL GAS |  | 5617 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-23 23:55 | 2022-01-27 21:30 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-01-23 23:25 | NO | [11 empty] | 0 | 2022-01-23 22:41 | 2022-01-23 23:25 | ONSHORE | MI | 48062 | ARMADA | MACOMB | NOT APPLICABLE |  | RAY COMPRESSOR STATION | RELIEF VALVE RV-22 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | RELIEF VALVE OPP | 1966 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEVE VALVE ACTIVATION | CLASS 1 LOCATION | NO |  | 702 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 19154 | 19154 | 8175 | 8175 | 285 | 285 | 0 | 0 |  | 3.41 | 27614 | 16300.0519082135583508970099667774086379 | 27614 | 0 | 0 | 0 | 0 | NO |  |  |  | 1389 | 0 | 1800 | OTHER | THE VESSEL CONSTRUCTED BASED ON THE 1965 ASME CODE FOR UNFIRED VESSELS MAY 1966 | 1966-05-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE COMPRESSOR STATION IS MONITORED BY SCADA HOWEVER THERE IS NO INSTRUMENTATION ON RV-22 THAT WOULD HAVE PROVIDED INDICATION TO THE OPERATOR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [19 empty] | YES | [7 empty] | YES | [163 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON JANUARY 23, 2022 AT APPROXIMATELY 22:41 HOURS CONSUMERS ENERGY WAS NOTIFIED OF A POSSIBLE GAS RELEASE AT THE RAY COMPRESSOR STATION. RAY COMPRESSOR STATION IS LOCATED AT 69333 OMO ROAD, ARMADA, (MACOMB COUNTY) MICHIGAN. A STATION MECHANIC WAS DISPATCHED AND ARRIVED AT THE SITE AT APPROXIMATELY 23:25 HOURS. UPON ARRIVAL THE MECHANIC COMMUNICATED WITH EMERGENCY RESPONDERS THAT WERE ALREADY AT THE SITE AND PROCEEDED INTO THE PLANT TO DETERMINE THE SOURCE OF THE RELEASE. THE MECHANIC DISCOVERED GAS BLOWING FROM THE RELIEF VALVE (RV-22) ON THE PLANT 1 FILTER-SEPARATOR EQUIPMENT. PLANT 1 PROCESSING EQUIPMENT WAS SHUT-IN AND ISOLATED FROM THE STORAGE FIELD ELIMINATING ANY POTENTIAL HAZARDS AND ALLOWING FOR FURTHER INVESTIGATION. OPERATIONS EMPLOYEES BEGAN INVESTIGATING ON JANUARY 24, 2022. DURING THE INVESTIGATION, IT WAS DETERMINED RAY COMPRESSOR STATION RELIEF VALVE (RV-22) EXPERIENCED AN ABNORMAL OPERATING CONDITION, RV-22 ACTIVATION OCCURRED AT 1389 PSIG INSTEAD OF THE SET POINT ACTIVATION OF 1926 PSIG. THE PREMATURE ACTIVATION OCCURRED BECAUSE OF THE PRESENCE OF FOREIGN MATERIAL. DURING AN EXTERNAL EVALUATION OF THE RELIEF VALVE, EXCESSIVE LUBRICANT WAS VISUALLY OBSERVED AND AN INTERNAL INSPECTION OF THE RELIEF BLOWDOWN VALVE IDENTIFIED A FAILED O-RING, THE COMBINATION OF THE EXCESSIVE LUBRICANT AND THE FAILED O-RING CAUSED TO RELIEF VALVE TO FAIL. IMMEDIATE CORRECTIVE ACTIONS WERE IMPLEMENTED AND THE CONTROL VALVE WAS REBUILT, BENCH TESTED AND FIELD TESTED PRIOR TO RETURNING THE EQUIPMENT TO NORMAL OPERATIONS. ADDITIONAL CORRECTIVE ACTIONS AND EXTENT OF CONDITION IS BEING EVALUATED TO MINIMIZE FUTURE OCCURRENCE ACROSS THE SYSTEM.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220019 | 36416 | 2022-02-23 12:19 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-01-24 11:50 | 2022 | EASTERN | NO | 39.6387 | -79.3409 | 1327197 | 2022-01-24 13:27 | 1327381 | NATURAL GAS |  | 3434.4 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | JUST THE COMPRESSOR STATION WAS SHUT IN |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-01-24 11:50 | 2022-01-24 11:50 | ONSHORE | MD | 21520 | Not Within a Municipality | GARRETT | MILEPOST | 0 | TEXAS EASTERN TRANSMISSION, LP ACCIDENT STORAGE | ACCIDENT COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1966 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUT DOWN (ESD) | CLASS 1 LOCATION | NO |  | 354 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 13841 | 13841 | 1000 | 1000 | 500 | 500 | 0 | 0 |  | 4.03 | 15341 | 9743.461820157560533222591362126245847176 | 15341 | 0 | 0 | 0 | 0 | NO |  |  |  | 2540 | 396210 | 3550 | 192.619(A)(2) |  | 1965-11-08 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLERS ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | MALFUNCTION OF A FIRE DETECTION DEVICE. | [161 empty] | MICHAEL MCGRATH |  | michael.mcgrath@enbridge.com | 6128056542 |  |  |  |  | NATHAN ATANU |  | 7136275008 | nathan.atanu@enbridge.com | MALFUNCTION OF FIRE DETECTION DEVICE RESULTED IN AN UNINTENTIONAL EMERGENCY SHUTDOWN (ESD) AND VENTING OF THE STATION. THE FAULTY DEVICE HAS BEEN REPLACED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220020 | 37101 | 2022-02-25 17:47 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2022-01-27 00:25 | 2022 | CENTRAL | NO | 30.3511 | -97.5886 | 1327416 | 2022-01-27 10:07 | 1327538 | NATURAL GAS |  | 35.03 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-27 02:34 | 2022-02-03 17:45 |  | YES | OPERATOR | 2022-01-27 02:34 | NO | [11 empty] | 0 | 2022-01-27 02:34 | 2022-01-27 02:34 | ONSHORE | TX | 78653 | MANOR | TRAVIS | SURVEY STATION NO. | 36+53 | P-20 | P-20 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 8.625 | NO | 0.322 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | PAINT |  | YES | [26 empty] | 2015 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | 3RD PARTY VEHICLE DAMAGE ON ABOVE-GROUND PIPING | CLASS 1 LOCATION | NO |  | 166 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 276 | 276 | 298701 | 298701 | 828 | 828 | 0 | 0 |  | 7.874 | 299805 | 132321.8193953979150291129568106312292359 | 299805 | 0 | 0 | 0 | 0 | NO |  |  |  | 699 | 1120.8 | 778 | 192.619(A)(2) |  | 2015-09-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | YES |  | YES | SMALL TRUCK | ROADWAY | 50 | YES |  | YES | [236 empty] | DALE GAMBRELL | SUPERVISOR COMPLIANCE | dale.gambrell@atmosenergy.com | 512-310-3841 |  | DALE GAMBRELL | dale.gambrell@atmosenergy.com | 512-310-3841 | MARLO SUTTON | VP TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON JANUARY 27, 2022, AT APPROXIMATELY 1:06 AM, A PASSERBY MADE AN EMERGENCY REPORT THAT A VEHICLE HAD DAMAGED NATURAL GAS FACILITIES NEAR 8514 EAST PARMER LANE. THE NATURAL GAS FACILITIES AT THIS LOCATION ARE PRIMARILY OWNED AND OPERATED BY TEXAS GAS SERVICE (TGS), AND TGS REPRESENTATIVES WERE ON THE SCENE. ATMOS SERVICE TECHNICIAN ARRIVED AT 2:34 AM, VERIFIED THAT THE GAS WAS SHUT OFF, AND REQUESTED THAT A MEASUREMENT, INSTRUMENT, AND CONTROLS (MIC)TECHNICIAN BE DISPATCHED TO THE SCENE AS WELL. THE MIC TECHNICIAN WAS IMMEDIATELY DISPATCHED. TGS HANDLED THE REMOVAL OF THE VEHICLE AND TEMPORARY FENCING. ATMOS ENERGY WAS ONSITE, STANDING BY. PRELIMINARILY, IT APPEARED THAT THE PROPERTY DAMAGE WAS NEARLY ENTIRELY DAMAGE TO THE FACILITIES OF TGS RATHER THAN THE FACILITIES OF ATMOS ENERGY. HOWEVER, DURING THE COURSE OF THE EMERGENCY RESPONSE, AT APPROXIMATELY 9:30 AM CST, ATMOS ENERGY DETERMINED THERE MAY BE SUFFICIENT DAMAGE TO ATMOS ENERGY'S PROPERTY TO EXCEED THE COST THRESHOLD ESTABLISHED IN 49 CFR 191.3. THEREFORE, ATMOS ENERGY REPORTED THE EVENT TO NRC AT 10:07 AM CST. A CLAMP-ON ULTRASONIC METER WAS INSTALLED AND TEMPORARY REPAIRS WERE MADE TO BE ABLE TO PLACE STATION BACK IN SERVICE. SERVICE FROM ATMOS ENERGY TO TGS WAS RESTORED ON FEBRUARY 3, 2022, AT 5:45 PM.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220021 | 37436 | 2022-02-28 07:48 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2022-02-04 14:20 | 2022 | EASTERN | NO | 40.8248 | -80.7567 | 1328093 | 2022-02-04 14:50 | 1328149 | NATURAL GAS |  | 40 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-01-31 19:10 | 2022-12-02 13:30 |  | YES | OPERATOR | 2022-01-01 18:45 | YES | 2022-01-31 17:45 | OPERATOR/CONTRACTOR |  | 40 | NO | [6 empty] | 0 | 2022-01-31 17:51 | 2022-01-31 18:00 | ONSHORE | OH | 44431 | LEETONIA | COLUMBIANA | NOT APPLICABLE |  | BRINKER COMPRESSOR STATION | DEHYDRATION SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | DEHYDRATOR/DRIER/TREATER/SCRUBBER | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | NO |  | 65 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 132 | 132 | 460000 | 460000 | 1000 | 1000 | 0 | 0 |  | 3.3 | 461132 | 203462.1553197857301229235880398671096346 | 461132 | 0 | 0 | 0 | 0 | NO |  |  |  | 40 | 1179 | 50 | 192.619(A)(1) |  | 2003-06-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FIRE WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | FIRE ON DEHYDRATION UNIT | [15 empty] | YES | AN INVESTIGATION TEAM WAS FORMED TO DETERMINE THE PROBABLE CAUSE OF THE FIRE | [161 empty] | KAMRAN ROSTAMI ASRABADI |  | kamran_rostami@tcenergy.com | (304)590-5956 |  |  |  |  | PAUL SHAFFER |  | (304)550-4866 | paul_shaffer@tcenergy.com | ON JANUARY 31ST, 2022, BRINKER COMPRESSOR STATION (CS) EXPERIENCED AN UNINTENTIONAL RELEASE OF NATURAL GAS (MATERIAL) INTO ATMOSPHERE. BRINKER IS A TRANSMISSION CS THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COMPANY), A TC ENERGY ENTITY. BRINKER CS IS LOCATED IN COLUMBIANA COUNTY, OHIO. AT 17:45 EST, A COMPANY EMPLOYEE RECEIVED A NOTIFICATION FROM THE PUBLIC OF A FIRE AT BRINKER CS. COMPANY OPERATIONS PERSONNEL ARRIVED ON-SITE AT 18:00 EST AND THE FIRE ON THE DEHYDRATION UNIT WAS CONFIRMED. AFTER AN INITIAL ASSESSMENT OF THE SITUATION AND TAKING ALL SAFETY PRECAUTIONS, PERSONNEL ISOLATED THE FUEL GAS SUPPLY TO THE DEHYDRATION SYSTEM AT 18:35 EST AND THE FIRE WAS EXTINGUISHED. THE PRELIMINARY MATERIAL LOSS CALCULATION WAS DETERMINED TO BE 44 MCF. ON FEBRUARY 4, 2022, AFTER THE DAMAGE CAUSED BY THE FIRE WAS FULLY EVALUATED AND ASSESSED, IT WAS DETERMINED THAT THE COST OF REPAIRS MAY EXCEED $122,000 SO THE EVENT WAS PROMPTLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC). AN INVESTIGATION TEAM WAS FORMED TO DETERMINE THE PROBABLE CAUSE OF THE FIRE ON THE DEHYDRATION UNIT. THE INITIAL NRC REPORT NO.1328093 AND THE NRC 48-HOUR REPORT NO.1328149 HAVE BEEN RECEIVED ON FEBRUARY 4TH AND FEBRUARY 5TH RESPECTIVELY. AN INVESTIGATION WAS COMPLETED, AND THE FOLLOWING CASUAL FACTORS (CF) WERE IDENTIFIED: 1- INTERNAL MESH OF THE CONTRACTOR PREVENTED WET GLYCOL RETURN VALVE FOR CLOSING. 2- DUE TO THE GLYCOL FLOODING THE REBOILER AND SURGE TANK, GAS PRESSURE DID NOT REACH PRESSURE SAFETY VALVE (PSV)-100 THAT WAS LOCATED ON REBOILER, THEREFORE PSV-100 DID NOT ACTIVATE TO RELEASE GAS PRESSURE. THE FOLLOWING RECOMMENDATIONS WERE ISSUED IN ORDER TO AVOID FUTURE RE-OCCURRENCE FROM TAKING PLACE AT THIS CS. 1- CREATE PREVENTIVE MAINTENANCE AND MONITORING PLAN SPECIFICALLY FOR THE BRINKER CONTACT TOWER WITH INCREASED INTERNAL INSPECTION 2- THE TOWER WILL BE REPLACED. 3- INSTALL HIGH LEVEL ALARM FOR THE REBOILER AND SURGE TANK THAT ALARMS TO THE STATION CONTROL PANEL AND HIGH-HIGH SWITCH TO DRAIN THE REBOILER THE PROJECT AT BRINKER CS WAS COMPLETED AND DEHY WAS PLACED INTO SERVICE ON DECEMBER 2, 2022,
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220022 | 36580 | 2022-03-01 11:53 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2022-02-03 11:57 | 2022 | CENTRAL | YES | 36.0192 | -94.0508 | 1327992 | 2022-02-03 12:07 | 1328134 | NATURAL GAS |  | 12740 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-03 09:45 | 2022-02-03 13:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-03 09:30 | VALVE CLOSURE |  | 2022-02-03 09:45 | 0 | 2022-02-03 05:48 | 2022-02-03 05:48 | ONSHORE | AR | 72701 | FAYETTEVILLE | WASHINGTON | MILEPOST | MM 160 | 24751 | P-228 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | BOLTED DRESSER COUPLING | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | BOLTED DRESSER COUPLING & PIPE SEPARATION | CLASS 1 LOCATION | NO |  | 160 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 77969 | 77969 | 1400 | 1400 | 6788 | 6788 | 0 | 0 |  | 6.12 | 86157 | 54771.2934671505687695548172757475083056 | 86157 | 0 | 0 | 5 | 0 | NO |  |  |  | 445 | 2235 | 635 | 192.619(A)(3) |  | 2009-07-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 3700 | NO |  | YES | [5 empty] | YES |  |  |  | YES |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM ACTIONS WERE NOT A CONTRIBUTING FACTOR TO THIS INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | MECHANICAL COUPLING | [17 empty] | YES |  | YES | BOLTED DRESSER COUPLING FAILURE | [161 empty] | PRESTON J WALKER | PIPELINE SAFETY PROFESSIONAL | preston.walker@blackhillscorp.com | 4796018392 |  | TRON HODGES | tron.hodges@blackhillscorp.com | 479-601-8382 | PRESTON J WALKER | PIPELINE SAFETY PROFESSIONAL | 4796018392 | preston.walker@blackhillscorp.com | ON FEBRUARY 3, 2022 @ APPROXIMATELY 4:30AM BLACK HILLS ENERGY GAS CONTROL CENTER NOTICED A SIGNIFICANT DROP IN GAS PRESSURE BETWEEN OZARK & THE MCDONALDS VALVE SET IN FAYETTEVILLE. AT 4:53 AM BLACK HILLS ENERGY RECEIVED A GAS LEAK CALL @ 12018 STRAIN COMMUNITY RD IN FAYETTEVILLE. BHEA OPERATIONS TECH ARRIVED ON SITE AT THE BAGLEY VALVE SETTING AROUND 5:48 AM TO DISCOVER THE LEAKING MAIN. BHEA MAINTENANCE CREW WAS DISPATCHED TO THE SCENE AND WITH ASSISTANCE FROM THE ENGINEERING TEAM & GAS CONTROL THE FLOW OF GAS WAS REROUTED, AND THE MAINTENANCE TEAM WAS ABLE TO SAFELY GAIN CONTROL OF THE ESCAPING GAS @ 9:45 AM. REPAIRS CONSISTED OF REMOVAL OF THE 8-INCH BOLTED DRESSER COUPLING AND INSTALLING TWO 8-INCH WELD CAPS OF BOTH ENDS OF THE AFFECTED SEGMENT TO RESTORE SERVICE TO 5 EFFECTED CUSTOMERS. THIS LATERAL 8-INCH PIPE SEGMENT BETWEEN BAGLEY VALVE & HILL VALVE SETTING IS UNDER THE PLANNING STAGES OF REPLACEMENT.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220023 | 36590 | 2022-03-03 11:47 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-02-10 02:30 | 2022 | CENTRAL | NO | 31.9986 | -104.1253 | 1328568 | 2022-02-10 02:43 | 1328715 | NATURAL GAS |  | 66 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-10 00:20 | 2022-02-13 09:45 |  | YES | OPERATOR | 2022-02-09 23:45 | YES | 2022-02-09 23:38 | OPERATOR/CONTRACTOR |  | 66 | NO | [6 empty] | 0 | 2022-02-10 00:20 | 2022-02-10 00:20 | ONSHORE | TX | 79770 | ORLA | CULBERSON | MILEPOST | 0+00 | DELAWARE COMP TX-CULBERSON_T-P RW T1S BLK 58,59 SU | #5 COMPRESSOR DISCHARGE CHECK VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2012 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3 | 1.5 |  | CLASS 1 LOCATION | NO |  | 80 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 284 | 284 | 290000 | 290000 | 500 | 500 | 0 | 0 |  | 4.31 | 290784 | 128343.8195691853196129568106312292358804 | 290784 | 0 | 0 | 0 | 0 | NO |  |  |  | 980 | 32000 | 1200 | 192.619(A)(2) |  | 2021-03-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TYPE A GATHERING | NO |  |  |  |  | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | MATERIAL/WELD/EQUIP FAILURE | FAILURE OF EQUIPMENT BODY | [166 empty] | FAILURE OF EQUIPMENT BODY (EXCEPT COMPRESSOR), VESSEL PLATE, OR OTHER MATERIAL | [23 empty] | YES | [9 empty] | YES | [155 empty] | YES | [8 empty] | CHRISTOPHER PALAFOX | SPECIALIST REGULATORY COMPLIANCE | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON FEBRUARY 10, 2022 AT APPROXIMATELY 00:20, A FIRE OCCURRED AT THE DELAWARE COMPRESSION STATION, A NON-REGULATED GATHERING STATION, 18 MILES NORTH-NORTHWEST OF ORLA, TX, 0.1 MILE SOUTH OF THE NEW MEXICO STATE LINE. OPERATIONS RECEIVED A CALL FROM GAS CONTROL STATING THAT THE COMPRESSOR STATION HAD A LOSS OF GAS AND OPERATIONS IMMEDIATELY DISPATCHED A TECHNICIAN TO THE STATION. WHEN THE TECHNICIAN ARRIVED ON SITE, HE CONFIRMED THE STATION WAS ON FIRE, ESD THE STATION AND BEGAN TO EXTINGUISH THE FIRE WITH CAUTION. WHEN THE FIRE WAS COMPLETELY EXTINGUISHED THE TECHNICIAN CALLED THE LOCAL FIRE DEPARTMENT IN CASE THERE WAS A RE-FLASH. WHEN THE STATION WAS SAFE TO ENTER, OPERATIONS BEGAN THE DAMAGE ASSESSMENT. IT WAS DETERMINED AT APPROXIMATELY 02:30 ON FEBRUARY 10, 2022, THE INCIDENT REPORTING CRITERIA WAS GOING TO BE MET. THE ASSESSMENT WAS DETERMINED THAT THE #5 UNIT'S DISCHARGE CHECK VALVE RUPTURED CAUSING THE INTAKE OF THE #3 UNIT, THE SECOND STAGE SCRUBBER ON THE #4 UNIT AND #5 UNIT TO CATCH FIRE AND THE ESTIMATED DAMAGE AND REPAIR DOLLAR AMOUNT WAS GOING TO BE OVER $122,000. THE DAMAGED DISCHARGE CHECK VALVE WAS REMOVED AND REPLACED WITH A NEW CHECK VALVE AND HAS BEEN SENT TO THE LAB FOR ANALYSIS. THE CAUSE OF THE RUPTURE IS UNKNOWN AT THIS TIME, A SUPPLEMENTAL REPORT WILL BE SUBMITTED ONCE THE CAUSE IS KNOWN. ON FEBRUARY 13, 2022, AT APPROXIMATELY 09:45 THE DELAWARE COMPRESSOR STATION WAS PUT BACK INTO SERVICE. ON MARCH 30, 2022, THE LAB REPORT WAS RECEIVED AND REVIEWED BY OUR METALLURGIST. IT WAS DETERMINED THAT A MANUFACTURING DEFECT COMBINED WITH THERMAL STRESS WAS THE CAUSE OF THE FAILURE. THIS WAS AN ISOLATED INCIDENT. OPERATIONS WILL REVIEW OTHER CHECK VALVES AT OTHER LOCATIONS AND REPLACE IF NEEDED TO PREVENT THIS FROM REOCCURRING.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220024 | 36531 | 2022-03-07 13:37 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-02-10 17:06 | 2022 | EASTERN | NO | 40.1615 | -75.2003 | 1328644 | 2022-02-10 17:25 | 1328765 | NATURAL GAS |  | 17.02 | 302 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-09 10:00 | 2022-02-12 17:00 |  | YES | OPERATOR | 2022-02-10 17:25 | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-09 11:30 | VALVE CLOSURE |  | 2022-02-09 13:30 | 0 | 2022-02-09 09:20 | 2022-02-09 09:00 | ONSHORE | PA | 19002 | UPPER DUBLIN | MONTGOMERY | MILEPOST | 2.34 | TRANSCO | ORELAND B LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 1970 | 1970 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | NO |  | 312 |  | NO | NO |  |  | YES | YES |  | 0 | 0 | 1057 | 1057 | 60 | 60 | 150000 | 150000 | 0 | 0 | 0 | 0 |  | 3.5 | 151117 | 66679.9317938642902803289036544850498339 | 151117 | 0 | 0 | 0 | 0 | NO |  |  |  | 638 | 94492 | 800 | 192.619(C) |  | 2002-09-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | REMOTELY CONTROLLED | MANUAL | 32630 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | INSULATING FLANGE GASKET FAILURE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS SUCH A SMALL LEAK FOR THE SYSTEM TO DETECT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | WEAR OVER TIME | [150 empty] | YES | [10 empty] | DIKA ONYEDIRIM | PIPELINE SAFETY ENGINEER | dika.onyedirim@williams.com | 2816608503 |  | JEFFREY EWING | jeffrey.a.ewing@williams.com | 6107316754 | TYSON GREEN | MANAGER PIPELINE SAFETY | 3464398090 | tyson.green@williams.com | ON 2/8/2022 AROUND 5:00 PM ON CALL PERSON RECEIVED A CALL FROM GAS CONTROL ABOUT A SMELL OF GAS AT 616 SUSQUEHANNA ROAD AMBLER, PA UPPER DUBLIN TOWNSHIP. EMPLOYEE ARRIVED ON SITE AROUND 6:15 PM. WHEN HE TURNED ON FLAME I (GAS DETECTOR) IT WENT OFF IMMEDIATELY. EMPLOYEE CALLED HIS SUPERVISOR AROUND 6:40 PM. SUPERVISOR ADVISED HIM TO CALL PECO (LOCAL LDC IN AREA) TO CHECK FOR LEAKS ON THERE SYSTEM WHICH IS WITHIN 20 FT. SUPERVISOR ARRIVED ON SITE AT 8:30 PM. AT 4:00 AM ON 2/9/2022 PECO DETERMINED IT WASN'T THEIR SYSTEM LEAKING. EMPLOYEE ON SITE CALLED SUPERVISOR RIGHT AWAY. WILLIAMS CREW WAS ON SITE AT 7:00 AM TO HAND DIG PIPELINE AND DISCOVERED IT WAS THE FLANGE LEAKING AT 9:20 AM. SUPERVISOR CALLED SOC AT 9:30 AM ON 2/9/2022. LINE WAS TAKEN OUT OF SERVICE AND DRAWN DOWN FROM 638 PSI TO 90 PSI. LEAK ON FLANGE WAS AS A RESULT OF WEAR AND TEAR THIS IS A VINTAGE INSULATING FLANGE NO ONE HAS EVER SEEN BEFORE. WILLIAMS CREW TRIED TO TORQUE BOLTS WITH NO LUCK. ON 2/10/2022 WILLIAMS CREW BROUGHT IN A BIGGER TORQUE GUN IN THAT WOULD GO HIGHER WITH NO LUCK. AT THIS POINT, WILLIAMS DETERMINED PROPERTY DAMAGE WOULD EXCEED THE REPORTABLE LIMIT OF $122,000 AND NOTIFIED THE NRC. DECISION WAS MADE TO CUT OUT FLANGE. 2/11/2022 LINE WILL BE BLOWN DOWN TO 0 PSI. REPLACEMENT INSULATING FLANGE DID NOT ARRIVE ON SCHEDULE SO CREWS INSTALLED A 24" PUP AND RETURNED THE LINE BACK IN SERVICE ON 2/12/2022 AROUND 5:00 PM. INSULATING FLANGE WILL BE INSTALLED AT A LATER DATE. NO RCA IS NEEDED AS CAUSE OF FAILURE IS NOT A WIDESPREAD.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220025 | 36436 | 2022-03-07 18:03 | ORIGINAL | 842 | AIR LIQUIDE LARGE INDUSTRIES U.S. LP | 9811 KATY FREEWAY SUITE 100 | HOUSTON | TX | 77024 | 2022-02-05 15:29 | 2022 | CENTRAL | YES | 28.2037 | -98.3783 | 1328173 | 2022-02-05 15:29 |  | HYDROGEN GAS |  | 136 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-02 13:28 | 2022-02-07 21:00 |  | YES | OPERATOR | 2022-02-05 15:29 | YES | 2022-02-05 12:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 135 | YES | VALVE CLOSURE |  | 2022-02-05 13:28 | VALVE CLOSURE |  | 2022-02-05 18:15 | 0 | 2022-02-05 12:45 | 2022-02-05 15:03 | ONSHORE | TX | 78071 | Not Within a Municipality | MC MULLEN | SURVEY STATION NO. | 100060-400000 | CORPUS TO THREE RIVERS HYDROGEN PIPELINE | 100060-400000 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 29 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 8 |  | 0.322 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1926 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | COMPLETE WELD FAILURE | CLASS 1 LOCATION | NO |  | 124 |  | NO | NO |  |  | NO |  |  | 20000 | 20000 | 0 | 0 | 302 | 302 | 70000 | 70000 | 0 | 0 | 10000 | 10000 | LAB WORK | 2.22 | 100302 | 44314.3262164841019933554817275747508306 | 100302 | 0 | 0 | 0 | 0 | NO |  |  |  | 338 | 284 | 375 | 192.619(A)(1) |  | 2011-01-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | MANUAL | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL CRM TASK COMPLETED PER CRM GUIDELINES AND PROCEDURES. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED |  | YES | [7 empty] | YES | HYDROGEN INDUCED CRACKING (HIC). | [19 empty] | YES | HYDROGEN INDUCED CRACKING (HIC). | UNKNOWN | [54 empty] | YES | YES | [6 empty] | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [51 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BOBBY L SKELTON | REGULATORY COMPLIANCE MANAGER | bobby.skelton@airliquide.com | 8327312176 |  | BOBBY L SKELTON | bobby.skelton@airliquide.com | 8327312176 | BOBBY L SKELTON | REGULATORY COMPLIANCE MANAGER | 8327312176 | bobby.skelton@airliquide.com | AT ~12:45 PM ON 02/05/22 THE AIR LIQUIDE OPERATION CONTROL CENTER (OCC) RECOGNIZED THAT A CUSTOMER FLOW AND PRESSURE DROPPED SIGNIFICANTLY. AT 13:28 THE OCC CONTROLLER MADE THE DECISION TO CLOSE THE UPSTREAM REMOTE OPERATED VALVE. AT 15:00 THE PIPELINE TECHNICIAN ARRIVED ON SITE AND CONFIRMED THE BREACH IN THE PIPELINE. ADDITIONAL PIPELINE OPERATIONS TECHNICIANS WERE DEPLOYED TO ISOLATE BOTH MANUAL BLOCK VALVE UPSTREAM AND DOWNSTREAM OF THE INCIDENT SITE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220027 | 36445 | 2022-03-10 10:33 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-02-20 08:04 | 2022 | CENTRAL | NO | 35.3346 | -92.6733 | 1329308 | 2022-02-20 10:16 | 1329431 | NATURAL GAS |  | 13750 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2022-02-20 08:04 | 2022-02-20 09:15 | ONSHORE | AR | 72063 | HATTIEVILLE | CONWAY | NOT APPLICABLE |  | ROUND MOUNTAIN COMPRESSOR STATION | LINE J | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | ESD | [5 empty] | CLASS 1 LOCATION | NO |  | 524 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 60225 | 60225 | 4000 | 4000 | 2750 | 2750 | 0 | 0 |  | 4.38 | 66975 | 42494.2451342306170838870431893687707641 | 66975 | 0 | 0 | 0 | 0 | NO |  |  |  | 880 | 300 | 1000 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STATION ESD DUE TO POWER FAILURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ACTUATOR SUPPLY GAS BLOCKAGE. | [147 empty] | YES | YES | [12 empty] | CASEY ROBERTS | LEAD SPECIALIST | casey.roberts@energytransfer.com | 4056263981 |  | CASEY ROBERTS | casey.roberts@energytransfer.com | 4056263981 | SUSIE SJULIN | DIRECTOR - REGULATORY COMPLIANCE | 4055575271 | susie.sjulin@energytransfer.com | ON 2/20/2022 THE ROUND MOUNTAIN COMPRESSOR STATION ESD'D WHEN A COMMERCIAL POWER FAILURE OCCURRED IN THE AREA. THE STATION WAS IDLE AT THE TIME OF THE POWER FAILURE. SYSTEM CONTROL RECOGNIZED THE ESD (AND A FLOW INCREASE FOR EGT LINE J) AND DISPATCHED OPS TO THE STATION TO DETERMINE CAUSE. WHEN OPS ARRIVED, THEY FOUND THE SUCTION VALVE OF THE STATION HAD NOT CLOSED ALLOWING LINE J (IN-SERVICE) GAS TO VENT INTO THE ATMOSPHERE. THE SUCTION VALVE WAS CLOSED BY THE RESPONDING OPERATOR AND THE UNINTENTIONAL RELEASE OF GAS WAS ELIMINATED. AFTER CLOSING THE SUCTION VALVE, OPERATIONS DETERMINED A REPORTABLE RELEASE HAD OCCURRED AND A CALL WAS PLACED TO THE NRC (NRC#1329308). A 48 HR. FOLLOW UP WAS PROVIDED (NRC#1329431) ON 2/22/2022. AFTER FURTHER INVESTIGATION, IT WAS DETERMINED THE SUCTION VALVE FAILED TO CLOSE DUE TO DEBRIS IN THE ACTUATOR GAS SUPPLY LINE. THE DEBRIS WAS CLEARED FROM THE LINE AND A TEST WAS PERFORMED TO CONFIRM THE VALVE WAS OPERABLE. GOING FORWARD, A FILTER WILL BE PLACED ON THE LINE TO REMOVE CONTAMINANTS FROM THE GAS SUPPLY ALLOWING THE ACTUATOR TO WORK AS INTENDED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220028 | 36462 | 2022-03-10 14:02 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2022-02-24 12:05 | 2022 | MOUNTAIN | YES | 40.0472 | -108.7744 | 1329662 | 2022-02-24 16:26 | 1329711 | NATURAL GAS |  | 9879 | 315 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-24 12:20 | 2022-02-25 16:25 |  | NO |  |  | NO | [11 empty] | 0 | 2022-02-24 12:05 | 2022-02-24 12:05 | ONSHORE | CO | 81648 | RANGELY | RIO BLANCO | MILEPOST | 278.13 | NWP RANGELY COMPRESSOR STATION | RANGELY COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1994 | 1993 | CARBON STEEL |  | OTHER | [8 empty] | SIDE GATE VALVE ACTUATOR DIDN'T PROPERLY CLOSE THE VALVE, RESULTING IN 3" AND 8" VENT VALVES VENTING TO ATMOSPHERE WHILE THE STATION WAS NOT COMPLETELY ISOLATED. | CLASS 1 LOCATION | NO |  | 510 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 1433 | 1433 | 44949 | 44949 | 62500 | 62500 | 7000 | 7000 | 0 | 0 |  | 4.55 | 115882 | 60786.0375339094321865481727574750830565 | 115882 | 0 | 0 | 0 | 0 | NO |  |  |  | 650 | 250000 | 809 | 192.619(A)(2) |  | 1956-02-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE HARDWARE CONTROLLERS WERE AFFECTED BY A WATER LINE BREAK, WHICH CAUSED THEM TO MALFUNCTION AND NOT PROPERLY CLOSE THE SIDE GATE VALVE WHEN MANUALLY GIVEN AN ESD COMMAND | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | CONTROLS FOR THE ACTUATOR MALFUNCTIONED DUE TO WATER EXPOSURE IN CONTROL ROOM | [161 empty] | TAYLER JENSEN | PIPELINE SAFETY ENGINEER | tayler.jensen@williams.com | 2813828869 |  |  |  |  | TYSON GREEN |  | 346-439-9090 | tyson.green@williams.com | ON FEBRUARY 24TH, 2022 THERE WAS A WATER MAIN RUPTURE INSIDE THE CONTROLS ROOM AT NORTHWEST PIPELINE RANGELY COMPRESSOR STATION. EMERGENCY CONTROL DEVICES WERE IMPACTED AND EXPOSED TO WATER AS A RESULT OF THE LEAK, CAUSING OPERATIONS TO MAKE THE DECISION TO BLOW THE STATION DOWN. WHILE THE STATION WAS BLOWING DOWN, OPERATIONS PERSONNEL NOTICED THE BLOWDOWN WAS TAKING LONGER THAN IT TYPICALLY WOULD AND STARTED TO INVESTIGATE. OPERATIONS IDENTIFIED THAT THE SIDEGATE ACTUATOR HAD ONLY CLOSED 75% OF THE WAY. AS A RESULT, TWO OF THE STATION BLOWDOWN VALVES (3" AND 8" PLUG VALVES) WERE VENTING MAINLINE PRESSURE GAS TO THE ATMOSPHERE FROM THE TIME THE ESD SYSTEM WAS ACTIVATED TO THE TIME THE SIDEGATE WAS MANUALLY CLOSED BY OPERATIONS PERSONNEL. IT IS ESTIMATED THAT IT TOOK OPERATIONS 15 MINUTES BETWEEN ORIGINAL ESD ACTIVATION AND COMPLETE SHUT IN OF THE MALFUNCTIONING SIDE GATE VALVE AND COMPRESSOR STATION. ONCE THE SIDEGATE WAS PROPERLY CLOSED, AND THE STATION WAS SHUT IN FROM THE MAINLINE, A PROPER ESD WAS SUCCESSFULLY EXECUTED. IT WAS IDENTIFIED THAT THE SIDEGATE VALVE ACTUATOR DID NOT PROPERLY SHUT THE VALVE AS A RESULT OF THE ACTUATOR CONTROLS MALFUNCTIONING DUE TO THE WATER EXPOSURE IN THE CONTROL ROOM. SINCE THE INCIDENT ALL AFFECTED CONTROL SYSTEMS HAVE BEEN REPLACED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220029 | 37246 | 2022-03-10 17:45 | SUPPLEMENTAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2022-02-13 16:15 | 2022 | CENTRAL | NO | 32.5073 | -87.4283 | 1328835 | 2022-02-13 17:33 | 1328958 | NATURAL GAS |  | 166880 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-13 17:41 | 2022-08-31 17:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-02-13 17:15 | YES | 2022-02-13 16:15 | ALLOWED TO BURN OUT |  | 166880 | NO | VALVE CLOSURE |  | 2022-02-13 17:26 | VALVE CLOSURE |  | 2022-02-13 17:41 | 0 | 2022-02-13 16:31 | 2022-02-13 16:52 | ONSHORE | AL | 36786 | Not Within a Municipality | PERRY | MILEPOST | 155.755 | SOUTH MAIN LINE | GALLION TO SELMA | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 38 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 18 | NO | 0.312 | 52000 | API-5L | FLASH WELDED |  | A O SMITH | COAL TAR |  | YES | [26 empty] | 1951 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 83 | 56 |  | CLASS 1 LOCATION | NO |  | 430 |  | NO | NO |  |  | NO |  |  | 25000 | 25000 | 0 | 0 | 846082 | 846082 | 247901 | 247901 | 15000 | 15000 | 131805 | 131805 | SPECIMEN TRANSPORT, LABORATORY COST, INVESTIGATION COST; | 5.07 | 1265788 | 740311.6845160703863746910299003322259136 | 1265788 | 0 | 0 | 0 | 0 | NO |  |  |  | 1169 | 305000 | 1200 | 192.619(C) |  | 1975-06-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 43671 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DEEMED THE INCIDENT INDEPENDENT OF CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | HARD SPOT | [6 empty] | YES | [8 empty] | 1180 | [54 empty] | YES | YES |  |  | YES |  |  |  | 2014 | FREE SWIMMING | HARD SPOTS |  |  |  | 2014 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2014 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2003 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | WM. MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253509 | WILLIAM PICKARD | billy_pickard@kindermorgan.com | 2058412217 | JAIME HERNANDEZ | DIRECTOR ENGR COMPLIANCE CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON FEBRUARY 13, 2022, SOUTHERN NATURAL GAS COMPANY, LLC (SNG) 18-INCH SOUTH MAIN LINE EXPERIENCED AN IN-SERVICE FAILURE RESULTING IN A PIPELINE RUPTURE WITH FIRE. THE PRELIMINARY TIMELINE OF EVENTS IS AS FOLLOWS: 16:15-HOURS, AN UNDESIRED RELEASE OF NATURAL GAS OCCURRED ON THE SNG 18-INCH SOUTH MAIN LINE. 16:20-HOURS, PERRY COUNTY SHERRIFF ARRIVED ON SCENE, BLOCKED A LOCAL ROAD AND INSTRUCTED ARRIVING DEPUTIES TO SECURE THE AREA. 16:31-HOURS, A CITIZEN CALLED SNG GAS CONTROL AND REPORTED A FIRE NEAR THE 18-INCH SOUTH MAIN LINE ROW. 16:33-HOURS, SNG GAS CONTROL RECEIVED A CALL FROM ANOTHER CITIZEN REGARDING THE FIRE. 16:34-HOURS, SNG GAS CONTROL NOTIFIED SNG OPERATIONS OF A PRESSURE DROP AT THE GALLION COMPRESSOR STATION AND SELMA COMPRESSOR STATION AND A POTENTIAL RUPTURE NEAR THE 18-INCH SOUTH MAIN LINE SYSTEM. 16:52-HOURS, SNG OPERATIONS LOCATED THE PIPELINE RUPTURE ON THE SOUTH MAIN LINE SYSTEM AT MP 155.755. 17:15-HOURS, SNG EMERGENCY RESPONSE LINE+ (ERL+) CALL NOTIFICATIONS INITIATED PER SNG PROCEDURES TO COORDINATE THE EMERGENCY RESPONSE. 17:26-HOURS, SNG OPERATOR #1 CLOSED UPSTREAM GATE VALVE #18 LOCATED AT, MP 150.783. 17:33-HOURS, SNG INITIATED CALL TO NRC. (REPORT NUMBER 1328835) 17:39-HOURS, SNG OPERATOR #2 CLOSED CROSSOVER VALVE 155 LOCATED AT, MP 155.000. 17:41-HOURS, SNG OPERATOR #3 CLOSED DOWNSTREAM GATE VALVE #19 LOCATED AT, MP 159.054, COMPLETELY ISOLATING THE SOUTH MAIN LINE SYSTEM. 22:01-HOURS, THE FIRE WAS EXTINGUISHED. SNG'S INVESTIGATION BEGAN ON FEBRUARY 14, 2022 AND RECEIVED A CORRECTION ACTION ORDER (CAO) CPF NO. 2-2022-007-CAO FROM PHMSA ON FEBRUARY 18, 2022. SNG SENT THE FAILED SPECIMEN TO A THIRD-PARTY METALLURGICAL LABORATORY. THE METALLURGICAL REPORT WAS COMPLETED ON APRIL 4, 2022 AND CONCLUDED THAT THE SNG 18-INCH SOUTH MAIN LINE RUPTURED LIKELY FROM A HYDROGEN STRESS CRACK INITIATED AT THE PIPE OD IN A LOCALIZED HARD SPOT. IN ORDER TO PREVENT REOCCURRENCE SNG AND ITS ILI VENDOR PERFORMED A FOOT-BY-FOOT MANUAL ANALYSIS OF ALL AVAILABLE RESIDUAL DATA SETS ON THE 18-INCH LINE TO IDENTIFY SIMILAR CONDITIONS TO THOSE IN THE FAILED JOINT. SNG REMEDIATED 21 FEATURES WITH SIMILAR CHARACTERISTICS TO THE ANOMALY IN THE FAILED JOINT. IN ADDITION TO THE REMEDIATION PROJECT SNG WILL IMPLEMENT TESTING, AND INTEGRITY VERIFICATION MEASURES, TO PROMOTE THE ONGOING SAFE OPERATION OF THE PIPELINE CONSIDERING THE RESULTS OF THE ANALYSES, INSPECTIONS, EVALUATIONS, AND CORRECTIVE MEASURES UNDERTAKEN PURSUANT TO THE CAO. THE PIPELINE WAS RETURNED TO SERVICE ON AUGUST 31, 2022, FOLLOWING THE REQUIREMENTS FROM THE CAO. SNG SUBMITTED THE FINAL QUARTERLY REPORT ON SEPTEMBER 29, 2022 AND REQUESTED CAO CLOSURE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220030 | 36463 | 2022-03-14 11:11 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2022-02-25 12:00 | 2022 | MOUNTAIN | YES | 42.7619 | -112.8347 | 1329717 | 2022-02-25 13:28 | 1329774 | NATURAL GAS |  | 2.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | IT WAS DETERMINED THAT THE PIPELINE COULD REMAIN OPERATING IN A SAFE MANNER |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-02-25 12:20 | 2022-02-25 12:40 | ONSHORE | ID | 83211 | AMERICAN FALLS | POWER |  |  | AMERICAN FALLS METER STATION | NORTHWEST PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 4.5 | NO | 0.237 | 35000 | GRADE B | SEAMLESS |  | UNKNOWN | PAINT |  | YES | [26 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | OTHER | A 1/4" VALVE WAS 25% OPEN | [5 empty] | CLASS 1 LOCATION | NO |  | 483 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 12 | 12 | 530000 | 530000 | 12000 | 12000 | 0 | 0 |  | 4.55 | 542012 | 239117.5155352042979202657807308970099668 | 542012 | 1 | 0 | 0 | 0 | NO |  |  |  | 150 | 2447 | 850 | 192.619(A)(2) |  | 1973-11-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DUE TO A VEHICLE HITTING THE PIPING AND WASN'T RELATED TO ANY CONTROLLERS OR ACCESSORIES WITHIN THE CONTROL ROOM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | NO | [5 empty] | NO |  | YES | SMALL TRUCK | ROADWAY | 150 | YES |  |  |  | YES | DIRT BERM ON THE OUTSIDE OF THE FACILITY | [233 empty] | TAYLER K JENSEN | PIPELINE SAFETY ENGINEER | tayler.jensen@williams.com | 2813828869 |  |  |  |  | TYSON GREEN | PIPELINE SAFETY MANAGER | 346-439-9090 | tyson.green@williams.com | ON FEBRUARY 25TH, 2022 AN ERRANT VEHICLE RAN INTO SOME ABOVE-GROUND PIPING AT NORTHWEST PIPELINE'S AMERICAN FALLS METER STATION LOCATED IN IDAHO. OPERATIONS WAS NOTIFIED OF THE INCIDENT BY PIPELINE CONTROLLERS. OPERATIONS TRAVELLED TO THE SITE AND IDENTIFIED THAT THERE WERE NO PIPELINE RUPTURES OR CATASTROPHIC FAILURES ASSOCIATED WITH THE INCIDENT. A LEAKING 1/4" VALVE WAS IDENTIFIED. THOUGH THERE WERE NO PIPING FAILURES, THE VEHICLE THAT RAN INTO THE FACILITY WAS STOPPED ON TOP OF SOME ABOVE-GROUND PIPING. OPERATIONS DEEMED IT NECESSARY TO BYPASS THIS PIPING TO AVOID INTERRUPTION OF SERVICE UNTIL THE TRUCK COULD BE REMOVED AND THE TOTAL SCOPE OF DAMAGE COULD BE IDENTIFIED AND PROPERLY ADDRESSED. A BYPASS AROUND THE AFFECTED PIPING WAS QUICKLY PUT IN PLACE UTILIZING APPROPRIATELY TESTED HIGH-PRESSURE HOSING AND ASSOCIATED COMPONENTS. THROUGH FURTHER INVESTIGATION, IT WAS DETERMINED THAT THE PIPING THAT HAD BEEN STRUCK BY THE VEHICLE SHOULD BE REPLACED WITH SIMILAR AND NEW PIPING COMPONENTS. THE DRIVER OF THE VEHICLE WAS TAKEN TO THE HOSPITAL BY EMERGENCY RESPONDERS AND LATER RELEASED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220031 | 37337 | 2022-03-15 08:39 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2022-02-16 17:00 | 2022 | CENTRAL | NO | 30.038 | -92.0089 | 1329059 | 2022-02-16 18:15 | 1329122 | NATURAL GAS |  | 16935 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A RELIEF VALVE WAS VENTING AND MANUALLY SECURED. |  |  |  | YES | OPERATOR | 2022-02-16 18:15 | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-16 17:00 | OPERATIONAL CONTROL | RELIEF VALVE ISOLATION WAS MANUALLY SHUT. |  | 0 | 2022-02-16 16:28 | 2022-02-16 16:50 | ONSHORE | LA | 70510 | ABBEVILLE | VERMILLION | NOT APPLICABLE |  | EAST LATERAL 200 | VS 1204 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE RELEASE. | CLASS 1 LOCATION | NO |  | 480 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 105505 | 105505 | 0 | 0 | 1350 | 1350 | 0 | 0 |  | 6.23 | 106855 | 69822.2709537564224200996677740863787375 | 106855 | 0 | 0 | 0 | 0 | NO |  |  |  | 825 | 4500 | 839 | 192.619(A)(1) |  | 1967-06-19 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | NO |  | MANUAL |  | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | NO | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS NOT RELATED TO CONTROL ROOM ACTIVITY. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THIS CATEGORY WAS CHOSEN SINCE IT FITS UNDER "RELIEF VALVE" CATEGORY IN AN EFFORT TO AVOID SELECTING G8. THE EAST LATERAL, ESPECIALLY AT MLV 1204, IS PROVIDING PRESSURE CONTROL USING RELIEF VALVES. THIS CONFIGURATION DOES NOT ALLOW A CONTROLLED PRESSURE REDUCTION, BUT INSTEAD AN IMMEDIATE PRESSURE REDUCTION BY A GAS RELEASE. THIS CONFIGURATION ALSO DOES NOT ALLOW FOR A SET POINT ABOVE THE LOWEST MAOP OF THE LINE WHERE IT IS INSTALLED OR ADJACENT COMMON LINE | [15 empty] | YES | NO OTHER SUB-CAUSE APPLIES. | [161 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304.539.9311 |  |  |  |  | PAUL SHAFFER | MANAGER | 304.550.4866 | paul_shaffer@tcenergy.com | ON THE EVENING OF WEDNESDAY FEBRUARY 16TH, 2022 A PIPELINE RELIEF VALVE, ON COLUMBIA GULF TRANSMISSION'S EAST LATERAL 200 (EL200) LINE, AT VALVE SETTING VS-1204, FAILED TO THE OPEN POSITION RELEASING (AT THE TIME) AN UNKNOWN VOLUME OF NATURAL GAS. THE VALVE SETTING IS LOCATED NEAR 2037 DURPHY ROAD, IN ABBEVILLE LOUISIANA. THE ODOR OF GAS WAS REPORTED BY A PRIVATE CITIZEN; LOCAL EMERGENCY SERVICES WERE DISPATCHED AND CLOSED THE NEARBY ROAD. THE CAUSE OF THE RELIEF VALVE MALFUNCTION IS UNDER INVESTIGATION; HOWEVER, THE MAOP WAS NOT EXCEEDED AS INDICATED BY SCADA TRANSMITTER DATA. THE PRESSURE AT THE TIME OF THE EVENT WAS CHECKED ON SCADA. A LOSS OF COMMUNICATIONS WITH SCADA TRANSMITTER WAS NOTED BY THE GAS CONTROLLER, THEN UPON RESTORING COMMUNICATIONS, A DROP IN PIPELINE PRESSURE WAS OBSERVED. AT 4:19 PM CENTRAL TIME, WHEN TRANSMITTER COMMS WAS LOST, THE PRESSURE ON EL200 WAS 825 PSIG; THE PRESSURE WHEN COMMS RESUMED AT 4:54 PM CENTRAL WAS 816 PSIG. EL200 FROM RAYNE COMPRESSOR STATION TO VS-1204 HAS AN MAOP OF 973 PSIG. HOWEVER, EL200 IS CURRENTLY IN COMMON WITH EAST LATERAL 300 LINE, RESULTING IN AN OVERRIDE MAOP OF 839 PSIG FOR THE LIMITING COMPONENT IN THIS MODE OF OPERATION. EL200 RELIEF VALVE WAS FOUND VENTING INTO ATMOSPHERE AND WAS MANUALLY SECURED. THE CALCULATED AMOUNT OF RELEASED MATERIAL INTO ATMOSPHERE WAS 16,935 MCF, HENCE MEETING THE REPORTING THRESHOLD. MONITORING CENTER'S PERSONNEL CALLED LOUISIANA STATE POLICE TO REPORT THE RELEASE OF MATERIAL INTO ATMOSPHERE. THE EAST LATERAL, ESPECIALLY AT MLV 1204, IS PROVIDING PRESSURE CONTROL USING RELIEF VALVES. THIS CONFIGURATION DOES NOT ALLOW A CONTROLLED PRESSURE REDUCTION, BUT INSTEAD AN IMMEDIATE PRESSURE REDUCTION BY A GAS RELEASE. THIS CONFIGURATION ALSO DOES NOT ALLOW FOR A SET POINT ABOVE THE LOWEST MAOP OF THE LINE WHERE IT IS INSTALLED OR ADJACENT 'COMMON' LINE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220032 | 36467 | 2022-03-16 13:24 | ORIGINAL FINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2022-02-14 15:30 | 2022 | EASTERN | NO | 41.4009 | -80.2823 | 1328898 | 2022-02-14 17:11 | 1329033 | NATURAL GAS |  | 3142 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ISOLATED PRIMARY REGULATOR AND OPERATED STATION THROUGH SECONDARY REGULATOR |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-02-14 15:02 | 2022-02-14 15:02 | ONSHORE | PA | 16125 | OTTER CREEK | MERCER | NOT APPLICABLE |  | OCM-2534 (KITCH RD STATION) | PRIMARY REGULATOR (RG1) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1989 | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | REGULATOR | OTHER | [8 empty] | RELIEF VALVE RELEASE | CLASS 1 LOCATION | NO |  | 111 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 1359 | 1359 | 546 | 546 | 1049 | 1049 | 0 | 0 |  | 0.4324 | 2954 | 1595.355570428668935099667774086378737542 | 2954 | 0 | 0 | 0 | 0 | NO |  |  |  | 57 | 6288 | 60 | 192.619(A)(2) |  | 1982-05-14 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | DEBRIS | [161 empty] | STEVEN MONNIE | ENGINEER III | monnies@natfuel.com | (814) 871-8204 |  | WARREN BOWMAN | bowmanw@natfuel.com | (724) 962-6284 | CRAIG FERRIS | SUPERINTENDENT | (716) 827-2305 | ferrisc@natfuel.com | NATIONAL FUEL GAS SUPPLY CORPORATION ("NATIONAL FUEL") IS REPORTING THIS NATURAL GAS INCIDENT AS A RESULT OF AN UNINTENTIONAL RELEASE OF NATURAL GAS ESTIMATED AT GREATER THAN THREE (3) MILLION CUBIC FEET, WHICH OCCURRED AT A REGULATOR STATION IN OTTER CREEK TOWNSHIP, MERCER COUNTY, PA. ON MONDAY, FEBRUARY 14, 2022, AT APPROXIMATELY 3:02 PM, NATIONAL FUEL DISCOVERED A VENTING RELIEF VALVE AT STATION OCM-2534 (KITCH RD). AT APPROXIMATELY 3:50 PM, THE PRIMARY REGULATOR WAS ISOLATED WHICH STOPPED THE UNINTENTIONAL RELEASE OF GAS FROM THE RELIEF VALVE. AT APPROXIMATELY 4:23 PM THE PRESSURE RECORDING CHART WAS REMOVED FOR ANALYSIS. AT 5:11 PM, NATIONAL FUEL NOTIFIED THE NRC AFTER REVIEW OF THE PRESSURE CHART INDICATED THE THREE (3) MILLION CUBIC FEET REPORTING THRESHOLD COULD POTENTIALLY BE EXCEEDED. THE FINAL GAS LOSS AMOUNT WAS DETERMINED AFTER A COMPREHENSIVE REVIEW AND USING CONSERVATIVE CALCULATIONS. THE PROBABLE CAUSE OF THE INCIDENT WAS EQUIPMENT FAILURE OF A PRESSURE REGULATOR CAUSED BY DEBRIS WHICH PREVENTED THE REGULATOR FROM SEATING AND THE RELIEF VALVE TO VENT AS DESIGNED. THERE WERE NO INJURIES, PROPERTY DAMAGE, OR AFFECTED PUBLIC/WILDLIFE AS A RESULT OF THIS EVENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220033 | 37047 | 2022-03-16 14:05 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-02-23 14:22 | 2022 | EASTERN | NO | 35.1851 | -78.6777 | 1329562 | 2022-02-23 16:14 | 1329641 | NATURAL GAS |  | 999 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A BYPASS WAS MADE ON THE PIPE. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | A BYPASS WAS RAN. |  | OPERATIONAL CONTROL | A BYPASS WAS RAN. |  | 0 | 2022-02-23 14:22 | 2022-02-23 15:05 | ONSHORE | NC | 28344 | GODWIN | CUMBERLAND | NOT APPLICABLE |  | LINE 5 | 1404352 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.188 | 42000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.3 | 0.3 | [7 empty] | CLASS 1 LOCATION | NO |  | 200 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 3996 | 3996 | 327967 | 327967 | 0 | 0 | 0 | 0 |  | 4 | 331963 | 147308.4396273665808975049833887043189369 | 331963 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 13000 | 695 | 192.619(A)(2) |  | 1958-12-31 | YES | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 52040 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY CUT THE TRANSMISSION LINE AND NOTIFIED US OF THE DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | AGRICULTURE | NO |  |  | CONTRACT LOCATOR | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR DAMAGED A 10" STEEL TRANSMISSION LINE WITH A TRENCHER WHILE PERFORMING AGRICULTURE WORK. THE RELEASE WAS FROM A MECHANICAL PUNCTURE. THE SIZE OF THE MECHANICAL PUNCTURE WAS 0.25 X 0.25 BUT THE PORTAL WILL NOT ALLOW TWO DECIMAL PLACES. CONTRACTOR FAILED TO NOTIFY THE ONE-CALL CENTER.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220034 | 37300 | 2022-03-23 20:33 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-02-21 11:25 | 2022 | CENTRAL | NO | 31.9642 | -93.9676 | 1329420 | 2022-02-22 00:28 | 1329583 | NATURAL GAS |  | 37070 | 2100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-21 11:34 | 2022-07-06 10:40 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-02-21 11:43 | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-21 11:27 | VALVE CLOSURE |  | 2022-02-21 11:34 | 0 | 2022-02-21 11:25 | 2022-02-22 01:50 | ONSHORE | LA | 71049 | Not Within a Municipality | DE SOTO | MILEPOST | 247.628 | TEXAS EASTERN LINE 11 | JOQN-REDR /11 VS-03 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.312 | 52000 | API-5L | FLASH WELDED |  | A.O. SMITH | COAL TAR |  | NO | [26 empty] | 1953 | 1953 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 1324 | 60 |  | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 9450 | 9450 | 166815 | 166815 | 5473114 | 5473114 | 2644000 | 2644000 | 0 | 0 |  | 4.5 | 8293379 | 3694583.82002909996210268438538205980066 | 8293379 | 0 | 0 | 0 | 0 | NO |  |  |  | 901 | 0 | 973 | 192.619(A)(1) |  | 2015-05-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | REMOTELY CONTROLLED | 89500 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 7 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | YES |  |  | YES | PRIVATE LANDOWNER | YES | [6 empty] | CONTRACTOR | UNKNOWN/OTHER | NATURAL GAS | YES | 210333944 | LOUISIANA 811. | FACILITY OWNER | YES | YES | NO |  | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | MICHAEL MCGRATH |  | michael.mcgrath@enbridge.com | 6128056542 |  |  |  |  | NATHAN ATANU |  | 17136275008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 11:25 P.M. CT ON FEBRUARY 21, 2021, TETLP'S 24-INCH DIAMETER LINE 11 TRANSPORTING NATURAL GAS FROM JOAQUIN COMPRESSOR STATION TO RED RIVER VALVE SITE RUPTURED NEAR M.P. 247.268 IN DE SOTO PARISH LOUISIANA, APPROXIMATELY 2.7 MILES DOWNSTREAM OF THE JOAQUIN COMPRESSOR STATION. THE RUPTURE DID NOT IGNITE. THE LINE HAD MINIMAL FLOW AT THE TIME OF THE INCIDENT (APPROXIMATELY 0.5 MSCF/D). AT 11:25 P.M. CT GAS CONTROL IDENTIFIED A RAPIDLY DECREASING DISCHARGE PRESSURE AT THE JOAQUIN COMPRESSOR STATION. AT 11:27 P.M. CT GAS CONTROL CLOSED THE JOAQUIN COMPRESSOR STATION VALVE. AT 11:34 P.M. GAS CONTROL CLOSES VALVE RCV-11-327 ISOLATING THE PIPELINE SEGMENT. TETLP EMPLOYEES WERE DISPATCHED TO SEVERAL OTHER VALVES SITES TO FURTHER MITIGATE THE LINE BLOWDOWN LOCATED AT THE SABINE RIVER (11-270) AND THE MANSFIELD METER STATION (11-283). TETLP INITIATED THE NOTIFICATION TO THE NRC AT 12:28 A.M. CT ON FEBRUARY 22, 2022, AFTER RECEIVING CONFIRMED DISCOVERY OF THE PIPELINE FAILURE AND GATHERING THE INITIAL INFORMATION TO MAKE THE NRC NOTIFICATION. THE APPARENT CAUSE OF THE INCIDENT IS UNDER INVESTIGATION AND WILL BE UPDATED ONCE THE INVESTIGATION IS COMPLETE. UPDATED NOVEMBER 2, 2022. THE APPARENT CAUSE OF THE FAILURE WAS DETERMINED TO BE 2ND PARTY EXCAVATION DAMAGE CAUSED DURING AN INTEGRITY REPAIR IN THE AREA COMPLETED IN THE FALL OF THE PREVIOUS YEAR. UPDATED PART G APPARENT CAUSE, AND UPDATED ESTIMATED DAMAGE COST IN PART D.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220036 | 36811 | 2022-03-28 12:47 | SUPPLEMENTAL FINAL | 6660 | GREAT LAKES GAS TRANSMISSION LIMITED PARTNERSHIP | 700 LOUISIANA STREET | HOUSTON | TX | 77002 | 2022-03-06 13:03 | 2022 | EASTERN | NO | 46.4397 | -89.8374 | 1330379 | 2022-03-08 15:21 | 1330544 | NATURAL GAS |  | 40700 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-06 14:14 | 2022-03-07 18:00 |  | NO |  |  | NO | [11 empty] | 0 | 2022-03-06 12:37 | 2022-03-06 13:50 | ONSHORE | MI | 49968 | WAKEFIELD | GOGEBIC | NOT APPLICABLE |  | GREAT LAKES GAS TRANSMISSION LIMITED PARTNERSHIP | WAKEFIELD CS-7 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY SHUT DOWN (ESD) | CLASS 1 LOCATION | NO |  | 776 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 140822 | 140822 | 1000 | 1000 | 0 | 0 | 0 | 0 |  | 3.46 | 141822 | 92840.978976450555305647840531561461794 | 141822 | 0 | 0 | 0 | 0 | NO |  |  |  | 744 | 0 | 974 | 192.619(A)(1) |  | 1968-03-24 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR IDENTIFIED THE ALARM AND FOLLOW THE PROCEDURES TO INITIATE AN INVESTIGATION. FIELD PERSONNEL WAS DISPATCHED TO THE SITE AND RESPONDED TO THE LOCATION OF THE ALARM. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | ICE ACCUMULATION CONTRIBUTED TO THE VALVE FAILURE | [18 empty] | YES | [166 empty] | ROBERTA PRIMERA | COMPLIANCE SPECIALIST | roberta_primera@tcenergy.com | 2485617803 |  | ROBERTA PRIMERA | roberta_primera@tcenergy.com | 2485617803 | ROGER STREET | INTERIM MANAGER REGULATORY COMPLIANCE | 8325702966 | roger_street@tcenergy.com | ON MARCH 6TH AT 12:37 EST, GLGT GAS CONTROL RECEIVED AN EMERGENCY SHUTDOWN SYSTEM (ESD) VALVE OUT OF POSITION ALARM, AT WAKEFIELD COMPRESSOR STATION LOCATED AT 400 GREAT LAKES ROAD, WAKEFIELD, MI 49968, (46.43969, -89.83737). WHEN THE ALARM WAS DETECTED, A TECHNICIAN WAS DISPATCHED TO THE COMPRESSOR STATION TO INVESTIGATE. UPON ARRIVAL AT THE SITE AT 13:50 EST, THE TECHNICIAN DISCOVERED NATURAL GAS BEING RELEASED TO THE ATMOSPHERE THROUGH THE EIGHT-INCH VENT STACK. IMMEDIATE ACTION WAS TAKEN BY VERIFYING NO EMERGENCY EXISTED AND CLOSED THE VALVE, WHICH ENDED THE RELEASE AT 14:14 EST. UNINTENTIONAL GAS LOSS WAS CALCULATED TO APPROXIMATELY 40.7 MILLION CUBIC FEET (MMCF). INVESTIGATION INDICATED THAT THE SYSTEM VENT VALVE (Y-01-DE) FAILED DUE TO A SOLENOID FAILURE THAT HOLDS THE ESD VALVE CLOSED WHICH CONTRIBUTED TO THE GAS LOSS. ADDITIONALLY, AN AUTOMATIC ISOLATION VALVE (Y-02-D) FAILED TO COMPLETELY CLOSE DUE TO ICE ACCUMULATION FREEZING THE VALVE IN THE OPEN POSITION RESULTING IN THE CONTINUING RELEASE OF GAS TO THE ATMOSPHERE THROUGH THE 8-INCH VENT STACK. BOTH SOLENOIDS WERE REPLACED ON MARCH 7TH, 2022. THE ESD SYSTEM HAS BEEN INSPECTED AND TESTED ACCORDING TO PROCEDURES AND OPERATED CORRECTLY. THE SYSTEM HAS BEEN PLACED BACK INTO FULL-SERVICE MARCH 7TH AT 18:00 EST.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220037 | 36771 | 2022-03-28 15:07 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2022-02-26 23:48 | 2022 | CENTRAL | NO | 34.9942 | -95.0538 | 1329828 | 2022-02-27 10:48 | 1329933 | NATURAL GAS |  | 4162 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | COMPRESSOR UNIT 4 WAS ISOLATED, AND NORMAL OPERATIONS CONTINUED THROUGH. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-02-26 23:02 | 2022-02-26 23:48 | ONSHORE | OK | 74563 | Not Within a Municipality | LATIMER | NOT APPLICABLE |  | R-913 / RED OAK COMPRESSOR STATION | COMPRESSOR UNIT # 4 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2002 | 2002 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF WENT OFF PRIOR TO SETPOINT. | CLASS 1 LOCATION | NO |  | 368 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 17636 | 17636 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4.2375 | 17636 | 11571.7940199335548172757475083056478405 | 17636 | 0 | 0 | 0 | 0 | NO |  |  |  | 896 | 31.32 | 960 | 192.619(A)(1) |  | 2008-04-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE RELIEVED PRIOR TO SETPOINT, NO OPERATOR OR CONTROLLER WAS DIRECTLY INVOLVED WITH THE RELIEF RELIEVING PRIOR TO SETPOINT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [13 empty] | YES | [164 empty] | YES | [12 empty] | BRANDON LEE | REGULATORY COMPLIANCE SPECIALIST II | brandon.lee@oneok.com | 918-613-1492 |  | BRANDON LEE | brandon.lee@oneok.com | 918-613-1492 | BILL BROMLEY | VP NATURAL GAS PIPELINE OPERATIONS | 9185887615 | bill.bromley@oneok.com | APPROXIMATELY 11:02PM ON FEBRUARY 26, 2022 GAS CONTROL WAS NOTIFIED BY NEARBY LANDOWNER OF LOUD NOISE NEAR RED OAK STATION. THE OGT EMPLOYEE RESPONDED AND WAS ONSITE AT 11:48PM. THE OGT EMPLOYEE HAD GAS CONTROL SHUT COMPRESSOR UNIT #4 DOWN UPON ARRIVAL AND DETERMINATION OF RELIEF VALVE VENTING. THE COMPRESSOR UNIT 4 WAS LOCKED OUT OF SERVICE UNTIL TESTING COULD BE PERFORMED. RELIEF VALVE WAS REMOVED ON MARCH 4, 2022 AND DEBRIS WAS NOTED IN THE VALVE BELOW, AND DEBRIS WAS REMOVED AS PART OF THE INSPECTION. RELIEF VALVE WAS FOUND TO BE IN GOOD REPAIR, AND WAS RE-TESTED TO VERIFY THE FUNCTIONALITY OF THE RELIEF WAS OPERATING PROPERLY, AND PLACED BACK INTO A READY FOR SERVICE STATUS. SUPPLEMENTAL REPORT WAS MADE TO CORRECT THE DATE OF THE NRC NOTIFICATION DATE. THE DATE OF NRC NOTIFICATION WAS 02/27/2022 NOT 03/27/2022. 06/16/2022--SUPPLEMENTAL REPORT WAS MADE TO UPDATE THE CAUSE OF THE INCIDENT DUE TO SUPPLEMENTAL INFORMATION RECEIVED FROM A PULSATION STUDY- VIBRATION WAS THE ROOT CAUSE OF THE INCIDENT BY CAUSING THE SETPOINT TO DRIFT BELOW THE SETPOINT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220038 | 36620 | 2022-03-28 15:18 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-02-27 06:20 | 2022 | CENTRAL | NO | 33.1092 | -98.4117 | 1329823 | 2022-02-27 08:53 | 1329940 | NATURAL GAS |  | 4375.3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-27 06:20 | VALVE CLOSURE |  | 2022-02-27 07:09 | 0 | 2022-02-27 06:20 | 2022-02-27 07:05 | ONSHORE | TX | 76427 | BRYSON | JACK | NOT APPLICABLE |  | BRYSON TAP - BRYSON COMPRESSOR STATION | 9166 BRYSON TAP_ BRYSON COMP STATION 16-INCH | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REGULATOR/CONTROL VALVE | [38 empty] | 2013 | 2013 | CARBON STEEL |  | OTHER | [8 empty] | RELEASE FROM STATION BLOWDOWN | CLASS 1 LOCATION | NO |  | 384 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 20258 | 20258 | 500 | 500 | 0 | 0 | 0 | 0 |  | 4.63 | 20758 | 13512.7901526771048953488372093023255814 | 20758 | 0 | 0 | 0 | 0 | NO |  |  |  | 679 | 0 | 944 | 192.619(A)(1) |  | 1974-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 50 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS DID NOT AFFECT THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | YES | [33 empty] | YES | VERSA VALVE FAILED TO SHIFT | [123 empty] | YES | [37 empty] | ANGELA MORGAN | LEAD SPECIALIST | angela.morgan@energytransfer.com | 903-243-6541 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON 2/27/22 AT 6:20, ENERGY TRANSFER GAS CONTROL CALLED ENERGY TRANSFER (ETC) OPERATIONS TECHNICIAN TO NOTIFY HIM OF A STATION ESD AT THE BRYSON FACILITY. ETC OPERATIONS TECHNICIAN ARRIVED AT THE BRYSON FACILITY AT 7:05 AND FOUND THE STATION BLOWDOWN ACTIVELY RELEASING NATURAL GAS TO ATMOSPHERE. ETC OPERATIONS TECHNICIAN IDENTIFIED THE VALVE THAT FAILED TO CLOSE DURING THE ESD AND AT 7:09 HE MANUALLY CLOSED THE VALVE TO STOP THE RELEASE. THE QUANTITY OF GAS RELEASED WAS CALCULATED AND DETERMINED TO BE REPORTABLE AT 08:20. INITIAL NOTIFICATION WAS MADE TO THE NRC (REPORT # 1329823) AT 8:50 ON 2/27/22. THE 48-HOUR UPDATE WAS MADE TO NRC (REPORT # 1329940) AT 8:41 ON 3/01/22. FURTHER INVESTIGATION INDICATED THE VERSA VALVE ON THE CONTROL VALVE FAILED TO OPERATE, THEREFORE THE CONTROL VALVE FAILED TO CLOSE AND ALLOWED THE RELEASE OF NATURAL GAS FROM 9166 BRYSON TAP - BRYSON COMPRESSOR STATION 16-INCH PIPELINE. THE REASON FOR THE ESD WAS LOSS OF INSTRUMENT AIR PRESSURE. THE 9166 BRYSON TAP - BRYSON COMPRESSOR STATION 16-INCH PIPELINE WAS IDLE AT THE TIME OF THE ESD. THE PIPELINE WAS NOT SHUTDOWN AS IT WAS NOT CURRENTLY NEEDED, HOWEVER IT WAS AVAILABLE TO RETURN TO SERVICE WHEN NEEDED, AT 11:50 ON 2/27/22.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220039 | 37024 | 2022-03-29 14:25 | SUPPLEMENTAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-02-27 16:30 | 2022 | CENTRAL | NO | 28.2897 | -93.3007 | 1329873 | 2022-02-28 11:13 | 1329959 | NATURAL GAS |  | 33613 | 60122 | 3.83 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-02-27 17:10 | 2022-08-12 08:45 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-02-27 17:40 | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-27 17:00 | VALVE CLOSURE |  | 2022-02-27 17:10 | 0 | 2022-02-28 10:15 | 2022-02-27 17:00 | OFFSHORE | [6 empty] | STINGRAY PIPELINE | STINGRAY 30-IN LINE 1004C-100 | [20 empty] | 190 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 550 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 0.568 | 60000 | API 5L X-60 | DSAW |  | US STEEL | OTHER | CONCRETE | UNKNOWN | [26 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 262132 | 262132 | 146553 | 146553 | 1314087 | 1314087 | 821369 | 821369 | 0 | 0 |  | 4.36 | 2544141 | 1153884.19069511738286191362126245847176 | 2544141 | 0 | 0 | 0 | 0 | NO |  |  |  | 830 | 597.24 | 1200 | 192.619(A)(1) |  | 1975-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 318991 | YES | [7 empty] | YES |  |  |  |  | YES | LAUNCHER IS SUBSEA | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK AND TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES |  |  |  | YES |  | YES |  |  |  | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PEGGY WEST | SR. REGULATORY ANALYST | peggy.west@energytransfer.com | 409-202-3088 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | AT 4:30 ON 02/27/2022, ET PERSONNEL WERE NOTIFIED BY A PRODUCER THAT THEY OBSERVED A SHEEN NEAR ETS 30-INCH PIPELINE LOCATED AT WC 550 BLOCK. A CALL WAS PLACED TO THE NRC BY THE PRODUCER (NRC #1329846). ET PERSONNEL ARRIVED ONSITE AND CLOSED THE UPSTREAM VALVE AT 5:00 PM. THE DOWNSTREAM VALVES WERE CLOSED AT 5:10 PM ISOLATING THE PIPELINE. AN OVERFLIGHT WAS ACCOMPLISHED ON 02/28/22 AT 10:15 AM. ONCE THE LINE WAS CONFIRMED TO BE ETCS PIPELINE, ETC PLACED A CALL TO THE NRC (NRC# 1329873) AND THE 48 HOUR NOTIFICATION WAS MADE ON 03/01/2022 AT 1304. THE REPAIRS ON THIS 30-INCH LINE ARE STILL PENDING DUE TO THE DEPRESSURIZATION PROCESS. THE DEPRESSURIZATION STARTED ON 3/1/22 UTILIZING A DEPRESSURIZATION VESSEL AND ARE CURRENTLY STILL IN THE PROCESS OF DEPRESSURIZING THE 30-INCH LINE TO A SAFE WORKING PRESSURE FOR THE DIVE COMPANY SO THEY CAN BEGIN REPAIR. SINCE THE BEGINNING OF THE DEPRESSURIZATION PROCESS, THE DEPRESSURIZATION VESSEL HAS HAD TO DEAL WITH INTERMITTENT HIGH SEAS AND STRONG WIND CONDITIONS MAKING THE DEPRESSURIZATION OPERATIONS UNABLE TO SAFELY PROGRESS. THE CREWS HAVE HAD TO RUN INTO PROTECTED WATERS SEVERAL TIMES. REPAIRS ON THE LINE WILL COMMENCE ONCE THE LINE HAS BEEN SAFELY DEPRESSURIZED. OPERATIONS WILL CONTINUE TO SCHEDULE OVERFLIGHTS FOR MONITORING AS WEATHER ALLOWS. ***07/13/22 UPDATE: POOR OFFSHORE WEATHER CONDITIONS AND LACK OF AVAILABILITY OF RESOURCES TO MOBILIZE HAVE PROLONGED IDENTIFYING AND REPAIRING THE LEAK. ON MAY 29, 2022, DSV ARRIVED ON LOCATION AND DURING DEPRESSURIZATION THE MAIN JET PUMP FAILED, DSV CONTINUED WITH A SMALLER BACK-UP SYSTEM UNTIL A TENDER(OPERATOR) ON THE DSV INJURED HIS ARM BY PLACING IT IN A PINCH POINT (ARM WAS BRUISED NOT BROKEN). DSV RETURNED TO DOCK TO OBTAIN NEW PUMPS AND RETURN TO THE SITE AND BEGAN DIVING OPERATIONS. ONCE THE DSV ARRIVED BACK ON LOCATION, THE CREW FOUND THE LEAK ON JUNE 2, 2022. IT WAS LOCATED ON A FIELD JOINT AT THE 5:30 POSITION (SMALL PINHOLE). ON JUNE 6, 2022, AN ERROR WAS MADE WHILE THE CONTRACT DIVERS WERE INSTALLING A LEAK CLAMP. THIS ERROR REQUIRED THE REMOVAL OF THE NEWLY INSTALLED CLAMP. DSV RETURNED TO DOCK TO PROCURE A REPLACEMENT CLAMP AND IS AWAITING THE AVAILABILITY OF ANOTHER DIVE VESSEL TO CONTINUE WITH THE REPAIR OPERATIONS. ET WILL CONTINUE TO MAKE OVERFLIGHTS UNTIL THE REPAIRS ARE COMPLETE. ***08/12/22 UPDATE: CLAMP WAS INSTALLED AND PRESSURE INTRODUCED TO THE 30-INCH LINE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220040 | 36756 | 2022-03-31 11:31 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-03-04 12:16 | 2022 | CENTRAL | NO | 29.7961 | -90.3203 | 1330236 | 2022-03-04 12:33 | 1330344 | NATURAL GAS |  | 64.6 | 805.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-04 14:09 | 2022-03-18 17:35 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-03-04 12:33 | YES | 2022-03-04 11:38 | ALLOWED TO BURN OUT |  | 64.6 | NO | VALVE CLOSURE |  | 2022-03-04 12:05 | VALVE CLOSURE |  | 2022-03-04 14:09 | 0 | 2022-03-04 09:27 | 2022-03-04 11:38 | ONSHORE | LA | 70070 | Not Within a Municipality | ST CHARLES | MILEPOST | 4.93 | TRANSCO | BAYOU COUBA LATERAL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | MARSH | 60 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | 0.322 | 35000 | API-5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | LONE STAR STEEL COMPANY | ASPHALT |  | YES | [26 empty] | 1961 | 1961 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 223 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 4389 | 4389 | 352 | 352 | 283000 | 283000 | 0 | 0 | 0 | 0 |  | 5.45 | 287741 | 127015.9834584974759441295681063122923588 | 287741 | 0 | 0 | 0 | 0 | NO |  |  |  | 411 | 3000 | 995 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 81312 | NO | YES |  |  |  |  | YES | TRAP MODIFICATIONS. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, BUT THE INVESTIGATION OF THE CONTROL ROOM AND/OR CONTROLLER ACTIONS HAS NOT YET BEEN COMPLETED BY THE OPERATOR (SUPPLEMENTAL REPORT REQUIRED) | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  |  |  | YES | [5 empty] | YES | PREVIOUS LEAKS SIMILAR TO THIS LEAK. | YES | [5 empty] | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DIKA ONYEDIRIM | PIPELINE SAFETY ENGINEER | dika.onyedirim@williams.com | 2816608503 |  | TRACI BRENTANO | traci.brentano@williams.com | 2815200007 | TYSON GREEN | MANAGER PIPELINE SAFETY | 3464398090 | tyson.green@williams.com | ON MARCH 4, 2022, WILLIAMS OPERATIONS REP RECEIVED A CALL FROM A THIRD PARTY INSPECTOR FOR P66 NOTING FUMES AND A HISSING SOUND APPROXIMATELY 2200FT FROM THE WILLIAMS P66 CROSSING TO THE WEST. WILLIAMS SUPERVISION CALLED IN OFFSHORE OPERATIONS REP WITH HELICOPTER TO FLY OVER THE SUBJECT AREA AT 9:31AM. AT 11:38AM, WILLIAMS SUPERVISION RECEIVED A VIDEO FROM WILLIAMS OPERATIONS REP FROM THE FLY OVER AND ALSO THE GPS COORDINATES OF THE LOCATION. AT THAT POINT, WILLIAMS IDENTIFIED THE LOCATION WAS IGNITED AND WAS A LOCALIZED BURN AREA IN THE MARSH. AT 11:42AM, WILLIAMS SUPERVISION CALLED PIPELINE CONTROL TO NOTIFY OF NEED TO ISOLATE THE RACELAND LATERAL. THE LINE SEGMENT WAS THEN ISOLATED AND BLOWDOWN OF THE LINE STARTED AT 2:09 PM. AT 4:12PM, ANOTHER HELICOPTER OVERFLIGHT WAS CONDUCTED AND THE FIRE WAS MUCH SMALLER THAN ORIGINAL, NOW APPROXIMATELY 1FT IN HEIGHT. AT 4:30PM, 1 PSI CONFIRMED ON THE SECTION ISOLATED AND BLOWN DOWN. FIRE CONFIRMED OUT ON MARCH 5, AT 7AM WITH OVERFLIGHT. LINE DOWN AND SAFE. WILLIAMS OPERATIONS VISITED SITE VIA AIRBOAT AND IDENTIFIED LINE IS 5FT DEPTH IN MARSH. APPROXIMATELY 1FT OF SOLID, THEN ALL LOOSE MARSH/WATER. WILLIAMS NOTIFIED FERC AND OCM ON MARCH 10 OF INTENT TO REPAIR UNDER EMERGENCY USE AUTHORIZATION. ALL APPROVALS RECEIVED FOR EXCAVATION AND REPAIR ON MARCH 11. THE PIPELINE WAS PLANNED TO BE EXCAVATED VIA MARSH EXCAVATOR, BUT ONLY THE TOP 1FT WAS ABLE TO BE REMOVED. DIVERS HAD TO BE CALLED IN TO INSTALL AN 8" PLIDCO HIGH PRESSURE CLAMP OVER THE LEAK LOCATION. DIVERS REMOVED COATING AND CLEANED AREA PER MANUFACTURER'S REQUIREMENTS, THEN INSTALLED CLAMP AND TORQUED. ONLY ONE LEAK LOCATION WAS IDENTIFIED, APPROXIMATELY 0.15INCHES DIAMETER. ON MARCH 17, CLAMP WAS INSTALLED, TORQUED AND LINE PRESSURED BACK UP TO CONFIRM LEAK REPAIR. LINE WAS APPROVED TO RETURN TO SERVICE AT 9AM ON MARCH 18. WILLIAMS IS EVALUATING POSSIBLE PREVENTIVE MEASURES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220041 | 36534 | 2022-04-01 09:21 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-03-09 13:30 | 2022 | EASTERN | NO | 36.3449 | -76.9349 | 1330740 | 2022-03-10 14:38 | 1330814 | NATURAL GAS |  | 0.1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | NO INITIAL ACTION TAKEN PLACE. |  | OPERATIONAL CONTROL | NO INITIAL ACTION TAKEN PLACE. |  | 0 | 2022-03-09 13:15 | 2022-03-09 14:30 | ONSHORE | NC | 27910 | AHOSKIE | HERTFORD | NOT APPLICABLE |  | LINE 208 | 208_MLV_1 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 65 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.312 | 42000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR |  | YES | [26 empty] | 2002 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 2 LOCATION | NO |  | 254 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 770000 | 770000 | 30000 | 30000 | 0 | 0 |  | 0.1 | 800000 | 352929.3605624376 | 800000 | 0 | 0 | 0 | 0 | NO |  |  |  | 775 | 5 | 800 | 192.619(A)(2) |  | 2021-09-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 44536 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [19 empty] | YES |  |  | YES |  | YES | [6 empty] | YES |  |  | YES | GASKET FAILURE | [161 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | DURING A SITE VISIT TO INSPECT NEWLY INSTALLED STATION RESTORATION, A GAS ODOR WAS DETECTED NEAR THE VALVE SETTING. WATER WAS PRESENT AROUND THE BASE OF THE VALVE DUE TO PREVIOUS WEATHER AND BUBBLES WERE NOTICED AT GROUND LEVEL. LEAK WAS DEEMED NOT FIXABLE BY NORMAL MEANS (GREASING) SO VALVE WAS REPLACED. DUE TO THE NATURE OF THE LEAK, THE VOLUME OF GAS LOSS WAS SMALL BUT COULD NOT BE DETERMINED.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220042 | 36541 | 2022-04-01 13:48 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-03-03 02:15 | 2022 | EASTERN | NO | 39.6387 | -79.3409 | 1330107 | 2022-03-03 02:46 | 13320217 | NATURAL GAS |  | 3131.3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-03 02:15 | 2022-03-03 17:00 |  | NO |  |  | NO | [11 empty] | 0 | 2022-03-03 02:15 | 2022-03-03 02:30 | ONSHORE | MD | 21520 | Not Within a Municipality | GARRETT | MILEPOST | 0 | TEXAS EASTERN TRANSMISSION, LP ACCIDENT STORAGE | ACCIDENT STORAGE FACILITY | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1966 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | SYSTEM ESD | CLASS 1 LOCATION | NO |  | 354 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 14780 | 14780 | 2000 | 2000 | 500 | 500 | 0 | 0 |  | 4.72 | 17280 | 10800.7447833190792940199335548172757475 | 17280 | 0 | 0 | 0 | 0 | NO |  |  |  | 2365 | 396000 | 3550 | 192.619(A)(2) |  | 1965-11-08 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  |  | YES | [5 empty] | YES | [24 empty] | YES | DEBRIS IN VALVE SOLENOID | [161 empty] | MICHAEL MCGRATH |  | michael.mcgrath@enbridge.com | 6128056542 |  |  |  |  | NATHAN ATANU |  | 17136275008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 2:15 AM EST ON MARCH 3, 2022, THE ACCIDENT STORAGE FACILITY (GARRETT COUNTY, MD) EXPERIENCED AN ESD. THE ESD OCCURRED WHILE IN THE PROCESS OF TRANSITIONING FROM STORAGE INJECTION TO STORAGE WITHDRAWAL. THE CAUSE WAS DETERMINED BE A VALVE MALFUNCTION. THE VALVE MALFUNCTION WAS DUE TO DEBRIS IN A SOLENOID. THE SOLENOID WAS REPLACED, AND THE SYSTEM WAS RETURNED TO SERVICE THE SAME DAY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220043 | 36563 | 2022-04-07 18:02 | ORIGINAL FINAL | 13120 | NATURAL GAS PIPELINE CO OF AMERICA (KMI) | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-03-09 09:04 | 2022 | CENTRAL | YES | 38.4201 | -98.9307 | 1330611 | 2022-03-09 11:56 | 1330790 | NATURAL GAS |  | 5021 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2022-03-09 08:15 | 2022-03-09 07:00 | ONSHORE | KS | 67530 | GREAT BEND | BARTON | NOT APPLICABLE |  | NGPL - COMPRESSOR STATION 104 | NGPL - COMPRESSOR STATION 104 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2010 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | COMPRESSOR SUCTION VALVE | [5 empty] | CLASS 1 LOCATION | NO |  | 479 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 24402 | 24402 | 0 | 0 | 684 | 684 | 0 | 0 |  | 4.86 | 25086 | 16313.0336730483260084651162790697674419 | 25086 | 0 | 0 | 0 | 0 | NO |  |  |  | 195 | 5021 | 712 | 192.619(A)(2) |  | 1991-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DEEMED INDEPENDENT OF THE CONTROLLER(S) ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [33 empty] | YES | VALVE SOLENOID LIMIT SWITCH DRIFTED | [161 empty] | JORGE LOPEZ |  | jorge_lopez@kindermorgan.com | 7134204675 |  |  |  |  | JAIME HERNANDEZ |  | 7133699443 | jaime_hernandez@kindermorgan.com | ON 3/09/2022, AT 05:43 NATURAL GAS PIPELINE COMPANY (NGPL) GAS CONTROL SHUT DOWN UNIT 14 REMOTELY VIA SCADA SYSTEM. SUBSEQUENTLY, NGPL OPERATIONS SPECIALIST RECEIVED AN ALARM REGARDING STATION 104, UNIT 14 AND STARTED TO INVESTIGATE THE CAUSE. AT 07:00, OPERATIONS SPECIALIST ARRIVED ON SITE TO START TROUBLESHOOTING THE ALARM. AT 08:15, AN OPERATIONS SPECIALIST #2 ARRIVED ON SITE TO SUPPORT MITIGATE THE ALARM. UPON ARRIVAL WAS ABLE TO HEAR GAS VENTING THROUGH A SILENCER ON UNIT 14. AT 09:59, OPERATIONS SPECIALIST #2 CLOSED THE VENT VALVE AND CALLED NGPL OPERATIONS SUPERVISOR. AT 11:00, OPERATIONS SUPERVISOR ARRIVED ON SITE TO INVESTIGATE THE EVENT. AT 11:45, THE EMERGENCY RESPONSE LINE (ERL) CALL COMMENCED AND DURING THE CALL, OUT OF ABUNDANCE OF CAUTION NGPL DECIDED TO REPORT THE EVENT TO THE NRC FROM A VOLUME RELEASE STANDPOINT. NGPL STARTED THE INVESTIGATION AND CONCLUDED THAT THE VOLUME RELEASED EXCEEDED THE REPORTING THRESHOLD PER THE COMPRESSOR UNIT PLC DATA. THE UNIT 14 SUCTION VALVE DID NOT CLOSE COMPLETELY AFTER SHUT DOWN, ALLOWING GAS TO VENT THROUGH THE VENT VALVE SILENCER. FURTHERMORE, THE INVESTIGATION ALSO DISCOVERED THAT THE SUCTION VALVE DID NOT CLOSE PROPERLY DUE TO THE LIMIT SWITCHES FOR THE VALVE POSITIONER AND THE SOLENOID OPERATOR. NGPL DETERMINED THAT THE LIMIT SWITCH THAT DE-ENERGIZES THE CLOSED SOLENOID ON THE VALVE OPERATOR NEEDED TO BE READJUSTED. NGPL E&C TECH READJUSTED THE LIMIT SWITCH AND CYCLED THE VALVE NUMEROUS TIMES TO ASSURE THE VALVE OPERATION. NGPL PUT UNIT 14 BACK IN SERVICE THE SAME DAY. IN ORDER TO PREVENT REOCCURRENCE NGPL WILL BE REVISING THE UNIT PLC LOGIC AND REMOVING THE LIMIT SWITCHES IN THE VALVE CONTROL CIRCUITS TO THE VALVE CONTROL SOLENOIDS TO AVOID INTERRUPTION OF THE UNIT VALVE OPEN AND CLOSE SIGNALS FROM THE PLC.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220045 | 36579 | 2022-04-14 10:00 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2022-03-18 05:23 | 2022 | CENTRAL | YES | 31.3322 | -90.2197 | 1331347 | 2022-03-18 05:56 | 1331478 | NATURAL GAS |  | 1170 | 2855 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-18 05:23 | 2022-03-21 17:10 |  | YES | OPERATOR | 2022-03-18 05:32 | YES | 2022-03-18 05:23 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1170 | NO | [6 empty] | 1 | 2022-03-18 05:23 | 2022-03-18 04:30 | ONSHORE | MS | 39641 | Not Within a Municipality | WALTHALL | SURVEY STATION NO. | 170.6 | MCCOMB COMPRESSOR STATION | INDEX 130 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | LIGHTNING STRIKE CAUSED SHAFER ACTUATOR TO IGNITE | CLASS 1 LOCATION | NO |  | 18 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 13047 | 13047 | 5347 | 5347 | 7936 | 7936 | 13157 | 13157 | 0 | 0 |  | 4.57 | 39487 | 18569.6740832644830517607973421926910299 | 39487 | 0 | 0 | 1 | 0 | NO |  |  |  | 705 | 412 | 930 | 192.619(C) |  | 1971-03-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORM | [301 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | DURING A SEVERE THUNDERSTORM EVENT ON 3/18/2022 AT APPROXIMATELY 05:23, GULF SOUTH EXPERIENCED A FIRE ON A SHAFER ACTUATOR AT ITS MCCOMB COMPRESSOR STATION IN WALTHALL COUNTY, MS DUE TO A LIGHTNING STRIKE. THE ON-CALL EMPLOYEE WAS ALREADY ONSITE IN RESPONSE TO A COMMUNICATIONS OUTAGE THAT ALSO RESULTED FROM THE STORM. THE FIRE OCCURRED OUTSIDE OF THE ESD SYSTEM AND ESD SYSTEM WAS NOT MANUALLY ACTIVATED TO ENSURE BLOWN-DOWN GAS WOULD NOT DRIFT INTO THE FIRE, WORSENING THE EVENT. INTERNAL AND EXTERNAL NOTIFICATIONS WERE MADE AND PERSONNEL WERE DISPATCHED. THE STATION PIPING WAS DEPRESSURIZED TO 98 PSIG AND THE POWER GAS TAP WAS CLOSED TO ISOLATE FUEL GAS TO FIRE. ONCE THE AREA WAS SAFE, THE FIRE DEPARTMENT EXTINGUISHED RESIDUAL FIRE ON THE VALVE ACTUATOR. THE VALVE WAS INSPECTED AND DEEMED TO BE UNDAMAGED. THE SHAFER OPERATOR WAS REMOVED FROM THE VALVE AND GULF SOUTH HAS NO PLANS TO REPLACE IT. THE FACILITY WAS RETURNED TO SERVICE. THROUGHOUT THE DAY, GULF SOUTH PERSONNEL AND EMERGENCY RESPONDERS REMAINED IN CONTACT TO MONITOR THE EVENT. A SINGLE RESIDENTIAL DWELLING WAS EVACUATED AS A SAFETY PRECAUTION; THE DWELLING WAS NOT IMPACTED BY THIS EVENT. THE LIGHTNING STRIKE WAS NOT A DIRECT STRIKE BUT, INSTEAD, STRUCK A TREE. THE LIGHTNING STRIKE IS BELIEVED TO HAVE TRAVELED UNDERGROUND IN THE WET SOIL CONDITIONS FROM THE TREE ROOTS TO THE PIPELINE FACILITY RESULTING IN THE FIRE ON THE ACTUATOR.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220046 | 37036 | 2022-04-14 18:37 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-03-15 16:20 | 2022 | EASTERN | YES | 41.8023 | -85.5867 | 1331135 | 2022-03-15 18:59 | 1331245 | NATURAL GAS |  | 7505 | 596 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-15 16:39 | 2022-04-01 11:50 |  | NO |  |  | NO | [11 empty] | 0 | 2022-03-15 16:20 | 2022-03-15 16:37 | ONSHORE | MI | 49099 | WHITE PIGEON TOWNSHIP | ST. JOSEPH | NOT APPLICABLE |  | WHITE PIGEON COMPRESSOR STATION | VALVE 635 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2009 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | PLANT 3 SUCTION BLOWDOWN VALVE OPERATED WITHOUT COMMAND RESULTING A RELEASE OF 8.1 MMCF | CLASS 2 LOCATION | NO |  | 585 |  | NO | NO |  |  | YES | YES |  | 0 | 0 | 2336 | 2336 | 29420 | 29420 | 222280 | 222280 | 600 | 600 | 0 | 0 |  | 3.92 | 254636 | 118660.4941835440776702724252491694352159 | 254636 | 0 | 0 | 0 | 0 | NO |  |  |  | 644 | 403 | 1000 | 192.619(A)(2) |  | 2009-10-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER RECEIVED SCADA ALARM AND FOLLOWED THE REQUIRED RESPONSE PROTOCOL | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [11 empty] | YES | AT THE TIME OF THIS REPORT, THE PROBABLE CAUSE HAS BEEN DETERMINED TO BE AN ELECTRIC FAULT THAT OCCURRED IN THE VALVE ACTUATOR TERMINAL BOX DUE TO MOISTURE THAT EITHER ENERGIZED THE OPEN SOLENOID OR DE-ENERGIZED THE ESD SOLENOID CAUSING THE VALVE TO OPERATE AND GAS TO BE RELEASED. | [22 empty] | YES | WATER INTRUSION | [161 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON MARCH 15, 2022 AT APPROXIMATELY 16:20 HOURS CONSUMERS ENERGY GAS CONTROL RECEIVED A FIREGATE TROUBLE ALARM AT THE WHITE PIGEON COMPRESSOR STATION. WHITE PIGEON COMPRESSOR STATION IS LOCATED AT 68536 A ROAD, WHITE PIGEON TOWNSHIP, (ST. JOSEPH COUNTY) MICHIGAN. A STATION MECHANIC WAS DISPATCHED AND ARRIVED AT THE SITE AT APPROXIMATELY16:37 HOURS. THE MECHANIC OBSERVED MULTIPLE ESD VALVE POSITION FAULTS AT THE STATION CONTROL SCREEN AND GAS WAS BEING RELEASED NEAR PLANT 3, LATER DETERMINED TO BE A RELEASE AT THE PLANT 3 SUCTION BLOWDOWN VALVE (VALVE 635). THE MECHANIC ACTIVATED THE FIREGATE SYSTEM AT APPROXIMATELY 16:39 HOURS TO ISOLATE AND RELIEVE ALL GAS FROM THE PLANT 3 PIPING. THE VENTING WAS COMPLETE AT APPROXIMATELY 16:43 HOURS AND A SITE INSPECTION WAS COMPLETED TO CONFIRM ALL POTENTIAL HAZARDS WERE ELIMINATED. ON MARCH 16, 2022 AN INITIAL SITE ASSESSMENT AND INCIDENT REVIEW WAS CONDUCTED WITH THE MICHIGAN PUBLIC SERVICE COMMISSION. THE CAUSE INVESTIGATION CONTINUED FOR SEVERAL WEEKS AND INCLUDED ELECTRICAL TESTING AND FUNCTIONAL TESTING OF THE VALVE. BASED ON THE EVALUATION, REPAIR AND REPLACEMENT OF SELECTED COMPONENTS WERE COMPLETED AND SENT TO THE VENDOR FOR FURTHER EVALUATION. ADDITIONAL ACTIONS WERE COMPLETED ON SIMILAR EQUIPMENT PRIOR TO RETURNING PLANT 3 TO SERVICE ON APRIL 1, 2022 AT APPROXIMATELY11:50 HOURS. AT THE TIME OF THIS REPORT, THE PROBABLE CAUSE HAS BEEN DETERMINED TO BE AN ELECTRIC FAULT THAT OCCURRED IN THE VALVE ACTUATOR TERMINAL BOX DUE TO MOISTURE THAT EITHER ENERGIZED THE OPEN SOLENOID OR DE-ENERGIZED THE ESD SOLENOID CAUSING THE VALVE TO OPERATE AND GAS TO BE RELEASED. THE ESD SOLENOID AND THE RELAY MODULE HAVE BEEN SENT TO ROTORK AND DET-TRONICS RESPECTIVELY FOR ADDITIONAL VENDOR EVALUATION TO DETERMINE IF EITHER COMPONENT MAY HAVE CAUSED OR CONTRIBUTED TO THE EVENT. THE LABORATORY REPORTS FROM THE VENDOR, PETER PAUL ELECTRONICS CONCLUDED THE FAILURE TO BE OPEN CIRCUITS WITHIN THE COIL. THIS OCCURS WHEN THERE IS A BREAK IN THE WIRES OR CONNECTION. THE LAB ANALYSIS SHOWS THE LEAD CONNECTORS WERE INTACT, CONFIRMING THE BREAK WAS INSIDE THE COIL. THIS WAS CONFIRMED WHEN THE LAB REPLACED THE COIL IN THE VALVE AND THE OPEN CIRCUIT ISSUE WAS NOT OBSERVED. CONFIRMING THE ROOT CAUSE TO BE THE ESD SOLENOID FAILING AND OPERATING THE VALVE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220047 | 36586 | 2022-04-15 15:54 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-03-16 09:20 | 2022 | EASTERN | YES | 42.7414 | -83.7651 | 1331163 | 2022-03-16 10:24 | 1331246 | NATURAL GAS |  | 283400 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-16 10:13 |  | YES | YES | OPERATOR | 2022-03-16 09:22 | NO | [5 empty] | VALVE CLOSURE |  | 2022-03-16 10:13 | VALVE CLOSURE |  | 2022-03-16 09:22 | 0 | 2022-03-16 09:20 | 2022-03-16 09:20 | ONSHORE | MI | 48430 | FENTON | LIVINGSTON | NOT APPLICABLE |  | CONSUMERS ENERGY LINE 400 | 400-1 FENTON INTERCHANGE TO LAINGSBURG INTERCHANGE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.281 | 52000 | API 5L | SINGLE SAW |  | COLORADO IRON AND FUEL | OTHER | DEARBORN NO OX-ID 6X AND NO 7 DEARBORN WRAPPER | YES | [26 empty] | 1952 | 1950 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | ORIENTATION HAS NOT BEEN DETERMINED - LABORATORY ANALYSIS IS ON-GOING |  |  |  | CLASS 2 LOCATION | NO |  | 447 |  | NO | NO |  |  | YES | YES | YES | 6600 | 6600 | 0 | 0 | 1110928 | 1110928 | 1115000 | 1115000 | 1663 | 1663 | 0 | 0 |  | 3.92 | 2234191 | 1224471.77820750435677960465116279069767 | 2234191 | 0 | 0 | 0 | 0 | NO |  |  |  | 644 | 199000 | 730 | 192.619(A)(2) |  | 1968-10-13 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 49347 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE CONTROLLERS ACTIONS WAS COMPLETED AND DETERMINED THE ACTIONS WERE IN LINE WITH PROCEDURE REQUIREMENTS. | [12 empty] | YES | 12 | 0 | YES | 6 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON MARCH 16, 2022 AT APPROXIMATELY 09:20 HOURS A BURIED 24-INCH DIAMETER NATURAL GAS TRANSMISSION PIPELINE SEGMENT (LINE 400-1) OWNED AND OPERATED BY CONSUMERS ENERGY RUPTURED IN TYRONE TOWNSHIP (LIVINGSTON COUNTY) BETWEEN OLD HIGHWAY 23 AND LINDEN ROAD. LINE 400 WAS INSTALLED IN 1952 AND IS APPROXIMATELY 35.1 MILES FROM FENTON INTERCHANGE IN FENTON, MICHIGAN TO LAINGSBURG INTERCHANGE IN LAINGSBURG, MICHIGAN. CONSUMERS ENERGY EMPLOYEES AND CONTRACT EMPLOYEES WERE POSITIONED AT VARIOUS LOCATIONS ALONG THE PIPELINE PERFORMING AN INLINE INSPECTION (ILI) OF THE PIPELINE AT THE TIME OF THE RUPTURE. THE ILI TOOL WAS LAUNCHED AT APPROXIMATELY 09:06 HOURS FROM FENTON INTERCHANGE AND TRAVELED APPROXIMATELY TWO MILES WEST BEFORE THE RUPTURE OCCURRED. CONSUMERS ENERGY GAS OPERATIONS WORKED WITH GAS CONTROL TO IDENTIFY UPSTREAM AND DOWNSTREAM ISOLATIONS LOCATIONS. THE DOWNSTREAM VALVE LOCATED AT FENTON INTERCHANGE WAS CLOSED AT APPROXIMATELY 09:22 HOURS AND THE UPSTREAM VALVE LOCATED AT LUTZ ROAD WAD CLOSED AT APPROXIMATELY 10:13 HOURS. ONCE INITIAL ISOLATION WAS COMPLETE, GAS OPERATIONS PERSONNEL PROCEEDED TO CLOSE ADDITIONAL VALVES (DOUBLE BLOCK) AT BOTH THE UP AND DOWNSTREAM LOCATIONS FOR ADDED SAFETY. THE MICHIGAN STATE POLICE AND THE LOCAL POLICE AND FIRE DEPARTMENTS WERE ON SCENE AND ASSISTED WITH SHUTTING-DOWN TRAFFIC ON US HIGHWAY 23 AND OLD US HIGHWAY 23. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE RUPTURE. THE PIPELINE SEGMENTS WERE REMOVED FROM BOTH HIGHWAYS AND TRAFFIC ON ALL LANES ON US HIGHWAY 23 RESUMED AT APPROXIMATELY 13:32 HOURS. THE DAMAGE PIPELINE SEGMENTS AND ILI TOOL COMPONENTS WERE LOCATED AND TRANSPORTED TO SECURE LOCATIONS AT CONSUMERS ENERGY (PIPELINE SEGMENTS ) JACKSON, MICHIGAN AND THE ROSEN GROUP'S (ILI TOOL COMPONENTS) COLUMBUS, OHIO FACILITIES FOR FURTHER EVALUATION. INTERNAL TEAMS FOR BOTH CONSUMERS ENERGY AND THE ROSEN GROUP HAVE BEEN ASSEMBLED AND ARE WORKING TO DETERMINE THE CAUSE OF THE FAILURE. THE RUPTURE SEGMENT OF THE PIPELINE WILL NOT BE RETURNED TO SERVICE UNTIL THE INVESTIGATION IS COMPLETE, THE FAILURE CAUSE IS IDENTIFIED AND APPROPRIATE REMEDIATION AND PREVENTATIVE ACTIONS HAVE BEEN COMPLETED.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20220048 | 37133 | 2022-04-22 09:26 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2022-03-23 04:30 | 2022 | CENTRAL | YES | 32.5209 | -97.0822 | 1331720 | 2022-03-23 04:21 | 1331898 | NATURAL GAS |  | 33202 | 0 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-03-23 03:43 | 2022-03-30 20:30 |  |  |  |  | YES | 2022-03-23 01:14 | OTHER | SHUT VALVE | 33202 | NO | [6 empty] | 593 | 2022-03-23 03:00 | 2022-03-23 02:40 | ONSHORE | TX | 76063 | MANSFIELD | ELLIS | SURVEY STATION NO. | 162 | LINE X64 | MS 8981.1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | PIPE | PIPE BODY | 8 | NO | 0.322 | 52000 | X52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | PAINT |  | YES | [26 empty] | 2017 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 4 |  | CLASS 1 LOCATION | NO |  | 184 |  | NO | NO | NO |  | YES |  | YES | 60000 | 60000 | 0 | 0 | 175751 | 175751 | 1550000 | 1550000 | 50000 | 50000 | 0 | 0 |  | 5.2934 | 1835751 | 847646.7703431377542192691029900332225914 | 1835751 | 0 | 0 | 1100 | 10 | NO |  |  |  | 655 | 318.72 | 960 | 192.619(A)(2) |  | 2017-12-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAR CRASHED INTO STATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | YES |  |  |  | YES | UNKNOWN, NOT PROVIDED IN THE POLICE REPORT | UNKNOWN |  | YES | PASSENGER CAR | ROADWAY | 125 | YES |  | YES | [236 empty] | JORDAN BULLOCK | OPERATIONS MANAGER | jordan.bullock@atmosenergy.com | 214-206-2606 |  | JORDAN BULLOCK | jordan.bullock@atmosenergy.com | 214-206-2606 | MARLO SUTTON | VP TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | PRELIMINARY INVESTIGATION INDICATES THAT ON MARCH 23, 2022, A VEHICLE TRAVELING AT A HIGH RATE OF SPEED GOING SOUTHBOUND IN THE NORTHBOUND LANES OF HWY 360 CROSSED OVER U.S. 287 SOUTHBOUND SERVICE ROAD, TRAVELED AN ADDITIONAL 125 FEET, AND STRUCK AN ATMOS ENERGY MEASURING STATION NEAR MANSFIELD, TEXAS. THE GAS IGNITED. THE SYSTEM PRESSURE WAS AT 655 PSIG AT THE TIME OF THE INCIDENT. ATMOS ENERGY WAS NOTIFIED BY EMERGENCY RESPONDERS AT APPROXIMATELY 1:40 A.M. AND ATMOS ENERGY PERSONNEL ARRIVED ONSITE AT 2:40 A.M. THE FIRE DEPARTMENT HAD THE AREA SEALED OFF UNTIL 3:00 A.M., AT WHICH TIME THE TECHNICIAN WAS ABLE TO ACCESS THE SCENE AND DETERMINE THAT OUR FACILITY WAS INVOLVED. AT 3:43 A.M., AN UPSTREAM VALVE WAS ACTIVATED TO STOP THE FLOW OF GAS, WHICH RESULTED IN THE LOSS OF SERVICE TO ATMOS ENERGYS CUSTOMER, SIENERGY. SIENERGY INFORMED ATMOS ENERGY THAT IT HAD APPROXIMATELY 1,110 CUSTOMERS DOWNSTREAM THAT LOST SERVICE. THE FIRE DEPARTMENT EVACUATED A ONE-MILE RADIUS. REGARDING QUESTION A23 OF THIS REPORT, THE NUMBER OF PERSONS EVACUATED IS UNKNOWN, HOWEVER THERE WERE 593 STRUCTURES IN THE EVACUATION ZONE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220049 | 36615 | 2022-04-27 14:18 | ORIGINAL FINAL | 31728 | GULF SOUTH PIPELINE COMPANY, LLC | 9 GREENWAY PLAZA SUITE 2800 | HOUSTON | TX | 77046 | 2022-04-04 01:33 | 2022 | CENTRAL | YES | 32.0285 | -90.1423 | 1332640 | 2022-04-04 02:39 | 1332763 | NATURAL GAS |  | 3394 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-04-04 01:33 | 2022-04-04 10:21 |  | YES | OPERATOR | 2022-04-04 01:42 | NO | [11 empty] | 0 | 2022-04-04 01:33 | 2022-04-04 02:21 | ONSHORE | MS | 39073 | Not Within a Municipality | SIMPSON | NOT APPLICABLE |  | HARRISVILLE COMPRESSOR STATION | INDEX 817 / 817-L / 818 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2007 | 2007 | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION ESD | CLASS 1 LOCATION | NO |  | 272 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 18124 | 18124 | 651 | 651 | 630 | 630 | 0 | 0 |  | 5.34 | 19405 | 12457.1214940823307817508305647840531561 | 19405 | 0 | 0 | 0 | 0 | NO |  |  |  | 1424 | 2300 | 1480 | 192.619(A)(1) |  | 2008-05-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | O-RING FAILURE ON ENGINE OIL FILTER HOUSING | [15 empty] | YES | O-RING FAILURE ON ENGINE OIL FILTER HOUSING | [161 empty] | SHANNON MATTINGLY | PA OQ AND EVENT PROGRAM LEADER | shannon.mattingly@bwpipelines.com | 2709035764 |  |  |  |  | TINA BAKER | MANAGER COMPLIANCE SERVICES | 2703146547 | tina.baker@bwpipelines.com | ON APRIL 4, 2022 AT APPROXIMATELY 1:33 AM, GULF SOUTH PIPELINES EXPERIENCED A STATION ESD AT ITS HARRISVILLE COMPRESSOR STATION. GAS CONTROL DISPATCHED LOCAL OPERATIONS PERSONNEL WHO CONFIRMED THERE WAS NO FIRE AT THE TIME OF ARRIVAL. INVESTIGATION REVEALED THAT A BLOWN O-RING ON AN ENGINE OIL FILTER HOUSING OF UNIT #3 ALLOWED OIL TO SPRAY ON THE EXHAUST MANIFOLD WHICH CAUSED A BRIEF FIRE. THIS FLASH FIRE WAS RECOGNIZED BY FIRE DETECTION WHICH INITIATED THE ESD. THE DAMAGE WAS ISOLATED TO THE OIL FILTER HOUSING AND EXHAUST MANIFOLD INSULATION BLANKET. UNIT #3 WAS LOCKED OUT/TAGGED OUT, PARTS WERE REPLACED, THE AREA WAS CLEANED UP AND THE UNIT WAS RETURNED TO SERVICE THE SAME DAY. THE ANSWER PROVIDED FOR E1 IS 1,424 PSIG WHICH IS THE DISCHARGE PRESSURE. THE SUCTION PRESSURE AT THE STATION WAS 994 PSIG.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220050 | 36617 | 2022-04-27 16:07 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-03-29 13:45 | 2022 | CENTRAL | YES | 35.6919 | -100.2275 | 1332234 | 2022-03-29 15:06 | 1332315 | NATURAL GAS |  | 5800 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE VALVE WAS ISOLATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-03-29 14:18 | 2022-03-29 14:18 | ONSHORE | TX | 79011 | BRISCOE | HEMPHILL | NOT APPLICABLE |  | WOODALL PLANT | AD-23 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1978 | 1978 | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE GAS RELEASE | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 28420 | 28420 | 15000 | 15000 | 1000 | 1000 | 1000 | 1000 | RV TESTING. | 4.9 | 45420 | 26147.4233305564501627906976744186046512 | 45420 | 0 | 0 | 0 | 0 | NO |  |  |  | 964 | 2000 | 1000 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PREMATURE RV RELEASE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PREMATURE RELEASE | [147 empty] | YES | [13 empty] | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM SPECIALIST | casey.roberts@energytransfer.com | 4055575271 |  | SUSIE SJULIN | susie.sjulin@energytransfer.com | 4055575271 | SUSIE SJULIN | DIRECTOR - REGULATORY COMPLIANCE | 4055575271 | susie.sjulin@energytransfer.com | A RELIEF VALVE WAS DISCOVERED VENTING AT THE WOODALL PLANT YARD. THE RELEASE WAS SECURED, AND IT WAS DETERMINED THAT A REPORTABLE RELEASE OF NATURAL GAS OCCURRED. THE NRC WAS NOTIFIED (INITIAL #1332234, 48 HR. @1332315). UPON INVESTIGATION, IT WAS DETERMINED THE RV RELIEVED PREMATURELY. LINE AD-23 HAS A 1000 PSI MAOP AND WAS OPERATING NEAR 964 PSI AT THE TIME OF RELEASE. THE RV WAS RE TESTED AND SET AT 1000 PSI. THIS RELIEF VALVE IS AT A LOCATION WHERE ALL CONNECTING PIPELINES (AD WEST, AD-23, AND ADM-14) COME TOGETHER, ALL WITH A 1000 PSIG MAOPS. A NEW RV HAS BEEN ORDERED AND A PROJECT IS BEING DEVELOPED TO POSSIBLY RELOCATE THE VALVE TO LINE AD-WEST WHEN IT ARRIVES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220051 | 36631 | 2022-05-02 00:26 | ORIGINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-03-31 07:59 | 2022 | CENTRAL | YES | 32.2041 | -87.949 | 1332360 | 2022-03-31 08:38 | 1332454 | NATURAL GAS |  | 3927 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE OPENED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-03-31 07:00 | 2022-03-31 07:00 | ONSHORE | AL | 36782 | SWEET WATER | MARENGO | NOT APPLICABLE |  | STATION 90 | MU 16 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE FAILED AFTER POWER SURGE AND SEVERE STORMS DURING THE NIGHT | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 21402 | 21402 | 300 | 300 | 0 | 0 | 0 | 0 |  | 5.45 | 21702 | 14175.1890417723758940199335548172757475 | 21702 | 0 | 0 | 0 | 0 | NO |  |  |  | 200 | 0 | 800 | OTHER | MU RELIEF VALVE. NOT ON PIPELINE | 2022-05-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELIEF VALVE VENTING. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | POWER SURGE DURING STORMS | [161 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 918-264-0522 |  |  |  |  | TYSON GREEN | PIPELINE SAFETY MANAGER | 360-594-2137 | tyson.green@williams.com | MAIN UNIT FUEL GAS RELIEF VALVE ACTIVATED. OPERATIONS DISCOVERED RELIEF VALVE AT 7AM. OPERATIONS THINKS A POWER SURGE CAUSED A TURBINE TO GO DOWN WHICH LED TO THE RELEASE DURING SEVERE STORMS OVERNIGHT. OPERATIONS TRENDED THE RELEASE, IT STARTED AROUND 745 PM LAST NIGHT. RELEASE WAS REPORTED TO THE NRC OUT OF AN ABUNDANCE OF CAUTION AND GAS VENTED WAS LATER DETERMINED TO BE 3.9927MMSCF.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220052 | 36632 | 2022-05-02 00:48 | ORIGINAL | 31565 | GULFSTREAM MANAGEMENT & OPERATING SERVICES,LLC | 1905 INTERMODAL CIRCLE, SUITE 310 | PALMETTO | FL | 34221 | 2022-04-02 09:12 | 2022 | CENTRAL | YES | 30.3938 | -88.1848 | 1332546 | 2022-04-02 10:29 | 1332645 | NATURAL GAS |  | 4983 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-CONSTRUCTION COMMISSIONING | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2022-04-02 09:10 | 2022-04-02 09:12 | ONSHORE | AL | 36523 | CODEN | MOBILE | NOT APPLICABLE |  | STATION 410 | STATION 410 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2022 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | INADVERTENT OPENING OF RELIEF VALVE | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 27157 | 27157 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5.45 | 27157 | 17818.9617940199335548172757475083056478 | 27157 | 0 | 0 | 0 | 0 | NO |  |  |  | 1963 | 0 | 2180 | 192.619(A)(2) |  | 2002-05-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | PAINTER REMOVING MASKING MATERIAL, CAUGHT ACTUATION HANDLE, AND OPENED THE VALVE. |  |  |  | YES | PAINTER ON SITE DURING CONSTRUCTION ACCIDENTALLY CAUSE VALVE TO OPEN. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | STEPHANIE ROSS | PIPELINE SAFETY ENGINEER | stephanie.ross@williams.com | 918-264-0522 |  |  |  |  | TYSON GREEN | PIPELINE SAFETY MANAGER | 360-594-2137 | tyson.green@williams.com | AT APPROXIMATELY 9:10 AM, THE PAINTING CREW WAS CONDUCTING PAINTING ACTIVITIES/REMOVING PLASTIC FROM PREVIOUSLY PAINTED PIPING AND VALVES IN CONSTRUCTION AREA. WHILE REMOVING THE PLASTIC FROM VALVE XV-9910 THE PLASTIC CONTACTED THE 3-WAY VENT VALVE CONNECTED TO THE LATCHING VERSA VALVE, CAUSING GAS TO VENT AND THE VERSA TO ACTIVATE LETTING THE BLOWDOWN VALVE OPEN. OPERATIONS WAS IN THE VICINITY AND IMMEDIATELY CLOSED THE 8' MANUAL VALVE WITHIN MINUTES. STATION 410 WAS ONLINE WITH TWO UNITS RUNNING BUT THE UNITS DID NOT SHUT DOWN. NO INJURIES OR DAMAGE OCCURRED. VALVE IS PART OF NEW INSTALLATION/CONSTRUCTION AT THE FACILITY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220053 | 36660 | 2022-05-09 10:58 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-04-11 07:45 | 2022 | CENTRAL | YES | 35.6919 | -100.2275 | 1333256 | 2022-04-11 12:58 | 1333381 | NATURAL GAS |  | 6975 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE RELIEF WAS ISOLATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-04-11 08:30 | 2022-04-11 08:30 | ONSHORE | TX | 79011 | BRISCOE | HEMPHILL | NOT APPLICABLE |  | WOODALL PLANT | AD-23 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | 1978 | 1978 | CARBON STEEL |  | OTHER | [8 empty] | PREMATURE GAS RELEASE | CLASS 1 LOCATION | NO |  | 175 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 34178 | 34178 | 1000 | 1000 | 1000 | 1000 | 0 | 0 |  | 4.9 | 36178 | 23308.0875210074229036544850498338870432 | 36178 | 0 | 0 | 0 | 0 | NO |  |  |  | 967 | 2000 | 1000 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PREMATURE GAS RELEASE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [18 empty] | YES | [158 empty] | YES | [9 empty] | YES |  |  |  | CASEY ROBERTS | LEAD DOT COMPLIANCE PROGRAM MANAGER | casey.roberts@energytransfer.com | 4056263981 |  | SUSIE SJULIN | susie.sjulin@energytransfer.com | 4055575271 | SUSIE SJULIN | DIRECTOR - REGULATORY COMPLIANCE | 4055575271 | susie.sjulin@energytransfer.com | OPERATIONS PERSONNEL ARRIVED AT THE WOODAL PLANT YARD ON APRIL 11TH AND DISCOVERED A RELIEF VALVE VENTING ON LINE AD-23. THE RELIEF WAS ISOLATED AND IT WAS DISCOVERED THE RELIEF WAS RELIEVING PREMATURELY 967 PSI. THE MAOP OF AD-23 IS 1000 PSI. THE NRC WAS NOTIFIED ON 4/11/2022 (#1333256) OF THE RELEASE AND A 48 HR. FOLLOW UP WAS PROVIDED ON 4/12/2022 (#1333381). THIS RELIEF VALVE HAS RELIEVED PREMATURELY PREVIOUSLY AND OPERATIONS ORDERED A REPLACEMENT VALVE IN APRIL OF 2022. LEAD TIME ON THE NEW VALVE WAS 18 WEEKS AT TIME OF ORDER AND HAS NOT YET BEEN RECEIVED. AFTER THIS RELEASE WAS SECURED, OPERATIONS NOTICIDED THE THE EXISTING VALVE WAS A DIAPHRAGM TYPE PILOT AND THOUGHT THAT MIGHT BE THE ISSUE CAUSING IT TO RELIEVE PREMATURELY. THE PILOT HAS SINCE BEEN UPGRADED FROM A DIAPHRAGM TYPE TO A PISTON TYPE. THE OPERATIONS GROUP LOCATED A PISTON PILOT THAT WAS NOT IN USE AND A SPARE PISTON PILOT OPERATOR HAS BEEN ORDERED TO KEEP ON THE SHELF (TENTATIVELY SCHEDULED FOR RECEIPT IN AUGUST 2022). A FULL REBUILD KIT FOR THE RELIEF VALVE HAS BEEN ORDERED AS WELL SHOULD IT BE NEEDED. A PROJECT IS BEING DEVELOPED TO POSSIBLY RELOCATE THE VALVE. LINE AD-23, ADM-14, AND LINE AD-WEST ARE ALL TIED TOGETHER AT THE WOODALL PLANT YARD. ALL LINES HAVE A 1000 PSI MAOP AND ARE ALL COMMON. OVER THE LAST COUPLE OF YEARS, AD-WEST HAS ROUTINELY OPERATED AT A HIGHER PRESSURE ANYWHERE FROM 925 TO 975 PSI. SINCE EACH RELEASE HAS BEEN PREMATURE, ENABLE THOUGHT REPLACING THE DIAPHRAGM PILOT (WHICH HAS A +/- 5% INITIATION) WITH A PISTON PILOT WOULD ALLOW AD-WEST TO OPERATE CLOSER TO MAOP. THE DIAPHRAGM WORKED WELL WHEN THE LINE WAS OPERATING AT A LOWER PRESSURE BUT COULD CONTINUE TO PREMATURELY RELIEVE +/- 50 PSI EARLY IF NOT CHANGED TO THE PISTON STYLE. 05.12.2022 SUPPLEMENTAL PART H NARRATIVE UPDATED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220054 | 37350 | 2022-05-09 22:22 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-04-12 08:21 | 2022 | CENTRAL | YES | 32.2041 | -87.9484 | 1333337 | 2022-04-12 09:14 | 1333505 | NATURAL GAS |  | 53185 | 3424 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-04-12 08:23 | 2022-09-14 14:20 |  | YES | OPERATOR | 2022-04-12 08:27 | NO | [5 empty] | VALVE CLOSURE |  | 2022-04-12 08:23 | VALVE CLOSURE |  | 2022-04-12 08:34 | 0 | 2022-04-12 08:21 | 2022-04-12 08:21 | ONSHORE | AL | 36782 | Not Within a Municipality | MARENGO | MILEPOST | 811.18 | STATION 90 | MAINLINE A | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 30 |  | 0.5 | 52000 | API 5L | DSAW |  | BETHLEHEM STEEL | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | 1957 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | A HARD SPOT (APPROXIMATELY 6.5" LONG BY 3" WIDE) WAS LOCATED AT THE ORIGIN OF THE RUPTURE. | 105.6 | 48 |  | CLASS 1 LOCATION | NO |  | 585 |  | NO | NO |  |  | NO |  |  | 13000 | 13000 | 15408 | 15408 | 239333 | 239333 | 5350000 | 5350000 | 0 | 0 | 0 | 0 |  | 4.5 | 5617741 | 2529785.05390969088492350830564784053156 | 5617741 | 0 | 0 | 1 | 0 | NO |  |  |  | 779 | 40000 | 800 | 192.619(A)(1) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED | MANUAL | 80098 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INVESTIGATION FOUND THAT THE PIPELINE WAS OPERATING NORMALLY AT THE TIME OF THE INCIDENT AND THAT THE CONTROL ROOM WAS NOT A FACTOR IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | PRESENCE OF PRE-EXISTING HARD SPOT MANUFACTURING DEFECT. | [6 empty] | YES | [8 empty] | UNKNOWN | [54 empty] | YES |  | YES |  |  | YES | [14 empty] | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | HIGH RESOLUTION | [23 empty] | 2018 | FREE SWIMMING | [12 empty] | NO |  |  | NO | [13 empty] | NO | [47 empty] | YES | YES | [14 empty] | MARIE SOTAK | ENGINEER PRINCIPAL | marie.sotak@williams.com | 832-331-4275 |  |  |  |  | MARIE SOTAK | ENGINEER PRINCIPAL | 832-331-4275 | marie.sotak@williams.com | ON 4/12/22, A SEGMENT OF MAINLINE A RUPTURED IN THE VALVE YARD OF STATION 90 COMPRESSOR FACILITY. NO EXPLOSION, FIRE OR INJURY OCCURRED. LOCAL OPERATING PERSONNEL PROVIDED TEMPORARY TRAFFIC CONTROL FOR ~30 MINUTES FOLLOWING THE RELEASE. NO OTHER PUBLIC IMPACT RESULTED FORM THE RELEASE. MAINLINE A IS ONE OF 5 PARALLEL PIPELINES THAT RUN THROUGH THE FACILITY. NO OTHER PIPELINE WAS INVOLVED OR DAMAGED DURING THE INCIDENT. OPERATING PERSONNEL AT THE FACILITY IMMEDIATELY INITIATED A COMPLETE COMPRESSOR STATION ESD AND PRESSURE BLOWDOWN. MAINLINE A WAS ISOLATED BETWEEN STATION 90 AND THE NEAREST PIPELINE ISOLATION VALVE WITHIN 12 MINUTES OF THE RUPTURE. THE NRC WAS NOTIFIED OF THE INCIDENT 45 MINUTES FOLLOWING THE RUPTURE. THE PIPELINE SEGMENT THAT FAILED WAS A 30-INCH OUTSIDE DIAMETER, 0.500-INCH WALL THICKNESS BETHLEHEM STEEL PIPE MANUFACTURED IN 1957 THAT WAS PROTECTED FORM CORROSION WITH EXTERNAL COATING AND IMPRESSED CURRENT CATHODIC PROTECTION. THE FRACTURE INVOLVED PIPE INSTALLED WITH A PIG LAUNCHER IN 1959 AND PIPE INSTALLED DURING MODIFICATION OF THIS PIG LAUNCHER IN 1997. METALLURGICAL ANALYSIS CONCLUDED THE RUPTURE ORIGINATED IN A HARD SPOT IN THE BODY OF PIPE INSTALLED IN 1959. ANALYSIS FURTHER IDENTIFIED A CRACK HAD DEVELOPED AT THE RUPTURE ORIGIN IN A MICROSCOPIC CORROSION PIT. INVESTIGATION CONCLUDED THE PIPELINE RUPTURE RESULTED FROM A HYDROGEN-ASSISTED STRESS CRACK THAT DEVELOPED IN A PREEXISTING HARD SPOT, WHICH EXTENDED THROUGH THE ENTIRE PIPE WALL. THE BRITTLE STRUCTURE OF THE HARD METAL ALLOWED THE STRESS CRACK TO PROPAGATE TO THE POINT OF FRACTURE. INVESTIGATION FURTHER IDENTIFIED ENVIRONMENTALLY ASSISTED CORROSION IN THE FORM OF A MICROSCOPIC PIT AND ELEVATED CATHODIC PROTECTION ELECTRONEGATIVITY AS CONTRIBUTING FACTORS TO DIRECT CAUSES.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20220055 | 36772 | 2022-05-13 14:37 | SUPPLEMENTAL | 32403 | ARCHAEA ENERGY OPERATING, LLC | 46280 DYLAN DRIVE SUITE 200 | NOVI | MI | 48377 | 2022-04-14 14:00 | 2022 | CENTRAL | NO | 35.3198 | -97.3601 | 1333605 | 2022-04-14 17:20 | 1333692 | NATURAL GAS |  | 961 | 0 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | ROUTINE START-UP | YES |  | 2022-04-14 14:05 | 2022-04-29 17:00 |  | YES | OPERATOR | 2022-04-14 14:05 | YES | 2022-04-14 14:00 | ALLOWED TO BURN OUT |  | 961 | NO | OPERATIONAL CONTROL | PROCESSING FACILITY WAS IMMEDIATELY SHUTDOWN |  | OPERATIONAL CONTROL | GAS FIRE ALLOWED TO SELF EXTINGUISH |  | 0 | 2022-04-14 14:00 | 2022-04-14 14:30 | ONSHORE | OK | 73149 | OKLAHOMA CITY | CLEVELAND | NOT APPLICABLE |  | SOUTHERN DOME | SOUTHERN DOME PIPELINE | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.25 | 24000 | UNKNOWN | FURNACE BUTT WELDED |  | RED MAN PIPE AND SUPPLY COMPANY | EPOXY |  | NO | [26 empty] | 2005 | 2000 | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASED AND IGNITED DURING ROUTINE PIGGING ACTIVITY | CLASS 1 LOCATION | NO |  | 230 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 8072 | 8072 | 80000 | 80000 | 0 | 0 | 0 | 0 |  | 8.4 | 88072 | 40589.3480163766503654485049833887043189 | 88072 | 0 | 1 | 0 | 0 | NO |  |  |  | 160 | 288 | 680 | 192.619(A)(1) |  | 2018-05-17 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 51216 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | THIRD-PARTY CONTRACTOR FAILED TO CLOSE THE PIG RECEIVER END WHILE PUSHING THE PIG WITH NATURAL GAS. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | NEVIN EDWARDS | AIR PERMITTING MANAGER | nedwards@archaea.energy |  |  | JOHN FREEMAN | jfreeman@archaea.energy | 405-698-6529 | EMILY ZAMBUTO | DIRECTOR OF ENVIRONMENTAL COMPLIANCE | 585-948-4616 | ezambuto@archaea.energy | ON APRIL 14, 2022 AT APPROXIMATELY 14:00 LOCAL TIME, THE SOUTHERN DOME PIPELINE WAS UNDERGOING ROUTINE MAINTENANCE WHEN GAS WAS RELEASED FROM THE PIPELINE AND IGNITED CAUSING A FIRE. THE PIPELINE WAS IN THE MIDDLE OF A PIG RUN WHEN THE INCIDENT OCCURRED. THIS WAS THE LAST PIGGING EVENT THAT WAS TO OCCUR DURING THE MAINTENANCE EVENT. A FINAL CLEANING PIG WAS INSERTED INTO PIPELINE TO COLLECT ANY REMAINING BUILD-UP IN THE LINE. THE PIG WAS BEING FORCED THROUGH THE PIPELINE WITH NATURAL GAS, RATHER THAN AIR OR NITROGEN. THE PIG RECEIVER DOOR WAS IN THE OPEN POSITION DURING THE PIG RUN. DURING THE PIG RUN, IGNITION OF THE NATURAL GAS OCCURRED WITH THE SUBSEQUENT GAS RELEASE AND IGNITION AT THE PIG RECEIVER LOCATION WHERE SEVERAL EMPLOYEES WERE LOCATED TO RECEIVE THE PIG. ONE EMPLOYEE WAS INJURED DURING THE INCIDENT. LOCAL RESPONDERS WERE DISPATCHED IMMEDIATELY TO THE SCENE TO ASSIST THE FIRE. THE FIRE AND GAS IN THE PIPELINE WERE ALLOWED TO EXTINGUISH ITSELF. THE FACILITY THAT PRODUCES NATURAL GAS TO SUPPLY THE PIPELINE WAS IMMEDIATELY SHUTDOWN AT 14:05 AFTER THE GAS RELEASE AND IGNITION TO PREVENT ADDITIONAL NATURAL GAS FROM BEING INTRODUCED INTO THE PIPELINE. THE EQUIPMENT INVOLVED IN THE INCIDENT WAS THOROUGHLY EVALUATED AND INSPECTED. AN N2 PRESSURE TEST AT 1080 PSI WAS COMPLETED ON THE PIPELINE WITH AN EIGHT HOUR HOLD TIME. AFTER SUCCESSFUL COMPLETION, THE FACILITY AND PIPELINE WERE RETURNED TO SERVICE ON 4/29/2022.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220056 | 37429 | 2022-05-18 14:37 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-04-23 12:59 | 2022 | CENTRAL | YES | 35.2968 | -93.4298 | 1334249 | 2022-04-23 01:14 | 1334340 | NATURAL GAS |  | 100 | 523 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-04-23 03:00 | 2022-05-07 10:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-04-22 06:00 | VALVE CLOSURE |  | 2022-04-22 06:00 | 0 | 2022-04-23 12:59 | 2022-04-10 01:00 | ONSHORE | AR | 72851 | Not Within a Municipality | LOGAN | SURVEY STATION NO. | 288638 | BT-14 | LAKE DARDANELLE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | OTHER | LEAK WAS NEAR SHORELINE OF SHOAL BAY | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | OTHER | [37 empty] | WELD PLUS FITTING" | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 264 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 3447 | 3447 | 659 | 659 | 466421 | 466421 | 1000 | 1000 | 0 | 0 |  | 6.59 | 471527 | 208161.3280188682484172624584717607973422 | 471527 | 0 | 0 | 0 | 0 | NO |  |  |  | 700 | 6000 | 901 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 13340 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE AMOUNT OF GAS BEING RELEASED WAS AT AN AMOUNT THAT WOULD NOT HAVE SET OFF ANY ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | LAB ANALYSIS IDENTIFIED THE LEAK AT THE DOWNSTREAM END OF THE WELD+ENDS COUPLER COINCIDING WITH THE CLAMP SCREW OVER PASS. THE LEAK COINCIDED WITH AN AREA OF UNDERCUT THAT CONNECTED TO THE FEMALE PORTION OF THE CLAMP SCREW ASSEMBLY THROUGH A TIGHT CRACK PATH. | [147 empty] | DANIEL ANTOINE | SR. DOT SPECIALIST | daniel.antoine@energytransfer.com | 501-472-5065 |  | SUSIE SJULIN | susie.sjulin@energytransfer.com | 405-557-5271 | SUSIE SJULIN | DIRECTOR REGULATORY COMPLIANCE | 405-557-5271 | susie.sjulin@energytransfer.com | A LEAK ON BT-14 NEAR LAKE DARDANELLE WAS REPORTED BY THE PUBLIC ON 4/10/2022. OPERATION PERSONNEL ARRIVED ON SITE AND COMPLETED A VISUAL INSPECTION ON BT-14 NEAR THE SHORELINE OF SHOAL BAY (LAKE DARDANELLE). OPERATING PRESSURE WAS REDUCED FROM 700 TO 315 PSIG AND THE LEAK WAS MONITORED VIA DAILY PATROLS FOR TWO WEEKS UNTIL WEATHER PERMITTED ACCESS TO THE PIPE TO EVALUATE THE CAUSE OF THE LEAK. THE SECTION OF PIPE CONTAINING THE LEAK WAS ISOLATED ON 4/22/2022. THE LEAK APPEARED TO BE THE RESULT OF A PINHOLE AT A "WELD PLUS FITTING'. ON 4/23/2022 AT 12:59 IT WAS DETERMINED THAT THE COST OF REPAIR WOULD EXCEED $122,000....AN INCIDENT NOTIFICATION WAS SENT TO THE NRC AT 1:14PM CENTRAL TIME (NRC# 1334249). A 48HR FOLLOW UP WAS PROVIDED (NRC# 1334340) ON 4/25/2022. THE SECTION OF PIPE WAS BLOWN FLAT AT APPROXIMATELY 3:00PM ON 4/23/2022. THE "WELD PLUS FITTING" WAS SENT TO A LAB TO DETERMINE THE EXACT CAUSE AND LOCATION OF THE LEAK; RESULTS FROM THE LAB ARE PENDING. A 115' REPLACEMENT WAS COMPLETED AND THE PIPELINE WAS RETURNED TO SERVICE ON 5-7-2022 AT 10AM. A SUPPLEMENTAL REPORT WILL BE FILED ONCE RESULTS FROM THE LAB HAVE BEEN RECEIVED. SUPPLEMENTAL REPORT 12/7/2022: UPDATED PART G AND PART H WITH THE INFORMATION BELOW: LAB ANALYSIS IDENTIFIED THE LEAK AT THE DOWNSTREAM END OF THE WELD+ENDS COUPLER COINCIDING WITH THE CLAMP SCREW OVER PASS. THE LEAK COINCIDED WITH AN AREA OF UNDERCUT THAT CONNECTED TO THE FEMALE PORTION OF THE CLAMP SCREW ASSEMBLY THROUGH A TIGHT CRACK PATH.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220057 | 36716 | 2022-06-01 17:48 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2022-05-02 19:03 | 2022 | CENTRAL | YES | 43.1568 | -93.4297 | 1335257 | 2022-05-05 17:13 | 1335325 | NATURAL GAS |  | 10 | 300 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-05-03 02:00 | 2022-05-05 14:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-05-03 02:00 | VALVE CLOSURE |  | 2022-05-03 02:00 | 0 | 2022-05-02 19:03 | 2022-05-02 20:00 | ONSHORE | IA | 50428 | CLEAR LAKE | CERRO GORDO | MILEPOST | 4 | MASON CITY BRANCH LINE | IAB72001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1931 | 1931 | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 166 |  | NO | NO |  |  | NO |  |  | 250 | 250 | 1461 | 1461 | 49 | 49 | 23000 | 23000 | 107000 | 107000 | 5000 | 5000 | NDT | 4.87 | 136760 | 60343.8084276049560914186046511627906977 | 136760 | 0 | 0 | 0 | 0 | NO |  |  |  | 398 | 2 | 447 | 192.619(C) |  | 1931-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 32831 | NO |  | YES |  | YES |  | YES | DRESSER COUPLED PIPE | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | THREADED FITTING | [6 empty] | YES | [163 empty] | YES | [11 empty] | JOHN GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 402-398-7494 |  | GARY KRICHAU | gary.krichau@nngco.com | 402-398-7274 | TOM CORRELL | VP PIPELINE SAFETY AND RIST | 402-398-7715 | thomas.correll@nngco.com | BLACK HILLS ENERGY, THE LOCAL DISTRIBUTION OPERATOR, DISCOVERED SOME FROST IN THE GROUND AT THE FARM TAP LOCATED ON THE MASON CITY (IAB72001) 10-INCH BRANCH LINE NEAR MP 4.16. THIS VERY MINOR GRADE 3 TYPE LEAK TOOK 3 DAYS TO REPAIR. FIRST OF ALL, THE FARM TAP AND EXCAVATION COULD NOT BE MADE SAFE ENOUGH FOR EMPLOYEES TO ENTER; AND SECOND, NORTHERN CONTINUED TO PROVIDE SERVICE TO MASON CITY, VENTURA, AND 6 FARM TAPS. ULTIMATELY, THE LINE WAS COMPLETELY BLOWN DOWN SO REPAIRS COULD BE MADE. THE CONTRACTOR AND COMPANY PERSONNEL WERE ON SITE AROUND THE CLOCK DURING THE ENTIRE REPAIR. THE LEAK WAS DUE TO THREAD FAILURE BELOW THE FARM TAP ROOT VALVE. ULTIMATELY, THE OLD TAP WAS CUT OFF AND CONTAINED IN A TYPE B PRESSURE CONTAINING SLEEVE. A NEW TAP WITH A FULL ENCIRCLEMENT SLEEVE WAS COMPLETED AND THE FARM TAP RE-BUILT. THE NRC WAS NOTIFIED THAT THIS WOULD NOT TURN INTO A REPORTABLE INCIDENT. THAT WAS BEFORE WE ACCUMULATED ALL THE COSTS OF REPAIR FOR THIS TINY LEAK. A NOTE WAS SENT TO THE INFORMATION RESOURCES OFFICER THAT NORTHERN WOULD BE REPORTING AN INCIDENT.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220058 | 36776 | 2022-06-02 14:52 | SUPPLEMENTAL FINAL | 31711 | SOUTHERN STAR CENTRAL GAS PIPELINE, INC | 4700 STATE ROUTE 56; BOX 20010 | OWENSBORO | KY | 42301 | 2022-05-04 06:53 | 2022 | CENTRAL | YES | 38.47 | -96.2818 | 1335105 | 2022-05-04 07:44 | 1335197 | NATURAL GAS |  | 0 | 500 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-05-04 07:00 | 2022-05-06 09:54 |  | YES | OPERATOR | 2022-05-04 06:57 | NO | [11 empty] | 0 | 2022-05-04 06:53 | 2022-05-04 06:53 | ONSHORE | KS | 66801 | Not Within a Municipality | LYON | NOT APPLICABLE |  | AMERICUS COMPRESSOR STATION | AMERICUS COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | AUXILIARY ROOM AND EQUIPMENT | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | AUXILIARY ROOM AND EQUIPMENT | OTHER | [8 empty] | INTENTIONAL CONTROLLED RELEASE DUE TO ACTIVATION OF ESD | CLASS 1 LOCATION | NO |  | 538 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 3325 | 3325 | 0 | 0 | 1000000 | 1000000 | 60000 | 60000 | 0 | 0 |  | 6.65 | 1063325 | 469098.265400067451275 | 1063325 | 0 | 0 | 0 | 0 | NO |  |  |  | 800 | 100000 | 900 | 192.619(C) |  | 1970-01-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO OPERATIONAL CHANGES MADE BY CONTROLLERS THAT WOULD HAVE INITIATED THE INCIDENT AND THERE WERE NO ALARMS ASSOCIATED WITH THIS EVENT. | [12 empty] | YES | 1 | 1 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | ERIC GLAHN | PIPELINE COMPLIANCE ENGINEER | eric.glahn@southernstar.com | 2702310561 | 2708525016 | CRAIG THOMAS | craig.thomas@southernstar.com | 2703138424 | SHAWN PATTERSON | VP AND CHIEF OPERATIONS OFFICER | 2708524670 | shawn.patterson@southernstar.com | ON 5/4/2022 AT 6:53 AM CDT, SOUTHERN STAR CENTRAL GAS PIPELINE (SSCGP) OPERATOR EMPLOYEE ARRIVED AT THE SSCGP AMERICUS COMPRESSOR STATION IN LYON COUNTY, KS. THE OPERATOR EMPLOYEE NOTICED SMOKE COMING FROM THE COMPRESSOR STATION BUILDING AND NOTIFIED HIS IMMEDIATE SUPERVISOR AT 6:55 AM. A CALL WAS PLACED TO GAS CONTROL AT 6:56 AM TO NOTIFY OF THE SITUATION. A CALL WAS PLACED TO 911 AT 6:57 AM. THE STATION WAS MANUALLY ESD AT 7:00 AM. THE LOCAL FIRE DEPARTMENT ARRIVED ON SCENE AND HAD THE FIRE EXTINGUISHED BY 7:35 AM. THE COMPRESSOR STATION WAS RESTARTED ON 5/6/2022 AT 9:54 AM. BECAUSE OF THE EXTENT OF THE DAMAGES, A PROJECT IS BEING PLANNED REPLACE THE AUXILIARY ROOM AND AFFECTED EQUIPMENT. THE ONLY RELEASE OF NATURAL GAS WAS FROM THE ESD OF THE STATION AND THERE WAS NO GAS IGNITION. WHILE THE FIRE MOST LIKELY STARTED IN THE AUXILIARY/CONTROL ROOM PORTION OF THE BUILDING, IDENTIFYING THE EXACT CAUSE OF THE FIRE WAS NOT POSSIBLE GIVEN THE STATE OF DESTRUCTION AND COPIOUS AMOUNTS OF DEBRIS.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220059 | 37659 | 2022-06-09 15:01 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2022-05-12 05:55 | 2022 | CENTRAL | YES | 28.8595 | -96.577 | 1335788 | 2022-05-12 09:01 | 1335798, 1336002 | NATURAL GAS |  | 6700 | 4100 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | NORMAL OPERATION |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-05-12 07:08 | VALVE CLOSURE |  | 2022-05-12 07:07 | 0 | 2022-05-12 05:55 | 2022-05-12 06:30 | ONSHORE | TX | 77995 | EDNA | JACKSON | MILEPOST | 257+78 | TEXAS CITY EXTENSION | 15 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 40 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | CHECK-VALVE CAP FAILED | [5 empty] | CLASS 1 LOCATION | NO |  | 348 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 25912 | 25912 | 42344 | 42344 | 5000 | 5000 | 0 | 0 | 0 | 0 |  | 6.32 | 73256 | 41421.0443127305955085182724252491694352 | 73256 | 0 | 0 | 0 | 0 | NO |  |  |  | 637 | 3800 | 945 | 192.619(A)(1) |  | 2014-03-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 42240 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS AN EQUIPMENT FAILURE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | CORROSION OF BOLTS SECURING THE CHECK VALVE CAP | [161 empty] | AMIT SHAMGAR | SENIOR PIPELINE COMPLIANCE SPECIALIST | ashamgar@eprod.com | 713-381-6741 |  | AMIT SHAMGAR | ashamgar@eprod.com | 713-381-6741 | NHAN TRUONG | SR. MANAGER PIPELINE COMPLIANCE | 713-381-2493 | nvtruong@eprod.com | ON MAY 12TH AT 0555, THE PIPELINE SUPERVISOR SENT OPERATIONS PERSONNEL TO INVESTIGATE A LEAK INDICATION. AT AROUND 0630, A POSSIBLE GAS LEAK WAS VISUALLY IDENTIFIED AND OPERATIONS PROCEEDED TO ISOLATE THE PIPELINE. BY 0707, THE DOWNSTREAM AND UPSTREAM MANUAL VALVES WERE CLOSED, ISOLATING THE PIPELINE. AT 0900, OPERATIONS WAS ABLE TO SAFELY APPROACH THE LEAK SITE AND DETERMINED THE LEAK SIZE AND ORIGIN. BASED ON THE SIZE OF THE LEAK, ENTERPRISE CALCULATED THAT THE RELEASE VOLUME EXCEEDED 3 MMSCF AND THE NRC WAS IMMEDIATELY NOTIFIED. ON MAY 13TH LINE 15 WAS EXCAVATED AND ENTERPRISE CONFIRMED THE RELEASE WAS DUE TO A FAILURE OF A 3RD PARTY CHECK VALVE CAP. THE CHECK VALVE WAS REMOVED AND THE CONNECTION WAS CAPPED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220061 | 37704 | 2022-06-10 18:11 | SUPPLEMENTAL FINAL | 31978 | ATMOS PIPELINE - TEXAS | 5420 LBJ FREEWAY, SUITE 1500 | DALLAS | TX | 75240 | 2022-05-11 11:30 | 2022 | CENTRAL | YES | 32.2752 | -94.3452 | 1335714 | 2022-05-11 13:35 | 1335862 | NATURAL GAS |  | 14334 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-05-11 11:43 | 2022-05-11 11:43 |  | YES | OPERATOR | 2022-05-11 12:14 | NO | [5 empty] | VALVE CLOSURE |  | 2022-05-11 11:43 | OPERATIONAL CONTROL | OPERATIONAL CONTROL ALLOWED SECTION TO BLOW DOWN. |  | 15 | 2022-05-11 11:30 | 2022-05-11 12:54 | ONSHORE | TX | 75631 | Not Within a Municipality | PANOLA | SURVEY STATION NO. | 5658+55 | LINE S2 | LACY TO CARTHAGE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.281 | 60000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 1988 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 235 | 56 |  | CLASS 2 LOCATION | NO |  | 478 |  | NO | NO |  |  | YES | YES |  | 0 | 0 | 0 | 0 | 97553 | 97553 | 387049 | 387049 | 0 | 0 | 0 | 0 |  | 6.8057 | 484602 | 234760.2233346162961103089700996677740864 | 484602 | 0 | 0 | 15 | 1 | NO |  |  |  | 890 | 0 | 1200 | 192.619(A)(2) |  | 1988-12-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED |  | 45059 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VISUAL CONFIRMATION IN THE FIELD INDICATED THERE WAS A RUPTURE. THERE WAS NO CONTROL ROOM ERROR INVOLVED IN THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  |  | YES |  |  | YES | [5 empty] | NO | NO | YES | NO | [168 empty] | YES | YES |  |  | YES |  |  |  | 2017 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION |  | 2008 | FREE SWIMMING | METAL LOSS |  | STANDARD RESOLUTION | [21 empty] | 2017 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | 2008 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BRUCE CAUGHRON | OPERATIONS SUPERVISOR | bruce.caughron@atmosenergy.com | 903-242-4820 |  | BRUCE CAUGHRON | bruce.caughron@atmosenergy.com | 903-242-4820 | JEFF KNIGHTS | SR VP TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | ON MAY 11, 2022, GAS CONTROL NOTICED AN UNANTICIPATED DROP IN PRESSURE ON LINE S2 AT 11:30 AM AND NOTIFIED LOCAL OPERATIONS AT 11:34 AM. UPON NOTIFICATION, OPERATIONS IMMEDIATELY BEGAN TO EVALUATE POTENTIAL CAUSES FOR THE DROP IN PRESSURE AND BEGAN MOBILIZING RESOURCES, WHILE ALSO REACHING OUT TO OFFICIALS ALONG THE SECTIONS OF THE PIPELINE. WITH NO APPARENT OPERATIONAL CAUSE FOR THE PRESSURE DROP, GAS CONTROL TOOK MEASURES CONSISTENT WITH AN ABNORMAL CONDITION AND CLOSED A REMOTE CONTROL VALVE LOCATED AT BUSBY GATE AT 11:43 AM. AFTER DISCUSSIONS WITH LOCAL LAW ENFORCEMENT AT 12:14 PM, ATMOS ENERGY PROCEEDED TO THE LOCATION OF THE INCIDENT AND ARRIVED ONSITE AT 12:54 PM. UPON ARRIVAL, ATMOS ENERGY DISCOVERED A PIPE RUPTURE ADJACENT TO LACY PIGGING STATION. IN ADDITION TO CLOSING THE REMOTE VALVE, LOCAL OPERATIONS CLOSED THE MANUALLY OPERATED VALVE AT THE LACY PIGGING STATION TO FURTHER SEGMENT LINE S2 AND MINIMIZE GAS RELEASE. BASED UPON INFORMATION ATMOS ENERGY RECEIVED FROM LOCAL OFFICIALS, FIRST RESPONDERS CLOSED ROADS AND EVACUATED RESIDENTS IN THE AREA OUT OF AN ABUNDANCE OF CAUTION. ATMOS ENERGY DOES NOT HAVE DETAILS ON THAT EVACUATION BUT HAS ESTIMATED A NUMBER IN RESPONSE TO QUESTION A23. SUPPLEMENTAL: PART A QUESTION 16, THE LINE WAS NO LONGER IN SERVICE AS OF MAY 11, 2022 AT 11:43 AM CST, AND IS BEING ABANDONED. WHILE THIS LINE IS IN THE PROCESS OF BEING REPLACED, ATMOS ENERGY CUSTOMERS ARE BEING SERVED THROUGH OTHER FACILITIES AND NO CUSTOMERS ARE AFFECTED BY THE ABANDONMENT OF THE LINE. FOR THIS REASON, THE RESTART TIME REFLECTED IN THIS QUESTION IS THE SAME TIME THAT THE LINE WAS SHUT DOWN. AFTER THE INCIDENT OCCURRED, ATMOS ENERGY FOLLOWED ITS PROCEDURES AND INSPECTED THE PIPE IN QUESTION. THE METALLURGICAL REPORT RESULTING FROM THE INVESTIGATION CONCLUDED THAT MICROBIOLOGICALLY INFLUENCED CORROSION (MIC) AND CHLORIDE CORROSION WERE THE PRIMARY CORROSION MECHANISMS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220062 | 36778 | 2022-06-20 17:03 | ORIGINAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2022-05-22 18:51 | 2022 | MOUNTAIN | YES | 41.68 | -107.9836 | 1336824 | 2022-05-22 20:43 | 1336701 | NATURAL GAS |  | 22752 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-05-22 19:24 | 2022-05-22 20:05 |  | NO |  |  | NO | [11 empty] | 0 | 2022-05-22 18:44 | 2022-05-22 19:30 | ONSHORE | WY | 82336 | WAMSUTTER | SWEETWATER | NOT APPLICABLE |  | WAMSUTTER CS | WAMSUTTER CS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | VENT VALVE OPENED. | [5 empty] | CLASS 1 LOCATION | NO |  | 549 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 178603 | 178603 | 300 | 300 | 1200 | 1200 | 0 | 0 |  | 7.85 | 180103 | 117851.4186307887897691029900332225913621 | 180103 | 0 | 0 | 0 | 0 | NO |  |  |  | 794 | 185000 | 845 | 192.619(A)(3) |  | 1970-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DEEMED INDEPENDENT FROM CONTROLLER(S) ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ESD PNEUMATIC SWITCH FAILED DUE TO DEBRIS ACCUMULATION | [161 empty] | JORGE LOPEZ |  | jorge_lopez@kindermorgan.com | 7134204675 |  |  |  |  | JAIME HERNANDEZ |  | 17133699443 | jaime_hernandez@kindermorgan.com | ON MAY 22, 2022 AT 18:44, COLORADO INTERSTATE GAS CO (CIG) GAS CONTROL RECEIVED AN ALARM INDICATING THAT VENT VALVE VO-26 AT THE WAMSUTTER COMPRESSOR STATION (CS) OPENED. CONSEQUENTLY, GAS CONTROL CONTACTED OPERATIONS PERSONAL REGARDING THE ALARM. AT 19:30, CIG OPERATOR ARRIVED ON SITE AND CONFIRMED DISCOVERY OF THE LEAK. AT 19:34, CIG OPERATOR MANUALLY CLOSED THE VENT VALVE VO-26 AND COMMUNICATED THE DETAILS OF THE EVENT TO HIS SUPERVISOR. CIG INITIATED THE EMERGENCY RESPONSE LINE (ERL) AND DURING THE CALL, THE EVENT WAS DEEMED REPORTABLE. THE ROOT CAUSE INVESTIGATION CONCLUDED THAT THE SUPPLY SIDE OF THE GAS PNEUMATIC ESD SWITCH ON VENT VALVE VO-26, ACCUMULATED DEBRIS ALLOWING THE VALVE TO OPEN INADVERTENTLY. CIG OPERATIONS REPLACED THE SWITCH AND TESTED THE VALVE FOR PROPER OPERATION. THE STATION WAS RETURNED TO SERVICE THE SAME DAY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220063 | 37364 | 2022-06-21 13:42 | SUPPLEMENTAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-05-25 11:56 | 2022 | CENTRAL | YES | 35.2215 | -94.3898 | 1336943 | 2022-05-25 11:56 | 1337137 | NATURAL GAS |  | 1050 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-05-24 06:30 | 2022-05-27 07:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-05-24 06:30 | VALVE CLOSURE |  | 2022-05-24 06:30 | 0 | 2022-05-24 07:30 | 2022-05-24 07:30 | ONSHORE | AR | 72916 | Not Within a Municipality | SEBASTIAN | SURVEY STATION NO. | 317+87 | OT-13 | BONANZA COMPRESSOR, OT-13 TO LINE O | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 | NO | 0.188 | 42000 | X-42 | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1964 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | SECTION OF PIPE WAS EJECTED DUE TO RUPTURE. ORIGIN AND INTERACTION WITH SEAM UNKNOW AT THIS TIME. WILL UPDATE AFTER LAB ANALYSIS. | 44.5 |  |  | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 500 | 500 | 0 | 0 | 8400 | 8400 | 95000 | 95000 | 200000 | 200000 | 31850 | 31850 | LAB COST FOR FAILURE ANALYSIS REPORT. | 8 | 335750 | 149925.9106321191796360465116279069767442 | 335750 | 0 | 0 | 0 | 0 | NO |  |  |  | 740 | 6427 | 899 | 192.619(A)(2) |  | 2012-03-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | CHECK VALVE | 34792 | NO | [5 empty] | YES | NO LAUNCHERS OR RECEIVERS INSTALLED ON PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | NOTIFIED BY 3RD PARTY PRODUCER OF A LOW FLOW. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [9 empty] | YES |  |  | YES | YES | 2003 | NO | YES | YES | YES |  |  | 2022 | 2018 |  |  | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [13 empty] | YES | [49 empty] | LEVI CROSS | SR. SPECIALIST - DOT COMPLIANCE | levi.cross@energytransfer.com | 318-347-9238 |  | DANNY BRADLEY | daniel.bradley@energytransfer.com | 479-221-7202 | JIMMY CROSS | SR. MANAGER - REGULATORY COMPLIANCE | 318-426-2515 | jimmy.cross@energytransfer.com | ON 5/24/2022 AT APPROXIMATELY 3:30AM, THE COMPANY WAS NOTIFIED BY A PRODUCER OF A LOW PRESSURE FROM AN INPUT TIED TO OT-13. ASSUMING THERE WAS A LEAK, PERSONNEL WERE DISPATCHED BY MANAGEMENT TO ISOLATE THE LINE AND LOCATE ANY POSSIBLE ISSUES. THREE VALVES AND A CHECK VALVE WERE UTILIZED TO ISOLATE THE SECTION WITH THE FINAL VALVE BEING CLOSED AT 6:30AM. AT 7:30AM A RUPTURE WAS FOUND IN A RURAL AREA APPROXIMATELY 1350FT SOUTH OF BEAR CREEK LOOP RD. NEAR BONANZA, ARKANSAS. INTERNAL INCIDENT COMMUNICATIONS WERE MADE, AND THE EVENT WAS DETERMINED TO BE NON-REPORTABLE DUE TO ESTIMATES MADE BY MANAGEMENT AND ENGINEERING SUPPORT FOR THE COST OF REPAIR/CLEAN-UP AND RELEASE VOLUME. AN ENVIRONMENTAL CLEAN-UP CONTRACTOR WAS DISPATCHED TO THE SITE AND ASSESSED ACCESS TO THE LOCATION, TERRAIN, AND THE TIMELINE FOR THE CLEAN-UP. COST ESTIMATES BASED ON PRIOR COMPANY EXPERIENCE REQUIRED SUBSTANTIAL ADJUSTMENTS AFTER INPUT FROM CONTRACTOR. UPON RECEIVING THE UPDATED INFORMATION, IT WAS DETERMINED THAT THE COST OF REPAIR/CLEAN-UP WOULD EXCEED $122K AND AN IMMEDIATE REPORT WAS MADE TO THE NRC ON 5/25 AT 10:56AM. A 44.5IN SECTION OF PIPE WAS EJECTED DUE TO THE RUPTURE AND THE DAMAGED PIECE WAS COLLECTED AND SENT TO THE LAB FOR FAILURE ANALYSIS ON 5/28. THE LAB HAS ESTIMATED THAT THE FAILURE ANALYSIS REPORT WILL BE COMPLETED BY THE WEEK OF 6/27. THE RUPTURE WAS REMEDIATED BY REPLACEMENT ON 5/26 AND RETURNED TO PARTIAL SERVICE ON 5/27 AT 3:30PM. OT-13 WILL REMAIN AT (200PSI) TO SUPPORT A LOCAL DISTRIBUTION COMPANY (16-20 CUSTOMERS) WITH A RETURN TO NORMAL OPERATING PRESSURE PENDING THE OUTCOME OF FAILURE ANALYSIS AND ADDITIONAL INTEGRITY ASSESSMENT ACTIONS. SUPPLEMENTAL: LAB RESULTS FROM THE INITIAL FAILURE WERE RECEIVED ON 7/18 AND CONCLUDED THE RUPTURED OCCURRED DUE TO EXTERNAL CORROSION. OPERATIONS MANAGEMENT DECIDED TO PRESSURE TEST OT-13 AND MODIFY TO MAKE THE LINE PIGGABLE. DURING A PRESSURE TEST ON 8/23, A SECTION OF THE LINE FAILED AT (35.174671, -94.388078), APPROXIMATELY 3.2 MILES SOUTH OF THE INITIAL FAILURE. AFTER REPAIRS WERE MADE, A SUCCESSFUL PRESSURE TEST WAS COMPLETED ON 9/14. OT-13 WAS RETURNED TO NORMAL OPERATION AT 750PSI ON 9/30. LAB RESULTS FROM THE PRESSURE TEST FAILURE WERE RECEIVED ON 11/11 AND CONCLUDED THAT THE RUPTURE OCCURRED DUE TO EXTERNAL CORROSION.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220064 | 37353 | 2022-06-23 11:13 | SUPPLEMENTAL FINAL | 31130 | DCP MIDSTREAM | 6900 E. LAYTON AVE. SUITE 900 | DENVER | CO | 80237-3658 | 2022-05-25 20:30 | 2022 | CENTRAL | NO | 32.4875 | -102.9412 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 4184 | 0 | 4 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE ISOLATED PRIOR TO INCIDENT FOR UNRELATED MAINTENANCE ACTIVITIES. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | PIPELINE SEGMENT ISOLATED PRIOR TO INCIDENT FOR UNRELATED MAINTENANCE. |  | OPERATIONAL CONTROL | PIPELINE SEGMENT ISOLATED PRIOR TO INCIDENT FOR UNRELATED MAINTENANCE. |  | 0 | 2022-05-25 20:30 | 2022-05-26 14:12 | ONSHORE | TX | 79714 | Not Within a Municipality | ANDREWS | NOT APPLICABLE |  | FULLERTON | FL | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 | NO | 0.25 | 52000 | API-5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 2011 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 24 | 12 |  | CLASS 1 LOCATION | NO |  | 339 |  | NO | NO |  |  | NO |  |  | 2500 | 2500 | 0 | 0 | 8368 | 8368 | 30000 | 30000 | 0 | 0 | 15000 | 15000 | METALLURGICAL EXAMINATION | 2 | 55868 | 26445.8120126306128986710963455149501661 | 55868 | 0 | 0 | 0 | 0 | NO |  |  |  | 627 | 0 | 1440 | 192.619(A)(2) |  | 2011-03-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 12460 | YES | [7 empty] | YES | YES | [5 empty] | TYPE C GATHERING | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | (N/A) PIPELINE IS NOT UNDER CONTROL ROOM MANAGEMENT | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES | [5 empty] | YES | [6 empty] | YES | THE CORROSION AND FRACTURE OCCURED AT TOP OF PIPE AND COINCIDED WITH THE ERW SEAM WELD; HOWEVER, THERE WAS NO PREFERENTIAL NATURE OF THE IDENTIFIED CORROSION AND THE ERW SEAM BONDLINE. | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | RUSSELL NICHOLS | SR. PIPELINE COMPLIANCE SPECIALIST | rnichols@dcpmidstream.com | 4325571637 |  | RUSSELL NICHOLS | rnichols@dcpmidstream.com | 4325571637 | MIKE PAVLAK | MANAGER PIPELINE COMPLIANCE | 9703970732 | mpavlak@dcpmidstream.com | PIPELINE SHUT IN UNDER PRESSURE DUE TO PLANT TURNAROUND. THE CALCULATED VOLUME OF GAS RELEASED WAS CONFIRMED REPORTABLE ON 5/26/2022 AT 18:56 AND WAS REPORTED TO THE TEXAS RRC/ INCIDENT # 2624. PIPE SENT FOR METALLURGICAL EVALUATION AND FINAL REPORT RECEIVED ON 10/21/2022. METALLURGICAL REPORT INDICATES INTERNAL CORROSION IN ENVIRONMENT CONTAINING H2S. PIPELINE RETURNED TO SERVICE WITH A REDUCED OPERATING PRESSURE BASED ON CALCULATED SAFETY MARGIN FROM FAILURE PRESSURE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220066 | 36846 | 2022-07-12 13:28 | ORIGINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-06-13 16:25 | 2022 | PACIFIC | YES | 36.6036 | -120.1244 | 1338665 | 2022-06-13 19:41 | 1338875 | NATURAL GAS |  | 1137.5 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-06-13 15:55 | 2022-06-14 17:25 |  | YES | OPERATOR | 2022-06-13 14:19 | NO | [5 empty] | VALVE CLOSURE |  | 2022-06-13 15:35 | VALVE CLOSURE |  | 2022-06-13 15:35 | 0 | 2022-06-13 15:01 | 2022-06-13 14:36 | ONSHORE | CA | 93660 | SAN JOAQUIN | FRESNO | MILEPOST | 3.55 | L-111A | MILE POINT: 3.55 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 | NO | 0.148 | UNKNOWN | APL5BL | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | POLYPROPYLENE | YES | [26 empty] | 1968 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 6 | 2 | [7 empty] | CLASS 1 LOCATION | NO |  | 79 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 3413 | 3413 | 181924 | 181924 | 72141 | 72141 | 40589 | 40589 | OTHER COSTS | 3 | 298067 | 132229.4866692546140602591362126245847176 | 298067 | 0 | 0 | 1190 | 6 | NO |  |  |  | 563 | 560 | 650 | 192.619(A)(1) |  | 1989-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | NO | MANUAL | MANUAL | 9187 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DIG-IN INCIDENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO | [10 empty] | YES | CONTRACTOR | BULLDOZER | GRADING | YES | X120401214 | USA NORTH 811 | FACILITY OWNER | YES | YES | YES | 26 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 5102987063 |  |  |  |  | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-328-5776 | gsr8@pge.com | ON JUNE 13, 2022, AT APPROXIMATE 16:25 HOURS PG&E INCIDENT ON-CALL PERSONNEL CONFIRMED THAT A DIG-IN IN SAN JOAQUIN, CA REACHED REPORTABLE INCIDENT CRITERIA. A BULLDOZER WITH A RIPPER ATTACHMENT STRUCK A 4 INCH STEEL TRANSMISSION LINE RESULTING IN A RELEASE OF GAS. PG&E PERSONNEL RESPONDED AND STOPPED GAS FLOW AROUND 15:55 HOURS. AN ESTIMATED 1,200 CUSTOMERS WERE IMPACTED. FIRE DEPARTMENT PRESENCE WAS REPORTED ON SITE. THERE WERE NO INJURIES OR FATALITIES, NO MEDIA WAS REPORTED. THIS INCIDENT WAS REPORTED TO THE DOT (#1338665/1338875) AND CPUC (220613-15187) ONCE ESTIMATED DAMAGE WAS CONFIRMED TO BE AT LEAST $122,000.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220067 | 37317 | 2022-07-13 11:17 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-06-02 07:30 | 2022 | CENTRAL | YES | 31.7864 | -103.0614 | 1338703 | 2022-06-14 08:50 | 1338920 | NATURAL GAS |  | 1667 | 0 | 0.28 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-06-02 07:30 | 2022-07-09 12:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-06-02 08:00 | VALVE CLOSURE |  | 2022-06-02 08:30 | 0 | 2022-06-02 07:30 | 2022-06-02 07:30 | ONSHORE | TX | 79745 | KERMIT | WINKLER | MILEPOST | 20+00 | WTG BOOSTER 10IN TX-WINKLER | 99991001 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.25 | 42000 | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 2010 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | COMPLETE BLOWOUT/SEPARATION |  |  |  | CLASS 1 LOCATION | NO |  | 199 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 14153 | 14153 | 500000 | 500000 | 0 | 0 | 0 | 0 |  | 8.49 | 514153 | 229867.2872285999119601328903654485049834 | 514153 | 0 | 0 | 0 | 0 | NO |  |  |  | 552 | 9 | 720 | 192.619(A)(1) |  | 2010-10-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 61248 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | YES | YES | YES | YES | YES | OTHER | NOTIFICATION FROM THIRD PARTY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOLS. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION | [5 empty] | YES | WALL THINNING DUE TO INTERNAL CORROSION |  | YES | [6 empty] | YES | TOP 3RD OF PIPE | YES | NO | YES | YES | [168 empty] | YES | YES |  |  | YES |  |  |  | 2019 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2012 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2019 | FREE SWIMMING | STANDARD RESOLUTION |  | NO CUPS | 2012 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [14 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | CHRIS PALAFOX | DOT COMPLIANCE SPECIALIST | chris.palafox@energytransfer.com | 7139894464 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON JUNE 2, 2022, THERE WAS A NATURAL GAS RELEASE ON THE 99991001 WTG BOOSTER 10IN TX-WINKLER_BLK B5 SUR 3,8,13,14,17,24, A TYPE C GATHERING LINE LOCATED 4.5 MILES SOUTH OF KERMIT, TX IN WINKLER COUNTY. THE LINE SEPARATED AND RELEASED 1,667 THOUSAND CUBIC FEET OF NATURAL FIELD GAS DUE TO INTERNAL CORROSION. ON JUNE 14, 2022, IT WAS DETERMINED THAT THE DAMAGE AND REPAIRS WAS GOING TO GO OVER THE $129,300.00 REPORTING CRITERIA. 2000 FEET OF PIPE WILL BE REPLACED WITH NEW PIPE AND TO PREVENT THIS FROM OCCURRING IN THE FUTURE, OPERATIONS WILL HAVE MEASUREMENT CONDUCT MONTHLY CHECKS ON THE THREE MONITORS FEEDING THE SYSTEM AND LOWER THE PPM HIGH AND HIGH HIGH ALARM SET POINTS. THE AFFECTED PORTION OF THE PIPE WAS SENT TO THE LAB, WAITING FOR RESULTS. A SUPPLEMENTAL REPORT WILL BE SUBMITTED WITH LAB RESULT FINDINGS. ON JULY 9, 2022, THE PIPELINE REPLACEMENT WAS COMPLETE AND AT 12:00 THE PIPELINE WAS PUT BACK IN SERVICE. ON NOVEMBER 2, 2022, THE RESULTS OF THE LAB WERE RECEIVED, AND METALLURGICAL ANALYSIS INDICATED PIPE WALL LOSS WAS DUE TO INTERNAL CORROSION. TO PREVENT THIS FROM OCCURRING IN THE FUTURE, OPERATIONS WILL NOW BE PIGGING THIS LINE TWICE A WEEK, WE HAVE WILL HAVE OUR CHEMICAL COMPANY CHECK COUPONS FOR CHEMICAL RESIDUE QUARTERLY BASIS. THE CHEMICAL COMPANY WILL ALSO BE RUNNING BACTERIA TESTS AND ADJUSTING CHEMICAL USAGE ACCORDINGLY. THIS LINE HAS ALSO BEEN BUDGED FOR AN ILI TOOL RUN IN 2023.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220068 | 37299 | 2022-07-14 11:39 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-06-17 05:03 | 2022 | CENTRAL | YES | 40.4016 | -74.909 | 1339011 | 2022-06-17 08:10 | 1339163 | NATURAL GAS |  | 10279.3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-06-17 05:12 | 2022-06-17 17:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-06-17 08:00 | NO | [11 empty] | 0 | 2022-06-17 05:03 | 2022-06-17 05:03 | ONSHORE | NJ | 08530 | Not Within a Municipality | HUNTERDON | MILEPOST | 1436 | TEXAS EASTERN TRANSMISSION, LP LAMBERTVILLE CS | LAMT | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1952 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE OPENED DUE TO OVER PRESSURE. | CLASS 1 LOCATION | YES | METHOD2 | 354 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 71338 | 71338 | 0 | 0 | 2000 | 2000 | 0 | 0 |  | 6.94 | 73338 | 47690.4795475854959933554817275747508306 | 73338 | 0 | 0 | 0 | 0 | NO |  |  |  | 731 | 54800 | 656 | 192.619(A)(1) |  | 1952-01-01 | NO | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [204 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  | YES |  |  |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | MICHAEL MCGRATH |  | michael.mcgrath@enbridge.com | 6128056542 |  |  |  |  | NATHAN ATANU |  | 17136275008 | nathan.atanu@enbridge.com | ON JUNE 17, 2022, AT APPROXIMATELY 2:14 A.M. CDT THE LAHASKA REGULATING STATION (MR 78127) BEGAN DRIFTING OPEN. THIS EVENTUALLY RESULTED IN THE PRESSURE EXCEEDING THE DOWNSTREAM MAOP. AT 5:01 A.M. CDT RELIEF VALVES BEGAN OPENING APPROXIMATELY 6 MILES DOWNSTREAM AT THE LAMBERTVILLE COMPRESSOR STATION (CS). THE VOLUME RELEASED EXCEEDED THE 3 MMCF PHMSA REPORTING THRESHOLD. THE UPSTREAM EAGLE CS SERVES TWO PARALLEL LINES, LINE 1 (20-INCH) AND LINE 2 (36 & 20-INCH). THE MAOP OF LINE 1 IS 656 P.S.I.G. AND LINE 2 IS 1000 P.S.I.G. AT THE DISCHARGE OF EAGLE CS. APPROXIMATELY 6 MILES UPSTREAM OF THE LAMBERTVILLE CS THE MAOP OF LINE 2 IS LOWERED TO 656 P.S.I.G. AT MR 78127. THE CONTROL VALVES AT MR 78127 HAD BEEN SHUT-OFF ON THE PREVIOUS MONDAY, JUNE 13, 2022 FOR PLANNED MAINTENANCE WORK. PRELIMINARY INVESTIGATION INDICATES THE CONTROL SUPPLY GAS WAS SHUT OFF DURING THE MAINTENANCE WORK ON THURSDAY JUNE 16, 2022 AND SUPPLY GAS GRADUALLY BLED-OFF OVERNIGHT WHICH ALLOWED THE CONTROL VALVES TO DRIFT OPEN. PRESSURES ON LINE 2 DOWNSTREAM OF MR 78127 REACHED 731 P.S.I.G. OR 111% OF THE 656 P.S.I.G. MAOP (66.7% SMYS) AT LAMBERTVILLE COMPRESSOR STATION. PRESSURES ON SEGMENT OF LINE 1 ALSO EXCEEDED MAOP, BUT LESS THAN ALLOWABLE BUILDUP. THE EFFECTED SEGMENTS WERE LEAK SURVEYED WITH LEAK DETECTION EQUIPMENT. IN ADDITION, A REVIEW OF ILI DATA CONFIRMED THERE WERE NO ACTIONABLE ANOMALIES AT THE ELEVATED PRESSURES IN THE AFFECTED SEGMENTS. THE EVENT REMAINS UNDER INVESTIGATION. OCTOBER 11, 2022 PART E11 REGARDING THE INVESTIGATION INTO THE CONTROL ROOMS ACTIONS WAS UPDATED. PART G APPARENT CAUSE WAS UPDATED PART H - THE INVESTIGATION CONCLUDED THAT CONTROL GAS VALVES WERE LEFT IN THE WRONG POSITION DURING MAINTENANCE ACTIVITY. PROCEDURES WILL BE UPDATED, AND TRAINING WILL BE PROVIDED TO PREVENT RECURRENCE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220069 | 37022 | 2022-07-15 13:38 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-06-18 10:25 | 2022 | CENTRAL | YES | 28.3162 | -91.9083 | 1339148 | 2022-06-18 13:25 | 1339250 | NATURAL GAS |  | 24.9 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-06-18 13:00 | 2022-08-23 16:39 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-06-18 14:47 | NO | [5 empty] | VALVE CLOSURE |  | 2022-06-18 13:00 | VALVE CLOSURE |  | 2022-06-18 13:00 | 0 | 2022-06-22 10:30 | 2022-06-18 13:00 | OFFSHORE | [6 empty] | SEA ROBIN - WEST | LINE 716 | [20 empty] | 220 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH MARSH ISLAND | 128A | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | VALVE | [31 empty] | MAINLINE | PLUG |  | GROVE |  |  |  | 2007 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 598 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 184 | 184 | 500000 | 500000 | 20000 | 20000 | 0 | 0 |  | 7.37 | 520184 | 229524.8152625944067774086378737541528239 | 520184 | 0 | 0 | 0 | 0 | NO |  |  |  | 735 | 48 | 1306 | 192.619(A)(1) |  | 2007-04-02 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 252912 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS TOO SMALL FOR SCADA TO DETECT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | OTHER | THREADED PLUG ON 24-INCH SUBSEA VALVE | [18 empty] | YES | PLUG LEAK | [161 empty] | PEGGY WEST | SR. REGULATORY ANALYST | peggy.west@energytransfer.com | 4092023088 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | AT APPROXIMATELY 10:25 AM ON 06/18/22, GAS CONTROL RECEIVED A CALL FROM A 3RD PART REPORTING BUBBLES IN THE AREA NEAR THE SEA ROBIN 716 PIPELINE IN SMI BLOCK 128A. THE INITIAL NRC NOTIFICATION (1339148) WAS CONDUCTED ON 6/18/22 AT 1:25 PM. SEA ROBIN DID NOT TAKE OWNERSHIP AT THIS TIME DUE TO THE UNCERTAINTY OF THE LEAK LOCATION BECAUSE OF THE INTERMITTENT NATURE OF THE RELEASE. THE 48-HOUR FOLLOW-UP NRC NOTIFICATION (1339250) WAS CONDUCTED ON 6/20/22 AT 10:42 AM. OVERFLIGHTS WERE CONDUCTED UNTIL WE WERE ABLE TO GET A MESOTECH AND SURVEY TECH ON A CREW BOAT TO BEGIN INVESTIGATION. THE SONAR EQUIPMENT DID DETECT A LEAK ON THE 24-INCH SEGMENT 15532 ON 6/22/22 AT APPROXIMATELY 10:30 AM. AN UPDATE WAS MADE TO THE NRC, (1339470) ON 6/22/22 AT 11:46 AM STATING THAT SEA ROBIN WAS TAKING OWNERSHIP OF THE LEAK. A DSV CREW WAS DISPATCHED TO THE LEAK SITE ON 6/24/22 AND ARRIVED ON 6/25/22. THE CONTRACTOR LOCATED THE LEAK COMING FROM A 1-INCH PLUG ON THE BODY OF THE 24-INCH SUBSEA BALL VALVE ON 6/27/22. DSV CREW COULD NOT MAKE REPAIRS ON THE VALVE UNTIL THE PIPELINE WAS DEPRESSURIZED. THE PROCESS OF DEPRESSURIZING THE PIPELINE IS ONGOING AND SEA ROBIN OPERATIONS IS WAITING ON THE AVAILABILITY OF DSV CREW TO MAKE THE REPAIR. A SUPPLEMENTAL REPORT WILL BE FILED ONCE THE REPAIRS HAVE BEEN COMPLETED. THE PLUG WAS REPLACED ON 8/21/22 AND THE LINE WAS PUT BACK IN SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220070 | 37593 | 2022-07-20 07:22 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2022-06-21 10:39 | 2022 | EASTERN | YES | 39.7495 | -77.7233 | 1339347 | 2022-06-21 10:39 | 1339555 | NATURAL GAS |  | 358.58 | 19.4 | 9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE REMAINED IN OPERATION DUE TO LOCAL MARKET DEMAND. PRESSURE REDUCED. |  |  |  | YES | OPERATOR | 2022-06-21 10:39 | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE REDUCTION TO 100PSIG |  | OPERATIONAL CONTROL | PRESSURE REDUCTION TO 100 PSIG |  | 0 | 2022-06-20 17:11 | 2022-06-20 17:11 | ONSHORE | PA | 17225 | GREENCASTLE | FRANKLIN | SURVEY STATION NO. | 23+71 | PIPELINE 1656 | 3010990 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 42 | NO | YES |  |  |  |  | YES | UNCASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 | NO | 0.28 | 24000 | UNKNOWN | OTHER | UNKNOWN SEAM TYPE | UNKNOWN | NONE |  | NO | [26 empty] | 1950 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | NO |  | 64 |  | NO | NO |  |  | NO |  |  | 5000 | 5000 | 158 | 158 | 2919 | 2919 | 984282 | 984282 | 0 | 0 | 0 | 0 |  | 8.14 | 992359 | 438418.3238412972422846511627906976744186 | 992359 | 0 | 0 | 0 | 0 | NO |  |  |  | 165 | 5000 | 175 | 192.619(A)(3) |  | 1957-09-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 9160 | NO |  | YES |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UNNECESSARY DUE TO LOCATION OF LEAK AND SUSPECTED CAUSE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 2002 | NO | YES | YES |  |  |  | 2021 |  |  |  | N/A Bare/Ineffectively Coated Pipe | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [13 empty] | YES | [49 empty] | CHRISTOPHER L. LEGG | US REGULATORY COMPLIANCE PROJECT SPECIALIST | chris_legg@tcenergy.com | 13045454350 |  |  |  |  | PAUL SHAFFER | SENIOR MANAGER - US REGULATORY COMPLIANCE | 304-550-4866 | paul_shaffer@tcenergy.com | PIPELINE 1656 IS A TRANSMISSION PIPELINE THAT IS OPERATED AND MAINTAINED BY COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) WITH AN OPERATOR ID 2616. COLUMBIA HAS IDENTIFIED A LEAK ON PIPELINE 1656 UNDER A TOWNSHIP ROADWAY NEAR THE TOWN OF GREENCASTLE, FRANKLIN COUNTY, PENNSYLVANIA. PIPELINE 1656 IS A 6-INCH DIAMETER, CARBON STEEL, 0.28-INCH WALL THICKNESS, BARE STEEL PIPELINE, WHICH IS CATHODICALLY PROTECTED IN THE AREA OF THE REPORTED LEAK. LINE 1656 HAS A MAXIMUM ALLOWABLE OPERATING PRESSURE OF 175 PSIG AND ITS OPERATING PRESSURE AT THE TIME OF DISCOVERY WAS APPROXIMATELY 165 PSIG. WHILE PERFORMING SCHEDULED CATHODIC PROTECTION SURVEYS, COLUMBIA OPERATIONS DISCOVERED THE PRESENCE OF NATURAL GAS IN A TEST STATION NEAR THE 100 BLOCK OF PENNSINGER ROAD, GREENCASTLE, PA. GAS MIGRATION STUDIES WERE PERFORMED, AND THE LOCAL DISTRIBUTION COMPANY PERFORMED GAS DETECTION SURVEYS WITHIN THE TWO NEARBY HOMES. NO NATURAL GAS WAS FOUND IN OR AT THE FOUNDATIONS OF EITHER HOME. THE LINE PRESSURE WAS REDUCED TO 100 PSIG TO MAINTAIN LOCAL MARKET. BELL HOLES WERE OPENED ON EITHER SIDE OF PENNSINGER ROAD, AND GAS MIGRATION SURVEYS HAVE BEEN PERFORMED TWICE DAILY SINCE DISCOVERY. AS OF JULY 7, 2022, PIPELINE 1656 HAS BEEN BLOW DOWN TO 0 PSIG AND 19 LDC CUSTOMERS HAVE BEEN PLACED ON TEMPORARY BOTTLED COMPRESSED NATURAL GAS (CNG) SERVICE. IN ADDITION, A CNG TANKER HAS BEEN PLACED TO KEEP THE TOWN OF HAGERSTOWN, MD IN SERVICE AS NEEDED. CURRENTLY HAGERSTOWN IS BEING SUPPLIED BY AN ALTERNATIVE SUPPLY. WORK WAS COMPLETED TO REPLACE 232 FEET OF FBE COATED CARBON STEEL PIPE ON JULY 18, 2022. THE PIPELINE HAS BEEN PURGED AND PLACED BACK INTO SERVICE AT 4:49PM EASTERN TIME ON JULY 18, 2022. THE INCIDENT INVESTIGATION REPORT WAS FINALIZED ON JANUARY 17, 2023. THE CAUSAL AND ROOT CAUSE FACTORS OF THIS PROCESS EQUIPMENT FAILURE INDICATE GENERAL EXTERNAL CORROSION LED TO A THROUGH WALL ANOMALY RESULTING IN THE RELEASE OF NATURAL GAS. THE CORROSION CAN LIKELY BE ATTRIBUTED TO INSUFFICIENT CATHODIC PROTECTION AT THE LEAK LOCATION OVER THE LIFE SPAN OF THE PIPE. FOR APPROXIMATELY THE FIRST 20 YEARS OF SERVICE THIS SECTION OF BARE STEEL PIPE OPERATED WITH NO CATHODIC PROTECTION IN PLACE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220071 | 36883 | 2022-07-20 22:04 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-05-19 10:33 | 2022 | CENTRAL | NO | 29.5324 | -96.1443 | 1339517 | 2022-06-22 15:40 | 1339562 | NATURAL GAS |  | 10814 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | UNPLANNED UNIT RELIEF VALVE ACTUATION |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-05-19 10:26 | 2022-05-19 10:44 | ONSHORE | TX | 77442 | Not Within a Municipality | WHARTON | SURVEY STATION NO. | 13+79 | TGP EAST BERNARD CS 17 | STATION 17-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | RELIEF VALVE | [6 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | MALFUNCTIONING PILOT REGULATOR | [5 empty] | CLASS 1 LOCATION | NO |  | 458 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 90838 | 90838 | 0 | 0 | 500 | 500 | 0 | 0 |  | 8.4 | 91338 | 59823.5874948697959252491694352159468439 | 91338 | 0 | 0 | 0 | 0 | NO |  |  |  | 735 | 9566 | 750 | 192.619(A)(1) |  | 1970-06-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DEEMED THE INCIDENT INDEPENDENT OF THE CONTROLLER(S) ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | RELIEF VALVE FAILED DUE TO DEBRIS AND FAILED INTERNAL SOFT GOODS. | [161 empty] | STEPHEN DINES | ENGINEER | stephen_dines@kindermorgan.com | 7193295633 |  | RON WACHOWIAK | ron_wachowiak@kindermorgan.com | 979-232-4145 | JAIME HERNANDEZ | DIRECTOR-ENGINEERING | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON MAY 19, 10:40 PM LOCAL TIME, GAS CONTROL RECEIVED A CALL ABOUT A NOISE COMPLAINT ASSOCIATED WITH TGP'S COMPRESSOR STATION NO. 17 (I.E., CS 17). GAS CONTROL CALLED TGP OPS SPECIALIST WHO ARRIVED ON SITE AT 10:44 PM LOCAL TIME TO INVESTIGATE THE NOISE. UPON ARRIVAL THE OPS SPECIALIST NOTICED THAT RELIEVE VALVE NO. 17-4D WAS VENTING NATURAL GAS. CONSEQUENTLY, THE OPERATIONS SPECIALIST CLOSED THE BLOCK VALVE UNDER THE RELIEF VALVE THEREBY STOPPING THE RELEASE AT 10:52 LOCAL TIME. THIS CALCULATED TO BE 1,828 MCF AND WAS DETERMINED TO BE LESS THAN THE PHMSA 3,000 MCF AND NOT REPORTABLE AT THE TIME. ON JUNE 22, 2022, IT WAS DETERMINED THAT THE TOTAL RELEASE TIME DID NOT INCLUDE THE ACTUAL INITIAL NOTIFICATION WHEN GAS CONTROL RECEIVED THE NOISE COMPLAINT AND THE INITIAL CALCULATED VOLUME UTILIZED THE INCORRECT RELIEF VALVE ORIFICE SIZE. THEREFORE, THE TOTAL TIME OF THE RELEASE CHANGED FROM 8 MINUTES TO 26 MINUTES AND, THE TOTAL RELEASE VOLUME WITH THE REVISED ORIFICE SIZE EXCEEDED THE REPORTING THRESHOLD. THE NEW GAS LOSS VOLUME CHANGED FROM 1,828 MCF TO 10,814 MCF. THE EVENT WAS REPORTED TO THE NRC ON JUNE 22, 2022 AT 15:40 PM LOCAL TIME. THE INVESTIGATION INTO THE RELEASE REVEALED THAT THE RELIEF VALVE FAILED IN THE OPEN POSITION DUE TO DEBRIS AND FAILED SOFT GOODS INTERNAL TO THE PILOT VALVE, WHICH CONTROLS THE RELIEF VALVE. ONCE THE PILOT WAS CLEANED, SERVICED AND REBUILT THE VALVE AND PILOT VALVE WAS SUCCESSFULLY TESTED AND RETURNED TO SERVICE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220072 | 37120 | 2022-07-20 22:20 | SUPPLEMENTAL FINAL | 19580 | TRANSCOLORADO GAS TRANSMISSION COMPANY LLC | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-06-25 09:24 | 2022 | MOUNTAIN | YES | 38.5335 | -108.0765 | 1339759 | 2022-06-25 10:57 | 1339760, 1339850 | NATURAL GAS |  | 24659 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2022-06-25 10:00 | 2022-06-25 10:50 | ONSHORE | CO | 81425 | Not Within a Municipality | MONTROSE | MILEPOST | 00 0715+72 | TRANSCOLORADO GAS - OLATHE COMPRESSOR STATION | TRANSCOLORADOMAINLINE 0080010000 | YES | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | INSTRUMENTATION | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | UNINTENDED VENT RELEASE | [5 empty] | CLASS 1 LOCATION | NO |  | 545 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 152886 | 152886 | 500 | 500 | 500 | 500 | 0 | 0 |  | 6.2 | 153886 | 100756.7264847562031461794019933554817276 | 153886 | 0 | 0 | 0 | 0 | NO |  |  |  | 865 | 185000 | 1287 | 192.619(A)(1) |  | 1974-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER'S ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  |  |  | YES | [6 empty] | YES | YES | LOSS OF COMMUNICATION BETWEEN THE STATION & ESD PLCS AND THE I/O MODULES. FAILURE OF THE ESD I/O MODULE TO "HOLD-LAST STATE" ON THE ESD SIDE-VENT VALVES. | [22 empty] | YES | COMMUNICATION WIRE TERMINATION BLOCKS (POOR CONNECTION/SHIELDING). | [161 empty] | STEPHEN DINES | ENGINEER | stephen_dines@kindermorgan.com | (719) 351-4199 |  | MIKE JOHNSON | mike_johnson2@kindermorgan.com | (505) 632-6042 | JAIME HERNANDEZ | DIRECTOR - ENGINEERING | (713) 369-9443 | jaime_hernandez@kindermorgan.com | ON 6/25 AT 9:12AM, TRANSCOLORADO GAS TRANSMISSION COMPANY LLC'S OLATHE COMPRESSOR STATION LOCATED IN MONTROSE COUNTY, COLORADO EXPERIENCED AN ABNORMAL EVENT WHILE IN STANDBY MODE WITH NO COMPRESSION IN OPERATION AT THE TIME. THE STATION EXPERIENCED A COMMUNICATION FAILURE BETWEEN THE STATION PLC, ESD PLC AND THE I/O MODULE CONTROLLING THE ESD VALVES. THE I/O MODULE CONTROLLING THE ESD VALVES ALSO FAILED TO "HOLD LAST STATE" UPON LOSS OF COMMUNICATION. THIS RESULTED IN THE STATION VENT VALVE OPENING (INSTEAD OF REMAINING CLOSED) AND AN UNPLANNED GAS RELEASE EVENT FOR 112 MINUTES. THE TOTAL VOLUME RELEASED WAS 24,659.50 MCF. THE IMMEDIATE CAUSE OF THE EVENT WAS DETERMINED TO BE THE FAILURE OF THE I/O CONTROLLER DESIGNED TO PROVIDE A "HOLD LAST STATE" COMMAND THAT KEEPS THE STATION VALVES IN THE CURRENT STATE WHEN COMMUNICATIONS ARE LOST. INVESTIGATION REVEALED THAT THERE WERE SHORT LOSSES OF COMMUNICATION PRIOR TO THIS EVENT, BUT THE I/O MODULE "HOLD LAST STATE" SETTING ALWAYS FUNCTIONED AS DESIGNED. ANOTHER CONTRIBUTING CAUSE WAS IDENTIFIED TO BE LOSS OF COMMUNICATION BETWEEN THE STATION & ESD PLCS AND THE I/O MODULES. THE INTERMITTENT LOSS OF COMMUNICATION WAS CAUSED BY POOR CONNECTIONS ON THE COMMUNICATION WIRES AT THE PLCS, I/O MODULES, AND SURGE-SUPPRESSION EQUIPMENT. ALL CONNECTIONS WITH THE COMMUNICATIONS WIRE HAVE BEEN CHECKED AND CORRECTED AS REQUIRED. THERE HAS BEEN NO COMMUNICATIONS FAILURES SINCE. THE I/O MODULE WAS ALSO REPLACED.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220073 | 37186 | 2022-07-26 14:39 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-06-27 10:56 | 2022 | CENTRAL | YES | 31.9036 | -93.7063 | 1339910 | 2022-06-27 11:37 | 1340030 | NATURAL GAS |  | 7640 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-06-27 12:04 | 2022-07-03 00:30 |  | YES | OPERATOR | 2022-06-27 11:19 | YES | 2022-06-27 10:56 | ALLOWED TO BURN OUT |  | 7640 | YES | VALVE CLOSURE |  | 2022-06-27 10:56 | VALVE CLOSURE |  | 2022-06-27 12:04 | 35 | 2022-06-27 11:07 | 2022-06-27 13:10 | ONSHORE | LA | 71052 | MANSFIELD | DESOTO | NOT APPLICABLE |  | COMSTOCK EXT 10-INCH | 20104059 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 60 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 | NO | 0.25 | 52000 | API-5LX | LONGITUDINAL ERW - HIGH FREQUENCY |  | BREDERO SHAW | EPOXY |  | NO | [26 empty] | 2011 | 2010 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 60 | 33 |  | CLASS 1 LOCATION | NO |  | 297 |  | NO | NO |  |  | NO |  |  | 5000 | 5000 | 0 | 0 | 58828 | 58828 | 350000 | 350000 | 10000 | 10000 | 0 | 0 |  | 7.7 | 423828 | 199623.7881984726201162790697674418604651 | 423828 | 0 | 0 | 6 | 0 | NO |  |  |  | 1100 | 100 | 1200 | 192.619(A)(2) |  | 2011-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 61776 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS REPORTED TO GAS CONTROL BY A THIRD PARTY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [5 empty] | YES | [8 empty] | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | ANGELA MORGAN | LEAD SPECIALIST REGULATORY COMPLIANCE | angela.morgan@energytransfer.com | 9032436541 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 7139897077 | chris.kresta@energytransfer.com | ON 6/27/22 AT APPROXIMATELY 10:56, GAS CONTROL RECEIVED A REPORT FROM LANDOWNER OF FIRE AND POSSIBLE RUPTURE IN THE VICINITY OF ENERGY TRANSFER (ET) PIPELINE KNOWN AS 20104059 COMSTOCK EXTENSION 10-INCH. AT 11:07, SCADA INFORMATION INDICATED A LOSS OF PRESSURE AT THE METER CLOSE TO THE LEAK SITE. ENERGY TRANSFER OPERATIONS PERSONNEL WERE NOTIFIED AND ENROUTE TO THE VALVE DOWNSTREAM FROM THE POSSIBLE LEAK SITE. THE SHUT-IN VALVE AT THE PETRO-HUNT WELLSITE HAD ALREADY CLOSED ON LOW PRESSURE. ET PIPELINE TECHNICIAN CLOSED THE DOWNSTREAM VALVE TO ISOLATE THE LOCATION AT APPROXIMATELY 12:04. ET PERSONNEL ARRIVED AT THE RUPTURE SITE AT 13:10 AND CONFIRMED THE FIRE WAS EXTINGUISHED AT 13:17. THE PIPELINE SECTION WAS EXCAVATED AND INSPECTED AND THE INITIAL CAUSE WAS THOUGHT TO BE MATERIAL DEFECT IN THE PIPE BODY. METALLURGICAL ANALYSIS INDICATED STRESS CORROSION CRACKING. THE PIPE SEGMENT AFFECTED BY THE RUPTURE WAS REPLACED. PIPELINE BACK IN SERVICE ON 7/3/2022 AT 0:30. LA STATE POLICE WAS NOTIFIED ON 6/27/2022 AT 11:19. AS A PRECAUTION, EMERGENCY RESPONDERS EVACUATED 35 PERSONS FROM APPROXIMATELY 6 RESIDENTIAL LOCATIONS. ONCE THE FIRE WAS EXTINGUISHED, THE EVACUATED PERSONS WERE ADVISED IT WAS SAFE TO RETURN TO THEIR RESIDENCES. NRC NOTIFICATION (1339910) WAS MADE AT 6/27/2022, 11:32 NRC 48-HOUR REPORT WAS MADE 6/28/2022, 15:38 (1340030).
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220074 | 37259 | 2022-07-28 10:52 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-06-20 09:16 | 2022 | EASTERN | YES | 36.3419 | -79.819 | 1339257 | 2022-06-20 10:00 | 1339379 | NATURAL GAS |  | 3755 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2022-06-20 09:16 | 2022-06-20 09:16 | ONSHORE | NC | 27320 | REIDSVILLE | ROCKINGHAM | NOT APPLICABLE |  | STATION 160 | STATION 160 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2003 | 2002 | CARBON STEEL |  | OTHER | [8 empty] | GAS VENTED THROUGH FUEL GAS BLOW-DOWN VALVE. | CLASS 2 LOCATION | NO |  | 1 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 25572 | 25572 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6.81 | 25572 | 16778.9700996677740863787375415282392027 | 25572 | 0 | 0 | 0 | 0 | NO |  |  |  | 340 | 7069 | 860 | 192.619(A)(1) |  | 2021-02-13 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INVESTIGATION PERFORMED DETERMINED ONE OF THE CONTRIBUTING FACTORS WAS THE LACK OF AN ALARM WHEN THE BLOWDOWN VALVE WAS OUT OF POSITION SUCH THAT THE OPERATOR WOULD NOT HAVE BEEN ABLE TO RECOGNIZE THE VALVE WAS OUT OF POSITION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | UNINTENDED VALVE MOVEMENT | [161 empty] | DIKA ONYEDIRIM | PIPELINE SAFETY ENGINEER | dika.onyedirim@williams.com | 2816608503 |  |  |  |  | JOHN BELL | MANAGER PIPELINE SAFETY | 3373179145 | john.bell@williams.com | THE CAUSE OF THE INCIDENT WAS UNINTENDED VALVE MOVEMENT. THE FUEL GAS BLOWDOWN VALVE ON THE TURBINE OPENED WHILE THE SUPPLY WAS ALSO OPEN. BLOWDOWN VALVE IS A 2-INCH PLUG. NO ALARMS WERE ASSOCIATED WITH THE EVENT. THE INVESTIGATION PERFORMED DETERMINED ONE OF THE CONTRIBUTING FACTORS WAS THE LACK OF AN ALARM WHEN THE BLOWDOWN VALVE WAS OUT OF POSITION SUCH THAT THE OPERATOR WOULD NOT HAVE BEEN ABLE TO RECOGNIZE THE VALVE WAS OUT OF POSITION. ALARM INSTALLATION SCHEDULED ALREADY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220075 | 37393 | 2022-07-28 14:19 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2022-07-01 11:04 | 2022 | CENTRAL | YES | 42.0489 | -94.0447 | 1340348 | 2022-07-01 13:49 | 1340436 | NATURAL GAS |  | 4274 | 6503 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-01 11:21 | 2022-07-01 16:30 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-07-01 06:30 | NO | [11 empty] | 1 | 2022-07-01 05:28 | 2022-07-01 05:40 | ONSHORE | IA | 50212 | Not Within a Municipality | BOONE | NOT APPLICABLE |  | OGDEN COMPRESSOR STATION | 520B REGULATOR NORTH | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 29 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 39603 | 39603 | 26029 | 26029 | 500 | 500 | 0 | 0 | 0 | 0 |  | 6.09 | 66132 | 34770.7365869487788908338870431893687708 | 66132 | 0 | 0 | 1 | 0 | NO |  |  |  | 665 | 20.1 | 800 | 192.619(C) |  | 1970-11-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES |  | YES | [175 empty] | DAVID CULLISON |  | david.cullison@nngco.com | 402-398-7439 |  | GARY KRICHAU | gary.krichau@nngco.com | 402-398-7274 | TOM CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | ON JULY 1, 2022, AT 0528 HOURS, OGDEN FIELD TEAM, WAS NOTIFIED BY A NEIGHBOR OF BLOWING GAS AT THE OGDEN, IOWA, COMPRESSOR STATION. TECHNICIAN ARRIVED AND OBSERVED GAS BLOWING OUT OF THE VALVE-29 REGULATOR BUILDING. IN ORDER TO ISOLATE THE LEAK AND GAIN ACCESS TO THE BUILDING THE TEAM HAD TO BLOW DOWN APPROXIMATELY 10 MILES OF 20-INCH PIPE ON THE M520B BETWEEN THE OGDEN COMPRESSOR STATION AND VALVE NUMBER TWO, NORTH OF THE STATION. ONCE THE LINE WAS BLOWN DOWN THE TEAM WAS ABLE TO ACCESS THE BUILDING AND FOUND A 1-INCH VALVE AND NIPPLE HAD SEPARATED FROM A 8-INCH BLIND FLANGE JUST ABOVE WHERE THE THREADS ENGAGED THE FLANGE. THE REMAINING PIECE OF NIPPLE WAS EXTRACTED FROM THE FLANGE AND A 1-INCH BULL PLUG WAS INSTALLED. THE M520B WAS RETURNED TO SERVICE ON JULY 1, 2022, AT 1630 HOURS. AT 13:26, PRELIMINARY GAS LOSS CALCULATIONS WERE COMPLETED. THE CALCULATION SHOWED THE REPORTING THRESHOLD WAS MET AT 11:05. WITH THAT CONFIRMATION, THE NRC WAS NOTIFIED AT 13:49. A TRAINING SESSION FOR PIPELINE CONTROL VALVE/REGULATOR VIBRATION RISK AWARENESS COMPLETED IN SEPTEMBER, 2022. THIS INCLUDED A TECHNICAL BULLETIN REVIEW AND DISCUSSION OF KNOWN ASSOCIATED CURRENT AND PRIOR ISSUES TO INCREASE AWARENESS AND RECOGNITION AND REMEDIATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220076 | 37656 | 2022-07-28 15:16 | SUPPLEMENTAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2022-07-05 09:25 | 2022 | EASTERN | YES | 46.496 | -88.7299 | 1340611 | 2022-07-05 09:57 | 1340749 | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A TEMPORARY CLAMP WAS INSTALLED TO STOP THE LEAK |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | PRESSURE REDUCTION |  | OPERATIONAL CONTROL | PRESSURE REDUCTION |  | 0 | 2022-06-30 17:00 | 2022-07-01 13:00 | ONSHORE | MI | 49967 | Not Within a Municipality | HOUGHTON | MILEPOST | 63.57 | WAKEFIELD TO MARQUETTE | M433B | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE |  | 16 |  | 0.203 | 60000 | API 5LX | LONGITUDINAL ERW - LOW FREQUENCY |  | YOUNGSTOWN | COLD APPLIED TAPE |  | YES | [7 empty] | PIPE GIRTH WELD |  | NO | [16 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 359 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 6 | 6 | 198500 | 198500 | 1500 | 1500 | 0 | 0 |  | 6.09 | 200006 | 88236.2770176858119601328903654485049834 | 200006 | 0 | 0 | 0 | 0 | NO |  |  |  | 740 | 1 | 945 | 192.619(A)(2) |  | 1965-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 105600 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | AIR PATROL |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS NOT DISCERNABLE FROM SCADA. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [7 empty] | YES | [14 empty] | YES | [8 empty] | 1202 | [54 empty] | YES | YES | YES |  | YES | YES |  |  | 2021 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2018 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2021 | FREE SWIMMING | HIGH RESOLUTION |  | 2018 | FREE SWIMMING | HIGH RESOLUTION | [13 empty] | 2021 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | INSIDE ILI CUPS | 2018 | FREE SWIMMING | 2014 | FREE SWIMMING | [10 empty] | NO |  |  | NO | [13 empty] | NO | [41 empty] | YES | [21 empty] | DAVID CULLISON |  | david.cullison@nngco.com | 402-398-7439 |  | GARY KRICHAU | gary.krichau@nngco.com | 402-398-7274 | TOM CORRELL |  | 402-398-7715 | thomas.correll@nngco.com | A 157 PPM LEAK WAS INDICATED VIA AERIAL PATROL ON THE M433B WAKEFIELD-TO-MARQUETTE MAINLINE AT MILEPOST 63.57 ON 6/30/2022. ON 7/1/2022, A GRADE 3 LEAK WAS CONFIRMED AND THOUGHT TO BE FROM A FLANGED CONNECTION OF A STOPPLE FITTING. ON 7/5/2022, THE FLANGED CONNECTION OF THE STOPPLE WAS EXAMINED AND DETERMINED NOT TO BE THE SOURCE OF THE LEAK. IT WAS DETERMINED THAT THIS LEAK WOULD BE AN INCIDENT SINCE THE REPAIR COSTS WOULD LIKELY EXCEED THE $122K REPORTING THRESHOLD. THE LEAK WAS EXAMINED ON 7/13/2022. THE LEAK WAS ON A GIRTH WELD, WHICH WAS 8-1/2-INCHES DOWNSTREAM OF THE STOPPLE INSTALLED IN 2020. THE LEAK WAS IN THE CENTERLINE OF THE GIRTH WELD AT THE 5:00 POSITION AND WAS APPROXIMATELY 3-INCHES LONG. THE LEAK WAS SECURED WITH A TEMPORARY REPAIR UNTIL A TYPE-B SLEEVE WAS INSTALLED. THE NEXT DOWNSTREAM GIRTH WELD WAS ALSO REINFORCED WITH A TYPE-B SLEEVE TO MITIGATE CONCERN OF MOVEMENT CAUSED BY THE 2020 CONSTRUCTION. 01/13/2023 - TIME ZONE CORRECTED TO EASTERN TIME. 01/31/2023 - CORRECTED THE DATE THE LEAK WAS EXAMINED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220077 | 37130 | 2022-08-03 17:32 | SUPPLEMENTAL FINAL | 473 | WESTERN MIDSTREAM PARTNERS, LP | 9950 WOODLOCH FOREST DR SUITE 2800 | THE WOODLANDS | TX | 77380 | 2022-06-17 08:00 | 2022 | MOUNTAIN | YES | 44.7306 | -105.7425 | NRC NOTIFICATION REQUIRED BUT NOT MADE |  |  | NATURAL GAS |  | 65274 | 317 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-04 10:52 | 2022-07-07 09:00 |  | YES | OPERATOR | 2022-07-04 11:35 | NO | [5 empty] | VALVE CLOSURE |  | 2022-07-04 10:00 | VALVE CLOSURE |  | 2022-07-04 10:55 | 0 | 2022-07-04 07:00 | 2022-07-04 09:00 | ONSHORE | WY | 82725 | RECLUSE | CAMPBELL | NOT APPLICABLE |  | MIGC | MIGC RECLUSE TO RAWHIDE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 46 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 | NO | 0.125 | 52000 | API 5L | SEAMLESS |  | UNKNOWN | EXTRUDED POLYEHYLENE |  | YES | [26 empty] | 1969 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 154 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 2430 | 2430 | 500456 | 500456 | 122000 | 122000 | 0 | 0 | 0 | 0 |  | 7.667 | 624886 | 383266.0427772841249209634551495016611296 | 624886 | 0 | 0 | 0 | 0 | NO |  |  |  | 860 | 14637 | 1130 | 192.619(A)(1) |  | 1986-12-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 32062 | NO |  | YES |  |  |  | YES | LACK OF NEARBY PIG LAUNCHERS AND RECEIVERS | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT IS NOT UNCOMMON TO HAVE VOLUME IMBALANCES ON THE SYSTEM DUE TO UNPREDICTABLE SEASONAL AND OPERATIONAL CHANGES (E.G., TEMPERATURE CHANGES). | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | THE LEAK WAS CAUSED BY COATING DISBONDMENT AND ROCK GUARD DISADHESION TRAPPING MOISTURE CAUSING LOSS OF CP AND EXTERNAL CORROSION. |  |  | YES |  |  |  | YES | YES | 1970 | YES | YES | YES | YES |  |  | 2021 | 2017 |  |  | YES | [190 empty] | NO | [63 empty] | YES | 1986 | 1413 | NO | [13 empty] | YES | [5 empty] | CLOSE INTERVAL SURVEY | 2017 | [5 empty] | YES | [50 empty] | SYLVIA WHITE | DOT ADVISOR | sylvia.white@westernmidstream.com | 3467865148 |  | JUSTIN HALLERMANN | justin.hallermann@westernmidstream.com | 3076964820 | CRAIG COLLINS | SVP AND COO | 8326361009 | craig.collins@westernmidstream.com | COMPANY CONTACTED BY LOCAL RESIDENT WITH CONCERNS OF DEAD GRASS NEAR THE RIGHT OF WAY. UPON INVESTIGATION, A LEAK WAS DISCOVERED AND THE PIPELINE WAS SHUT IN AND REPAIRED. APPROXIMATELY 60 INCHES OF PIPE WAS CUT OUT AND REPLACED.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220078 | 36931 | 2022-08-04 10:38 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2022-07-08 21:08 | 2022 | CENTRAL | YES | 26.4467 | -98.041 | 1341241 | 2022-07-11 17:00 | 1341428 | NATURAL GAS |  | 3500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THIS LINE HAVE ANOTHER PSV, THE PSV THAT OPENED PREMATURELY HAS BEEN BLOCKED OFF |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-07-08 23:09 | VALVE CLOSURE |  | 2022-07-08 23:09 | 0 | 2022-07-08 21:08 | 2022-07-08 23:05 | ONSHORE | TX | 78549 | HARGILL | HIDALGO | MILEPOST | 1019+64 | MONTE CHRISTO (TECO) - 608 | 608 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | 1983 | CARBON STEEL |  | OTHER | [8 empty] | EQUIPMENT FAILURE - PSV OPENED UP PREMATURELY, AND CLOSED. | CLASS 1 LOCATION | NO |  | 385 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 23275 | 23275 | 6400 | 6400 | 0 | 0 | 0 | 0 |  | 6.65 | 29675 | 18095.2372100808961488372093023255813953 | 29675 | 0 | 0 | 0 | 0 | NO |  |  |  | 1009 | 5000 | 1030 | 192.619(A)(1) |  | 2016-06-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 1 | YES | [7 empty] | YES |  |  | YES |  |  |  | TYPE C GATHERING | YES | YES | YES | YES | NO | OTHER | NOTIFIED BY A TECHNICIAN FROM A THIRD PARTY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS AN EQUIPMENT FAILURE (PSV) | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | NORMAL WEAR & TEAR OF INTERNAL PARTS (SEAL) | [161 empty] | AMIT SHAMGAR | SENIOR PIPELINE COMPLIANCE SPECIALIST | ashamgar@eprod.com | 713-381-6741 |  | AMIT SHAMGAR | ashamgar@eprod.com | 713-381-6741 | NHAN TRUONG | SR. MANAGER PIPELINE COMPLIANCE | 713-381-2493 | nvtruong@eprod.com | ON JULY 8TH AT 2105, ENTERPRISE WAS NOTIFIED BY A THIRD PARTY THAT HARGILL STATION WAS VENTING NATURAL GAS. AT APPROXIMATELY 2305, AN ENTERPRISE TECHNICIAN ARRIVED ON SITE AND BLOCKED THE PSV TO STOP THE RELEASE. THE PSV WAS INSPECTED AND REPAIRED. INITIAL ESTIMATES OF THE LEAK VOLUME DID NOT MEET REPORTING THRESHOLD. HOWEVER, A REVIEW OF MEASUREMENT DATA DETERMINED THAT THE VOLUME EXCEEDED 3 MMSCF AND THE NRC (NRC #1335788 & #1336002) AND RRC (INCIDENT #2619) WERE IMMEDIATELY NOTIFIED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220079 | 37064 | 2022-08-04 12:07 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-07-07 10:37 | 2022 | CENTRAL | YES | 29.5936 | -96.0297 | 1340839 | 2022-07-07 11:55 | 1341027 | NATURAL GAS |  | 40825 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-07 12:00 | 2022-07-09 20:00 |  | YES | OPERATOR | 2022-07-07 11:00 | YES | 2022-07-07 10:37 | ALLOWED TO BURN OUT |  | 40538 | YES | VALVE CLOSURE |  | 2022-07-07 11:00 | VALVE CLOSURE |  | 2022-07-07 12:00 | 0 | 2022-07-07 10:37 | 2022-07-07 11:45 | ONSHORE | TX | 77485 | WALLIS | FORT BEND | SURVEY STATION NO. | 2220+15 | OLD OCEAN (SWEENY TO BURLESON CO) , 24-INCH | 9054 LINE O AMOCO PLANT BELLVILLE OLD OCEAN | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 108 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 24 |  | 0.312 | 52000 | API 5L | FLASH WELDED |  | A.O. SMITH | COLD APPLIED TAPE |  | YES | [26 empty] | 1960 | 1960 | CARBON STEEL |  | RUPTURE |  |  |  |  | OTHER | COMPLETE BLOWOUT/SEPARATION | 227 | 75 |  | CLASS 1 LOCATION | NO |  | 499 |  | YES | NO |  |  | NO |  |  | 500000 | 500000 | 0 | 0 | 224946 | 224946 | 300000 | 300000 | 900 | 900 | 0 | 0 |  | 5.51 | 1025846 | 500923.8645648311396421926910299003322259 | 1025846 | 0 | 0 | 3 | 0 | NO |  |  |  | 760 | 180000 | 811 | 192.619(A)(1) |  | 2018-02-28 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 80256 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  |  | YES |  | YES |  |  | DIRECT CURRENT | TRUNKLINE GAS COMPANY PIPELINE CATHODIC PROTECTION SYSTEM |  | YES |  |  | YES | YES | 1960 | YES | YES |  | YES |  |  |  | 2011 |  |  | YES | [190 empty] | YES | YES | YES |  | YES | YES |  |  | 2022 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2010 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION |  | 2018 | FREE SWIMMING | HIGH RESOLUTION | [17 empty] | 2018 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2010 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2018 | FREE SWIMMING | [12 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | TIMOTHY BUNAG | ENGINEER - REGULATORY COMPLIANCE | timothy.bunag@energytransfer.com | 832-294-5324 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON JULY 7, 2022, AT APPROXIMATELY 10:37AM, ENERGY TRANSFER GAS CONTROL OBSERVED A SUDDEN DROP IN FLOW AT THE SWEENY ENTERPRISE METER, DOWNSTREAM OF THE OLD OCEAN (SWEENY TO BURLESON COUNTY), 24-INCH PIPELINE. GAS CONTROL IMMEDIATELY INITIATED AN EMERGENCY AREA SHUTDOWN BY SHUTTING DOWN BELLVILLE COMPRESSOR STATION AND NOTIFYING OPERATIONS PERSONNEL. AT 11:14AM, OPERATIONS PERSONNEL CONFIRMED THERE WAS A LEAK AND FIRE ON THE OLD OCEAN (SWEENY TO BURLESON COUNTY), 24-INCH PIPELINE SEGMENT. ET PERSONNEL WERE IMMEDIATELY DISPATCHED TO THE UPSTREAM AND DOWNSTREAM VALVE AT 10:40AM. THE AUTOMATED UPSTREAM BLOCK VALVE WAS CLOSED AT 11:00AM AND THE DOWNSTREAM BLOCK VALVE WAS MANUALLY CLOSED AT 12:00 PM ISOLATING THE VALVE SECTION AND LETTING THE FIRE BURN OUT. AT 11:45AM, ET PERSONNEL ARRIVED ON SITE. A HALF MILE RADIUS WAS SECURED FROM THE PUBLIC WITH THE HELP OF LOCAL LAW ENFORCEMENT. THE FIRE WAS PUT OUT AT 12:15PM. ONCE THE AREA WAS DEEMED SAFE, REPAIRS WERE INITIATED. THE FAILED SECTION OF PIPE WAS CUT OUT AND REPLACED AND LINE WAS RETURNED TO SERVICE AS OF 8:00 PM ON JULY 9, 2022. THE CAUSE FOR THE FAILURE WAS DETERMINED TO BE EXTERNAL CORROSION DUE TO STRAY CURRENT INTERFERENCE. TO PREVENT RE-OCCURRENCE, ET HAS REPLACED SEGMENTS OF BOTH PIPELINES, PUT IN PERMANENT ELECTRODES, TEST STATIONS, AND INSTALLED A CRITICAL BOND BETWEEN BOTH PIPELINES. THE BOND WILL BE MONITORED EVERY TWO MONTHS NOT TO EXCEED 2.5 MONTHS. THIS PIPELINE IS A CLASS 1 TRANSMISSION PIPELINE LOCATED IN FORT BEND COUNTY NEAR WALLIS, TEXAS. THIS FACILITY IS UNDER THE JURISDICTION OF THE TEXAS RAILROAD COMMISSION. ON JULY 7, 2022, THIS INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER (NRC) AT 11:55AM. A COURTESY CALL WAS ALSO MADE TO THE TEXAS RAILROAD COMMISSION AT 12:15 PM INCIDENT #2649.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220080 | 36940 | 2022-08-05 12:55 | ORIGINAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-07-07 04:15 | 2022 | CENTRAL | YES | 36.3459 | -86.8682 | 1340803 | 2022-07-07 06:32 | 1340934 | NATURAL GAS |  | 3905 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-07 04:13 | 2022-07-07 13:28 |  | NO |  |  | NO | [11 empty] | 0 | 2022-07-07 04:13 | 2022-07-07 04:50 | ONSHORE | TN | 37080 | Not Within a Municipality | DAVIDSON | SURVEY STATION NO. | 13+22 | COMPRESSOR STATION 563 | LINE 500-1; VS 563-1-1; | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2018 | 2018 | CARBON STEEL |  | OTHER | [8 empty] | ESD OF COMPRESSOR STATION AS DESIGNED; RELEASE VOLUME GREATER THAN 3,000 MCF; | CLASS 2 LOCATION | NO |  | 760 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 22766 | 22766 | 1150 | 1150 | 350 | 350 | 400 | 400 | COST OF INVESTIGATION AND ANALYSIS; | 5.83 | 24666 | 15776.0311516015700308970099667774086379 | 24666 | 0 | 0 | 0 | 0 | NO |  |  |  | 848 | 1600000 | 936 | 192.619(A)(1) |  | 2018-08-22 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ALL CONTROL ROOM MANAGEMENT PROCESSES WERE FOLLOWED; | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [177 empty] | WM. MARTIN MULLER | SPECIALSIT-PIPELINE TECHNICAL | martin_muller@kindermorgan.com | 2053253863 | 2053253787 | SCOTT P. SMITH | scott_p_smith@kindermorgan.com | 6153237922 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND COMPLIANCE | 17133699443 | jaime_hernandez@kindermorgan.com | ON JULY 7, 2022, TENNESSEE GAS PIPELINE (TGP) STATION 563 LOST COMMERCIALLY PROVIDED ELECTRIC POWER SERVICE FROM 03:49 TO 03:53. AT 03:58, TGP GAS CONTROL NOTIFIED THE ON CALL TECHNICIAN THAT STATION 563 WAS OFF-LINE. SUBSEQUENTLY, AT 04:13 THE STATION EXPERIENCED AN EMERGENCY SHUT DOWN (ESD) RELEASING GAS TO ATMOSPHERE. AT 04:50, TGP TECHNICIAN ARRIVED ON SITE AND DETERMINED THE STATION SAFE TO ENTER. UPON ARRIVAL TECHNICIAN STARTED THE INCIDENT ROOT CAUSE INVESTIGATION. AT 06:26, THE ESD INCIDENT AT STATION 563 WAS DEEMED REPORTABLE DUE TO THE GAS RELEASED VOLUME AND REPORTED ACCORDINGLY. INVESTIGATION RESULTED IN DISCOVERY OF A 3/4-INCH BROKEN NIPPLE ON THE STATION 6-INCH BLOWDOWN PIPING THAT PROMPTED THE STATION TO ESD. TGP OPERATOR REPAIRED THE BROKEN NIPPLE IMMEDIATELY. SAFETY CHECKS AND PRACTICAL REVIEWS WERE CONDUCTED FOR STATION 563, AND WITH SATISFACTORY OBSERVATIONS STATION 563 WAS RETURNED TO NORMAL SERVICE AT 13:28.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220081 | 37237 | 2022-08-09 15:32 | SUPPLEMENTAL FINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-07-11 14:50 | 2022 | CENTRAL | YES | 39.6341 | -89.6327 | 1341239 | 2022-07-11 16:44 | 1341382 | NATURAL GAS |  | 5928 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-11 14:50 | 2022-07-11 15:30 |  | NO |  |  | NO | [11 empty] | 0 | 2022-07-11 14:50 | 2022-07-11 14:50 | ONSHORE | IL | 62536 | GLENARM | SANGAMON | NOT APPLICABLE |  | GLENARM COMPRESSOR STATION ESD | GLENARM COMPRESSOR STATION ESD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 621 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 38117 | 38117 | 3 | 3 | 50 | 50 | 0 | 0 |  | 6.43 | 38170 | 25033.7054904030422218970099667774086379 | 38170 | 0 | 0 | 0 | 0 | NO |  |  |  | 770 | 0 | 898 | 192.619(A)(1) |  | 1966-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION IDENTIFIED NO CONTROLLER ISSUES. CONTROLLER ACTIONS WERE CONSISTENT WITH COMPANY PROTOCOLS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | O-RING | [17 empty] | YES | O-RING FAILURE | [161 empty] | CHRISTOPHER PALAFOX | SPECIALIST - REGULATORY COMPLIANCE | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON JULY 11, 2022, AT APPROXIMATELY 14:50 A NATURAL GAS RELEASE OCCURRED AT THE GLENARM COMPRESSOR STATION LOCATED IN SANGAMON COUNTY, ILLINOIS. THE NATURAL GAS RELEASE WAS DUE TO A FAILED O-RING IN THE SYSTEM THAT SUPPLIED DOME PRESSURE ON AN ESD BLOWDOWN VALVE. THE DOME LOST PRESSURE WHICH CAUSED THE BLOWDOWN VALVE TO FAIL OPEN. AT 15:08, A LOCAL OPERATOR ISOLATED AND CLOSED THE ESD VALVE, THE POWER GAS PRESSURE WAS STABILIZED, AND THE RELEASE WAS SECURED. THE DAMAGED O-RING WAS REPLACED WITH A NEW O-RING AND THE SYSTEM WAS PUT BACK INTO SERVICE. AT APPROXIMATELY 16:20, IT WAS CONFIRMED THAT THE UNINTENTIONAL GAS LOSS WAS AT 5.928 MMCF, WHICH EXCEEDED THE 3 MMCF REPORTING CRITERIA AND THE NRC WAS NOTIFIED AT 16:44.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220082 | 37470 | 2022-08-11 16:08 | SUPPLEMENTAL FINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2022-07-14 03:17 | 2022 | CENTRAL | YES | 37.309 | -85.0628 | 1341463 | 2022-07-14 05:38 | 1341574 | NATURAL GAS |  | 8072.6 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | GAS RELEASE WAS STOPPED; CAUSE FOUND AND CORRECTED. |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-07-14 03:50 | NO | [11 empty] | 0 | 2022-07-14 03:17 | 2022-07-14 03:50 | ONSHORE | KY | 42539 | LIBERTY | CASEY | NOT APPLICABLE |  | CLEMENTSVILLE COMPRESSOR STATION | VALVE 206-1BD | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | SHORTED WIRE ON VALVE OPERATOR (206-1PV) CAUSED CONTROL VOLTAGE TO DROP OUT THAT HELD 6 INCH BLOWDOWN VALVE (206-1BD) OPEN RESULTING GAS RELEASE. | CLASS 1 LOCATION | NO |  | 517 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 71200 | 71200 | 0 | 0 | 4500 | 4500 | 0 | 0 |  | 8.82 | 75700 | 48702.8356265856384102990033222591362126 | 75700 | 0 | 0 | 0 | 0 | NO |  |  |  | 815 | 420000 | 975 | OTHER | ANSI RATED 600 VALVE; MFG DATE UNKNOWN, DATE 2B IS APPRX | 1977-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  |  |  | YES | IT WAS DETERMINED THAT A SHORTED CLOSED LIMIT WIRE ON A VALVE ACTUATOR (206 1PV) CAUSED BLOWDOWN VALVE (206 1BD) TO REMAIN OPEN; REMEDYING THIS SHORT CORRECTED THE MALFUNCTION, ENDING THE INCIDENT. | [22 empty] | YES | N/A | [161 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304-539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER | 304-550-4866 | paul_shaffer@tcenergy.com | COLUMBIA GULF TRANSMISSION, LLC OPERATES AND MAINTAINS CLEMENTSVILLE COMPRESSOR STATION LOCATED IN LIBERTY, KENTUCKY. ON THURSDAY JULY 14TH, 2022 THE MONITORING CENTER CALLED OUT STATION PERSONNEL TO INVESTIGATE THE SHUTDOWN OF 3 COMPRESSOR UNITS AT THE STATION AFTER GAS CONTROL HAD RECEIVED UNIT FAULT INDICATIONS. STATION PERSONNEL ARRIVED ON SITE AND DISCOVERED GAS BLOWING AT THE SIDE GATE OF THE STATION, THEY THEN CHECKED THE HMI CONTROL PANEL AND SAW THE 3 COMPRESSOR UNITS WERE STILL ONLINE AND RUNNING AND PROCEEDED TO SHUT THOSE UNITS DOWN. THE STATION PERSONNEL THEN WENT BACK TO THE HMI TO REVIEW ALARMS AND VALVE MOVEMENTS, AT THAT POINT THE BLOWDOWN HAD STOPPED. OTHER STATION TECHNICIANS WERE CALLED IN TO ASSIST AND AFTER TROUBLESHOOTING, DISCOVERED A SHORTED CLOSED LIMIT WIRE ON VALVE ACTUATOR 206-1PV. THE SHORTED WIRE TRIPPED A 24VDC BREAKER THAT FEEDS POWER TO DISCRETE I/O MODULES, WHICH ALSO CAUSED THE COMMS TO NOT FUNCTION. AFTER THE REPAIR OF THE SHORTED WIRE ROUTINE SAFETY CHECKS WERE COMPLETED WHICH INCLUDED A CHECK OF THE ESD SYSTEM TO ENSURE SAFETY AND RELIABILITY. ALL ALARMS WERE CLEARED AT THE CONTROL PANEL, FUNCTIONAL TESTS WERE COMPLETED WITH NO NEW ERRORS GENERATED TO ENSURE NORMAL OPERATION OF THE THREE UNITS. AN INVESTIGATION IS STILL UNDERWAY INTO THE CAUSE OF THE RELEASE. THE CALCULATED VOLUME OF GAS RELEASED WAS ESTIMATED TO BE 8,072.6 MCF THE CHRONOLOGY OF EVENTS ON JULY 14TH, 2022 ARE AS FOLLOWS (ALL TIMES WERE RECORDED IN LOCAL CENTRAL DAYLIGHT SAVING TIME): - 3:17 AM: A UNIT FAULT INDICATION WAS RECEIVED BY TC GAS CONTROL; - 3:50 AM: TC OPERATIONS PERSONNEL ARRIVED AT THE SITE AND LOCAL RESPONDERS WERE AT THE SITE; - 4:04 AM: TC REGULATORY COMPLIANCE MADE A REQUEST FOR VALVE SIZE, PRESSURE, AND TIME OF RELEASE; - 5:31 AM: TC MONITORING CENTER WAS NOTIFIED OF TOTAL GAS LOST, WHICH AT THE TIME, WAS CALCULATED TO BE 5792.8 MCF BY TC OPERATIONS MANAGER; - 5:35 AM: TC MONITORING CENTER NOTIFIED TC REGULATORY COMPLIANCE OF TOTAL GAS LOST; - 5:38 AM: NATIONAL RESPONSE CENTER WAS NOTIFIED OF THE INCIDENT; - 5:45 AM: PHMSA ACCIDENT INVESTIGATION DIVISION WAS NOTIFIED OF THE INCIDENT. THE DURATION OF THE GAS RELEASE WAS DETERMINED FROM OUR CONTROL SYSTEMS TO BE 29 MINUTES. INSPECTIONS REVEALED THAT THE MAIN BREAKER POWERING THE REMOTE I/O PANEL THAT CONTROLS VALVE 206-1BD WAS TRIPPED (CB244). FURTHER INVESTIGATION DISCOVERED DAMAGED AND SHORTED WIRING FEEDING VALVE 206-1PV WHICH WAS CONFIRMED TO BE THE CAUSE OF BREAKER CB244 FAULTING. NOTE REGARDING THE REVISED TIME IN QUESTION A4 ABOVE: IN RESPONSE TO THIS QUESTION THE TIME PROVIDED HERE IS AT THE DIRECTION OF PHMSA AID AND IS NOT AN ADMISSION; WE DID NOT HAVE SUFFICIENT INFORMATION TO DETERMINE WE HAD A REPORTABLE INCIDENT UNTIL 05:31.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220083 | 37686 | 2022-08-11 18:16 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-07-12 17:23 | 2022 | EASTERN | YES | 41.666 | -78.5852 | 1341348 | 2022-07-12 20:06 | 1341525 | NATURAL GAS |  | 10821 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-12 17:25 | 2022-08-02 04:30 |  |  |  |  | YES | 2022-07-12 17:23 | ALLOWED TO BURN OUT |  | 10821 | YES | VALVE CLOSURE |  | 2022-07-12 17:25 | VALVE CLOSURE |  | 2022-07-12 17:25 | 0 | 2022-07-12 18:59 | 2022-07-12 19:23 | ONSHORE | PA | 16740 | CLERMONT | MCKEAN | MILEPOST | 309-1+5.349 | 300-1 PIPELINE | VALVE SECTION 309-1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 24 | NO | 0.281 | 52000 | API 5L OR EQUIVALENT | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | A.O. SMITH | COAL TAR |  | YES | [26 empty] | 1953 | 1953 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 312 | 78 |  | CLASS 1 LOCATION | NO |  | 485 |  | NO | NO |  |  | NO |  |  | 102446 | 102446 | 0 | 0 | 66225 | 66225 | 280007 | 280007 | 15000 | 15000 | 95508 | 95508 | COSTS FOR INVESTIGATION AND AERIAL LEAKAGE SURVEY | 6.12 | 559186 | 260928.7938711717621337774086378737541528 | 559186 | 0 | 0 | 0 | 0 | NO |  |  |  | 854 | 400000 | 858 | 192.619(C) |  | 1970-08-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | AUTOMATIC | 55968 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE WAS IN NORMAL OPERATIONAL MODE WITH NO MAOP EXCEEDANCE. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | STRESS CORROSION CRACKING | [12 empty] | YES | NONE | UNKNOWN | [54 empty] | YES | YES |  |  | YES |  |  |  | 2019 | FREE SWIMMING | OTHER | METAL LOSS AND HARD SPOTS |  |  | 2009 | FREE SWIMMING | METAL LOSS |  | HIGH RESOLUTION | [21 empty] | 2019 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | 2009 | FREE SWIMMING | HIGH RESOLUTION |  | NO CUPS | [14 empty] | YES | 1990 | 1144 | NO | [13 empty] | NO | [63 empty] | DANIEL GRANT | PIPELINE ENGINEER II | daniel_grant@kindermorgan.com | 2545483437 |  | TOM SUTTON | tom_sutton@kindermorgan.com | 7164723015 | JAIME HERNANDEZ | DIRECTOR ENGINEERING CODES AND STANDARDS | 7133699443 | jaime_hernandez@kindermorgan.com | ON JULY 12, 2022, TENNESSEE GAS PIPELINE (TGP) WAS NOTIFIED BY LOCAL EMS PERSONNEL THAT THERE HAD BEEN A RUPTURE IN THE VICINITY OF TGP'S 300 PIPELINE SYSTEM IN MCKEAN COUNTY, PA, WITH THE PRESENCE OF A VISIBLE FIRE. TGP CONFIRMED THE PRESENCE OF THE RUPTURE IN THE 309 VALVE SECTION OF THE 300-1 PIPELINE AND FOUND THAT AUTO-CLOSE VALVES HAD OPERATED AS DESIGNED TO ISOLATE THE RUPTURE LOCATION. THE FIRE WAS CONTAINED AND ALLOWED TO BURN OUT. METALLURGICAL ANALYSIS REVEALED THAT THE LINE RUPTURED FROM NEAR-NEUTRAL-PH STRESS CORROSION CRACKING. HISTORICAL IN-LINE INSPECTION (ILI) ASSESSMENT TECHNOLOGIES AVAILABLE ON THE PIPELINE ARE NOT DESIGNED TO DETECT STRESS CORROSION CRACKING. AFTER THE INCIDENT, TGP COMPLETED AN EMAT ILI ASSESSMENT, WHICH IS DESIGNED TO DETECT CRACKING. BASED ON THE RESULTS OF THAT ASSESSMENT TGP WILL REMEDIATE ACCORDINGLY. SUPPLEMENTAL REPORT WILL BE SUBMITTED WITH UPDATES WHEN ADDITIONAL INFORMATION IS AVAILABLE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220084 | 37240 | 2022-08-12 09:21 | SUPPLEMENTAL FINAL | 2859 | CRANBERRY PIPELINE CORP (WV) | 1600 CORPORATE DRIVE | BIRMINGHAM | AL | 35242 | 2022-07-13 07:20 | 2022 | EASTERN | YES | 38.5252 | -81.7768 | 1341366 | 2022-07-13 09:00 |  | NATURAL GAS |  | 3827.7 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | YES | OPERATOR | 2022-07-13 08:45 | NO | [11 empty] | 0 | 2022-07-13 04:51 | 2022-07-13 07:20 | ONSHORE | WV | 25312 | Not Within a Municipality | PUTNAM | NOT APPLICABLE |  | X-7266 | X-7266 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 1 LOCATION | NO |  | 92 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 26794 | 26794 | 21356 | 21356 | 0 | 0 | 0 | 0 |  | 7 | 48150 | 27002.2300111112816987774086378737541528 | 48150 | 0 | 0 | 0 | 0 | NO |  |  |  | 383 | 0 | 1000 | 192.619(A)(2) |  | 2005-10-19 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY NATURAL FORCES THAT THE CONTROL ROOM HAD NO CONTROL OVER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | NATURAL FORCE DAMAGE | TREES/VEGETATION ROOTS | [52 empty] | TREES/VEGETATION ROOTS | [5 empty] | NO | [270 empty] | YES | [35 empty] | BILLY CULBERTSON | COMPLIANCE SUPERVISOR | bculbertson@dgoc.com | 6062060002 |  | TRAVIS HARRISON | tharrison@dgoc.com | 3049840114 | SHAWN BAILEY | VP OF TECHNICAL SERVICES | 6062133560 | jsbailey@dgoc.com | ON 7/13/2022 THE COMPLIANCE DEPARTMENT WAS NOTIFIED OF A LINE STRIKE DUE TO A FALLEN TREE, LOCATED IN PUTNAM COUNTY, WV GPS 38.525151; -81.776834. THE TREE STRUCK X-7266 ADJACENT TO WELL 1388 WHERE THE GAS IS METERED, RUPTURING THE PIPING. IT WAS DETERMINED THAT THE REPORTING THRESHOLD OF 3 MMCF HAD BEEN REACHED.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220085 | 37316 | 2022-08-16 09:37 | SUPPLEMENTAL FINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-07-22 10:10 | 2022 | CENTRAL | YES | 32.3665 | -93.3547 | 1342244 | 2022-07-22 11:34 | 1342376 | NATURAL GAS |  | 8200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-22 10:52 | 2022-08-05 18:00 |  | YES | OPERATOR | 2022-07-22 10:22 | NO | [5 empty] | VALVE CLOSURE |  | 2022-07-22 10:52 | VALVE CLOSURE |  | 2022-07-22 10:39 | 0 | 2022-07-22 10:10 | 2022-07-22 11:15 | ONSHORE | LA | 71068 | Not Within a Municipality | BIENVILLE | NOT APPLICABLE |  | TRISTATE 9047, CHK WEYERHAEUSER 15-1 | 20101088 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 204 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8.625 | NO | 0.188 | 52000 | API-5LX | SEAMLESS |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 2010 | 2007 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 240 | 20 |  | CLASS 1 LOCATION | NO |  | 239 |  | NO | NO |  |  | NO |  |  | 8000 | 8000 | 0 | 0 | 57072 | 57072 | 208500 | 208500 | 0 | 0 | 0 | 0 |  | 6.96 | 273572 | 132959.0829530402402840531561461794019934 | 273572 | 0 | 0 | 0 | 0 | NO |  |  |  | 1145 | 100 | 1440 | 192.619(A)(1) |  | 2010-03-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 10050 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ENVIRONMENTAL CRACKING-RELATED | MATERIAL/WELD/EQUIP FAILURE | ENVIRONMENTAL CRACKING-RELATED | [132 empty] | ENVIRONMENTAL CRACKING-RELATED |  | YES | [15 empty] | OTHER | INTERNAL ENVIRONMENTAL CRACKING |  |  |  |  | YES | [8 empty] | 2102 | [54 empty] | NO | [63 empty] | YES | 2019 | 1400 | NO | [13 empty] | NO | [63 empty] | ANGELA MORGAN | LEAD SPECIALIST - REGULATORY COMPLIANCE | angela.morgan@energytransfer.com | 903-243-6541 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON 7/22/22 AT APPROXIMATELY 10:10, A PRODUCER CONTACTED ENERGY TRANSFER OPERATIONS PERSONNEL TO REPORT A LOSS OF PRESSURE AND WELL SHUT IN BIENVILLE PARRISH. THE 2 WELLS REPORTED TO BE SHUT IN WERE BOTH INLETS INTO THE ENERGY TRANSFER PIPELINE REFERENCED AS 20101088 TRISTATE 9047 CHK WEYERHAEUSER 15-1. OPERATIONS PERSONNEL WERE MOBILIZED AND ENROUTE TO SHUT MANUAL VALVES TO ISOLATE THE SEGMENT OF PIPELINE. THE UPSTREAM AND DOWNSTREAM VALVES WERE SHUT IN AND ENERGY TRANSFER PERSONNEL LOCATED A PIPELINE RUPTURE ON THE WEYERHAEUSER 15-1. ONCE ISOLATED, THE PIPELINE WAS ALLOWED TO BLOWDOWN AT THE RUPTURE SITE. A SEGMENT OF PIPE WAS LOCATED OUTSIDE OF THE RUPTURE AREA AND WAS PRESERVED TO SEND FOR METALLURGICAL ANALYSIS. REPORTS WERE MADE TO THE LA STATE POLICE ON 722/22 AT 10:22 AND LA DNR ON 7/22/22 AT 11:46. NRC NOTIFICATIONS WERE MADE (1342244 & 48-HR FOLLOW UP 1342376). METALLURGICAL ANALYSIS IS BEING COMPLETED ON THE SAMPLE RECOVERED FROM THE RUPTURE SITE. THE SEGMENT OF PIPE AFFECTED HAS BEEN REPLACED AND WAS PLACED BACK IN SERVICE ON 8/5/22 AT 18:00. METALLURGICAL ANALYSIS INDICATED THE CAUSE IS INTERNAL ENVIRONMENTAL CRACKING.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220086 | 37360 | 2022-08-19 11:11 | SUPPLEMENTAL FINAL | 39147 | ENABLE GAS GATHERING, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-08-19 07:20 | 2022 | CENTRAL | YES | 34.5479 | -97.6707 | 1344930 | 2022-08-19 07:47 | 1348266 | NATURAL GAS |  | 1000 | 8935.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-08-19 07:30 | 2022-08-20 18:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-08-19 07:30 | VALVE CLOSURE |  | 2022-08-19 07:30 | 0 | 2022-08-19 07:20 | 2022-08-19 07:20 | ONSHORE | OK | 73052 | Not Within a Municipality | STEPHENS | NOT APPLICABLE |  | COTTONWOOD STATION | FACILITY STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | FLANGE ASSEMBLY | [38 empty] | 2014 | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | GASKET | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 81582 | 81582 | 9130 | 9130 | 13000 | 13000 | 0 | 0 | 0 | 0 |  | 9.13 | 103712 | 47716.5705938357906895481727574750830565 | 103712 | 0 | 0 | 0 | 0 | NO |  |  |  | 986 | 10000 | 1200 | 192.619(A)(2) |  | 2014-12-05 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 52800 | NO |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | NON-REGULATED GATHERING | TYPE C GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | GASKET | [17 empty] | YES | GASKET | [150 empty] | YES | [10 empty] | JIMMY CROSS | SR. MANAGER REGULATORY COMPLIANCE | jimmy.cross@energytransfer.com | 4055768230 |  | JIMMY CROSS | jimmy.cross@energytransfer.com | 4055768230 | JIMMY CROSS | SR. MANAGER REGULATORY COMPLIANCE | 4055768230 | jimmy.cross@energytransfer.com | DURING NORMAL PIGGING OPERATIONS A VALVE GASKET FAILED APPROXIMATELY 6 FEET FROM THE PIG TRAP. THERE WAS NO PRESSURE EXCEEDANCE. THE GASKET WAS INSPECTED, BUT THE INSPECTION AND REVIEW OF THE EVENT FOUND NO CAUSAL FACTORS CONTRIBUTING TO THE GASKET FAILURE. OPERATIONS CLEARED THE FACILITY FOR SAFETY REASONS AND BEGAN ISOLATION AND BLOWN DOWN OF THE SITE AT ADJACENT INTERCONNECTING FACILITIES, WHICH CONTRIBUTED TO THE RELEASE VOLUME MAKING IT REPORTABLE. THE VALVE WAS REMOVED AND BOTH GASKETS WERE REPLACED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220087 | 37043 | 2022-08-19 12:05 | SUPPLEMENTAL FINAL | 18152 | SEA ROBIN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-07-23 16:42 | 2022 | CENTRAL | YES | 28.2483 | -91.6933 | 1342409 | 2022-07-24 17:36 | 13426241345136 | NATURAL GAS |  | 2647.87 | 29414.76 | 28.89 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | YES | OPERATOR | 2022-07-24 17:46 | NO | [5 empty] | OPERATIONAL CONTROL | VALVES ALREADY CLOSED DUE TO PREVIOUS INCIDENT. |  | OPERATIONAL CONTROL | VALVES ALREADY CLOSED DUE TO PREVIOUS INCIDENT. |  | 0 | 2022-07-23 16:42 | 2022-07-23 16:42 | OFFSHORE | [6 empty] | SEA ROBIN EI BLOCK 330 | SEGMENT # 7109 LINE 716-10-1 | [20 empty] | 260 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | EUGENE ISLAND | 330 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 8.625 | NO | 0.438 | 24000 | API 5L X-52 | OTHER | UNKNOWN | UNKNOWN | OTHER | MASTIC AND CONCRETE | YES | [26 empty] | 1973 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 165 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 111 | 111 | 375000 | 375000 | 75000 | 75000 | 0 | 0 |  | 8.25 | 450111 | 198595.5975422847712624584717607973421927 | 450111 | 0 | 0 | 0 | 0 | NO |  |  |  | 735 | 10 | 1306 | 192.619(A)(1) |  | 1977-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 31680 | NO |  |  | YES |  |  |  |  | YES |  |  | YES |  | YES | MULTIPLE DIAMETER PIPE | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES |  |  |  | YES |  | YES |  |  |  | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PEGGY WEST | SR. REGULATORY ANALYST | peggy.west@energytransfer.com | 409-202-3088 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | 7/23/22, SEA ROBIN GAS CONTROL RECEIVED NOTIFICATION OF A SHEEN IN THE EI 330 BLOCK AREA. THE THIRD-PARTY PRODUCER WHO OBSERVED THE SHEEN NOTIFIED THE NRC AND THOSE WHO HAVE LINES IN THE AREA. 7/24/22, ET MADE AN OVERFLIGHT TO CONFIRM SHEEN. FINDINGS WERE REPORTED TO THE NRC AT 17:36, NRC#1342409. 7/25/22, THE PRODUCER WHO ORIGINALLY SPOTTED THE SHEEN HAS A DSV ON CONTRACT AND ARE IN THE PROCESS OF INVESTIGATING THE SOURCE. THEY ARE JUST ARRIVING IN THE FIELD BUT WILL UPDATE US AS THEY DETERMINE OWNERSHIP. 7/26/22, THE DSV SHOWS THE LEAK SOURCE IS AT A CROSSING BETWEEN THE SEA ROBIN WEST 8-INCH LINE AND A THIRD PARTY 6-INCH LINE. DUE TO THE LIMITATIONS OF THE DSV THAT RESPONDED, THEY WERE UNABLE TO SAFELY ACCESS THE CROSSING TO VERIFY WHICH LINE IS AT FAULT. THE SEA ROBIN WEST 8-INCH LINE IS CONNECTED TO THE SEA ROBIN WEST 24-INCH, WHICH IS CURRENTLY IN THE PROCESS OF DEPRESSURIZATION DUE TO THE LEAKING FITTING IN SMI128. THAT DEPRESSURIZATION WORK WILL CONTINUE AS WILL OUR ATTEMPTS TO LOCATE A DSV WITH THE NEEDED CAPABILITIES. THE NRC 48-HOUR UPDATE WAS MADE, AND THE REPORT WAS UPDATED WITH OVERFLIGHT FINDINGS. NRC#1342624. 8/19/2022, WE HAVE BEEN UNABLE TO SOURCE A DSV TO RESPOND TO OUR INCIDENTS. THE RESPONSIBLE PARTY FOR THIS RELEASE IS YET TO BE DETERMINED. 8/21/2022, ENERGY TRANSFER PLACED A CALL TO THE NRC TO TAKE OWNERSHIP OF THE RELEASE AND UPDATE RESPONSIBLE PARTY TO SEA ROBIN PIPELINE. NRC# 1345136. CONDENSATE FOUND LEAKING FROM A PINHOLE LEAK AT THE 5 O'CLOCK POSITION. 8/22/2022, THE REPAIR CLAMP HAS BEEN INSTALLED. OPERATIONS PERSONNEL BEGINNING THE PRESSURIZATION OF PIPELINE TO PERFORM LEAK CHECKS AT MULTIPLE STAGES. NO LEAKS WERE OBSERVED BY THE DIVERS OR OVERFLIGHT PERSONNEL THROUGHOUT EACH INCREASE IN PRESSURE POINTS. 8/23/22, THE LINE WAS BACK TO FULL PRESSURE (EQUALIZED) AT 16:39.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220088 | 37145 | 2022-08-19 15:45 | SUPPLEMENTAL FINAL | 39263 | HAYNESVILLE GATHERING LP | 12377 MERIT DRIVE SUITE 1200 | DALLAS | TX | 75251 | 2022-07-22 09:00 | 2022 | CENTRAL | YES | 32.2508 | -93.3903 | 1342234 | 2022-07-22 10:30 | 1342340 | NATURAL GAS |  | 3900 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-22 09:40 | 2022-09-19 16:00 |  |  |  |  | NO | [5 empty] | OPERATIONAL CONTROL | THE WELL PAD UPSTREAM OF THE FAILURE SHUT IN AS A RESULT OF A LOW PRESSURE TRIP. |  | VALVE CLOSURE |  | 2022-07-22 09:25 | 2 | 2022-07-22 09:00 | 2022-07-22 09:20 | ONSHORE | LA | 71068 | Not Within a Municipality | BIENVILLE | NOT APPLICABLE |  | CONLY 16 INCH | WHITMAR EXTENSION | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 65000 | API 5L, GRADE X65 | LONGITUDINAL ERW - HIGH FREQUENCY |  | U.S. STEEL | OTHER | FUSION BONDED EPOXY | NO | [26 empty] | 2010 | 2007 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 8 |  |  | CLASS 1 LOCATION | NO |  | 419 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 30420 | 30420 | 450000 | 450000 | 230 | 230 | 0 | 0 |  | 7.8 | 480650 | 218584.1992849414886837541528239202657807 | 480650 | 0 | 0 | 2 | 0 | NO |  |  |  | 1380 | 100000 | 1440 | 192.619(A)(1) |  | 2010-10-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  | MANUAL | 28311 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE NEVER EXCEEDED MAOP AND THE EVALUATION OF THE PIPING INDICATED A PREMATURE FAILURE AS A RESULT OF MICROBIAL INDUCED INTERNAL CORROSION. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  |  | YES | [6 empty] | YES | 6 O'CLOCK POSITION ON THE PIPE. THIS SEGMENT WAS ON A DOWNHILL SLOPE OF THE RIGHT-OF-WAY. | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | JASON MOXLEY | HSE MANAGER | jmoxley@aethonenergy.com | 214-412-9821 |  | JASON MOXLEY | jmoxley@aethonenergy.com | 214-412-9821 | JASON MOXLEY | HSE MANAGER | 214-412-9821 | jmoxley@aethonenergy.com | DURING THE MORNING OF THE INCIDENT, THUNDERSTORMS WERE MOVING THROUGH THE AREA AND THE DOWNSTREAM AMINE TREATMENT PLANT WAS STRUCK BY LIGHTING AND LOST POWER SUBSEQUENTLY SHUTTING IN AT AROUND 08:30. AT 09:00, OPERATIONS RECEIVED A NOTICE FROM EMERGENCY RESPONDERS THAT A WELL WAS BLOWING OUT OR RELIEVING NEAR HWY 4. SUPERVISORS AND OPERATORS BEGAN TO MAKE THEIR WAY AROUND TO THAT SIDE OF THE FIELD TO INVESTIGATE BUT TOOK EXTRA TIME DUE TO TREES BEING ACROSS THE ROAD. SOON THEREAFTER IT WAS DETERMINED THAT A WELL WAS NOT BLOWING OUT, BUT A PIPELINE HAD RUPTURED IN THAT AREA. THE EXACT LOCATION OF RUPTURE WAS UNKNOWN AT THE TIME, BUT THE PIPELINE WAS IDENTIFIED AND OPERATIONS BEGIN ISOLATING THE WELLS AND THE PIPELINE BETWEEN 09:20 AND 09:25. LOCAL EMERGENCY RESPONDERS EVACUATED 2 HOMES AS A PRECAUTION AND SHUT DOWN HWY 4 ONCE THE LEAK LOCATION WAS IDENTIFIED. NO INJURIES OR DAMAGE TO PROPERTY OCCURRED. THE EXACT LOCATION OF THE FAILURE WAS CONFIRMED AROUND 09:30 AND THE PIPELINE WAS COMPLETELY ISOLATED BY 09:40. NRC WAS NOTIFIED AT 10:30, BUT THE CALLER SAT ON HOLD FOR 20 MINUTES AND DID NOT SPEAK TO AN OPERATOR TILL AROUND 10:50. FURTHER EVALUATION OF THE RUPTURE IDENTIFIED INTERNAL CORROSION WITH PITTING. DAMAGED SECTION OF PIPE WAS CUT BACK TO CLEAN PIPE AND SENT OFF TO BE EVALUATED WHICH WAS DETERMINED TO BE MICROBIAL INDUCED CORROSION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220089 | 37136 | 2022-08-22 14:43 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-08-01 14:25 | 2022 | EASTERN | NO | 35.3931 | -78.0811 | 1343245 | 2022-08-01 16:52 | 1343435 | NATURAL GAS |  | 785 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-08-02 20:00 | 2022-08-03 02:31 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-08-01 14:22 | NO | [5 empty] | OPERATIONAL CONTROL | STOPPLE CUPS WERE PLACED AND BLEW DOWN THE LINE BETWEEN. |  | OPERATIONAL CONTROL | STOPPLE CUPS WERE PLACED AND BLEW DOWN THE LINE BETWEEN. |  | 4 | 2022-08-01 14:22 | 2022-08-01 14:46 | ONSHORE | NC | 27530 | GOLDSBORO | WAYNE | NOT APPLICABLE |  | LINE 5 | LINE 5 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.188 | 42000 | X42000 ERW | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 4710 | 4710 | 362171 | 362171 | 5000 | 5000 | 0 | 0 |  | 6 | 371881 | 165072.2313138218587413189368770764119601 | 371881 | 0 | 0 | 0 | 0 | NO |  |  |  | 613 | 8000 | 695 | 192.619(A)(3) |  | 2014-06-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 6340 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [9 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | A222074120 | NA | FACILITY OWNER | NO | NO | NO |  | LOCATING PRACTICES NOT SUFFICIENT |  | FACILITY MARKING OR LOCATION NOT SUFFICIENT | [264 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR BORED INTO A 10" HIGH PRESSURE STEEL MAIN WHILE INSTALLING TELECOMMUNICATION LINES. INACCURATE/INSUFFICIENT LOCATE MARKS WERE PLACED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220090 | 37424 | 2022-08-25 14:36 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 295 CHIPETA WAY | SALT LAKE CITY | UT | 84108 | 2022-07-28 12:41 | 2022 | PACIFIC | YES | 45.7777 | -121.6261 | 1342913 | 2022-07-29 01:52 | 1342995 | NATURAL GAS |  | 52000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [8 empty] | NO | [11 empty] | 0 | 2022-07-28 22:10 | 2022-07-28 23:50 | ONSHORE | WA | 98605 | COOK | KLICKITAT | MILEPOST | 1175.17 | NWP WILLARD COMPRESSOR STATION | WILLARD COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 1992 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 620 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 466960 | 466960 | 0 | 0 | 2000 | 2000 | 15000 | 15000 | OTHER COSTS INVOLVE RCA INVESTIGATION TEAM AND OPERATIONS TROUBLESHOOTING EFFORT | 8.98 | 483960 | 313893.7688455066162757475083056478405316 | 483960 | 0 | 0 | 0 | 0 | NO |  |  |  | 360 | 242000 | 809 | 192.619(A)(2) |  | 1992-08-03 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  |  | YES | [5 empty] | YES | CONTRIBUTING FINDINGS INCLUDE: - LOADING OR SUCTION VALVE FAILED TO CLOSE FULLY. -POWER TURBINE PERCENT SPEED AND SUCTION / DISCHARGE PRESSURES WERE INDICATED ON LOCAL HMI AND OBSERVABLE BY GAS CONTROL BUT WERE NOT SPECIFICALLY REVIEWED. | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [216 empty] | MISCELLANEOUS | THE INVESTIGATION TEAM CONCLUDED THAT THERE WAS LIKELY DEBRIS THAT FOUND THEIR WAY INTO THE SEAT OF THE VALVE. THIS DEBRIS COULD'VE ORIGINATED FROM HYDROTEST PROJECTS THAT HAD BEEN TAKING PLACE NEAR THE COMPRESSOR STATION EARLIER THIS YEAR. THIS REMAINS THE MOST LIKELY CAUSE, AND IS STILL SEEN AS A "HYPOTHETICAL" CAUSE AS NO DEBRIS WERE FOUND AFTER FURTHER INVESTIGATION. | [147 empty] | TAYLER JENSEN | PIPELINE SAFETY ENGINEER | tayler.jensen@williams.com | 2813828869 |  |  |  |  | JOHN BELL | PIPELINE SAFETY MANAGER | 3373179145 | john.bell@williams.com | ON JULY 28TH, 2022 THERE WAS AN IMPROPER SEALING OF A UNIT VALVE AT NORTHWEST PIPELINE WILLARD COMPRESSOR STATION. WILLIAMS OPERATIONS RECEIVED A CALL FROM SKAMANIA COUNTY 911 DISPATCH AT 22:10 LOCAL TIME REPORTING A STRONG SMELL OF GAS FROM A NEIGHBOR NEAR THE COMPRESSOR STATION. WILLIAMS OPERATIONS PERSONNEL IMMEDIATELY RESPONDED TO THE CALL AND ARRIVED ON-SITE AT 23:50 LOCAL TIME TO ASSESS THE SITUATION. WHILE ON-SITE IT WAS DISCOVERED THAT THE VENT VALVE ON UNIT ONE AT THE COMPRESSOR STATION WAS SHOWING CLOSED ON THE HMI BUT WAS STILL VENTING GAS. IN AN EFFORT TO STOP THE GAS FROM VENTING AS QUICKLY AS POSSIBLE OPERATIONS TECHNICIANS AT THE SITE CONSULTED WITH PIPELINE CONTROL AND THE OPERATIONS SUPERVISOR AND AGREED TO ISSUE A START COMMAND TO UNIT ONE. ISSUING THIS START COMMAND WAS FOUND TO CAUSE ALL VALVES TO POSITION THEMSELVES CORRECTLY, THUS STOPPING THE GAS FROM VENTING TO THE ATMOSPHERE. SHORTLY AFTER, A STOP COMMAND WAS SUBSEQUENTLY ISSUED TO THE SAME UNIT, WITH OPERATIONS NOTING THAT ALL VALVES ALSO CORRECTLY POSITIONED THEMSELVES AGAIN. IT WAS NOTED BY PIPELINE CONTROL THAT THIS UNIT WOULD NOT BE NEEDED FOR THE REST OF THE NIGHT, SO UNIT ONE WAS LEFT OFF AND UNAVAILABLE UNTIL THE NEXT DAY. ONCE THE UNIT HAD BEEN SHUT DOWN AND NO ADDITIONAL VENTING WAS CONFIRMED, OPERATIONS CONTACTED THE SECURITY OPERATIONS CENTER (SOC) AT 01:40 LOCAL TIME. AT THIS TIME, THE SOC RAN GAS LOSS ESTIMATION CALCULATIONS AND WAS ABLE TO CONFIRM DISCOVERY THAT THE 3MMSCF RELEASE THRESHOLD WAS REACHED. SHORTLY AFTER, AT 01:52, AFTER A CONVERSATION BETWEEN THE SOC AND PIPELINE SAFETY, IT WAS DETERMINED TO REPORT THE INCIDENT TO THE NRC. OPERATIONS PERSONNEL THAT RESPONDED TO THE INCIDENT WENT HOME TO REST BEFORE ARRIVING ON-SITE THE NEXT MORNING TO CONTINUE THE TROUBLESHOOTING PROCESS. THE FOLLOWING MORNING OPERATIONS AND TECH SERVICES EMPLOYEES WORKED TO TROUBLESHOOT THE VALVE POSITION INDICATORS AND WERE NOT ABLE TO RECREATE THE PROBLEM THAT CAUSED UNIT ONE SUCTION VALVE TO REMAIN CRACKED DURING A REMOTE STOP. TO BETTER ALERT OPERATION PERSONNEL OF A SIMILAR INCIDENT OCCURRING, PIPELINE CONTROL PLACED A TEMPORARY PRESSURE ALARM TO MONITOR CASE PRESSURE. OVER THE COURSE OF THE FOLLOWING WEEKS, OPERATIONS PERSONNEL ATTEMPTED TO RECREATE THE ISSUE TO BETTER UNDERSTAND WHAT CAUSED THE INITIAL INCIDENT. MULTIPLE EFFORTS TO RECREATE THE ISSUE WERE UNSUCCESSFUL AND A FULL ROOT-CAUSE INVESTIGATION HAS SINCE TAKEN PLACE. THE FINDINGS OF THE INVESTIGATION REVEALED THAT THE UNIT 1 BLOWDOWN VALVE HAD BEEN LEAKING 12 HOURS PRIOR TO PIPELINE CONTROL RECEIVING NOTIFICATION FROM THE EMERGENCY DISPATCH. THE INVESTIGATION INTO WHY THE BLOWDOWN VALVE FAILED TO SEAL FOUND THAT THERE WAS LIKELY SOME DEBRIS IN THE SEAT OF THE UNIT VALVE THAT CAUSED IT TO NOT SEAL PROPERLY. IT'S BELIEVED THAT THESE DEBRIS MAY HAVE ORIGINATED FROM PIPELINE CLEANING / PIGGING EFFORTS AS PART OF A SERIES OF HYDROTEST PROJECTS THAT HAD RECENTLY OCCURRED IN THE AREA. IT WAS ALSO FOUND THAT POWER TURBINE PERCENT SPEED AND SUCTION/DISCHARGE PRESSURES WERE NOT UTILIZED TO SHOW INDICATION OF A POTENTIAL ISSUE WITH THE COMPRESSOR. THESE ITEMS WEREN'T SPECIFICALLY REVIEWED AT THE TIME AS THERE WERE NO ALARMS GIVEN TO PIPELINE CONTROL. TO PREVENT THIS FROM HAPPENING IN THE FUTURE, WILLIAMS IS IMPLEMENTING A CONTINUOUS VENTING UNIT ALARM WITHIN SCADA, STATION, AND UNIT CONTROL SYSTEMS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220091 | 37033 | 2022-08-26 12:45 | ORIGINAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2022-07-28 15:10 | 2022 | EASTERN | NO | 40.3966 | -78.8893 | 1342865 | 2022-07-28 15:10 | 1343109 | NATURAL GAS |  | 3605 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-28 14:40 | 2022-07-29 04:05 |  | YES | OPERATOR | 2022-07-28 13:10 | YES | 2022-07-28 15:20 | ALLOWED TO BURN OUT |  | 639 | NO | VALVE CLOSURE |  | 2022-07-28 14:40 | VALVE CLOSURE |  | 2022-07-28 14:40 | 0 | 2022-07-28 13:05 | 2022-07-28 13:05 | ONSHORE | PA | 15909 | JACKSON TWP | CAMBRIA | NOT APPLICABLE |  | TP-7220 | PIL0117721 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 37 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1951 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | 2 INCH SAVE-A-VALVE WAS BROKEN OFF OF THE MAINLINE PIPE DURING EXCAVATION. | CLASS 1 LOCATION | NO |  | 226 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 54349 | 54349 | 527 | 527 | 75869 | 75869 | 24630 | 24630 | CUSTOMER RELIGHTS | 15.0761 | 155375 | 80229.6906795449630990764119601328903654 | 155375 | 0 | 0 | 337 | 16 | NO |  |  |  | 320 | 11000 | 401 | 192.619(A)(3) |  | 1971-04-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 38886 | NO | YES |  | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [10 empty] | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 20221153475 | PA ONECALL | FACILITY OWNER | YES | YES | YES | 15 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | FAILURE TO MAINTAIN CLEARANCE | [263 empty] | DANIEL KUEHN | MANAGER COMPLIANCE | daniel.kuehn@peoples-gas.com | 724-444-3251 |  | DANIEL KUEHN | daniel.kuehn@peoples-gas.com | 724-444-3251 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412-258-4453 | edward.a.palombo@peoples-gas.com | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS, STRUCK AND DAMAGED A 2" SAVE-A-VALVE ON TRANSMISSION LINE WHILE DIGGING TIE-IN HOLE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220092 | 37039 | 2022-08-29 10:06 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-08-16 18:46 | 2022 | CENTRAL | YES | 35.227 | -92.399 | 1344682 | 2022-08-16 18:53 | 1344853 | NATURAL GAS |  | 1 | 14.6 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-08-16 22:50 | 2022-08-18 11:27 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-08-16 07:11 | NO | [5 empty] | VALVE CLOSURE |  | 2022-08-16 22:40 | VALVE CLOSURE |  | 2022-08-16 22:50 | 4 | 2022-08-16 16:15 | 2022-08-16 16:15 | ONSHORE | AR | 72058 | GREENBRIER | FAULKNER | NOT APPLICABLE |  | BM-21 | PIPELINE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 4 | NO | 0.188 | 30000 | UNKNOWN | FURNACE BUTT WELDED |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 55 |  | NO | NO | [5 empty] | 0 | 0 | 135 | 135 | 9 | 9 | 69351 | 69351 | 0 | 0 | 852 | 852 | HOTEL STAYS FOR THOSE EVACUATED. | 9.28 | 70347 | 31036.3370196655378261993355481727574751 | 70347 | 0 | 0 | 2 | 1 | NO |  |  |  | 260 | 3534 | 310 | 192.619(A)(2) |  | 2012-03-30 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 8661 | NO |  | YES |  | YES |  | YES | NO LAUNCHER/RECEIVER; DEAD LEGS ARE PRESENT | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | OTHER | AN EMERGENCY LOCATE REQUEST WAS SUBMITTED BY SUMMIT UTILITIES. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS VERY SMALL (PIN HOLE) AND NOT SOMETHING A CONTROLLER WOULD BE ABLE TO IDENTIFY. | [12 empty] | NO |  |  | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | MATERIAL/WELD/EQUIP FAILURE | CONSTRUCTION, INSTALLATION OR FABRICATION-RELATED | [132 empty] | DESIGN-, CONSTRUCTION-, INSTALLATION-, OR FABRICATION-RELATED | YES | [8 empty] | YES | PIN HOLE IN WELD | [19 empty] | YES | PIN HOLE IN WELD | UNKNOWN | [54 empty] | NO | [63 empty] | YES | 2018 | 388 | Yes, but the point of the Accident was not identified as a dig site |  | 2020 | 2020 | 2020 |  |  |  |  | YES | YES |  |  |  | NO | [13 empty] | YES | [49 empty] | DANIEL ANTOINE | SR. DOT SPECIALIST | daniel.antoine@energytransfer.com | 501-472-5065 |  | BRANDON BYRD | brandon.byrd@energytransfer.com | 870-769-2435 | JIMMY CROSS | SR. MANAGER REGULATORY COMPLIANCE | 318-426-2515 | jimmy.cross@energytransfer.com | A EMERGENCY LOCATE REQUEST WAS SENT IN FROM SUMMIT UTILITIES AT APPROXIMATELY (15:45) ON AUGUST 16, 2022. OUR OPERATIONS TECHNICIAN RESPONDED TO THE SCENE AT (16:15) AND DISCOVERED A GAS READING OF 3% LEL IN THE ATMOSPHERE....MORE TECHNICIANS ARRIVED AND BEGAN BAR HOLE TESTING WHICH REVEALED READINGS AS HIGH AS 50% GAS. THE PIPELINE (BM-21) IS IN THE VICINITY OF 2 DUPLEXES AND RUNS UNDER 2 CONCRETE DRIVEWAYS TO THESE DUPLEXES; THE SUSPECTED LEAK WAS UNDER ONE OF THESE CONCRETE DRIVEWAYS. THE DECISION WAS MADE TO EVACUATE THE RESIDENTS OF THE 2 DUPLEXES AS A PRECAUTION; THIS DECISION WAS MADE AT APPROXIMATELY 18:40 ON AUGUST 16, 2022. AFTER EVACUATING THE RESIDENTS, OPERATIONS PERSONNEL FORMED A PERIMETER AND MONITORED GAS LEVELS WHILE WAITING FOR EQUIPMENT TO ARRIVE TO ISOLATE AND BLOW DOWN THE AFFECTED PIPELINE SEGMENT. OPERATIONS ISOLATED 8,661' OF PIPE BY PLACING A STOPPLE PLUG IN A STOPPLE FITTING LOCATED AT LINE PLUS 540+95 AND BY CLOSING BLOCK VALVE 43120 AT GREENBRIER TOWN BOARDER STATION LOCATED AT LINE PLUS 627+56; THE LINE WAS BLOWN FLAT AT 22:50 ON AUGUST 16, 2022. CONTRACTORS MOBILIZED TO THE SITE ON THE MORNING OF AUGUST 17, 2022....AFTER HEAVY RAIN MOVED OUT OF THE AREA, THE CONTRACTORS BEGAN REMOVING BOTH CONCRETE DRIVEWAYS. THE PIPE WAS UNCOVERED ON THE AFTERNOON (AUGUST 17TH) AND A SMALL PINHOLE LEAK WAS DISCOVERED IN A GIRTH WELD. THE PIPE WAS CUTOUT AND 44' OF 0.237: WT, 4.5" DIA, X52 GRADE PIPE WAS INSTALLED IN ITS PLACE. THE PIPE WAS PURGED AND LOADED AND THEN BROUGHT BACK INTO SERVICE ON THE MORNING OF AUGUST 18TH, 2022.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220094 | 37062 | 2022-09-01 09:57 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-07-31 14:01 | 2022 | CENTRAL | YES | 39.6976 | -81.4906 | 1343302 | 2022-08-02 11:07 | 1343862 | NATURAL GAS |  | 3490 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE VENTED DUE TO A REGULATOR FAILURE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-07-31 14:00 | 2022-07-31 14:00 | ONSHORE | OH | 43724 | Not Within a Municipality | NOBLE | MILEPOST | 668.698 | MR 70095 | ATHE-BURN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1998 | 1998 | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE VENTED | CLASS 2 LOCATION | NO |  | 41 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 26908 | 26908 | 500 | 500 | 500 | 500 | 0 | 0 |  | 7.71 | 27908 | 18096.7430960518842093023255813953488372 | 27908 | 0 | 0 | 0 | 0 | NO |  |  |  | 420 | 500 | 625 | 192.619(A)(1) |  | 1993-11-30 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INDICATION OR EVIDENCE OF CONTROL ROOM OR CONTROLLER CONTRIBUTION TO THE INCIDENT WAS IDENTIFIED; OPERATIONS (I.E., PRESSURES AND FLOWS) IN THE AREA WERE NORMAL AND WITHIN DESIGNED RANGES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | BUILD-UP OF MATERIAL IN CONTROL LINE. | [161 empty] | MICHAEL MCGRATH | PIPELINE PERFORMANCE AND COMPLIANCE SPECIALIST | michael.mcgrath@enbridge.com | 612-805-6542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 713-627-5008 | nathan.atanu@enbridge.com | AT APPROXIMATELY 10:02 AM CDT ON JULY 31, 2022, A 2-INCH RELIEF VALVE BEGAN VENTING AT A METER AND REGULATING STATION (MR 70095) AS THE RESULT OF A REGULATOR FAILURE. A NEARBY RESIDENT REPORTED THAT THE RELIEF VALVE WAS VENTING. THE REGULATOR FAILURE WAS CAUSED BY A BUILDUP OF MATERIAL IN THE REGULATOR PILOT LINE. THE PILOT LINE WAS CLEANED, AND THE REGULATOR WAS PLACED BACK INTO SERVICE ON THE SAME DAY. AT THE TIME OF THE EVENT, IT WAS UNKNOWN HOW LONG THE RELIEF VALVE HAD BEEN VENTING. A LATER REVIEW OF DATA (SCADA) ON AUGUST 2, 2022, SHOWED THAT THE RELIEF VALVE HAD BEEN VENTING FOR APPROXIMATELY 4 HOURS RESULTING IN A 3.490 MMCF CALCULATED GAS RELEASE. PRESSURE ALARMS AT THE REGULATOR STATION WERE ADJUSTED TO HELP IN IDENTIFYING SIMILAR EVENTS.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220095 | 37537 | 2022-09-01 15:43 | SUPPLEMENTAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2022-08-06 00:01 | 2022 | CENTRAL | YES | 31.9457 | -101.7464 | 1343686 | 2022-08-06 02:47 | 1343804 | NATURAL GAS |  | 233 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-08-06 00:01 | 2022-08-30 11:00 |  | YES | OPERATOR | 2022-08-06 00:50 | YES | 2022-08-06 00:01 | ALLOWED TO BURN OUT |  | 233 | NO | [6 empty] | 0 | 2022-08-06 00:50 | 2022-08-06 00:50 | ONSHORE | TX | 79706 | Not Within a Municipality | GLASSCOCK | NOT APPLICABLE |  | MACK STATION | MACK STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2021 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | FAILURE WAS DUE TO ABNORMAL VIBRATIONS OF COMPRESSOR. | CLASS 1 LOCATION | NO |  | 197 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 2181 | 2181 | 1153 | 1153 | 0 | 0 | 0 | 0 |  | 9.36 | 3334 | 1939.714258186360699305647840531561461794 | 3334 | 0 | 0 | 0 | 0 | NO |  |  |  | 1031 | 18100 | 1280 | 192.619(A)(1) |  | 2021-08-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TYPE C GATHERING | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MACK STATION IS NOT REMOTELY CONTROLLED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | FAILURE WAS DUE TO ABNORMAL VIBRATIONS OF COMPRESSOR. | [5 empty] | YES | [177 empty] | GORDON WILLIAMS | ENGINEER - SENIOR PIPELINE COMPLIANCE | gswilliams@eprod.com | 713-381-6211 |  | GORDON WILLIAMS | gswilliams@eprod.com | 713-381-6211 | GORDON WILLIAMS | ENGINEER - SENIOR PIPELINE COMPLIANCE | 713-381-6211 | gswilliams@eprod.com | ON 8-6-2022 AT 00:01 CST, ENTERPRISE RECEIVED A SHUTDOWN ALARM FROM THE MACK STATION COMPRESSOR UNIT 1. AT 00:50, ENTERPRISE ARRIVED AT THE STATION AND SAW THAT UNIT 1 WAS ON FIRE. AT 00:51, ENTERPRISE ISOLATED AND BLEW DOWN THE STATION BY PUSHING THE ESD BUTTON. THE GLASSCOCK POLICE DEPARTMENT AND THE STANTON VOLUNTEER FIRE DEPARTMENT ARRIVED AT THE STATION ON 00:49 AND 01:30, RESPECTIVELY. AT 02:25, ENTERPRISE DETERMINED THAT THE EVENT WOULD MEET THE DEFINITION OF AN INCIDENT BASED ON ANTICIPATED COSTS OF THE UNIT 1 FIRE. UNITS 1 AND 2 ARE LEASED BY ENTERPRISE FROM ARCHROCK AND THE COSTS TO REPAIR OR REPLACE THE UNITS ARE NOT AVAILABLE TO ENTERPRISE. THE NRC AND TXRRC WERE NOTIFIED OF THE EVENT BY ENTERPRISE AT 02:47 AND 02:52, RESPECTIVELY. ON 8-6-2022 AT 06:45, THE FIRE SELF-EXTINGUISHED. UNIT 2, WHICH IS ADJACENT TO UNIT 1, WAS DAMAGED BY THE FIRE; HOWEVER, NO STATION PIPING WAS INVOLVED IN THE FIRE. MACK STATION WAS OUT OF SERVICE FROM 8-6-2022 TO 8-28-2022. UNIT 1 WAS REMOVED FROM MACK STATION AND A REPLACEMENT FOR UNIT 1 WAS PLACED INTO SERVICE ON 8-29-2022. UNIT 2 WAS REPAIRED AND PLACED INTO SERVICE ON 9-23-2022. AN INVESTIGATION OF THE INCIDENT DETERMINED THAT AN ABNORMAL VIBRATION FROM THE SECOND STAGE DISCHARGE RECEIVER CAUSED BOLTS ON THE PIPE FLANGES TO LOOSEN WHICH CAUSED A LOSS OF CONTAINMENT. NATURAL GAS MADE CONTACT WITH AN IGNITION SOURCE AND CAUSED A FIRE.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220096 | 37074 | 2022-09-06 08:04 | ORIGINAL | 31604 | EQUITRANS MIDSTREAM CORPORATION | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2022-08-14 01:40 | 2022 | EASTERN | YES | 39.8239 | -80.8844 | 1344464 | 2022-08-14 11:01 |  | NATURAL GAS |  | 9507 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PART OF COMPRESSOR STATION WITH THE ISSUE WAS ISOLATED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-08-14 01:40 | 2022-08-14 03:10 | ONSHORE | OH | 43942 | POWHATAN POINT | MONROE | NOT APPLICABLE |  | ZINK COMPRESSOR STATION | COMPRESSOR # 5 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | TUBING | [35 empty] | STAINLESS STEEL | RIGID |  | 2015 | 2015 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | STAINLESS STEEL TUBING | OTHER | [8 empty] | TUBING ON A RELIEF VALVE FAILED CAUSING THE RELIEF VALVE TO OPEN AND BEGIN RELEASING GAS. | CLASS 1 LOCATION | NO |  | 620 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 86038 | 86038 | 1150 | 1150 | 0 | 0 | 0 | 0 |  | 9.05 | 87188 | 56960.8409391972083689368770764119601329 | 87188 | 0 | 0 | 0 | 0 | NO |  |  |  | 1521 | 565046 | 1625 | 192.619(A)(2) |  | 2015-01-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TYPE C GATHERING | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER DISCOVERED THE CONDITION AND REPORTED IT APPROPRIATELY. THE CONTROLLER DID NOT HAVE REMOTE CAPABILITIES TO SHUTDOWN THE UNIT AND THEREFORE COULD NOT HAVE MITIGATED GAS LOSS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [16 empty] | YES | [174 empty] | DANIEL MOORE | INTEGRITY ENGINEER II | dkmoore@equitransmidstream.com | 4126390289 |  |  |  |  | JACOB LYONS | MANAGER PIPELINE SAFETY AND COMPLIANCE | 4122953962 | jlyons@equitransmidstream.com | AT APPROXIMATELY 1:40 A.M. ON AUGUST 14TH, 2022, GAS CONTROL RECEIVED A LOW FLOW ALERT FOR EQUITRANS' ZINK COMPRESSOR STATION. GAS CONTROL THEN NOTICED AN APPROXIMATE 250 PSIG DROP IN DISCHARGE PRESSURE ON COMPRESSOR #5 AT THE STATION. THE ON CALL OPERATION EMPLOYEE WAS DISPATCHED AND FOUND A RELIEF VALVE WAS VENTING AT THE STATION. THE RELIEF VALVE CEASED VENTING AT APPROXIMATELY 3:15 A.M.. THE CAUSE FOR THE RELIEF VALVE VENTING WAS DETERMINED TO BE PILOT FAILURE ON THE RELIEF VALVE. PRESSURE AT THE RELIEF VALVE AT THE TIME OF THE PILOT FAILURE WAS APPROXIMATELY THE STATION DISCHARGE PRESSURE OF 1521 PSIG. ONCE THE RELIEF VALVE BEGAN VENTING, THE PRESSURE AT THE RELIEF VALVE DROPPED TO THE STATION SUCTION PRESSURE OF APPROXIMATELY 1040 PSIG. A CALCULATION WAS PERFORMED AND IT WAS DETERMINED THAT THE GAS LOSS EXCEEDED THE 3 MILLION CUBIC FOOT THRESHOLD FOR REPORTING AS PER CFR49 PART 191.3.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220097 | 37086 | 2022-09-07 12:16 | ORIGINAL FINAL | 602 | ENABLE GAS TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-08-31 17:27 | 2022 | CENTRAL | YES | 33.6528 | -94.0982 | 1346087 | 2022-08-31 19:55 | 1346509 | NATURAL GAS |  | 2877 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A 3 WAY STOPPLE FITTING WAS USED TO ALLOW FOR REPAIRS. |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | 3 WAY STOPPLE FITTING |  | OPERATIONAL CONTROL | 3 WAY STOPPLE FITTING |  | 0 | 2022-08-31 17:27 | 2022-08-31 17:27 | ONSHORE | AR | 71822 | ASHDOWN | LITTLE RIVER | NOT APPLICABLE |  | AM-182 | 33.6527893 -94.0982092 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1968 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 7000 | 7000 | 0 | 0 | 27792 | 27792 | 195000 | 195000 | 0 | 0 | 0 | 0 |  | 9.66 | 229792 | 107350.2781599556933355481727574750830565 | 229792 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 3000 | 500 | 192.619(A)(2) |  | 1968-03-11 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 21806 | NO |  |  |  | YES |  |  |  | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY DAMAGE EVENT. THE PERSON WHO DAMAGED THE PIPE CALLED SYSTEM CONTROL AT THE TIME OF THE DAMAGE AND MAD THE NOTIFICATION. ALSO, THERE IS LOW FLOW ON THIS LINE SO DUE TO THE SIZE OF THE SMALL DIAMETER OF THE HOLE CAUSED BY THE DAMAGE IT DID NOT SET OFF ANY ALARMS OR SHOW A SIGNIFICANT DROP IN PRESSURE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | LARGE TRUCK | OFF-ROAD | 0 | NO | [238 empty] | CHARLES ALEXANDER | DOT COMPLIANCE | charles.alexander@energytransfer.com | [5 empty] | JIMMY CROSS | SR. MANAGER COMPLIANCE | 405-576-8230 | jimmy.cross@energytransfer.com | 8.31.22 WHILE CUTTING GRASS ON A TRACTOR, A LANDOWNER RAN OVER A 1" TAP VALVE THAT IS SUSPECTED TO HAVE BECOME EXPOSED DUE TO THE RECENT RAINFALL AMOUNTS IN THE AREA. THE TRACTOR CAUSED DAMAGE TO A PUNCHING TEE BELOW GROUND BY OPENING A 1/8" HOLE IN THE THREADS OF THE TEE. THE LANDOWNER THEN CALLED ET SYSTEM CONTROL AND NOTIFIED THEM OF THE SITUATION. AT 1630 SYSTEM CONTROL NOTIFIED MEMBERS OF THE EMMET TEAM AND THEY CONFIRMED THE DAMAGE AND LEAK AT 1727 OF THE SAME DAY. THE DECISION WAS MADE TO LOWER THE LINE PRESSURE FROM 350 TO 200PSI AND MONITOR UNTIL REPAIRS COULD BEGIN ON 9.1.22, DUE TO THE NEED TO MAINTAIN DELIVERY TO A CUSTOMER. THE INITIAL BELIEF WAS WE WOULD NOT EXCEED THE REPORTING THRESHOLD, AS WE BELIEVED WE COULD EXPOSE THE VALVE AND SHUT THE FLOW OFF. FURTHER INVESTIGATION OF THE DAMAGED FITTING REVEALED BROKEN THREADS BELOW THE VALVE. ONCE WE DISCOVERED THIS WE MADE THE REPORT, AS THE REPORTING CRITERIA WOULD BE MET BEFORE THE REPAIRS COULD BE COMPLETED. REPAIRS BEGAN AT APPROXIMATELY 1730 ON 9.1.22 AND CONTINUED INTO 9.2.22. THE LEAK WAS TERMINATED AT 0300 ON 9.2.22. ET EMPLOYEES AND CONTRACTORS INSTALLED A THREE-WAY STOPPLE FITTING AND REPLACED A 5' SECTION OF THE PIPE TO COMPLETE THE REPAIR. THE DAMAGED COMPONENT WAS REMOVED FROM THE SYSTEM. THERE WERE NO INJURIES OR INTERRUPTION TO CUSTOMERS AS A RESULT OF THIS EVENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220098 | 37155 | 2022-09-09 09:31 | SUPPLEMENTAL FINAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-09-03 07:51 | 2022 | CENTRAL | YES | 33.3316 | -85.0092 | 1346318 | 2022-09-03 10:27 | 1346427 | NATURAL GAS |  | 15 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELEASE DID NOT IMPACT PIPELINE OPERATIONS |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-09-03 07:52 | NO | [5 empty] | OPERATIONAL CONTROL | THE RATE OF DROP DEVICE WAS RETURNED TO NORMAL OPERATION. SITE WAS RETURNED TO NORMAL OPERATION. |  | OPERATIONAL CONTROL | THE RATE OF DROP DEVICE WAS RETURNED TO NORMAL OPERATION. SITE WAS RETURNED TO NORMAL OPERATION. |  | 4 | 2022-09-03 07:52 | 2022-09-03 09:02 | ONSHORE | GA | 30217 | Not Within a Municipality | HEARD | MILEPOST | 1001.35 | 110C20 VALVE SETTING | 110C20 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REGULATOR/CONTROL VALVE | [38 empty] | 1961 | 1961 | CARBON STEEL |  | OTHER | [8 empty] | THE RATE OF DROP TRIGGERED A PILOT DUE TO FLOW FLUCTUATION FROM THE DOWNSTREAM LOCATION, INITIATING RELEASE AT THE CONTROL DEVICE. THE CONTROL DEVICE FUNCTIONED AS DESIGNED. | CLASS 2 LOCATION | NO |  | 644 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 122 | 122 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8.14 | 122 | 80.04983388704318936877076411960132890365 | 122 | 0 | 0 | 2 | 0 | NO |  |  |  | 703 | 1000000 | 800 | 192.619(A)(1) |  | 2001-08-04 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 1 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RATE OF DROP OF VALVE PILOT WORKED AS DESIGNED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | RATE OF DROP SENSED A PRESSURE DIFFERENCE TRIGGERING THE VALVE TO RELEASE GAS. | [15 empty] | YES | RATE OF DROP SENSED A PRESSURE DIFFERENCE TRIGGERING THE VALVE TO RELEASE GAS. | [161 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-303-9956 |  | KEVIN MAZINGO | kevin.l.mazingo@williams.com | 205-417-5097 | JOHN BELL | MANAGER PIPELINE SAFETY | 337-317-9145 | john.bell@williams.com | 110C20 BLOCK VALVE HAS A RATE OF DROP ON IT THAT SENSES PRESSURE, IT TRIGGERED AND CLOSED THE VALVE, BUT THE PILOT CONTINUED VENTING NATURAL GAS. THERE ARE HOUSES NEARBY, AND THE NOISE OF THE RELEASE IS WHAT CAUSED THE OWNERS TO CALL 911 TO REPORT THE NOISE. LOCAL 911 EVACUATED 2 HOMES AND CLOSED COUNTY ROAD 34 (ENON GROVE RD) UNTIL WILLIAMS ARRIVED AND STOPPED THE RELEASE. RATE OF DROP DEVICE RESET AND THE ROAD WAS OPENED AGAIN, AND THE HOMEOWNERS ARE BACK IN THEIR HOMES. UPDATE - THIS REPORT WAS DONE SOLELY ON THE BASIS OF OPERATOR JUDGEMENT DUE TO THE 911 CALL AND FIRST RESPONDERS CLOSING ENON GROVE RD.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220099 | 37455 | 2022-09-09 12:50 | SUPPLEMENTAL FINAL | 32363 | MID-CONTINENT MARKET CENTER | 100 WEST FIFTH STREET | TULSA | OK | 74103-4298 | 2022-08-11 21:01 | 2022 | CENTRAL | YES | 37.587 | -98.2355 | 1344257 | 2022-08-11 22:51 | 1344347 | NATURAL GAS |  | 4110 | 307 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-08-11 21:30 | 2022-08-15 19:00 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-08-11 21:30 | VALVE CLOSURE |  | 2022-08-11 20:10 | 0 | 2022-08-11 21:05 | 2022-08-11 21:05 | ONSHORE | KS | 67068 | Not Within a Municipality | KINGMAN | MILEPOST | 7M SW KINGMAN | MID-CONTINENT MARKET CENTER | 1204 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12.75 | NO | 0.375 | 35000 | GRADE B - .375 WALL | LAP WELDED |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1955 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 84 | 12 |  | CLASS 1 LOCATION | NO |  | 226 |  | NO | NO |  |  | NO |  |  | 1500 | 1500 | 2527 | 2527 | 33825 | 33825 | 19500 | 19500 | 1100 | 1100 | 0 | 0 |  | 8.23 | 58452 | 33058.6337214863637181694352159468438538 | 58452 | 0 | 0 | 0 | 0 | NO |  |  |  | 659 | 5000 | 660 | 192.619(C) |  | 1970-11-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | REMOTELY CONTROLLED | 89760 | NO | YES | [6 empty] | YES |  |  |  |  | YES | NOMINAL PIPE SIZE CHANGES | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | [6 empty] | YES | THREE PRESSURE INDICATORS DROPPED FROM 656 PSI TO 5 PSI WITH NO RESPONSE FROM CONTROLLER. THERE WAS NO RESPONSE FROM THE CONTROL ROOM UNTIL THE CALL WAS RECEIVED FROM THE EMERGENCY RESPONDERS. | YES | 1 | 0 | NO |  |  | MATERIAL FAILURE OF PIPE OR WELD | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) | MATERIAL/WELD/EQUIP FAILURE | MANUFACTURING-RELATED | [132 empty] | ORIGINAL MANUFACTURING-RELATED (NOT GIRTH WELD OR OTHER WELDS FORMED IN THE FIELD) |  | YES | [13 empty] | YES | SEE NARRATIVE. | [13 empty] | YES | SEE NARRATIVE. | UNKNOWN | [54 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | BRENT THEEDE | SUPERVISOR - REGULATORY COMPLIANCE | brent.theede@oneok.com | 6208203047 |  | BRENT THEEDE | brent.theede@oneok.com | 6208203047 | BRENT THEEDE | SUPERVISOR - REGULATORY COMPLIANCE | 6208203047 | brent.theede@oneok.com | ON 8/11/22, AN INCIDENT OCCURRED ON THE MCMC 1204 PIPELINE. OPERATIONS RESPONDED AND DISCOVERED A PIPELINE RUPTURE APPROXIMATELY 7 MILES SOUTHWEST OF KINGMAN, KS. THE PIPELINE WAS ISOLATED, BLOWN DOWN, AND DAMAGED SECTION OF PIPE REMOVED FOR METALLURGICAL ANALYSIS. GAS LOSS WAS CALCULATED AT 4.11 MMCF. UPDATE: THE FAILURE ANALYSIS REPORT INDICATED FATIGUE CRACKS LOCATED ON THE INSIDE DIAMETER AND AT INTERNAL METALLURGICAL DEFECTS AT THE LOCATION OF THE RUPTURE. THE RUPTURE OCCURRED AT A BULGE IN THE PIPE DUE TO FATIGUE CRACKING, WHICH REDUCED EFFECTIVE WALL THICKNESS THAT COULD NO LONGER CONTAIN NORMAL PIPELINE PRESSURE. THE ANALYSIS INDICATED THAT BULK ALLOY CHEMISTRY DID NOT CONTRIBUTE TO THE CAUSE OR MECHANISM OF THE RUPTURE. THE FAILURE DID NOT OCCUR AT A GIRTH OR LONG SEAM WELD. BRENT THEEDE 12/12/2022
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220100 | 37098 | 2022-09-09 14:04 | ORIGINAL FINAL | 40069 | STINGRAY PIPELINE COMPANY, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-08-17 09:55 | 2022 | CENTRAL | YES | 28.3047 | -93.2692 | 1344742 | 2022-08-17 10:50 | 13448931345524 | NATURAL GAS |  | 5.6 | 12839.7 | 98.11 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | POST-MAINTENANCE/REPAIR | [5 empty] | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-08-18 18:45 | NO | [5 empty] | VALVE CLOSURE |  | 2022-02-27 17:00 | VALVE CLOSURE |  | 2022-08-17 08:45 | 0 | 2022-08-17 07:43 | 2022-08-17 08:00 | OFFSHORE | [6 empty] | STINGRAY PIPELINE | STINGRAY 30-INCH OFFSHORE PIPELINE (PSN 3394) | [20 empty] | 190 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | WEST CAMERON | 550 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 30 | NO | 0.568 | 60000 | API 5L X-60 | DSAW |  | US STEEL | OTHER | CONCRETE | UNKNOWN | [26 empty] | 1975 | 1975 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 717 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 122106 | 122106 | 53 | 53 | 482592 | 482592 | 209195 | 209195 | 0 | 0 |  | 9.51 | 813946 | 359093.1958178133376188405315614617940199 | 813946 | 0 | 0 | 0 | 0 | NO |  |  |  | 300 | 0 | 1200 | 192.619(A)(1) |  | 1975-03-03 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 318991 | YES | [7 empty] | YES |  |  |  |  | YES | LAUNCHER IS SUBSEA | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | THIRD PARTY PRODUCER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DUE TO A SMALL PINHOLE LEAK AND TOO SMALL FOR SCADA TO DETECT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES |  |  |  | YES |  | YES |  |  |  | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | PEGGY WEST |  | peggy.west@energytransfer.com | [5 empty] | CHRIS KRESTA |  | 713-989-7077 | chris.kresta@energytransfer.com | ON 8/17/22 AT APPROXIMATELY 07:43, WHILE RE-PRESSURIZING LINE SEGMENT 3394, ENERGY TRANSFER WAS NOTIFIED BY A PRODUCER THAT A SHEEN WAS SPOTTED IN THE VICINITY OF STINGRAY 30-INCH LINE SEGMENT 3394 IN THE WC550 BLOCK. STEPS WERE IMMEDIATELY TAKEN TO SHUT IN AND ISOLATE LINE. A CALL WAS PLACED TO THE NRC BY THE PRODUCER. ET CONFIRMED THE SHEEN WITH AN OVERFLIGHT. ET OUTSOURCED A DEPRESSURIZATION SPREAD AND DIVE COMPANY TO INVESTIGATE THE LEAK SITE. A NOTIFICATION WAS MADE TO THE NRC AT 10:50 (NRC # 1344742) AND THE 48-HOUR NRC NOTIFICATION WAS MADE ON 8/18/22 AT 16:22 (NRC # 1344893). OUR CREW AT WC509 IS WORKING TO REMOVE PRESSURE FROM THE LINE. THE DEPRESSURIZATION VESSEL ARRIVES ONSITE, 8/20/22, TO EXPEDITE THE PROCESS. ON 8/22/22, THE DSV MESOTECH SONAR CONFIRMS THIS IS OUR LINE AND A NEW LEAK. DUE TO THE LINE PRESSURE AND CONDENSATE, THE DSV WAS UNABLE TO DIVE. VENTING AND DEPRESSURIZATION SPREAD CONTINUED UNTIL CONDENSATE WAS NO LONGER VISIBLE. THE DSV ARRIVED ONSITE AT APPROXIMATELY 01:00 ON 8/24/22. DIVERS CONFIRMED A PIN HOLE LEAK AT THE 6 OCLOCK POSITION IN A FIELD JOINT. THE DEPRESSURIZATION VESSEL WILL STAY AT WC 509 UNTIL THE CLAMP IS INSTALLED. ENERGY TRANSFER CALLED THE NRC ON 8/25/22 AT 13:33 TO TAKE OWNERSHIP OF THE RELEASE AND UPDATE RESPONSIBLE PARTY TO STINGRAY. NRC# 1345524 A CLAMP WAS INSTALLED ON THE 30-INCH LINE AND IT WAS RETURNED TO SERVICE ON 8/27/22.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220101 | 37140 | 2022-09-13 16:14 | SUPPLEMENTAL FINAL | 31613 | MIDCOAST PIPELINES (EAST TEXAS), L.P. | 600 TRAVIS SUITE 5500 | HOUSTON | TX | 77002 | 2022-08-22 17:45 | 2022 | CENTRAL | NO | 31.8939 | -95.9388 | 1345234 | 2022-08-22 18:07 | 1345390 | NATURAL GAS |  | 10708 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MIDCOAST WAS ABLE TO MANUAL BLOCK IN ESD VALVE |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-08-22 12:53 | 2022-08-22 13:43 | ONSHORE | TX | 75861 | TENNESSEE COLONY | ANDERSON | NOT APPLICABLE |  | BETHEL STATION | TXDD-36 BETHEL TO CARTHAGE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2019 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | MECO REGULATOR FAILED, THAT SUPPLIED SUPPLY GAS TO VALVE WHICH KEPT VALVE CLOSED | CLASS 1 LOCATION | NO |  | 829 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 89251 | 89251 | 0 | 0 | 0 | 0 | 525 | 525 | MECO REGULATOR REPLACEMENT | 8.335 | 89776 | 58793.3125506764086450996677740863787375 | 89776 | 0 | 0 | 0 | 0 | NO |  |  |  | 689 | 50000 | 1050 | 192.619(A)(2) |  | 2005-05-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INITIAL RESPONSE TO INVESTIGATION DETERMINED EQUIPMENT FAILURE LOCALLY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | YES | [24 empty] | YES | REGULATOR MALFUNCTION RESULTING IN FAILURE | [161 empty] | BENITA KALKA | GIS ANALYST | benita.kalka@midcoastenergy.com | 17138212072 |  | BENITA KALKA | benita.kalka@midcoastenergy.com | 17138212072 | BENITA KALKA | GIS ANALYST | 17138212072 | benita.kalka@midcoastenergy.com | A FAILED REGULATOR, CONTROLLING THE COMPRESSOR SUCTION LINE ESD VALVE, ALLOWED THE ESD VALVE TO OPEN RESULTING IN GAS RELEASE TO ATMOSPHERE. THE COMPRESSOR SUCTION LINE WAS MANUALLY ISOLATED AND BLOCKED IN THUS STOPPING THE RELEASE OF GAS TO THE ATMOSPHERE. THE FAILED REGULATOR WAS REPLACED WITH A NEW REGULATOR. A REDUNDANT SOURCE FROM ANOTHER SUPPLY, INCLUDING AN ADDITIONAL REGULATOR, WAS ADDED TO PREVENT FUTURE EVENTS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220102 | 37157 | 2022-09-23 12:06 | ORIGINAL | 13063 | NATIONAL FUEL GAS SUPPLY CORP | 6363 MAIN STREET | WILLIAMSVILLE | NY | 14221-5887 | 2022-08-24 09:51 | 2022 | EASTERN | YES | 41.8999 | -77.9148 | 1345378 | 2022-08-24 10:35 | 1345573 | NATURAL GAS |  | 34.579 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | SECTION OF STATION PIPING ISOLATED BUT OPERATION OF CONNECTED PIPELINE CONTINUED |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-08-24 09:51 | 2022-08-24 09:51 | ONSHORE | PA | 16923 | GENESEE | POTTER | NOT APPLICABLE |  | ELLISBURG COMPRESSOR STATION | ELLISBURG STORAGE DISCHARGE HEADER | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2020 | 2018 | CARBON STEEL |  | OTHER | [8 empty] | STORAGE HEADER ESD BLOWDOWN | CLASS 1 LOCATION | NO |  | 403 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 265 | 265 | 310841 | 310841 | 6480 | 6480 | 0 | 0 |  | 7.65 | 317586 | 140163.7507663331053262026578073089700997 | 317586 | 0 | 0 | 0 | 0 | NO |  |  |  | 1739 | 0 | 2372 | 192.619(A)(2) |  | 2020-06-29 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AT TIME OF INCIDENT, FACILITY UNDER LOCAL CONTROL WITH CONTROL ROOM MONITORING | [12 empty] | YES | 2 | 0 | YES | 2 | 0 | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | ESD VENT STACK ASSEMBLY FAILURE |  |  | YES | [175 empty] | STEVEN MONNIE | INTEGRITY ENGINEER | monnies@natfuel.com | (814) 871-8204 |  |  |  |  | BRIAN KEMPSKI | SUPERINTENDENT | (716) 827-2131 | kempskib@natfuel.com | ON AUGUST 24, 2022 AT 9:51 AM EST, ELLISBURG COMPRESSOR STATION EXPERIENCED AN ESD SYSTEM ACTIVATION ON THE STORAGE DISCHARGE HEADER WHICH RESULTED IN FAILURE OF THE VENT STACK ASSEMBLY. THE FORCE FROM THE RELEASE OF VENTING GAS DAMAGED A NEARBY STATION BUILDING. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THE EVENT.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220103 | 37185 | 2022-09-26 09:28 | SUPPLEMENTAL FINAL | 31565 | GULFSTREAM MANAGEMENT & OPERATING SERVICES,LLC | 4610 BUCKEYE RD | PALMETTO | FL | 34221 | 2022-09-17 14:00 | 2022 | EASTERN | YES | 27.4996 | -81.2779 | 1347536 | 2022-09-17 16:11 | 1347582 | NATURAL GAS |  | 8145 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELEASE DID NOT IMPACT PIPELINE OPERATIONS |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-09-17 14:00 | 2022-09-17 15:15 | ONSHORE | FL | 33870 | Not Within a Municipality | HIGHLANDS COUNTY | MILEPOST | 521.5 | COMPRESSOR STATION 430 | ML 500 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2008 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | A LIGHTING STRIKE CAUSED THE ESD VALVE TO OPEN, BUT THERE WAS ALSO OPERATOR ERROR BY LEAVING THE LOADING LINE PARTIALLY OPEN DURING ESD TEST PERFORMED A COUPLE OF DAYS EARLIER. | CLASS 1 LOCATION | NO |  | 205 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 63205 | 63205 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7.76 | 63205 | 41471.7192691029900332225913621262458472 | 63205 | 0 | 0 | 0 | 0 | NO |  |  |  | 300 | 129600 | 1480 | 192.619(A)(1) |  | 2004-08-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ESD WAS CAUSED BY LIGHTNING STRIKE, DAMAGING VALVE SOLENOID | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | [204 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | [5 empty] | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-303-9956 |  | SHAWN DEUTSCHER | shawn.deutscher@williams.com | 941-232-1488 | JOHN BELL | MANAGER PIPELINE SAFETY | 337-317-9145 | john.bell@williams.com | ON WEDNESDAY, SEPTEMBER 14TH THE ANNUAL ESD TEST WAS PERFORMED AT COMPRESSOR STATION 430. ONCE COMPLETED THE TWO TECHNICIANS WERE PUTTING THE STATION BACK IN SERVICE AND WERE REPRESSURIZING THE SUCTION AND DISCHARGE HEADERS UTILIZING THE 4" LOADING LINES AROUND THE STATION SIDE GATES. TECHNICIAN 1 WAS TAKING CARE OF THE SUCTION HEADER, AND TECHNICIAN 2 WAS TAKING CARE OF THE DISCHARGE HEADER. ONCE THE VALVES WERE PARTIALLY OPENED, AND THE LINES WERE BEING PRESSURED UP TECHNICIAN 1 NOTICED A WASP NEST NEAR HIM AND RETURNED TO HIS VEHICLE TO GRAB A CAN OF WASP SPRAY. HE SPRAYED DOWN THE NEST AND RETURNED THE CAN TO HIS TRUCK. HE THEN PROCEEDED TO TECHNICIAN 2 TO DISCUSS THE NEXT STEPS IN THE PROCEDURE. THE LINES CONTINUED TO PACK UP TO LINE PRESSURE. TECHNICIAN 1 FAILED TO RETURN TO AND CLOSE THE 4" LOADING LINE ON THE SUCTION HEADER. BOTH TECHNICIANS CONTINUED AND BROUGHT THE STATION BACK INTO SERVICE. ON SATURDAY, SEPTEMBER 17TH A THUNDERSTORM ROLLED THROUGH THE AREA, AND A LIGHTNING STRIKE CAUSED A STATION EBD. GAS CONTROL CALLED TECHNICIAN 1 WHO WAS WORKING ON EQUIPMENT AT ANOTHER STATION WHEN PIPELINE CONTROL CALLED HIM TO MAKE HIM AWARE OF THE BLOWDOWN EVENT. THE STATION WAS NOT ONLINE AT THE TIME, SO THE EMPLOYEE INFORMED GAS CONTROL HE WOULD SWING BY ON HIS WAY HOME. THE EMPLOYEE WRAPPED UP WHAT HE WAS DOING AND LOGGED IN REMOTELY TO THE STATION HMI AND NOTICED ONLY THE SUCTION HEADER HAD BLOWN DOWN, BUT THE TRANSMITTER WAS STILL SHOWING 300 PSI. TECHNICIAN 1 RECOGNIZED THIS WAS ABNORMAL AND CALLED THE MANAGER OF OPERATIONS. THE MANAGER OF OPERATIONS LOGGED INTO THE SECURITY CAMERAS AND WAS ABLE TO DETERMINE THAT GAS WAS STILL BLOWING FROM THE SUCTION LINE BLOWDOWN VENT. THIS WAS APPROXIMATELY 30 MINUTES AFTER THE INITIAL CALL THAT THE STATION HAD BLOWN DOWN. TECHNICIAN 1 STARTED HEADING TO THE STATION BUT WAS AN HOUR AWAY, MANAGER OF OPERATIONS CALLED TECHNICIAN 2, AND HE ALSO STARTED HEADING TO THE STATION. BOTH TECHS ARRIVED AT STATION 430C AT APPROXIMATELY THE SAME TIME AND FOUND THE 4" SUCTION LOADING VALVE PARTIALLY OPEN FROM THE ESD TEST THAT WAS PERFORMED ON WEDNESDAY. GAS VENTED FOR 90 MINUTES AT 300PSI FOR A TOTAL OF 8.145MMSCF THE LIGHTNING STRIKE HAD BLOWN 2 FUSES AND BURNED UP THE SOLENOID ON THE SUCTION BLOW-DOWN VALVE, WHICH IS WHY IT ACTUATED AND THE DISCHARGE BLOWDOWN DID NOT. EMPLOYEES WERE NOT ABLE TO MAKE REPAIRS THAT EVENING AS THE THUNDERSTORM CONTINUED WITH HEAVY RAIN AND LIGHTNING. EMPLOYEES RETURNED THE NEXT MORNING AND MADE REPAIRS AND PUT THE STATION BACK IN SERVICE. AN INVESTIGATION WILL BE CONDUCTED AND MOVING FORWARD THE LOADING VALVES ON THE STATION SUCTION AND DISCHARGE WILL BE ADDED TO THE SAFETY CRITICAL DEVICE LIST AND WILL HAVE CAR SEALS INSTALLED THAT WILL REQUIRE REMOVAL AND INSTALLATION ANYTIME THE VALVES ARE OPERATED IN ORDER TO CONFIRM THEY ARE LEFT IN THE CORRECT POSITION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220104 | 37641 | 2022-09-30 19:10 | SUPPLEMENTAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2022-09-02 09:14 | 2022 | PACIFIC | YES | 34.5319 | -118.649 | 1346206 | 2022-09-02 06:41 | 1346389 | NATURAL GAS |  | 4152 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-09-02 13:59 |  | YES |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-09-02 13:58 | VALVE CLOSURE |  | 2022-09-02 13:58 | 0 | 2022-09-02 04:31 | 2022-09-02 12:18 | ONSHORE | CA | 91384 | CASTAIC | LOS ANGELES | MILEPOST | 141.57 | L-85 | M.P 141.57 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | WELD/FUSION, INCLUDING HEAT-AFFECTED ZONE | [19 empty] | OTHER BUTT WELD | [18 empty] | 1931 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 24912 | 24912 | 130000 | 130000 | 0 | 0 | 0 | 0 |  | 6 | 154912 | 73696.9347126585684717607973421926910299 | 154912 | 0 | 0 | 0 | 0 | YES |  | YES | YES | 120 | 120 | 120 | 192.619(A)(1) |  | 2018-11-26 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | NO |  | MANUAL | MANUAL | 81892 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ISSUE FOUND | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [52 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION. WILDFIRE OCCURRED AROUND AND NEAR L-85 SPAN. | YES |  |  |  | YES | HIGH SEASONAL WINDS OCCURRING AT THE TIME OF INCIDENT. | [270 empty] | YES | [30 empty] | FRANK SANTA CRUZ |  | fsantacruz@socalgas.com | 213-407-0168 |  |  |  |  | FRANK SANTA CRUZ |  | 213-407-0168 | fsantacruz@socalgas.com | ON 09/02/2022, SOCALGAS WAS NOTIFIED OF A WILDFIRE IN THE AREA OF CASTAIC NAMED THE ROUTE FIRE. SOCALGAS CREWS INVESTIGATED REPORTS OF AN AUDITABLE LEAK AT AN ABOVE GROUND SPAN ON TRANSMISSION LINE 85. AS A PRECAUTIONARY MEASURE THE TRANSMISSION PIPELINE WAS ISOLATED AND IS STILL CURRENTLY OUT OF SERVICE WITH INVESTIGATION ONGOING. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND DAMAGES EXCEEDING $129,000. SOCALGAS IS CURRENTLY NEGOTIATING WITH CONTRACTORS FOR ASSESSMENT AND REPAIRS AND DEVELOPING ENGINEERING SOLUTIONS FOR L-85 SPAN REPAIRS.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220105 | 37215 | 2022-10-03 12:00 | SUPPLEMENTAL FINAL | 31613 | MIDCOAST PIPELINES (EAST TEXAS), L.P. | 600 TRAVIS SUITE 5500 | HOUSTON | TX | 77002 | 2022-09-06 08:30 | 2022 | CENTRAL | NO | 31.7639 | -94.4048 | 1346518 | 2022-09-06 08:53 | 1346709 | NATURAL GAS |  | 18557.79 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MIDCOAST WAS ABLE TO PUT ON SPARE UNIT. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-09-06 07:15 | 2022-09-06 07:15 | ONSHORE | TX | 75975 | TIMPSON | SHELBY | NOT APPLICABLE |  | GRAND OAKS STATION | GRAND OAKS STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2008 | UNKNOWN | CARBON STEEL |  | OTHER | [9 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 154679 | 154679 | 0 | 0 | 0 | 0 | 6 | 6 | INSTALLED THREEDED PLUG | 8.335 | 154685 | 101494.6818539251485145581395348837209302 | 154685 | 0 | 0 | 0 | 0 | NO |  |  |  | 820 | 95000 | 1440 | 192.619(A)(2) |  | 2008-09-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TYPE C GATHERING | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INITIAL RESPONSE TO INVESTIGATION DETERMINED EQUIPMENT FAILURE LOCALLY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE |  |  |  |  | YES | [165 empty] | YES | [11 empty] | BENITA KALKA | GIS ANALYST | benita.kalka@midcoastenergy.com | 17138212072 |  | BENITA KALKA | benita.kalka@midcoastenergy.com | 17138212072 | BENITA KALKA | GIS ANALYST | 17138212072 | benita.kalka@midcoastenergy.com | MIDCOAST GC RECEIVED A CALL 9/6/2022 @ 6:00 A.M. CONCERNING A "HISSING" NOISE COMING FROM OUR STATION. GC DISPATCHED ON CALL OPERATOR TO SITE @ 6:20 A.M. OPERATOR ARRIVED ON SITE AT 7:15 A.M. AND DISCOVERED A NIPPLE HAD FAILED CASING THE RELEASE, THE OPERATOR SHUTDOWN COMPRESSOR AT 7:16 A.M. MIDCOAST OPERATOR ISOLATED COMPRESSOR AND DEPRESSURIZED IMMEDIATELY. MIDCOAST OPERATOR PUT ON A SPARE UNIT AND REPAIRED LEAK BY INSTALLING A PLUG.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20220106 | 37543 | 2022-10-03 17:07 | SUPPLEMENTAL FINAL | 32549 | GILL RANCH STORAGE LLC | 10000 MEMORIAL DR SUITE 330 | HOUSTON | TX | 77024 | 2022-09-03 13:43 | 2022 | PACIFIC | YES | 36.7879 | -120.2301 | 1346366 | 2022-09-03 17:12 | 1346484 | NATURAL GAS |  | 1 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | WELL 32-21-106 WAS TAKEN OUT OF SERVICE FOR WELLHEAD REPLACEMENT. |  |  |  | YES | OPERATOR | 2022-09-03 17:12 | NO | [11 empty] | 0 | 2022-09-03 13:43 | 2022-09-03 13:43 | ONSHORE | CA | 93637 | Not Within a Municipality | MADERA | NOT APPLICABLE |  | WELL 32-21-106 | N/A | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTRASTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2022 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 1 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 91000 | 91000 | 429000 | 429000 | SECURING NECESSARY RESOURCES (NEEDED & CAUTIONARY). | 8 | 520008 | 229409.3335350196559468438538205980066445 | 520008 | 0 | 0 | 0 | 0 | NO |  |  |  | 2150 | 0 | 5000 | OTHER | WELL PRESSURE ESTABLISHED BY WELLHEAD EQUIPMENT. | 2022-08-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | WIRELINE TOOLS MALFUNCTIONED RESULTING IN THE TOOL STRING LODGING IN THE 7 1/16" WELLHEAD VALVE. | [15 empty] | YES | WIRELINE TOOLS MALFUNCTIONED RESULTING IN THE TOOL STRING LODGING IN THE 7 1/16" | [149 empty] | YES | YES | [10 empty] | TIMOTHY MORGAN | VICE PRESIDENT - REGSAFE | timothy.morgan@regsafe.com | 281-357-5577 | 281-516-9578 |  |  |  | JOHN THRASH | CEO | 713-520-0993 | jfthrash@ecorpintl.com | ENTERED WELL 32-21-106 TO ISOLATE PRESSURE FROM SURFACE TO REPLACE WELLHEAD AS PART OF MAINTENANCE. NOTE, THIS WELLHEAD REPLACEMENT WAS FOR SAFETY ENHANCEMENT AND MECHANICAL INTEGRITY. WHILE RETRIEVING THE WIRELINE TOOL IT BECAME LODGED IN THE 7 1/16" WELLHEAD PRIMARY ISOLATION VALVE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220107 | 37205 | 2022-10-07 13:34 | ORIGINAL | 38902 | HIGH POINT GAS TRANSMISSION, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2022-09-08 16:12 | 2022 | CENTRAL | YES | 29.7919 | -89.8053 | 1346790 | 2022-09-08 16:48 | 1346927 | NATURAL GAS |  | 35000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PIPELINE WAS ALREADY DOWN DUE TO BUSINESS NEEDS | [6 empty] | YES | 2022-09-08 16:12 | ALLOWED TO BURN OUT |  | 35000 | NO | VALVE CLOSURE |  | 2022-09-08 10:00 | VALVE CLOSURE |  | 2022-09-08 17:15 | 0 | 2022-09-08 16:12 | 2022-09-08 17:00 | ONSHORE | LA | 70040 | ST BERNARD | PLAQUEMINES | MILEPOST | 51.18 | MAIN PASS TO FRANKLIN 20" | GATE 6 TO TOCA 20" | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  |  | NO | YES | [6 empty] | YES | UNCASED | LAKE LERY | 6 | BELOW WATER, PIPE BURIED BELOW BOTTOM (NOT IN BORED/DRILLED CROSSING) | YES | [10 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.344 | 52000 | X-52 | FLASH WELDED |  | A.O. SMITH | OTHER | CONCRETE | NO | [26 empty] | 1953 | 1953 | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 20 | 1 |  | CLASS 1 LOCATION | NO |  | 447 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 279650 | 279650 | 1300000 | 1300000 | 341000 | 341000 | 0 | 0 |  | 7.99 | 1920650 | 907437.6299234675688604651162790697674419 | 1920650 | 0 | 0 | 0 | 0 | NO |  |  |  | 1051 | 0 | 1072 | OTHER | PRIOR TO CODE | 1959-10-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | NICKLAS PAVLOVSKY | MANAGER PIPELINE REGULATORY COMPLIANCE | npavlovsky@third-coast.com | 3462413368 |  |  |  |  | NICKLAS PAVLOVSKY | MANAGER PIPELINE REGULATORY COMPLIANCE | 3462413368 | npavlovsky@third-coast.com | ON 9/08/22 AT APPROXIMATELY 4:12PM THIRD COAST (HIGH POINT GAS TRANSMISSION (HPGT)) CONTROL CENTER RECEIVED A CALL FROM ST. BERNARD PARISH FIRE DEPARTMENT STATING THAT OUR PIPELINE IN LAKE LERY HAD POSSIBLY BEEN STRUCK BY A VESSEL OR BARGE AND THAT THERE WAS A NATURAL GAS LEAK AND FIRE. HPGT MOBILIZED AN AIRCRAFT TO CONDUCT AN OBSERVATION AND CONFIRMED THE LEAK TO BE FROM THE MAIN PASS TO FRANKLINTON 20' IN A NORTH-SOUTH DIRECTION SINCE THERE ARE SEVERAL PIPELINES IN THE SAME RIGHT-OF-WAY, ONE BEING OWNED AND OPERATED BY ANOTHER OPERATOR. BETWEEN THE CONTROL CENTER SEEING A PRESSURE DROP AND THE AERIAL OBSERVATION, IT WAS CONFIRMED THAT THE RELEASE WAS FROM THE HPGT MAIN PASS TO FRANKLINTON 20' (TOCA TO GATE 6' SEGMENT). THE ICS WAS ESTABLISHED WITH FOREFRONT EMERGENCY MANAGEMENT. ST. BERNARD FIRE DEPARTMENT MADE AN INITIAL NRC NOTIFICATION (9/8/22 NRC# 1346786). ON BEHALF OF HPGT, FOREFRONT MADE AN NRC CALL (NRC# 1346790) TO TAKE RESPONSIBILITY FOR THE RELEASE AND REPORT MORE INFORMATION. THE UPSTREAM VALVE HAD BEEN CLOSED EARLIER IN THE DAY DUE TO BUSINESS NEEDS. AT THE TIME OF THE RELEASE THE DOWNSTREAM VALVE WAS CLOSED COMPLETELY ISOLATING THE RUPTURE. THERE IS APPROXIMATELY 17 MILES BETWEEN VALVES WITH A CALCULATED 35MMCF OF NATURAL GAS IN THE SEGMENT. THE ST. BERNARD AND PLAQUEMINE PARISH WATER AUTHORITIES ASSUMED RESPONSIBILITY FOR PATROLLING THE LAKE AND KEEPING ALL BOATING TRAFFIC AWAY FROM THE FIRE. MULTIPLE FLIGHTS WERE TAKEN BY HPGT TO MONITOR THE FIRE. ALL 35MMCF OF GAS WAS CONSUMED BY THE FIRE. THE FIRE BURNT ITSELF OUT 4:39 ON 9/9/22. A BOOM WAS PLACED 360 DEGREES AROUND THE RELEASE POINT TO CATCH ANY RESIDUAL CONDENSATE. NO PRODUCT WAS OBSERVED COMING FROM PIPE AFTER FIRE WAS EXTINGUISHED. ON 9/10/22 AT 9:29AM A 48HR CALL WAS PLACED TO THE NRC (NRC# 1346927) TO UPDATE THAT THE FIRE WAS EXTINGUISHED, THE VOLUME RELEASED, GPS COORDINATES AND OTHER UPDATED INFORMATION. ON MONDAY 9/12/22 A SURVEYING COMPANY MARKED ALL THREE PIPELINES IN THE RIGHT-OF-WAY THOUGH THE ENTIRE LAKE. ON TUESDAY 9/13/22'THURSDAY 9/15/22, A DIVING COMPANY ARRIVED ON SITE TO ASSESS THE DAMAGE TO THE 20' AND ASSESSED THE OTHER 2 PIPELINES FOR ANY DAMAGE. NO DAMAGE WAS NOTED TO THE OTHER PIPELINES AND FLOW CONTINUED ON THOSE PIPELINES. THE DIVERS CUT THE 20' BACK ON GOOD PIPE BOTH UPSTREAM AND DOWNSTREAM OF THE RUPTURE. PLUGS WERE INSTALLED ON BOTH ENDS TO PREVENT ANY POSSIBLE RELEASE OF ANY RESIDUAL PRODUCT. BOTH SECTIONS OF CUT PIPE (UPSTREAM/DOWNSTREAM) WERE RECOVERED TO THE SURFACE AND PRESERVED FOR METALLURGICAL ANALYSIS. THE SPECIMENS WERE SENT TO A LAB IN HOUSTON, TX, FOR ANALYSIS. PLANNED REPAIR WILL BE TO INSTALL FLANGES AND DROP IN A SPOOL PIECE. DUE TO BUSINESS NEEDS, ONCE THE PIPE IS REPAIRED, THE 20' LINE FROM GATE 6 TO TOCA STATION WILL BE PURGED AND PLACED UNDER A NITROGEN BLANKET AND AIR GAPPED AT GATE 6.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220108 | 37221 | 2022-10-11 10:23 | SUPPLEMENTAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-09-06 20:09 | 2022 | EASTERN | YES | 40.3304 | -77.9796 | 1346606 | 2022-09-06 22:31 | 1346708 | NATURAL GAS |  | 1231 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-09-06 18:17 | 2022-09-06 22:00 |  |  |  |  | YES | 2022-09-06 18:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 5 | NO | [6 empty] | 0 | 2022-09-06 18:00 | 2022-09-06 18:00 | ONSHORE | PA | 17052 | Not Within a Municipality | HUNTINGDON | MILEPOST | 92.82 | M&R STATION 71455 | ENTR-PERU | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 1954 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | NORMALLY VENTING CONTROL VALVE | CLASS 1 LOCATION | NO |  | 53 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 10033 | 10033 | 50000 | 50000 | 2000 | 2000 | 0 | 0 |  | 8.15 | 62033 | 29523.5230544986433355481727574750830565 | 62033 | 0 | 0 | 0 | 0 | NO |  |  |  | 866 | 1106 | 1050 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [52 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [306 empty] | MICHAEL MCGRATH |  | michael.mcgrath@enbridge.com | 6128056542 |  |  |  |  | NATHAN ATANU | MANAGER OPERATIONAL COMPLIANCE | 17136275008 | nathan.atanu@enbridge.com | THE REGULATOR AT THIS STATION IS FEED OFF MAIN LINES 12 AND 19 THROUGH 2-INCH LINES. THE COORDINATES UNDER PART A5 REFLECT THE APPROXIMATE TAP LOCATION OFF LINE 12. THE REGULATOR AT THIS STATION VENTS GAS DURING NORMAL OPERATION. THIS VENTING GAS WAS LIKELY IGNITED BECAUSE OF LIGHTING IN THE AREA. THE ENSUING FIRE EVENTUALLY DAMAGED THE REGULATOR ENOUGH TO CAUSE THE RELIEF VALVE TO OPEN. THE FIRE DEPARTMENT PUT THE FIRE OUT AT THE REGULATOR. THE EVENT WAS REPORTED UNDER 192.3 (3) REPORTING REQUIREMENTS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220109 | 37431 | 2022-10-13 14:54 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-09-20 14:05 | 2022 | EASTERN | NO | 35.2743 | -80.5351 | 1347796 | 2022-09-20 16:18 | 1347952 | NATURAL GAS |  | 13029 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | A SECTION OF THE PIPELINE WAS BLOCKED OFF. |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-09-20 15:38 | VALVE CLOSURE |  | 2022-09-21 19:23 | 0 | 2022-09-20 14:05 | 2022-09-20 14:11 | ONSHORE | NC | 28031 | CORNELIUS | MECKLENBURG | NOT APPLICABLE |  | LINE 369 | 415035 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 42 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10 | NO | 0.307 | 35000 | UNKNOWN | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 24 | 10 | [7 empty] | CLASS 3 LOCATION | YES | METHOD1 |  | NOT FLAMMABLE | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 78174 | 78174 | 165750 | 165750 | 29250 | 29250 | 0 | 0 |  | 6 | 273174 | 137320.1030656655935714285714285714285714 | 273174 | 0 | 0 | 0 | 0 | NO |  |  |  | 675 | 11823 | 796 | 192.619(C) |  | 1970-07-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 16368 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPE WAS DAMAGED BY A 3RD PARTY COMPANY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | YES |  |  |  | YES | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | NO | [5 empty] | YES | 48 | ONE-CALL NOTIFICATION PRACTICES NOT SUFFICIENT | NO NOTIFICATION MADE TO THE ONE-CALL CENTER | [265 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A CONTRACTOR DAMAGED A 10" STEEL MAIN WITH A TRACKHOE WHILE IN THE PROCESS OF DIGGING A PROPOSED RETENTION POND. THE CONTRACTOR DID NOT CONTACT THE ONE-CALL CENTER FOR THE AREA BEING EXCAVATED.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220110 | 37235 | 2022-10-18 14:02 | ORIGINAL FINAL | 31618 | ENTERPRISE PRODUCTS OPERATING LLC | 1100 LOUISIANA STREET | HOUSTON | TX | 77002 | 2022-09-19 15:16 | 2022 | CENTRAL | YES | 27.5918 | -97.6106 | 1347704 | 2022-09-19 17:05 | 1347901 | NATURAL GAS |  | 390 | 0 | 11.9 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-09-19 16:10 |  | YES |  |  |  | YES | 2022-09-19 15:16 | ALLOWED TO BURN OUT |  | 390 | YES | VALVE CLOSURE |  | 2022-09-19 16:00 | VALVE CLOSURE |  | 2022-09-19 16:10 | 2 | 2022-09-19 15:50 | 2022-09-19 15:50 | ONSHORE | TX | 78343 | BISHOP | NUECES | MILEPOST | 81+97 | LUBY LATERAL | 9D | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | YES | [6 empty] | YES | UNCASED | COTULLA DITCH | UNKNOWN | SHORELINE/BANK/MARSH CROSSING | NO | [10 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 10.75 | NO | 0.219 | 46000 | API-5L-X-46-46000 | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1967 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 8 |  | CLASS 1 LOCATION | NO |  | 298 |  | NO | NO |  |  | NO |  |  | 500000 | 500000 | 0 | 0 | 3175 | 3175 | 639000 | 639000 | 0 | 0 | 0 | 0 |  | 8.14 | 1142175 | 504566.4412203718619036544850498338870432 | 1142175 | 2 | 0 | 1 | 0 | NO |  |  |  | 877 | 149 | 1114 | 192.619(A)(2) |  | 1982-05-19 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 9276 | NO | [5 empty] | YES | NO LAUNCH AND RECEIVER FACILITIES | NO | [6 empty] | TYPE C GATHERING | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | AMIT SHAMGAR | SR. PIPELINE COMPLIANCE SPECIALIST | ashamgar@eprod.com | 713-381-6741 |  |  |  |  | NHAN TRUONG | SR. COMPLIANCE MANAGER | 713-381-2493 | nvtruong@eprod.com | AT ABOUT 15:16HRS 19SEP2022 ENTERPRISE CONTROL ROOM WAS CONTACTED BY THE NUECES COUNTY SHERIFF DEPARTMENT CONCERNING A GRASS FIRE IN THE VICINITY OF AN ENTERPRISE GAS PIPELINE. THE CONTROLLER IMMEDIATELY DISPATCHED FIELD PERSONNEL TO INVESTIGATE. AT ABOUT 15:50HRS FIELD PERSONNEL ARRIVED ON SITE THEN CONTACTED ENTERPRISE CONTROL ROOM CONFIRMING A PIPELINE FAILURE AND FIRE. THE LOCAL FIRE DEPARTMENT WERE ON SITE ALREADY. THE FIRE WAS ALLOWED TO BURN-OUT. AT ABOUT 16:00HRS FIELD PERSONNEL BEGAN CLOSING MANUAL VALVES; THE LAST ONE (VALVE #3) WAS CLOSED AT 16:10HRS, TOTALLY ISOLATING THE RUPTURE SITE. AT ABOUT 17:30HRS THE FIRE HAD EXTINGUISHED ITSELF, AND WE WERE ABLE TO SAFELY INSPECT THE SITE. THE FIRE DEPARTMENT DID NOT EVACUATE LANDOWNERS OR CLOSE ROADS. PROPERTY DAMAGE OR ENVIRONMENTAL IMPACT ARE BEING EVALUATED. THE FAILURE SEGMENT WAS CUT-OUT. CURRENTLY, THERE IS NO PLAN TO RETURN THE PIPELINE TO SERVICE. THE RRC WAS CONTACTED ON 19SEP2022 AT 1706. TRRC INCIDENT NUMBER 2706
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220111 | 37356 | 2022-10-20 15:30 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2022-10-03 09:46 | 2022 | CENTRAL | YES | 30.7434 | -91.2656 | 1348896 | 2022-10-03 11:28 | 1349060 | NATURAL GAS |  | 32000 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-03 09:46 | 2022-10-04 20:49 |  | YES | OPERATOR | 2022-10-03 09:34 | NO | [11 empty] | 0 | 2022-10-03 09:23 | 2022-10-03 09:55 | ONSHORE | LA | 70748 | JACKSON | EAST FELICIANA | MILEPOST | 588.51 | COMPRESSOR STATION 60 | LE5048B BLOWDOWN VALVE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2016 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EMERGENCY BLOWDOWN VALVE INADVERTENTLY OPENED. | CLASS 1 LOCATION | NO |  | 151 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 180480 | 180480 | 5000 | 5000 | 0 | 0 | 0 | 0 |  | 5.64 | 185480 | 120627.0709619869957973421926910299003322 | 185480 | 0 | 0 | 0 | 0 | NO |  |  |  | 585 | 600000 | 800 | 192.619(A)(1) |  | 2001-07-22 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER DOES NOT HAVE CONTROL OF ANY OF THE EBD VALVES FROM A REMOTE LOCATION. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | CONTROLS WERE SPEC'D WRONG FOR PIPELINE APPLICATION. | [161 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-303-9956 |  | TRACI BRENTANO | traci.brentano@williams.com | 281-520-0007 | JOHN BELL | MANAGER PIPELINE SAFETY | 337-317-9145 | john.bell@williams.com | WHILE COMPRESSING IN NORMAL OPERATIONS A 10-INCH STATION BLOWDOWN UNEXPECTEDLY OPENED WITHOUT A CORRESPONDING SHUTDOWN FROM THE EMERGENCY SHUTDOWN (ESD) / EMERGENCY BLOWDOWN (EBD) SYSTEMS. OPERATIONS THEN MANUALLY INITIATED AN ESD, HOWEVER, ONE SIDE-GATE VALVE FAILED TO CLOSE, AND GAS CONTINUED TO RELEASE FROM THE 10-INCH BLOWDOWN. OPERATIONS THEN ATTEMPTED TO MANUALLY CLOSE THE SIDE-GATE VALVE BUT WERE UNSUCCESSFUL. OPERATIONS WAS ABLE TO ISOLATE THE STATION BY CLOSING AN UPSTREAM VALVE LOCATED APPROXIMATELY SIX MILES AWAY, 23 MINUTES AFTER THE INITIAL BLOWDOWN OPENED. THAT PARTICULAR VALVE IS OUT OF SERVICE PENDING A CONTROLS SPECS STUDY.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220112 | 37313 | 2022-10-25 16:33 | SUPPLEMENTAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2022-10-01 20:40 | 2022 | CENTRAL | YES | 43.3737 | -96.7101 | 1348816 | 2022-10-01 22:25 | 1348928 | NATURAL GAS |  | 5200 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ABLE TO MAINTAIN SERVICE |  |  |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-10-01 21:15 | NO | [11 empty] | 0 | 2022-10-01 20:40 | 2022-10-01 21:15 | ONSHORE | SD | 57013 | Not Within a Municipality | LINCOLN | MILEPOST | 77.26 | CHANCELLOR ETHANOL | 78367 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2022 | 2021 | CARBON STEEL |  | OTHER | [8 empty] | BATTERY-OPERATED EQUIPMENT FAILED WHEN POWER WAS LOST. | CLASS 1 LOCATION | NO |  | 241 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 29120 | 29120 | 500 | 500 | 250 | 250 | 0 | 0 |  | 5.6 | 29870 | 19437.8480197133317616279069767441860465 | 29870 | 0 | 0 | 0 | 0 | NO |  |  |  | 448 | 3300 | 800 | 192.619(A)(2) |  | 2022-09-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | NO | NO | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS DID NOT RECEIVE ANY ALERTS OR ALARMS DUE TO THE POWER LOSS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [7 empty] | YES | [17 empty] | YES | [167 empty] | YES | YES |  |  |  | JOHN GORMLEY | SR PIPELINE SAFETY SPECIALIST | john.gormley@nngco.com | 4026811574 | 4023987313 | MARIO GRADILLAS | mario.gradillas@nngco.com | 4025303305 | TOM CORRELL | VP PIPELINE SAFETY AND RIST | 14023987715 | thomas.correll@nngco.com | AT 20:40 ON SATURDAY OCTOBER 01, 2022, NORTHERN RECEIVED A CALL FROM THE OPERATIONS COMMUNICATION CENTER (OCC) STATING THAT A PASSERBY HEARD A LOUD NOISE FROM CHANCELLOR ETHANOL TBS. THE LOCAL TECHNICIAN WAS SENT TO THE STATION TO INVESTIGATE. THE TECHNICIAN CONTACTED GAS CONTROL AND DISCOVERED THAT NO ALARMS WERE REPORTING, AND SCADA WAS NOT COMMUNICATING. NORTHWESTERN (THE LDC) WAS ONSITE AND REPORTED THAT GAS WAS BLOWING. NORTHERN'S TECHNICIAN ARRIVED ON SCENE AT APPROXIMATELY 21:15 AND FOUND THE RELIEF VALVE RELIVING STACKS HALF OPEN. THE TECHNICIAN CHECKED PRESSURES FROM THE ELECTRONIC FLOW MEASUREMENT (EFM) AND NOTICED THAT NO DISPLAYS WERE WORKING. HE ALSO NOTICED THE EFM WAS NOT BEING POWERED. THE TECHNICIAN CORRECTED THE RELIEF VENTING BY LOWERING THE SET POINT OF THE SECONDARY PNEUMATIC VALVE CONTROLLER. THE PRIMARY REGULATOR IS CONTROLLED WITH A DIGITAL VALVE CONTROLLER WHICH IS POWERED WITH 24 VOLTS. WHEN THE POWER WAS LOST TO THE DIGITAL VALVE CONTROLLER, THE REGULATOR FAILED OPEN CAUSING THE RELIEF TO VENT DUE TO THE SECONDARY REGULATOR BEING SET SLIGHTLY HIGHER THAN THE RELIEF. IF THE RELIEF WAS SET HIGHER THAN THE SECONDARY REGULATORS, THE RELIEF MAY NOT HAVE OPENED. ON OCTOBER 3, 2022, FURTHER INVESTIGATION WAS CONDUCTED CONCERNING THE POWER FAILURE TO THE STATION. IT WAS DISCOVERED THAT THE SOLAR PANELS WERE NOT WIRED CORRECTLY TO CHARGE THE BATTERIES. THE BATTERIES WERE ONLY GETTING 19 VOLTS TO CHARGE 24-VOLT BATTERIES. THE BATTERIES WERE FULLY CHARGED WHEN THE STATION WAS PUT INTO SERVICE ON SEPTEMBER 28, 2022. THE BATTERIES SLOWLY DEPLETED FROM NOT BEING CHARGED CORRECTLY. UPON FURTHER REVIEW OF THE REGULATOR, THIS MODEL REGULATOR HAS A LOW VOLTAGE PROTECT FUNCTION THAT DISCONNECTS ALL THE LOAD ONCE THE BATTERIES REACH 23 VOLTS. NORTHERN NATURAL GAS SETS A LOW VOLTAGE ALARM AT 22 VOLTS. DUE TO THE VOLTAGE REGULATOR DISCONNECTING POWER AT 23 VOLTS, NO ALARMS WERE RECEIVED, NOR COULD ANY OTHER MONITORING BE PERFORMED REMOTELY.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20220113 | 37725 | 2022-10-28 16:39 | SUPPLEMENTAL FINAL | 405 | ANR PIPELINE CO | 700 LOUISIANA STREET SUITE 700 | HOUSTON | TX | 77002 | 2022-09-29 15:40 | 2022 | CENTRAL | YES | 37.5964 | -87.4341 | 1348627 | 2022-09-29 16:30 | 1348783 | NATURAL GAS |  | 189 | 3677 | 0.1 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-09-29 18:39 | 2023-01-13 11:39 |  | YES | OPERATOR | 2022-09-29 16:30 | NO | [5 empty] | VALVE CLOSURE |  | 2022-09-29 16:46 | VALVE CLOSURE |  | 2022-09-29 16:39 | 1 | 2022-09-29 15:40 | 2022-09-29 15:40 | ONSHORE | KY | 42327 | Not Within a Municipality | MCLEAN | MILEPOST | 582.6 | MAINLINE VALVE 45A | 8245501-ANR MAINLINE LOOP 2 2-501 MLV 45 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 1986 | 1986 | CARBON STEEL |  | OTHER | [8 empty] | VALVE FAILURE | CLASS 1 LOCATION | NO |  | 830 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 25298 | 25298 | 1300 | 1300 | 1300000 | 1300000 | 10000 | 10000 | 100000 | 100000 | LABORATORY AND INVESTIGATION COSTS | 6.88 | 1436598 | 634051.4967289045443681262458471760797342 | 1436598 | 0 | 0 | 1 | 0 | NO |  |  |  | 580 | 385 | 858 | 192.619(A)(1) |  | 1972-10-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 12277 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT OCCURRED DURING MAINTENANCE OPERATIONS WHILE TECHNICIANS WERE AT THE FACILITY. | [12 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | TECHNICIAN BELIEVED THAT VALVE NEEDED TO BE CLOSED DURING THE CORRECTIVE MAINTENANCE OF REPLACING THE DHV HAND PUMP. TECHNICIAN DID NOT BECOME AWARE OF THE SHAFER DHV HAND PUMP INSTALLATION PROCEDURE THAT INCLUDED A NOTE TO HAVE THE VALVE OPEN AT THE START OF MAINTENANCE. | YES |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [149 empty] | ROGER R STREET | MANAGER US REGULATORY COMPLIANCE WEST | roger_street@tcenergy.com | 16154655123 |  | ROGER R STREET | roger_street@tcenergy.com | 16154655123 | PAUL SHAFFER | SENIOR MANAGER USGO REGULATORY COMPLIANCE | 304-357-2245 | paul_shaffer@tcenergy.com | ON 29 SEPTEMBER 2022, TC ENERGY TECHNICIANS WERE PERFORMING A CORRECTIVE WORK ORDER TO REPLACE THE HYDRAULIC FLUID IN THE 501-45A-34 VALVE. WHILE PERFORMING THE WORK, AN INCIDENT OCCURRED RESULTING IN INJURIES AND A RELEASE OF GAS. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER, #1348627. THE ANR 2-501 PIPELINE MP582.6 TO MP585.1 - 2-501 LOOP SOUTH END TO MAINLINE VALVE 46 (ISOLATED SEGMENT), HAS BEEN BLOWN DOWN AND ISOLATED. IN ADDITION, TC ENERGY HAS SUSPENDED QUALIFICATIONS ON COVERED TASKS ASSOCIATED WITH THE WORK BEING PERFORMED ASSOCIATED WITH THE INCIDENT AND CONDUCTED DRUG TESTING. THE PIPELINE SEGMENT REMAINED OUT OF SERVICE UNTIL REPAIR OF THE PIPELINE WAS COMPLETED. REPAIR TO THE PIPELINE INCLUDED THE REPLACEMENT OF THE VALVE AND VALVE OPERATOR. THE PIPELINE WAS RESTARTED AND RETURNED TO FULL SERVICE ON JANUARY 13, 2023 AT 11:39 CST. THE PRIMARY CAUSE OF THE FAILURE HAS BEEN DETERMINED TO BE THE RESULT OF THE TECHNICIAN FAILING TO CONFIRM MANUFACTURER'S REPAIR PROCEDURE AND OPENING THE VALVE DURING CORRECTIVE MAINTENANCE TO REPLACE THE HYDRAULIC HAND PUMP. FOLLOWING THE REPAIR, WHEN THE VALVE WAS ACTUATED USING THE HAND PUMP, HYDRAULIC OIL BEGAN TO MOVE TO THE OPEN SIDE OF THE VALVE STEM AND THE VALVE GATE DISENGAGED AND MOVED IN AN UNCONTROLLED MANNER. THE RESULT OF THIS ACTION CAUSED A FAILURE IN THE VALVE ACTUATOR CONNECTION AND A RELEASE OF PIPELINE FLUIDS AND HYDRAULIC OIL TO THE SURROUNDING AREA.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220114 | 37297 | 2022-11-01 11:15 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-10-04 17:19 | 2022 | EASTERN | NO | 34.9451 | -79.8522 | 1349128 | 2022-10-05 17:27 | 1349268 | NATURAL GAS |  | 0.01 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-07 17:37 | 2022-10-09 20:36 |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | LEAK IDENTIFIED BY CUSTOMER FIELD OPERATIONS. TO ISOLATE LEAKING SECTION. |  | OPERATIONAL CONTROL | LEAK IDENTIFIED BY CUSTOMER FIELD OPERATIONS. TO ISOLATE LEAKING SECTION. |  | 0 | 2022-10-04 17:19 | 2022-10-04 18:15 | ONSHORE | NC | 28379 | ROCKINGHAM | RICHMOND | NOT APPLICABLE |  | LINE 1 | LINE 1 SECTION 3 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 56 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | 1959 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 400000 | 400000 | 40000 | 40000 | 0 | 0 |  | 8.49 | 440000 | 194111.14830934068 | 440000 | 0 | 0 | 0 | 0 | NO |  |  |  | 518 | 45000 | 630 | 192.619(A)(3) |  | 2016-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 31680 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | LEAK CLAMP | [15 empty] | YES | NO OTHER FACTORS. | [161 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | WHILE PERFORMING NEARBY SURVEY WORK, 2ND PARTY CONTRACTOR NOTIFIED THE OPERATION CENTER OF THE SMELL OF NATURAL GAS ON LINE 1. AFTER INVESTIGATION, IDENTIFIED LOCATION WAS A LEAKING LEAK CLAMP ON THE PIPELINE. PIPE WAS CUT OUT AND REPLACED WITH A NEW SECTION OF PIPE.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20220115 | 37305 | 2022-11-03 09:22 | ORIGINAL | 15105 | PANHANDLE EASTERN PIPELINE CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-10-03 00:18 | 2022 | CENTRAL | YES | 39.5725 | -89.9794 | 1348876 | 2022-10-03 02:04 | 1349019 | NATURAL GAS |  | 7100 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-03 00:30 | 2022-10-06 11:00 |  |  |  |  | YES | 2022-10-03 00:18 | ALLOWED TO BURN OUT |  | 7100 | NO | [6 empty] | 2 | 2022-10-03 00:21 | 2022-10-03 00:25 | ONSHORE | IL | 62692 | WAVERLY | MORGAN | SURVEY STATION NO. | 0+47 | WAVERLY STORAGE FIELD | ST PETER DRIP 24-INCH | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 168 | NO | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | PULSATION BOTTLE OR DRIP/DRIP COLLECTION DEVICE | [38 empty] | 2005 | 2005 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 72 | 48 |  | CLASS 1 LOCATION | NO |  | 481 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 31453 | 31453 | 496065 | 496065 | 0 | 0 | 1427 | 1427 | REPAYMENT TO FARMER/RANCHER WHO LEASED LAND FOR CATTLE. | 4.43 | 528945 | 240112.1825868911551339667774086378737542 | 528945 | 0 | 0 | 0 | 0 | NO |  |  |  | 843 | 28900 | 845 | 192.619(A)(2) |  | 2005-06-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS DID NOT AFFECT THE INCIDENT. | [12 empty] | YES | 4 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | todd.nardozzi@energytransfer.com | 713-989-7126 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON 10/03/22 AT 00:18, THE 24-INCH ST PETER DRIP LINE IN THE WAVERLY STORAGE FIELD FAILED RESULTING IN A FIRE. THE PIPE APPEARS TO HAVE FAILED AT THE 6 O'CLOCK POSITION ON THE SOUTH END OF THE PIPE. APPROXIMATELY 7.1 MMCF OF NATURAL GAS WAS RELEASED. THE PIPELINE WAS ISOLATED AND BLOWDOWN BY AREA OPERATIONS RESULTING IN THE FIRE BEING EXTINGUISHED. LOCAL EMERGENCY MANAGEMENT CLOSED ROADS AND EVACUATED RESIDENTS NEAR THE FAILURE SITE TO PREVENT TRAFFIC FROM ENTERING THE AREA. THE FAILED SECTION OF PIPE WAS REMOVED AND THE LINE WAS RESTARTED ON 10/06/22 AT 11:00. THE CAUSE OF THE FAILURE IS UNDER INVESTIGATION AND PENDING 3RD PARTY LABORATORY ANALYSIS OF THE FAILED PIPE. WHEN INVESTIGATION IS COMPLETE A SUPPLEMENTAL AND FINAL 7100.2 REPORT WILL BE FILED.
2023-02-28 09:42 | YES | YES | GG (Gas Gathering) | 20220116 | 37653 | 2022-11-04 17:50 | SUPPLEMENTAL FINAL | 31178 | XTO ENERGY INC | 22777 SPRINGWOODS VILLAGE PARKWAY | SPRING | TX | 77389 | 2022-10-11 14:00 | 2022 | MOUNTAIN | NO | 32.1077 | -103.8231 | 1349703 | 2022-10-12 11:00 | 1349850 | NATURAL GAS |  | 2 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE PIPELINE CONTINUED TO OPERATE THROUGH THE PIPELINE BYPASS PIPING. |  |  |  | YES | OPERATOR | 2022-10-11 14:07 | NO | [5 empty] | VALVE CLOSURE |  | 2022-10-11 14:00 | VALVE CLOSURE |  | 2022-10-11 14:00 | 0 | 2022-10-11 14:00 | 2022-10-11 14:50 | ONSHORE | NM | 88263 | Not Within a Municipality | EDDY | MILEPOST | BUCK JACKSON | EAGLE COMPRESSOR STATION TO ROW 5 CENTRAL RACK 20 | ROW 5 | YES | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 2022 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | EVENT WAS RESULT OF PRESSURE RELEASE DURING NORMAL OPERATIONS RESULTING IN PERSONAL INJURY. | CLASS 1 LOCATION | NO |  | 628 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 0 | 0 | 0 | 0 |  | 0 | 200 | 88.2323401406094 | 200 | 0 | 1 | 0 | 0 | NO |  |  |  | 1166 | 0 | 1440 | 192.619(A)(2) |  | 2022-05-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 15 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  |  |  | ROUTINE MAINTENANCE | NO | [150 empty] | JAMESON GOWIN | DOT COMPLIANCE | jameson.gowin@exxonmobil.com | 8172019373 |  |  |  |  | CURTIS JOHNSON | OPERATIONS SUPERINTENDENT | 3462542891 | curtis.johnson@exxonmobil.com | DURING PIGGING OPERATIONS, THE INJURED PERSON ENCOUNTERED DIFFICULTY REMOVING THE PLUG TO DE-PRESSURE THE PIG BARREL VIA THE 2' VENT LINE ON TOP OF THE RECEIVER. THE INDIVIDUAL THEN PROCEEDED TO POSITION HIMSELF INTO A SAFE POSITION TO OPERATE THE LOWER DRAIN DOWN VALVE. THEN PROCEEDED TO OPEN THE 2' DRAIN LINE ON THE BOTTOM OF THE BARREL TO RELIEVE PRESSURE ON THE PIG BARREL. WHILE OPENING THE VALVE IT APPEARS THE DRAIN ASSEMBLY WHICH WAS THREADED, ROTATED TOWARDS THE INDIVIDUAL AND THE RELEASE OF PRESSURE FROM THE DRAIN LINE IMPACTED THE LOWER EXTREMITIES OF THE INDIVIDUAL.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20220117 | 37324 | 2022-11-07 07:52 | ORIGINAL FINAL | 32595 | HIGH POINT GAS GATHERING, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2022-10-08 17:14 | 2022 | CENTRAL | YES | 29.7194 | -88.8773 | 1349385 | 2022-10-08 17:54 | 1349499 | NATURAL GAS |  | 4983 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | PRODUCER KEPT FLOW AT 150 PSI TO PREVENT WATER FROM ENTERING PIPE |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-10-17 17:14 | OPERATIONAL CONTROL | DOWNSTREAM WAS BLINDED NO VALVE |  | 0 | 2022-10-07 11:00 | 2022-10-16 20:44 | OFFSHORE | [6 empty] | MAIN PASS TO FRANKLIN 26" | SP 160 LATERAL 18" (BSEE 4283) | [20 empty] | 200 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | MAIN PASS | 148 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 18 | NO | 0.5 | 52000 | X-52 | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | OTHER | CONCRETE AND MASTIC | NO | [26 empty] | 1974 | 1973 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 354 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 33635 | 33635 | 470637 | 470637 | 93300 | 93300 | 0 | 0 |  | 6.75 | 597572 | 270856.8827535602625506279069767441860465 | 597572 | 0 | 0 | 0 | 0 | NO |  |  |  | 814 | 0 | 1200 | 192.619(A)(2) |  | 1974-01-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | REMOTELY CONTROLLED |  | 58608 | NO | [5 empty] | YES | DOWNSTREAM END OF PIPE BLINDED | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | NOT CUT OPEN |  | YES | [5 empty] | YES | [6 empty] | YES |  |  | NO | NO | NO | NO | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | NICKLAS PAVLOVSKY | MANAGER PIPELINE REGULATORY COMPLIANCE | npavlovsky@third-coast.com | 3462413368 |  |  |  |  | NICKLAS PAVLOVSKY | MANAGER PIPELINE REGULATORY COMPLIANCE | 3462413368 | npavlovsky@third-coast.com | ON 10/07/22 AT APPROXIMATELY 11:04AM WHILE FIELD PERSONNEL WERE FLYING BACK FROM DUTIES AT ANOTHER LOCATION, THEY SPOTTED BUBBLES ON THE SEA SURFACE WITH NO SHEEN IN CLOSE PROXIMITY TO ONE OF OUR PIPELINES (HIGH POINT GAS GATHERING (HPGG), SP160 BSEE 4283). AT THAT TIME CONTROL CENTER DID NOT SEE A PRESSURE DROP. A CALL WAS PLACED TO THE NRC AT 6:12PM ON 10/07/22 (NRC# 1349308) TO REPORT AN UNKNOWN RELEASE AS WELL TO THE COAST GUARD TO ISSUE A BROADCAST WARNING TO ALL MARINE TRAFFIC. THIRD COAST HPGG SHUT IN PRODUCTION AND ISOLATED THE LATERAL TO STABILIZE AND MONITOR THE PRESSURE. THIRD COAST ALSO CONTRACTED A VESSEL TO BE AT THE RELEASE SITE TO MONITOR AND KEEP TRAFFIC AT A SAFE DISTANCE. ON 10/8/22 AFTER THE PRESSURE SETTLED DUE TO PRODUCTION AND RECEIVING SHUTTING DOWN; A SLOW PRESSURE DROP WAS OBSERVED. IT WAS DETERMINED THAT THE RELEASE WAS COMING FROM OUR PIPELINE. ON 10/08/22 AT 6:54PM A CALL WAS PLACED TO THE NRC (NRC# 1349385) TO TAKE OWNERSHIP OF THE RELEASE AND UPDATE WITH KNOWN INFORMATION. HPGG KEPT THE LATERAL ISOLATED FROM THE MAINLINE UPSTREAM; DOWNSTREAM OF THE RELEASE WAS BLINDED. CONTROL CENTER HAD PRODUCTION MAINTAIN FLOW IN THE LINE TO KEEP A 150PSI TO 200PSI ON THE LINE TO PREVENT WATER ENTERING UNTIL REPAIRS COULD BE MADE. ON 10/10/22 AT 2:40PM A 48HR CALL WAS PLACED TO THE NRC (NRC# 1349499) TO UPDATE WITH NEW INFORMATION. DUE TO AVAILABILITY, A DIVE BOAT COULD NOT ARRIVE ON LOCATION UNTIL 10/16/22 TO LOCATE THE RELEASE. DIVERS LOCATED THE RELEASE AND CONFIRMED THAT IT WAS COMING FROM THE SP160 LATERAL. DUE TO WEATHER, THE DIVE BOAT HAD TO RETURN TO THE DOCK. ON 10/20/22 THE DIVE BOAT WAS BACK ON LOCATION DIVING AND MAKING THE REPAIR. ON 10/23/22 AT 2:46AM THE REPAIR WAS MADE WITH A CLAMP AND THE RELEASE STOPPED. APPROXIMATELY 4.983 MILLION CUBIC FEET OF NATURAL GAS WAS RELEASED. THE DIVERS THEN MOVED UPSTREAM ISOLATING THE PIPELINE VIA A SUBSEA VALVE SETS FROM THE PRODUCER. THE SP160 LATERAL WILL BE PURGED OF HYDROCARBONS AND KEPT ISOLATED.
2023-02-28 09:42 | YES | YES | GT (Gas Transmission) | 20220118 | 37588 | 2022-11-07 18:00 | SUPPLEMENTAL FINAL | 32459 | HOOKS GAS PIPELINE, LLC | 9950 WOODLOCH FOREST DR | THE WOODLANDS | TX | 77380 | 2022-10-06 14:48 | 2022 | CENTRAL | YES | 29.6749 | -98.0229 | 1349227 | 2022-10-06 15:54 | 1349376 | NATURAL GAS |  | 210 | 0 | 0 | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-06 15:35 | 2022-10-18 07:00 |  | YES | OPERATOR | 2022-10-06 14:48 | YES | 2022-10-06 14:48 | ALLOWED TO BURN OUT |  | 210 | NO | VALVE CLOSURE |  | 2022-10-06 15:35 | OPERATIONAL CONTROL | THE EOL OF THIS SYSTEM HAS NO CUSTOMERS ALLOWED THE DOWNSTREAM PORTION TO BURN OFF. |  | 0 | 2022-10-06 14:48 | 2022-10-06 15:35 | ONSHORE | TX | 78130 | NEW BRAUNFELS | GUADALUPE COUNTY | NOT APPLICABLE |  | HOOKS GAS PIPELINE, LLC | NAVARRO RANCH | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 8 | NO | [9 empty] | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | [20 empty] | 2021 | UNKNOWN | PLASTIC |  | OTHER | [8 empty] | DUE TO THE CONTRACTORS SQUEEZERS FAILING, GAS WAS RELEASED INTO THE HOLE THE CONTRACTOR WAS WORKING IN. | CLASS 3 LOCATION | NO |  | 62 |  | NO | NO | NO |  | NO |  |  | 0 | 0 | 0 | 0 | 3150 | 3150 | 27500 | 27500 | 0 | 0 | 0 | 0 |  | 15 | 30650 | 14198.8072344500715697674418604651162791 | 30650 | 0 | 0 | 0 | 0 | NO |  |  |  | 48 | 0 | 100 | 192.619(A)(2) |  | 2021-10-20 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL |  | 21000 | NO | [5 empty] | YES | 8" HDPE POLY | NO | [6 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | [166 empty] | OTHER EQUIPMENT FAILURE | [19 empty] | THE HYDRAULIC PUMP USED TO CLOSE THE JAWS OF THE SQUEEZER FAILED. THIS FAILURE CAUSED THE JAWS TO OPEN ON THE SQUEEZERS THE CONTRACTOR RENTED. | [15 empty] | YES | FAILURE TO UTILIZE SADDLE CLAMP | [160 empty] | YES | KYLE KNAPP | REGULATORY INSPECTOR | kyle.knapp@centric-us.com | 8323492538 | 2812529252 |  |  |  | AMY DOYAL | DIRECTOR OF REGULATORY COMPLIANCE | 2812526700 | amy.doyal@centric-us.com | IT IS CENTRIC'S OPINION THAT THE PRIMARY ROOT CAUSE OF THE INCIDENT WAS EQUIPMENT FAILURE (HYDRAULIC SQUEEZERS). THROUGH INVESTIGATION IT WAS REPORTED THAT SOMETHING MALFUNCTIONED IN THE HYDRAULIC PUMP, CAUSING THE JAWS OF THE SQUEEZERS TO RELEASE AND ALLOW GAS TO ENTER THE HOLE. BROADHEAD HAS REQUESTED MAINTENANCE RECORDS FROM EQUIPMENT SUPPLIER GAJESKE, INC. BUT THESE RECORDS HAVE NOT YET BEEN PROVIDED BY GAJESKE, INC. CENTRIC WAS INITIALLY INFORMED THAT NO CLAMPS WERE PROVIDED WITH THE RENTAL. AFTER FOLLOW-UP QUESTIONING CENTRIC RECEIVED THE FOLLOWING FROM BROADHEADS LAWYER "THE LOCKING DEVICES WERE PROVIDED BUT THEY WERE NOT USED." LEADING US TO IDENTIFY THIS AS A CONTRIBUTING FACTOR. OTHER CONTRIBUTING FACTORS INCLUDE THAT THE CONTRACTORS WERE NOT WEARING APPROPRIATE PPE (IN CONTRAVENTION TO THEIR CONTRACT WITH CENTRIC), AND HAZARD RECOGNITION WAS INADEQUATE BY THE CONTRACTOR STAFF ON SCENE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220119 | 37457 | 2022-11-09 12:59 | SUPPLEMENTAL FINAL | 26330 | ENABLE OKLAHOMA INTRASTATE TRANSMISSION, LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-10-24 14:20 | 2022 | CENTRAL | YES | 33.9784 | -96.0073 | 1350720 | 2022-10-24 14:20 | 1350783, 1350817 | NATURAL GAS |  | 16619 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | NO | THIS WAS A LOADING VALVE FAILURE ON A COMPRESSOR SKID. UNIT DID NOT START UP. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-10-24 08:25 | 2022-10-24 08:25 | ONSHORE | OK | 74723 | Not Within a Municipality | BRYAN | NOT APPLICABLE |  | BENNINGTON COMPRESSOR STATION | COMPRESSOR UNIT #442 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2008 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | THIS WAS A LOADING VALVE FAILURE ON A COMPRESSOR SKID. UNIT DID NOT START UP. THE LOAD VALVE FAILED PARTIALLY OPEN ALLOWING GAS TO VENT. | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 86086 | 86086 | 2700 | 2700 | 0 | 0 | 0 | 0 |  | 5.18 | 88786 | 57676.1365918982269 | 88786 | 0 | 0 | 0 | 0 | NO |  |  |  | 350 | 175000 | 1650 | 192.619(A)(2) |  | 2009-04-15 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIONS OF THE CONTROLLER IN THIS INCIDENT DID NOT WARRANT AN INVESTIGATION. THE CONTROLLER NOTIFIED FIELD PERSONNEL OF A UNIT BEING DOWN AT THE COMPRESSOR STATION. THE INCIDENT OCCURRED WHEN THE FIELD PERSONNEL TRIED TO START UNIT 442 AND THE LOAD LINE VALVE FAILED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | SEAL FAILURE AS WELL AS PLC PROGRAMMING CONTRIBUTED TO THIS INCIDENT. | [20 empty] | YES | PROGRAM LOGIC ISSUE | [148 empty] | YES | [12 empty] | JEFF OSBORN | SR SPECIALIST DOT COMPLIANCE | jeff.osborn@energytransfer.com | 405-380-7618 | 405-379-7282 | JEFF OSBORN | jeff.osborn@energytransfer.com | 405-380-7618 | JIMMY CROSS | MANAGER DOT COMPLIANCE | 318-426-2515 | jimmy.cross@energytransfer.com | ON OCTOBER 21ST, 2022, AT APPROXIMATELY 19:00 HOURS, TECH WAS DISPATCHED TO BENNINGTON CS UNIT 447 TO TROUBLESHOOT UNIT 447 GOING DOWN. TECH CORRECTED THE ISSUE, PUT IT BACK ONLINE AND DEPARTED. UNIT 447 WENT BACK DOWN ON OIL TEMPERATURE ON THE SAME DATE AT APPROXIMATELY 20:30 HOURS. AT APPROXIMATELY 20:35 HOURS, TECH ADVISED GAS CONTROL TO START UNIT 442 REMOTELY. TECH THEN WENT BACK TO STATION TO RESET THE OIL COOLER TEMPERATURE SHUTDOWN ON UNIT 447. DURING THIS TIME, UNIT 442 FAILED TO START DUE TO NOT BEING PRESSURIZED. AT APPROXIMATELY 21:05, TECH THEN STARTED UNIT 447 AND PUT BACK ONLINE AND ADVISED GAS CONTROL THAT UNIT 442 WAS UNAVAILABLE DUE TO THE LOAD VALVE FAILURE. ON MONDAY, OCTOBER 24TH, 2022, AT APPROXIMATELY 07:00 HOURS, TECH ARRIVED AT THE STATION AND WAS REVIEWING ALARMS THAT OCCURRED OVER THE WEEKEND. HE NOTICED THAT THE LOAD VALVE FAILURE ALARM ON UNIT 442 WAS STILL ACTIVE. TECH WENT OUT TO UNIT 442 TO PHYSICALLY INSPECT WHY THE ALARM WAS STILL ACTIVE. TECH DISCOVERED THAT UNIT 442'S LOAD VALVE WAS PARTIALLY OPEN AND VENTING GAS. AT 08:25 HOURS, TECH MANUALLY CLOSED THE LOAD VALVE ON UNIT 442 TO PREVENT IT FROM VENTING AND NOTIFIED HIS SUPERVISOR OF THE INCIDENT AT APPROXIMATELY 08:30 HOURS. SUPERVISOR THEN INITIATED AN INVESTIGATION OF THE INCIDENT TO TRY AND DETERMINE HOW LONG THE VALVE HAD VENTED GAS AND WHAT CAUSED THE INCIDENT. A BALANCE SEGMENT WAS DONE ON BENNINGTON COMPRESSOR STATION TO DETERMINE THE VOLUME OF GAS VENTED. IT WAS DETERMINED THAT THE VALVE HAD VENTED GAS FROM OCTOBER 21ST, 2022, AT 21:02 HOURS TO OCTOBER 24TH, 2022, AT 08:25 HOURS (APPROXIMATELY 59 HOURS AND 23 MINUTES). ON OCTOBER 24TH AT APPROXIMATELY 14:10 HOURS, SUPERVISOR NOTIFIED DOT COMPLIANCE PERSONNEL. AT THIS POINT, IT WAS DETERMINED TO BE A REPORTABLE INCIDENT. INCIDENT WAS REPORTED TO NRC ON OCTOBER 24TH, 2022, AT 14:20. ON OCTOBER 25TH, 2022, AT APPROXIMATELY 13:00 HOURS, PLC PROGRAMMER REVIEWED THE PROGRAMMING ON UNIT 442 AND DETERMINED THERE WAS NOT A LOGIC IN THE PLC THAT WOULD PREVENT THIS FROM HAPPENING. ON OCTOBER 26TH, 2022, AT APPROXIMATELY 10:00 HOURS, PLC PROGRAMMER AND STATION I&E TECH, MADE THE PLC LOGIC CHANGES THAT WOULD PREVENT THIS FROM HAPPENING AGAIN. WE NOW HAVE A TIMED LOCKOUT ON THE UNIT THAT IF IT DOES NOT START IN A CERTAIN PROGRAMMED TIME, THE VALVE WILL AUTOMATICALLY CLOSE THE VENT VALVE AND GIVE AN ALARM OF THE LOCKOUT. THE UNIT WAS LEFT LOCKED AND TAGGED OUT UNTIL SUCH PLC PROGRAMMING COULD BE TESTED AND VERIFIED TO BE ACCURATE. ON DECEMBER 1ST, 2022, AT APPROXIMATELY 08:00 HOURS, LOGIC WAS TESTED ON THE PLC FOR UNIT 442, AND PROVEN TO BE EFFECTIVE. THIS CHANGE WILL PREVENT FURTHER INCIDENTS FROM OCCURRING. A SPECIFIC CAUSE OF THE LOAD VALVE FAILURE COULD NOT BE PINPOINTED THEREFORE, A NEW LOAD VALVE (NEW VALVE AND ACTUATOR) WAS ORDERED AND IS WAITING TO BE INSTALLED. UNIT 442 IS LOCKED AND TAGGED OUT OF SERVICE UNTIL A STATION OUTAGE CAN BE SCHEDULED TO REPLACE THE LOAD VALVE ON UNIT 442.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220120 | 37400 | 2022-11-10 17:27 | SUPPLEMENTAL | 32374 | MONROE GAS STORAGE COMPANY, LLC | 508 MINDEN ST. SUITE A | RUSTON | LA | 71270 | 2022-10-03 16:47 | 2022 | CENTRAL | NO | 34.0078 | -88.4517 | 1348951 | 2022-10-03 17:38 | 1349098 | NATURAL GAS |  | 1556.3 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-03 17:30 | 2022-10-11 11:05 |  | YES | OPERATOR | 2022-10-03 16:55 | YES | 2022-10-03 16:46 | ALLOWED TO BURN OUT |  | 358.3 | NO | VALVE CLOSURE |  | 2022-10-03 16:57 | VALVE CLOSURE |  | 2022-10-03 16:58 | 0 | 2022-10-03 16:46 | 2022-10-03 16:57 | ONSHORE | MS | 38821 | Not Within a Municipality | MONROE | MILEPOST | 8+47.1 | MONROE GAS STORAGE | 12" EAST LATERAL | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.375 | 52000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | EDGAR CARBON | EPOXY |  | YES | [26 empty] | 2009 | 2009 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 300 |  | NO | NO |  |  | NO |  |  | 45000 | 45000 | 0 | 0 | 10707 | 10707 | 428974 | 428974 | 0 | 0 | 0 | 0 |  | 6.88 | 484681 | 216124.5330718831416351428571428571428571 | 484681 | 0 | 0 | 0 | 0 | NO |  |  |  | 931 | 6 | 1314 | 192.619(A)(2) |  | 2009-04-06 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 2682 | NO | [5 empty] | YES | THE LINE WAS NOT INSTALLED WITH A LAUNCHER AND RECEIVER. | NO | [6 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | NO | NO | NOT APPLICABLE - NOT MAINLINE PIPE | NOT APPLICABLE - NOT MAINLINE PIPE | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | RJ SHEFFIE | OPERATIONS COMPLIANCE MANAGER | rj.sheffie@hartreegs.com | 3182548951 |  | RJ J SHEFFIE | rj.sheffie@hartreegs.com | 13182241124 | KENNETH FOYIL | VP OPERATIONS | 3182548951 | kenneth.foyil@hartreegs.com | WHILE PERFORMING ROUTINE ROUNDS A MONROE GAS STORAGE EMPLOYEE ARRIVED AT THE T (T IS REFERRED TO AS WHERE THE WELL ROAD FROM THE EAST GATE MEETS THE WELL ROAD THAT LEADS LEFT TOWARDS WELL #7 AND RIGHT TOWARD WELLS #15,16,17, &9) APPROXIMATE AT 1646 AND DISCOVERED THE FIRE COMING FROM WHAT WE NOW KNOW WAS THE 12' EAST LATERAL. AFTER ASSESSING THE LOCATION OF THE INCIDENT, THE EMPLOYEE BEGIN CALLING IN ADDITIONAL PERSONNEL AND EMERGENCY OFFICIALS TO ASSIST WHILE SHUTTING DOWN THE FACILITY ONCE ADDITIONAL PERSONNEL ARRIVE THE LINE WAS ISOLATED MANUALLY AND ALLOWED TO BURN ITSELF OUT. MONROE GAS STORAGE EMPLOYEES DIRECTED THE FIRE DEPARTMENT TO THE INCIDENT AREA AND REQUESTED THAT THEY ACTIVELY COOLED THE SURROUNDING AREA TO ENSURE THE FIRE WAS CONTAINED. THE FIRE WAS OUT, AND INCIDENT CONTAINED APPROXIMATELY 40 MINUTES AFTER DISCOVERY. THE IDENTIFIED INTERNAL CORROSION WAS CONSISTENT WITH MESA CORROSION, TYPICALLY OCCURRING IN A CARBON DIOXIDE (CO2) ENVIRONMENT LIKELY EXACERBATED VIA THE PRESENCE OF SALT WATER AND SAND (RESULTING IN AN UNDER-DEPOSIT PHENOMENON). TO MITIGATE THE DAMAGE FROM THE FAILURE AND IDENTIFIED CORROSION MGS PERFORMED THE FOLLOWING: REPLACED IN KIND 42FT NORTH OF POINT OF FAILURE AND 801 FT WEST OF POINT OF FAILURE. REPLACED IN KIND ONE 90-DEGREE ELBOW. MGS ALSO INSTALLED A 2 INCH LOW POINT DRAIN. THE DETERMINATION OF HOW MUCH OF PIPE NEEDED TO BE REPLACE WAS MADE USING A COMBINATION OF VISUAL INSPECTION, HAND-HELD UT GAUGE AND GUIDED WAVE TECHNOLOGY. GUIDED WAVE TECHNOLOGY WAS UTILIZED UPSTREAM AND DOWNSTREAM OF REPLACED PIPE, OF WHICH NO ADDITIONAL INTEGRITY ISSUES WERE FOUND AND NO FOLLOW-UPS WERE RECOMMENDED. THE 2 INCH LOW POINT DRAIN WAS THE FIRST PHASE OF STEPS MGS IS TAKING TO PREVENT RECURRENCE, THE SECOND INCLUDES DEVELOPING AND IMPLEMENTING A PIGGING AND CHEMICAL TREATMENT PLAN PRIOR TO BRINGING THE 12' EAST LATERAL IN SERVICE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220121 | 37473 | 2022-11-15 10:52 | SUPPLEMENTAL FINAL | 39167 | SABAL TRAIL TRANSMISSION, LLC (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-10-21 22:42 | 2022 | EASTERN | YES | 28.262 | -81.5556 | 1350565 | 2022-10-22 10:18 | 1350683 | NATURAL GAS |  | 7080 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ONE OF TWO COMPRESSOR UNITS AT THIS STATION CONTINUED TO OPERATE. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-10-22 09:12 | 2022-10-22 09:12 | ONSHORE | FL | 33896 | DAVENPORT | OSCEOLA | MILEPOST | 482.36 | REUNION COMPRESSOR STATION | DUNN-REUN/1 & REUN-EOLN | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2017 | 2016 | CARBON STEEL |  | OTHER | [8 empty] | UNIT LOADING VALVE FAILED TO FULLY CLOSE ON SHUT DOWN. | CLASS 1 LOCATION | NO |  | 62 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 35046 | 35046 | 0 | 0 | 1000 | 1000 | 1200 | 1200 | REPLACED COMPONENT | 4.95 | 37246 | 23965.8547448689625362126245847176079734 | 37246 | 0 | 0 | 0 | 0 | NO |  |  |  | 150 | 0 | 1456 | 192.619(A)(2) |  | 2017-05-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INDICATION OR EVIDENCE OF CONTROL ROOM OR CONTROLLER CONTRIBUTION TO THE INCIDENT; OPERATIONS (I.E., PRESSURES AND FLOWS) IN THE AREA WERE NORMAL AND WITHIN DESIGNED RANGES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | O-RING | [17 empty] | YES | O-RING FAILURE | [161 empty] | MICHAEL MCGRATH |  | mcgratm@comcast.net | 6128056542 |  |  |  |  | NATHAN ATANU |  | 17136275008 | nathan.atanu@enbridge.com | ON OCTOBER 22, 2022, AT APPROXIMATELY 9:12 AM EST, AN EMPLOYEE AT THE REUNION COMPRESSOR STATION IDENTIFIED GAS BLOWING THROUGH THE STATION BLOWDOWN STACK. THIS WAS NOT A PLANNED ACTIVITY AND INDICATED AN ISSUE. HE EXAMINED THE STATION AND IDENTIFIED AN ICE BUILDUP ON THE 2-INCH COMPRESSOR UNIT #1 LOADING VALVE. UNIT #1 WAS NOT IN OPERATION AT THE TIME BUT DID HAVE GAS AT A PRESSURE OF 150 PSIG LEAKING THROUGH THE VALVE INTO THE STATION BLOWDOWN SYSTEM. EARLIER UNDER NORMAL OPERATION UNIT #1 WAS SHUT DOWN TO SWITCH TO UNIT #2. THROUGH THIS PROCESS THE UNIT LOADING VALVE ON UNIT #1 FAILED TO TRAVEL TO THE FULLY CLOSED POSITION BUT DID INDICATE IT WAS CLOSED ON THE SYSTEM CONTROLS DUE TO A FAULTY LIMIT SWITCH. THE VALVE FAILING TO FULLY CLOSE ALLOWED FOR GAS TO VENT THROUGH THE STATION BLOWDOWN SYSTEM OVERNIGHT. THE RESTRICTED FLOW PATH CREATED A RESTRICTION AND PRESSURE DROP THAT CAUSED THE FORMATION OF ICE AT THE VALVE. THE FAULTY LIMIT SWITCH ON THE 2-INCH LOADING VALVE WAS ALSO REPLACED. UNIT #1 REMAINED OFF THROUGHOUT THIS TIME, UNIT #2 REMAINED RUNNING TO MEET ALL NEEDED CAPACITIES. THE FAILED COMPONENTS WERE REPLACED BEFORE RETURNING UNIT #1 TO NORMAL OPERATION. THE GAS LOSS BASED UPON THE RESTRICTION AND DURATION WAS CALCULATED TO BE 7.08 MMSCF. DECEMBER 15, 2022 PART A 4 - UPDATED TO REFLECT THE DATE AND TIME THE RELEASE STARTED PART G - CHANGED SUB-CAUSE FROM "COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT" TO "NON-THREADED CONNECTION FAILURE - O-RING" PART H UPDATED NARRATIVE
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220122 | 37367 | 2022-11-18 16:18 | ORIGINAL FINAL | 18516 | SOUTHERN NATURAL GAS CO | 1001 LOUISIANA ST, STE 1000 SUITE 1000 | HOUSTON | TX | 77002 | 2022-10-26 09:50 | 2022 | CENTRAL | NO | 32.4996 | -87.7146 | 1360890 | 2022-10-26 10:44 | 1351034 | NATURAL GAS |  | 38468 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-20 08:33 | 2022-10-25 09:00 |  | NO |  |  | YES | 2022-10-20 08:28 | ALLOWED TO BURN OUT |  | 500 | NO | [6 empty] | 0 | 2022-10-20 08:28 | 2022-10-20 08:28 | ONSHORE | AL | 36742 | GALLION | HALE COUNTY | MILEPOST | 138.858 | GALLION COMPRESSOR STATION | SOUTH MAINS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1989 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | CHECK VALVE SEAL FAILURE | [5 empty] | CLASS 2 LOCATION | NO |  | 344 |  | NO | NO |  |  | YES | YES |  | 0 | 0 | 0 | 0 | 210805 | 210805 | 30000 | 30000 | 109 | 109 | 0 | 0 |  | 5.48 | 240914 | 151601.8329953052514253255813953488372093 | 240914 | 1 | 0 | 0 | 0 | NO |  |  |  | 939 | 0 | 1200 | 192.619(A)(1) |  | 2003-09-08 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR DEEMED INCIDENT INDEPENDENT OF CONTROLLER'S ACTIONS | [12 empty] | YES | 1 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [5 empty] | YES | [29 empty] | YES | NOT APPLICABLE | [161 empty] | VIGNESH RAMAN | PIPELINE ENGINEER | vignesh_raman@kindermorgan.com | 2817705911 |  |  |  |  | JORGE LOPEZ | MANAGER ENGINEER | 7134204675 | jorge_lopez@kindermorgan.com | ON OCTOBER 20TH, 2022 AT 8:28AM, A SOUTHERN NATURAL GAS (SNG) TECHNICIAN WAS MANUALLY OPERATING A VALVE CONTACTOR ON THE DISCHARGE SIDE OF UNIT 4 AT THE GALLION COMPRESSOR STATION. WHILE THE TECHNICIAN WAS OPERATING THE VALVE CONTACTOR, A NEIGHBORING CHECK VALVE CAUGHT FIRE. IMMEDIATELY THE TECHNICIAN INITIATED THE STATION EMERGENCY SHUTDOWN TO ISOLATE THE STATION. THE STATION WAS ISOLATED AT 8:55AM. THE TECHNICIAN ON SITE SUSTAINED BURNS REQUIRING TREATMENT IN A MEDICAL FACILITY BUT NOT REQUIRING OVERNIGHT IN-PATIENT HOSPITALIZATION. THE EVENT WAS DETERMINED TO BE NON-REPORTABLE, AND THE INTERNAL INCIDENT INVESTIGATION COMMENCED. ON OCTOBER 26TH, 2022, AFTER INVESTIGATING THE INCIDENT FURTHER, DATA INDICATED THAT ADDITIONAL GAS WAS VENTED DUE TO A FAULTY CHECK VALVE LOCATED IN THE VALVE PNEUMATIC SYSTEM WHICH DID NOT SEAL PROPERLY LEADING TO ADDITIONAL GAS VOLUME RELEASED. THEREFORE, THE INCIDENT WAS DEEMED REPORTABLE AND REPORTED TO THE NRC. IN ORDER TO PREVENT REOCCURRENCE SNG OPERATIONS WILL BE REPLACING ALL GALLION STATION PNEUMATIC SYSTEM CHECK VALVES.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220123 | 37502 | 2022-11-28 10:01 | SUPPLEMENTAL FINAL | 31846 | CAROLINA GAS TRANSMISSION, LLC | 121 MOORE HOPKINS LANE | COLUMBIA | SC | 29210 | 2022-10-30 02:50 | 2022 | EASTERN | YES | 34.2385 | -79.8108 | 1351225 | 2022-10-30 08:13 | 1351347 | NATURAL GAS |  | 1757 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-30 08:21 | 2022-12-20 15:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-10-30 03:32 | NO | [11 empty] | 0 | 2022-10-30 03:07 | 2022-10-30 04:04 | ONSHORE | SC | 29501 | FLORENCE | FLORENCE | MILEPOST | 1.1 | FLORENCE TEC TOWN BORDER STATION | 13-110 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | METER | [38 empty] | 1980 | 1980 | CARBON STEEL |  | OTHER | [8 empty] | THIRD PARTY DAMAGE. AN INDIVIDUAL NOT AFFILIATED WITH THE COMPANY AND NOT A CONTRACTOR WORKING FOR THE COMPANY DROVE A VEHICLE OFF THE ROAD AND COLLIDED WITH AND DAMAGED THE FACILITY. | CLASS 3 LOCATION | NO |  | 85 |  | NO | NO |  |  | YES | YES | YES | 0 | 0 | 0 | 0 | 8820 | 8820 | 156652 | 156652 | 5000 | 5000 | 30000 | 30000 | ESTIMATED DAMAGE TO THE 3RD PARTY VEHICLE THAT COLLIDED WITH & DAMAGED FACILITY. | 5.02 | 200472 | 90336.7315654659450393488372093023255814 | 200472 | 0 | 0 | 0 | 0 | NO |  |  |  | 610 | 14.38 | 714 | 192.619(A)(2) |  | 2012-12-12 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN INDIVIDUAL NOT AFFILIATED WITH THE COMPANY AND NOT A CONTRACTOR WORKING FOR THE COMPANY DROVE A VEHICLE OFF THE ROAD AND COLLIDED WITH AND DAMAGED THE FACILITY. CONTROLLER ACTIONS OR CONTROL ROOM ISSUES WERE NOT A CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | PASSENGER CAR | ROADWAY | 40 | YES |  |  |  | YES | WOODEN FENCE | [233 empty] | DANIEL STAHL | PIPELINE INTEGRITY ENGINEER | daniel.stahl@bhegts.com | 3042666062 |  | MIKE FERGUSON | mike.ferguson@bhegts.com | 803-260-0335 | MIKE FERGUSON | MANAGER - PIPELINE INTEGRITY | 803-260-0335 | mike.ferguson@bhegts.com | ON 10/30/22 AT APPROXIMATELY 02:50, AN INDIVIDUAL NOT AFFILIATED WITH THE COMPANY AND NOT A CONTRACTOR WORKING FOR THE COMPANY DROVE A VEHICLE OFF THE ROAD AT THE INTERSECTION OF WEST LUCAS STREET (HIGHWAY 52) AND PISGAH ROAD IN FLORENCE, SOUTH CAROLINA. AFTER LEAVING THE ROAD, THE VEHICLE COLLIDED WITH AND DAMAGED THE FLORENCE TEC TOWN BORDER STATION (13-110) THAT IS SITUATED APPROXIMATELY 40 FT FROM THE SIDE OF THE INTERSECTION. THE VEHICLE CAME TO A STOP ON TOP OF THE STATION. THE FUNCTION OF THE STATION IS METERING AND REGULATING THE NATURAL GAS BEING SUPPLIED TO THE CITY OF FLORENCE. THE STATION WAS IN NORMAL OPERATION WITH AN OPERATING PRESSURE OF APPROXIMATELY 610 PSIG WHEN THE INCIDENT OCCURRED. THE COLLISION RESULTED IN THE ENTIRE STATION BEING SHEARED OFF AT THE RISERS AND NATURAL GAS BEGAN BLOWING TO THE ATMOSPHERE. THE INDIVIDUAL DRIVING THE VEHICLE WAS NOT INJURED AND SAFELY EXITED THE VEHICLE. THE VEHICLE DID NOT IGNITE THE BLOWING NATURAL GAS. AT APPROXIMATELY 03:07, GAS CONTROL RECEIVED A SCADA LOW LOW PRESSURE ALARM ON THE STATION. AT APPROXIMATELY 03:14, GAS CONTROL DISPATCHED OPERATIONS PERSONNEL TO INVESTIGATE THE SCADA LOW LOW PRESSURE ALARM AT THE STATION. AT APPROXIMATELY 03:32, GAS CONTROL RECEIVED NOTIFICATION FROM THE FLORENCE COUNTY 911 DISPATCHER. AT APPROXIMATELY 04:04, OPERATIONS PERSONNEL ARRIVED AT THE STATION AND ASSESSED THE SITUATION. AT APPROXIMATELY 04:07 OPERATIONS PERSONNEL AT THE SITE REQUESTED ADDITIONAL SUPPORT TO HELP ISOLATE THE STATION. IT WAS DETERMINED AT 07:41 THAT THE INCIDENT LIKELY INVOLVED AN ESTIMATED PROPERTY DAMAGE OF $129,300 OR MORE WHICH WOULD CLASSIFY IT AS REPORTABLE INCIDENT. INITIAL TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AT 08:13. THE NATIONAL RESPONSE CENTER ASSIGNED INCIDENT REPORT #1351225 TO THE INITIAL NOTIFICATION OF THE INCIDENT. OPERATIONS PERSONNEL STARTED TO ISOLATE THE STATION AT APPROXIMATELY 08:05. OPERATIONS PERSONNEL COMPLETED THE ISOLATION OF THE STATION AT APPROXIMATELY 08:21. THE ISOLATION OF THE STATION WAS ACCOMPLISHED BY HYDRAULICALLY PINCHING THE INLET RISER WHERE IT HAD BEEN SHEARED OFF BY THE VEHICLE AND WELDING ON A CAP WITH A NEEDLE VALVE AS A PRECAUTIONARY MEASURE TO RELIEVE ANY POTENTIAL OVER PRESSURIZATION. THE TAP VALVE TO THE STATION WAS ALSO CLOSED AND THE ENTIRE STATION WAS REMOVED FROM THE SITE. A FOLLOW UP TELEPHONIC NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER ON 10/31/22 AT 16:16 TO CONFIRM THE INITIAL TELEPHONIC NOTIFICATION AND PROVIDE AN UPDATE ON THE CURRENT STATUS OF THE STATION AND THE ESTIMATED VOLUME OF UNINTENTIONAL GAS LOSS. THE NATIONAL RESPONSE CENTER ASSIGNED INCIDENT REPORT #1351347 TO THE FOLLOW UP TELEPHONIC NOTIFICATION. FOLLOWING INCIDENT REPORT #1351347, THE ESTIMATED VOLUME OF UNINTENTIONAL GAS LOSS WAS LATER CONFIRMED TO BE 1757 MCF. THE FOLLOWING REMEDIATION ACTIONS WERE COMPLETED: THE ENTIRE STATION WAS REBUILT, THE REBUILT STATION WAS INSTALLED AT THE SITE, AND THE REBUILT STATION WAS RESTARTED AND RETURNED TO SERVICE ON 12/20/22 AT 15:00. ENHANCED PROTECTION MEASURES FOR THE STATION ARE PLANNED TO BE INSTALLED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220124 | 37425 | 2022-11-29 11:38 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 2800 POST OAK BLVD | HOUSTON | TX | 77056 | 2022-10-31 16:00 | 2022 | MOUNTAIN | YES | 42.7243 | -112.8906 | 1351359 | 2022-10-31 17:08 | 1351525 | NATURAL GAS |  | 359 | 9019 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-10-31 17:09 | 2022-11-04 10:54 |  |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-10-31 17:09 | VALVE CLOSURE |  | 2022-10-31 17:06 | 0 | 2022-10-31 16:24 | 2022-10-31 16:24 | ONSHORE | ID | 83211 | AMERICAN FALLS | POWER COUNTY |  |  | NORTHWEST PIPELINE | 22" 1400 MAINLINE MP 619.1 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 19 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 22 | NO | 0.25 | 52000 | API 5LX | DSAW |  | CONSOLIDATED | ASPHALT |  | YES | [26 empty] | 1955 | 1955 | CARBON STEEL |  | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 1 LOCATION | NO |  | 442 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 80991 | 80991 | 3224 | 3224 | 385000 | 385000 | 1500 | 1500 | 0 | 0 |  | 8.98 | 470715 | 208354.5399057601716550730897009966777409 | 470715 | 0 | 0 | 0 | 0 | NO |  |  |  | 723 | 250000 | 850 | 192.619(A)(2) |  | 1955-12-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 63148 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY AN EXTERNAL FORCE (FARMER DEEP-PLOWING HIS FIELD) AND THE COMPANY DIDN'T FEEL A CONTROL ROOM INVESTIGATION TO BE NECESSARY AS A RESULT OF THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [7 empty] | FARMER | FARM EQUIPMENT | GRADING | NO | [5 empty] | NO |  | OTHER |  |  |  | FARMER DIDN'T NOTIFY ONE-CALL, HOWEVER THERE WERE SUFFICIENT LINE MARKINGS NEAR THE AREA IN WHICH HE USED TO CONTACT LOCAL AUTHORITIES TO ALERT WILLIAMS ON THE LINE STRIKE. | [262 empty] | TAYLER K JENSEN | PIPELINE SAFETY ENGINEER | tayler.jensen@williams.com | 2813828869 |  |  |  |  | JOHN BELL | PIPELINE SAFETY MANAGER | 3373179145 | john.bell@williams.com | ON OCTOBER 31, 2022 WILLIAMS SECURITY OPERATION CENTER WAS NOTIFIED BY NEARBY AUTHORITIES THAT A FARMER HAD STRUCK OUT 22" MAINLINE WITH FARMING EQUIPMENT WHILE HE WAS DEEP PLOWING HIS FIELD FOR THE WINTER. IMMEDIATELY AFTER RECEIVING NOTIFICATION OF THE INCIDENT, PIPELINE OPERATIONS RESPONDED AND WENT TO THE SITE OF THE INCIDENT AS QUICKLY AS POSSIBLE. ONCE ON SITE, OPERATIONS NOTICED THAT THE LINE HAD BEEN STRUCK HARD ENOUGH TO CREATE A SMALL PUNCTURE IN THE LINE, VENTING HIGHLY PRESSURIZED GAS TO THE ATMOSPHERE. OPERATIONS QUICKLY MOVED TO MANUALLY CLOSE THE UPSTREAM AND DOWNSTREAM MAINLINE VALVES TO ISOLATE THIS SECTION OF MAINLINE FROM PRESSURIZED GAS. ONCE THIS SECTION OF MAINLINE WAS ISOLATED, CONSTRUCTION CREWS AND OPERATIONS WORKED TOGETHER TO CUT OUT THE PIECE OF DAMAGED PIPE AND INSTALL A NEW SPOOL OF PRE-TESTED PIPE. OVER THE COURSE OF THE NEXT FOUR DAYS THIS EFFORT WAS COMPLETED AND WILLIAMS WAS ABLE TO RESTORE THIS SECTION OF THE MAINLINE BACK TO SERVICE. DURING THE OUTAGE, THE 1401 LINE, WHICH RUNS PARALLEL TO THE DAMAGED 1400 LINE, WAS ABLE TO OPERATE UNDER NORMAL CONDITIONS TO AVOID ANY SIGNIFICANT DISRUPTIONS TO OUR CUSTOMERS.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220125 | 37423 | 2022-12-01 10:28 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 2800 POST OAK BLVD | HOUSTON | TX | 77056 | 2022-11-09 07:14 | 2022 | MOUNTAIN | NO | 41.8233 | -110.7896 | 1352168 | 2022-11-09 16:54 | 1352310 | NATURAL GAS |  | 3895 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | JUST THE COMPRESSOR UNIT THAT HAD THE RELIEF VALVE DISCHARGE WAS SHUT DOWN. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-11-09 06:45 | 2022-11-09 06:45 | ONSHORE | WY | 83101 | Not Within a Municipality | LINCOLN | NOT APPLICABLE |  | NWP KEMMERER COMPRESSOR STATION | KEMMERER COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2019 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | GAS RELEASED VIA A PRESSURE RELIEF VALVE | CLASS 1 LOCATION | NO |  | 510 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 34977 | 34977 | 800 | 800 | 0 | 0 | 0 | 0 |  | 8.98 | 35777 | 23302.9542775059591946843853820598006645 | 35777 | 0 | 0 | 0 | 0 | NO |  |  |  | 776 | 661000 | 866 | 192.619(A)(2) |  | 1956-12-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PSV ACTIVATION WAS NOT DUE TO A CONTROL ROOM RELATED FAILURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | PSV PILOT WAS FOUND TO FAIL DUE TO HARMONICS | [161 empty] | TAYLER K JENSEN | PIPELINE SAFETY ENGINEER | tayler.jensen@williams.com | 2813828869 |  |  |  |  | JOHN BELL | PIPELINE SAFETY MANAGER | 3373179145 | john.bell@williams.com | ON NOVEMBER 9, 2022 OPERATIONS PERSONNEL ON SITE AT THE KEMMERER COMPRESSOR STATION HEARD WHAT APPEARED TO BE A COMPRESSOR RELIEF VALVE RELIEVING GAS. UPON FURTHER INVESTIGATION THE OPERATIONS TECHNICIAN DISCOVERED THE UNIT 1 PSV WAS RELIEVING. IN ORDER TO REMEDY THE SITUATION AS QUICKLY AS POSSIBLE, THE TECHNICIAN SHUT THE UNIT DOWN, ISOLATED IT FROM PRESSURE, AND BLEW IT DOWN. IT WAS NOTED BY THE TECHNICIAN AT THE TIME THAT THE RELIEF VALVE WOULD NOT RESEAT ITSELF AFTER DECREASING PRESSURE. IT WAS ALSO NOTED THAT THE RELIEF VALVE HAD OPENED UP PREMATURELY AT A PRESSURE OF AROUND 770PSI, WHERE THE SET PRESSURE ON THE RELIEF VALVE WAS 928 PSI. SINCE OPERATIONS DIDN'T KNOW EXACTLY WHEN THE RELIEF VALVE STARTED RELEASING GAS, THEY WORKED WITH TECH SERVICES AND GAS CONTROL TO ATTEMPT TO FIND ANY DATA SIGNIFYING WHEN THE RELEASE STARTED TO OCCUR. HMI TRENDS AND STATION CCTV CAMERAS WERE UTILIZED TO TRY AND DETERMINE WHEN THE UNIT STARTED TO RELIEVE, BUT WERE UNSUCCESSFUL IN DETERMINING THE EXACT TIME. AFTER REVIEWING THAT DATA THROUGHOUT THE DAY ON NOVEMBER 9TH AND NOT FINDING A DEFINITIVE ANSWER, IT WAS DECIDED TO CALCULATE A GAS LOSS ESTIMATION FROM THE MOMENT THE OPERATOR ARRIVED ON SITE AT 06:45 TO THE TIME THE UNIT WAS COMPLETELY ISOLATED AND GAS HAD STOPPED RELEASING AT 07:22. ONCE THIS TIMEFRAME WAS DECIDED, THE GAS LOSS CALCULATION WAS PROMPTLY RUN AND FOUND TO BE IN EXCESS OF THE 3MMSCF THRESHOLD. THAT GAS LOSS ESTIMATION WAS THEN COMMUNICATED TO THE SECURITY OPERATIONS CENTER AT WILLIAMS AND WAS IMMEDIATELY REPORTED TO THE NRC THAT AFTERNOON. OVER THE COURSE OF THE FOLLOWING WEEKS, OPERATIONS WORKED WITH GAS CONTROL, SCADA, AND TECH SERVICES TO INVESTIGATE WHY THE VALVE HAD OPENED AT A LOWER PRESSURE THAN DESIGNED. IT WAS DISCOVERED THAT THE PILOT ON THIS PSV FAILED DUE TO A HARMONIC FREQUENCY AT THE STATION. IN ORDER TO REMEDY THE SITUATION, OPERATIONS WORKED TO GET A NEW AND DIFFERENT PILOT INSTALLED ON THIS PSV THAT WOULDN'T BE SUSCEPTIBLE TO PREMATURE RELIEVING AS A RESULT OF HARMONICS. OPERATIONS SUCCESSFULLY INSTALLED THE NEW PILOT ON THE PSV AND RETURNED THE COMPRESSOR UNIT TO SERVICE ON 11/18/2022.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220126 | 37404 | 2022-12-02 07:47 | ORIGINAL | 32595 | HIGH POINT GAS GATHERING, LLC | THIRD COAST MIDSTREAM, LLC PO BOX 1227 | HOUSTON | TX | 77251 | 2022-11-04 05:45 | 2022 | CENTRAL | NO | 28.869 | -88.9867 | 1351712 | 2022-11-04 10:53 | 1351906 | NATURAL GAS |  | 0.601 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | MINIMAL RELEASE ON A SECTION OF PIPE NOT AFFECTING MAIN PIPE |  |  |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | RELEASE DOES NOT IMPACT FLOW BUBBLES NOT REACHING SURFACE CONTROL CENTER MONITORING PRESSURE |  | OPERATIONAL CONTROL | RELEASE DOES NOT IMPACT FLOW BUBBLES NOT REACHING SURFACE CONTROL CENTER MONITORING PRESSURE |  | 0 | 2022-11-04 05:45 | 2022-11-18 11:00 | OFFSHORE | [6 empty] | MC 194 16" HPGT | MC 109 LATERAL 12" (BSEE 14970) | [20 empty] | 770 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | MISSISSIPPI CANYON | 108 | BELOW WATER, PIPE ON OR ABOVE SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | TAP FITTING(STOPPLE, THREAD-O-RING, WELD-O-LET, ETC.) | [38 empty] | 1985 | 1985 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 253 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 102000 | 102000 | 0 | 0 |  | 6.11 | 102004 | 45001.1180564284019734219269102990033223 | 102004 | 0 | 0 | 0 | 0 | NO |  |  |  | 828 | 0 | 1200 | 192.619(A)(2) |  | 1985-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 1 | NO | [5 empty] | YES | PIPE BLINDED OFF 8 FEET FROM LEAKING HOT TAP STOPPLE | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | CONTRACTOR WORKING FOR ANOTHER OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | [166 empty] | THREADED CONNECTION/COUPLING FAILURE | [15 empty] | PIPE NIPPLE | [19 empty] | YES | NORMAL WEAR | [161 empty] | NICKLAS PAVLOVSKY | MANAGER PIPELINE REGULATORY COMPLIANCE | npavlovsky@third-coast.com | 3462413368 |  |  |  |  | NICKLAS PAVLOVSKY | MANAGER PIPELINE REGULATORY COMPLIANCE | 3462413368 | npavlovsky@third-coast.com | ON 11/04/22 AT APPROXIMATELY 5:45AM A THIRD-PARTY OPERATOR WHILE CONDUCTING UNDER WATER (770FT) INSPECTIONS WITH A REMOTELY OPERATED VEHICLE (ROV) ON THEIR SUBSEA TIE-IN WITHIN 20 FEET OF OUR PIPE AND VALVE SITE; NOTICED BUBBLES COMING FROM A HOT TAP COMPLETION VALVE ON OUR (HIGH POINT GAS GATHERING) MC 109 LATERAL (BSEE 14970). THE OPERATOR CONTACTED OUR ENGINEERS TO REPORT THE RELEASE. FROM REPORTS THE BUBBLES BEING RELEASE ARE MINOR. THE AREA WAS FLOWN, AND NO BUBBLES WERE VISIBLE ON THE WATER SURFACE. THIS WAS ALSO CONFIRMED BY THE BOAT PRESENT ON LOCATION. CONTROL CENTER DID NOT SEE A PRESSURE DROP EITHER. AT 10:30AM IT WAS DETERMINED THAT THE MONETARY AMOUNT FOR REPAIR WOULD EXCEED THE THRESHOLD FOR IMMEDIATE NOTIFICATION AND A CALL WAS PLACED TO THE NRC AT 10:53AM ON 11/04/22 (NRC # 1351712). ON 11/07/22 AT 7:10AM A 48HR UPDATE TO THE NRC WAS PLACED (NRC# 1351906). ON 11/18/22 A SATURATION DIVE CREW ARRIVED ON SITE TO PREFORM WORK FOR THE OPERATOR THAT IDENTIFIED THE RELEASE WITHIN 20FT OF THE RELEASE. HIGH POINT GAS GATHERING WAS ABLE TO CONTRACT THE DIVE CREW TO INVESTIGATE AND REPORT ON THE RELEASE. THE PIN HOLE LEAK SEEMS TO BE COMING FROM THE STOPPLE WELD-O-LET. DUE TO THE DEPTH (770FT) AND THE AVAILABILITY OF DIVE BOAT/CREWS AND MINIMAL SIZE OF THE RELEASE; REPAIR PLANS/LOGISTICS ARE STILL BEING DEVELOPED AND SUBMITTED TO BSEE FOR APPROVAL. APPROXIMATELY 0.601 MCF OF NATURAL GAS HAS BEEN RELEASED. A SUPPLEMENTAL REPORT WILL BE FILED ONCE REPAIRS ARE COMPLETE.
2023-02-28 09:42 | YES | NO | UNGS (Underground Natural Gas Storage) | 20220127 | 37696 | 2022-12-05 17:11 | SUPPLEMENTAL | 31604 | EQUITRANS MIDSTREAM CORPORATION | 2200 ENERGY DRIVE | CANONSBURG | PA | 15317 | 2022-11-06 15:28 | 2022 | EASTERN | YES | 40.4116 | -78.945 | 1351880 | 2022-11-06 17:03 | 1352149 | NATURAL GAS |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-11-20 09:56 |  | YES | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-11-06 16:15 | NO | [11 empty] | 0 | 2022-11-06 16:15 | 2022-11-06 16:15 | ONSHORE | PA | 15906 | JACKSON TOWNSHIP | CAMBRIA COUNTY | NOT APPLICABLE |  | RAGER MOUNTAIN STORAGE | GEORGE L. READE #1 STORAGE WELL/API:37-021-20005 | NO | OPERATOR-CONTROLLED PROPERTY | BELOWGROUND STORAGE OR ABOVEGROUND STORAGE VESSEL, INCLUDING ATTACHED APPURTENANCE |  |  |  |  | NO | [22 empty] | INTERSTATE | BELOWGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | UNDERGROUND GAS STORAGE OR CAVERN | [38 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | UNDER INVESTIGATION - CURRENTLY UNKNOWN | OTHER | [8 empty] | STORAGE GAS FROM THE 7" PRODUCTION CASING WAS RELEASED THROUGH A 2" ANNULUS VENT VALVE ON THE 9 5/8" INTERMEDIATE CASING. THE FAILURE WHICH ALLOWED THE COMMUNICATION OF GAS BETWEEN THE CASINGS IS UNDER INVESTIGATION. THE ONGOING INVESTIGATION, UPON ITS CONCLUSION WILL PROVIDE THE DETAILS NEEDED TO CLASSIFY THE TYPE OF RELEASE. THESE DETAILS ARE UNKNOWN AT THIS TIME. | CLASS 1 LOCATION | NO |  | 243 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 3000000 | 3000000 | 4000000 | 4000000 | 750000 | 750000 | ENVIRONMENTAL CLEAN UP | 2.5 | 7750000 | 3419003.18044861425 | 7750000 | 0 | 0 | 0 | 0 | NO |  |  |  | 3088 | 0 | 3200 | OTHER | FERC ORDER CP15-553 3200 PSIG, DISCOVERY PRESSURE ON WELL 10/16/1965 - 3193 PSIG | 1965-10-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION IN STORAGE FIELD | YES | YES | YES | NO | NO | OTHER | ANOTHER OPERATOR IN THE AREA NOTIFIED ETRN GAS CONTROL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MONITORED PRESSURE WAS NOT AFFECTED AT TIME OF INCIDENT, DUE TO THE WELL BEING SHUT-IN AS PART OF THE INVENTORY VERIFICATION TEST. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | JOSH BOWERS | SR. ENGINEER | jbowers@equitransmidstream.com | 304-641-1112 |  | JACOB LYONS | jlyons@equitransmidstream.com | 412-295-3962 | GREGG WEST | VP ENVIRONMENTAL SAFETY AND COMP | 412-480-9900 | gwest@equitransmidstream.com | EQUITRANS RAGER MOUNTAIN STORAGE FIELD WAS SHUT-IN ON 11/1/2022 TO PERFORM ROUTINE SHUT-IN INVENTORY VERIFICATION TESTING. ON NOVEMBER 6, 2022, EQUITRANS PERSONNEL WAS NOTIFIED OF AN ISSUE AND ARRIVED ON SITE AT GSW2244 AT APPROXIMATELY 4:15 PM. UPON ARRIVAL, PERSONNEL FOUND GAS ESCAPING FROM THE 9 5/8" CASING THROUGH A 2" VENT (ANNULAR VENT). THE SITE WAS SECURED AND AN INVESTIGATION BY EQUITRANS AND CUDD PRESSURE CONTROL ENSUED. STORAGE GAS FROM THE 7" PRODUCTION CASING WAS COMMUNICATING WITH THE 9 5/8" INTERMEDIATE CASING AND VENTING TO ATMOSPHERE. EQUITRANS AND CUDD COORDINATED TO SAFELY ADDRESS THE MIGRATING GAS USING A DYNAMIC KILL PROCEDURE. ON 11/19/2022, A TEMPORARY PLUG WAS SET IN THE 7" CASING FOLLOWED BY A SECOND TEMPORARY PLUG AND APPROXIMATELY 270' OF CEMENT ON 11/20/2022. AN INVESTIGATION IS UNDERWAY TO DETERMINE THE ROOT CAUSE FAILURE ANALYSIS (RCFA) OF THE NATURAL GAS RELEASE. IN THE INTERIM, EQUITRANS PLANS TO PERFORM THE FOLLOWING ACTIVITIES TO INFORM THE RCFA AND ENSURE WELL INTEGRITY PER PHMSA SAFETY REGULATIONS AND API 1171. 1- INSTALLING REAL TIME PRESSURE MONITORS ON THE ANNULUS OF ALL RAGER MOUNTAIN GAS STORAGE WELLS. 2- REANALYZING THE 2016 VERTILOG WIRELINE RESULTS OF THE PRODUCTION CASING FROM WELL 2244 USING THE MOST RECENT SOFTWARE. 3- CONDUCTING A NEW WIRELINE SURVEY (ASSESSMENT) OF THE PRODUCTION CASINGS FOR THE OTHER WELLS WITH A HIGH DEFINITION, METAL LOSS VERTILOG TOOL. 4- EVALUATING ANY OTHER MECHANICAL GAS MIGRATION PATHWAYS BETWEEN THE PRODUCTION AND INTERMEDIATE CASING 5- REVIEWING EXISTING STORAGE WELL EMERGENCY PREPAREDNESS AND RESPONSE PROCEDURES BASED ON LESSONS LEARNED FROM SHUTTING IN WELL 2244 TO IDENTIFY AND IMPLEMENT POTENTIAL IMPROVEMENTS. FEBRUARY 2023 SUPPLEMENT NOTIFICATION OF THE INCIDENT CLARIFICATION: AT 3:28 PM ON 11/6/2022 EQUITRANS WAS NOTIFIED BY ANOTHER OPERATOR IN THE AREA (PEOPLES) WHO RECEIVED A NOTIFICATION FROM CAMBRIA COUNTY 911 SERVICE. EMERGENCY RESPONDERS WERE ON SITE WHEN EQUITRANS ARRIVED AT 4:15 PM. EQUITRANS EMPLOYEES VERIFIED THE ASSET WAS EQUITRANS GSW 2244 AND WERE IN COMMUNICATION WITH EMERGENCY RESPONDERS ON SITE. INVENTORY REDUCTION AND COSTS: FOLLOWING THE INCIDENT, EQUITRANS CONDUCTED A TEST TO ESTIMATE THE TOTAL CHANGE IN INVENTORY AT THE RAGER STORAGE RESERVOIR. THE RESULTS INDICATE AN ESTIMATED INVENTORY REDUCTION OF APPROXIMATELY 1.29 BCF. EQUITRANS CONTINUES TO EVALUATE THE ALLOTMENT OF THIS INVENTORY REDUCTION THAT MAY BE ATTRIBUTABLE TO VENTING OR POTENTIAL MIGRATION. IN THIS REPORT, EQUITRANS ESTIMATES GAS COSTS OF APPROXIMATELY $3MM (LINE D7F AND D7H), WHICH IS BASED ON A POTENTIAL 2023 UNIT PRICE TO REPLACE THE ENTIRETY OF THE ESTIMATED 1.29 BCF OF INVENTORY REDUCTION, AND ESTIMATED TOTAL COST OF $10.75MM (LINE D7I). EQUITRANS INCLUDES THIS INFORMATION FOR REPORTING PURPOSES ONLY; INCLUDING SUCH INFORMATION DOES NOT REQUIRE OR IMPLY THAT EQUITRANS WILL INCUR SUCH COSTS.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220128 | 37435 | 2022-12-08 09:07 | ORIGINAL FINAL | 31130 | DCP MIDSTREAM | 6900 E. LAYTON AVE. SUITE 900 | DENVER | CO | 80237-3658 | 2022-11-08 23:36 | 2022 | CENTRAL | YES | 36.3821 | -98.6899 | 1352141 | 2022-11-09 13:00 | 1352235 | NATURAL GAS |  | 3574.99 | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-11-09 00:35 |  | YES | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | UNITS UPSTREAM OF FAILURE LOCATION SHUTDOWN AUTOMATICALLY WITH LOSS OF DISCHARGE PRESSURE |  | VALVE CLOSURE |  | 2022-11-09 00:35 | 0 | 2022-11-08 23:36 | 2022-11-09 00:35 | ONSHORE | OK | 73737 | Not Within a Municipality | MAJOR COUNTY | NOT APPLICABLE |  | CM-5-8 | CM-5-8 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE SEAM | 8.625 |  | 0.188 | 42000 | API 5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1984 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 192 | 12 |  | CLASS 1 LOCATION | NO |  | 188 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 10189 | 10189 | 20000 | 20000 | 0 | 0 | 0 | 0 |  | 2.85 | 30189 | 15508.7074359878502990033222591362126246 | 30189 | 0 | 0 | 0 | 0 | NO |  |  |  | 930 | 8000 | 1000 | 192.619(A)(2) |  | 1984-05-25 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  | MANUAL | 52800 | NO |  |  | YES |  |  |  |  | NO | [6 empty] | TYPE C GATHERING | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE IS NOT UNDER CONTROL ROOM MANAGEMENT AND IS ONLY MONITORED REMOTELY. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING | [5 empty] | YES | FAILED PIPE SENT FOR LABORATORY ANALYSIS TO DETERMINE CAUSE OF CORROSION - SUPPLEMENTAL REPORT WILL BE FILED UPON RECEIPT OF FINAL LABORATORY REPORT. |  | YES | YES | FAILED PIPE SENT FOR LABORATORY ANALYSIS TO DETERMINE CAUSE OF CORROSION - SUPPLEMENTAL REPORT WILL BE FILED UPON RECEIPT OF FINAL LABORATORY REPORT. |  |  |  |  | YES | TOP POINT OF THE PIPE, 12 O'CLOCK | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | MICHAEL MAY | PIPELINE COMPLIANCE SPECIALIST | mlmay@dcpmidstream.com | 4055093343 |  | MICHAEL MAY | mlmay@dcpmidstream.com | 4055093343 | MIKE PAVLAK | PIPELINE COMPLIANCE MANAGER | 9703970732 | mpavlak@dcpmidstream.com | OPERATOR ON CALL WAS NOTIFIED BY ICC (DCP REMOTE MONITORING CENTER) THAT RATTLESNAKE BOOSTER WENT DOWN ON LOW DISCHARGE PRESSURE TO BARNEY BOOSTER AT 11:49 PM CST ON 11-8-22. OPERATOR REVIEWED SCADA PRESSURE TRENDS AND DETERMINED THAT THERE WAS A PIPELINE FAILURE BETWEEN RATTLESNAKE AND BARNEY BOOSTERS. OPERATOR DROVE TO BARNEY BOOSTER AND SHUT THE BLOCK VALVE AT 12:35 AM CST ON 11-9-22 ISOLATING THE LINE. RATTLESNAKE BOOSTER'S DISCHARGE BLOCK VALVES CLOSED AUTOMATICALLY DUE TO LOW DISCHARGE PRESSURE SHUTDOWN SET POINTS. OPERATOR LOCATED FAILURE POINT AND ENSURED SITE WAS SAFE. FAILED PIPE CUT OUT AND SENT FOR LABORATORY ANALYSIS. PIPELINE REPAIRS ARE NOT COMPLETE AT THIS TIME. SUPPLEMENTAL REPORT WILL BE FILED. RELEASE DETERMINED TO BE REPORTABLE BASED ON UNINTENTIONAL GAS LOSS VOLUME CALCULATION ON 11-9-22 AT 12:30 PM CST.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220129 | 37713 | 2022-12-09 10:38 | SUPPLEMENTAL FINAL | 32005 | ENLINK PROCESSING SERVICES, LLC | 1722 ROUTH STREET SUITE 1300 | DALLAS | TX | 75201 | 2022-11-11 23:30 | 2022 | CENTRAL | NO | 29.8624 | -92.4471 | 1352375 | 2022-11-12 02:23 | 1352481 | NATURAL GAS |  | 20420 | 34843 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [8 empty] | YES | 2022-11-11 23:30 | ALLOWED TO BURN OUT |  | 20420 | NO | VALVE CLOSURE |  | 2022-11-12 01:37 | VALVE CLOSURE |  | 2022-11-12 01:40 | 0 | 2022-11-11 23:30 | 2022-11-12 03:50 | ONSHORE | LA | 70548 | Not Within a Municipality | VERMILION | NOT APPLICABLE |  | P1122 FLORENCE 6" LATERAL | P1122 FLORENCE 6" LATERAL | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | SCRAPER/PIG TRAP | [38 empty] | 1977 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | NO |  | 146 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 231358 | 231358 | 135589 | 135589 | 36898 | 36898 | 0 | 0 | 0 | 0 |  | 6.64 | 403845 | 207310.4775027334531084119601328903654485 | 403845 | 0 | 0 | 0 | 0 | NO |  |  |  | 885 | 42.4 | 1100 | 192.619(A)(2) |  | 1977-11-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 204811 | NO | [5 empty] | YES | PIPELINE IS NOW SHUTDOWN. WAS NOT IN USE AT THE TIME OF THE INCIDENT. | YES |  |  | YES |  |  |  | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM PERSONNEL RESPONDED TO THE LOSS OF PRESSURE AS EXPECTED. INCIDENT WAS NOT CAUSED BY CONTROLLER ACTION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [103 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [261 empty] | CORDELL THERIOT | SR. DOT SPECIALIST | cordell.theriot@enlink.com | 3373226682 |  | CORDELL THERIOT | cordell.theriot@enlink.com | 3373226682 | CORDELL THERIOT | SR. DOT SPECIALIST | 3373226682 | cordell.theriot@enlink.com | A LANDOWNER WAS BURNING HIS FIELD WHEN THE FIRE SPREAD TO THE WOODEN PIPELINE SUPPORT STRUCTURE. WHEN THE SUPPORT STRUCTURE WAS DESTROYED, THE ABOVE GROUND PIPING COLLAPSED. THIS CAUSED THE PIPING TO SEPARATE AT AN INSULATING FLANGE, WHICH THEN RELEASED AND IGNITED THE GAS IN THE PIPELINE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220130 | 37463 | 2022-12-14 15:33 | ORIGINAL | 2620 | COLUMBIA GULF TRANSMISSION, LLC | 700 LOUISIANA ST. SUITE 700 | HOUSTON | TX | 77002 | 2022-11-19 14:48 | 2022 | EASTERN | YES | 37.8885 | -83.8615 | 1353001 | 2022-11-19 15:21 | 1353101 | NATURAL GAS |  | 5328.8 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | INCIDENT WAS ISOLATED AT 14:30 |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-11-19 13:45 | 2022-11-19 14:00 | ONSHORE | KY | 40380 | Not Within a Municipality | POWELL | NOT APPLICABLE |  | STANTON COMPRESSOR STATION | UNIT 108 BLOWDOWN VALVE AOV-8810 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2001 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | UNINTENTIONAL VALVE RELEASE. | CLASS 2 LOCATION | NO |  | 88 |  | NO | NO |  |  | YES | YES |  | 0 | 0 | 0 | 0 | 26857 | 26857 | 0 | 0 | 240 | 240 | 0 | 0 |  | 5.04 | 27097 | 17727.9967483680668281727574750830564784 | 27097 | 0 | 0 | 0 | 0 | NO |  |  |  | 779 | 170286 | 1007 | OTHER | ANSI 600 VALVE | 2001-02-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AT THIS TIME THE CAUSE OF THE INCIDENT WAS DUE TO PLC POWER AND RELAY FAILURE, NOT CONTROL ROOM ACTION. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | BEN HUNLEY | COMPLIANCE SPECIALIST | ben_hunley@tcenergy.com | 304-539-9311 |  |  |  |  | PAUL SHAFFER | MANAGER | 304-550-4866 | paul_shaffer@tcenergy.com | COLUMBIA GULF TRANSMISSION, LLC, A TC ENERGY COMPANY, OPERATES AND MAINTAINS STANTON COMPRESSOR STATION LOCATED IN STANTON, KENTUCKY. ON SATURDAY NOVEMBER 19TH, 2022 A TC ENERGY CLEANING CONTRACTOR HEARD GAS VENTING INTO THE ATMOSPHERE WHILE PERFORMING THEIR DUTIES AT STANTON COMPRESSOR STATION. THE CONTRACTOR IMMEDIATELY CONTACTED COMPRESSOR STATION PERSONNEL; THE STATION PERSONNEL RESPONDED TO THE GAS RELEASE AT STANTON COMPRESSOR STATION AND ADDRESSED THE UNINTENDED RELEASE OF NATURAL GAS THAT WAS VENTING FROM UNIT 108 BLOWDOWN DISCHARGE STACK. THE STATION PERSONNEL INSPECTED AND SECURED THE AREA TO ENSURE THAT IT WAS SAFE; THEN THEN IDENTIFIED VALVES TO ISOLATE THE GAS LINE. THE LINE WAS ISOLATED AT 14:30 EASTERN TIME. ONCE THE LINE WAS ISOLATED THE STATION OPERATING PERSONNEL BEGAN TROUBLESHOOTING THE ISSUE. ALL ALARMS WERE CLEARED AT THE CONTROL PANEL, FUNCTIONAL TESTS WERE COMPLETED WITH NO NEW ERRORS GENERATED TO ENSURE NORMAL OPERATION OF THE STATION. PRELIMINARY INVESTIGATION IDENTIFIED THE PROBABLE CAUSE THAT LED TO THIS UNINTENDED RELEASE AT UNIT 108 WAS DUE TO A LOSS OF POWER TO A PROGRAMMABLE LOGIC CONTROLLER (PLC) AND RELAY FAILURE. THE LOSS OF POWER TO THIS PLC CAUSED THE COMPRESSOR UNIT BLOW DOWN VALVE (AOV 8810) TO REMAIN OPEN. THE VALVE REMAINED OPEN FOR 50 MINUTES RESULTING IN AN ESTIMATED TOTAL GAS LOST OF 5,328.8 MCF. THE PRESSURE OF THE LINE AT THE TIME OF THE INCIDENT WAS 779 LBS. AN INVESTIGATION IS STILL UNDERWAY INTO THE CAUSE OF THE RELEASE.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20220131 | 37480 | 2022-12-16 10:05 | ORIGINAL FINAL | 39913 | DTM LOUISIANA GATHERING, LLC | 500 WOODWARD AVE. SUITE 2900 | DETROIT | MI | 48226 | 2022-10-05 15:37 | 2022 | CENTRAL | NO | 32.0409 | -93.5421 | 1350334 | 2022-10-19 14:36 | 1350687 | NATURAL GAS |  | 32.9 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE SHUTDOWN | [5 empty] | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-10-05 16:10 | OPERATIONAL CONTROL | DOWNSTREAM OF THE OPP RELIEF VALVE HAD ALREADY BEEN SECURED PRIOR TO THE RELEASE DUE TO MAINTENANCE |  | 0 | 2022-10-05 15:37 | 2022-10-05 16:00 | ONSHORE | LA | 71032 | GRAND CANE | DESOTO | NOT APPLICABLE |  | DTM LOUISIANA GATHERING AREA 1 | M5L-308-00A | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | OVER PRESSURE CONDITION FROM THE UPSTREAM PRODUCER'S WELL LED TO THE OPERATION OF A DTM OVER PRESSURE PROTECTION DEVICE (RELIEF VALVE) | CLASS 1 LOCATION | NO |  | 197 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 436 | 436 | 0 | 0 | 5000 | 5000 | 0 | 0 |  | 13.25 | 5436 | 2491.888237734504102990033222591362126246 | 5436 | 0 | 0 | 0 | 0 | NO |  |  |  | 1210 | 2100 | 1200 | 192.619(A)(2) |  | 2010-12-17 | NO | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO |  | MANUAL |  | 6963 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM IS A MONITOR-ONLY FOR THAT SYSTEM AND SUCCESSFULLY HANDLED THE PRESSURE ALARM BY CALLING OUT LOCAL FIELD STAFF. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [204 empty] | OTHER INCORRECT OPERATION |  |  | FAILURE OF PRODUCER'S PRESSURE CONTROL AND OVER PRESSURE PROTECTION TO CONTROL DELIVERY TO DTM'S GATHERING LINE, RESULTING IN THE OPERATION OF DTM'S OPP DEVICE. |  |  |  | YES | THE PRODUCER'S PRESSURE CONTROL DEVICES WERE SET TO A POINT ABOVE THEIR CONTRACTUAL MAXIMUM (1200 PSIG) | NORMAL OPERATING CONDITIONS | NO | [150 empty] | PATRICK RAICHEL | SENIOR SUPERVISOR | patrick.raichel@dtmidstream.com | 17163276630 |  | REX GAGE | rex.gage@dtmidstream.com | 3047121758 | PHILIP COLEMAN | DIRECTOR CODES AND REGULATORY | 7347304870 | philip.coleman@dtmidstream.com | AN ACTUATION OF DTM'S OPP DEVICE LED TO AN UNINTENTIONAL RELEASE OF NATURAL GAS EXCEEDING 3 MMCF. THIS ACTUATION WAS CAUSED BY THE INCORRECT SET POINTS ON THE PRODUCER'S PRESSURE REGULATING EQUIPMENT UPSTREAM OF THE CUSTODY TRANSFER POINT BETWEEN THE TWO SYSTEMS.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220132 | 37592 | 2022-12-18 15:44 | SUPPLEMENTAL FINAL | 2564 | COLORADO INTERSTATE GAS CO | 1001 LOUISIANA ST, SUITE 1000 | HOUSTON | TX | 77002 | 2022-11-18 10:05 | 2022 | MOUNTAIN | NO | 42.3757 | -107.4268 | 1352961 | 2022-11-19 23:52 | 1353040 | NATURAL GAS |  | 59321 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | IDLE | [5 empty] | NO |  |  | NO | [11 empty] | 0 | 2022-11-18 22:13 | 2022-11-18 23:20 | ONSHORE | WY | 82301 | MUDDY GAP | CARBON | NOT APPLICABLE |  | MUDDY GAP COMPRESSOR STATION | MUDDY GAP COMPRESSOR STATION | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 2001 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | OTHER | VENT VALVE OPENED | [5 empty] | CLASS 1 LOCATION | NO |  | 406 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 335164 | 335164 | 500 | 500 | 300 | 300 | 0 | 0 |  | 5.65 | 335964 | 220269.5074336521385966777408637873754153 | 335964 | 0 | 0 | 0 | 0 | NO |  |  |  | 798 | 0 | 1100 | 192.619(A)(1) |  | 1977-11-21 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | [24 empty] | YES | ESD VALVE SOLENOID FAILED DUE TO DEBRIS ACCUMULATION | [161 empty] | JORGE LOPEZ |  | jorge_lopez@kindermorgan.com | 7134204675 |  |  |  |  | JAIME HERNANDEZ |  | 17133699443 | jaime_hernandez@kindermorgan.com | ON 11/18/2022, AT 09:37, A 3 INCH EMERGENCY SHUT DOWN (ESD) VALVE UNINTENTIONALLY OPENED AT THE COLORADO INTERSTATE GAS (CIG), MUDDY GAP COMPRESSORS STATION. AT 22:14, CIG GAS CONTROL CALLED THE FIELD OPERATOR ON DUTY AND COMMUNICATED THAT PRESSURE WAS TRENDING DOWN AND A VENT VALVE MAY BE OPEN AT THE MUDDY GAP COMPRESSOR STATION. AT 23:30, CIG FIELD OPERATOR ARRIVED ON SITE AND DISCOVERED AN ESD VALVE WAS OPEN. THE OPERATOR CLOSED THE VALVE. THE INCIDENT WAS DEEMED REPORTABLE. THE NRC NOTIFICATION WAS ISSUED, AND THE INTERNAL INVESTIGATION STARTED. THE INTERNAL INVESTIGATION CONCLUDED THAT THE ESD VALVE SOLENOID FAILED DUE TO AN ACCUMULATION OF WATER AND DEBRIS FROM THE STATION SUPPLY AIR SYSTEM THAT FROZE CAUSING THE VALVE TO OPERATE ABNORMALLY SENDING A PNEUMATIC OPEN SIGNAL TO THE ESD VALVE. IN ADDITION, THE VALVE STATUS WAS NOT IN SCADA AND THE CONTROLLERS DID NOT GET AN ALARM NOTIFYING THEM THAT THE VENT VALVE WAS OPEN. IN ORDER TO PREVENT REOCCURRENCE CIG OPERATIONS CLEANED AND RE-TESTED THE VALVE SOLENOID. OPERATIONS IS REVIEWING PROCESSES AND PREVENTIVE MAINTENANCE MEASURES TO VERIFY THAT THE MUDDY GAP CS SUPPLIED AIR SYSTEMS ARE DRY THROUGHOUT THE ENTIRE SYSTEM. IN ADDITION, OPERATIONS ADDED VALVE STATUS PLC LOGIC ALARMS IN SCADA FOR THE MUDDY GAP ESD VALVES.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20220133 | 37487 | 2022-12-19 10:37 | ORIGINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2022-11-20 05:48 | 2022 | EASTERN | NO | 42.207 | -83.9692 | 1353096 | 2022-11-21 09:48 | 1353170 | NATURAL GAS |  | 3560 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | THE LEVEL-CONTROLLER AND DUMP VALVE WAS BY-PASSED (MANUAL OPERATION) |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-11-21 06:00 | 2022-11-21 06:00 | ONSHORE | MI | 48158 | MANCHESTER | WASHTENAW | NOT APPLICABLE |  | FREEDOM COMPRESSOR STATION | FILTER-SEPARATOR CONDENSATE SYSTEM | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2020 | 2018 | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | LEVEL CONTROLLER | OTHER | [8 empty] | CONTINUOUS VENTING DUE TO THE LEVEL CONTROLLER HOLDING DUMP VALVE OPEN ALLOWING NATURAL GAS TO FREELY FLOW FROM THE FILTER SEPARATOR TO THE CONDENSATE STORAGE TANK VENT. | CLASS 3 LOCATION | YES | METHOD2 | 85 |  | NO | NO | [5 empty] | 0 | 0 | 0 | 0 | 20541 | 20541 | 5707 | 5707 | 68 | 68 | 0 | 0 |  | 5.77 | 26316 | 16025.6074926564419399501661129568106312 | 26316 | 0 | 0 | 0 | 0 | NO |  |  |  | 668 | 225 | 960 | 192.619(A)(2) |  | 2019-04-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AS DESIGNED THERE WERE NO ALARM NOTIFICATIONS SENT TO GAS CONTROL | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | [204 empty] | EQUIPMENT NOT INSTALLED PROPERLY | [6 empty] | YES | THE LEVEL CONTROLLER WAS NOT CALIBRATED DURING COMMISSIONING DUE TO THE LACK OF CONDENSATE LIQUID NEEDED TO APPROPRIATELY SET THE FUNCTIONAL LEVEL. | COMMISSIONING | NO | [150 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON E. PIONK | GAS COMPLIANCE MANAGER | 989-598-5031 | jason.pionk@cmsenergy.com | ON NOVEMBER 21, 2022, AT APPROXIMATELY 06:00 HOURS, A STATION MECHANIC REPORTING TO WORK AT THE CONSUMERS ENERGY'S FREEDOM COMPRESSOR STATION OBSERVED GAS BLOWING AT/NEAR THE CONDENSATE STORAGE TANK. FREEDOM COMPRESSOR STATION IS LOCATED AT 12201 E. PLEASANT LAKE ROAD, MANCHESTER, (WASHTENAW COUNTY) MICHIGAN. THE EMPLOYEE RESPONDED BY UTILIZING ISOLATION VALVE (30SDV-012) TO STOP THE GAS FROM BLOWING AND BEGAN A PRELIMINARY INVESTIGATION TO DETERMINE THE CAUSE OF THE GAS RELEASE. A REVIEW OF THE SECURITY FOOTAGE AND CONFIRMATION OF HISTORIAN DATA DETERMINED THE RELEASE BEGAN ON SUNDAY, NOVEMBER 20, 2022, AT APPROXIMATELY 05:48 HOURS. THE INITIAL INVESTIGATION ON NOVEMBER 21, 2022 DETERMINED THE FILTER SEPARATOR DUMP VALVE (30GV-528) DID NOT CLOSE AFTER THE CONDENSATE DUMP OPERATION AND ALLOWED GAS TO FLOW FREELY FROM THE FILTER-SEPARATOR TO THE CONDENSATE STORAGE TANK AND RELEASE TO ATMOSPHERE. CE PERSONNEL INITIATED AN ABNORMAL EQUIPMENT ALIGNMENT/CONFIGURATION REQUEST (AEC) TO ISOLATE THE FILTER-SEPARATOR CONDENSATE SYSTEM TO ALLOW FOR MANUAL OPERATION. FURTHER INVESTIGATION DETERMINED THE ROOT CAUSE OF THE RELEASE WAS DUE TO THE FILTER SEPARATOR SOUTH SUMP LEVEL CONTROLLER (LC_3001500). THE LEVEL CONTROLLER SENT A PNEUMATIC SIGNAL TO THE DUMP VALVE WHICH OPENED THE VALVE TO INITIATE THE CONDENSATE DUMP PROCESS. AFTER THE DUMP OPERATION WAS COMPLETE, THE SIGNAL TO CLOSE THE VALVE WAS NOT INITIATED (REMOVED) CAUSING THE DUMP VALVE TO REMAIN OPEN. ON DECEMBER 7, 2022, CONSUMERS ENERGY (CE) PERSONNEL MET WITH THE LOCAL MAGNETROL LEVEL CONTROLLER SALES ENGINEER TO TROUBLESHOOT THE LEVEL CONTROLLER OPERATION. DURING THE INVESTIGATION IT WAS DISCOVERED THE LEVEL ADJUSTMENT KNOB WAS SET AT 1 WHICH WAS LOWER THAN RECOMMENDED FOR THIS OPERATION. STATION PERSONNEL PROCEEDED TO INCREASE THE LEVEL CONTROL SET POINT WHILE MONITORING SYSTEM RESPONSE. AFTER ADJUSTING THE LEVEL TO A SET POINT OF 5, WHICH WAS DETERMINED TO BE AN ACCEPTABLE LEVEL SET POINT FOR OPERATION. CE PERSONNEL WILL CONTINUE TO EVALUATING GAS COMPRESSION STATION LEVEL CONTROLLERS AND GAS CONTROL NOTIFICATION METHODS TO ALARM IN THE EVENT OF GAS RELEASE ASSOCIATED WITH PNEUMATIC LEVEL CONTROL DEVICES. THE UNIT WILL REMAIN IN BY-PASS MODE UNTIL THE EVALUATION IS COMPLETED AND ACTIONS TO MITIGATE ARE IMPLEMENTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220134 | 37660 | 2022-12-20 13:15 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2022-12-02 00:01 | 2022 | MOUNTAIN | NO | 44.2584 | -108.9358 | 1353992 | 2022-12-02 13:50 | 1354119 | NATURAL GAS |  | 5212 | 0.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | BYPASSED FOR REPAIR, NOT SHUT DOWN |  |  |  | YES | OPERATOR | 2022-11-29 18:45 | NO | [5 empty] | OPERATIONAL CONTROL | GAS CONTROL MONITORED PRESSURE UNTIL REPAIRS WERE MADE. |  | OPERATIONAL CONTROL | GAS CONTROL MONITORED PRESSURE UNTIL REPAIRS WERE MADE. |  | 0 | 2022-11-29 13:53 | 2022-11-29 13:53 | ONSHORE | WY | 82414 | Not Within a Municipality | PARK | NOT APPLICABLE |  | JUNCTION TO MEETEETSE | NA | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.156 | UNKNOWN | UNKNOWN | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | NONE |  | NO | [26 empty] | UNKNOWN | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | .38 DIAMETER OF THE HOLE | CLASS 1 LOCATION | NO |  | 106 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 3 | 3 | 32731 | 32731 | 255026 | 255026 | 15000 | 15000 | 0 | 0 |  | 6.28 | 302760 | 140602.7734771497228812724252491694352159 | 302760 | 0 | 0 | 0 | 0 | NO |  |  |  | 340 | 1750 | 440 | OTHER | DEFAULT MIN ON MATERIALS | 1899-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 15840 | NO |  | YES | YES |  |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE TO TRANSMISSION LINE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [103 empty] | OTHER OUTSIDE FORCE DAMAGE | [9 empty] | LICENSED HUNTER ON A GUIDED TOUR SHOT AT ANIMAL AND INSTEAD HIT AN ABOVE GROUND PIPELINE | [251 empty] | KACY BOULEY | PIPELINE SAFETY PROFESSIONAL | kacy.bouley@blackhillscorp.com | 3078400590 |  | ROD WIETZKI | rod.wietzki@blackhillscorp.com | 307-761-0068 | KACY BOULEY | PIPELINE SAFETY PROFESSIONAL | 307-840-0590 | kacy.bouley@blackhillscorp.com | ON 11-29-2022 AT APPROXIMATELY 13:53, A 6" TOP OF GROUND TRANSMISSION LINE WAS IDENTIFIED AS BEING SHOT BY A HUNTER WITH A BULLET. PRESSURE DROPPED AND STABILIZED AT 325LBS AT APPROXIMATELY 18:19. REPAIRS BEGAN 12-03-2022 FOR INSTALLING A BYPASS, PRESSURE TESTING, AND REPLACING PIPE. BLOWING GAS WAS STOPPED AT APPROXIMATELY 20:31. REPAIRS WERE FINISHED AND NORMAL OPERATIONS WERE RESTORED 12-04-2022 AT APPROXIMATELY 10:30.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20220135 | 37516 | 2022-12-27 13:21 | ORIGINAL | 2714 | EASTERN GAS TRANSMISSION AND STORAGE, INC. | 925 WHITE OAKS BOULEVARD | BRIDGEPORT | WV | 26330 | 2022-11-28 23:28 | 2022 | EASTERN | NO | 39.5501 | -80.6696 | 1353645 | 2022-11-29 01:04 | 1353781 | NATURAL GAS |  | 23403 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-11-28 23:33 |  | YES | YES | OPERATOR | 2022-11-28 23:30 | NO | [5 empty] | OPERATIONAL CONTROL | UNIT C300 AT HASTINGS COMPRESSOR STATION SHUTDOWN AND ASSOCIATED UNIT VALVES CLOSED. |  | VALVE CLOSURE |  | 2022-11-28 23:33 | 0 | 2022-11-28 23:23 | 2022-11-28 23:50 | ONSHORE | WV | 26419 | PINE GROVE | WETZEL | SURVEY STATION NO. | 5+00 | TL-442 | TL-442 | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 62 | NO | NO | [22 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 60000 | API X-60 | LONGITUDINAL ERW - HIGH FREQUENCY |  | REPUBLIC STEEL | OTHER | PIPE COATING WAS COAL TAR, GIRTH WELD COATING WAS COLD APPLIED TAPE | YES | [26 empty] | 1981 | 1981 | CARBON STEEL |  | RUPTURE |  |  |  |  | LONGITUDINAL |  | 50.3 | 0.1 |  | CLASS 1 LOCATION | NO |  | 347 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 140418 | 140418 | 380000 | 380000 | 5000 | 5000 | 553600 | 553600 | FAILURE ANALYSIS, WIRELINE & VIDEO CAMERA INSPECTION, INITIAL VERIFICATION DIGS | 6 | 1079018 | 506209.1064991490171900332225913621262458 | 1079018 | 0 | 0 | 0 | 0 | NO |  |  |  | 947 | 134047.19 | 990 | 192.619(A)(1) |  | 1981-11-10 | NO | PRESSURE DID NOT EXCEED MAOP | YES | NO | NOT MANDATED | NO |  |  | REMOTELY CONTROLLED | 1420 | NO | [5 empty] | YES | NO LAUNCHERS OR RECEIVERS ARE INSTALLED TO FACILITATE IN-LINE INSPECTION OF THE PIPELINE. | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS OR CONTROL ROOM ISSUES WERE NOT A CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. GAS CONTROL ISOLATED TL-442 11 MINUTES AFTER INITIATION OF THE RUPTURE BY REMOTELY CLOSING VALVE-420JJ. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES | YES |  |  | YES | YES | 1981 | YES | YES | YES | YES |  |  | 2021 | 2017 |  |  | NO | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | DANIEL STAHL | PIPELINE INTEGRITY ENGINEER | daniel.stahl@bhegts.com | 3042666062 |  | MATT PAPE | brian.pape@bhegts.com | 6814954250 | MIKE FERGUSON | MANAGER - PIPELINE INTEGRITY | 8032600335 | mike.ferguson@bhegts.com | ON 11/28/22 AT APPROX 23:22, TL-442 RUPTURED AT STA 5+00 UNDER AN ACCESS ROAD ON COMPANY PROPERTY IN PINE GROVE, WV. INITIAL NOTICE WAS RECEIVED FROM AN OUTSIDE PARTY AT APPROX 23:23. TL-442 IS A 16 IN OD TRANSMISSION PIPELINE APPROX 0.30 MI LONG AND TRANSPORTS NATURAL GAS FROM HASTINGS CS TO MOCKINGBIRD HILL CS. THE MAOP OF TL-442 IS 990 PSIG. A PRESSURE RESTRICTION OF 960 PSIG WAS EST FOR TL-442 DUE TO ITS CONNECTION TO TL-430 AT HAUGHT JCT. TL-442 WAS IN NORMAL OPERATION WITH AN OP OF 947 PSIG WHEN THE INCIDENT OCCURRED. AT APPROX 23:30, OPS PERSONNEL CALLED 911. ALSO AT APPROX 23:30, THE C-300 UNIT AT HASTINGS CS SHUTDOWN AND THE ASSOCD UNIT VALVES CLOSED, ISOLATING TL-442 UPSTREAM OF THE RUPTURE. AT APPROX 23:33, GAS CONTROL REMOTELY CLOSED VALVE-420JJ, ISOLATING TL-442 DOWNSTREAM OF THE RUPTURE. AT APPROX 23:50, OPS PERSONNEL ARRIVED AT THE SITE. THE RUPTURE RESULTED IN AN APPROX 40 FT LENGTH OF PIPE OPENING CIRCUMFERENTIALLY AND LONGITUDINALLY (NOT SEAM ORIENTED) AND BOTH ENDS FOLDING UP AND COMING OUT OF THE GROUND; APPROX 23,403 MCF OF GAS LOSS; DAMAGE TO THE ACCESS ROAD; AND DEBRIS BEING BLOWN ON THE RIGHT-OF-WAY, STATE ROUTE 20, AND A RR. STATE ROUTE 20 AND THE RR WERE TEMP CLOSED AT 23:40 TO REMOVE DEBRIS. THE GAS DID NOT IGNITE AND THERE WERE NO FIRES, INJURIES, FATALITIES, OR EVACS. IT WAS DETERMINED ON 11/29/2022 AT 00:44 THAT THE INCIDENT INVOLVED AN UNINTENTIONAL EST VOL OF GAS LOSS OF 3 MMSCF OR MORE. INITIAL NOTIFICATION (#1353645) WAS MADE TO THE NRC ON 11/29/22 AT 01:04. FOLLOW UP NOTIFICATION (#1353781) WAS MADE TO THE NRC ON 11/30/22 AT 11:46 TO CONFIRM THE INITIAL NOTIFICATION AND UPDATE THE CURRENT STATUS OF TL-442, THE GPS COORDS, THE EST VOL OF UNINTENTIONAL GAS LOSS, AND THE TEMP CLOSURE (AND REOPENING) OF STATE ROUTE 20 AND THE RR IN ORDER TO REMOVE DEBRIS. THE EST VOL OF UNINTENTIONAL GAS LOSS WAS LATER CONFIRMED TO BE 23,403 MCF. THE ISOLATION OF TL-442 REMAINS IN EFFECT. THE FOLLOWING REMEDIATION ACTIONS WERE COMPLETED: THE FIRST 300 FT OF TL-442 WAS REMOVED AND REPLACED ALONG WITH VALVE-425D TO RESUME THE FLOW OF GAS BETWEEN HASTINGS CS AND MOCKINGBIRD HILL CS THROUGH TL-597 AND INTO TL-430 WHILE THE REMEDIATION OF TL-442 IS COMPLETED. BOTH ENDS OF THE PIPE WERE CUT AT THE RUPTURE ON TL-442, UPSTREAM AND DOWNSTREAM OF THE HINGED AREAS WHERE THE PIPE FOLDED UP AND CAME OUT OF THE GROUND. THE 2 PIECES OF PIPE THAT WERE CUT-OUT AT THE RUPTURE WERE SENT TO KIEFNER FOR METALLURGICAL ANALYSIS AND REPLACEMENT PIPE WAS INSTALLED. THE METALLURGICAL REPORT FROM KIEFNER IS PENDING, BUT THE PRELIM INDICATION IS THAT EXTERNAL CORROSION WAS THE APPARENT CAUSE OF THE FAILURE. PIPE WAS CUT-OUT AT SELECTED LOCATIONS TO PROVIDE ACCESS TO THE INSIDE OF TL-442 FOR WIRELINE INSPECTIONS. WIRELINES USING CAL AND MFL TOOLS WERE CONDUCTED TO ASSESS THE INTEGRITY OF TL-442 AND REPLACEMENT PIPE WAS INSTALLED AT THE ACCESS LOCATIONS. INITIAL VERIFICATION DIGS WERE COMPLETED ON EITHER SIDE OF THE RUPTURE TO ASSIST IN VALIDATING THE ACCURACY OF THE DATA FROM THE WIRELINES. BASED ON THE DATA FROM THE WIRELINES, THE RESULTS FROM THE INITIAL VERIFICATION DIGS, AND THE EVALUATION OF ANOMALIES AS DESCRIBED BELOW, APPROX 950 FT OF TL-442 WAS REPLACED. THIS INVOLVED REPLACING 2 SECTIONS OF TL-442, FROM VALVE-425D TO THE SOUTH SIDE OF FISHING CREEK AND FROM THE NORTH SIDE OF STATE ROUTE 20 TO MOCKINGBIRD HILL JCT. THE ANOMALIES LOCATED IN THESE 2 SECTIONS WERE EVALUATED AS THE PIPE WAS EXCAVATED PRIOR TO REMOVAL AND FURTHER VERIFIED THE ACCURACY OF THE DATA FROM THE WIRELINES. APPROX 120 FT OF TL-442 LOCATED IN A CASING UNDER THE RR AND STATE ROUTE 20 WAS REMOVED AND REPLACEMENT PIPE WAS INSTALLED. AN ANOMALY LOCATED ON THE CASED PIPE THAT WAS REMOVED WAS EVALUATED AND FURTHER VERIFIED THE ACCURACY OF THE DATA FROM THE WIRELINES. A SUPPLEMENTAL INCIDENT REPORT WILL BE SUBMITTED ONCE TL-442 IS RETURNED TO SERVICE AND WILL CONFIRM THE APPROX SIZE OF THE RUPTURE AND THE APPARENT CAUSE OF THE FAILURE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20230001 | 37701 | 2023-01-09 17:08 | SUPPLEMENTAL FINAL | 13845 | NORTHWEST PIPELINE LLC | 2800 POST OAK BLVD | HOUSTON | TX | 77056 | 2022-12-19 01:38 | 2022 | MOUNTAIN | NO | 40.5685 | -109.3326 | 1355337 | 2022-12-19 02:48 | 1355413 | NATURAL GAS |  | 3790 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | NO | THE FACILITY REMAINED OPERATIONAL, THIS SPECIFIC UNIT WAS SHUTDOWN |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-12-19 00:43 | 2022-12-19 02:45 | ONSHORE | UT | 84078 | VERNAL | UINTAH | MILEPOST | 330.26 | NWP VERNAL COMPRESSOR STATION | NORTHWEST PIPELINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | VALVE | [31 empty] | AUXILIARY OR OTHER VALVE | [6 empty] | 2010 | 2010 | CARBON STEEL |  | OTHER | [8 empty] | VENTING THROUGH A VENT VALVE | CLASS 1 LOCATION | NO |  | 510 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 34034 | 34034 | 0 | 0 | 1500 | 1500 | 0 | 0 |  | 8.98 | 35534 | 22993.0216208220123604651162790697674419 | 35534 | 0 | 0 | 0 | 0 | NO |  |  |  | 686 | 661000 | 809 | 192.619(A)(2) |  | 2010-06-10 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM IDENTIFIED THE VALVE BEING OPEN, WHICH LEAD TO THE CONFIRMED DISCOVERY OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | YES | [34 empty] | YES | UNIT VALVE WAS FROZEN, CAUSING IT TO NOT OPERATE PROPERLY WHEN GIVING COMMANDS. | [161 empty] | TAYLER K JENSEN |  | tayler.jensen@williams.com | 2813828869 |  |  |  |  | JOHN BELL |  | 3373179145 | john.bell@williams.com | ON DECEMBER 19, 2022 WILLIAMS GAS CONTROL SENT A START COMMAND TO UNIT 1 AT VERNAL COMPRESSOR STATION, LOCATED ON THE NORTHWEST PIPELINE SYSTEM. SHORTLY AFTER THE START COMMAND WAS SENT, GAS CONTROL RECEIVED A VOLTAGE IMBALANCE ALARM. GAS CONTROL FURTHER INVESTIGATED THIS ALARM VIA THE HMI SYSTEM AND NOTICED THAT THE UNIT 1 LOADING VALVE WAS ISSUING A COMMAND DISAGREE ALARM. IT WAS ALSO NOTED AT THIS TIME THAT THE HMI SCHEMATIC SHOWED THE LOADING VALVE WAS OPEN (IT SHOULD'VE BEEN CLOSED). GAS CONTROL CALLED THE LOCAL ON-CALL TECHNICIANS TO HEAD TO THE SITE TO INVESTIGATE. WHEN OPERATIONS PERSONNEL ARRIVED ON SITE THEY WERE ABLE TO CONFIRM THAT THE LOADING VALVE WAS IN FACT OPEN AND VENTING GAS TO THE ATMOSPHERE. IT WAS DISCOVERED THAT THE VALVE WAS FROZEN IN THE OPEN POSITION. THE TECHNICIANS QUICKLY ACTED TO CLOSE THE LOADING VALVE BY WARMING THE VALVE AND MANUALLY MOVING IT TO THE CLOSED POSITION, CAUSING THE VENTING TO STOP. ONCE THE VALVES WERE COMPLETELY THAWED, OPERATIONS AND GAS CONTROL MANUALLY AND REMOTELY OPENED AND CLOSED THE VALVE TO ENSURE THAT PROPER FUNCTION HAD BEEN RESTORED. OVER THE NEXT SEVERAL HOURS, OPERATIONS WORKED WITH TECH SERVICES TO DEVELOP AN ACCURATE ESTIMATE FOR THE QUANTITY OF GAS THAT WAS RELEASED. A FINAL NUMBER OF 3,790 MSCF WAS CALCULATED. SINCE THE INITIAL OCCURRENCE, THE VALVE HAS OPERATED CORRECTLY EACH TIME AN OPEN / CLOSE COMMAND HAS BEEN ISSUED. ADDITIONAL DETAIL ADDED 02/13/23: THE LOADING VALVE IS A 2' VALVE THAT IS USED TO PURGE AND BRING THE COMPRESSOR UP TO PIPELINE PRESSURE BEFORE THE MAIN UNIT VALVES CAN BE OPENED. THIS IS A FAIL CLOSED VALVE THAT USES PNEUMATIC POWER TO OPEN. ICING WAS PRESENT IN THE OPERATOR AND PNEUMATIC VENT, HOLDING THE VALVE IN THE OPEN POSITION. AFTER HEAT WAS APPLIED TO REMOVE THE ICE, THE VALVE WAS ABLE TO BE MOVED AND CYCLED NORMALLY.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230002 | 37562 | 2023-01-10 10:48 | ORIGINAL FINAL | 19610 | TRANSWESTERN PIPELINE COMPANY LLC | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-12-18 19:30 | 2022 | MOUNTAIN | NO | 35.4262 | -108.2361 | 1355332 | 2022-12-18 22:31 | 1355407 | NATURAL GAS |  | 13414 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-12-18 19:30 | 2022-12-18 23:45 |  | NO |  |  | NO | [11 empty] | 0 | 2022-12-18 19:30 | 2022-12-18 20:30 | ONSHORE | NM | 87020 | GRANTS | MCKINLEY | SURVEY STATION NO. | 0+00 | STATION 5 THOREAU | 30" TW MAINLINE | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1960 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | THE ESD BLOWDOWN VALVE CAME OPEN AFTER THE POWER GAS PILOT LINE FROZE | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 81155 | 81155 | 1164 | 1164 | 100 | 100 | 0 | 0 |  | 6.05 | 82419 | 53807.171579057422172119601328903654485 | 82419 | 0 | 0 | 0 | 0 | NO |  |  |  | 900 | 13414 | 1008 | 192.619(A)(1) |  | 1960-06-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | YES | NO | PHMSA | NO | [19 empty] | TRANSMISSION SYSTEM | NO |  |  |  |  | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [52 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | YES |  |  |  | YES | COLD FRONT CAUSED TEMPERATURES TO BE IN THE 20'S AND THE ESD BLOWDOWN VALVE OPENED AFTER THE POWER GAS PILOT LINE FROZE | [287 empty] | YES | [13 empty] | CHRISTOPHER PALAFOX | SPECIALIST REGULATORY COMPLIANCE | christopher.palafox@energytransfer.com | 713-989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON DECEMBER 18, 2022, AT APPROXIMATELY 19:30 MOUNTAIN TIME, THERE WAS A RELEASE OF NATURAL GAS AT THE THOREAU STATION N0. 5 ON THE TRANSWESTERN SYSTEM 30 MILES NORTHWEST OF GRANTS, NEW MEXICO IN MCKINLEY COUNTY. OPERATIONS RESPONDED TO CALL OUT FROM GAS CONTROL. AFTER ARRIVING AT THE STATION, IT WAS DISCOVERED THAT THE ESD BLOWDOWN VALVE OPENED AFTER THE POWER GAS PILOT LINE FROZE CAUSING THE STATION TO SHUT DOWN AND RELEASED NATURAL GAS. THE ESD WAS SHUT MANUALLY SECURING THE RELEASE. THE FROZEN LINE WAS REPLACED, AND THE PILOT LINE WAS PUT BACK IN SERVICE. AT 22:00 MOUNTAIN TIME, IT WAS DETERMINED THE UNINTENTIONAL GAS RELEASE AMOUNT WAS GOING TO BE OVER THE 3 MMCF REPORTABLE QUANTITY CRITERIA. THE STATION WAS RESET AND AT APPROXIMATELY 23:45 MOUNTAIN TIME, THE STATION WAS BACK ONLINE. THIS WAS AN ISOLATED INCIDENT. TO PREVENT THIS FROM OCCURRING IN THE FUTURE, OPERATIONS WILL INSTALL WATER KNOCK OUT EQUIPMENT AND LARGER TUBING.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230003 | 37568 | 2023-01-11 14:46 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2022-12-13 17:20 | 2022 | EASTERN | NO | 35.2178 | -80.2637 | 1354947 | 2022-12-13 18:39 | 1355034 | NATURAL GAS |  | 2923 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-12-13 19:57 | 2022-12-14 19:53 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2022-12-13 17:33 | NO | [5 empty] | VALVE CLOSURE |  | 2022-12-13 19:57 | VALVE CLOSURE |  | 2022-12-13 19:50 | 0 | 2022-12-13 17:52 | 2022-12-13 18:57 | ONSHORE | NC | 28129 | OAKBORO | STANLY | NOT APPLICABLE |  | LINE 10 | LINE 10 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6 | NO | 0.188 | 35000 | 6 INCH .188 GRADE B STEEL | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1959 | UNKNOWN | CARBON STEEL |  | MECHANICAL PUNCTURE | 9 | 6 | [7 empty] | CLASS 1 LOCATION | NO |  | 121 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 20461 | 20461 | 656018 | 656018 | 22568 | 22568 | 0 | 0 |  | 7 | 699047 | 312791.560810022037588511627906976744186 | 699047 | 0 | 0 | 2522 | 707 | NO |  |  |  | 505 | 3000 | 625 | 192.619(A)(2) |  | 1960-07-21 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 11080 | NO | YES | YES | YES | YES |  |  |  | YES | YES | YES | YES | YES | YES | LINE CURRENTLY RETROFITTED FOR STATIONS | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [64 empty] | EXCAVATION DAMAGE BY THIRD PARTY | NO |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | A223343443 | N/A | FACILITY OWNER | YES | YES | YES | 40 | EXCAVATION PRACTICES NOT SUFFICIENT |  |  | EXCAVATION PRACTICES NOT SUFFICIENT (OTHER) | [263 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A CONTRACTOR INSTALLING A LARGE DIAMETER WATER LINE STRUCK A 6" HIGH PRESSURE TRANSMISSION GAS LINE WITH A BACKHOE. THE DAMAGE RESULTED IN 3,229 CUSTOMER OUTAGES. THE USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20230004 | 37571 | 2023-01-12 16:17 | ORIGINAL | 31130 | DCP MIDSTREAM | 6900 E. LAYTON AVE. SUITE 900 | DENVER | CO | 80237-3658 | 2022-06-07 17:45 | 2022 | MOUNTAIN | NO | 32.5244 | -103.2664 | 1355166 | 2022-12-16 10:41 | 1355343 | NATURAL GAS |  | 488 | 0 | 23 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-06-07 20:00 |  | YES |  |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-06-07 19:30 | VALVE CLOSURE |  | 2022-06-07 19:30 | 0 | 2022-06-07 17:45 | 2022-06-07 19:30 | ONSHORE | NM | 88240 | Not Within a Municipality | LEA | NOT APPLICABLE |  | V | OIL CENTER DISCHARGE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.218 | 42000 | API 5L | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1973 | UNKNOWN | CARBON STEEL |  | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 120 | 16 |  | CLASS 1 LOCATION | NO |  | 294 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 3758 | 3758 | 12943 | 12943 | 129600 | 129600 | 0 | 0 |  | 7.7 | 146301 | 65350.3096455071195509003322259136212625 | 146301 | 0 | 0 | 0 | 0 | NO |  |  |  | 530 | 7808 | 710 | 192.619(A)(2) |  | 2021-03-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 10296 | NO |  |  |  | YES |  |  |  | YES |  |  |  |  | YES | LACK OF ADEQUATE LAUNCHER/RECEIVER | TYPE C GATHERING | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  | YES | [6 empty] | YES |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | YES | 2021 | 984 | NO | [13 empty] | NO | [63 empty] | GABRIEL MCCOWN | SR. COMPLIANCE SPECIALIST | gmccown@dcpmidstream.com | 405-215-7767 |  |  |  |  | MIKE PAVLAK | MANAGER - PIPELINE COMPLIANCE | 970-397-0732 | mpavlak@dcpmidstream.com | DCP'S TYPE C GAS GATHERING 16-IN 'V' OIL CENTER DISCHARGE PIPELINE RUPTURED AND DCP WAS NOTIFIED OF THE RUPTURE BY THE COUNTY SHERIFF. DCP PERSONNEL RESPONDED PROMPTLY AND ISOLATED THE LINE. THE FAILED PIPE SEGMENT WAS SENT FOR METALLURGICAL ANALYSIS AND RESULTS INDICATED LOCALIZED INTERNAL CORROSION PITTING DUE TO THE PRESENCE OF HYDROGEN SULFIDE IN THE PRODUCT STREAM. THE PIPELINE WAS REPAIRED AND REMAINS OUT OF SERVICE. A RETURN TO SERVICE DATE HAS NOT BEEN SET AT THIS TIME DUE TO OVERALL SYSTEM OPERATIONS. DCP'S INITIAL COST ESTIMATE WAS BELOW THE REPORTING THRESHOLD, BUT ACTUAL REMEDIATION COSTS EXCEEDED THE INITIAL ESTIMATE, REQUIRING DCP TO REPORT ONCE FINAL COSTS WERE AVAILABLE. REMEDIATION COST WERE DETERMINED TO MEET INCIDENT REPORTING THRESHOLD ON DECEMBER 16, 2022, AND THE NRC WAS NOTIFIED AT THAT TIME. A SUPPLEMENTAL REPORT WILL BE FILED WHEN THE LINE IS RETURNED TO SERVICE.
2023-02-28 09:42 | NO | NO | GG (Gas Gathering) | 20230005 | 37576 | 2023-01-13 10:12 | ORIGINAL FINAL | 31130 | DCP MIDSTREAM | 6900 E. LAYTON AVE. SUITE 900 | DENVER | CO | 80237-3658 | 2022-11-14 11:00 | 2022 | CENTRAL | NO | 32.7004 | -102.7157 | 1355087 | 2022-12-15 14:54 | 1355180 | NATURAL GAS |  | 6423 | 680 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | GRADE 2 LEAK, MONITORED UNTIL REPAIR. SEE NARRATIVE. |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-12-01 13:00 | VALVE CLOSURE |  | 2022-12-01 13:00 | 0 | 2022-11-14 11:00 | 2022-11-14 11:00 | ONSHORE | TX | 79360 | Not Within a Municipality | GAINES | NOT APPLICABLE |  | FULLERTON | H | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 84 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 20 | NO | 0.22 | 52000 | API 5L | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | COAL TAR |  | NO | [26 empty] | 1970 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | NO |  | 204 |  | NO | NO |  |  | NO |  |  | 720 | 720 | 1360 | 1360 | 12846 | 12846 | 25000 | 25000 | 0 | 0 | 0 | 0 |  | 2 | 39926 | 20375.5126756365194045182724252491694352 | 39926 | 0 | 0 | 0 | 0 | NO |  |  |  | 100 | 357 | 219 | 192.619(A)(3) |  | 2022-04-07 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 47131 | YES | [7 empty] | NO | [6 empty] | TYPE C GATHERING | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  | YES |  |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | YES | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | RUSSELL NICHOLS | SR. PIPELINE COMPLIANCE SPECIALIST | rnichols@dcpmidstream.com | 4325571637 |  | RUSSELL NICHOLS | rnichols@dcpmidstream.com | 4325571637 | MIKE PAVLAK | MANAGER PIPELINE COMPLIANCE | 9703970732 | mpavlak@dcpmidstream.com | THIRD PARTY CONTRACTOR NOTIFIED DCP MIDSTREAM LOCAL REPRESENTATIVE OF POTENTIAL LEAK ON THE H LINE ON 11/14/2022. LEAK WAS CONFIRMED ON 11/14/2022 TO BE ON THE H LINE AND OPERATIONS DETERMINED LEAK TO BE A GRADE 2 LEAK AND FOLLOWED ITS PROCEDURES IN ACCORDANCE WITH STATE REGULATION FOR MONITORING UNTIL PLAN WAS ESTABLISHED TO SHUT IN PIPELINE AND REPAIR LEAK. GRADE 2 IS NON-HAZARDOUS AT THE TIME OF DETECTION, BUT REQUIRES THE OPERATOR TO SCHEDULE REPAIR BASED ON PROBABLE FUTURE HAZARD. IT CAN BE SCHEDULED FOR REPAIR ON A NORMAL ROUTINE BASIS WITH PERIODIC RE-INSPECTION AS NECESSARY. LINE WAS SUBSEQUENTLY SHUT IN ON 12/01/2022. NDE EXAMINATION OF FAILURE SITE CONDUCTED AND RESULTS INDICATED LOCALIZED CORROSION INTERNAL PITTING. FULL ENCIRCLEMENT B-SLEEVE REPAIR WAS COMPLETED ON 12/03/2022. LINE RETURNED TO SERVICE ON 12/03/2022. ON 12/14/2022 DCP ENVIRONMENTAL REPRESENTATIVE PERFORMED AN UPDATED GAS LOSS CALCULATION FROM CONFIRMED DAMAGE SIZE AND CONCLUDED THAT THE LOSS OF 6423 MCF WOULD MAKE THIS A REPORTABLE INCIDENT. CALCULATION RESULTS WERE CONFIRMED ON 12/15/2022 AND NRC/RRC NOTIFICATIONS WERE MADE.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20230006 | 37591 | 2023-01-18 17:52 | ORIGINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2022-12-20 06:52 | 2022 | PACIFIC | YES | 40.6844 | -124.1987 | 1355507 | 2022-12-20 18:52 | 1355656 | NATURAL GAS |  | 20 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | L126-B WAS NOT SHUT DOWN. |  |  |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-01-21 01:00 | VALVE CLOSURE |  | 2022-01-21 01:00 | 0 | 2022-12-20 02:34 | 2022-12-20 06:35 | ONSHORE | CA | 95501 | LOLETA | HUMBOLDT | MILEPOST | 4 | L-126B | MILE POINT 4.0 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 0.75 | NO | 0.25 | UNKNOWN | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | [26 empty] | 1949 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  |  | NOT FLAMMABLE | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 60 | 60 | 43435 | 43435 | 0 | 0 | 0 | 0 |  | 3 | 43495 | 19201.2272408009660463289036544850498339 | 43495 | 0 | 0 | 0 | 0 | NO |  |  |  | 150 | 0 | 170 | 192.619(A)(3) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | MANUAL | MANUAL | 5 | NO | [5 empty] | YES | 3/4 INCH LINE | YES |  |  |  |  | YES | 3/4 INCH LINE | TRANSMISSION SYSTEM | NO |  |  |  |  | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [52 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [306 empty] | ROSA DUENAS | GAS PROGRAM MANAGER | r1dj@pge.com | 510/298-7063 |  |  |  |  | SUSIE RICHMOND | GAS OPS COMPLIANCE AND RISK MANAGER | 925-928-5776 | gsr8@pge.com | ON DECEMBER 20, 2022, A MAGNITUDE 6.4 EARTHQUAKE STRUCK FERNDALE, IN HUMBOLDT COUNTY, AT 02:34. PG&E ACTIVATED THE GAS EMERGENCY CENTER (GEC) AND EMERGENCY OPERATIONS CENTER (EOC) AND SET UP A BASE CAMP IN HUMBOLDT COUNTY TO SUPPORT THIS EVENT. OVER 24,000 SERVICES WERE SURVEYED WITH A COMBO OF PICARRO AND FOOT SURVEY. GAS SERVICES REPRESENTATIVES WERE DISPATCHED THROUGHOUT THE TERRITORY WITH CONSTRUCTION CREWS ARRIVING SHORTLY AFTER TO SUPPORT INVESTIGATIONS AND LEAK REPAIRS. OF THE VARIOUS LEAKS IDENTIFIED THROUGHOUT THE TERRITORY, THE HIGHEST REPAIR COSTS FOR A SINGLE RELEASE OF GAS OCCURRED ON A FARMTAP OFF L-126B IN LOLETA, CA. PG&E ALSO RECEIVED MULTIPLE NO GAS CALLS AND ODOR COMPLAINTS THROUGHOUT THE TERRITORY. THE NO GAS CALLS WERE DUE TO TRIPPED EARTHQUAKE VALVES WHICH INCLUDED A MASTER METERED MOBILE HOME PARK. GPOM ASSESSED BELOW GROUND STATIONS FOR DAMAGE AND THE PIPELINE PATROL GROUP PATROLLED THE AREA; NO ISSUES WERE DISCOVERED. PG&E EVALUATED LANDSLIDE POTENTIALS THAT COULD HAVE AFFECT TRANSMISSION LINES IN THE AREA. THERE ARE NO REPORTS OF INJURIES OR FATALITIES DUE TO NATURAL GAS FACILITIES. THIS INCIDENT WAS REPORTED BASED ON OPERATOR JUDGEMENT DUE TO ITS SIGNIFICANCE AND PUBLIC ATTENTION. THIS EVENT WAS REPORTED TO DOT (NRC # 1355507/1355656).
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230007 | 37595 | 2023-01-19 14:59 | ORIGINAL FINAL | 19235 | TEXAS EASTERN TRANSMISSION, LP (SPECTRA ENERGY PARTNERS, LP) | 915 NORTH ELDRIDGE PARKWAY | HOUSTON | TX | 77079 | 2022-12-23 22:30 | 2022 | CENTRAL | NO | 32.4089 | -90.2632 | 1355840 | 2022-12-24 12:04 | 1355906 | NATURAL GAS |  | 15080 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | COMPRESSOR STATION ESD BUT PIPELINE CONTINUED OPERATION |  |  |  | YES | OPERATOR | 2022-12-23 22:35 | NO | [11 empty] | 0 | 2022-12-23 22:30 | 2022-12-23 22:30 | ONSHORE | MS | 39213 | Not Within a Municipality | HINDS | MILEPOST | 317.56 | CLINTON COMPRESSOR STATION | CLIN-KOSC | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | ESD SYSTEM, BUT EXCLUDING PRODUCT DRAIN LINES AND TUBING | [38 empty] | 1956 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | COMPRESSOR STATION EMERGENCY SHUTDOWN (ESD) | CLASS 1 LOCATION | NO |  | 182 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 110235 | 110235 | 0 | 0 | 2000 | 2000 | 0 | 0 |  | 7.31 | 112235 | 73212.597487784831541528239202657807309 | 112235 | 0 | 0 | 0 | 0 | NO |  |  |  | 755 | 1200000 | 936 | 192.619(A)(1) |  | 2016-01-01 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROL ROOM INVESTIGATION WAS NECESSARY DUE TO KNOWN/IDENTIFIED INITIAL CAUSE AND THE NATURE OF THE EVENT. FIELD PERSONNEL WERE ON-SITE. THE SCADA SYSTEM PERFORMED AS EXPECTED AND GENERATED ALARMS TO WHICH THE CONTROLLER PROPERLY RESPONDED. NO EVIDENCE THAT CONTROL ROOM CONTRIBUTING FACTORS EXISTS IN THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES |  |  | YES | [5 empty] | YES | [24 empty] | YES | FAILED GAS DETECTOR INITIATED AN ESD | [161 empty] | MICHAEL MCGRATH |  | mcgratm@comcast.net | 6128056542 |  |  |  |  | NATHAN ATANU |  | 17136275008 | nathan.atanu@enbridge.com | ON DECEMBER 23, 2022, AT APPROXIMATELY 10:30 PM CST THE CLINTON COMPRESSOR STATION IN HINDS COUNTY MISSISSIPPI ESD'ED BLOWING DOWN THE STATION. THE ESD WAS THE RESULT OF LOW SIGNAL (AMPERAGE) AT THE FIRE EYES AND GAS DETECTORS DUE TO ABNORMALLY COLD WEATHER IN THE AREA. THE LOW SIGNAL AT A GAS DETECTOR EVENTUALLY INITIATED A STATION ESD. IN ADDITION, A BLOCKED (FROZEN) TUBING LINE ON AN ACTUATOR FOR A 30-INCH VALVE ON THE STATION DISCHARGE FAILED TO FULLY CLOSE THE VALVE FOR APPROXIMATELY 23 MINUTES ALLOWING MORE VOLUME TO VENT THAN A TYPICAL ESD. THERE ARE SEVERAL REMEDIATIONS BEING CONSIDERED TO PREVENT UNCOMMON COLD WEATHER COMPLICATIONS GOING FORWARD.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230008 | 37599 | 2023-01-20 12:56 | ORIGINAL FINAL | 13750 | NORTHERN NATURAL GAS CO | 1111 SOUTH 103RD STREET | OMAHA | NE | 68124 | 2022-12-22 21:06 | 2022 | CENTRAL | YES | 42.048 | -94.0443 | 1355698 | 2022-12-22 23:14 | 1355859 | NATURAL GAS |  | 5500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | ABLE TO MAINTAIN SERVICE WHILE REPAIRING EQUIPMENT |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-12-22 21:06 | 2022-12-22 21:30 | ONSHORE | IA | 50212 | Not Within a Municipality | BOONE | NOT APPLICABLE |  | DES MOINES | IAB65001 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | 2022 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | THE OVERPRESSURE WAS DUE TO CONSTRUCTION DEBRIS IN THE WHISPER TRIM CAGE OF THE VALVE 49 REGULATOR. THE DEBRIS CAUSED THE REGULATOR TO NOT CLOSE COMPLETELY. | CLASS 1 LOCATION | NO |  | 246 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 92785 | 92785 | 3500 | 3500 | 1500 | 1500 | 0 | 0 |  | 16.87 | 97785 | 63086.3317593291884883720930232558139535 | 97785 | 0 | 0 | 0 | 0 | NO |  |  |  | 456 | 4975 | 380 | OTHER | 192.611(A)(2) | 2018-05-08 | NO | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | DEBRIS | [161 empty] | JOHN GORMLEY |  | john.gormley@nngco.com | 4023987494 |  | LOGAN CHASE HAMMEL | logan.hammel@nngco.com | 4025302745 | TOM CORRELL | VP PIPELINE SAFETY AND RIST | 14023987715 | thomas.correll@nngco.com | ON DECEMBER 22, 2022, AT 2106 FIELD OPERATIONS TECHNICIAN WAS NOTIFIED OF A VENTING RELIEF VALVE IN THE OGDEN COMPRESSOR STATION. IT WAS DETERMINED TO BE THE RELIEF VALVE DOWNSTREAM OF VALVE 113 ON THE DES MOINES A-LINE (IAB65001). ACCORDING TO DATA TRENDS THE RELIEF VALVE VENTED 20 TIMES FOR AN AVERAGE OF 40 SECONDS EACH FROM 2100 HOURS TO 2116 HOURS. HIGHEST PRESSURE RECORDED WAS 456 PSIG AT 2109 HOURS. AT 2116 HOURS THE PRESSURE RETURNED TO NORMAL OPERATING PRESSURE OF 355PSIG. THE INVESTIGATION REVEALED THE CAUSE OF THE OVERPRESSURE WAS DUE TO CONSTRUCTION DEBRIS IN THE WHISPER TRIM CAGE OF THE VALVE 49 REGULATOR. THE DEBRIS CAUSED THE REGULATOR TO NOT CLOSE COMPLETELY. THE TEAM HAD MIDWEST VALVE TO INSPECT THE VALVE AND FOUND THE DEBRIS IN THE REGULATOR CAGE. THE CAGE WAS CLEANED OF ALL DEBRIS. THE STEM AND SEAT WERE VERIFIED TO HAVE NO DAMAGE. NEW SOFT GOODS AND SEALS WERE INSTALLED IN THE REGULATOR. WORK WAS COMPLETED ON JANUARY 5, 2023. THE CONTRACTOR TESTED THE VALVE FOR PROPER OPERATION AND FOUND NO ISSUES WITH THE VALVE OPENING AND CLOSING.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20230009 | 37613 | 2023-01-23 15:11 | ORIGINAL | 32099 | ENERGY TRANSFER COMPANY | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2022-12-30 01:15 | 2022 | MOUNTAIN | NO | 32.0625 | -103.6931 | 1356334 | 2022-12-30 07:21 | 1356507 | NATURAL GAS |  | 1500 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-12-30 02:27 | 2022-12-30 15:30 |  | YES | OPERATOR | 2022-12-30 02:27 | YES | 2022-12-30 01:15 | ALLOWED TO BURN OUT |  | 1500 | YES | [6 empty] | 0 | 2022-12-30 01:15 | 2022-12-30 02:27 | ONSHORE | NM | 88252 | JAL | LEA | SURVEY STATION NO. | 0+00 | DOMINATOR COMPRESSOR STATION UNIT #6 | DOMINATOR COMPRESSOR STATION UNIT #6 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2021 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | MANUAL ESD OF STATION | CLASS 1 LOCATION | NO |  | 660 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 6720 | 6720 | 2600000 | 2600000 | 4320 | 4320 | 4000 | 4000 | CONTRACTORS TO ISOLATE UNIT | 4.48 | 2615040 | 1155100.1895033529463888372093023255814 | 2615040 | 0 | 0 | 0 | 0 | NO |  |  |  | 1150 | 10000 | 1440 | 192.619(A)(1) |  | 2018-04-11 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TYPE C GATHERING | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A REVIEW OF THE ACCIDENT DETERMINED THAT THERE WERE NO CONTROL ROOM ACTIONS THAT CONTRIBUTED TO THE EVENT | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [216 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [146 empty] | CHRISTOPHER PALAFOX | SPECIALIST REGULATORY COMPLIANCE | christopher.palafox@energytransfer.com | 713 -989-4464 |  |  |  |  | CHRIS KRESTA | MANAGER - REGULATORY COMPLIANCE | 713-989-7077 | chris.kresta@energytransfer.com | ON DECEMBER 30, 2022 AT APPROXIMATELY 01:15 LOCAL TIME, A FIRE OCCURRED AT THE DOMINATOR COMPRESSOR STATION ON UNIT #6, 30 MILES WEST OF JAL, NEW MEXICO IN LEA COUNTY. OPERATIONS RECEIVED A CALL FROM THE 911 DISPATCHER AND THE FIRE DEPARTMENT WAS DISPATCHED TO THE STATION. THE OPERATIONS MECHANIC, WHO IS ALSO A VOLUNTEER FIRE FIGHTER, ARRIVED WITH THE FIRE DEPARTMENT AND ESD THE STATION. A DECISION WAS MADE TO LET THE FIRE BURN ITSELF OUT. AT 06:00 MOUNTAIN TIME, THE STATION WAS SAFE TO ENTER AND OPERATIONS MADE AN INITIAL ASSESSMENT AND IT WAS DETERMINED THE REPAIRS AND DAMAGES WOULD EXCEED THE $123,900.00 REPORTABLE DOLLAR CRITERIA. AT APPROXIMATELY 15:30, UNIT #6 WAS ISOLATED AND THE STATION WAS PUT BACK ONLINE BY USING THE OTHER COMPRESSORS. THE UNINTENTIONAL GAS LOSS WAS CALCULATED AT 1500 MCF. THE CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION. COMPONENTS HAS BEEN SENT TO THE LAB FOR ANALYSIS TO DETERMINE THE CAUSE OF THE FIRE. AND UNIT #6 WILL BE SENT TO THE MANUFACTURER TO BE DISMANTLED AND EXAMINED. A SUPPLEMENTAL REPORT WILL BE SUBMITTED ONCE THE DETERMINATION HAS BEEN MADE.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20230010 | 37689 | 2023-01-24 13:32 | SUPPLEMENTAL | 19570 | TRANSCONTINENTAL GAS PIPE LINE COMPANY | ONE WILLIAMS CENTER MD 43-4 | TULSA | OK | 74172 | 2023-01-06 08:50 | 2023 | CENTRAL | NO | 28.3194 | -92.0114 | 1356969 | 2023-01-06 09:51 | 1357074 | NATURAL GAS |  | 13 | 457 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2023-01-06 10:43 | 2023-01-10 11:10 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2023-01-06 17:00 | VALVE CLOSURE |  | 2023-01-06 10:43 | 0 | 2023-01-06 08:50 | 2023-01-06 10:43 | OFFSHORE | [6 empty] | SMI130A - UWTI SMI130 | SMO1303-G-G-T (BSEE #4757) | [20 empty] | 215 | ON THE OUTER CONTINENTAL SHELF (OCS) |  |  |  |  | OCS-GULF OF MEXICO | SOUTH MARSH ISLAND | 130 | BELOW WATER, PIPE BURIED OR JETTED BELOW SEABED | INTERSTATE | OFFSHORE PIPELINE, INCLUDING RISER AND RISER BEND | PIPE | PIPE BODY | 12 | NO | 0.625 | 35000 | API5L | SEAMLESS |  | KAISER STEEL CORP | OTHER | CEMENT | YES | [26 empty] | 1978 | 1978 | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 128 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 1673 | 1640.056120774532608 | 48 | 48 | 350000 | 343107.9750574336 | 0 | 0 | 0 | 0 |  | 3.66 | 351721 | 152121.1227652163789660631229235880398671 | 344796.031178208132608 | 0 | 0 | 0 | 0 | NO |  |  |  | 668 | 147 | 1440 | 192.619(A)(1) |  | 2001-12-12 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | AUTOMATIC | 49896 | NO | YES | [6 empty] | YES |  |  | YES |  |  |  | OFFSHORE GATHERING | YES | YES | YES | NO | NO | OTHER | 3RD PARTY VESSEL -TALOS |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS REPORTED BY THIRD PARTY VESSEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | EDGAR RODRIGUEZ | REGULATORY COMPLIANCE SPECIALIST SR. | edgar.x.rodriguez@williams.com | 713-303-9956 |  | TRACI BRENTANO | traci.brentano@williams.com | 281-520-0007 | JOHN BELL | MANAGER PIPELINE SAFETY | 337-317-9145 | john.bell@williams.com | 1-6-23 ' 08:50 GAS CONTROL NOTIFIED OPERATIONS THAT A THIRD PARTY VESSEL REPORTED BUBBLES LOCATED IN THE SMI130 BLOCK ' 08:57 THIRD PARTY COMPANY WAS CONTACTED TO VERIFY WHAT WAS REPORTED TO PIPELINE CONTROL AND TO GET COORDINATES OF LEAK LOCATION. ' 09:05 OPERATIONS PLOTTED THE COORDINATES WHICH PUT THE BUBBLES WITHIN 500 TO 600' FOOT OF THE WILLIAMS 12' PIPELINE FROM SMI130A SMI130 UWTI ' 09:10 OPERATIONS CONTACTED WILLIAMS HELICOPTER AND TECHNICIANS TO FLY OVER TO VERIFY THERE ARE BUBBLES AND CONFIRM THE COORDINATES OF THE REPORTED LEAK ' 09:30 CONTACTED WILLIAMS SOC TO REPORT THE POSSIBLE LEAK ' 09:55 WILLIAMS REP CONTACTED WITH WIT O'BRIEN'S ' 10:19 WIT O'BRIENS MADE THE NRC, BSEE AND PHMSA NOTIFICATIONS ' 10:37 WIT O'BRIENS CONTACTED WILLIAMS REP TO VERIFY INFO FOR THE NRC REPORT ' 10:43 WILLIAMS TECHNICIAN CONFIRMED BUBBLES WERE PRESENT AND GAVE UPDATED COORDINATES AND THE PIPELINE WAS BEING ISOLATED AND LOTO ' 1045 PROCURED A 12' CLAMP FROM VENDOR ' 12:10 BLOWDOWN AT SMI106 BEGAN WITH 668PSI ' 15:30 BLOWDOWN WAS STOPPED AT 460PSI TO FLY OVER BUBBLES TO VERIFY IF LEAK STILL REMAINS ' 15:40 NO BUBBLES WERE PRESENT ACCORDING TO WILLIAMS TECHNICIAN ON FLY OVER ' 17:53 DIVE VESSEL WAS PROCURED 1-7-23 ' 22:00 DIVE VESSEL MOVED OUT TO LOCATION 1-8-23 ' 16:46 ETA OF DIVE VESSEL ' 16:46 DROPPED MESOTECH TO PINPOINT LEAK ' 22:30 ANCHOR SET COMPLETE 1-9-23 ' 02:00 DIVER JETTING TO FIND PIPELINE ' 09:00 VERIFIED IT IS 12' WILLIAMS PIPELINE ' 09:46 REMOVING CONCRETE COATING IN ORDER TO INSTALL 12' CLAMP ' 21:57 12' CLAMP WAS INSTALLED AND TORQUED 1-10-23 ' 09:17 WILLIAMS TECHNICIAN STARTED PRESSURING UP PIPELINE ' 09:18 DIVER ON BOTTOM CHECKING FOR LEAKS ON CLAMP ' 11:10 PIPELINE WAS PRESSURED BACK UP AND DIVERS REPORTED NO LEAKS ' 16:32 SYNTHO-GLASS WAS APPLIED TO AFFECTED AREA, 3N1 BAGS WERE INSTALL TO COVER LOCATION AND ANCHORS WERE RETRIEVED
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20230011 | 37650 | 2023-01-31 07:12 | ORIGINAL FINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2023-01-02 14:52 | 2023 | EASTERN | NO | 27.9419 | -82.7336 | 1356612 | 2023-01-02 15:51 | 1356779, 1356847 | NATURAL GAS |  | 3450 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2023-01-02 13:00 | 2023-01-02 14:00 |  | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2023-01-02 11:15 | NO | [11 empty] | 0 | 2023-01-02 13:00 | 2023-01-02 12:55 | ONSHORE | FL | 34624 | CLEARWATER | PINELLAS | SURVEY STATION NO. | 39858 | FLORIDA GAS TRANSMISSION | FLBXT 4" CLEARWATER SOUTH LATERAL REGULATOR STA. | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE REGULATOR/METERING STATION EQUIPMENT AND PIPING | REGULATOR/CONTROL VALVE | [38 empty] | UNKNOWN | UNKNOWN | MATERIAL OTHER THAN CARBON STEEL OR PLASTIC | BUNA-N (RUBBER) | OTHER | [8 empty] | DAMAGED REGULATOR DIAPHRAGM CAUSED RELIEF VALVE ACTIVATION | CLASS 3 LOCATION | NO |  | 51 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 13455 | 13455 | 1500 | 1470.462750246144 | 0 | 0 | 0 | 0 |  | 3.9 | 14955 | 9477.158691572888098006644518272425249169 | 14925.462750246144 | 0 | 0 | 0 | 0 | NO |  |  |  | 116 | 2300 | 275 | 192.619(A)(1) |  | 1962-12-31 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | OTHER | THIRD PARTY DELIVERY CUSTOMER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INVESTIGATION DID NOT IDENTIFY CONTROLLER ACTION AS CONTRIBUTING FACTOR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [25 empty] | YES | EXCESSIVE WEAR OF SOFT COMPONENTS | [161 empty] | MARK BUTEAU | LEAD SPECIALIST - DOT COMPLIANCE | mark.buteau@energytransfer.com | 337-451-2944 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON JANUARY 2, 2023, AT APPROXIMATELY 1206 HOURS, AN FGT TECHNICIAN WAS NOTIFIED BY A DOWNSTREAM CUSTOMER THAT A RELIEF VALVE AT THE CLEARWATER SOUTH REGULATOR STATION WAS CURRENTLY ACTIVATED. THE CLEARWATER STATION IS SHARED WITH ANOTHER OPERATOR (CLEARWATER GAS COMPANY). THE FGT TECHNICIAN PROMPTLY RESPONDED TO THE AREA AND ISOLATED THE SOURCE AT APPROXIMATELY 1300 HRS. LOCAL FIRE DEPARTMENT AND POLICE RESPONDED TO A 3RD PARTY NOTIFICATION, AND THEY BLOCKED TRAFFIC IN BOTH DIRECTIONS UNTIL THE COMPANY TECHNICIAN ISOLATED THE REGULATOR RUN. ACCORDING TO SCADA, THE RELIEF VALVE BEGAN VENTING AT APPROXIMATELY 1030 HRS THAT DAY. THE PRESSURE EXCEEDED THE HI ALARM LIMIT THAT WOULD HAVE INITIATED CLOSER MONITORING BY GAS CONTROL HOWEVER THE PRESSURE DID NOT EXCEED THE HIHI CRITICAL ALARM LIMIT THAT WOULD HAVE GENERATED A CALL OUT AND FIELD INVESTIGATION. THE VOLUME RELEASED WAS CALCULATED TO BE APPROXIMATELY 3.45 MMSCF NATURAL GAS. THE DETERMINATION TIME FOR THIS ESTIMATE WAS APPROXIMATELY 1452 HRS. NRC NOTIFICATION OCCURRED AT APPROXIMATELY 1551 HRS. THE CLEARWATER SOUTH REGULATOR STATION DOES CONTAIN COVERED SEGMENTS IN THE COMPANY IMP, HOWEVER THE PIPING ASSOCIATED WITH THIS INCIDENT IS NOT A COVERED SEGMENT AS DETERMINED BY METHOD 2 (PIR). UPON INVESTIGATION THE CAUSE OF THE INCIDENT WAS CONFIRMED AS A DAMAGED DIAPHRAGM IN A MOODY PILOT ON THE REGULATOR WHICH ALLOWED HIGHER PRESSURE FLOW THROUGH THE STATION WHICH ACTIVATED THE RELIEF VALVE. THE RELIEF CAPACITY WAS VALIDATED DURING THE RELEASE VOLUME CALCULATION. THE DAMAGED EQUIPMENT WAS IMMEDIATELY REPLACED BY THE TECHNICIAN. TO PREVENT RECURRENCE THE COMPANY IS REVIEWING THE HIHI CRITICAL ALARM SETTING AT THIS LOCATION IN RELATION TO RELIEF VALVE SETTING AND WILL RESET THE HIHI ALARM AT A LEVEL BELOW THE RELIEF VALVE SETTING. THIS WILL RESULT IN A CALL OUT TO THE FIELD TO PERFORM INVESTIGATION BEFORE THE RELIEF ACTIVATES OR SHORTEN THE LENGTH OF TIME A RELIEF IS ACTIVATED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230012 | 37661 | 2023-02-01 14:51 | ORIGINAL | 40149 | MPLX LP | 1515 ARAPAHOE STREET SUITE 1600 | DENVER | CO | 80202 | 2022-10-11 22:19 | 2022 | CENTRAL | NO | 34.6339 | -96.179 | 1349661 | 2022-10-11 23:43 | 1349843 | NATURAL GAS |  | 3399 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | ROUTINE START-UP | YES |  | 2022-10-11 22:30 |  | YES | YES | OPERATOR | 2022-10-11 22:30 | YES | 2022-10-11 22:20 | ALLOWED TO BURN OUT |  | 3399 | YES | [6 empty] | 0 | 2022-10-11 22:05 | 2022-10-11 22:50 | ONSHORE | OK | 74538 | COALGATE | COAL | NOT APPLICABLE |  | ARKOMA CS | ARKOMA CS | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | OTHER | [37 empty] | COMPRESSOR AND PIPING | 2009 | 2008 | CARBON STEEL |  | OTHER | [8 empty] | WE HAVE DETERMINED THAT MULTIPLE FACTORS CAUSED THE EVENT, INCLUDING FAULTY AND MISSING CHECK VALVES AND LOW-PRESSURE BRAIDED HOSES EXPOSED TO HIGH PRESSURE FROM THE VENT SYSTEM. | CLASS 1 LOCATION | NO |  | 630 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 374 | 374 | 27400000 | 27400000 | 0 | 0 | 0 | 0 | THESE COSTS ARE SPECIFIC TO THE COMPRESSOR STATION COSTS | 0.11 | 27400374 | 12088075.99793458414551495016611295681063 | 27400374 | 0 | 0 | 0 | 0 | NO |  |  |  | 950 | 500000 | 1440 | 192.619(A)(2) |  | 2009-06-14 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | WE HAVE DETERMINED THAT MULTIPLE FACTORS CAUSED THE EVENT, INCLUDING FAULTY AND | [6 empty] | YES | [176 empty] | KEITH NORRIS | PIPELINE COMPLIANCE | wknorris@mplx.com | 5053600834 |  | IAN LEYBAS | ileybas@mplx.com | (918) 470-7667 | TONY MINUTILLO | PIPELINE COMPLIANCE MANAGER | 3034893275 | tminutillo@mplx.com | THIS REPORT IS FOR THE FIXED FACILITY EVENT THAT OCCURRED ON OCTOBER 11,2022: AT 9:45 PM ON OCTOBER 11TH, ARKOMA 1 COMPRESSOR STATION WAS IN NORMAL OPERATIONS AT STEADY STATE CONDITIONS WHEN ENGINE/COMPRESSOR UNIT #2203 SHUT DOWN ON HIGH ENGINE COOLANT TEMPERATURE. THE ON-SITE OPERATOR INSPECTED THE UNIT AND INITIATED A BLOW DOWN TO PREPARE IT FOR RE-START. AT APPROXIMATELY 10:12 PM, DURING THE UNIT BLOW DOWN, TWO (2) LEL GAS MONITORS ACTIVATED WITHIN THE ENCLOSED COMPRESSOR BUILDING, ACTIVATING AN ESD WHICH TRIPPED ALL COMPRESSORS (4 TOTAL) AND SHUT ELECTRICAL POWER TO THE SITE AS DESIGNED. THE OPERATOR EVACUATED THE BUILDING. GAS WAS RELEASED AND IGNITED, AND THE BUILDING BECAME ENGULFED IN FLAMES AT APPROXIMATELY 10:16 PM. THERE WERE MULTIPLE LOSS OF CONTAINMENT (LOPC) POINTS AND EQUIPMENT FAILURES. THE EVENT WAS CLASSIFIED AS AN ENCLOSED VAPOR CLOUD DEFLAGRATION FOLLOWED BY A FIRE. THE INITIAL CAUSE OF THE ESD AND THE INITIATING IGNITION SOURCE COULD NOT BE DEFINITIVELY IDENTIFIED. IT IS SUSPECTED THAT LOPC ASSOCIATED WITH UNIT #2202 INITIATED THE ESD. INCIPIENT FIRES FUELED BY THE RESIDUAL ENGINE OIL, COOLANT, AND INSULATION CONTINUED TO BURN UNTIL THE FIRE WAS EXTINGUISHED ON OCTOBER 12, 2022, AT APPROXIMATELY 11:00 AM CST. ROOT CAUSE: WE HAVE DETERMINED THAT MULTIPLE FACTORS CAUSED THE EVENT, INCLUDING FAULTY AND MISSING CHECK VALVES AND LOW-PRESSURE BRAIDED HOSES EXPOSED TO HIGH PRESSURE FROM THE VENT SYSTEM. PATH FORWARD: WE HAVE SINCE COMPLETED ISOLATING INDIVIDUAL VENTILATION LINES FROM THE PRE-LUBE PUMPS AND STARTERS, WHICH WILL SEPARATE HIGH-PRESSURE FROM LOW-PRESSURE COMPONENTS. FOR THREE DAYS, WE ALSO HAD 20 + PEOPLE GO FLANGE TO FLANGE COMPLETE A PROCESS HAZARD ANALYSIS, CONFIRMING ALL THE DESIGNS AND P&IDS ARE CORRECT AND CORRECTED WHERE NEEDED. RE-DESIGNING SKIDS TO REMOVE AS MANY THREADED CONNECTIONS AS POSSIBLE. IMPLEMENTED AND SCHEDULED REPLACEMENTS OF WORN ITEMS SUCH AS BRAIDED HOSES. INSTRUMENT AND COMPRESSOR START GAS HAVE BEEN CONVERTED TO AIR. THE NEW BUILDING WILL BE OPEN WITH NO WALLS FOR IMPROVED VENTILATION. ONCE THE COMPRESSOR STATION IS COMMISSIONED, A SUPPLEMENTAL REPORT TO THIS ONE WILL BE SUBMITTED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230013 | 37703 | 2023-02-02 07:10 | SUPPLEMENTAL FINAL | 2616 | COLUMBIA GAS TRANSMISSION, LLC | 700 LOUISIANA ST. | HOUSTON | TX | 77002 | 2023-01-04 14:54 | 2023 | EASTERN | NO | 39.8983 | -77.3144 | 1356895 | 2023-01-05 14:44 | 1356967 | NATURAL GAS |  | 365.42 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2023-01-15 09:15 | 2023-01-16 10:44 |  | NO |  |  | NO | [5 empty] | OPERATIONAL CONTROL | NO INITIAL ACTION WAS TAKEN TO CONTROL UPSTREAM OF LEAKAGE. |  | OPERATIONAL CONTROL | NO INITIAL ACTION WAS TAKEN TO CONTROL DOWNSTREAM OF LEAKAGE. |  | 0 | 2023-01-04 14:54 | 2023-01-04 16:15 | ONSHORE | PA | 17307 | Not Within a Municipality | ADAMS | SURVEY STATION NO. | 1543+45 | LINE-138 | 138-410/ PIPELINE ROUTE ID 3008770 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  |  | NO | YES |  |  |  |  | YES | CASED | [16 empty] | INTERSTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 | NO | 0.188 | UNKNOWN | UNKNOWN | OTHER | UNKNOWN | UNKNOWN | COAL TAR |  | YES | [26 empty] | 1965 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 114 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 2152 | 2152 | 360000 | 352911.06005907456 | 0 | 0 | 0 | 0 | 0 | 5.89 | 362152 | 157102.8700306492897009966777408637873754 | 355063.06005907456 | 0 | 0 | 0 | 0 | NO |  |  |  | 83 | 78 | 125 | 192.619(A)(1) |  | 2004-11-09 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES |  |  | 18677 | NO | YES | YES | YES |  |  | YES | PLASTIC PIPE IS PARTS OF THE PIPELINE | YES |  | YES | YES |  |  |  | TRANSMISSION SYSTEM | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAKAGE WAS NOT DUE TO ANY INVOLVEMENTS BY GAS CONTROL PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | YES | NO | [8 empty] | YES | [190 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | KAMRAN ROSTAMI ASRABADI |  | kamran_rostami@tcenergy.com | 3043572351 |  |  |  |  | PAUL SHAFFER |  | 3045504866 | paul_shaffer@tcenergy.com | ON JANUARY 4, 2023, COLUMBIA GAS TRANSMISSION, LLC (COLUMBIA) MONITORING CENTER RECEIVED A CALL REGARDING A LEAK AT 330 PLEASANT VALLEY RD, PA. THE COLUMBIA EMPLOYEE ARRIVED ON SITE AT 4:15 PM AND IDENTIFIED A GRADE 2 LEAK ON LINE 138 NEAR PLEASANT VALLEY RD. THE LEAK WAS THEN SCHEDULED FOR REPAIR. ON JANUARY 5, 2023 COLUMBIA EMPLOYEES BEGAN EXCAVATING LINE 138 IN PREPARATION OF REPAIRING THE LEAK AND DISCOVERED THE LEAK WAS COMING FROM WITHIN THE 10" CASING RUNNING UNDER PLEASANT VALLEY RD. AT 2:10 PM THE LEAK WAS RECLASSIFIED AS A GRADE 1 LEAK REQUIRING PROMPT REPAIR. IT WAS DETERMINED THE COST OF THE REPAIR MAY EXCEED $129,300 SO THE EVENT WAS PROMPTLY REPORTED TO THE NATIONAL RESPONSE CENTER. THE LINE WAS MONITORED DAILY UNTIL THE REPAIR WAS MADE. ON JANUARY 15, 2023 AT 9:15 AM LINE 138 WAS ISOLATED AND BLOWN DOWN TO 0 PSIG AND 2 LDC CUSTOMERS WERE PLACED ON TEMPORARY BOTTLED COMPRESSED NATURAL GAS (CNG) SERVICE. THE REPLACEMENT OF 93 FEET OF PLASTIC PIPELINE WAS COMPLETED ON JANUARY 16, 2023 AND THE LINE WAS PLACED BACK INTO SERVICE AT 10:44 AM.
2023-02-28 09:42 | NO | NO | GT (Gas Transmission) | 20230014 | 37750 | 2023-02-02 19:52 | SUPPLEMENTAL FINAL | 19160 | TENNESSEE GAS PIPELINE COMPANY | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2022-12-23 09:43 | 2022 | CENTRAL | NO | 38.5618 | -82.955 | 1355725 | 2022-12-23 10:45 | 1355892 | NATURAL GAS |  | 5985 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | RELIEF VALVE LIFTED FOR 8 MINUTES THEN RESEATED. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2022-12-23 09:42 | 2022-12-23 09:42 | ONSHORE | KY | 41144 | GREENUP | GREENUP | NOT APPLICABLE |  | TGP 200-1 | TGP 200-1 | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2022 | UNKNOWN | CARBON STEEL |  | OTHER | [8 empty] | RELIEF VALVE LIFTED | CLASS 2 LOCATION | NO |  | 501 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 34294 | 34294 | 0 | 0 | 30 | 30 | 0 | 0 |  | 5.73 | 34324 | 22515.1119274330515428903654485049833887 | 34324 | 0 | 0 | 0 | 0 | NO |  |  |  | 744 | 1255000 | 765 | 192.619(C) |  | 1970-07-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DEEMED THE INCIDENT INDEPENDENT FROM THE CONTROLLERS ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [166 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [28 empty] | YES | WRONG SET POINT SETUP FOR RELIEF VALVE | [161 empty] | RONALD BARNES II | ENGINEER - CODES AND STANDARDS | ronald_barnesii@kindermorgan.com | 713-420-2324 |  | DEAN HUNTLEY | dean_huntley@kindermorgan.com | 931-215-3680 | JAIME HERNANDEZ | DIRECTOR - ENGINEERING CODES AND STANDARDS | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON 12/23/2022 AT 9:39 AM EST, STATION 200 EXPERIENCED AN ABNORMAL OPERATION WITH THE STATION DISCHARGE RELIEF VALVE (RV) 200-1A. TENNESSEE GAS PIPELINE (TGP) OPERATOR THAT WAS AT THE STATION HEARD THE AUDIBLE SOUND OF GAS RELEASE AND ASSESSED THE EVENT. THE RELIEF VALVE RE-SEATED AND SEALED AFTER 8 MINUTES. AT 10:30AM EST TENNESSEE GAS PIPELINE (TGP) INITIATED THE ERL CALL AND THE EVENT WAS DEEMED REPORTABLE. THE ROOT CAUSE ANALYSIS/INTERNAL INVESTIGATION WAS COMPLETED 01/31/2023. IN ORDER TO PREVENT REOCCURRENCE, THE RELIEF VALVE MANUFACTURER TECHNICIAN'S RECOMMENDED TO TGP TO HAVE A 5% SEPARATION MARGIN SETPOINT. IN ADDITION, TGP INCREASED THE RELIEF VALVE SET POINTS FOR ALL THREE RELIEF VALVES AT THE STATION PER THE MANUFACTURER'S RECOMMENDATION. THE RELIEF VALVE IN QUESTION WAS DISASSEMBLED, CLEANED, AND RECTIFIED BY A VENDOR'S TECHNICIAN AND NEW VALVE SOFT PARTS AND CONTROLS WERE INSTALLED.
2023-02-28 09:42 | YES | NO | GG (Gas Gathering) | 20230015 | 37690 | 2023-02-09 15:27 | ORIGINAL FINAL | 31130 | DCP MIDSTREAM | 6900 E. LAYTON AVE. SUITE 900 | DENVER | CO | 80237-3658 | 2022-07-28 00:45 | 2022 | MOUNTAIN | YES | 32.2159 | -104.2228 | 1357430 | 2023-01-11 15:29 | 1357569 | NATURAL GAS |  | 283 | 0 | 8 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2022-07-28 01:15 | 2022-08-05 12:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2022-07-28 01:20 | VALVE CLOSURE |  | 2022-07-28 01:30 | 0 | 2022-07-28 00:45 | 2022-07-28 00:45 | ONSHORE | NM | 88268 | Not Within a Municipality | EDDY | NOT APPLICABLE |  | 10200 | COTTON DRAW DISCHARGE | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 72 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 12 | NO | 0.38 | 35000 | API 5L | SEAMLESS |  | UNKNOWN | COAL TAR |  | UNKNOWN | [26 empty] | 1976 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | NO |  | 238 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 3255 | 3255 | 10300 | 10300 | 163870 | 163870 | 0 | 0 |  | 11.5 | 177425 | 78972.8892254031843620930232558139534884 | 177425 | 0 | 0 | 0 | 0 | NO |  |  |  | 600 | 100 | 737 | 192.619(A)(4) |  | 1976-04-23 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 8290 | YES | [7 empty] | YES |  |  | YES |  |  |  | TYPE C GATHERING | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | INTERNAL CORROSION | [29 empty] | GENERAL CORROSION |  |  |  | YES |  |  |  | YES |  |  |  | YES | [5 empty] | YES | NO | NO | YES | [168 empty] | NO | [63 empty] | NO |  |  | NO | [13 empty] | NO | [63 empty] | GABRIEL MCCOWN | SR. COMPLIANCE SPECIALIST | gmccown@dcpmidstream.com | 405-215-7767 |  | GABRIEL MCCOWN | gmccown@dcpmidstream.com | 405-215-7767 | MIKE PAVLAK | MANAGER - PIPELINE COMPLIANCE | 970-397-0732 | mpavlak@dcpmidstream.com | THE MORNING OF JULY 28, 2022 AT APPROXIMATELY 12:45 AM MST DCP PERSONNEL ARRIVED ON SITE FOLLOWING A CALL FROM THE LANDOWNER AND CONFIRMED A LEAK FROM THE 12" 10200 COTTON DRAW DISCHARGE PIPELINE. PERSONNEL INITIATED PIPELINE SHUTDOWN AND ISOLATED THE LEAKING SEGMENT. RELEASE MET REPORTING CRITERIA ON 1-11-23 DUE TO REMEDIATION COST AND NRC WAS NOTIFIED AT THAT TIME. LINE REPAIRED AND CURRENTLY IDLE.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230016 | 37694 | 2023-02-10 14:24 | ORIGINAL | 31451 | KINDER MORGAN TEXAS PIPELINE CO | 1001 LOUISIANA ST, STE 1000 | HOUSTON | TX | 77002 | 2023-01-13 09:53 | 2023 | CENTRAL | NO | 29.6851 | -95.3011 | 1357578 | 2023-01-13 10:07 | 1357705 | NATURAL GAS |  | 291.82 | 2360.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2023-01-13 09:47 | 2023-01-14 09:00 |  | NO |  |  | NO | [5 empty] | VALVE CLOSURE |  | 2023-01-13 00:10 | VALVE CLOSURE |  | 2023-01-13 00:25 | 0 | 2023-01-13 09:47 | 2023-01-12 18:00 | ONSHORE | TX | 77087 | HOUSTON | HARRIS COUNTY | MILEPOST | 17.6 | PIERCE JUNCTION TO CLINTON DRIVE | LAUNCHER TO WELD CAP | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  | 55 | YES | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 16 | NO | 0.25 | 42000 | API-5LX | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | OTHER | CTE (COAL TAR EPOXY) | UNKNOWN | [26 empty] | 1957 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 321 |  | NO | NO | [5 empty] | 0 | 0 | 8497 | 8329.681325894323712 | 1051 | 1051 | 215000 | 210766.32753528064 | 14000 | 13724.319002297344 | 20000 | 19606.17000328192 | METALLURGICAL TEST REPORT | 3.6 | 258548 | 112050.5127359626443816112956810631229236 | 253477.497866754227712 | 0 | 0 | 0 | 2 | NO |  |  |  | 640 | 94 | 650 | 192.619(A)(1) |  | 1970-01-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | AUTOMATIC | MANUAL | 26816 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | OTHER | THIRD PARTY EMPLOYEE FROM CENTERPOINT ENERGY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ALARMS WERE TRIGGERED, LEAK WAS DUE TO EXTERNAL CORROSION | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | WAITING ON METALLURGICAL REPORT, SUPPLEMENTAL REPORT NEEDED. |  |  | YES |  |  |  | YES | YES | 1957 | YES | YES |  | YES |  |  |  | 2022 |  |  | YES | [190 empty] | YES | YES | YES | [5 empty] | 2022 | FREE SWIMMING | HARD SPOTS |  |  |  | 2015 | FREE SWIMMING | HARD SPOTS |  |  |  | 2022 | FREE SWIMMING | HIGH RESOLUTION | [41 empty] | YES | 2001 | 980 | Yes, but the point of the Accident was not identified as a dig site |  | 2017 | 2017 | 2017 | 2017 |  |  |  | YES | YES | YES |  |  | NO | [63 empty] | VIGNESH RAMAN | PIPELINE ENGINEER | vignesh_raman@kindermorgan.com | 2817705911 |  |  |  |  | JAIME HERNANDEZ | DIRECTOR ENGINEER | 713-369-9443 | jaime_hernandez@kindermorgan.com | ON JANUARY 12TH AT 3:25 PM KMTP RECEIVED A CALL OF A POSSIBLE GAS LEAK FROM CENTERPOINT ENERGY EMPLOYEE. AT THE TIME IT WAS UNKNOWN WHETHER THIS LEAK WAS FROM THE KMTP LINE OR THE CENTERPOINT ENERGY LINE BECAUSE THE KMTP PIERCE JUNCTION TO CLITON DRIVE LINE RUNS IN PARALLEL WITH CENTERPOINT ENERGY'S LINE. JANUARY 13TH AT 9:47AM, IN AN EFFORT TO LOCATE THE POTENTIAL GAS LEAK, KMTP PROCEEDED TO BLOWDOWN THE LINE AND SUBSEQUENTLY EXPOSED THE PIPELINE SEGMENT IN ORDER TO FIND THE LEAK. THE LEAK WAS CONFIRMED AND DISCOVERED ON JANUARY 13TH AT 7:22 PM. THE 7 FT SEGMENT OF PIPE WAS CUT OUT AND REPLACED. THE CUT-OUT SEGMENT OF THE PIPE WAS SENT TO THE METALLURGY LAB AND KMTP IS CURRENTLY WAITING ON THE RESULTS OF THE TEST. REPAIRS ON THE PIPE WERE COMPLETED, AND THE LINE WAS PUT BACK IN SERVICE ON JANUARY 14TH. THE CAUSE OF THE LEAK IS UNKNOWN AT THIS TIME. A SUPPLEMENTAL REPORT WILL BE FILED ONCE THE METALLURGICAL REPORT IS COMPLETED.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230017 | 37712 | 2023-02-15 14:07 | ORIGINAL | 5304 | FLORIDA GAS TRANSMISSION CO | 1300 MAIN STREET | HOUSTON | TX | 77002 | 2023-01-16 07:30 | 2023 | EASTERN | NO | 29.6638 | -82.8464 | 1357823 | 2023-01-16 15:44 | 1357998 | NATURAL GAS |  | 102600 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | AFFECTED COMPRESSOR WAS ISOLATED. SYSTEM CONTINUED TO RUN WITH SEPARATE UNIT. |  |  |  | NO |  |  | NO | [11 empty] | 0 | 2023-01-16 07:00 | 2023-01-16 07:00 | ONSHORE | FL | 32693 | TRENTON | GILCHRIST | SURVEY STATION NO. | 1336+27 | FLORIDA GAS TRANSMISSION COMPANY | COMPRESSOR STATION 24 TRENTON (F0442) | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTERSTATE | ONSHORE COMPRESSOR STATION EQUIPMENT AND PIPING | COMPRESSOR | [38 empty] | 2000 | 2000 | CARBON STEEL |  | OTHER | [8 empty] | SUCTION VALVE ACTUATOR MALFUNCTION WHICH CAUSED COMPRESSOR UNIT TO VENT THROUGH A BLOWDOWN VALVE. | CLASS 1 LOCATION | NO |  | 737 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 400140 | 400140 | 0 | 0 | 0 | 0 | 1000 | 980.308500164096 | OPERATOR MAN-HOURS | 3.9 | 401140 | 262982.8067910596662624584717607973421927 | 401120.308500164096 | 0 | 0 | 0 | 0 | NO |  |  |  | 740 | 1100000 | 1268 | 192.619(A)(1) |  | 2020-10-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO | [19 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INVESTIGATION DID NOT IDENTIFY CONTROLLER ACTION AS A CONTRIBUTING FACTOR. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | PUMP/COMPRESSOR OR PUMP/COMPRESSOR-RELATED EQUIPMENT | [166 empty] | COMPRESSOR OR COMPRESSOR-RELATED EQUIPMENT | [13 empty] | OTHER | SUCTION VALVE ACTUATOR MALFUNCTION | [20 empty] | YES | RCFA IS PENDING | [161 empty] | MARK BUTEAU | LEAD SPECIALIST DOT COMPLIANCE | mark.buteau@energytransfer.com | 337-451-2944 |  |  |  |  | TODD NARDOZZI | DIRECTOR - REGULATORY COMPLIANCE | 713-989-7126 | todd.nardozzi@energytransfer.com | ON JANUARY 16, 2023, AT APPROXIMATELY 07:00, A FLORIDA GAS TRANSMISSION TECHNICIAN DISCOVERED A COMPRESSOR UNIT VENT VALVE WAS VENTING NATURAL GAS TO ATMOSPHERE AT THE COMPRESSOR STATION 24, NEAR TRENTON, FL. THE TECHNICIAN ISOLATED THE COMPRESSOR AT APPROXIMATELY 0730 HRS. ACCORDING TO COMPANY SCADA, THE VENT VALVE HAD BEGUN VENTING AT APPROXIMATELY 13:00 ON JANUARY 15, 2023, BUT NO OTHER SCADA ALARMS WERE TRIGGERED. THE UNIT WAS SHUT DOWN REMOTELY BY GAS CONTROL AT 11:00 ON JANUARY 15, 2023. THE COMPRESSOR UNIT AUTOMATICALLY VENTS AFTER TWO (2) HOURS OF SHUTDOWN. THE SHUTDOWN AND ALL VALVE POSITIONS INDICATED CLOSURE; THEREFORE, NO ALARMS WERE TRIGGERED. THE VOLUME RELEASED WAS CALCULATED TO BE APPROXIMATELY 102.6 MMSCF NATURAL GAS. THE DETERMINATION TIME FOR THIS ESTIMATE WAS APPROXIMATELY 14:52 ON JANUARY 16, 2023, WHICH WAS FOLLOWED BY THE NRC NOTIFICATION THAT OCCURRED AT APPROXIMATELY 15:44. THE CAUSE OF THE INCIDENT WAS LATER CONFIRMED TO BE A SUCTION SIDE ISOLATION VALVE NOT FULLY SEATING AFTER THE COMPRESSOR UNIT WAS SHUTDOWN. SPECIFICALLY, IT APPEARS THAT THE VALVE ACTUATOR MALFUNCTIONED RESULTING IN THE VALVE NOT FULLY SEATING, THEREBY ALLOWING PIPELINE PRESSURE TO BLEED BY INTO THE COMPRESSOR UNIT CAUSING THE NATURAL GAS TO BE VENTED TO ATMOSPHERE. THE SUCTION SIDE VALVE WAS FULLY CLOSED MANUALLY BY THE TECHNICIAN TO STOP FLOW OF GAS THROUGH THE COMPRESSOR. A ROOT-CAUSE INVESTIGATION IS UNDERWAY, AND THIS INCIDENT REPORT WILL BE SUPPLEMENTED WHEN ADDITIONAL INFORMATION IS AVAILABLE FROM THE INVESTIGATION.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230018 | 37726 | 2023-02-17 15:09 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 4720 PIEDMONT ROW DR. | CHARLOTTE | NC | 28210 | 2023-01-21 17:20 | 2023 | EASTERN | YES | 35.6189 | -80.3958 | 1358400 | 2023-01-24 09:39 | 1358492 | NATURAL GAS |  | 0.01 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | REPLACEMENT WAS ON NORMALLY CLOSED BYPASS PIPING AROUND OPEN MAINLINE VALVE. | [6 empty] | NO | [11 empty] | 0 | 2023-01-21 17:20 | 2023-01-21 17:55 | ONSHORE | NC | 28146 | SALISBURY | ROWAN | NOT APPLICABLE |  | LINE 272-MLV-3 | LINE 272 | NO | PIPELINE RIGHT-OF-WAY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE |  |  |  | NO | [22 empty] | INTRASTATE | ABOVEGROUND STORAGE, INCLUDING ASSOCIATED EQUIPMENT AND PIPING | VALVE | [31 empty] | MAINLINE | BALL |  | ROCKWELL |  |  |  | 1998 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 2 LOCATION | NO |  | 137 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 200000 | 196061.7000328192 | 5000 | 4901.54250082048 | 0 | 0 |  | 0.1 | 205000 | 88657.285854939225 | 200963.24253363968 | 0 | 0 | 0 | 0 | NO |  |  |  | 658 | 3300 | 900 | 192.619(A)(2) |  | 1998-11-16 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | YES | YES | [18 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS TOO SMALL TO REGISTER ON THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [103 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [9 empty] | UNKNOWN | [5 empty] | UNKNOWN |  | YES | PASSENGER CAR | OFF-ROAD | 50 | YES | YES | YES | [236 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | PIEDMONT NATURAL GAS RESPONDED TO A REPORT OF A VEHICLE DAMAGING A MAINLINE VALVE. UPON ARRIVAL OPERATOR OBSERVED VISUAL DAMAGE OF THE BLOWDOWN STACK AND DETECTED A SMALL GAS LEAK FROM A GREASE FITTING ON THE MAINLINE VALVE. UNABLE TO DETERMINE GAS VOLUME.
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230019 | 37739 | 2023-02-22 09:19 | ORIGINAL | 31406 | FRONTIER NATURAL GAS COMPANY | 110 PGW DR. | ELKIN | NC | 28621 | 2023-02-21 12:00 | 2023 | EASTERN | YES | 36.475 | -80.6069 | 136059 | 2023-02-21 12:00 |  | NATURAL GAS |  | 0 | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | NO | WE WERE ABLE TO BYPASS AND REPLACE LEAKING PIPE |  |  |  | YES | OPERATOR | 2023-02-21 12:00 | NO | [5 empty] | OPERATIONAL CONTROL | CONTROLLING FLOW WAS NOT NECESSARY AS PLEDCO FITTING HELD LEAK IN PLACE UNTIL IT COULD BE CUT OUT. |  | OPERATIONAL CONTROL | CONTROLLING FLOW WAS NOT NECESSARY AS PLEDCO FITTING HELD LEAK IN PLACE UNTIL IT COULD BE CUT OUT. |  | 0 | 2023-01-11 12:00 | 2023-01-23 08:00 | ONSHORE | NC | 27030 | MOUNT AIRY | SURRY COUNTY | NOT APPLICABLE |  | FRONTIER NATURAL GAS | TRANSMISSION LINE T-2 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER PAVEMENT |  |  | NO | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [16 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | PIPE | PIPE BODY | 6.625 | NO | 0.188 | 52000 | UNKNOWN | LONGITUDINAL ERW - HIGH FREQUENCY |  | UNKNOWN | EPOXY |  | NO | [26 empty] | 1999 | UNKNOWN | CARBON STEEL |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | YES | METHOD2 | 150 |  | NO | NO | [5 empty] | 7000 | 6862.159501148672 | 0 | 0 | 0 | 0 | 63000 | 61759.435510338048 | 75000 | 73523.1375123072 | 0 | 0 |  | 0 | 145000 | 62708.811946176525 | 142144.73252379392 | 0 | 0 | 0 | 0 | NO |  |  |  | 550 | 20000 | 1000 | 192.624(C)(1) |  | 1999-12-01 | NO | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  |  |  | 40000 | NO |  |  |  | YES |  |  |  | NO | [6 empty] | TRANSMISSION LINE OF DISTRIBUTION SYSTEM | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [204 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  |  |  | CONSTRUCTION | NO | [100 empty] | YES | [41 empty] | YES |  |  | YES | YES |  |  |  | TAYLOR YOUNGER | MANAGER OF COMPLIANCE AND OPERATIONS | tyounger@frontiernaturalgas.com | 336-526-1781 |  |  |  |  | TAYLOR YOUNGER | MANAGER OF COMPLIANCE AND OPERATIONS | 336-526-1781 | tyounger@frontiernaturalgas.com | WRINKLE BEND CREATED DURING INITIAL CONSTRUCTION IN 1999, FOUND WHEN DUG IN 2022- ROOT CAUSE OF THE LEAK ' FAILURE TO PINPOINT AND REPAIR LEAK IN 2018- GRADE 3 LEAKS WERE NOT PROPERLY TRACKED ' PLEDCO WAS USED IN AUGUST 2022, SHOULDN'T HAVE BEEN USED ACCORDING TO MANUFACTURER'S SPECIFICATIONS. ' PLEDCO FAILED IN JANUARY 2023, AND WE CALLED TDW TO STOPPLE AND REPLACED PIPE
2023-02-28 09:42 | YES | NO | GT (Gas Transmission) | 20230020 | 37741 | 2023-02-22 17:27 | ORIGINAL FINAL | 3 | ACADIAN GAS PIPELINE SYSTEM | 1100 LOUISIANA ST. | HOUSTON | TX | 77002 | 2023-01-26 11:00 | 2023 | CENTRAL | NO | 29.8963 | -91.3228 | 1359602 | 2023-02-08 17:41 | 1359742 | NATURAL GAS |  | 67 | 21000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NORMAL OPERATION, INCLUDES PAUSES DURING MAINTENANCE | YES |  | 2023-01-27 15:00 | 2023-02-11 08:30 |  | YES | OPERATOR | 2023-01-26 14:30 | NO | [5 empty] | VALVE CLOSURE |  | 2023-01-27 15:00 | VALVE CLOSURE |  | 2023-01-27 15:00 | 0 | 2023-01-27 10:55 | 2023-01-27 10:55 | ONSHORE | LA | 70538 | BELLE RIVER | ST. MARTIN | SURVEY STATION NO. | 1619+81 | CHICO B | 307-0100 | NO | PIPELINE RIGHT-OF-WAY | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [22 empty] | INTRASTATE | ONSHORE PIPELINE, INCLUDING VALVE SITES | REPAIR SLEEVE OR CLAMP | [38 empty] | 2013 | 2013 | CARBON STEEL |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | NO |  | 430 |  | NO | NO |  |  | NO |  |  | 0 | 0 | 64680 | 63406.35379061372928 | 206 | 206 | 325000 | 318600.2625533312 | 2000 | 1960.617000328192 | 0 | 0 |  | 3.08 | 391886 | 169526.8037893597162312292358803986710963 | 384173.23334427312128 | 0 | 0 | 0 | 0 | NO |  |  |  | 840 | 70 | 970 | 192.619(A)(2) |  | 1966-08-17 | BI-DIRECTIONAL | PRESSURE DID NOT EXCEED MAOP | NO |  |  | NO |  | MANUAL | MANUAL | 89760 | YES | [7 empty] | NO | [6 empty] | TRANSMISSION SYSTEM | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) OR CONTROL ROOM WERE NOT CONTRIBUTING FACTORS IN THIS INCIDENT, THIS WAS A LEAKING CLAMP ON THE PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | [166 empty] | NON-THREADED CONNECTION FAILURE | [17 empty] | SEAL (NOT COMPRESSOR SEAL) OR PACKING | [17 empty] | YES | CLAMP END SEAL FAILURE. | [161 empty] | NATHAN GRAY | SENIOR PIPELINE COMPLIANCE SPECIALIST | ngray@eprod.com | 985-493-4629 |  | NATHAN GRAY | ngray@eprod.com | 985-493-4629 | NHAN TRUONG | SENIOR COMPLIANCE MANAGER | 713-381-2493 | nvtruong@eprod.com | ON JANUARY 26, 2023 AT 11:00 CENTRAL TIME (CT), ENTERPRISE OPERATIONS RECEIVED A CALL FROM A LOCAL FISHERMAN OF BUBBLES IN THE WATER NEAR OUR CHICO B PIPELINE IN THE ATCHAFALAYA BASIN. AT 11:45 CT, OPERATIONS PERSONNEL CONFIRMED THE BUBBLES IN THE WATER WERE NEAR THE CHICO B PIPELINE. ON JANUARY 27, 2023 AT 10:55 CT DIVERS CONFIRMED THE LEAK FROM THE CHICO B PIPELINE. THE UPSTREAM AND DOWNSTREAM MANUAL VALVES WERE CLOSED AT 15:00 CT TO ISOLATE THE LEAK AREA. ENTERPRISE DETERMINED THE EVENT TO BE REPORTABLE TO THE NRC DUE TO EXCEEDANCE OF REPAIR COST ON FEBRUARY 8, 2023 AT 17:41 CT. AN EXISTING PIPELINE CLAMP WAS DETERMINED TO BE LEAKING. THE CLAMP WAS REMOVED AND REPLACED WITH A NEW CLAMP.